## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0292000001 | Yankee-Rowe | 12/06/1999 | 02/25/2000 | ML00368691 | <strong>This is a voluntary LER. (No title given.)</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER. Yankee Nuclear Power Station was permanently shutdown in February 1992 and is currently decommissioning the facility. On December 6, 1999, following an extensive verification of radiation worker exposure records, it was discovered that the personnel exposure for one individual in 1972 was incorrectly recorded due to a mathematical error. The correction of this mathematical error resulted in the identification that the individual received an exposure above the regulatory limits imposed at that time (10CFR20.101).It was also determined that this error had been first discovered in April 1992 and that the exposure records had been corrected at that time. However, at the time of this correction, the exposure was not identified by the correcting individual as an unreported exposure above regulatory limits. By the current regulations in 10CFR20.2203 (amended in 5/21/91 and implemented at YNPS on 1/1/94), this exposure is not an exposure above regulatory limits as the limit was changed from a quarterly to an annual limit. No other previously unidentified exposures above 3 rem/quarter were found following a re-examination of the database.
0292000002 | Yankee-Rowe | 03/15/2000 | 04/15/2000 | ML00370423 | <strong>Fuel Movement Exceeds Travel Height Restriction</strong><br /><i>Abstract:&nbsp;</i>Yankee Nuclear Power Station was permanently shutdown in February 1992 and is currently being decommissioned. In the early 1980s, spent fuel storage capacity was increased by adding an upper tier of fuel storage racks. During preparation to conduct spent fuel inspections in the Spent Fuel Pool, it was discovered that past practice used in moving spent fuel from the lower tier racks to the upper tier racks was contrary to the design basis as described in the FSAR. The FSAR states that "the racks are designed to maintain proper spacing and structural integrity after being impacted by a fuel assembly dropped onto any location from a height of six inches above the top of the racks." The plant procedures for moving fuel assemblies had established a precaution to restrict travel height for moving fuel over lower tier racks. The maximum fuel assembly travel height over "ungrated" SFP racks is six (6) inches above the plane of the top of the rack. Past practice, however, permitted spent fuel movement over the lower tier racks to heights higher than 6 inches to enable movement up and over installed grating for storage in the upper tier racks. This resulted in lifting fuel approximately 13 inches above the racks, which is outside the design basis. As such, this LER is submitted in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis of the plant. No fuel handling evolutions were in progress at the time of discovery of this issue.
2192000001 | Oyster Creek | 01/21/2000 | 02/24/2000 | ML00368695 | <strong>Manual Scram Following Multiple Reactor Recirculation Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2000, at approximately 1049 hours, control room operators manually scrammed the reactor in response to a multiple reactor recirculation pump trip. Human error caused the multiple pump trip during performance of an isolation condenser actuation system surveillance. The isolation condenser actuation system also inserts trip signals into the reactor recirculation pump trip system. After testing the first instrument, the recirculation pump trip system was not properly reset before proceeding to the second instrument. When a test signal was introduced to the second instrument, the pumps tripped as designed. Plant response to the manual scram was normal. A human performance assessment has been completed and corrective actions to reinforce management expectations will be completed.
2192000002 | Oyster Creek | 02/08/2000 | 04/24/2001 | ML01121034 | <strong>Unanalyzed Condition With Backup Pressure Regulator Inoperable Between 25% and 90% Power</strong><br /><i>Abstract:&nbsp;</i>Power operation with the electric pressure regulator or the mechanical pressure regulator out of service is not described in the Final Safety Analysis Report. General Electric Service Information Letter (SIL) 614 warns that during operation without a backup pressure regulator, a downscale failure of the primary pressure regulator could cause closure of the turbine control valves (TCV) without opening the bypass valves or actuation of the anticipatory reactor scram associated with TCV fast closure. Consequently, a scram would occur on either high neutron flux or high reactor pressure, depending on valve closure speed and initial reactor power. The SIL also states that, at less than 90% power for a downscale pressure regulator failure without backup, the margin to thermal limits would be less than previously analyzed. A review of the Oyster Creek operating history has determined there have been periods of power operation at less than 90%power when the backup pressure regulator was out of service. Administrative controls have been implemented to restrict plant operation when the backup pressure regulator is out of service. Additionally, plant specific analysis has confirmed that sufficient margin to thermal limits exists while operating at greater than or equal to 90% rated thermal power.
2192000004 | Oyster Creek | 05/11/2000 | 06/09/2000 | ML00372489 | <strong>Fire Barrier Enclosure Does Not Meet Design Requirements Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On,May 11,2000,at approximately 1300 hours,it was determined that Oyster Creek was outside the design basis for mitigating the consequences of afire. The evaluation for compliance, with Appendix R utilized a fire resistance rating of three hours in accordance with Section III .G.2.a. criteria for the fire barriers enclosing and separating Fire Areas TB-FA-3A and TB-FA-3B,Subsequently, it was determined that while the wall and roof panels of the enclosures are covered with a sufficient thickness of fireproofing material to provide a three hour fire rating, the thickness of the fireproofing material covering the structural steel only provides a fire resistance rating of two hours. The root cause of this condition was the failure to properly translate design basis criteria from Appendix A to Branch Technical Position APCSB 9.5-1 for the fire barrier rating requirements to construction documents and then to properly reflect as-built conditions in the FHAR. Given the fixed fire detection and suppression features in the area,the existing fire resistance rating of the barriers in question, the low combustible loading and potential for a fire and the availability of a trained fire brigade, the safety significance of this condition is considered to be minimal .Additional fireproofing material will be applied to the structural steel in question to provide a three hour rating.
2192000005 | Oyster Creek | 06/01/2000 | 08/07/2000 | ML00374044 | <strong>Failure to Identify that Charcoal Filter Failed Surveillance on Methyl Iodine Removal Efficiency Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>In response to Generic Letter (GL)99-02, GPU Nuclear committed to using ASTM D3803-1989. The review of the GL did not initially recognize that the acceptance criterion for charcoal absorption efficiency would also be affected. The surveillance procedure was modified to reflect use of the new standard and, separately, the acceptance criterion for charcoal absorption was changed. Upon receipt of the test results, the values were entered into a field copy of the procedure, compared to the former criterion and deemed acceptable. In a subsequent review by a system engineer, it was determined that the charcoal in one train had not met the required value. This submittal is a voluntary report. The Oyster Creek FSAR considers the possible loss of the electric duct heaters used to control the relative humidity and enhance the efficiency of the charcoal. The analysis assumes that the charcoal filters will become saturated with water and the charcoal efficiency is reduced to 78%. The analysis concludes that with charcoal filter efficiency at 78%, the offsite doses remain well within the guideline values of 10CFR100. The efficiency of the deficient charcoal was greater than 93%, therefore, the health and safety of the public was not adversely affected. The train of SGTS that failed the acceptance criterion was declared inoperable, and the charcoal was replaced. A review of surveillance procedures will be conducted to determine if any others are susceptible to a similar occurrence.
2192000006 | Oyster Creek | 05/26/2000 | 09/28/2000 | ML00375756 | <strong>Skin Dose Associated with Control Room HVAC System B Exceeds Limit After Re-evaluation</strong><br /><i>Abstract:&nbsp;</i>The "B" control room (CR) heating, ventilation and air conditioning (HVAC) system was installed during the cycle 12R refueling outage. Atmospheric dispersion coefficients (X/Q values) for the B system have been recently determined to be more limiting than the A CR HVAC system with respect to turbine building ground level releases due to a slight but meaningful difference in air intake location. X/Q values were not calculated for the B CR HVAC system at the time of installation. An evaluation using recently calculated X/Q values (Murphy-Campe) for the B CR HVAC system has indicated that the skin dose to control room personnel would exceed the allowable limit if the B CR HVAC system is in operation during the design basis accident. An evaluation of atmospheric dispersion characteristics associated with the B CR HVAC system has been performed using the more recent ARCON96 methodology. The results confirm that ARCON96 X/Qs for the B system are smaller than the original X/Qs for the A system and, consequently, the doses will be less than currently calculated in the licensing basis. X/Q values for both CR HVAC systems were developed using newer (ARCON96) atmospheric dispersion methodology. New dose rates for the CR HVAC systems will be calculated using the ARCON96 X/Qs and the licensing basis will be revised to reflect the use of the ARCON96 methodology.
2192000007 | Oyster Creek | 07/17/2000 | 08/16/2000 | ML00374424 | <strong>Plant Operation Outside of the Technical Specifications due to a Failed Acoustic Monitor</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2000 at approximately 1915 hours while the plant was in the RUN mode, the EMRV NR108A acoustic monitor failed a surveillance test and was declared inoperable. This started a 48 hour Technical Specification action statement. Immediate corrective action was taken to start the troubleshooting process. Troubleshooting with vendor support concluded that the problem was inside containment and would require COLD SHUTDOWN and containment entry to repair. Therefore, Oyster Creek requested and was granted enforcement discretion related to EMRV NR108A acoustic monitor operability. Based on industry experience, we suspect that the cause is a loose or intermittent connection between the accelerometer and the hard line cable to the line driver located in the containment. To prevent recurrence, future installations will use the new vendors pin alignment kit to ensure proper connector pin retention. The failed monitor will be repaired prior to restart from the next time the plant is placed in the COLD SHUTDOWN condition. The spare equipment and cables to be used in the next outage have been prepared using the new pin alignment kit.
2192000008 | Oyster Creek | 08/14/2000 | 09/12/2000 | ML00375134 | <strong>A Degradation in Secondary Containment Resulted in the Completeness of a Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2000 at approximately 07:04 AM, it was determined that Secondary Containment was degraded because the Standby Gas Treatment System (SGTS)could not maintain design negative pressure. A walkdown of the plant was conducted to find the source of the leak. After several unsuccessful attempts to isolate the leak, it was determined that the Secondary Containment ventilation system exhaust valves were leaking. The cause of leakage was age-related degradation of the valve seats. The reactor was shutdown and placed in a condition in which Secondary Containment integrity is not required. The safety significance of this discovery was minimal. Secondary Containment is required to ensure that any primary system leakage into the Secondary Containment will be properly filtered and elevated prior to release to the environment. As a negative pressure was always achieved, only minimal leakages to the environment would have been possible. The vast majority of any leakage would have been processed through the SGTS filters. The identified valves were repaired and a routine maintenance task will be generated to detect future degradation. Additionally, valves of similar characteristics will be inspected for generic implications.
2192000009 | Oyster Creek | 08/17/2000 | 09/14/2000 | ML00375276 | <strong>Missed Technical Specification Required Surveillance Tests Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2000, while the plant was shutdown due a degradation of secondary containment, it was discovered that two surveillances had not been performed as required prior to moving the Reactor Mode Switch from the Shutdown to Refuel position and subsequently exercising control rods. The required surveillances were to be performed in parallel with plant shutdown activities. The purpose of these surveillances is to check the operability of the Intermediate Range Monitor (IRM) System and the Source Range Monitor (SRM) System and associated trip channels using built in calibration equipment. The root cause of this event was personnel error in that the procedure attachment used to track these surveillances was marked NR for each surveillance and signed off by the Shift Manager. This information was not communicated to the oncoming shift. Additionally, the shutdown work schedule was inappropriately changed to indicate they had been completed. Once this omission was recognized, the Reactor Mode Switch was placed in the Shutdown position. Subsequently the SRM surveillance test was executed on 8/17/00 and the IRM surveillance was completed on 8/18/00. Both satisfied the acceptance criteria as operable. Corrective actions will include revising the Plant Shutdown procedure to strengthen the administrative controls on the performance of these surveillances, particularly if they are not completed prior to commencing the shutdown, and revision of the scheduling process to ensure surveillances remain scheduled until actually completed.
2192000010 | Oyster Creek | 10/14/2000 | 01/30/2001 | ML01037027 | <strong>Local Leak Rate Test Results in Excess of Technical Specification Limits due to Component Wear</strong><br /><i>Abstract:&nbsp;</i>On October 14,2000,Local Leak Rate Testing (LLRT) results indicated that Main Steam Isolation Valve V-1-0010 exceeded the Technical Specification leak rate limit of .05(.75) La at 35 psig (equivalent to 15 .98 SCFH). The leak was quantified as 21 .72 SCFH at 35 psig .The cause of this occurrence was component wear. The valve was repaired and the as-left leak rate was 4 .24 SCFH. Additionally,four containment isolation valves in two penetrations were removed from the plant with no as-found LLRT data collected. This was due to a change in the scheduled maintenance on the valves.The four removed valves had successfully passed their five previous as-found LLRTs with no maintenance. The safety significance of these events is considered minimal.The total penetration leakage would have been limited by Main Steam Isolation Valve V-1-0008 in the same steam header.The leakage past V-1-0008 was quantified at 7 .7 SCFH.
2192000011 | Oyster Creek | 11/15/2000 | 12/14/2000 | ML00378076 | <strong>Reactor Scram Due to Low Reactor Water Level Resulting From Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2000, during reactor startup from the 18 R outage, turbine pre-warming had been completed and Operators were transitioning to steam chest warming in accordance with procedures. Reactor Pressure was approximately 460 psig. Due to a misinterpretation of the procedure, the operators did not close the Bypass Valve Opening Jack prior to closing the Load Limiter. This resulted in several Turbine Bypass Valves (BPVs) rapidly opening and a subsequent reactor level increase. Immediate response to the high level condition was to reduce feedwater flow and increase letdown. This action combined with the inventory loss through the BPVs resulted in overcompensating and the level decreased to the low-level scram setpoint. A full reactor scram was received. All control rods inserted. Reactor level was stabilized. Reactor pressure continued to decrease until the bypass valves were shut (approximately 17 minutes into the transient). The main consequence of this transient was the scram, which resulted in the excessive cooldown rate, and exceeded the 100 degrees F per hour Technical Specification limit. The root cause of this event was personnel error. Operators demonstrated a lack of fundamental knowledge with respect to system operations in that they did not fully comprehend the consequences of not closing the bypass valve opening jack prior to closing the limit load and failed to close the BPVs. Corrective actions included revising the procedure to clarify the misinterpreted step. An evaluation of the effects of excessive cool down rate was also conducted.
2202000001 | Nine Mile Point 1 | 03/24/2000 | 04/24/2000 | ML00371095 | <strong>Technical Specification Violation When Noble Gas Grab Sample Not Collected Within Time Frame Required By the Limiting Condition For Operation</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2000, Nine Mile Point Unit 1 (NMP1) was at 100%power with stack effluent monitoring instrumentation inoperable. NMP 1 failed to comply with the Limiting Condition for Operation (LCO) specified in Technical Specification 3.6.14.b when a stack grab sample was not obtained within the required time frame of once per 12 hours. The stack grab sample was collected 38 minutes after the 12 hours expired. The cause was that the impact on priority activities from integration of emergent tasks was not adequately assessed by the technician or supervision. Contributing to this event was the rearranging of tasks to accommodate emergent tasks and inadequate department job coordination. Immediate corrective actions were to collect and analyze a stack grab sample and to have all dayshift chemistry technicians stop work, discuss the event and validate that the technicians understood the consequences of missing an LCO required action. Additional corrective actions taken include :increased the frequency of LCO required actions; provided guidelines and expectations for scheduling LCO actions and assessing changes to shift work scope; created a Chemistry Shift Scheduling Tool to house the administrative corrective actions and discussed the event with the remainder of chemistry technicians by 31 March 2000.
2202000002 | Nine Mile Point 1 | 05/05/2000 | 06/05/2000 | ML00372282 | <strong>Service Water Check Valves Fail Reverse Flow Test</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2000, with the Nine Mile Point Unit 1(NMP1) plant in the cold shut down condition, Service Water check valves 72-21 and 72-22 failed to meet the reverse flow testing criteria of procedure N1-ST-V14, "Service Water Check Valve and Emergency Service Water Pump and Check Valve Test," which is part of the Inservice Testing Program. Emergency Service Water was declared inoperable and the plant entered the action statement of Technical Specification 3.4.5 for the control room air treatment system. The failure of the valves was entered into the corrective action process for evaluation and efforts to repair the valves were initiated in the work control process. On May 7, 2000, work orders that cleaned the pivot pins, bearing caps and packing collars and repacked the valves were completed. The valves were then successfully tested in accordance with procedure N1-ST-V14, Emergency Service Water was declared operable and the plant exited the action statement of Technical Specification 3.4.5. The cause of the surveillance test failure was inadequate preventive maintenance. Check valves 72-21 and 72-22 were cleaned, repacked and successfully reverse flow tested. These valves were added to the Preventive Maintenance / Surveillance Test database for inspection, cleaning and packing replacement at a four-year interval. Niagara Mohawk Power Corporation will review the preventive maintenance activities for all the check valves contained in the NMP1 Check Valve Program Plan, by August 28, 2000, to ensure adequate preventive maintenance is performed.
2202000003 | Nine Mile Point 1 | 09/27/2000 | 04/11/2001 | ML01108001 | <strong>Reactor Trip on Low Reactor Water Level While Placing the Reactor Water Cleanup System in Service</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2000 at 0123 hours, while the plant was shutdown, Nine Mile Point Unit 1 experienced a reactor trip. The operators were placing the reactor water cleanup system in service when the reactor tripped on low reactor water level. When the reactor water cleanup system was placed in service, voids in the reactor water cleanup system were filled with reactor water resulting in the reactor water level decreasing t o the reactor trip setpoint. The cause of the reactor trip was a low reactor water level condition due to inadequate filling and venting of the reactor water cleanup system prior to placing the system in service. The corrective actions revised the procedure used for filling and venting the reactor water cleanup system an d reinforced and monitored Operations management expectations regarding the acceptance of inappropriate system operating characteristics and adequacy of contingency planning. Additionally, the inlet and outlet standby reactor water cleanup filter isolation valves have been repaired and high point vents have been installed in the reactor water cleanup system.
2202000004 | Nine Mile Point 1 | 10/02/2000 | 12/06/2000 | ML00377725 | <strong>Manual Reactor Scram and Unusual Event Declaration Due to Stuck-Open Electromatic Relief Valve and Failed Vacuum Breaker on Electromatic Relief Valve Discharge Line</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2000, during Nine Mile Point Unit 1 plant startup, at approximately 0555 hours, control room personnel identified that Electromatic Relief Valve (ERV) 111 had lifted. The plant startup was stopped and actions to close the ERV initiated. Efforts to close the ERV were unsuccessful and at 0625 hours the plan t was manually scrammed. During the event, a 10-inch, ERV discharge line vacuum breaker, CKV-66-26, failed open. The most probable cause of ERV 111 lifting was a bent pilot valve stem combined with partial disengagement of the disc and stem assembly. The cause of the vacuum breaker failure was design deficiency in that inadequate valve specifications were supplied by the Mark I Program vendor to the valve vendor. Corrective action for the ERV lifting included checking the straightness of the pilot valve stems in the six ERVs, modifying procedures to include straightness criteria for the pilot valve stems and prohibiting the cycling of pilot valves with the solenoid in a depressurized condition, and replacing the stems in the pilot valves for ERV 111 and ERV 112. Corrective action for the vacuum breaker failure included checking the internals of the 10-inch ER V discharge line vacuum breakers and modifying the valve hinge bumper weld in the 10-inch vacuum breakers. Additionally, a design change to correct the design deficiency will be installed by the completion of refueling outage 17.
2202000005 | Nine Mile Point 1 | 11/29/2000 | 01/11/2001 | ML01022023 | <strong>Loss of Secondary Containment due to Both Reactor Building Track Bay Inner and Outer Doors being Opening Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2000, while the plant was at 100 percent, Niagara Mohawk Power Corporation identified that the reactor building track bay inner door had not been fully closed while the outer door was inoperable and open , resulting in a breach of secondary containment. The preliminary investigation concluded that the inner door was partially opened for 2 hours and 39 minutes. On December 12, 2000, further investigation determined that the inner door was partially open for approximately 25 hours. This resulted in a condition that could have prevented the fulfillment of the safety function of secondary containment that affects the control of the release o f radioactive material and a condition that is prohibited by Technical Specifications. The cause of the secondary containment door being partially open is an inadequate procedure. Contributing causes are an inadequate as-built door configuration and a lack of preventive maintenance. The inner door was closed and verified closed. Procedure N1-OP-52, "Reactor Building Track Bay Doors," was revised to provide specific guidance of how operators are to verify that the door is fully closed and a preventive maintenance task will be developed and implemented.
2372000001 | Dresden 2, Dresden 3 | 02/15/2000 | 03/15/2000 | ML00369509 | <strong>Main Steam Low Pressure and Isolation Condenser High Pressure Time Delay Relays Technical Specification Calibration Frequency Intervals Exceeded due to Inadequate Management Oversight</strong><br /><i>Abstract:&nbsp;</i>On February 15,2000 at 1630 hours, during a review of the Improved Technical Specification (ITS)submittal it was determined that the calibration frequency for the Main Steam Low-Pressure Isolation time delay relays were being performed once every 18 months. Technical Specification (TS) Table 4.2.A-1 requires CHANNEL CALIBRATION to be performed on a quarterly frequency. In addition, on February 16,2000 at 1800 hours, it was determined that the calibration frequency for Isolation Condenser time delay relay was being performed once every two years, while TS Table 4.2.D-1 required CHANNEL CALIBRATION to be performed on a quarterly frequency. A detailed review was performed on the channel definition criteria. Completion of the review determined that although the CHANNEL is monitoring pressure and not time delay requirements, station personnel concluded that the CHANNEL CALIBRATION by definition should include the time delay function. Upon discovery of the missed calibration frequencies site personnel immediately performed the required instruments CHANNEL CALIBRATION for both relays with satisfactory results. The cause of this event was determined to be a programmatic weakness in the review process of the Technical Specification Upgrade Project (TSUP), implemented in 1997, associated with the review of the CHANNEL CALIBRATION definition change. The health and safety of the public were not compromised during this condition. Thus the safety significance of this condition is minimal.
2372000002 | Dresden 2 | 06/28/2000 | 07/28/2000 | ML00373809 | <strong>Failure to Recognize Degraded Condition of ASME Section XI Classed Piping/Weld Required Entry into Technical Specification due to Lack of Understanding of the TS Bases</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) 314.6.N "Structural Integrity" requires that structural integrity of American Society of Mechanical Engineers (ASME) Code Class 1, 2 and 3 components be maintained. On April 15, 2000, a small amount of water was found on the floor below the 2D Containment Cooling Service Water (CCSW) Pump discharge elbow following a surveillance test in support of the quarterly High Pressure Coolant Injection (HPCI) Inservice Test (IST) run. Engineering was notified and inspected the piping and the weld on the discharge side of the pump. No leakage was observed. A condition report was written and a pump run scheduled to inspect for leakage at operating pressure. The 2D CCSW Pump run was performed and moisture developed on the weld, this was not enough moisture to drip off of the pipe. Operations logged the inspection as "no leakage". On June 7, 2000, during a 2D CCSW pump run, the leak through the weld was observed to have increased to approximately 1-2 gpm, however TS 3/4.6.N was not immediately entered. The TS was entered on June 8, 2000, after being identified as applicable by Engineering. The root cause is a failure to recognize the leak of the CCSW pipe constituted a loss of structural integrity and required immediate entry into TS 314.6.N due to a knowledge deficiency with regards to the requirements of GL 90-05 "Guidance for Performing Temporary Non-Code Repair of ASME Code Class 1, 2, and 3 Piping" and the applicability of TS 3/4.6.N.
2372000003 | Dresden 2 | 06/29/2000 | 07/28/2000 | ML00373884 | <strong>Technical Specification Non Compliance Due to Untimely Submittal of an ASME Code Relief Request</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2000, at 1800 hours, during a review of the Inservice Inspection Program, it was identified that the snubber visual inspection requirements per Technical Specification (TS) Section 4.0.E were not being met. TS 4.0.E states in part: "Surveillance Requirements for inservice inspection and testing of ASME Code Class 1, 2, and 3 components shall be applicable as follows: 1. Inservice inspection of ASME Code Class 1,2,and 3 components and inservice testing of ASME Code Class 1,2, and 3 pumps and valves shall be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10 CFR Part 50,Section 50.55a(g)and 50.55a(f), respectively, except where specific written relief has been granted by the Commission pursuant to 10 CFR Part 50,Section 50.55a(f)(6)(i),respectively. TS surveillances were being performed in accordance with the alternative requirements described in TS 4.8.F, without obtaining a written relief for exceptions to the ASME Code requirements. TS 4.8.F allowed Dresden Nuclear Power Station to increase the snubber surveillance frequencies for up to forty-eight months as opposed to the ASME Code requirement of eighteen months. These surveillance requirements were implemented following the Technical Specification Upgrade Project (TSUP) in 1996. The cause of this event has been determined to be programmatic weaknesses in the snubber program that resulted in a failure to recognize the conflicting regulatory information and ASME Code requirements for the snubber inspection surveillance requirements.
2372000004 | Dresden 2, Dresden 3 | 11/30/2000 | 07/26/2002 | ML02217056 | <strong>Reactor Scram Due to a Failure to Close Current Transformer Knife Switches Following Maintenance</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2000, with Unit 2 in Mode 1 at 100%reactor power, Nuclear Operational Analysis Department (NOAD) and Sub Station Construction (SSC) personnel entered the 345Kv yard to perform work on the Oil Circuit Breaker (OCB) 2-7 circuit breaker, which was Out Of Service (OOS).To start the evolution, SSC personnel opened knife switches located in the upper portion of the OCB cabinet, per their approved procedure. Shortly thereafter, NOAD personnel opened 12 current transformer cutout knife switches. This was performed without procedure and resulted in a lack of configuration control to assure recovery of the switches following maintenance. SSC personnel remained unaware that this was performed for the duration of the event. At the conclusion of work for the shift, NOAD utilized inappropriate nomenclature when asking SSC personnel whether the knife switches had been re-closed. This resulted in the OCB being returned to service with the knife switches inappropriately positioned (open) causing a Unit 2 reactor scram from full power when the Operators attempted to close the OCB. The root cause, specific to the tripping of the 345Kv OCBs and reactor scram, was determined to be insufficient adherence to management standards, policies, and administrative controls by NOAD personnel. Corrective actions included: the NOAD Department Manager and DNPS NOAD First Line Supervisors were held accountable and disciplinary actions were taken in accordance with station policy; NOAD reinforced management expectations as delineated in procedure MM-AA-7001, "NOAD Management Expectations;" and development and implementation of an action plan that addressed NOAD's failure to instill and enforce management standards, policies and administrative controls.
2372000005 | Dresden 2 | 12/01/2000 | 12/14/2001 | ML02031035 | <strong>Recirculation Loop Temperature Failure Causes Shutdown Cooling Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2000, at 1000 hours, with Unit 2 in hot shutdown during a forced outage the "B" Reactor Recirculation Loop temperature instrumentation loop failed high. Failure of the instrumentation loop resulted in the Shutdown Cooling System (SDC) Isolation valves being interlocked closed. In the event of a unit scram or shutdown these valves must be opened for the SDC system to function. The cause of the event was determined to be degraded thermocouples, cabling and connections. Corrective actions associated with this root cause included, repair or replacement of the thermocouples, connectors and cabling, and replacement of the drywell instrument cable penetration (X202F).
2442000001 | Ginna | 09/18/2000 | 10/18/2000 | ML00376244 | <strong>Intermediate Range Channel Loss of Control Power, Due to Excessive Signal Noise, Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2000, at approximately 0503 EDST, the plant was in Mode 3 with the reactor coolant system being maintained at a temperature between 540 degrees F and 547 degrees F and a pressurizer pressure o f approximately 2235 psig. A planned plant shutdown was in progress, in preparation for beginning the 2000 refueling outage. During this shutdown, a fuse blew in a nuclear instrument system intermediate range circuit, causing a reactor trip. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed. Immediate corrective action was taken to stabilize the plant in Mode 3. The cause of the blown fuse was excessive signal noise in the intermediate range circuit. Corrective action to prevent recurrence is outlined in Section V.B.
2442000002 | Ginna | 09/19/2000 | 10/19/2000 | ML00376245 | <strong>Assumed Plant Fire May Cause Multiple Shorts and Result in Loss of Emergency Diesel Generator, Which is an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2000, the plant was in Mode 5. In activities unrelated to plant conditions, it was discovered that, for a postulated fire in the Screen House, there could be a loss of control power to the "B" emergency diesel generator due to postulated shorting of undervoltage cables from the 480 volt AC safeguards bus 17. This condition created the potential for no emergency diesel generators being available to provide emergency A C power, which is not an analyzed condition. The cause of this condition dates back to the original fire protection analyses which took place in the late 1970's and early 1980's for R.E. Ginna Nuclear Power Plant. Additional isolation fuses have been installed to isolate the specific cables. In the event a fire occurs in the Screen House, these fuses will open to isolate the cables from postulated faults, thus preventing the downstream control power fuses from opening. Corrective action to prevent recurrence is outlined in Section V.B.
2442000003 | Ginna | 09/20/2000 | 10/19/2000 | ML00376244 | <strong>Source Range Channel Not Promptly Discovered to be Inoperable, Due to Personnel Error, Resulted in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2000, at approximately 1652 EDST, with the plant in Mode 5, a nuclear instrument system source range channel became inoperable. This condition was not promptly discovered. When it was discovered, at approximately 0650 EDST, September 21, 2000, it was also discovered that the operators had not recognize d the need to apply the actions required by the plant's Technical Specifications. This constituted a condition prohibited by the plant's Technical Specifications. The cause of the source range channel becoming inoperable was a failure of the detector. The cause of not promptly discovering this condition, leading to not recognizing the need to apply the actions required by the plant's Technical Specifications, was personnel error. After this condition was discovered, the Control Room operators performed actions to assure that the plant was currently in compliance with these requirements. The source range drawer was connected to the spare source range detector and a source range channel was declared operable. Corrective action to prevent recurrence is outlined in Section V.B.
2442000004 | Ginna | 10/14/2000 | 11/13/2000 | ML00377035 | <strong>Two Fans Inoperable During Transition from Mode 5 to Mode 4, Due to Personnel Error, Resulted in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2000, at approximately 1745 EDST, the plant was shut down in Mode 4, having just transitioned from Mode 5 at 1514 EDST. A heatup was in progress, and reactor coolant system temperature was approximately 225 degrees F. It was discovered that two containment recirculation fan cooler fans were inoperable, and had been inoperable during the transition from Mode 5 to Mode 4.This condition is contrary to Ginna Station Improved Technical Specifications Limiting Condition for Operation 3.0.4. The cause of having the two fans inoperable during the transition from Mode 5 to Mode 4 was personnel error. Corrective action was to restore the two fans to operable status. Corrective action to prevent recurrence is outlined in Section V.B.
2442000005 | Ginna | 10/21/2000 | 11/20/2000 | ML00377205 | <strong>Loss of "B" Condenser Circulating Water Pump Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2000, at approximately 1418 EDST, with the plant in Mode 1 at approximately 71% steady state reactor power, the "B" condenser circulating water pump tripped. At approximately 1419 EDST, following procedural direction, the reactor was manually tripped. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. The tripping of the "B" condenser circulating water pump was caused by failure of the excitation voltage transformer, which resulted in loss of excitation field to the pump motor. The cause of the reactor trip was manual operator action. Corrective actions included replacing the excitation voltage transformer. Corrective action to prevent recurrence is outlined in Section V.B.
2452000001 | Millstone 1 | 03/28/2000 | 04/26/2000 | ML00371201 | <strong>Fuel Pool Level Technician Surveillance Missed Due To Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2000, with the unit in a PERMANENTLY DEFUELED CONDITION, it was discovered that the fuel storage pool level had not been recorded in accordance with Surveillance Requirement 4.10.C.The Surveillance Requirement specifies that the level be recorded daily whenever irradiated fuel is stored in the pool. Contrary to this requirement the pool level was not recorded for 33 hours, even though the pool level was monitored and discussed by the shift. The cause of the event is inadequate work practices in that the individuals responsible for completion and review of the surveillance did not perform their duties as required. The spent fuel pool level was maintained more than 4 feet above the Technical Specification limit during entire period of concern. An alarm would have sounded in the Control Room had the spent fuel pool level approached the limit. The corrective actions include coaching and counseling of the personnel involved in the event; reviewing the event with Unit 1 Operations personnel; and reinforcing with Unit 1 Operations personnel the expectations to review of control room logs and to complete priority control room tasks.
2452000002 | Millstone 1 | 11/16/2000 | 11/02/2001 | ML02015000 | <strong>Fuel Rod Accountability</strong><br /><i>Abstract:&nbsp;</i>In September, 2000, during reconciliation and verification of the Millstone Unit No. 1 spent nuclear fuel records, Unit No. 1 personnel concluded that the location of two full-length irradiated spent fuel rods could not be determined, and that these spent fuel rods were not properly tracked in the Special Nuclear Material (SNM) records. In accordance with the requirements of 10 CFR 20.2201(a)(1)(ii) and 10 CFR 50.72(b)(2)(vi) Northeast Nuclear Energy Company (NNECO) notified the Nuclear Regulatory Commission (NRC) on December 14, 2000 that two spent fuel rods from the Millstone Unit No. 1 spent fuel pool were determined to be unaccounted for. The investigation of this condition determined that the spent fuel rod s were either still in the Millstone Unit No. 1 spent fuel pool, or inadvertently transferred to one of three facilities licensed to store or dispose of radioactive material. The investigation also concluded that the health and safety of the public has not been adversely affected as a consequence of the potential inadvertent shipment of these spent fuel rods to any of the three licensed facilities. The Root Cause of this event is attributed to an unrecognized over-reliance upon Millstone Unit No. 1 Reactor Engineers to compensate for organizational and process weaknesses in implementing the SNM inventory and control procedures. Corrective actions will be implemented in accordance with the Millstone Corrective Action Program. On October 5, 2001, Dominion Nuclear Connecticut (DNC) notified the NRC in accordance with 10 CFR 70.52(a), that the rods could be considered lost.
2472000001 | Indian Point 2 | 02/15/2000 | 02/15/2001 | ML01058029 | <strong>Manual Reactor Trip Following Steam Generator Tube Rupture</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2000 at 19:29,Eastern Standard Time (EST), with Indian Point Station, Unit 2 operating at 99 percent reactor power, operators manually shut down the unit and declared an Alert due to a primary to secondary leak in 24 steam generator. The emergency response organization was activated. Operators began cooling down and depressurizing the reactor coolant system as required by procedures. 24 steam generator was isolated at about 20:34. At about 21:00, the rate of the plant cooldown that was in progress was observed to increase. Pressurizer level could not be maintained greater than 9 percent, and at about 21:05, operators manually initiated safety injection. Pressure in the reactor coolant system and 24 steam generator was equalized by 22:50.However, later events caused reactor coolant water to flow into the steam generator secondary side. The cooldown continued, including a transition to the residual heat removal system, on February 16 at 12:40. The plant was brought to cold shutdown on February 16 at 16:57, and the Alert was terminated at 18:50. There was no detectable increase in normal background levels of radioactivity as measured by offsite environmental sampling and monitoring equipment. As a result of the Alert, initial notifications to the State, local county authorities, and the NRC resident inspector were made on February 15 at 20:05. The NRC Operations Center was notified via the Emergency Notification System at 20:08. This report is being made pursuant to 10 CFR 50.73 (a)(2)(I)(A)due to the completion of a plant shutdown required by Technical Specifications as a result of the declaration of the Alert classification.
2472000002 | Indian Point 2 | 03/14/2000 | 04/13/2000 | ML00370832 | <strong>Failure of Cable Spreading Room Fire Dampers To Close During Survillance Testing</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2000, with the unit in cold shutdown condition, four of ten fire dampers in the Cable Spreading Room (CSR) failed to close during the performance of a main transformer deluge test. The cause of the failure of one of the dampers was due to part of the damper being bent. The cause of the failure of the other three dampers has been attributed to the improper installation of "electro-thermal" links (ETL) that are designed to melt when exposed to heat, or in response to an electrical voltage. During the test, the circuits for the ETLs are deenergized by placing the ETL switch in the "Test" position. However, during this deluge test, the ETL5 in all ten dampers were inadvertently energized. The ETL switch is being sent to a laboratory for evaluation. This report is being made per 10CFR50.73(a)(2)(ii)(B) as a condition found to be outside the design basis of the plant. Pursuant to 10CFR50.72(b)(1)(ii)(B), this event was reported to the NRC on March 16,2000. The health and safety of the public was not affected by this event.
2472000003 | Indian Point 2 | 03/23/2000 | 03/28/2001 | ML01089036 | <strong>Steam Generators 21 and 24 Classified as Category C-3 per Technical Specification Table 4.13-1</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2000, Indian Point Unit 2 steam generator inspection results were classified a s Category C-3 in accordance with Technical Specification Table 4.13-1. Indian Point Unit 2 was manually shutdown on February 15, 2000 due to the detection of a primary to secondary leak in 24 steam generator. Eddy current inspections of all active steam generator tubes were subsequently initiated following the plant shutdown. On March 23, with approximately 9 0 percent of the inspections performed, 21 and 24 steam generators were determined to have more than 1 percent of their tubes inspected defective. Per Technical Specification Table 4.13-1, a steam generator would be classified as Category C-3 if more than 10 percent of the total tubes inspected were degraded, or if more than 1 percent of the tubes inspected were defective. The majority of the indications were located at the support plate intersections and at Row 2 U-bend areas. Several improved inspection techniques were used to assess steam generator tube degradation, including ultrasonic testing and use of high frequency eddy current inspection probes. The inspections have confirmed that the root cause for the tub e failure in 24 steam generator was Primary Water Stress Corrosion Cracking (PWSCC) in the ape x of the U-bend region of the tube identified as Row 2 Column 5. This report is being made per 10 CFR 50.73(a)(2)(ii)(A) as a condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly compromise s plant safety. Pursuant to 10 CFR 50.72(b)(2)(I), this condition was reported to the NRC on March 23, 2000.
2472000004 | Indian Point 2 | 04/06/2000 | 05/04/2000 | ML00371299 | <strong>Design Basis Compliance Failure Due to Spent Fuel Storage Rack Boraflex Degradation</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2000, Northeast Technology Corp (NETCO)presented the preliminary results of the BADGER (Boron-10 Areal Density Gauge for Evaluating Racks)testing of the Unit 2 spent fuel racks. The preliminary results showed that besides thinning, some Boraflex panels have developed gaps. The maximum size of the gaps is 7 inches. Since the rack design is supposed to provide unrestrained shrinkage of Boraflex to preclude any mechanism that might cause gaps to form, no gap formation was assumed in the current criticality analysis. Therefore, the assumptions used in the current criticality analysis are no longer met. Interim corrective actions included "checkerboarding" the fuel assemblies in the spent fuel pool. Analysis performed by NETCO demonstrates that with this fuel "checkerboard" pattern, the spent fuel pool Keff can be conservatively maintained below 0.95 without taking credit for the soluble boron in the spent fuel pool water. The cause of the Boraflex degradation is high cumulative gamma radiation exposure and long term exposure to the spent fuel pool water.
2472000005 | Indian Point 2 | 04/20/2000 | 05/22/2000 | ML00371873 | <strong>Steam Generator Primary to Secondary Side Design Pressure Differential Exceeded</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2000 Consolidated Edison Company of New York, Inc., the licensee for Indian Point Unit 2 received a letter from Westinghouse Electric Company, the Nuclear Steam Supply System (NSSS) supplier, which stated that Westinghouse was in the process of completing a Nuclear Safety Advisory Letter regarding the primary to secondary design differential pressure in the steam generators [EIIS :SG ]. At the time of discovery of this condition, the plant was in a refueling outage. The current design pressure listed in the steam generator equipment specification is 1550 psi. Based upon past operating cycle steam generator dome pressure values of approximately 700 psia, this design pressure would be exceeded. However, Westinghouse has performed an analysis which demonstrates that acceptable stress results may be obtained if a new design pressure differential of 1700 psi is assumed. This condition will be corrected prior to plant restart, by updating the design specification and stress reports in accordance with Section IWA-4312, Rerating, of Section XI of the ASME Code, 1995 Edition with 1996 Addenda, thereby demonstrating compliance with the Code. No equipment failures occurred as a result of this condition. This report is being made per 10 CFR 50.73 (a)(2)(ii)(B)as a condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. Pursuant to 10 CFR 50.72(b)(2)(i), this condition was reported to the NRC on April 20, 2000.
2472000006 | Indian Point 2 | 08/03/2000 | 10/23/2000 | ML00376413 | <strong>Source Range Detector High Flux Trip Circuitry Outside of Plant Design Basis Due to Revised Local Cabinet Temperature Uncertainty</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2000, with the plant at cold shutdown, a determination was made that the source range portion of the Nuclear Instrumentation System (NIS) was outside of the plant design basis. It was determined that the temperature errors associated with the maximum control room design temperature limit of 120 degrees F had not been explicitly accounted for in establishing the current high flux trip set point of 5.0E5 counts per second (cps).The original set point supplied by Westinghouse was 1.0E5 cps. Data taken during Cycle 1 startup physics testing in 1973 showed the source range and intermediate range detector overlap curve to be slightly different than expected. To prevent unnecessary reactor trips on high source range indications, Westinghouse recommended changing the trip set point from 1.0E5 cps to 5.0E5 cps. However, the temperature errors associated with the maximum control room design temperature limit of 120 degrees F were not explicitly accounted for, based on information available and the set point methodologies used in 1973. LER 2000-006-00 stated that the set point was lowered to 2.3E5 cps to assure system operability during maximum expected operating temperatures in the control room. This is not the case. While the calculation for the new set point value has been approved, the set point change had not been implemented. The set point change will be implemented prior to the reactor trip breakers being closed. The reporting error is not considered significant, nor was the public health and safety affected, since the reactor trip breakers are open.
2472000007 | Indian Point 2 | 11/17/2000 | 05/31/2001 | ML01158010 | <strong>Administrative Error Leads to Exceeding Tech Spec 4.10 Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2000, with the unit at zero percent power and in a refueling outage, an internal audit identified that several Technical Specification required surveillances were inadvertently exceeded. These surveillances are required to be performed every 31 days by Technical Specification Sections 4.10.A (items 4 and 5), "Radioactive Liquid Effluents," and 4.10.B (items 4, 5, and 6), "Radioactive Gaseous Effluents." These radioactive effluent surveillances are dose calculations and dose projections performed utilizing data from the previous month, and then documented in a single report around the 15th of each month. However, the surveillance for the month of October 2000 had been documented earlier than usual (10/5/2000).During an internal audit, it was subseouently discovered that the November surveillance had been documented on the 15th, thereby exceeding the 31 days allowed by the Technical Specifications. Furthermore, when allowance is taken for the maximum allowable extension of 25 percent per Technical Specification 4.0.1, the surveillance interval was still exceeded by 3 days. Since the surveillances (cumulative and projected doses) evaluate data from the previous month, and the affected surveillances were satisfactory and did not reveal any radiological release or dose limits being exceeded, there were no adverse safety consequences as a result of this event.
2472000008 | Indian Point 2 | 12/07/2000 | 01/08/2001 | ML01010025 | <strong>Refueling Water Storage Tank Sampling Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2000, with the unit at zero percent power, an internal licensee audit identified that between April 10, 2000 and June 1, 2000, the curie content of the Refueling Water Storage Tank (RWST) had not been determined. During this period, the plant was in an extended refueling outage, requiring several large RWST water inventory adjustments. Technical Specification 4.10.A.6 requires that the quantity of radioactivity in the RWST be determined at least once a month when radioactive materials are being added to the tank. Furthermore, Technical Specification 3.9.A.5 requires the quantity of radioactive material in the RWST to be less than or equal to 10 curies, excluding tritium and dissolved or entrained noble gases. In accordance with established procedures, Chemistry personnel normally obtain a monthly RWST sample and determine boron concentration and gross activity. However, at the time that the sample was to be obtained, the RWST water inventory was below the level at which a representative sample could be obtained. The surveillance was not rescheduled to meet the Technical Specification requirements. During the time the RWST was not sampled, there were no liquid releases from the RWST to the environment. Therefore, there were no adverse safety consequences as a result of this event.
2472000009 | Indian Point 2 | 12/21/2000 | 01/23/2001 | ML01037037 | <strong>Accumulator Pressure Potentially Exceeded Analytical Limits</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2000, with the plant at hot shutdown conditions and Tavg approximately 330 degrees F, it was determined that the safety injection accumulator tank pressure may have exceeded the value assumed in the accident analysis. This condition was identified during a review of accident assumption sand inputs. It was determined that plant procedures and alarm setpoints may not control operation of the accumulators within the upper pressure limit assumed in the best estimate loss of coolant accident analysis (LOCA) analysis. Procedures and alarm setpoints were revised to ensure accumulator pressure was controlled within the required limit prior to entering a plant condition requiring operability of the accumulators. Evaluations conducted during the investigation of the issue verified that the plant had remained within its design basis. The cause for the potential operation of the plant outside the analytical limit was an incomplete implementation of Technical Specification Amendment 188 with respect to accumulator pressure limits. There were no actual or potential safety consequences as a result of this event. This condition is being reported as a voluntary report.
2492000001 | Dresden 3 | 03/24/2000 | 04/24/2000 | ML00371050 | <strong>Instrument Root Valve Found Closed During Unit 3 LPCI System Pump In-Service Testing</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2000 at 2047 hours, during the performance of surveillance DOS 1500-10, "LPCI System Pump Operability Test With Torus Available and In-Service Testing (1ST) Program", the 3C LPCI (Low Pressure Coolant Injection) Pump was started and then the 3D LPCI Pump was secured. Control room annunciator alarm 903-3 H-13, "LPCI/CS PP AT PRESS" cleared when it should have remained in the alarmed state. Operators were dispatched t o investigate why the alarm did not remain in the alarm state with the 3C LPCI Pump running. It was identified that th e instrument header root valve (3-1554C-HV) for the Unit 3 LPCI Pump Automatic Depressurization System (ADS) 10 0 psig permissive pressure switches (PS 3-1554H and PS 3-1554C) was in the incorrect position (closed). An investigation into the event utilized the Control Room Sequence of Events Recorder to determine that the header root valve was closed sometime after September 28, 1999 and prior to December 28, 1999. Based on the investigation performed, the exact time or group responsible for the loss of configuration control event could not b e determined but is not believed to have been performed as part of a surveillance activity. The most likely root cause for the event is human error involving failure to self-check / verify. Corrective action includes implementing procedures and verification practices to ensure concurrent verification is performed during instrument valving, both during the isolation of instruments and return of instruments to service.
2492000002 | Dresden 3 | 05/03/2000 | 06/02/2000 | ML00372240 | <strong>Reactor SCRAM Caused by Failure to Use Correct Procedural Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2000, at 0946 hours, Dresden Operating Department began to transfer the "B" Reactor Protection System (RPS) Bus from its Normal Power Supply to its Reserve power supply per station procedure DOP 0500-03, "Reactor Protection System Power Supply Operation." The "3A" MG Set Drive Motor feeds the "3B" RPS bus. During this evolution, the breaker to the "3B" MG Set Drive Motor (hence "3A" RPS Bus) tripped on thermal overloads causing a loss of the "3A" RPS Bus and an automatic reactor SCRAM. The cause for the "3B" MG Set Drive Motor breaker tripping on thermal overloads was due to the breaker thermal overload trip setpoint being set too low due to the wrong acceptance criteria utilized by the electrician during the performance of a preventive maintenance activity. The reason for not identifying the wrong acceptance criteria prior to returning the breaker to service was failure to verify acceptance criteria. The safety significance of this event was minimal. All safety systems operated as designed and all ECCS system s were available to mitigate the consequences of an accident.
2492000003 | Dresden 3 | 05/04/2000 | 12/14/2001 | ML02031034 | <strong>Manual Scram on Loss of Vacuum from Air Binding of Condenser Tubes Due to Off-Gas Recombiner Train Failure</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2000, at 2018 hours, Operations inserted a manual reactor scram per station procedure when the condensate inlet temperature to the demineralizers reached 135 degrees. A degrading condenser vacuum during a plant startup, coupled with an increasing condensate temperature characterize d this event. A manual scram was initiated per procedure, on high condensate temperature, to protect the condensate demineralizer resins. The root cause of this event determined four specific areas of failure that in the aggregate establish the conditions that resulted in Operations inserting a manual scram. The four specific areas include, 1) failure of the 3A Offgas (OG) system was determined to be installation of an incorrectly sized orifice, 2) failure to follow procedures by the system engineer involved with post modification testing of the system, 3) failure of system flow indication was caused by inappropriate application of the installed flow element, and 4) failure of the Seal Steam Bypass valve yoke was determined to be a procedural deficiency which allowed inappropriate use of the valve at Reactor pressures higher than designed. Corrective actions include installation of correctly sized orifice into the 3A OG system, revised operating procedures t o ensure the 3A OG Condenser is not overloaded under normal operating conditions, revised operating procedure to ensure Seal Steam bypass valve is operated <250 psig Reactor pressure and counseled the system engineer on the importance of strictly following the post modification testing and special procedures, including creating proper acceptance criteria. The safety significance of this event was minimal. Plant equipment response was per design. The Operations decision to manually scram was proper per procedure and pre-briefed in accordance with conservative decision making philosophy. With exception of the abnormalities causing and contributing to the need for a manual scram, plant equipment response was per design and required no operator action.
2492000004 | Dresden 3 | 09/18/2000 | 02/15/2001 | ML01053003 | <strong>Technical Specification Non-Compliance Due to Primary Containment Inboard and Outboard Feedwater Isolation Valves Exceeding Local Leak Rate Test Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2000, at 2230 hours, with Unit 3 shutdown for Refuel Outage D3R16, the Primary Containment Outboard Feedwater Check Valve 3-0220-62A failed the as found local leak rate test (LLRT) during performance o f Dresden Operating Surveillance (DOS) 7000-26, "Local Leak Rate Testing Of Unit 2(3) Feedwater System Valves. " Since this valve is paired in series with Inboard Feedwater Check Valve 3-0220-58A that also failed its LLRT, this placed the unit in a condition prohibited by the Technical Specifications. The safety significance of the leakage through the primary containment isolation valves is considered to be minimal. Both valves were inspected, repaired and tested satisfactorily prior to the completion of D3R16. The investigation resulted in two root causes. For valve 3-0220-58A, the 18-bolt seat assembly installed was determined to be a poor design for this application. For valve 3-0220-62A, the valve had normal wear creating a gap between the seats. Corrective actions taken include the installation of a new 20-bolt assembly with an o-ring style seat for the 3-0220-58A valve. The repaired valve successfully passed the LLRT. The 3-0220-62A valve sea t assembly was replaced and tested satisfactorily. In addition, preventive maintenance tasks will be created o r revised to replace the seat assembly at least every four refueling outages.
2492000005 | Dresden 3 | 09/20/2000 | 03/16/2001 | ML01081028 | <strong>Technical Specification Non-Compliance Due to Primary Containment 'B' Inboard and Outboard Main Steam Isolation Valves Exceeding Local Leak Rate Test Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2000, at 1830 hours, with Unit 3 shutdown for Refuel Outage D3R16, the Primary Containment Outboard Main Steam Isolation Valve 3-0203-2B failed the as found local leak rate test (LLRT) during performance of Dresden Operating Surveillance (DOS) 7000-02, "Local Leak Rate Testing Of Main Stream Isolation Valves (Wet Test)." Subsequently, an informational leak test of the Inboard Main Steam Isolation Valve 3-0203-1B identified high leakage. The total leakage through the two valves was declared to be undetermined placing the unit in a condition prohibited by the Technical Specifications. The safety significance of the leakage through the primary containment isolation valves is considered to be minimal. The root cause for the LLRT failure of the inboard 2-0203-1 B MSIV was due to normal wear indications on the main seating surface. The root cause for the LLRT failure of the 3-0203-2B MSIV was due to pre-testing manipulation of the valve and closing the valve with less than full closing pressure rather than by its normal mode, using air pressure and spring force as the motive force. Corrective actions performed were that both valves were inspected, repaired and tested satisfactorily prior to the completion of D3R16. Additionally, the administrative requirements to properly control OOS sequencing for performance of MSIV LLRT activities during refuel outages are to be incorporated into the MSIV scheduling logic.
2492000006 | Dresden 3 | 09/27/2000 | 10/22/2001 | ML02003038 | <strong>Unanalyzed Condition Resulting From Inadequate Design Control for Bus 34 Undervoltage Relay</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2000, at 1845 hours, with Unit 3 shutdown for Refuel Outage D3R16, during the performance of Division II (Div II) Undervoltage (UV) testing, the Overvoltage (OV) coil in relay 127-2-B34 failed. The failure of this relay caused the test to be suspended until replacement of the failed relay was completed. The new relay was installed and it subsequently failed during testing. The cause of the failure was an improper overvoltage coil tap setting. The root cause of this event was ineffective design configuration control for the relays. Contributing to this was inadequate questioning attitude of the System Engineer and System Protection, Operation Analysis Department, as a result of the historical method of control for relay settings. The corrective action for this event is to include relay configuration in a station approved design control process. Based on a risk assessment, the safety significance of this event is minimal.
2492000007 | Dresden 3 | 10/03/2000 | 11/02/2000 | ML00376727 | <strong>HPCI System Declared Inoperable due to Faulty HPCI Pressure Switch Resulting in the Loss of Ability to Reset the HPCI Turbine</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2000, at 2151 hours, with Unit 3 returning to full power after completion of a refuel outage (D3R16), the High Pressure Coolant Injection (HPCI) System was declared inoperable during the performance of DOS 2300 03, "High Pressure Coolant Injection System Operability Verification," when a Nuclear Station Operator identified that the blue turbine trip reset light on main control room panel 903-3 was not illuminated. During troubleshooting of the HPCI Turbine Stop Valve Reset Pressure Switch, it was determined that the internally sealed contacts for the pressure switch had failed preventing remote reset of the HPCI logic. The cause of this event was determined to be degradation of the Unit 3 HPCI Turbine Stop Valve Reset Pressure Switch 3-2303-PS1 accelerated by a switch solenoid valve failure on June 12, 1997 allowing the maximum inrush current for the switch to be exceeded. Corrective actions for this event include replacement, calibration and satisfactory testing of the pressure switch, perform an evaluation of the pressure switch upon removal in approximately one year, evaluate those results for potential increase in preventive maintenance frequencies and incorporate additional post maintenance testing requirements for the SV8 solenoid valve. The safety significance of this event was determined to be minimal.
2502000001 | Turkey Point 3 | 03/11/2000 | 04/06/2000 | ML00370588 | <strong>Steam Generator Tube Plugging Places Steam Generator 3B in Category C-3</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2000, with Turkey Point Unit 3 in a refueling outage, eddy current testing of the Unit 3 steam generators identified that more than one percent of the first sample (1 tube of 96 tubes selected) in the B steam generator exceeded program acceptance criteria. This placed the B steam generator inspection results into Category C-3. As required by the Turkey Point Technical Specifications 3/4.4.5, "Steam Generators," Table 4.4-2, a 4-hour, non-emergency report to the Nuclear Regulatory Commission was made pursuant to 10 CFR 50.72(b)(2)(i). The inspection of the three steam generators was completed on March 16, 2000. A total of 69 tubes in the three steam generators were plugged as a result of this inspection. Five of these tubes were plugged due to mechanical wear at the anti vibration bars in the u-bend; one of these tubes exceeded the plugging limit specified in the Turkey Point Units 3 and 4 Technical Specification, Section 4.4.5.4.a, and the other four were preventatively plugged prior to exceeding the limit. The remaining 64 tubes contained possible corrosion degradation or original manufacturing indications, and were plugged on detection. Turkey Point maintains a comprehensive steam generator program to minimize steam generator tube degradation.
2502000003 | Turkey Point 3, Turkey Point 4 | 08/01/2000 | 08/31/2000 | ML00374810 | <strong>Incorrect Limit Switch Wiring Design of Containment Isolation Solenoid Valves</strong><br /><i>Abstract:&nbsp;</i>On 8/1/00, with the Turkey Point Units 3 & 4 at 100% in Mode 1, FPL determined that the indicating light circuits of containment isolation solenoid valves SV-3/4-2911, SV-3/4-2912, and SV-3/4-2913 did not comply with the requirements of Regulatory Guide 1.97 for accident monitoring instrumentation, or with the description in the UFSAR Tables 7.5-1 and 7.5-2. The valves are equipped with limit switches which change state at the fully opened and fully closed positions. The open limit switch provided contact output to a relay which controlled the red, green, and white position indicating lights. The position indication was designed and wired to provide Open/Not Open indication, rather than the Open/Closed indication stated in the UFSAR, or the Closed/Not Closed indication required by Regulatory Guide 1.97.This design existed on both units. This condition was reported on August 1, 2000, under the requirement of 10 CFR 50.72(b)(1)(ii)(B) as a condition that is outside of the design basis. The cause of this event was human error in designing the wiring of the limit switches in the early 1970s, which provided inaccurate indication of valve position. The limit switch wiring was modified and the UFSAR Tables 7.5-1 and 7.5-2 will be updated to bring the valve position indication into conformance with Regulatory Guide 1.97 requirements.
2512000001 | Turkey Point 4 | 01/24/2000 | 02/23/2000 | ML00368700 | <strong>Manual Reactor Trip due to Main Feedwater Flow Control Valve Cage Disengagement</strong><br /><i>Abstract:&nbsp;</i>At approximately 7 :30 AM on January 24, 2000, FPL's Turkey Point Unit 4 reduced power to 95% t o investigate main feedwater flow instabilities caused by the "A" Steam Generator (SG) Feedwater Flo w Control Valve, FCV-4-478. At approximately 11:14 AM feedwater flow appeared to increase causing a SG level deviation. The Operators placed FCV-4-478 in manual operation. A preliminary determination of valve internal problems versus control problems resulted in the decision to shut down the Unit b y performing a fast load reduction. At approximately 11:42 AM, the Reactor Control Operator (RCO) manually tripped the reactor due to difficulty in controlling SG levels. All rods were fully inserted and all systems except Feedwater functioned as designed. The immediate cause of the reactor trip was a manual action taken by the RCO in response to Mai n Feedwater flow instabilities. The underlying cause of the trip was a failure in FCV-4-478 valve internals. The valve cage had disengaged from the valve body web. The root cause of the failure of FCV-4-478 is inadequate change management in the 1980's when the practice of periodic replacement of the cage was stopped; specifically, FPL failed to require periodic re-torque of a re-used FCV cage. FCV-4-478 was repaired. FPL established inspection controls to monitor for signs of valve degradation. Cage torque will be verified for all feedwater FCV at the next opportunity.
2512000002 | Turkey Point 4 | 09/30/2000 | 01/16/2001 | ML01023027 | <strong>Containment Ventilation System Inoperable due to Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>During the Unit 4, Cycle 18/19, refueling outage, reactor core offload was started on September 30, 2000, with the containment purge system in operation. However, all of the required testing of the containment purge system was not completed. Generation of the isolation signal was tested, and the valves were stroked manually, but the automatic isolation function was not tested as required b y Technical Specification 4.9.4. The root cause was inadequate procedures. The purge valves were not originally intended to be opened during core alterations. When plans changed, the impact of the change was not adequately reviewed since the controlling procedures did not trigger a re-review. Because containment (including purge valve closure) is not credited in the fuel handling accident analysis, the health and safety of the public were not affected by the inadequate surveillance test. The two procedures identified as inadequate will be revised. Implementing procedures for all of the refueling section of Technical Specifications will be reviewed to determine if there are other instances where a procedure provides condition options and does not provide a barrier to reconsider the impact if the condition changes. Personnel involved have been counseled. This event has been discussed with each operating crew.
2512000003 | Turkey Point 4 | 10/05/2000 | 11/06/2000 | ML00376855 | <strong>Emergency Containment Filter Charcoal Failure to Meet Surveillance Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2000, during the Florida Power and Light (FPL) Turkey Point Unit 4 refueling outage, it was reported to FPL that charcoal samples from the 4A, 4B, and 4C Emergency Containment Filters (ECFs) did not meet the acceptance criteria as specified in Technical Specification 4.6.3.b.2 of less than 35% penetration of methyl iodide. The cause of the charcoal failing it s penetration test appears to be the age of the charcoal, combined with the application of a more stringent charcoal test method. FPL replaced the charcoal in the 4A, 4B, and 4C ECF with new charcoal which meets the state d performance requirements of Technical Specification 4.5.3.b.2 prior to Unit 4's entry into Mode 4. The removal efficiency of the tested charcoal was above the 30% removal efficiency for methyl iodide required by Section 6.3.1 of the Updated Final Safety Analysis Report. Therefore, the design function of the ECFs could still be accomplished and the offsite dose would not exceed the 10 CFR 100 guidelines. The reduced efficiency of the charcoal would not have adversely affected the health and safety of the public.
2512000004 | Turkey Point 4 | 10/21/2000 | 11/16/2000 | ML00377043 | <strong>Loss of Offsite Power and Actuation of Safety Injection While In Mode 3</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2000, Turkey Point Unit 4 was in Mode 3 while restarting from the Cycle 19 refueling outage. The 4 kV vital buses were being powered from the startup transformer. At approximately 0425 hours, the startup transformer tripped causing a loss of offsite power (LOOP) to the 4 kV vita l busses. The LOOP automatically started all Auxiliary Feedwater (AFW) pumps, the 4A and 4 B Emergency Diesel Generators (EDGs), and the associated Emergency Load Sequencers. The 4A and 4B EDG's re-energized their respective 4 kV vital buses. An unusual event was declared at 043 5 hours. As a result of the low decay heat and the loss of Reactor Coolant Pump (RCP) heat input, the steam demand from the 4B Steam Generator (S/G), supplying steam to steam driven AFW Pump s caused a safety injection actuation at 0557 hours due to differential pressure between the steam line and the 4B S/G. Safety injection was reset, offsite power was restored at 0616 hours, the EDGs were shutdown, and the plant was stabilized by restoring forced cooling using the RCPs. Turkey Point Unit 4 exited the unusual event at 0645 hours. The cause for the loss of the startup transformer was the internal failure of a control cable in the circuit for the string bus differential relays that provides the 4 kV breaker failure backup protection for the startup transformer. The faulted cable was removed from service.
2542000001 | Quad Cities 1, Quad Cities 2 | 02/03/2000 | 03/03/2000 | ML00368914 | <strong>Inadvertent Start of the Shared Emergency Diesel Generator During Automatic Depressurization System Logic Testing</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2000, at 1021 hours, Unit 1 was in the Run Mode at 100% power and Unit 2 was in the Refuel Mode when an Electrical Maintenance (EM) worker inadvertently actuated a relay during the performance of an Automatic Depressurization System Logic Test. This caused the Shared Emergency Diesel Generator (EDG) to auto-start. The root cause of this event was an ineffective work practice Corrective actions will include skill based refresher training on finger block installation. The safety significance of this event was minimal. In the event that either Unit EDG was needed they were operable. There was a similar event in January 1998, (LER 1998-001.) However, the circumstances surrounding generation of the auto start signals were not common between these two events.
2542000002 | Quad Cities 1, Quad Cities 2 | 10/04/2000 | 04/10/2002 | ML02134053 | <strong>Inadequate Calibration of Post Accident Torus Temperature Monitors</strong><br /><i>Abstract:&nbsp;</i>At 1630 hours on October 4, 2000, with Unit 1 at 100% power and Unit 2 at 83%power, it was determined that a full loop calibration was not being performed on the torus water temperature recorders (TR) 1(2)-1640-200A and 200B as required by Technical Specifications. Technical Specification Table 4.2.F.1, "Accident Monitoring Instrumentation Surveillance Requirements," required that the torus water temperature post-accident monitors receive a channel calibration once every 18 months. Although the recorders were being calibrated as required, the full loop instrument calibration was not being performed. The root causes of this event were historical weaknesses in the modification process that resulted in a failure to specify periodic calibration of the instrument loop and inadequate tracking and maintenance of instrument loops identified to address Regulatory Guide (RG) 1.97 variables. On October 5, 2000, the loops on Unit 1 and Unit 2 were calibrated and found to be within acceptable limits. Also, daily channel checks are performed by Operations to compare the average temperature indicated on TR 1640-200A and 200B with torus temperature indicated by other instrumentation and confirm agreement within 10°F. Therefore, the safety significance of this event is minimal. This event is reportable in accordance with 10 CFR 50.73 (a) (2)(i)(B).
2542000003 | Quad Cities 1 | 03/21/2000 | 05/02/2000 | ML00371285 | <strong>Unit 1 High Pressure Coolant Injection Subsystem Auxiliary Oil Pump Failure to Continue Running on an Auto-Initiation Signal During Logic Functional Test.</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2000 at 1758 hours the Unit 1 High Pressure Coolant Injection (HPCI) Auxiliary Oil Pump (AOP) failed to continuously operate when initiated as a part of QCOS 2300-29, "HPCI System Logic Functional Test." The AOP was observed to cycle on and off about every 3 seconds for approximately 10 minutes when given an auto-start signal as a part of the surveillance test. The logic test was stopped and an adjustment was made to the oil Pressure Regulating Valve 1-2399-PRV3 (PRV #3). The valve was adjusted to maintain a slightly lower pressure. Two more tests of the auto-initiation logic of Unit 1 HPCI were performed and on each of these occasions the AOP started and continued to run, normally. The logic testing was completed with satisfactory results. The root cause of this event was inadequate design margin between the AOP trip setpoint and the control oil header pressure maintained by the setpoint of PRV #3. The safety significance of this event was minimal. The Automatic Depressurization System and Low Pressure Emergency Systems were operable during this event.
2542000004 | Quad Cities 1, Quad Cities 2 | 05/19/2000 | 09/13/2000 | ML00375315 | <strong>Trip of Safety-Related Control Room Emergency Ventilation System Refrigeration Control Unit</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2000, during performance of QCOS 5750-02, "Control Room Emergency Filtration Monthly Test," the safety related control room emergency ventilation (CREV) refrigeration control unit (RCU) tripped due to a loose local control switch cam follower retaining screw. The CREV RCU was declared inoperable and at 1334 hours a 4hour Emergency Notification System phone call was made in accordance with 10CFR50.72(b)(2)(iii)(D). On May 23, 2000, while the switch was being verified to operate correctly, it was discovered that the switch ha d been incorrectly assembled on December 16, 1999. The switch was reassembled correctly and tested. The root cause for this event was determined to be an inadequate decision during a troubleshooting effort. A previous occurrence involving the loose retaining screw had not been adequately investigated. The switch was replaced. Further corrective actions include replacement and inspection of the switch in one year, determination of further replacement frequency based on the inspection, and training for the Engineering department concerning troubleshooting. The safety significance of this event was minimal. The CREV system filtration capability was not lost, control room temperature was maintained during the event, and the non-safety related train of control room ventilation was operable throughout this event.
2542000005 | Quad Cities 1 | 05/23/2000 | 06/22/2000 | ML00372723 | <strong>Failure to Demonstrate Operability of Offsite Power Source in Response to Emergency Diesel Generator Inoperability in Timeframe Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2000, at 0837 hours, the Unit I Emergency Diesel Generator (EDG) was taken out of service (OOS) for scheduled quarterly and six-year preventive maintenance. During the afternoon shift it was discovered that the demonstration of operability of offsite power sources required by Technical Specifications (TS) to be performed within one hour had not been performed. The demonstration of operability of offsite power sources was completed satisfactorily at 1600 hours. At 1921 hours the EDG was declared operable. The root causes of the missed TS surveillance are inadequate procedural adherence and weaknesses in the sensitivity, review and management of TS on the part of the Unit Supervisor involved in this event. The safety significance of the event was minimal. Although the demonstration of the operability of offsite circuit power sources was not performed within the timeframe required by TS, offsite circuit power sources were operable, the Unit 1/2 EDG was operable, and no physical work was being performed in the switchyard.
2542000006 | Quad Cities 1 | 10/19/2000 | 11/20/2000 | ML00377295 | <strong>Main Steam Isolation Valve Local Leak rate Test Results in Excess of Technical Specification Limits due to Component Wear</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2000, with Unit 1 in the refueling mode, both 'D' Main Steam Line Isolation Valves (MSIV) failed the individual as-found local leak rate tests (LLRT) with results in excess of Technical Specification criteria. The failure of both 'D'MSIVs also led to the inability to quantify the minimum pathway leakage for all containment penetrations. The valves were subsequently disassembled and repaired. The root cause for each individual MSIV failure was found to be normal wear of the main stellite seat ring. In addition, the root cause for the failure of both valves during the same interval was determined to be inadequate trending. The safety significance of this event was minimal. The inboard and outboard 'D' MSIVs would have closed, although with an inadequate seal. Estimates based on observed leakage of the inboard MSIV show that the leakage would have exceeded the Technical Specification requirements for the MSIVs by an insignificant amount, and the total as-found minimum-path leakage through Primary Containment valves would have been below the Technical Specification requirements. Corrective actions to be completed include the development of comprehensive criteria for trending containment valves, and the inclusion of comprehensive trending criteria for containment valves in the site leak-rate testing program.
2542000007 | Quad Cities 1 | 12/27/2000 | 01/26/2001 | ML01032011 | <strong>Inadequate Fill and Vent Surveillance Performed on High Pressure Coolant Injection Resulting in Air in Discharge Piping</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2000, during the monthly verification of fill for the High Pressure Coolant Injection (HPCI) system, it was determined that the HPCI discharge piping was not completely filled. The discharge line was vented for an additional 5 minutes until full continuous flow was observed. As a result of the air pocket found in the discharge piping, Unit 1 HPCI was declared inoperable. On December 27, 2000, at 2014 hours Unit 1 HPCI was declared operable. It was subsequently determined that the system had been inadequately vented on November 30, 2000, following maintenance. The root cause of the event was an inadequate review of the fill and vent procedure during the revision process, resulting in an ineffective procedure. Corrective actions include revising the appropriate procedures and reviewing the event with the Operations Procedure Group. The safety significance of this event was minimal. Engineering analysis determined that the additional stresses generated by the collapsing air void created piping stresses that remained below the design allowable limits. Supporting structures were judged to be acceptable as well. The piping remained qualified for all loading conditions with no mode restrictions. Also, engineering analysis determined that the air void would not delay injection following an accident. Based on the engineering analyses, the HPCI and system would have been able to perform its safety function.
2542000008 | Quad Cities 1, Quad Cities 2 | 10/28/2000 | 11/27/2000 | ML00377367 | <strong>Secondary Containment Breach Due to Open 1" Conduit</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2000, an open line was found in the Unit I High Pressure Coolant Injection (HPCI) room with air flow into the HPCI room. This was determined to be a potential breach of secondary containment and the line was immediately capped to close the breach. After initial investigation the routing of the line could not be determined and on October 28, 2000, a breach of secondary containment was assumed to have occurred. A boroscope examination later confirmed that the conduit breached secondary containment. Because the event is believed to have occurred prior to 1993, the root cause of this event could not be determined. Throughout the time the condition is believed to have existed, secondary containment pressure tests were performed satisfactorily. Therefore, the safety significance of this event is minimal.
2542000009 | Quad Cities 1 | 11/03/2000 | 06/13/2001 | ML01187014 | <strong>Wiring Error in Average Power Range Monitor Flow Biased Neutron Flux Instrument</strong><br /><i>Abstract:&nbsp;</i>At 0214 hours on November 3, 2000, the APRM 4, 5 and 6 flow biased neutron flux high reactor trips were determined to be not operable. The "B" channel of the reactor protection system (RPS) was tripped in accordance with Technical Specifications. It was determined that two power wires to the flow biased proportional amplifier were swapped. Consequently, when the reactor mode switch was placed in RUN (Mode 1) the "B" channel APRM relays that transfer trip setpoints from the fixed high flux level for Mode 2 to the flow biased level for Mode 1 would not energize. The wiring error was subsequently corrected. The root cause of this event was personnel error, in that maintenance personnel failed to follow station procedural guidance for documenting electrical leads that are lifted or landed and for temporary labeling of those leads. The safety significance of this event was minimal. The APRMs on the "B" division would have provided an RPS trip signal at a lower (i.e., more conservative) power level than that required by Technical Specifications and design This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B),which requires reporting of any operation or condition prohibited by the plant's Technical Specifications.
2542000010 | Quad Cities 1 | 12/06/2000 | 04/29/2002 | ML02134053 | <strong>Automatic Reactor Scram from Low Reactor Vessel Level</strong><br /><i>Abstract:&nbsp;</i>At 0940 hours on December 6, 2000, with reactor power at 100%, Unit One reactor water level started to decrease and the low-level alarm was received. The operators took the Feedwater Level Control System (FWLC) out of three-element control and placed it in single-element control. They then took manual control of the 'B' Feedwater Regulating Valve (FWRV) and opened the valve, causing reactor level to increase. At about 0941 hours reactor level started to decrease rapidly and the 'A' FWRV locked up. A reactor scram signal was received at 0942 hours, with indicated reactor water level at 20 inches. All automatic actions occurred consistent with a low-level reactor scram. The root cause of this event was an age-related failure of a solder joint on the master controller for the ‘A' FWRV. Additionally, operations procedures and training did not support reducing power to mitigate or prevent the reactor scram as an immediate operator action. The safety significance of this event was minimal. Although the event resulted in a reactor trip, all safety systems responded as designed. This report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv).
2552000001 | Palisades | 01/25/2000 | 02/22/2000 | ML00368693 | <strong>Failure to Perform Technical Specification Surveillance of the Power Dependent Insertion Limit Alarm</strong><br /><i>Abstract:&nbsp;</i>Technical Specification Table 4.17.6, Item 18,requires that the Channel Functional Test for the setpoint verification on the Power Dependent Insertion Limit (PDIL) Alarm be performed every 31 days (+25%), and Technical Specification Table 3.17.6 identifies the applicable condition for the PDIL Alarm at Hot Standby and above. Collectively, Technical Specifications 3.0.4 and 4.0.4 preclude entry into an operating condition when the conditions for the Limiting Conditions for Operation, including applicable surveillance requirements, are not met and the associated action requires a shutdown. Contrary to the above, on January 25, 2000 at approximately 1211 hours, it was discovered that the required surveillance of the PDIL Alarm had not been performed within its specified interval plus allowable extension before entering Hot Standby condition. This occurrence is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. The occurrence was caused when License Amendment 85 incorporated LCO 3.0.4 into Technical Specifications. The surveillance procedure did not implement the new Technical Specification requirements and the discrepancy was not recognized. The PDIL surveillance procedure will be revised to align with the Technical Specifications.
2552000002 | Palisades | 02/28/2000 | 03/23/2000 | ML10295054 | <strong>Non-Conformance with Technical Specification Requirements for Auxiliary Feedwater Pump P-8B</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.5.1.a requires steam driven Auxiliary Feedwater Pump P-8B to be operable prior to making the reactor critical. Technical Specification 4.9a.2, requires the steam-driven pump to be started alternately from each control room switch and from the pump test-key switch in a three month period. The phrase "each control room switch" refers to the switches that operate the steam supply valves for the normal (automatically actuated) and backup (manually actuated) supplies to the P-8B turbine. The existence of this surveillance requirement, which specifically requires testing of the manual backup steam supply valve, implies that this manual backup steam supply line is a required feature to support operability of P-8B. Contrary to the above, on February 28, 2000, the reactor was made critical with the manual backup steam supply for P-8B inoperable. A Notice of Enforcement Discretion (NOED) had been granted to allow for this condition. This occurrence is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B)as a condition prohibited by Technical Specifications. A Technical Specification Amendment was requested and subsequently granted on March 14, 2000.
2552000003 | Palisades | 04/04/2000 | 05/04/2000 | ML00371467 | <strong>Inadvertent Closure of Emergency Diesel Generator 1-1 Output Breaker</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2000 at approximately 0620 hours with the plant operating at 99.9%power,an error by an auxiliary operator (AO) while attempting to rack-out the 2400 volt Emergency Diesel Generator 1-1 (EDG 1-1) output breaker 152-107,resulted in the EDG 1-1 output breaker being closed onto 2400 Volt Safeguards Bus 1-C with the EDG not in operation. The resultant voltage transient on the Safeguards Transformer and Bus 1-C led to the automatic starting of both emergency diesel generators, a manual reactor trip in accordance with operating procedures and an auxiliary feedwater actuation (AFAS). The safety significance of this event was minimal. Applicable safety systems functioned as expected, and there was no damage to plant equipment caused by this event. The automatic starting of both emergency diesel generators, the manual actuation of the reactor protection system and the auxiliary feedwater actuation are reportable to NRC in accordance with 10 CFR 50.73(a)(2)(iv)as Engineered Safety Feature (ESF) actuations.
2552000004 | Palisades | 09/05/2000 | 10/04/2000 | ML00375900 | <strong>Discovery of Inoperable Check Valve CK-ES3332 Results in Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 5, 2000, at 1820 hours, with the plant at approximately 100%power, radiography of check valve CK-ES3332 in the Train "A" common minimum flow recirculation line from High Pressure Safety Injection (HPSI) Pump P-66A and Low Pressure Safety Injection (LPSI) Pump P-67A revealed that the check valve's disc/arm assembly was detached from the hinge pin and was positioned in the bottom of the check valve body.CK-ES3332 was declared inoperable and Technical Specification 3.0.3 was entered. At 1901 hours, plant shutdown was commenced, with shutdown being completed at 2353 hours. Plant cooldown to less than 300 degrees F was completed on September 6, 2000, at 1813 hours, at which time the plant exited Technical Specification 3.0.3. The event resulted from the failure to properly assemble check valve CK-ES3332 from original plant construction.CK-ES3332 was inspected and reassembled, restoring it to its intended condition. The event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A)and (B)as both the completion of a shutdown required by Technical Specifications and as a condition prohibited by Technical Specifications. There were no failure consequences identified for the Emergency Core Cooling System as the result of this condition, and therefore, no impact on plant risk.
2552000005 | Palisades | 09/20/2000 | 10/19/2000 | ML00376237 | <strong>Failure to Perform Channel Check Surveillance on Core Exit Thermocouples</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2000 at approximately 1000 hours, the required channel check surveillance on Core Exit Thermocouples (CETs) was discovered to have lapsed during five previous shutdown periods, rendering the CETs inoperable. Upon subsequent startups, the plant failed to take appropriate action in accordance with Technical Specifications (TS) 3.17.4.6 and 3.17.4.4. The channel check surveillance requirements were inappropriately incorporated into a procedure which is not performed before entering the applicable mode. This discrepancy was not recognized during subsequent reviews until discovery in September, 2000. There were no safety consequences with this occurrence. While not performed prior to the startups, the channel check surveillance has been routinely performed on CETs during normal power operation in conformance with TS Table 4.17.4; therefore, the significance of the issue lies in TS compliance rather than safety consequences. Both the procedure which implements this surveillance, and the surveillance test scheduling database, will be revised to align with Technical Specifications. A review of selected surveillance procedures will be completed to look for other potential inconsistencies between surveillance requirements and the corresponding implementing procedure.
2602000001 | Browns Ferry 2 | 07/01/2000 | 07/28/2000 | ML01159002 | <strong>Mode Change Not Allowed by Technical Specifications SR 3.0.4 Made During Reactor Startup</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2000, during a reactor startup on Unit 2, the requirements of Technical Specifications (TS) Surveillance Requirement (SR) 3.0.4 were not fully met. Specifically, several TS instrument channel checks were not performed prior to changing from Mode 3 to Mode 2.The plant had been shutdown (in Mode 3)for approximately two days for maintenance and the subject instrument channel checks were not being performed since there was no Mode 3 applicability. Hence, the channel checks were out of their ordinary 24-hour frequency. SR 3.0.4 required the channel check SRs be performed prior to entering Mode 2. On discovery of the condition shortly after entering Mode 2, the readings were immediately obtained with no deficiencies identified. The root cause of this event was determined to be a failure to adequately implement SR 3.0.4 requirements in training and procedures. Corrective actions to prevent recurrence include revision of applicable procedures and operator training on SR 3.0.4. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(i)(B)as a condition prohibited by the plant's TS.
2602000002 | Browns Ferry 2, Browns Ferry 3 | 07/24/2000 | 08/23/2000 | ML01249023 | <strong>Failure to Meet Appendix R Criteria Resulting in a Condition Not Covered by Plant Operating Procedures</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2000, at approximately 1322 hours Central Daylight Time (CDT),TVA concluded that a condition involving noncompliance with 10 CFR Part 50 Appendix R, Criterion III.L.2.b existed for BFN Units 2 and 3. Specifically, during a postulated Appendix R event requiring Low Pressure Coolant Injection, the Safe Shutdown Instructions (SSI) require that the operator start one Residual Heat Removal (RHR) pump at time (T)=10 minutes. At T =20 minutes, the SSI require the operator open three main steam relief valves and depressurize the reactor to less than the shutoff head of the RHR pump.RHR injection would begin when reactor pressure less than the shutoff head of the RHR pump is attained, approximately 5 minutes after initiation of reactor depressurization. Pump startup at T=10 minutes and reactor depressurization delay until T=20 minutes could result in a dead-head of the RHR pump for up to 16 minutes if a spurious closure of the RHR pump minimum flow valve occurs. The root cause of this event is an inadequate GE Appendix R Analysis regarding the operation of the minimum flow valves.TVA discussed the issue in the analysis with GE and they are currently working to a resolution to the discrepancy.TVA reviewed the Appendix R Analysis provided by GE for potential similar instances of inadequate or unclear analysis. None were identified. Significant improvements have been instituted in the Engineering Design process since the 1985 time frame. These improvements effectively address the requirement to question design information provided by vendors. In order to address the power/control cables for the RHR minimum flow valves, TVA will issue an evaluation, or a design modification, as appropriate, to provide a permanent resolution to this condition. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(C),as a condition during operation that results in the nuclear power plant in a condition not covered by the plant's operating and emergency procedures.
2612000001 | Robinson 2 | 06/21/2000 | 07/21/2000 | ML00373524 | <strong>Manual Reactor Trip Due to Turbine Electro-Hydraulic Control Tubing Failure</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2000, at 0257 hours EDST, the H.B. Robinson Steam Electric Plant. Unit No.2 reactor was manually tripped from approximately 68%power. The manual reactor trip was initiated in response to leakage of main turbine system Electro-Hydraulic (EH) control system fluid. At 0210 hours an EH alarm for hi/lo-lo level occurred. Investigation of the alarm revealed an EH oil leak on non-isolable supply tubing to the hydraulic actuator for the Moisture Separator Reheater 2A Reheat Intercept Valve. Investigation of the leak revealed a circumferentially oriented crack in the EH fluid tubing. The tubing failure was caused by corrosion fatigue initiated at a defect on the outer diameter surface of the tube. The failed section of tubing was repaired. Planned corrective actions to prevent recurrence of this type of EH control system tubing failure include weather protection for selected exposed fittings, installation of flexible tubing where appropriate, and changing to a different fitting design on the 14 Main Steam and Main Turbine system valves operated by the EH system. There were no operator errors or procedural deficiencies that contributed to the event.
2632000001 | Monticello | 01/11/2000 | 02/10/2000 | ML00368437 | <strong>Containment Isolation Valve Leakage Greater than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Local leak rate testing indicated that the following limits established in the Technical Specifications for Containment Isolation Valve leakage were exceeded:1) the main steam isolation valve leakage limit, and 2) combined maximum flow path leakage rate for all containment penetrations and valves subject to Type B and C tests. The valves with excessive leakage were inspected and repaired as necessary. The redundant valves for the identified valves seated properly. Therefore, the health and safety of the public was not affected by this event.
2632000002 | Monticello | 02/03/2000 | 03/03/2000 | ML00369160 | <strong>Personal Error Results in Failure to Comply with Requirements of Section XI Operability Test For Emergency Filtration Treatment Service Water Pump</strong><br /><i>Abstract:&nbsp;</i>During the 2000 refueling outage, the circulating pump basins were drained to allow the pumps to be inspected. With the basins drained, the two basin level instruments became inoperable. These level instruments are normally used for Section XI testing of the Emergency Service Water (ESW) pumps to calculate pump differential pressure. Cooling water to the Control Room Emergency Filtration Treatment (EFT) system air conditioning condensers is supplied by 13 and 14 ESW pumps. To allow performance of an ASME Code Section XI operability test of 14 ESW pump with the circulating pump basins drained, an alternative river water level instrument channel was used. This alternative level instrumentation had been used before under similar conditions in 1996 for Section XI testing. After the test was completed, and 14 ESW pump was declared operable, it was learned that the span of the alternative level channel had been increased in 1997. The increased span no longer satisfied the Section XI requirement that full-scale range of each test instrument cannot exceed three times the reference value. Therefore the testing of 14 ESW pump did not meet Section XI requirements and the pump should not have been declared operable. During this period, movement of fuel in the reactor was initiated and the redundant 13 ESW pump was removed from service for maintenance and testing. While testing later confirmed that 14 ESW pump was operable during this period, this event represents a condition prohibited by the Monticello Technical Specifications.
2632000003 | Monticello | 02/07/2000 | 03/08/2000 | ML00369144 | <strong>Procedural Inadequacy Results in Two Automatic Closures of Recirculation Sample Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>During the 2000 refueling outage, a work order was initiated to repair a small valve, HWC-16, in a branch connection on the reactor recirculation loop "B" sampling line. The outboard containment isolation valve in the sampling line, CV-2791, was opened to drain the affected line. On 2/7/2000, Standby Liquid Control (SBLC) refueling tests were initiated while work on HWC-16 was in progress. When a SBLC pump was started in accordance with the test procedure, CV-2791 closed automatically as designed. One day later, during performance of the main steam isolation valve (MSIV) functional test, CV-2791 once again closed automatically as designed when a Group 1 containment isolation signal was generated during performance of the MSIV test. Each instance of automatic closure of CV-2791 is considered an automatic engineered safety feature actuation reportable to the NRC. Steps in both test procedures did not adequately recognize or pre-plan the automatic closure of CV-2791. Procedure enhancements will be made to the SBLC and MSIV test procedures. In addition, other procedures will be reviewed to find and correct similar deficiencies. The procedure writers guide will be revised as necessary to address this concern. Training will be provided to engineering and operations personnel to emphasize the need for self checking to detect conflicts between test procedures and work in progress.
2632000004 | Monticello | 02/21/2000 | 03/22/2000 | ML00369936 | <strong>Reanalysis of the High Energy Line Break Resulted in Potential Loss of Division I 4kV Switchgear</strong><br /><i>Abstract:&nbsp;</i>An analysis of a high energy line break (HELB) on the 911ft elevation of the Turbine Building indicated flooding of the Division I 4kV switchgear room and possible loss of the Division I 4kV switchgear. The analysis indicated that the peak flood level on the 911ft elevation of the Turbine Building Division I 4kV switchgear room would cause a loss of Division I 4kV power. With an assumed loss of offsite power, Division II Emergency Diesel Generator was considered the worst case single active failure. Therefore, this event could potentially result in loss of the station AC power from both divisions of the 4kV distribution system. Modifications were installed to prevent water from entering the Division I 4kV switchgear room.
2632000005 | Monticello | 02/23/2000 | 03/22/2000 | ML00369936 | <strong>Design Deficiency Results in Secondary Containment Leakage Pathway Which Bypasses Standby Gas Treatment System Filters</strong><br /><i>Abstract:&nbsp;</i>During the 2000 refueling outage, special tests were performed to determine the capability of the Standby Gas Treatment System (SBGT) to maintain an adequate vacuum in Secondary Containment (SCT) under various postulated conditions. During testing on 2/21/2000, the SBGT Room was found to be at a lower pressure than the Reactor Building. With the SBGT Room negative with respect to SCT, some air could be drawn into the room from SCT during a design basis loss of coolant accident (LOCA). This air would bypass the SBGT filters before being released from the plant stack. The result would be an increase in calculated LOCA radiation doses in the Control Room and offsite. Calculated doses, however, would remain a small fraction of 10 CFR 50, Appendix A, General Design Criterion 19 and 10 CFR Part 100 guidelines. It was determined that a less restrictive path for air supplied to the SBGT Room was required. A modification was completed, prior to startup from the 2000 refueling outage, to improve the air supply to the SBGT room under SCT isolation conditions which corrected this condition.
2632000006 | Monticello | 02/28/2000 | 03/29/2000 | ML00370050 | <strong>Procedural Inadequacy Results in Loss of Isolation Signal to Secondary Containment Dampers When Standby Gas Treatment System Train Control Power Deenergized</strong><br /><i>Abstract:&nbsp;</i>During the 2000 refueling outage, as a consequence of preparing electrical isolations, it was discovered that deenergizing Standby Gas Treatment System (SBGT) Train A or Train B control power also prevents the automatic closure of several Secondary Containment (SCT) isolation dampers which are closed by a single relay. In the past, SBGT control power has been deenergized for periods of up to three days for SBGT train testing or maintenance as permitted by Limiting Condition for Operation (LCO) 3.7.B.1.a. However, LCO 3.7.0.3 only allows SCT dampers to be inoperable for eight hours. Therefore deenergizing SBGT train control power for more than 8 hours represents a condition which is prohibited by the Monticello Technical Specifications. This condition was caused by procedural inadequacies which failed to recognize that removing the control power for a SBGT train can also result in the inoperability of certain SCT isolation dampers.
2632000007 | Monticello | 03/03/2000 | 04/03/2000 | ML00370183 | <strong>Procedural Adherence Error Results in Missed Periodic Fire Watch</strong><br /><i>Abstract:&nbsp;</i>Breakers for three motor operated valves (MOVs) are normally maintained open to achieve the cable separation required by 10 CFR 50, Appendix R. When pumping the Suppression Pool (Torus) to Radwaste, the breaker for the Residual Heat Removal (RHR) System to Radwaste MOV, MO-2032 is closed to facilitate the evolution. This creates the potential for draining the Torus in the event of fire induced cable damage. Hourly fire patrols with operable fire detectors, or continuous fire watches, are established as a compensatory measure while the breaker is closed. Due to a lapse of procedural adherence, the fire watch patrols were not properly maintained and completed within the required frequency. Corrective actions are to counsel personnel on expectations concerning procedural adherence and to address the underlying and contributing causes in the corrective action program.
2632000008 | Monticello | 03/03/2000 | 04/03/2000 | ML00370182 | <strong>Primary Containment Isolation of TIP Ball Valves Does Not Function Independently of Normal Controls</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2000, with the plant operating at 100% power, a design deficiency was identified in the traversing in-core probe (TIP) system. The deficiency could result in the TIP guide tube isolation ball valve failing to maintain primary containment integrity during a design basis accident. Power to the TIP ball valves has been isolated to assure the valves do not inadvertently open.
2632000009 | Monticello | 04/04/2000 | 05/03/2000 | ML00371441 | <strong>Procedural Inadequacy Results in Mismatch of Feedwater Flow Instruments and Process Computer Calibration Causing Operation Above Licensed Power</strong><br /><i>Abstract:&nbsp;</i>During normal full power operation on April 4, 2000, an Instrument and Control Technician performing a calibration of feedwater flow transmitters noted a small mismatch between the transmitter calibration values and the corresponding values generated by the plant process computer. Investigation revealed that the span of the instruments was changed on October 22, 1998, following an increase in maximum licensed thermal power. However, the process computer calibration constants for feedwater flow were not changed as required. These computer points are used in the reactor thermal power calorimetric calculations. It is estimated that this error resulted in a calculated reactor power of less than 3.7 MWt, or 0.2%, below actual power. The net effect of this error was that the reactor exceeded maximum licensed power by no more than 0.2% for a total of 316 days since the error was introduced. This event was the result of procedural inadequacies.
2632000010 | Monticello | 06/08/2000 | 07/07/2000 | ML00376241 | <strong>Technical Specification Surveillance Requirement for Containment Isolation Valves Not Performed</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2000, while operating at 100% power, it was determined that MO-2026 and MO-2027, reactor head spray outboard and inboard isolation valves, even though closed, should have been declared inoperable (i.e., it had not been demonstrated that the valves meet criteria that assure automatic closure capability). Technical Specification 4.7.D.2 requires that the position of at least one fully closed valve in each line having an inoperable automatic containment isolation valve be recorded daily. This surveillance requirement had not been met for MO-2026 and MO-2027. MO-2026 and MO-2027 were declared inoperable and were deactivated by isolating power. Daily position status logging was initiated. A Technical Specification revision will be submitted to clearly state that an automatic containment isolation valve that is deactivated in the closed position is considered operable. The corresponding specification in the Standard Specifications, NUREG-1433, will be considered in the proposed Technical Specification revision.
2632000011 | Monticello | 07/19/2000 | 08/18/2000 | ML00374748 | <strong>Service Water Radiation Monitor Alarm Setpoint Did Not Meet Technical Specification Requirements With Circulating Water Pumps Shutdown</strong><br /><i>Abstract:&nbsp;</i>During review of the Monticello Offsite Dose Calculation Manual (ODCM), it was discovered that the setpoint for the service water discharge radiation monitor was non-conservative for certain modes of plant operation. The ODCM setpoint takes credit for the 240,000 gpm of dilution flow in the discharge canal normally provided by the circulating water pumps. When these pumps are shutdown during outages, this dilution flow is no longer available. As a consequence, the service water discharge radiation monitor alarm was inoperable during these times, i.e. the setpoint was higher than allowed by Technical Specification 3.8.A.1.d. This condition was caused by an inadequate ODCM procedure for determining the service water discharge monitor alarm setpoint. No detectable release of radioactive material occurred at any time as the result of this error.
2632000012 | Monticello | 08/30/2000 | 09/29/2000 | ML00375925 | <strong>Inoperable Containment Isolation Valve Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During a planned shutdown on August 27, 2000, the inboard main steam line drain isolation valve, MO-2373, failed to indicate full open following a manual actuation of the valve from the closed to the open position. After receiving dual indication, the valve was cycled successfully in both the closed and open directions. Based on this, MO-2373 was not considered to be inoperable. A subsequent investigation of the actuator internals on August 30, 2000 revealed that the original dual position indication condition was the result of a personnel error to adequately terminate the open and close torque switch connections following a 1998 maintenance activity on the actuator. It was determined that this condition could have rendered MO-2373 incapable of performing its isolation function, and therefore MO-2373 was considered inoperable from the time of the maintenance activity in 1998. There were times during the period that MO-2373 was considered inoperable where MO-2373 and its associated redundant primary containment isolation valve, MO-2374, were both open. This represents a condition prohibited by the Monticello Technical Specifications .The redundant valve, MO-2374, was capable of performing its safety function at all times that primary containment integrity was required.
2632000013 | Monticello | 09/02/2000 | 10/13/2000 | ML00376046 | <strong>Initiation of Containment Purge Prior to Sampling and Analysis of Containment Atmosphere in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On the morning of September 2, 2000, the plant was in the process of starting up following a short maintenance outage. At 1040, believing all prerequisites had been met, the Shift Supervisor authorized containment purging with nitrogen to begin. Approximately two hours later, following a review of the prestart checklist, it was determined that a grab sample of the containment atmosphere had not been obtained and analyzed prior to containment purging as required by Technical Specification 4.8.B.6.b. At 1306 purging was stopped and the containment vent and purge valves were closed. The required containment atmosphere grab sample was obtained and analyzed at approximately 1350 and purging was resumed at 1435. Based on analysis of the containment grab sample, no significant release of radionuclides occurred as a result of the purge. The event was caused by inadequate procedures.
2632000014 | Monticello | 09/20/2000 | 10/17/2000 | ML00376237 | <strong>Missed Standby Liquid Control System (SLC) Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>During the Operations Committee review of a proposed Technical Specification change to the Standby Liquid Control System, it was recognized that the SLC surveillance test procedure did not include the steps necessary to recycle the test tank on a monthly basis as required by Surveillance Requirement 4.4.A.1. The procedure was changed to recycle the test tank monthly, and the required surveillance was subsequently performed with satisfactory results.
2632000015 | Monticello | 10/25/2000 | 11/22/2000 | ML00377197 | <strong>Relay Failure Results in Inoperable Control Room Ventilation (CRV)/Emergency Filtration (EFT) System</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2000 during a scheduled surveillance test, a control relay in the Control Room Ventilation System failed to change state in response to a valid logic signal. On October 25, 2000, the plant staff determined that the apparent cause of this failure was degradation of the vinyl plastic material used to encase the relay bearing pad. The remaining portions of the bearing pad had decomposed and mechanically prevented plunger movement. All CRVIEFT system relays were subsequently inspected. On October 25, 2000, seven additional relays were found with decomposed pad material in the relay casing. All degraded relays were Struthers -Dunn type 219BBX222NE with 120V AC coils and date code stamp 8209. The relays had been in service since 1983 except one (1990). On October 27, 2000 two additional degraded relays in the CRV/EFT system were identified by an inspection. All of the degraded relays were replaced with spare relays with silicon rubber relay bearing pads and were successfully tested. No additional Struthers-Dunn relays with debris were found in other plant systems. This event is considered to have minimal impact on the health and safety of the public.
2652000001 | Quad Cities 2, Quad Cities 1 | 01/19/2000 | 02/18/2000 | ML00368914 | <strong>Safe Shutdown Makeup Pump Injection Valve Inoperable due to Failure to Use Vendor Manual for Correct Staking of Yoke Bushing</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2000, the Safe Shutdown Makeup Pump (SSMP) Unit 2 injection valve was determined to be inoperable due to the failure of the yoke bushing to remain staked to the yoke. The operator was removed from the valve, the bushing was returned flush to the yoke and staked and the operator was re-installed. A motor operated valve diagnostic test was performed on the valve for post maintenance testing and the SSMP system was declared operable. This failure was determined to be the result of inadequate staking of the bushing in August, 1993, due to failure to utilize vendor documentation. This event was not safety significant .The SSMP system is a backup to the Reactor Core Isolation Cooling system, which was operable and available throughout this event. Also, the complete failure of the valve to operate occurred only after the system was removed from service for maintenance. The only other two valves of this design in the plant have been visually examined and are operable. The yoke bushing staking will be inspected and repaired as necessary.
2652000002 | Quad Cities 2 | 01/28/2000 | 02/23/2000 | ML00368975 | <strong>Emergency Diesel Generator Inoperable due to Inadvertent Movement of Ventilation Fan Power Select Switch</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2000, at approximately 0015 hours, Unit 2 was in Mode 5 with Core Alterations in progress, when the Unit 2 Emergency Diesel Generator (EDG) ventilation fan power supply selector switch was determined to be in the alternate feed position. The power supply was immediately changed to normal feed at 0030 hours. The switch was apparently moved out of the normal position by either Security guards sitting in the room or contractor personnel who were using the room as a place to change clothes. The cause of this event was inadequate communication of the expectation for workers to stay out of areas unless assigned duties placed them there. Immediate corrective actions were to place the switch in the correct position and to communicate the expectation to the affected work groups that access to plant areas is only on an as-needed basis. Long term corrective actions include providing training on the expectations for accessing plant areas and providing additional postings for equipment being relied upon for maintaining shutdown safety or meeting Technical Specification (TS) requirements during outages .Station procedures direct that the EDG be declared inoperable when the vent fan power select switch is in the alternate feed position .Because Core Alterations were in progress and the Unit 1/2 EDG was inoperable to Unit Two due to planned maintenance, the Technical Specifications were not met. With the vent fan power select switch in the alternate position, the power for the vent fan would be supplied by a Unit 1 safety bus. The Unit 1 EDG was operable throughout the time frame that the switch could have been mispositioned. Therefore, the safety significance of this event was minimal.
2652000003 | Quad Cities 2 | 02/01/2000 | 11/27/2001 | ML02017032 | <strong>Movement of Fuel With Fewer Intermediate Range Neutron Monitors Operable than Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Between February 1, 2000, and February 5, 2000, the Unit 2 Reactor Protection System (RPS) Trip System B had only two operable Intermediate Range Neutron Monitoring (IRM) channels. Technical Specification 3.1.A-1 requires a minimum of three operable IRM channels for each RPS Trip System when in Refueling. This event was caused by inadequate communication between the Instrument Maintenance Department and the Operating Shift concerning the status of IRM 17 and by inadequate work instructions. Upon discovery, the IRM was declared inoperable and Technical Specification 3.1.A, Action 1, was entered. A Channel B 1/2 Scram was inserted to meet Technical Specification requirements. The safety significance of this event was minimal. All required Source Range Monitors (SRMs) were operable, all control rods were fully inserted in the core, and the rod motion control switch was out of service in the control room. Also, there were sufficient IRMs operable on each RPS channel to provide an RPS trip if required. Personnel were counseled and training was held concerning this event. Also, procedures have been enhanced to change the method for taking the IRMs out of service and the model work request has been revised to provide guidance concerning communications.
2652000004 | Quad Cities 2 | 02/09/2000 | 03/08/2000 | ML00369212 | <strong>Engineered Safety Feature Actuation During Instrument Backfilling Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>At 0421 hours on February 9, 2000, with Unit 2 in a shutdown condition, Unit 2 received the following Engineered Safety Feature (ESF) actuation signals: Reactor Protection System (RPS) scram, Group 2 isolation and Group 3 isolation. This included isolation of the Residual Heat Removal (RHR) Shutdown Cooling system which was in operation. The ESF actuation was invalid and occurred while backfilling the Unit 2 reactor instrumentation sensing lines. All safety systems responded as designed. The root cause of the ESF actuation was determined to be inadequate procedural guidance. The procedure for backfilling reactor instrumentation sensing lines will be revised to ensure common instrumentation is isolated when backfilling individual instrument sensing lines. The safety significance of this event was minimal. At the time of the event, Unit 2 was shutdown with all control rods fully inserted. RHR Shutdown Cooling was restored within 15 minutes of the event at 0432 hours. The associated increase in reactor coolant temperature was minimal-approximately 5 degrees Fahrenheit. For these reasons, there was no adverse impact on the health and safety of the public, including control room and site personnel.
2652000005 | Quad Cities 2 | 02/11/2000 | 09/18/2000 | ML00375453 | <strong>High Pressure Coolant Injection Inoperability During Low Pressure Testing Due to Incomplete Maintenance Activities and Inadequate Venting</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2000, at 0258 hours, Unit 2 was in the Startup mode with reactor pressure between 150 and 180 psig, when the High Pressure Coolant Injection (HPCI) pump failed to start during startup surveillance testing. The surveillance was terminated, the system was restored to standby lineup, and reactor pressure was reduced below 150 psig to place the reactor in a condition where HPCI was not required to be operable. It was determined that work performed on HPCI during the refueling outage was not complete and the work package had been closed out in error. The work was subsequently completed and the startup was recommenced. In addition, when the HPCI discharge piping was vented in preparation for re-testing of HPCI, air in the discharge piping exceeded procedural acceptance criteria. This indicated that a satisfactory vent had not been obtained on the discharge piping prior to the first test. The piping was subsequently filled and vented, reactor pressure was increased to between 150 and 180 psig, and HPCI was successfully tested. The root cause of the failure to complete the maintenance was inadequate training concerning procedural requirements for work completion. The root cause of the failure to obtain a satisfactory vent of the discharge line prior to the first HPCI test was an inadequate venting procedure that did not require venting for a sufficient amount of time. The safety significance of this event was minimal. The reactor pressure was less than 180 psig, and the automatic depressurization system and all low-pressure emergency core cooling systems were operable.
2652000006 | Quad Cities 2 | 05/05/2000 | 09/13/2000 | ML00375372 | <strong>Primary Coolant Isolation and Reactor Trip due to Adjustment of Incorrect Main Steam Line High Flow Switch During Calibration</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2000, at 0940 hours, a Group I Primary Coolant isolation and a reactor trip were received on Unit 2 during calibration of Main Steam Line High Flow switches. The individual performing the calibration adjusted a switch other than the one that was isolated and prepared for calibration. The root causes of this event were inadequate individual performance on the part of the Instrument Maintenance Technician in the field, failure to adequately enforce management expectations concerning established human performance initiatives, insufficient barriers considering the risk associated with testing Group I isolation instruments, and a lack of oversight and communication. Additionally, previous corrective actions were inadequate. The safety significance of this event was minimal. No mitigating equipment was degraded, and all Emergency Core Cooling Systems were operable throughout the event Several immediate corrective actions were taken commensurate with the seriousness of the event. Corrective actions that remain to be taken include divisionalization of Instrument Maintenance (IM) procedures with the potential to cause a unit trip or derating.
2652000007 | Quad Cities 2 | 05/22/2000 | 06/20/2000 | ML00377367 | <strong>Reactor Scram and Reactor Water Cleanup System Isolation While Returning Turbine Control Valve to Service</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2000, at 2159 hours, the Unit 2 reactor scrammed on a high flux signal during a return to service for an electro-hydraulic control (EHC) solenoid replacement on a turbine control valve (CV). The high flux was due to an unanticipated response of the CVs, most likely from air entrapped in the EHC system. The root cause of this event was inadequate risk assessment. Corrective actions include improving the risk assessment process to ensure .available options are explored and independently reviewed, and strengthening the questioning attitude at the station. On May 22, 2000, at 2229 hours, a reactor water cleanup system isolation occurred on low reactor water level (RWL). The actuation occurred when operators delayed the start of a reactor feed pump while awaiting an in-plant check. The root cause of the isolation was inadequate decision-making regarding restart of components. Corrective actions to prevent recurrence include updated dynamic simulator training focusing on RWL control. The safety significance of these events was minimal. The only mitigating equipment that was not fully operable was the "D" residual heat removal service water pump. The unit was shut down using normal operating equipment. Although feedwater flow was not fully restored prior to receiving the low level isolation, the restoration was in progress and the low level signal was cleared within three minutes.
2652000008 | Quad Cities 2, Quad Cities 1 | 07/18/2000 | 11/02/2000 | ML00376881 | <strong>Reactor Trip due to a Main Generator Differential Relay Operation</strong><br /><i>Abstract:&nbsp;</i>At 0548 hours on July 18, 2000, Unit 2 automatically scrammed from full load due to a C-phase generator differential relay operation. The Unit 2 trip was concurrent with an insulator fault on the C-phase of a 345kV line. Equipment on Unit 2 responded to the scram as expected to shut the unit down. Approximately ten seconds after the Unit 2 scram an attempted automatic reclosure of a 345kV breaker in the switchyard caused a 345kV differential relay to operate. The result of this was a loss of power to the Reserve Auxiliary Transformer (RAT), which provides normal offsite power to one division of Unit 1. The loads normally supplied by the RAT automatically transferred to the Unit Auxiliary Transformer (UAT), which normally provides power from the Unit 1 generator to one division of Unit 1. Unit 1 continued to operate for about ten hours with power supplied to both Unit 1 divisions by the UAT, after which the RAT was reenergized and the loads transferred back. The root causes of this event included current transformer mismatch, an inappropriate breaker reclose scheme, and inadequate consideration of CT mismatch during implementation of distribution yard design changes. The safety significance of this event was minimal. On Unit 2, all control rods inserted, and reactor water level and pressure were controlled using the normal coolant supply and heat removal systems. On Unit 1, the UAT supplied power during the event, with offsite power available from the Unit 2 RAT, as designed.
2662000001 | Point Beach 1 | 01/21/2000 | 03/22/2000 | ML00370042 | <strong>Manual Reactor Trip Due to Decreasing Circulating Water System Fore Bay Level</strong><br /><i>Abstract:&nbsp;</i>Unit 1 reactor and turbine were manually tripped from approximately 41% reactor power, at 0239 on January 21, 2000, in accordance with AOP-13A, "Circulating Water System Malfunction" upon the circulating water system pump bay water level having decrease d to -11 feet from reference. A rapid load reduction had been initiated in accordance with AOP-17A at 0210 with the pump bay level at -10.5 feet. Circulating water intake crib ice blockage was the cause for the level decrease. With three minor equipment performance exceptions, all equipment operated per design during and following the trip. Initial NRC event notifications were made in accordance with 10 CFR 50.72(b)(1) for a TS required shutdown. A subsequent notification was made for 10 CF R 50.72(b)(2)(ii) for the manual reactor protection system actuation. After inspections to verify structural integrity of the circulating water intake structure and testing to assure operability of the system with two circulating pump operation, Unit 1 was restarted on January 22, 2000, and returned to full power operations at 1930 on January 24, 2000.
2662000002 | Point Beach 1, Point Beach 2 | 02/10/2000 | 03/11/2000 | ML00369426 | <strong>Technical Specification Surveillance Requirement to Verify ECCS Valve Position Not Fully Implemented</strong><br /><i>Abstract:&nbsp;</i>During a system walk down and inspection at the Point Beach Nuclear Plant (PBNP), four valves were identified (two in each unit) that were not being periodically verified to be in the correct (shut) position as required by Technical Specification (TS) surveillance TS 15.4.5.II.B.2, "Emergency Core Cooling System and Containment Cooling System Tests." The valves were immediately checked and verified to be in their proper shut position. The valves were subsequently red locked in the shut position. Valves which are locked, sealed or otherwise secured in position are not required to be checked every 31 days. The safety impact of this missed surveillance was negligible. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(i).
2662000003 | Point Beach 1, Point Beach 2 | 02/16/2000 | 03/16/2000 | ML00369604 | <strong>Inadequate Control of Cable Spreading Room High Energy Line Break Barrier</strong><br /><i>Abstract:&nbsp;</i>This event identified inadequate controls on a temporary use penetration through the wall of the cable spreading room (CSR) at the Point Beach Nuclear Plant (PBNP) which could have, in the event of a worst case high energy line break (HELB) in the PBNP turbine hall, resulted in the potential for exceeding the design basis temperature limitations for equipment located in the CSR. PBNP procedure NP 8.4.16, "PBNP High Energy Line Break Barriers," has been changed to incorporate more positive administrative and compensatory controls on barrier penetrations susceptible to HELB conditions. Due to the relatively short duration of the degraded condition of this penetration and the low probability of the initiating event, the safety significance of this condition was minimal. A root cause evaluation and an assessment of the plant for extent of this condition will be completed.
2662000004 | Point Beach 1, Point Beach 2 | 02/17/2000 | 03/20/2000 | ML00369618 | <strong>Potential Loss of Process Monitoring Instrumentation Due to a Fire in Containment</strong><br /><i>Abstract:&nbsp;</i>While conducting an evaluation of separation of cables inside containment for an ongoing Appendix R Rebaselining project, the licensee identified a potential fire location which could result in the failure to meet regulatory requirements. Title 10 CFR 50 Appendix R, Section III.G.2, specifically addresses containment equipment and requires that redundant equipment be maintained free of fire damage to support safe shutdown of the plant. This includes process monitoring instrumentation to maintain positive control of the cool down process with at least one steam generator Level Transmitter and one Temperature Element, each from the same reactor coolant system (RCS) loop, available. The fire location identified would leave one Level Transmitter and one Temperature element available, but, on opposite RCS Loops from each other. This condition does not meet the regulatory requirements and placed the plant outside the design basis for Appendix R. Plant modifications are planned to correct this condition. As a result of administrative controls which limit combustible materials in containment and alternate means to obtain cool down process information, the safety significance of this event is negligible.
2662000005 | Point Beach 1, Point Beach 2 | 03/09/2000 | 04/07/2000 | ML00370354 | <strong>Termination Criteria for Containment Spray in Emergency Operating Procedure Non-Conservative with Safety Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>While reviewing the design basis document for the Safety Injection and Containment Spray System a PBNP engineer questioned whether the early containment spray termination criteria identified in Emergency Operating Procedure (EOP) 1.3 was consistent with the duration of spray assumptions in the FSAR safety analyses (Section 14.3.5). Subsequent evaluation of this concern determined that there was a reasonable possibility that the reduction of spray duration due to the early spray termination criteria could prevent the fulfillment of a safety function necessary to control the release of radioactive material or mitigate the consequences of an accident. This concern was considered to be a procedural inadequacy. Mitigating circumstances were identified which would result in a reduction of potential radiological releases following a postulated design basis accident. However, given the assumptions required by the safety analysis for spray duration, this event was determined to be a reportable under 10 CFR 50.73 (a)(2)(vi). The EOP was promptly changed on March 8, 2000, to remove the early spray termination criteria. The cause of this event was an inadequate 10 CFR 50.59 evaluation of the procedure change.
2662000006 | Point Beach 1, Point Beach 2 | 05/24/2000 | 10/09/2000 | ML00376027 | <strong>Inadequate Procedural Guidance to Restore Equipment Necessary to Maintain Hot Safe Shutdown as Required by Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>While completing a re-verification and re-validation of the Fire Protection Evaluation Report fire scenarios, the licensee's Appendix R Rebaselining Project Team determined that the procedural guidance for restoration of cooling to the Primary Auxiliary Building battery and inverter rooms to ensure adequate cooling of the D-109 battery charger may have been less than adequate to ensure maintenance of temperatures for hot shutdown equipment. The Appendix R design basis does not allow for repairs of hot shutdown equipment needed to achieve or maintain hot safe shutdown; therefore, the plant was declared to be in a condition outside the Appendix R design basis. Procedure revisions have been made to establish timely cooling to the battery and inverter rooms to ensure operability of the inverter and preclude the need to repair the inverter. Testing and analyses completed subsequent to the original LER have demonstrated that there is adequate time to restore room ventilation during this Appendix R scenario and that an alternate source of power was available to the vital instrument bus inverters. Therefore this event had no safety significance.
2662000007 | Point Beach 1 | 07/07/2000 | 08/03/2000 | ML00373892 | <strong>Containment Upper Hatch Inner Door Vent Valve Found Unlocked</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2000, while entering the Point Beach Nuclear Plant (PBNP) Unit 1 upper containment air lock to conduct post maintenance testing of the outer door interlock mechanism, the plant staff discovered that the inner door vent mechanism had not been locked following an air lock entry earlier that day to perform maintenance on the interlock mechanism. Although not locked, the inner door vent valve was shut an d containment integrity had been satisfied at all times. However, in accordance with the PBNP Technical Specifications and plant procedures, the vent valve mechanism is require d to be locked, and by intent of the specification, to remain locked except when necessary for completion of maintenance activities, within 24 hours of the initial identification o f the inoperable interlock condition. The interlock mechanism was originally declared inoperable on June 30, 2000. This event is reportable as a condition prohibited by TS. There was no safety significance to this condition since containment integrity was maintained in accordance with the Technical Specification requirements throughout the event.
2662000008 | Point Beach 1, Point Beach 2 | 09/20/2000 | 10/19/2000 | ML00376414 | <strong>Inadequate Procedural Guidance for Spurious Opening of SI-851A/B Valves During Appendix R Alternate Shutdown</strong><br /><i>Abstract:&nbsp;</i>While completing a re-verification and re-validation of the Fire Protection Evaluation Report fire scenarios, the licensee's Appendix R Rebaselining Project Team determined that the procedural guidance in Appendix R alternate shutdown procedures, AOP-10A, "Safe Shutdown -Local Control," and AOP-10B, "Safe to Cold Shutdown in Local Control," did not adequately consider spurious operation of the SI-851A/B, "RHR to Containment Sump," isolation valves .Spurious operation of these valve during an Appendix R fire event could lead to diversion of RWST or RCS coolant volume to the containment sump. This would be contrary to an Appendix R performance goal to maintain pressurizer level and was determined to be a condition outside the design basis of the plant. The potential for this condition has been eliminated by changes to the identified procedures. Due to the availability of alternative water sources, the training provided to the operating staff to recognize and respond to this event, and the defense in depth to minimize the potential for the initiating fire event, this event was determined to have a low safety significant.
2662000009 | Point Beach 1, Point Beach 2 | 10/02/2000 | 11/01/2000 | ML00376720 | <strong>Initial Conditions Assumed for Control Room Habitability Dose Calculation Do Not Match Shielding Configuration</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2000, the licensee observed that the post accident control room dos e calculation assumed that shielding for the control room observation window and south doo r is in place at the beginning of the accident to limit the whole body dose to the control room personnel to less than 5 rem during the first 30 days after the accident. The shielding for these locations, although portable, is not installed by procedure until sometime after the initiation of the accident. The dose rate calculations and assumptions have been evaluated against the actual time to reach the procedural step that directs the installation and the actual time it took to put the shielding in place. Based on those determinations, in the event of a design basis accident, it is possible that the 5 re m dose rate could have been exceeded due to increased radiation streaming through the unshielded control room window prior to getting the shielding in place. A one hour NRC notification pursuant to 10 CFR 50.72 for a condition potentially outside the design basis for the plant was made on October 2, 2000. Since February 1999, we have committed to the NRC to maintain an administrative leak rate limit for the containment of one half the Technical Specification limit. Based on that lower permissible leak rate, adequate time exists to install the portable shielding and the 5 rem limit would not be exceeded.
2662000010 | Point Beach 1, Point Beach 2 | 10/27/2000 | 11/22/2000 | ML00377390 | <strong>Manual Reactor Trip Due to Concerns for Diver Safety</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2000, the Point Beach Nuclear Plant Unit 1 reactor was manually tripped, while operating at full power, due to concerns for the safety and welfare of contract divers who were conducting underwater inspections of the common circulating water pump house. Unit 2 was shut down and defueled at the time. The divers were inspecting the Unit 2 piping from the condensers to the outlet seal well when communications with one of the two underwater divers was lost. When the second diver was initially unsuccessful in pulling the first diver from the pipe using his safety tether, the decision was made to manually trip the operating unit and secure the Unit 1 circulating water pumps. The divers were subsequently removed from the water, examined by medical personnel and determined to be unharmed. Following the unit trip, systems and equipment operated as expected. An incident investigation and post trip review was completed in accordance with procedures and the unit was returned to full power operation on October 30, 2000. A root cause evaluation of the event is underway.
2662000011 | Point Beach 1 | 12/02/2000 | 01/02/2001 | ML01009039 | <strong>Loss of 120 VAC Vital Instrument Bus During Inverter Maintenance</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2000, the "white" channel 120 VAC vital instrumentation buses, 1Y-03 and 1Y-103, for the Point Beach Nuclear Plant (PBNP) Unit 1, were deenergized for approximately 30 seconds. This event occurred while an auxiliary operator (AO) was removing the DY-OC inverter from service to replace the input fuses. The AO was isolating the inverter using the instructions posted on the inverter which included a step to open the breaker for the backup power supply. This step was inappropriate for the conditions present at that time .Upon hearing the announcement regarding the loss of the white instrument buses, he immediately re-closed the backup supply breaker. This event caused PBNP Unit 1 to enter TS-15 .3 .0 .B for approximately one minute because of conditions or limitations beyond those specified in the permissible conditions of the Limiting Conditions for Operation (LCO). This event is reportable as "any operation or condition prohibited by the plant's Technical Specifications." PBNP Unit 1 was operating at full power prior to this event. Power was manually reduced to 95% and control rods switched to manual control after the rods stepped in during the event .A team root cause evaluation has been initiated. This event had no impact on the health and safety of the public or the plant staff.
2692000001 | Oconee 1 | 02/16/2000 | 03/17/2000 | ML00369435 | <strong>Shutdown for Unisolable RCS Leak due to Thermal Cycling In Drain Line</strong><br /><i>Abstract:&nbsp;</i>On 2/16/2000, during a Reactor Building entry with Unit 1 at 100% in Mode 1, a System Engineer observed an unisolable vapor leak at the 1B2 cold leg loop drain line on a low point of the Reactor Coolant System (RCS). The leak rate was determined to be approximately 0.04 gpm. In response, Operations shutdown the unit in accordance with Technical Specification 3.4.13, Condition B. The leak was in the base metal of the outer radius of a 1-1/2 inch 90 degree piping elbow. The root cause of this event is thermal fatigue in the drain pipe. Completed actions included replacement of the elbow and inspection of equivalent drains on the three other RCS loops. No other indications were identified. Planned actions during the next appropriate outages are to inspect equivalent drains on Units 2 and 3, and to insulate portions of these lines on all units t o limit future thermal cycling. This event is considered to have no significance with respect to the health and safety of the public.
2692000002 | Oconee 1, Oconee 2, Oconee 3 | 03/09/2000 | 04/06/2000 | ML01023011 | <strong>TS 3.0.3 Entry Due to Control Room Cooling Chiller Refrigerant Leaks</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2000, all three Oconee Units were operating at 100%power. At 0935 Operations swapped from the "B" Control Room Air Conditioning Chiller to the "A" Chiller for routine monitoring of "A" Chiller. At 1000, the "A" Control Room Air Conditioning Chiller tripped. The "A" Chiller was restarted but tripped again. At 1027 the "B" chiller was restarted, but it tripped at 1035. Operations declared entry into Technical Specification 3.0.3 for all three units. At 1116 the NRC was notified per 10 CFR 50.72. At 1130 Operations began to decrease power. Refrigerant leaks were found at tubing fittings on both chillers. Refrigerant was added to both chillers. The "B" and "A" Chillers were declared operable at 1246 and 1536, respectively. Degraded copper tubing flares at filter/dryer connections on the chillers caused refrigerant leaks. The root cause was insufficient detail in the maintenance procedures to evaluate the flares. A lack of effective monitoring for refrigerant loss contributed to the event. The tubing has been replaced and enhancements are planned for leakage monitoring. This event is considered to have no significance with respect to the health and safety of the public.
2692000003 | Oconee 1, Oconee 2, Oconee 3 | 06/06/2000 | 07/06/2000 | ML00373215 | <strong>TS 3.0.3 Entry Due to Control Room Cooling Chillers</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2000, while Oconee Units 1, 2, and 3 were operating at 100% power, Control Room Zone (CRZ) HVAC Chiller "B" tripped at 14:13 while Chiller "A" was removed from service for maintenance. Technical Specification (TS) 3.0.3 was entered for all three units due to a loss of required chilled water per TS 3.16.7, Condition E. Chiller "A" was restored to operation per the maintenance contingency plan at 14:33. TS 3.0.3 was exited before the shutdown power reduction was initiated. Chiller "B" tripped due to a failure of one of two solenoids that control chiller load. The apparent cause of the solenoid failure was the failure of a time delay relay installed in Chiller "B" in 1995. The failed time delay relay was removed, the failed solenoid replaced, and other potentially damaged circuit components replaced. Chiller "B" was tested and determined operable at 13:45 on June 9, 2000. During the 20-minute period both chillers were out of service, CRZ temperatures increased slightly, but remained well within TS 3.6.17 limits. This event is considered of no significance with respect to the health and safety of the public.
2692000005 | Oconee 1, Oconee 3 | 10/11/2000 | 11/09/2000 | ML00376931 | <strong>Reactor Protective System setpoints calibrated outside Technical Specification limits</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2000, at 1300 hours, while performing the Reactor Protective System (RPS) Channel 1C Main Feedwater Pump (MFDWP) and Main Turbine (MT) hydraulic oil/fluid pressure trip calibration procedure, a concern was raised by an NRC inspector who noted that the allowed calibration setpoint tolerances for the specified setpoint given in the procedure did not agree with Technical Specification (TS) Table 3.3.1-1 allowable values. Subsequent investigation confirmed that several of Units 1 and 3 "as-left" MFDWP and MT trip setpoint values had been calibrated slightly outside of TS Table 3.3.1-1 allowable values. Trip setpoint values were chosen when the Anticipatory Reactor Trip System was originally installed in the early 1980s and later carried on into Improved TS (ITS) during conversion. The deviations involved were very minor and it was concluded that this condition would not have adversely affected the ability of the RPS to perform its safety-related functions. The cause of this condition was a defective procedure resulting from an ineffective review of the procedure during the ITS implementation process. As corrective actions, the applicable setpoint calibration procedures were revised and the out-of-tolerance setpoints recalibrated in compliance with the TS Table 3.3.1-1 allowed values.
2692000006 | Oconee 1 | 12/04/2000 | 03/01/2001 | ML01071001 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Cracks Found in Several Small Bore Reactor Vessel Head Penetrations</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2000, at 0300 hours, with Oconee Unit 1 in Mode 5 and preparing to enter refueling outage 19, a periodic visual inspection of the top surface of the Reactor Pressure Vessel (RPV) head revealed small amounts of boric acid deposited on the vessel head surface. These deposits appeared to be located at the base of 5 (of the 8) unused thermocouple (T/C) and the #21 Control Rod Drive Mechanism (CRDM)nozzles at points where they penetrate the RPV head surface. A more detailed video inspection, performed on December 1, 2000, confirmed the presence of the boric acid around the suspect nozzles. On December 4, 2000, an eddy current test was performed on the inside surface of the 8 T/C nozzles and revealed axial crack-like indications on the ID of the nozzles in the vicinity of the partial penetration weld (on the underside of the RPV head).On December 9, 2000, dye penetrant (PT) testing on CRDM #21 identified two very small pin hole indications. After lightly grinding and performing another PT, a 0.75-inch radial indication running at a slightly skewed angle across the fillet weld was identified. Following completion of the root cause analyses, Primary Water Stress Corrosion Cracking was determined to be the primary failure mechanism of both the T/C nozzles and CRDM weld cracks. Prior to unit restart, the #21 CRDM weld was repaired and the 8 T/C nozzles removed and their resultant head penetrations permanently plugged. These actions were completed. This event is considered to have no significance with respect to the health and safety of the public.
2692000007 | Oconee 1, Oconee 2, Oconee 3 | 11/09/2000 | 01/04/2001 | ML01009030 | <strong>Source Lost - Not Secured During Unexpected Work Interruption</strong><br /><i>Abstract:&nbsp;</i>(Limit to 1400 spaces, i.e., approximately 15 single-spaced typewritten lines) (16) On October 30, 2000, Oconee lost positive control of a radioactive calibration source containing 0.022 microcurie of Am-241 when the user experienced an unrelated medical emergency and was sent to a doctor. Upon return to work on November 7, 2000, the user identified that the source was missing. Following an unsuccessful search, the missing source was classified as lost on November 9, 2000. During this time, all three Oconee Units were operating in Mode 1 at 100 5i power. An investigation concluded that the source was probably mistaken for a radiological sample and disposed of as dry active waste. In accordance with 10CFR 20.2201(a) a telephone report was made to the NRC Operations Center on December 7, 2000 (Event Number 37575). Planned corrective actions are to a) identify an appropriate method to better mark these sources to minimize the possibility of a source being mistaken for a sample, and b) communicate management expectations for supervisor action for events affecting the ability of an individual to complete work in progress. This event is considered to have no significance with respect to the health and safety of the public.
2692000008 | Oconee 1 | 12/14/2000 | 01/11/2001 | ML01022035 | <strong>Pressurizer Relief Valve Setpoint Found Out-of-Tolerance</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2000,with Oconee Unit 1 in refueling (mode 6), notification was received from an off-site testing facility that the as-found lift pressure (2602 psig) of one Reactor Coolant System (RCS) pressurizer relief valve, during testing, was greater than Technical Specification limits of 2500 psig +/-75 psi. This pressurizer relief valve was tested as required by Technical Specification surveillance. The cause is believed to be set point drift. This valve was replaced with a certified spare. Corrective action taken for the pressurizer relief valve included disassembly, inspection, and refurbishment. This event is considered to have no significance with respect to the health and safety of the public.
2702000001 | Oconee 2 | 01/06/2000 | 02/02/2000 | ML00368156 | <strong>Pressurizer Relief Valve Setpoint Found Out-of-Tolerance</strong><br /><i>Abstract:&nbsp;</i>On January 6,2000, with Oconee Unit 2 at 100 percent full power (mode 1), notification was received from an off-site testing facility that the initial as-found lift pressure (2547 psig) of one Reactor Coolant System (RCS) pressurizer Safety Valve, during testing, was greater than the Technical Specification limits of 2500 psig including tolerance of +/-25 psi. The cause is believed to be set point drift. This valve was replaced with a certified spare and is now at the off-site testing facility. Corrective action to be taken includes disassembly, inspection, and refurbishment. This valve will be tested as part of routine certification testing for pressurizer safety relief valves prior to being reinstalled. The condition posed no threat to public health and safety.
2702000002 | Oconee 2, Oconee 3 | 12/19/2000 | 07/12/2001 | ML01198034 | <strong>TS 3.0.3 Shutdown Initiated Due to Control Room Cooling Chillers</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2000, Oconee Units 2, and 3 were operating in Mode 1 at 100% power, and unit 1 was in Mode 6. During a Low Pressure Service Water System Flow Test, Control Room Zone (CRZ) HVAC Chiller "A" tripped at 1305 hours. Chiller "B" subsequently tripped at 1352 hours. Units 2 and 3 entered Technical Specification (TS) 3.0.3 due to a loss of two Chilled Water trains per TS 3.7.16. The flow test was aborted and air was vented from chiller service water (CSW) piping. Chiller "B" was started at 1426 but was not immediately declared operable. Units 2 and 3 initiated power reduction at 1452.At 1521, Chiller "B" was declared operable and both Units 2 and 3 exited TS 3.0.3 at 99.5% power. A root cause investigation found that the discharge piping configuration and flow test conditions allowed air that accumulated at the CSW discharge piping to go through a recirculation valve to the idle "B" CSW recirculation loop and then into the "A" CSW suction. Air binding of the CSW pumps caused the Chillers to trip. Corrective actions include procedural guidance for venting and planned piping changes to preclude air accumulation. During the event, CRZ temperatures remained well within TS 3.7.16 limits. This event is considered of no significance with respect to the health and safety of the public.
2712000001 | Vermont Yankee | 02/11/2000 | 03/09/2000 | ML00369158 | <strong>Apparent Degradation of Main Steam Isolation Valve Solenoid Operated Test Valve Leads to a Request for Enforcement Discretion and a Subsequent Violation of Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 02/11/00, Vermont Yankee (VY) exceeded the Technical Specification (TS) surveillance interval allowed for partial closure testing of a single inboard Main Steam Isolation Valve (MSIV). Additionally VY did not perform TS actions for an inoperable MSIV. Recent data from the twice-weekly test on one of the MSIV's had indicated that a related test solenoid valve Is degraded. Industry experience shows that such test valve degradation has resulted in undesirable plant transients at other facilities. Such transients include an inadvertent full closure of the MSIV during the "partial" closure test. A review of the balance of TS MSIV testing requirements, unaffected by the test solenoid valve, shows that the safety function is adequately tested, absent the partial closure test. Additionally, it was recognized that plants of similar design had previously recognize d that the test was no longer necessary to adequately demonstrate MSIV functionality and had obtained TS amendment s removing it from their TS. Exceeding the prescribed testing interval for the single MSIV was volitional, and followed discussion s with the USNRC consistent with the Notice Of Enforcement Discretion (NOED) process. VY obtained Enforcement Discretion prior to exceeding the surveillance interval time limit of TS. The test valve, along with the related MSIV, is within the primary containment making it impracticable to confirm the cause determination, until plant shutdown. Because the related MSIV safety function is being consistently and satisfactorily tested, and the MSIV remains fully functional, this event has no effect upon public health and safety.
2712000002 | Vermont Yankee | 05/09/2000 | 06/08/2000 | ML00372294 | <strong>Valve Repair/Replacement Activities were not Performed in accordance with ASME Section XI Requirements</strong><br /><i>Abstract:&nbsp;</i>On 5/09/00, with the reactor at 100% power, research was being done to determine the correct weld repair procedures to repair a leaking valve bonnet, leakoff line seal weld on a Reactor Core Isolation Cooling (RCIC) steam supply isolation valve. During this research, it was discovered that, contrary to plant-approved welding procedures, no determination had been made regarding the requirements for post-weld heat treatment of the seal weld. It was subsequently determined that a pinhole leak existed in the valve bonnet one-quarter inch leakoff line plug seal weld. Further investigation revealed that the same seal weld problem existed for two other RCIC isolation valves and a Main Steam Drain isolation valve. The post-weld heat treatment determination is a plant procedure requirement which in turn is a requirement of ASME Section XI Code .Adherence to ASME Section XI is a requirement of Vermont Yankee's Technical Specifications 4.6.E. Contrary to this, the requirements were not met following the seal welding of these leakoff plugs. This event is therefore reportable under 10.CFR50.73 (a)(2)(i) as a condition prohibited by Technical Specifications. The root cause of this event is attributed to inadequate administrative controls of the welding process. Immediate corrective action included an operability assessment which determined that continued operation was acceptable. Had the entire seal weld failed, any leak would have been limited by the small line size and threaded plug installed in the line, to within the bounds of any analyzed accident. Therefore this event posed no significant increased risk to the health and safety of the public.
2712000003 | Vermont Yankee | 06/08/2000 | 07/06/2000 | ML00373128 | <strong>Inadequate Change Management Results in the Failure to Test Primary Containment Vacuum Breakers at the Required Frequency</strong><br /><i>Abstract:&nbsp;</i>On 06/08/00, while reviewing a surveillance procedure, the VY IST Coordinator determined that the approach used to test torus-to-drywell vacuum breakers did not fully meet code requirements. Specifically, the force required to unseat the check valves that perform this function in the VY containment system had not been measured on a quarterly basis. Rather, the required measurement had been taken every six months. The unseating force had been measured within 3 months of the time of discovery. Therefore, the operability of the vacuum breakers was not in question .The code testing requirements for vacuum relief devices (per OM-1) have consistently been met for the subject vacuum breakers. However, the quarterly code testing requirement for measuring the unseating force per OM-10 was not met. The failure to perform quarterly testing on the torus-to- drywell vacuum breakers was caused by inadequate change management between the VY IST program improvement team and the test implementing department. The error resulted in an October, 1996 procedure change that allowed the reportable condition. The implementing procedure is being revised to ensure that the test will be performed on a quarterly basis in the future. Other administrative controls are being evaluated to identify and/or prevent similar events. Testing, performed each 6 months, verified that the unseating force was consistent with quarterly test acceptance values, demonstrating that the subject vacuum breakers were operable throughout this time period. Therefore, this event caused no increased risk to public health and safety.
2712000004 | Vermont Yankee | 09/13/2000 | 10/05/2000 | ML00376054 | <strong>Control Circuit Design and the Use of an Incorrect Light Bulb Extraction Tool Results in a Loss of Condenser Vacuum and a Manual Plant Trip</strong><br /><i>Abstract:&nbsp;</i>On 9/13/00, a licensed operator replaced a position indicating light bulb for a steam jet air ejector (SJAE) inlet steam supply valve. The SJAE's are part of a balance of plant, non-nuclear safety system. During the bulb replacement a momentary electrical short was created and caused a protective fuse to blow in the valve control circuit. Although the valve was not in service while the bulb was being replaced, the affected control circuitry shares a common power supply fuse with the redundant (in-service) SJAE steam supply valves. Therefore, the fuse also disconnected power from the in-service SJAE steam supply valves, closing the valves. This caused a lowering main condenser vacuum. The operating crew followed plant procedures for the lowering condenser vacuum while seeking a replacement fuse. Approximately four minutes later, in response to the lowering condenser vacuum, the Station Shift Supervisor directed a manual trip of the reactor. The operating crew brought the plant to a stable shutdown condition following the plant trip. Investigation revealed that the short was caused by the use of an incorrect model bulb extraction tool. The short led to a plant trip because of the design of the associated valve control circuitry. The incorrect model tools were collected and removed from service. The correct model tools were made available. Training on this event was provided to appropriate plant personnel and included the use of the correct extraction tool. An assessment is ongoing to determine if a better extraction tool is available. A review of the adequacy of the affected valve control power circuit design will be performed. All plant safety systems functioned as required to bring the plant to a safe, stable shutdown condition. Therefore, this event presented no significant increase in risk to public health and safety.
2722000001 | Salem 1 | 01/06/2000 | 02/07/2000 | ML00368384 | <strong>Salem Unit 1 Reactor Trip Due to Loss of Normal Feedwater</strong><br /><i>Abstract:&nbsp;</i>At 1611, on January 6,2000,a manual reactor trip was initiated at Salem Unit I due to loss of the 12 Steam Generator Feedpump (SGFP)and degraded SGFP suction pressure as a result of the isolation of condensate flow to the SGFPs. Immediately following the reactor trip, the 11 SGFP also tripped. The safety systems performed as required except for the 12 Auxiliary Feedwater (AFW) pump, which started but failed to inject flow and the N31 Source Range Detector. The redundant source range detector operated properly throughout the shutdown. The cause of the loss of condensate flow is attributed to radio frequency interference (RFI).Based on the troubleshooting performed, the feedwater heater level instrumentation was determined to be susceptible to RFI. Use of radios within the vicinity of the feedwater heater level instrumentation would cause the feedwater heater isolation valves (CN27s) to close. Radio use in the vicinity of the feedwater heater level instruments has been restricted. The feedwater heaters level instrumentation is currently installed in RFI vulnerable enclosures. The enclosures will either be shielded or replaced with enclosures less vulnerable to RFI. This event is reportable in accordance with 10CFR50.73(a)(2)(iv), “any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF),including the reactor protection system (RPS)...".
2722000002 | Salem 1 | 04/11/2000 | 05/10/2000 | ML00371508 | <strong>Salem Unit 1 Manual Reactor Trip Due to Unexpected Rapid Turbine Load Drop</strong><br /><i>Abstract:&nbsp;</i>At 1054, on April 12, 2000, a manual reactor trip was initiated at Salem Unit 1 due to a rapidly decreasing main generator electrical output, while a circuit card in the Valve Position Limiter (VPL) portion of the Electrohydraulic Control (EHC) system was being replaced. This card replacement was being performed as an Infrequently Performed Test and Evolution (IPTE) utilizing procedure SC.IC-GP.EHC.0002 (Z), General Troubleshooting for Main Turbine EHC System. The EHC card was being replaced to correct a previously identified slow downward drifting of the VPL. The apparent cause of the initial drifting of the VPL is attributed to induced signal noise being picked up by the EHC VPL circuitry. This noise was determined to be picked up by two unused wires within the control console push-button, which appeared to have been behaving as an antenna for noise. The cause of the reactor trip is attributed to the proper response by the licensed control room operator to the unexpected load drop following the replacement of the card. The apparent cause of the unexpected load drop has been attributed to a momentary power decrease on the Up/Down converter card while installing the 3QO2E2 card. Corrective actions taken to correct the initial drifting problem and the sudden power decrease included the elimination of the two unused wires within the control console push-button, and the replacement of 3 EHC cards.
2722000003 | Salem 1 | 08/09/2000 | 09/07/2000 | ML00374932 | <strong>Reactor Trip Caused By a Failed Voltage Regulation Circuit Card in the Rod Control System</strong><br /><i>Abstract:&nbsp;</i>At 1751, on August 9, 2000 an automatic reactor trip occurred on Salem Unit 1 in response to negative flux rate trip signals from Power Range Channels 2 and 3 in the Nuclear Instrument System. The negative flux rate trip signals were initiated in response to the insertion of Control Rods in Group B. All systems performed as designed to safely shutdown the reactor and maintain the reactor in a safe shutdown condition. The insertion of the Group B Control Rods was caused by the failure of a voltage regulation circuit card used to regulate power to the control rod drive mechanisms' stationary gripper coils. The defective voltage regulation circuit card was replaced and the Control Rod Drive System was satisfactorily retested. The failed circuit card was returned to the manufacturer for further analysis to determine the cause of failure.
2722000004 | Salem 1, Salem 2 | 09/25/2000 | 10/20/2000 | ML00372522 | <strong>Failure to Comply with Technical Specification 3.7.10 Action a.1</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2000, during the revision of an engineering evaluation for the chilled water system, engineering identified an invalid assumption associated with the determination of heat loads to remove from the chilled water system {KM/CHU}. Due to the invalid assumptions in the engineering evaluation, the table provided in the engineering evaluation for the amount of heat loads to remove from the system based on the chiller cooling water inlet temperature provided non-conservative heat load values. Due to the non-conservative heat loads, the operations procedures did not specify the removal of enough of the appropriate non-essential heat loads from the chilled water system {KM/CHU} to meet TSAS 3.7.10.a.1. Although TSAS 3.7.10.a.1 was not complied with, the chilled water system would have performed as required during a design basis accident. The apparent cause of this event is attributed to personnel errors. The engineering personnel involved in the development of the engineering evaluation did not validate the assumption used for chiller operation and the accuracy of the formula used to calculate the heat loads. Also, the verifier of the engineering evaluation did not identify the above errors. The engineering evaluation and operations procedures have been revised to correct the non-conservative heat load values. Appropriate personnel were held accountable for their actions and lessons learned from this event will be communicated to the appropriate Engineering personnel. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(I)(B).
2722000005 | Salem 1 | 12/08/2000 | 01/08/2001 | ML01016034 | <strong>Reactor Trip Due to a Failed Circuit Card in Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>At approximately 0630, on December 8, 2000, Salem Unit 1 Operators received an overhead alarm "Rx Trip -Low Tavern”. Immediate investigation determined that the Steam Generator levels were falling and the Operator initiated a manual trip. Post trip review determined that an automatic reactor trip occurred, one second prior to the manual trip, in response to low low level in the 13 steam generator. The level in the steam generator fell as result of the feedwater regulating valves going closed due to an invalid signal from the Solid State Protection System. All safety systems performed as designed in response to the trip. Auxiliary feedwater started as designed and steam generator level was returned to proper levels. Post trip investigation determined that an output driver circuit card in the Solid State Protection System had failed, causing the feedwater regulating valves to go closed. The defective circuit card was replaced and the Solid State Protection System was satisfactorily retested and the unit was returned to service on December 10, 2000. The failed circuit card will be returned to the manufacturer for further analysis to determine the cause of failure.
2752000001 | Diablo Canyon 1 | 05/27/1994 | 03/17/2000 | ML00369372 | <strong>Technical Specification 3.3.1 Not Met Due to Inadequate Post Maintenance Tests</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1994, with Unit 1 in Mode 1 (Power Operation) at 90 percent power, Technical Specification (TS) 4.3.1.2 "Reactor Trip System Response Time," surveillance for over temperature delta temperature, was not performed after the isolator associated with nuclear instrumentation (NI) power range channel N41 was replaced, which resulted in not meeting TS 3.3.1. Similarly, on December 3, 1995, with Unit 1 in Mode 1, at 100 percent power, the response time surveillance test was not performed after the isolator associated with NI channel N44 was replaced, which resulted in not meeting TS 3.3.1. On October 25, 1999, engineering concluded the post maintenance test (PMT) performed on Unit 1 channels N41 and N44 was inadequate. On October 27, 1999, the response time surveillance test was satisfactorily performed on N41 and verified current on N44. On February 17, 2000, after the NRC resident inspector questioned the event, PG&E determined the condition was reportable per 10 CFR 50 .73(a)(2)(i)(B). The cause of the TS violation was inadequate PMT due to personnel error .Maintenance personnel determined the PMT requirements without obtaining engineering input. The cause of the late LER was due to personnel error. Regulatory Services personnel failed to recognize the isolator replacement invalidated the response time surveillance. Corrective actions include revising the PMT procedure to incorporate engineering's guidance for required response time testing following maintenance of engineered safety feature and reactor trip system components.
2752000002 | Diablo Canyon 1, Diablo Canyon 2 | 03/09/2000 | 04/10/2000 | ML00370435 | <strong>Manual Control Room Ventialtion Actuation Due To Smoke Infiltration</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2000, at 0906 PST, with Units 1 and 2 operating in Mode 1 (Power Operation) at 100 percent power, plant operators placed the control room ventilation system (CRVS) in pressurization mode (Mode 4) due to smoke. On March 9, 2000, at 0903 PST the Unit 1 control rod drive Motor-Generator (MG) Set 1-2 tripped due to overcurrent and heavy smoke was reported in the immediate area Plant operators responded to alarms and indications in the control room and reports from fire crew members at the MG set location, and isolated the electrical power to MG Set 1-2. Approximately 3 minutes after the initial event, plant operators noticed the smell of smoke in the control room and placed the CRVS in Mode 4.A 4-hour non-emergency report was made to the NRC at 1158 PST in accordance with 10 CFR 50.72 (b)(2)(ii). The cause of this event was the failure of MG Set 1-2. Plant operators placed the CRVS in Mode 4 as a precautionary measure to prevent the build up of smoke in the control room. No corrective actions are required as the plant operators placed the CRVS in Mode 4 as a precautionary measure in accordance with good operating practices. However, as a prudent measure, a review will be performed of the cause of the heavy smoke and damage to MG Set 1-2 in accordance with plant procedures regarding plant equipment failures. This event is reported as a valid engineered safeguards features actuation system event to mitigate the potential for a continued infiltration of smoke into the control room challenging the habitability requirements for continued plant operation.
2752000003 | Diablo Canyon 1, Diablo Canyon 2 | 08/18/1999 | 10/02/2000 | ML00375915 | <strong>Non-Load Bearing Walls in the Turbine Building Do Not Meet Design Requirements Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1999, with Units I and 2 in Mode I at 100 percent power, PG&E determined that several non load bearing concrete walls in the turbine building did not meet design requirements applicable to a postulated Hosgri seismic event .In addition, some of the attached components and commodities did not satisfy similar design requirements .PG&E determined that although some design requirements were not met, the walls and supported components would have been capable of performing their safety functions. The condition was discovered by a PG&E engineer while evaluating the effect of a proposed plant modification. The condition was caused by personnel error and an inadequate design process. The original designers apparently did not consider the potential that quality-related equipment would be mounted on the walls .In addition, the calculation for a Hosgri seismic event did not consider the cumulative effect of the mounted equipment. Confirmatory reviews and calculations were completed to assure that all safety functions were maintained .The calculations identified the need to implement physical modifications to restore adequate design margin. Administrative controls including drawings, procedures, and the Q-List were changed to prevent recurrence.
2752000004 | Diablo Canyon 1, Diablo Canyon 2 | 05/15/2000 | 08/30/2000 | ML00374811 | <strong>Unit 1 Unusual Event Due to a 12 kV Bus Fault</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2000, at 0025 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Unit 1 experienced a unit trip, followed immediately by a turbine trip and automatic reactor trip. The cause of the unit trip was an electrical phase-to-phase fault on the 12 kV bus supplied by Auxiliary Transformer 1-1.The 12 kV electrical fault created electrical arcing (fire) which damaged a nearby 4 kV startup bus resulting in loss of both offsite sources of power to all 4 kV loads. All three onsite emergency diesel generators (EDGs) started, and vital loads automatically sequenced onto the EDGs as designed. In response to the fire and loss of both sources of offsite power to vital loads, an Unusual Event (UE) was declared at 0043 PDT. The onsite fire brigade extinguished the small fire with carbon dioxide. After clearing the room of smoke, the fire was declared out at 0143 PDT. On May 16, 2000, at 0959 PDT, after offsite power was restored and electrical loads were transferred from emergency diesel generators, the UE was terminated. On May 17, 2000, at 2000 PDT, the unit entered Mode 5 (Cold Shutdown). The cause of the electrical fault could not be conclusively determined but is believed to be associated with long-term degradation, and/or inadequate preventive maintenance (PM) exacerbated by a marginal design. Corrective actions include a new PM program and upgrades to the 4 kV and 12 kV nonsegregated buses on both units.
2752000005 | Diablo Canyon 1 | 05/15/2000 | 06/14/2000 | ML00372522 | <strong>Entry into TS 3.0.3 When Power was Restored to Reactor Coolant System Accumulator Valves Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2000, at approximately 1207 PDT, with Unit 1 in Mode 3 (Hot Standby), at 0 percent power, Technical Specification (TS) 3.0.3 was inadvertently entered when power was restored to all reactor coolant system (RCS) accumulator isolation valves while the RCS pressure was 1500 psig. TS 3.5.1 a requires RCS accumulator isolation valves to be open and have power removed in Modes 1, 2, and 3,while pressurizer pressure is above 1000 psig, for the accumulators to be considered operable. At 1455 PDT, while RCS pressure was approximately 1122 psig, the shift foreman recognized the entry into TS 3.0.3. At 1505 PDT,RCS pressure was reduced to less than 1000 psig and TS 3.0.3 was exited. The condition was caused by a personnel error. Operating Procedure L-5,"Plant Cooldown From Minimum Load to Cold Shutdown," and the accumulator isolation valve breaker lamicoid will be revised to contain a reference to TS 3.5.1a. Operating Procedure L-5 will state the specific pressurizer pressure value required by TS 3.5.1a. Lessons learned will be documented and distributed to each of the operating crews.
2752000006 | Diablo Canyon 1, Diablo Canyon 2 | 05/26/2000 | 06/30/2000 | ML00373130 | <strong>Technical Specification 3.4.9.1 Not Met due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2000, with Unit 1 in Mode 3 (Hot Standby), the Limiting Condition for Operation for Technical Specification 3.4.9.1, "Reactor Coolant System Pressure/Temperature Limits," was not met when operators did not adequately document hourly, compliance with Surveillance Requirement 4.4.9.1 during system heatup. On May 31, 2000, this condition was discovered by a utility employee performing a quality assessment. The condition was caused by an inadequate procedure. The procedure was revised February 19, 1999 to allow an alternate means of satisfying the surveillance requirement, but the revision did not adequately stipulate that a licensed operator document hourly that temperatures and pressures were within limits. The surveillance requirement was not met due to inadequate documentation, not an actual violation of temperature/pressure limits. The condition is assumed to have occurred on subsequent heatups and cooldowns on both units. The procedures will be revised to ensure adequate documentation of compliance with the surveillance requirement during reactor coolant system heatup and cooldown.
2752000007 | Diablo Canyon 1 | 10/13/2000 | 11/13/2000 | ML00377052 | <strong>Engineered Safety Feature Actuation - Component Cooling Water Pump Start Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2000, at 1714 PDT, with Unit 1 in Mode 6 (Refueling), an engineered safety feature (ESF) actuation signal initiated a trip of the auxiliary electrical power, separating vital Bus F from the offsite power. The loss of the auxiliary power source actuated an undervoltage relay, starting Component Cooling Water (CCW) Pump 1-1, an ESF component. On October 13, 2000, at 1918 PDT, a 4-hour nonemergency report was made in accordance with 10 CFR 50.72(b)(2)(ii). The root cause of the ESF actuation was personnel error by a utility licensed operator who determined that two tests could be performed simultaneously. A contributory cause was an inadequate procedure that did not include adequate precautions to prevent the inadvertent ESF actuation. The procedure has been revised to include a prerequisite to not perform the test when the affected diesel generator is running.
2752000009 | Diablo Canyon 1 | 10/23/2000 | 11/22/2000 | ML00377203 | <strong>Component Cooling Water Valves Would Not Close Properly Due to Misadjusted Travel Stops - Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 25, 2000, at 1230 PDT, with Unit 1 in Mode 6 (Refueling), PG&E determined that the unit had been outside design basis due to excessive component cooling water (CCW) flow in excess of 70 gpm, past valves that would not close properly. A 4-hour nonemergency report was made to the NRC at 1307 PDT, in accordance with 10CFR50.72(b)(2)(i). Utility engineering personnel discovered two CCW manual butterfly valves not closed properly on October 23, 2000, with the Unit 1 core in the spent fuel pool, while performing a temporary test of CCW System valves. The two CCW valves were not closed properly due to misadjusted travel stops that allowed the discs to rotate past the valve seats. This condition has apparently existed for the life of the plant and was due to personnel error during installation. Immediate corrective actions included: 1. Properly closing the two valves, 2. Adjusting their travel stops, and 3. Verifying proper adjustment of travel stops on similar butterfly valves in the CCW System of both units. Corrective action to prevent recurrence includes requiring maintenance verification testing for similar valves to ensure the travel stops are left properly adjusted after maintenance.
2752000010 | Diablo Canyon 1 | 10/28/2000 | 11/03/2000 | ML00376857 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2000, with Unit 1 in Mode 6 (Refueling), analysis of eddy current testing on Steam Generator (SG) 1-2 indicated that greater than 1 percent of the total tubes inspected were defective. On October 28, 2000, at 1336 PDT, PG&E made a 4-hour, nonemergency report to the NRC pursuant to 10 CFR 50.72(b)(2)(iii)(C), to report this condition as required by Technical Specification (TS) 5.5.9, "Steam Generator (SG) Tube Surveillance Program, "Table 5.5.9-2. On October 24, 2000, PG&E discussed the preliminary results of the eddy current inspection with the NRC during a phone conference as requested in NRC letter to PG&E dated October 12, 2000. During this phone conference, PG&E also notified the NRC that PWSCC and circumferential indications were detected at tube support plate (TSP) intersections, satisfying TS 5.6.10 paragraph d. The majority of the tube defects were attributed to primary water stress corrosion cracking and outside diameter stress corrosion cracking at TSP intersections. PG&E has plugged all defective Unit 1 tubes identified during the current refueling outage in accordance with TS 5.5.9. All defective tubes met the criteria of Regulatory Guide 1.121 for structural integrity at the end of Cycle 10. PG&E maintains a comprehensive program to minimize SG tube degradation.
2752000011 | Diablo Canyon 1 | 11/05/2000 | 12/05/2000 | ML00377661 | <strong>Manual Reactor Trip Due to Rod Control Failure</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2000, at 1707 PST with Unit 1 in Mode 2 (Startup), at 6E-9 amperes, the shift foreman ordered a manual trip of the reactor due to a failure in the rod control system. At 1744 PST, operators made a 4-hour, nonemergency notification in accordance with 10 CFR 50.72(b)(2)(ii). The root cause of the rod control failure was a faulty buffer memory card. The card was replaced and personnel performed the required maintenance verification testing.
2752000012 | Diablo Canyon 1 | 11/20/2000 | 12/20/2000 | ML00378127 | <strong>Unit 1 Automatic Reactor trip Due to Test Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2000, at 0352 PST, with Unit 1 in Mode 1 (Power Operation) at approximately 46 percent power, plant operators experienced an automatic reactor trip. Incore flux map testing was in progress when an intermittent electrical short circuit in test equipment attached to Nuclear Instrumentation (NI)-44, concurrent with a preexisting tripped condition associated with NI-41, provided a two out of four coincidence resulting in a reactor trip. This event is an engineered safety feature and reactor protection system actuation. On November 20, 2000, at 0445 PST, a 4-hour nonemergency report was made in accordance with 10 CFR 50.72(b)(2)(ii). Corrective actions to preclude recurrence include revising procedures, providing a case study regarding this event and expected test prerequisites to appropriate plant personnel.
2772000001 | Peach Bottom 2 | 07/26/2000 | 08/25/2000 | ML00374555 | <strong>The "B" Drywell Wide Range Pressure Instrument Inoperable for Greater Than Technical Specification Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2000, a surveillance was performed on the "B" Drywell Wide Range Pressure recorder in the main control room. The surveillance provides an incremented air test pressure signal of 52.5 psig to the transmitter .When the maximum test pressure was achieved it was noted that the recorder pen for the "B" Drywell Wide Range Pressure indicated 0 psig. Further investigation revealed that in September of 1999, maintenance was performed on the "B" Drywell Wide Range Pressure recorder to replace the drive motor. During performance of the maintenance, leads to several recorder pen servos were inadvertently disconnected. Upon completion of the maintenance, the lead for the "B" Drywell Wide Range Pressure recorder pen servo was incorrectly connected to a recorder pen servo which was not in service. This resulted in the "B" Drywell Wide Range pressure indication being inoperable for greater than the Technical Specification allowable outage time of 30 days. The LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(i)(B) due to the "B" Drywell Wide Range Pressure Post Accident Monitor inoperable for greater than allowable outage time identified in Technical Specifications.
2772000002 | Peach Bottom 2, Peach Bottom 3 | 08/01/2000 | 08/31/2000 | ML00374855 | <strong>This LER reports the Emergency Diesel Generators being in a degraded condition outside of the design basis for operation, in a condition prohibited by the Technical Specifications, and in a condition which could have prevented the fulfillment of the safety functions of the diesel generators.</strong><br /><i>Abstract:&nbsp;</i>On August 1, 2000, field data from Generic Letter 89-13 testing positively identified cross flow conditions being present between the Emergency Diesel Generators (EDG's) air coolant and jacket coolant heat exchangers. Based on this data, each EDG's loading and heat transfer requirements were re-evaluated. Results of this analysis identified that the heat sink temperature required to support the EDG's capability to mitigate a design basis Loss of Coolant Accident Loss of Offsite Power (LOCA/LOOP) event is lower than 90°F. Review of the plants operational history identified that in 1999, the Peach Bottom heat sink temperature exceeded the maximum temperature necessary to support all of the EDG's capability to mitigate a LOCA/LOOP. In 1992, a 10 CFR Part 21 report was issued by Coltec to address the potential for cross flow conditions which was not accounted for in the original design of the equipment. In 1992, the station performed thermography to determine if cross flow conditions existed, however, results of the thermography were determined to be inconclusive at a later date. Additional testing for cross flow was incorporated as part of the Generic Letter 89-13 testing which was conducted in July and August, 2000. The results of the July/August testing verified that cross flow existed between the air coolant and the jacket coolant heat exchangers but did not provide complete qualitative data to determine the entire impact of cross flow on the EDG operation. The main cause of this event is attributed to a design deficiency. The LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(i)(B), 10 CFR 50.73 (a)(2)(ii), and 10 CFR 50.73 (a)(2)(v) for the plant being outside of design basis, operation prohibited by Technical Specifications, and a condition which could have prevented the fulfillment of the safety functions of the diesel generators to mitigate a design basis LOCA/LOOP event.
2772000003 | Peach Bottom 2 | 09/15/2000 | 10/15/2000 | ML00376082 | <strong>Unplanned manual Reactor Protection System (RPS) Scram</strong><br /><i>Abstract:&nbsp;</i>On September 15, 2000 at 1505 hours, with Unit 2 operating at approximately 16% power in preparation for the 13th refueling outage, an unplanned manual reactor scram was inserted. The unplanned manual reactor scram was inserted as a result of the unplanned trip of the 2B Reactor Recirculation pump due to improper tag-out coordination in conjunction with the planned trip of the main turbine. As expected, Primary Containment Isolation System (PCIS) Group 2 and Group 3 isolations, and Secondary Containment isolation also initiated. RPS, PCIS, and Secondary Containment are Engineered Safety Features (ESF). This LER is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(iv) for the unplanned manual scram as a result of the 2B Reactor Recirculation pump trip.
2772000004 | Peach Bottom 2, Peach Bottom 3 | 09/28/2000 | 10/27/2000 | ML00377294 | <strong>Emergency Diesel Generators in a Degraded Condition Potentially outside of the design basis</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2000, data from an in-service surveillance test indicated a check valve did not prevent reverse flow from the safety related Emergency Service Water (ESW) system into the non-safety related Service Water (SW) system. This reduced the flow to each of the Emergency Diesel Generators (EDG) resulting in a reduction in the calculated allowable maximum heat sink temperature to maintain the EDG operable. No other supported ESW systems were impacted by this degradation. The last successful surveillance test on the check valve was completed on September 25, 1998. Because an evaluation could not determine when the check valve failed, an engineering analysis was performed of the as-found condition, from September, 1998 to September, 2000. Furthermore, because this condition coexisted with the EDG heat exchanger cross flow issue reported in LER 2-00-002, the analysis of accident scenarios conservatively considered both degraded EDG conditions for the two year period. This design basis analysis determined the calculated allowable heat sink temperature to be less than or equal to 78.5 degrees Fahrenheit. Since September, 1998, the actual heat sink temperature periodically exceeded this calculated maximum allowable heat sink temperature. Therefore, because the time of the check valve failure is indeterminate, the degraded condition resulted in a condition potentially outside of design basis. The EDG degradation is attributed to an ESW component failure that was corrected promptly.
2772000005 | Peach Bottom 2 | 10/04/2000 | 11/03/2000 | ML00376804 | <strong>Condition prohibited by Technical Specifications Due to Entering Mode 2 without performing a required surveillance test</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2000, it was discovered that a required post maintenance test (PMT) to scram time test control rod 34-55 was not performed prior to entering Mode 2 and commencing reactor startup. The test was required by Technical Specification SR 3.1.4.3 to verify control rod operability because maintenance was conducted on the control rod which could have affected its scram time. A plant startup was in progress and control rod 34-55 was moved to position 48 (full out) when a control room operator recognized that the appropriate PMT had not been performed. The reactor startup was immediately halted and the control rod was scram time tested satisfactorily. Technical Specification SR 3.0.4 states "Entry into a mode or other specified condition in the Applicability of an LCO shall not be made unless the LCO's Surveillances have been met with their specified Frequency." Since the required surveillance was not performed in order to demonstrate the operability of control rod 34-55, entry into Mode 2 was prohibited by Technical Specifications.
2772000006 | Peach Bottom 2 | 10/22/2000 | 11/20/2000 | ML00377210 | <strong>Primary Containment Inoperable Due to a Suppression Chamber-to-Drywell Vacuum Breaker valve disk not being properly seated</strong><br /><i>Abstract:&nbsp;</i>On 10/22/00, a controlled plant shutdown was initiated due to Primary Containment being declared inoperable. Primary Containment had been declared inoperable when a Drywell to Suppression Chamber bypass test indicated that the `H' Suppression Chamber-to-Drywell Vacuum Breaker was not seated. To perform repairs to the 'H' Vacuum Breaker, the plant was shutdown and Mode 4 was achieved exiting a plant operating condition in which Primary Containment was required to be operable. The cause of the event is the failure of the 'H' Suppression Chamber-to-Drywell Vacuum Breaker to properly seat when exercised on 10/22/00. This was due to a missing retaining clip on the hinge shaft of the vacuum breaker. The missing retaining clip allowed movement on the hinge shaft resulting in misalignment between the valve disk and the seat. The 'H' Vacuum Breaker was repaired and declared operable on 10/24/00. The preventative maintenance procedure will be revised to ensure that the vacuum breaker hinge pin shaft is thoroughly inspected in the future.
2782000001 | Peach Bottom 3 | 08/07/2000 | 09/06/2000 | ML00374894 | <strong>Reactor Protection System (RPS) actuation and Primary Containment Isolation System (PCIS) actuation. Condition prohibited by Technical Specifications and a Loss of Safety Function occurred During the event.</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2000, at 2126 hours, the Unit 3 reactor experienced an automatic shutdown (scram) due to an invalid low reactor water level signal sensed by the Reactor Protection System (RPS). The cause of the invalid reactor water level was the failure of the packing gland follower on RRV 3-2-654B which resulted in the depressurization of the variable leg to various instruments. A Primary Containment Isolation System (PCIS) Group 2 and Group 3 isolation signal, and secondary containment isolation also resulted. RPS, PCIS, and secondary containment isolation are Engineered Safety Features (ESF). During the scram recovery, due to a false low reactor water level signal, the operating crew was directed by procedure to override the low reactor level and high drywell pressure initiation signals on Standby Gas Treatment (SGT) to allow for restoration. The override removed the automatic start function of both SGT subsystems. In addition, the Unit was in Mode 3 when the initiation signal was overridden and SGT was required to be operable per Technical Specifications. As a result, this placed the unit in Technical Specification LCO 3.0.3. The LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(iv)due to the automatic actuation of Engineered Safety Features (ESF).Additionally, the reporting requirements of 10CFR50.73 (a)(2)(i)(B)and 10CFR50.73 (a)(2)(v)were met due to entry into Technical Specification LCO 3.0.3 and loss of safety function of Standby Gas Treatment (SGT) during the reactor scram recovery.
2782000002 | Peach Bottom 3 | 12/17/2000 | 01/12/2001 | ML01025006 | <strong>Primary Containment Isolation When Suppression Chamber Purge and Vent Valves Closed Due to a Spurious Invalid Signal Generated by a Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On 12/17/00, at 0540 hours, an isolation of the outboard vent and purge valves for the primary containment suppression chamber occurred when the communications board for the 'B' radiation monitor for the plant main off gas stack failed as a result of a lightning strike. The failure of the communications board resulted in the generation of a spurious invalid signal that resulted in the isolation. Repairs were promptly initiated to replace the communication board for the 'B' radiation monitor. Repairs and subsequent testing were complete on 12/17/00 at approximately 1600 hours. There were no actual safety consequences due to this event. The 'A' radiation monitor was not damaged by the lightning storm. At the time of the spurious isolation, there were no radiological concerns or abnormal conditions that actually required isolation.
2802000001 | Surry 1, Surry 2 | 04/18/2000 | 07/20/2000 | ML00373523 | <strong>Filtered Exhaust Fan Failure Results In Technical Specifications Violation</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2000, Unit 1 was at Cold Shutdown and Unit 2 was at 100% power. While testing the ventilation exhaust system, both fans automatically started as designed, but subsequently tripped. One fan was returned to service and a 7 day Technical Specification (TS) action statement was entered. Additional testing on April 19 concluded that the fans could not be relied upon to operate in parallel. A prior change to fan flow controls was preliminarily identified as the cause. The control setpoints were adjusted and after testing, the action statement was exited. Additionally, while testing on April 18, 2000, a Unit 1 damper failure rendered both fans inoperable for a short period causing Unit 2 to be in a 6 hour TS action statement to Hot Shutdown. Testing verified that the failed damper did not impact Unit 2 and the action statement was exited. A condition in which both fans were inoperable also occurred on June 21, 2000. This condition resulted from a soiled supply filter and the system operating configuration, which was permitted by procedural changes implemented to address the April 2000 ventilation transients. A root cause evaluation was initiated for these events and approved corrective actions will be implemented. This event resulted in no safety consequences or significant implications. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2802000002 | Surry 1, Surry 2 | 06/29/2000 | 09/15/2000 | ML00371824 | <strong>Effect of Ventilation Fans on Control Room Boundary Results in TS Violation</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2000, Units 1 and 2 were operating at 100% reactor power. While conducting a test of the Control Room Pressure Envelope (CRPE), newly installed differential pressure (DP) indicators between the CRPE and the Unit 1/2 Cable Tunnel/Vaults did not meet the acceptance criteria of Technical Specification (TS) 3.19.A. An 8 hour TS 3.19.13 Limiting Condition for Operation (LCO) was entered. Corrective actions were taken to eliminate localized low pressure areas within the envelope where the new indicators were installed. In addition, fans adjacent to the CRPE were secured to eliminate any influence that they may have had on the CRPE. Following these actions, a bottled dry air bank was discharged and the test was performed again. The test results met the acceptance criteria and the 8-hour LCO was exited. A root cause evaluation (RCE) was initiated. On August 17, 2000, after an Engineering evaluation of the test results, it was determined that the conditions found during the event were pre-existing and the event was reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by TSs. The most probable cause is the design of the return air flowpath for the MCR air handling units. Upon completion of the RCE approved corrective actions will be implemented. This event resulted in no safety consequences and the health and safety of the public was not affected.
2802000003 | Surry 1, Surry 2 | 10/03/2000 | 11/01/2000 | ML00376719 | <strong>Both Filtered Exhaust Fans Inoperable Due to Operation Close to Trip Setpoint</strong><br /><i>Abstract:&nbsp;</i>On October 3 and 4, 2000, with Unit 1 operating at 100% reactor power and Unit 2 at cold shutdown for a refueling outage, two events associated with the safety-related (SR) ventilation exhaust system occurred that were determined to be reportable conditions. On October 3, 2000 both SR exhaust fans tripped during Unit 2 train B logic testing. On October 4, 2000, with one SR fan operating, a non-SR exhaust fan was secured and the operating SR exhaust fan tripped. Following this event, one SR fan was maintained operable and a 7-day clock to return both fans to service was entered. Based upon the problems identified during the repair efforts, the operability of the fans was affected since the implementation of a design change in November 1999. The trip setpoint was changed to increase operating margin, the flow controllers tuned, maintenance performed on the inlet flow control dampers, and a fan start time delay implemented. The fans were returned to service and an amended 7-day clock was exited. A root cause evaluation was initiated and approved corrective actions will be implemented. This event did not affect the health and safety of the public. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
2802000004 | Surry 1 | 10/24/2000 | 11/21/2000 | ML00377196 | <strong>Reactor Trip on Lo Lo Steam Generator Level Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2000, at 07:41, with Unit 1 at 100% power, control room annunciators alarmed indicating a low low steam generator (SG) level and an automatic reactor trip of Unit 1 occurred. Immediately prior to the trip, the main steam dump valves were observed to have received an open demand, and a loss of turbine load was exhibited. The event was caused by human error due to work being performed on the wrong unit. Work was being conducted on the Unit 1 Electrical Hydraulic Controls (EHC) System instead of the intended Unit 2 EHC System. Approved Root Cause Evaluation recommendations, designed to prevent the recurrence of a similar event, will be implemented. The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on October 24, 2000 at 10:30. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv) as an event that resulted in the automatic actuation of engineered safety features and the reactor protection system.
2812000001 | Surry 2 | 01/27/2000 | 02/25/2000 | ML00369156 | <strong>Containment Isolation Valve Found with Unacceptable Leakage During Maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2000, a review of testing results indicated that during the replacement of 2-DA-TV-200A, the leakage through 2-DA-TV-200B was in excess of the allowable Type "C" limits. On January 25, 2000, with Unit 2 at 100% reactor power, 2-DA-TV-200A was replaced in less than one hour. The excessive leakage of 2-DA-TV-200B was not discovered until performing the post maintenance testing of 2-DA-TV-200A. Once this condition was identified, appropriate actions were taken in accordance with Technical Specifications. 2-DA-TV-200B was replaced, satisfactorily tested, and returned to service. Based upon preliminary indications, it is believed that 2-DA-TV-200B failed because dirt and debris became impacted between the ball and valve seat causing excessive wear. A root cause evaluation has been initiated and approved recommendations will be implemented through the Corrective Action Program. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. A 4-hour report was made on January 27, 2000 pursuant to 10CFR50.72(b)(2)(iii)(C). This event is being reported pursuant to 10CFR50.73(a)(2)(v)(C) and 10CFR50.73(a)(2)(i)(B).
2822000001 | Prairie Island 1, Prairie Island 2 | 01/12/2000 | 02/11/2000 | ML00368506 | <strong>Missed Surveillance Of Steam Exclusion Damper Due To Incorrect Wiring and Malfunctioning of Limit Switch</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2000, with Prairie Island Units 1 and 2 operating at 100% power, the CLOSE limit switch on the Auxiliary Building Steam Exclusion Area Train A damper CD-34176 was determined to provide improper indication of damper position. Damper position indication is relied upon during the monthly performance -of the surveillance procedure SP 1112, "Steam Exclusion Damper Test" to verify that all of the dampers in the Steam Exclusion Ventilation Isolation System have moved to the closed position as required to perform the safety function, ventilation isolation. The combination of a wiring error at the limit switch and a malfunctioning limit switch created a situation where each non-conforming condition concealed the other non-conforming condition from detection during the performance of SP 1112. A work order has been issued to conduct an inspection of all 26 steam exclusion dampers and their associated limit switches to establish that all dampers are operable, all associated limit switches are wired correctly and all associated limit switches function properly. A work order has been issued to remove the malfunctioning limit switch from CD-34176 and have it analyzed to determine the failure mechanism and identify a probable root cause for the failure. This issue will be tracked and resolved through the Prairie Island Corrective Action program.
2822000002 | Prairie Island 1, Prairie Island 2 | 08/21/2000 | 09/20/2000 | ML00375464 | <strong>Fuel Pellet Density Exceeds Assumption in Spent Fuel Pool Criticality Analysis</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2000, with the Prairie Island Nuclear Generating Plant (PINGP) Units 1 and 2 operating at 100% power, a representative of the current PINGP nuclear fuel assembly vendor informed PINGP staff by telephone that recent batches of fuel assemblies delivered to PINGP contained fuel pellets with nominal densities greater than the 95% of theoretical density assumed in the criticality analysis submitted in support of Amendments 129/121 to the PINGP Unit 1 and 2 Operating Licenses DPR-42 and DPR-60. This increased nominal fuel pellet density results in the calculated 95/95 Keff exceeding the Technical Specification 5.6.A.1.b limit (Keff,<1.0 if the spent fuel pool were fully flooded with unborated water) for fuel assemblies stored in both unrestricted and restricted (3x3 checkerboard) configurations. Actions have been taken to provide increased assurance that any significant dilution event will be detected before the boron concentration in the spent fuel pit could be reduced below 750 ppm. The investigation into the root causes of this event is still in progress and a final determination of the root causes and corrective actions has not been made.
2822000003 | Prairie Island 1, Prairie Island 2 | 10/26/2000 | 11/27/2000 | ML00377513 | <strong>Flooding from Postulated Failure of Air/Vacuum Valve has Potential to Disable Both Trains of Essential Service (Cooling) Water</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2000, with the Prairie Island Nuclear Generating Plant (PINGP) Units 1 and 2 operating at 100% power, the engineering staff concluded that the air/vacuum valve on the discharge pipe of each safety-related Cooling Water (essential service water) pump had the potential to fail to close when required. Such a failure would lead to flooding of the Cooling Water pump room in the screenhouse resulting in a common mode failure of the safety-related Cooling Water system and a loss of the ultimate heat sink for both units. While this postulated scenario may not be credible, an operator was stationed in the safety-related Cooling Water pump room to maintain a continuous "flood" watch on the air/vacuum valves until a modification was completed on November 15, 2000, which piped the discharge of the air/vacuum valves out of the pump room and back to the Cooling Water pump suction bay. Activities are in progress to evaluate the credibility, consequences and significance of postulated failures of these air/vacuum valves.
2822000004 | Prairie Island 1, Prairie Island 2 | 11/01/2000 | 03/22/2001 | ML01087029 | <strong>Inoperability of Safeguards Cooling Water (Essential Service Water) Pumps Caused by Unqualified Lubricating Water Supply to the Pump Shaft Bearings</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2000, at 1:40 PM CST, three safeguards vertical cooling water pumps were declared inoperable for lack of qualified source of lubricating water supply to line shaft bearings. The lubricating water had been originally designated as safety-related but had been downgraded in 1977 and subsequent physical changes did not maintain the original quality level. It was thought at the time that this independent source of water was not necessary for pump operability. Because of the downgrade, continued operation of the water supply could not be assured during certain design basis events and the cooling water pumps were administratively declared inoperable though still functional. Appropriate compensatory measures were developed and put in place. By November 13th installation was completed on a temporary modification which restored a qualified lubricating water supply to two of the three pumps, restoring their operability (only two pumps are required to be operable). Another temporary modification restored operability to the third pump at a later date.
2822000005 | Prairie Island 1, Prairie Island 2 | 12/27/2000 | 01/25/2001 | ML01030021 | <strong>Failure to Test Cooling (Service) Water Strainer Backwash Valves Due to Inadequate Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2000, with the Prairie Island Nuclear Generating Plant (PINGP) Units 1 and 2 operating at 100% power, the engineering staff concluded that the Cooling Water strainer backwash valves belong within the scope of the Inservice Test (IST) program. However unlikely, it is possible for external events to introduce a significant amount of disturbed and unsettled solids into the river water supply for the cooling water (service water) system. The use of such water may eventually require the strainer backwash function to maintain operation of the cooling water system. As such, the Cooling Water strainer backwash valves perform a specific function required to shut down the reactor and maintain the reactor in a safe shutdown condition. Therefore, these valves are required by regulations to meet the requirements applicable to valves which are classified as ASME Code Class 2 or Class 3, including the requirement to perform inservice testing in the manner prescribed by ASME Section XI. These valves have been placed into the IST Program and stroke time measurements have been obtained, reviewed and found to be acceptable.
2852000001 | Fort Calhoun | 03/09/2000 | 04/06/2000 | ML00370206 | <strong>Recalculation of Dose to the Control Room Operators Places the Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>The current design basis control room airborne dose calculations for accidents that result in radiological consequences to the Fort Calhoun Station (FCS) control room personnel assume an unfiltered control room in-leakage value of 0 standard cubic feet per minute (scfm). As a result of discussions with the NRC, tracer gas testing was performed to confirm this assumption. The testing determined that the unfiltered in-leakage rate is 8 scfm. On March 9, 2000, Design Engineering Nuclear (DEN) completed verification of the contractor analysis of the control room in-leakage test and the effect on control room dose. This evaluation determined that with the measured control room unfiltered in-leakage rate of 8 scfm, the design basis loss of coolant accident thyroid dose to the control room operators is about 32 rem. This is outside the current design basis of the plant of 30 rem thyroid dose. DEN had previously prepared a Safety Analysis for Operability (SAO) 99-01 to address the basis for continued operability in the event that tracer gas testing resulted in unfiltered in-leakage greater than 0 scfm. With the measured unfiltered in-leakage being less than 100 scfm, the control room remains operable based upon the analysis and bases documented in the SAO. Corrective actions to address this issue were included in the Station's response to Generic Letter 99-02 and LER 1998-013.
2852000002 | Fort Calhoun | 11/01/2000 | 12/01/2000 | ML00371954 | <strong>Plant Operation Outside of Low Temperature Overpressure Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2000, a Fort Calhoun Station (FCS) engineer was reviewing the station's low temperature overpressure protection (LTOP) analysis. The engineer noted that station operating procedures direct that the reactor coolant system (RCS) be taken water-solid to cool down the pressurizer when RCS temperature is below 200 degrees Fahrenheit. The LTOP analysis assumes that a steam volume is maintained in the pressurizer when RCS temperature is above 130 degrees Fahrenheit. This condition is reportable per 10 CFR 50.72(b)(2)(i). The root cause of this event is the process for incorporating the LTOP analysis assumption on pressurizer level into the Technical Specifications failed to capture a key assumption in the operating procedures. Shift and operations management were informed of the assumptions in the analysis and its implications for the plant. Procedures have been corrected to properly reflect the assumptions of the existing LTOP analysis.
2852000003 | Fort Calhoun | 11/03/2000 | 03/16/2001 | ML01080004 | <strong>Failure of Component Cooling Water System Valves by a Potential Common Mode</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2000, the AC-1C Component Cooling Water (CCW) heat exchanger (HX) inlet valve, HCV-491 A, did not fully open when placing the HX in operation. Minutes later, the AC-1B CCW HX inlet valve, HCV-490A, failed to open at all. Following the failure of HCV-491A and HCV-490A on October 23, 2000, a failure investigation was initiated. Results of the investigation concluded the actuator springs for all four CCW HX inlet valves were marginally sized and all four valves had packing torques that were excessive. The investigation also concluded that the failures that occurred in the October 23, 2000, time frame were not related to and not caused by the same failure mechanism. In order to increase valve reliability and prevent recurrence, the actuator springs for the CCW HX inlet and outlet valves were subsequently replaced with higher capacity springs.
2862000001 | Indian Point 3 | 01/17/2000 | 02/16/2000 | ML00369003 | <strong>Plant Outside Design Basis Due to a Mispositioned Valve Caused by a Procedure Error that Could Prevent Use of Low to High Head Safety Injection Recirculation Under Postulated Accident Conditions When Considering a Passive Failure</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2000, Operations discovered Safety Injection (SI) system manual butterfly valve SI-1863 mispositioned closed during an extent of condition inspection for the inability to establish excess letdown. The valve was opened shortly after discovery, the event was reviewed and the system was considered to be operable and not reportable. Further assessment of the event report on January 17 determined that the condition could potentially place the plant outside design basis and a one hour event notification was made to the NRC. FSAR Table 6.2-8 describes the use of an alternate low-to-high head SI flowpath during recirculation following a postulated accident should the normal flowpath be unavailable due to a passive failure. The inappropriate closure of valve SI-1863 could prevent the use of the alternate SI flowpath thereby placing the plant outside its design basis. The event was due to a deficiency in procedure SOP-RP-20, "Draining the Refueling Cavity," caused by personnel error as a result of inadequate error detection/self checking. The procedure did not require the valve to be returned to the Check Off List (COL) open position. Corrective actions for this event included opening valve SI-1863, issuance of a shift order for operators to review safety related procedures against their associated COL to ensure components are restored to the COL position upon completion of the procedure and the need for attention to detail, and re-performing accessible portions of safety related COLs. Procedure SOP-RP-20 will be revised prior to next use, and all safety related procedures will be reviewed to ensure they require components to be restored to the COL position. There was no effect on public health and safety.
2862000002 | Indian Point 3 | 03/30/2000 | 04/27/2000 | ML00371282 | <strong>Plant Outside Design Basis Due to Routing of Component Cooling Water Piping Within the Fuel Storage Building Which was not Designed for Tornado Effects During Original Plant Design</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2000, the plant was determined to be outside design basis after Engineering determined that one loop of the Component Cooling Water (CCW) system piping located in the Spent Fuel Storage Building (FSB) was not in compliance with FSAR design criteria. During review for the 10CFR50.54(f) program the discrepancy of the CCW piping design was identified. The FSAR indicates that CCW is protected from tornadoes and tornado generated missiles by structures designed for the effects of tornado loads. After further investigation Engineering determined the CCW piping located in the FSB is not protected from the effects of tornadoes by the FSB. Initially the issue was not considered reportable because protection of CCW piping from the effects of tornado missiles can be provided by the redundancy of the CCW system. An evaluation concluded that CCW system can sustain damage from a tornado missile and with manual operator action there is no loss of function. The evaluation credited operator action in existing procedures to initiate makeup water to the CCW system. The plant continued operation based on a Reasonable Expectation of Operability, and a Reasonable Assurance of Safety (RAS). The corrective action will be preparation of a submittal to the NRC for revision of the CCW design basis. There was no effect on public health and safety.
2862000003 | Indian Point 3 | 04/19/2000 | 05/17/2000 | ML00372048 | <strong>Automatic Acutation of Auxiliary Boiler Feedwater Pump 32 During Testing of Emergency Diesel Generator 32 Due to High Resistance in the Contacts of a Reset Switch in the Non-Safety Injection Blackout Logic Defeated Circuitry</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2000, the turbine driven Auxiliary Boiler Feedwater (ABFW) pump 32 automatically started unexpectedly coincident with opening the 32 Emergency Diesel Generator (EDG) output breaker during performance of monthly functional test 3PT-M79B. Normally the "Non-Safety Injection (SI) Blackout Logic Defeated" circuitry prevents automatic starting of equipment until manually reset. Operators secured the 32 ABFW pump. There was no injection of water into the steam generators. The cause of the event was a failed open Non-SI Blackout Logic Defeated push-button reset switch due to high resistance contacts. Corrective actions included troubleshooting that identified the cause, assessments that determined that the 32 ABFW pump and 32 EDG were operable, and replacement of the reset switch for bus 6A. The reset switches associated with EDGs 31 and 33 were tested and determined to be satisfactory. This event had no effect on the health and safety of the public.
2862000004 | Indian Point 3 | 02/05/1995 | 10/17/2000 | ML00376328 | <strong>Missed Control Room Oxygen Detector Surveillance Tests is a Condition Prohibited By Technical Specification Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2000, at approximately 0500 hours, with steady state power at approximately 100 percent, Operations determined that the channel check required by Technical Specification (TS) 4.5.A.5.e was not being performed on the Oxygen detector in the Control Room locker room. Operations subsequently determined that channel checks had not been documented between February 5, 1995 and May 18, 2000. The missed surveillance tests is a condition prohibited by TS 4.5.A.5.e. and, as noted in TS 4.1, constitutes a non-compliance with the limiting condition for operation in TS 3.3.H.3. The cause of the event was human error, removal of the channel check requirement from the operator log sheets. The cause of that human error is indeterminate. The event was found when an operator noticed the locker room Oxygen detector was turned off. Immediate corrective action was taken to turn on the oxygen detector and check the channel. Corrective action was taken to list the required detectors on the Conventional Cold Shutdown and Hot log sheets .An extent of condition review of channel checks required by Technical Specifications found no other channel check requirements missing from the log sheets .There is no safety significance to public health and safety. Two channels of oxygen detection were maintained per Technical Specification and analyses have shown that a C02 release would not result in toxic levels of C02 in the control room.
2862000005 | Indian Point 3 | 05/18/2000 | 06/19/2000 | ML00372681 | <strong>Pressurizer Safety Valves Discovered Outside Their As-Found Lift Setpoint Test Acceptance Criteria After Removal and Testing; A Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2000, performance engineering was notified by Wyle Laboratories that all three (3) pressurizer code safety valves (SV) were outside their As-Found (AF) lift setpoint test acceptance criteria (2461 - 2509 psig). The SVs were removed during the last refueling outage in the fall of 1999, and sent off site for testing. Wyle Labs used test 3PT-RO05A which contains an AF setpoint pressure criteria of 2485 psig +/-1%. The SVs tested low but above the setpoint of the pressurizer Power Operated Relief Valves (2335 psig). Technical Specification (TS) 3.1.A.2.b requires that all pressurizer Code SVs be operable whenever the reactor is above cold shutdown. TS 3.1.A.2.c requires the SVs to be set at 2485 psig with +/-1% allowance for error but there is no AF setpoint specification. Discrepancies found in TS surveillance tests are assumed to occur at the time of the test unless there is firm evidence to believe that it occurred earlier. In accordance with NRC guidelines, the existence of similar discrepancies in multiple valves is an indication that the discrepancies may have arisen over a period of time and therefore the condition may have existed during plant operation and is therefore reportable. The cause of the condition was attributed to setpoint drift over the last operating cycle. The valves will be overhauled and parts replaced as necessary and As-Left (AL) tested to the correct setpoint prior to installation. The test will be revised to reflect the ASME Code AF allowable of +/-3%. The SV currently installed were AL tested to +/-1%. The event had no effect on public health and safety.
2862000006 | Indian Point 3 | 06/20/1985 | 06/26/2000 | ML00372883 | <strong>Plant Outside Design Basis Because Cable Separation Criteria Were Violated Due to Human Error In Preparation of the Engineering Change for Sparing a Channel III Cable and in Configuration Control of Test Equipment</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2000, operations personnel determined that the plant was in a condition outside its design basis due to a violation of the licensing basis cable channelization criteria. A spare, non-vital channel III cable was found coiled in a channel II cable tray. The non-vital channel III cable was improperly spared on June 20, 1985 due to a human error. Short term corrective actions removed the spare cable from the channel II tray and disconnected the cable from its power source. On June 8, 2000, preliminary extent of condition general walkdowns identified two cables crossing between cable trays, a violation of licensing basis cable channelization criteria. The two cables, not in service, were removed. The extent of condition evaluation will be done by walking down a sample of cable trays to verify that cables have been properly spared and that cable runs do not cross between cable trays. These events had no effect on the health and safety of the public because no actual faults occurred and because postulated faults are either not credible or do not cause loss of redundant equipment.
2862000007 | Indian Point 3 | 06/04/2000 | 07/05/2000 | ML00373290 | <strong>Automatic Reactor Trip After Turbine Trip Due to Low Level in Steam Generator 31 as a Result of Personnel Error During Transfer of Feedwater Control</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2000, an automatic reactor trip (RT) occurred during plant startup with the main turbine generator tied to the grid and reactor power being raised to 30%. At approximately 22% reactor power, control of feedwater (FW) to the steam generators (SG) was being transferred from bypass feedwater flow to main FW flow by manually adjusting FW regulating valves (FRV). When adjustment to main boiler FW pump speed was made by a licensed operator, FW flow increased and the level in the 33 SG reached the high-high, level setpoint initiating a turbine trip (TT). The TT caused a rapid decrease in SG water level due to shrink. When the 31 SG reached the low-low level setpoint an automatic RT was initiated. Required equipment functioned as designed. The power operated relief valves (PORVs) and pressurizer safety valves did not lift due to the transient. Auxiliary feedwater actuated per design as a result of the RT. The plant was stabilized in the hot shutdown condition. The RT was caused by a cognitive personnel error by a licensed operator who failed to adequately control FIR pump speed during direction of an operator trainee who was controlling FRVs. Significant corrective actions taken include removal of responsible licensed operators from shift duty, preparation of an action plan for assessment of operations personnel performance and identification of improvements/recommendations. The event had no effect on public health and safety.
2862000008 | Indian Point 3 | 06/09/2000 | 07/07/2000 | ML00373289 | <strong>Automatic Reactor Trip as a Result of Direct Trip from the Buchanan 345 KV Substation Upon Protective Relay Conductors Low Insulation Resistance Fault</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2000 an automatic reactor trip (RT) occurred. The RT occurred as a result of a main turbine trip with reactor power greater than the P-8 permissive set point. The main turbine trip was caused by a main generator trip initiated by the electrical protective relaying direct trip circuitry from the offsite 345 KV Buchanan Substation. This direct trip circuitry actuated the main generator primary and backup lockout (86P and 86 BU) relays. All primary and secondary plant systems responded as required after the automatic RT. Station offsite power was maintained throughout the event and there was no automatic start of the Emergency Diesel Generators. The Auxiliary Feedwater system automatically started after this RT due to a low-low Steam Generator (S/G) level resulting from the SIG water level "shrink." The most probable cause of the direct trip circuitry actuation was a low insulation resistance between several conductors in a cable routed between Indian Point 3 (IP3) and the Buchanan Substation 345 KV South Ring Bus Control House. Corrective actions include disconnecting the faulted conductors and wiring in spare conductors and testing the direct trip circuitry for acceptable functionality. This event had no impact on the public health and safety.
2862000009 | Indian Point 3 | 07/20/2000 | 08/17/2000 | ML00374468 | <strong>Plant Outside Design Basis Due to Valve Seat Leakage During Maintenance That Exceeded the External Recirculation Leakage Limits for the Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2000, Operations determined that the Reactor Coolant System (RCS) indicated (total) leak rate increased to approximately 0.3 gpm. Water draining from the opened bonnet of the Chemical and Volume Control System (CVCS) deborating bed outlet isolation valve (CH-313) was measured. The bonnet on valve CH-313 was purposely loosened to provide a low point drain path to support a corrective maintenance (CM) activity. The measured leakage rate correlated to the observed increase in RCS leakage. After an assessment of possible leak pathways, Operations judged that the leak pathway was from the Reactor Coolant Pump (RCP) seal return line to the normal CVCS letdown line through the seat of relief valve CH-263 and through the opened bonnet of valve CH-313. Because valve CH-313 is in the Primary Auxiliary Building (PAB), a path was created for RCS to leak outside containment. Postulating a Design Basis Accident (DBA) concurrent with this condition would result in exceeding the assumed leak rate in the calculation for control room dose, placing the plant outside its design basis. The event was due to a presumed degraded relief valve, CH-263. Corrective actions for this event included isolating the leakage path, replacement of valve CH-313 bonnet and verification of system leak tightness. Valve CH-263 is scheduled to be inspected and repaired in the upcoming refueling outage, RO11, scheduled for May of 2001. There was no effect on public health and safety.
2862000010 | Indian Point 3 | 07/21/2000 | 11/13/2000 | ML00377049 | <strong>Isolation of the Containment Spray System Spray Additive Tank During Preventative Maintenance is a Condition Prohibited by Technical Specifications and Outside Design Basis Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2000 Engineering and Operations personnel determined that the Containment Spray (CS) system Sodium Hydroxide (NaOH) Spray Additive Tank (SAT) had been isolated on July 21, 2000 for approximately eight hours and forty minutes to perform preventative maintenance. The CS SAT was isolated, preventing automatic addition of NaOH to the CS system, by shutting SAT isolation valve, SI-1841, as part of the protective tagout for replacing the pilot solenoid on CS SAT discharge isolation valve, SI-AOV-876B. No allowed outage time is provided for this condition in Technical Specification section 3.3.B, so this is a condition prohibited by Technical Specifications. This event also resulted in the CS system being outside of its design basis. The cause of this event was human error. Operators misinterpreted the Technical Specifications when applying the system protective tagout. Corrective actions taken include an Operations Shift Order communication about this event to the operating crews. This event had no significant impact on public health and safety due to the short time period in which the SAT was isolated and because all three Emergency Diesel Generators (EDGs), both CS pumps and all five Containment Fan Cooler Units (FCUs) remained operable.
2862000011 | Indian Point 3 | 10/27/2000 | 11/27/2000 | ML00377437 | <strong>Reactor Core Quadrant Power Tilt Ratio Exceeded Technical Specification Limit During Startup and Specified Actions Not Taken; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2000, during startup at approximately 45% reactor power, Operations identified a condition which was not in accordance with Technical Specification (TS) 3.10.3.1. TS 3.10.3.1 requires that "Whenever the indicated quadrant power tilt ratio (QPTR) exceeds 1.02, except for physics tests, within two hours the tilt condition shall be eliminated or the following actions shall be taken: a) Restrict core power level and reset the power range high flux setpoint three percent of rated value for every percent of indicated power tilt ratio exceeding 1.0." During operator adjustment and assessment for exceeding a QPTR limit, a review of earlier startup QPTR records showed a previous QPTR calculation of greater than 1.02 at a lower power. Because an indicated QPTR calculation is expected at low powers when the tilt alarm is by design not functional, no action was taken. This is consistent with the TS basis. However, in subsequent review, Operations concluded the event was a condition prohibited by TS, based on the exact wording of TS 3.10.3.1. The cause of the condition was inadequate TS due to written communication as a result of personnel error, in that TS 3.10.3.1 does not specify that the limiting condition for operation is only applicable above 50% Rated Thermal Power, as implied in the TS basis. Failure to comply with the exact statements of the TS was due to inconsistency between the TS definition of QPTR and its application in the TS basis. Corrective actions include adjustment of the flux setpoints per the TS and the revision of the TS when the Improved TS (ITS) is implemented. The event had no effect on public health and safety.
2872000001 | Oconee 3 | 01/03/2000 | 02/02/2000 | ML00368156 | <strong>Reactor Trip After Manual Main Turbine Trip Due to Instrument Failure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1254 on January 3, 2000, with Unit 3 at approximately 100 percent power, a Stator Cooling runback occurred. Operations verified that plant equipment was responding appropriately. It was observed that Generator MWatts had run back to 0 with Generator MVARs indicating 260 and that the Generator breakers were closed. At approximately 1257, these conditions along with HiHi Generator Stator winding temperatures led Control Room personnel to manually trip the Main Turbine, which resulted in an anticipatory Reactor trip. Reactor Power was approximately 56 percent at the time of the Main Turbine trip. This event involved equipment failures on the secondary side only. Primary and secondary equipment and parameters responded as expected. There were no major problems encountered in placing the plant in Mode 3. Investigations revealed the Stator Cooling runback resulted from high Stator Cooling temperature. This condition was caused by the failure of the temperature controller for the Stator Cooling System proportioning valve. The cause of the reactor trip was inadequate installation of the temperature controller tubing. Corrective actions to prevent recurrence include replacement and analysis of the failed temperature controller. This event is considered of no significance with respect to the health and safety of the public.
2872000002 | Oconee 3 | 05/09/1999 | 02/23/2000 | ML00368694 | <strong>Missed Surveillance due to Incorrect Interpretation of Requirments</strong><br /><i>Abstract:&nbsp;</i>Improved Technical Specification (ITS) Surveillance Requirement (SR) 3.5.3.1 was added when Oconee converted to ITS on March 27, 1999. Position verification of the Oconee Unit 3 Decay Heat Removal (LPI) Heat Exchanger (HX) Bypass valves 3LP-92 and 3LP-93 were not included in the original scope of this surveillance based primarily on an assessment of common industry practices. Based on subsequent industry experience, Duke Energy conservatively decided to incorporate these valves into the SR verification program. The valves were added to the appropriate procedure and were found in their proper position when initially verified on November 3, 1999. An evaluation concluded on January 24, 2000, that these valves should have been included in the original scope of SR 3.5.3.1, so the initial position verification should have occurred on or before May 9, 1999. Unit 3 was operated in Mode 1 at 100% power during the period of March 27, 1999 to November 3, 1999, except for a 3-day reduction to Mode 3 in May, 1999. There are no equivalent valves on Unit 1 or 2. This event is considered to have no significance with respect to the health and safety of the public.
2872000003 | Oconee 3 | 04/16/2000 | 06/07/2000 | ML00372292 | <strong>Tech Spec Alarms Inoperable due to Operator Error and Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>At 2030 hours on 5-8-2000, Unit 3 was in Mode 5 preparing for restart from a refueling outage. Operators performed a review of computer alarm points required for Low Temperature Overpressure Protection (LTOP) during the restart. They discovered that two points required by Technical Specifications (TS) were in a "Delete From Alarm" (DALM) state such that they could not alarm. An investigation found that these points had been in DALM while they were required by TS from 4-13 to 4-16-2000 during shutdown for the refueling outage. However, LTOP compensatory measures had been in effect during two specific planned shutdown evolutions. Consequently, TS Allowed Action Times were only exceeded for less than 12 minutes at 2028 hours on 4-16-2000. The investigation also found that a TS surveillance had not detected the DALM condition. The root causes were that two Reactor Operators did not fully comply with the procedure and a surveillance procedure lacked sufficient clarity and detail. Corrective actions were to return the alarm points to service, revise the surveillance procedure, and counsel the operators. No operating conditions occurred to challenge the alarms. This event is considered to have no significance with respect to the health and safety of the public.
2872000004 | Oconee 3 | 01/03/1998 | 06/30/2000 | ML00373126 | <strong>Missed Leak Rate Test Due to Planning Process Weakness</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1998, Oconee Unit 3 was at 100% power. Fittings were replaced on impulse lines for four (4) reactor building pressure switches under a corrective work order (WO). The post maintenance testing (PMT) performed was visual checks for leaks "at normal system pressure." These fittings are part of the containment boundary and would require local leak rate tests (LLRTs) as PMT. On May 15, 2000, Unit 3 was in Mode 5 preparing to enter Mode 4 after refueling. During a review to ensure that surveillance requirements were satisfied prior to the mode change, the 1998 WO was reviewed and it was observed that LLRTs had not been performed on the fittings. LLRTs were satisfactorily completed prior to the mode change. The apparent cause of this event was a programmatic weakness in identifying the appropriate retest for some infrequently performed activities. A similar event occurred in December 1998, (see LER 287/98-01). Corrective actions from that event included enhancements to the PMT process. An additional corrective action will reassess current guidance to determine if additional enhancements are needed in light of this event. This event is considered to have no significance with respect to the health and safety of the public.
2892000001 | Three Mile Island 1 | 01/10/2000 | 02/09/2000 | ML00368410 | <strong>Automatic Start of Emergency Diesel Generator 1B Due to Failure of a Fault Pressure Relay on Auxiliary Transformer 1A</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2000 at approximately 11:45 a.m., the 1A Auxiliary Transformer (230 kV to 6900 V & 4160 V) tripped while supplying in-plant loads. The plant was operating at 100% power at the time of this spurious trip and remained at near full power during and following the event transient. Following the loss of the 1A auxiliary transformer, non-Class 1E loads transferred to the 1B Auxiliary Transformer and Class 1E loads transferred to the 1B emergency diesel generator which had automatically started in response to the event. The “A” Auxiliary Transformer tripped after water leaked into the transformer control cabinet enclosure and tracked onto the fault pressure seal-in electronic circuit board. The direct cause of the trip was a water induced short between two solder points. The water intrusion occurred as a result of a failure to weatherproof the screw penetrations on terminal strips directly above the circuit board after their installation in October 1999 during the 13R refueling outage. The failed fault pressure relay seal-in electronics board was replaced, the new board was mounted on standoffs, and the screw holes were sealed. The event was reported pursuant to 10 CFR 50.72(b)(2)(ii) at 2:02 p.m. on January 10, 2000.
2892000002 | Three Mile Island 1 | 06/28/2000 | 07/28/2000 | ML00373674 | <strong>Discovery of a Condition Outside the Fire Hazards Analysis Design Basis for the Alternate Shutdown Facility in Achieving Cold Shutdown in the Event of a Fire Which Forces Evacuation of the Control Room</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2000, AmerGen Energy LLC (AmerGen) discovered a condition, which was outside the plant design basis required by 10 CFR 50, Appendix R, III. L (1) and (3), as described in the Fire Hazards Analysis Report. Appendix R requires the capability to achieve COLD SHUTDOWN conditions (200°F) within 72 hours following the event of a fire which forces evacuation of the Control Room and control of the plant from Alternate Shutdown Facilities. Specifically, it has been determined that TMI Unit 1 lacks the defined capability, since such capability is not contained in plant procedures nor identified in operator training. The inability to meet the Appendix R requirement of the FHAR design basis description is reportable as an immediate notification to the NRC in accordance with 10 CFR 50.72 (b)(1)(ii)(b). A 30 day LER is required in accordance with 10 CFR 50.73(a)(2)(v) and (vii). Immediate compensatory measures were taken by way of written Operations Night Orders reviewed by all Shift Managers with each crew. The root cause has been determined to be: "Change Management Resources and Methods: Accuracy/Effectiveness of Change Not Verified or Validated," as applicable to implementation of Fire Protection commitments made in the 1980s. Significant process improvements have been implemented throughout the late 1990s that address the root cause of this event; therefore, no specific corrective actions to address the Root Cause of this event are required. Nonetheless, both short term and long term corrective actions have been initiated to bring the Unit into compliance with the requirements of 10 CFR 50, Appendix R, as described in the body of the report. This event did not involve any equipment failures or damage, nor were there any personal injuries as a result of this event. There were no adverse safety consequences resulting from this event, and the event did not affect the health and safety of the public.
2892000003 | Three Mile Island 1 | 08/05/2000 | 08/31/2000 | ML00374897 | <strong>Discovery of a Condition Outside the Updated FSAR (UFSAR) Design Basis for the Control Building Envelope (CBE) Due to Closed Volume Dampers</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2000, each train of the Control Building Emergency Ventilation System was tested to determine if each room in the Control Building Envelope (CBE) is maintained at a positive pressure with respect to adjacent areas outside the envelope. The test identified a negative pressure in Room 301, with respect to its adjacent area, which is in conflict with the design basis specified in the UFSAR. Closed volume dampers located in the supply diffusers in Room 301 caused the negative pressure. The date and reason that the volume dampers were closed could not be determined conclusively, however the most likely explanation is that the dampers were closed several years ago to improve pressure or temperature in other areas of the CBE. Sufficient makeup air is now provided to the room to provide positive pressure. Nearby rooms were checked to verify that air balance was not affected to the extent that negative pressure would occur in those rooms. Corrective actions will include restoration of the appropriate airflow from the diffusers in Room 301, posting of warning tags in this and similar diffuser locations in the Control Building Ventilation System, as well as the verification of the ventilation configuration in all safety related plant zones. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2892000004 | Three Mile Island 1 | 09/11/2000 | 04/11/2001 | ML01108047 | <strong>Discovery of a Condition Outside the Plant Design Basis for the Small Break Loss of Coolant Accident Analysis of Record for the Core Flood Tank Line Break Case</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2000, a condition potentially outside the design basis of the plant was discovered by AmerGen Energy Co. L.L.C. (AmerGen). Previously accepted analysis assumptions in the small break portion of the loss of coolant accident (LOCA) evaluation model (EM) related to the Core Flood Tank (CFT) line break were found to be non-conservative. This condition was reported by (Framatome ANP Inc.) in the Preliminary Safety Concern Report No. PSC 2-00. Analysis of the CFT line break with offsite power available yields an acceptable (peak clad temperature) PCT only when (1) reduced analysis margin for operator action is assumed, or (2) additional injection flow is provided to the reactor. Current abnormal transient procedure ATP 1210-10 requires tripping of the reactor coolant pumps (RCPs) as an immediate manual action upon loss of sub-cooling margin (LSCM); therefore, the procedural guidance remains unaffected by the analysis. AmerGen's final resolution will require updating TMI-1's response to NUREG-0737, II.K.3.5. This event was reported to the NRC by one-hour notification pursuant to 10 CFR 50.72(b)(1)(ii)(B). The root cause of this event, as determined by AmerGen, was the failure to consider that the CFT Line Break with offsite power available could be the most limiting event in the small break LOCA spectrum. Additionally, some analysis assumptions were not verified before application to the new EM. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public as the event is one of an error in analysis rather than an event related equipment failure, or an actual accident/operating transient.
2932000001 | Pilgrim | 07/29/1998 | 06/26/2000 | ML00372870 | <strong>Small Amount of Special Nuclear Material Misplaced and Located</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1998, four intermediate range monitors (IRMs) containing a small quantity of special nuclear material (SNM) were determined to be misplaced (i.e., not located in the expected location) in the Spent Fuel Pool (SFP), a material balance area. Later that day, one of the IRMs was found in the SFP, the material balance area of record for storage of that IRM. The second IRM was found in the SFP on August 18, 1998. The other two IRMs were subsequently located and returned to SFP by August 27, 1998. At all times the IRMs were handled or stored within Pilgrim Station radiological controls. This report was submitted voluntarily in accordance with NUREG-1022. The root cause was human error associated with a lack of attentiveness in the transfer of the IRMs into the SFP. Corrective action taken included installing permanent lighting in the SFP, removing unnecessary tie-offs from SFP railings, Nuclear Material Custodian review of work packages involving handling or movement of SNM, including this problem in the technician training program, changing the storage method of IRMs and similar detectors, and procedure revisions. The discovery occurred during 100 percent reactor power operation. The reactor mode selector switch was in the RUN position. The reactor vessel pressure was about 1032 psig with the reactor water temperature at the saturation temperature for that pressure. The IRMs posed no threat to public health and safety.
2932000002 | Pilgrim | 04/25/2000 | 05/25/2000 | ML00371945 | <strong>High Pressure Coolant Injection System Inoperable due to Power Inverter Failure</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2000, at 1545 hours, the High Pressure Coolant Injection (HPCI) system became inoperable when the inverter, which supplies power to the system's flow control circuitry, tripped but did not automatically reset as designed. The HPCI system was declared inoperable and a 14-day limiting condition for operation was entered. The inverter was replaced and the HPCI system was tested with satisfactory results and declared operable later on April 25, 2000. The results of the root cause analysis will be reported in a supplement to this report. The replaced inverter was sent to the designer (General Electric) for evaluation. This event occurred at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was about 1030 psig with the water temperature at the saturation temperature for that pressure. This event posed no threat to public health and safety.
2932000003 | Pilgrim | 12/11/2000 | 01/10/2001 | ML01017034 | <strong>125V DC Swing Bus Automatic Transfer Switch Degraded Performance</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2000, a monthly surveillance of the transfer switch 83-1 (Y10) SE relay was performed. The SE relay failed the surveillance by not operating immediately. The surveillance was then repeated several times without any discrepancies. Initially, the relay was considered operable based upon Engineering Evaluation 00-075. However, past surveillance results, as recent as December 11, 2000, indicated that the SE relay had been experiencing degraded performance for some time. Pilgrim declared LPCI inoperable on December 21, 2000 and a 7-day LCO was entered pending the replacement of the SE relay in Y10. The SE relay was replaced by a temporary modification on December 24, 2000, and the LCO was terminated. Prior to December 21, 2000, the LPCI system could have been inoperable due to the degraded performance of the SE relay. A root cause analysis will be completed and the results of the root cause analysis and approved corrective actions will be reported in a supplement to this report. This event occurred at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was about 1030 psig with the water temperature at the saturation temperature for that pressure. This event posed no threat to public health and safety.
2962000001 | Browns Ferry 3 | 04/15/2000 | 05/12/2000 | ML00371721 | <strong>Reactor Scram due to Feedwater Pump Control Oil System Problem</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2000, with Unit 3 in operation at 70% power, a low reactor water level scram occurred following a reactor feedpump 3C flow reduction. The feedpump 3C flow reduction was caused by a drop in control oil pressure due to a clogged control oil filter. Safety systems responded as expected. All control rods scrammed and fully inserted. The event evaluation determined that recent maintenance activities on feedpump 3C, which involved an atypically large number of feedpump trips and resets, had increased the particulate concentration in the control oil. This caused the filter to clog at a much faster rate than experienced in the past. Corrective actions include installing control oil filter differential pressure indicators to provide online oil pressure monitoring capability. Additional operational guidance has been added to the Alarm Response Procedures for feed pump control oil system problems. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an actuation of an engineered safety feature, including the reactor protection system.
2962000002 | Browns Ferry 3 | 04/16/2000 | 05/16/2000 | ML00371721 | <strong>Failure to Meet The Requirements Of Technical Specifications During Reactor Mode Switch Testing</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2000, at 1226 hours Central Daylight time (CDT), Unit 3 received an automatic reactor scram from 70 percent power. Following the scram, the reactor mode switch was placed in the shutdown position. On April 16, 2000, at 0835 hours CDT, plant operators commenced performance of surveillance Reactor Protection System Mode Switch in Shutdown Scram and Logic System Functional Test. This test requires that the mode switch be moved out of the shutdown position. On April 17, 2000, at approximately 1735 hours CDT, following satisfactory completion of mode switch testing, it was determined that 3-SR-3.3.1.2.4, Source Range Monitor (SRM) System Count Rate and Signal to Noise Ratio Check, was not performed as required. The SR was subsequently completed at approximately 2235 hours CDT. SRMs A, B, and D were found to be operable. Following completion of the SRM system test, it was determined that the mode switch testing had been conducted in violation of an action statement for inoperable SRMs which required the mode switch to be in the shutdown position. Therefore, TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(i)(B), as any operation or condition prohibited by the plants Technical Specifications. The root cause of this event was inadequate procedures, which resulted in misapplication of the requirements for operability of the SRMs. Corrective actions included revisions to appropriate procedures and personnel training.
2962000003 | Browns Ferry 3 | 04/21/2000 | 05/19/2000 | ML00372048 | <strong>Unplanned Diesel Generator Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2000 during testing of a switch for the 4KV shutdown board 3ED alternate feeder breaker from the 4KV bus tie board, the 3D diesel generator received an automatic start signal due to degraded voltage. At the time the start signal was received, the diesel generator and the 4 KV shutdown board were removed from service and inoperable for their Technical Specification functions. The automatic start was not preplanned, and the diesel generator started as a result of a valid initiation signal. The root cause of the event was a malfunction of a volt/ohm meter that was being used to check continuity on a compartment auxiliary switch associated with a breaker. There were no actual or potential safety consequences as a result of this event. This event did not adversely affect the safety of plant personnel or the public. This event is reportable per 10CFR 50.73 (a)(2)(iv) as any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF).
2962000004 | Browns Ferry 3 | 04/30/2000 | 05/30/2000 | ML00372089 | <strong>Missed Control Rod LCO</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2000, Operations personnel were performing Control Rod Drive (CRD) System Testing and Troubleshooting in conjunction with a surveillance requirement, CRD Coupling Integrity Check After Refueling or Maintenance. When control rod 42-55 was withdrawn, the full-in position indication remained illuminated. Subsequently, additional control rods were withdrawn prior to recognizing that all the required Limiting Condition for Operation actions for control rod 42-55, which had been considered inoperable, had not been completed. The root cause of this event was failure of the Senior Reactor Operator (utility, licensed), acting as Reactivity Manager, to ensure appropriate Technical Specifications Required Actions were taken upon recognition that the control rod was not functioning as expected. This was attributed to the mindset that the priority was to identify collectively all problems with CRDs and position indicators. Also, the pre-test brief did not adequately address the TS criteria and actions to be taken on any unexpected response. All Operations personnel will be briefed on management expectations for pre-evolution briefings including actions to take when unexpected responses occur. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2962000005 | Browns Ferry 3 | 05/24/2000 | 06/22/2000 | ML00372869 | <strong>Scram During Level Transmitter Calibration</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2000, with Unit 3 operating at 100 percent power, an invalid low reactor water level scram signal was generated while returning a feedwater level transmitter to service following scheduled calibration. The reactor scram caused reactor water level to decrease below the low level (level 3) and low-low level (level 2) setpoints. All emergency systems operated as expected in response to the scram, including insertion of all control rods. This event did not result in loss of the normal heat removal path as described in NEI 99-02, Revision 0, since the condenser remained available throughout the event and was used for decay heat removal. The root cause of this event was determined to be lack of specific proceduralized valving sequences for this level transmitter based on the current design and procedural guidance. The scram was the result of a pressure perturbation in the common variable sensing line shared with both channels of reactor protection system level transmitters. Corrective actions include revising the applicable procedure. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an actuation of an engineered safety feature, including the reactor protection system.
2962000006 | Browns Ferry 3 | 06/22/2000 | 07/24/2000 | ML00373668 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Setpoint Tolerance Due to Pilot Valve Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2000, TVA determined that 8 of the 13 Unit 3 main steam safety/relief valve (SRV) pilot cartridges removed during the Unit 3 Cycle 9 refueling outage bench tested outside the Technical Specifications (TS) setpoint tolerance of +/- 3 percent. Seven (7) of the SRV pilot cartridges tested above the TS setpoint and one (1) tested less that the setpoint. The Unit 3 SRV pilot cartridges were installed during the Cycle 8 refueling outage and were in service from September 1998 to April 2000. The cause for the SRV setpoint drift is attributed to SRV pilot disc/seat corrosion bonding at pilot disc/seat interface. Setpoint drift is a generic concern experienced by utilities using Target Rock Two-Stage SRVs (Model No. 7567F) in boiling water reactors. SRV pressure switches were previously installed during the Unit 3 Cycle 8 outage. The pressure switches ensure the initiation of any SRV should it fail to open at its setpoint; thus, minimizing the effects of SRV setpoint drift. This condition is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant's TS.
2962000007 | Browns Ferry 3 | 09/21/2000 | 10/20/2000 | ML00376414 | <strong>Inoperability of Two ECCS Injection/Spray Subsystems During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2000, at 1011 hours Central Daylight Time (CDT), with Unit 3 operating at 100 percent power, two Emergency Core Cooling System (ECCS) injection/spray subsystems became inoperable at the same time. This was preceded, at 0846 hours CDT, by entering a 7 day Limiting Condition for Operation (LCO) to perform initiation logic and injection valve opening pressure permissive logic functional testing on Residual Heat Removal (RHR) Loop I. At 1011 hours CDT a spurious fuse clearing caused Core Spray (CS) Loop I logic to become inoperable. In accordance with Technical Specification (TS) 3.5.1, ECCS-Operating, Action H, LCO 3.0.3 was entered immediately since two injection/spray subsystems were inoperable. By 1035 hours CDT, LCO 3.0.3 was exited after the fuse had been replaced and CS Loop I operability was restored. The cause of the fuse clearing was determined to be a short circuit condition. Possible causes were investigated, and even though there was no positive evidence, the most likely cause of the short circuit condition was the result of personnel performing the RHR logic testing in the panel. Following fuse replacement, all normally-energized components in the CS logic chain were inspected to verify their operability and to eliminate the possibility that a component failure resulted in the short circuit. This condition was evaluated and determined to have very little risk significance. Therefore, the safety of the plant, its personnel, and the public were not compromised by this event. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(i)(B) as any operation or condition prohibited by the plant's TS.
2982000001 | Cooper Station | 01/08/2000 | 02/07/2000 | ML00368639 | <strong>Turbine Bypass Valve Incorrect Setting Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During shutdown on January 8, 2000, Cooper Nuclear Station (CNS) determined turbine bypass valve (BPV) fast-open permissive setting was non-conservatively set at 200 megawatts electric (MWe) Gross, equivalent to 30-33 percent rated thermal power (RTP). It should have been less than 25 percent RTP per Technical Specifications (TS) and transient analysis. Cause was an inadequate correlation between turbine load and reactor thermal power during Digital Electro-Hydraulic (DEH) system design. Original design Incorrectly assumed a direct linear relationship between reactor power and generator output over full range of operation. Safety significance was negligible due to the low probability of transients occurring in the susceptible range, and an analysis that showed actual margin to thermal limits would maintain fuel Integrity. Immediate actions completed prior to plant startup Included calculation of the correct setting, a DEH modification that changed the setting to correspond to 23-24 percent RTP, and issuance of a standing order to avoid testing or operation that may divert steam from the main turbine at loads between 25 and 30 percent power, otherwise enter Limiting Condition for Operation 3.7.7. Other actions to be taken include revising procedures to Incorporate standing order provisions and ensure calibration and testing is captured in TS surveillance procedures. The DEH modification will be evaluated to try to add more margin to compensate for diverting main turbine steam between 25 and 30 percent.
2982000002 | Cooper Station | 01/11/2000 | 02/10/2000 | ML00368400 | <strong>Appendix R Safe Shutdown Analysis Vulnerability due to Potential Conductor to Conductor Hot Shorts</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2000, at 1752 hours Central Standard Time, Cooper Nuclear Station (CNS) discovered that a vulnerability to a fire induced hot short associated with the diesel fire pump control circuitry exists that could inhibit the ability of CNS to safely shutdown following a fire. During a postulated fire scenario in the Cable Spreading Room (CSR) fire area, the three sources of water to the service water (SW) pump gland seals would be lost due to Appendix R assumptions. The SW pumps are required to operate to supply the cooling water to the essential systems. A loss of the SW system [EIIS Code: BI) due to loss of the three sources of water for the gland seals would prevent the plant from achieving and maintaining safe shutdown following a postulated Appendix R fire. This condition, therefore, does not meet the 10CFR50, Appendix R, Section III.L requirements. The cause of this event is attributed to a human error. The risk significance evaluation determined this condition to be risk insignificant. Upon discovery of this condition, a continuous fire watch was instituted in the CSR as a compensatory measure. A plant modification will be installed to address the vulnerability of the diesel fire pump control circuitry to the fire induced hot short.
2982000003 | Cooper Station | 01/12/2000 | 02/14/2000 | ML00368553 | <strong>Failure to Meet Logic System Functional Testing (LSFT) Surveillance Requirement When Satisfied by Multiple Survelllance Procedures</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2000, during a review of the Technical Specification pre-startup checklist, it was identified that Surveillance Requirement (SR) 3.3.6.3.5 had not been fully satisfied since June 12, 1995. Specifically, a contact set of two SRV: Low-Low Set (EIIS:RV) arming logic relays (EIIS:RLY) had not been tested on an 18 month frequency to satisfy the Logic System Functional Test (LSFT) requirement of SR 3.3.6.3.5 (Table 3.3.6.3-1, Function 2). Procedure 6.SRV.303 was being performed to satisfy this requirement in lieu of Procedure 6.SRV.301. Both procedures indicated that their performance satisfied the surveillance requirement, but procedure 6.SRV.303 did not test one of the required relay contact sets. The plant was in a forced outage (shutdown) at the time of discovery. There was no actual safety significance for this event. Immediate actions were taken to perform the required test and successfully test the required contact set of both relays. Other contacts of the same relays have been routinely tested at the required frequency. Procedure 6.SRV.303 has been placed on administrative hold until corrected. Testing the required contact set was added to procedure 6.3.2.2 (now 6.SRV.301) as part of a 1994 LSFT project review. In 1994, the procedure change process lacked sufficient guidance to ensure procedure 6.2.2.2.7 (now 6.SRV.303) was also adequately revised. The current procedure change process includes explicit guidance for evaluating LSFT changes.
2982000004 | Cooper Station | 01/27/2000 | 02/28/2000 | ML00368824 | <strong>High System Flow During Restoration from Maintenance Causes Primary Containment Group 3 Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2000, at approximately 1 122 Central Standard Time, a Primary Containment Isolation System [EIIS:JM] Group 3 isolation occurred when placing the Reactor Water Cleanup (RWCU) [EIIS:CE] system in service following planned maintenance. The isolation occurred during performance of the initial pressurization of the RWCU system per the applicable Station Operating Procedure. The cause of this event is that the procedure, utilized for post maintenance filling and venting of the RWCU system does not provide a complete fill and vent of the system ensuring an event free pressurization of the system with the reactor at power. In previous maintenance of the RWCU system at power, the section of piping which was not completely filled and vented had not been drained. The Group 3 isolation was reset at approximately 1124, and RWCU system flow was restored at 1235. Corrective actions resulting from this event include revisions to the applicable station procedure to define the applicability of the FILL AND VENT section, and to add CAUTION STATEMENTS to alert the user of the potential for a Group 3 isolation. In addition, evaluations will be performed to determine the feasibility of alternate methods to accomplish system restoration following planned maintenance and changes to the existing system design.
2982000005 | Cooper Station | 02/26/2000 | 03/23/2000 | ML00369613 | <strong>Scaffold Construction Places Plant in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2000, at approximately 1420 Central Standard Time, Operations personnel discovered that scaffolding constructed to support upcoming Refueling Outage maintenance for the reactor building ventilation supply air operated Secondary Containment [EIIS:NG] isolation valve [EllS:ISV] would prevent the valve from fully closing. The valve was declared inoperable in accordance with Technical Specifications at 1436, the scaffolding obstruction was removed, and the valve was declared operable at 1603. Further investigation determined that the scaffolding had been constructed between February 16, 2000, and February 21, 2000. Therefore, it was concluded that the valve was not capable of performing its safety function for a period of time that exceeded Technical Specification Limiting Condition for Operation 3.6.4.2, Required Action Completion Time requirements. Corrective actions include: 1) A walkdown of other installed scaffolding to identify potential adverse interactions with plant equipment; 2) tailgate training to personnel responsible for erecting scaffolding to heighten awareness on the equipment interference issue; 3) notification to operations personnel addressing this issue to ensure this type of information is captured during initial walkdowns; 4) counseling of personnel involved; and 5) proposed revisions to the procedure.
2982000006 | Cooper Station | 03/05/2000 | 04/04/2000 | ML00370176 | <strong>Torus to Drywell Vacuum Breaker Misalignment Places Plant in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2000, at approximately 2200 Central Standard Time, primary containment was declared inoperable due to the failure to meet Technical Specification Surveillance Requirement 3.6.1.1.2, "Verify drywell to suppression chamber bypass leakage is equivalent to a hole less than 1.0 inch in diameter." The acceptance criteria for suppression chamber (torus) to drywell vacuum breaker valve leakage was not met in that the as-found value of 0.51 inches water per minute exceeded the operability value of less than or equal to 0.2 inches water per minute. Investigation revealed that the leakage was caused by improperly orienting the seals in 1997 and pallet/retaining ring misalignment during a previous refueling outage. This was due to inadequate work instructions caused by a failure to identify when the task is beyond the "skill of the craft" and determine when there is a need for additional component-specific guidance or criteria. Corrective Actions include performing necessary repairs using component - specific guidance obtained from the vendor, developing a detailed maintenance procedure, providing training on vacuum breaker maintenance, assessing where additional component-specific guidance/criteria is needed, and evaluating the test procedure to address the impacts different plant conditions may have on test results.
2982000007 | Cooper Station | 03/04/2000 | 05/10/2000 | ML00371517 | <strong>Failed Valve Motor Places Plant in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2000, while attempting to close Reactor Recirculation (RR) System [EIIS Code: AD] Loop A Discharge Valve a 250 VDC Bus 1A ground fault alarm occurred and the valve failed to fully close. This event was caused when brushes in the 250 VDC motor [EIIS Code: MO] failed to maintain adequate contact against the commutator which provides current to the armature winding. A Probabilistic Safety Analysis evaluation indicates this event is considered to be of minimal risk significance. Actions were taken to close the valve, replace the motor, and perform comprehensive testing prior to returning the valve to service. Results of plant and industry experience reviews indicate the failure mechanism was of an isolated nature. Additional testing of similar designed DC motors has been completed. Technical Specification (TS) Limiting Condition for Operation 3.5.1, Emergency Core Cooling Systems, requires this valve to be operable to ensure full Low Pressure Coolant Injection (LPCI) subsystem flow injection in the reactor via the recirculation jet pumps. If the valve is inoperable in the open position, the associated LPCI subsystem must be declared inoperable. This event is reportable because it has been conservatively determined that the valve was inoperable for a period of time longer than allowed by Technical Specifications. Actions taken on January 14, 2000 were not sufficient to resolve the cause for ground fault alarms that provided precursor indication of the March 4, 2000 valve failure.
2982000008 | Cooper Station | 04/01/2000 | 08/28/2000 | ML00374739 | <strong>Non-conservative Drywell Temperature Profile Places Plant in a Condition Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2000, during a review of Equipment Qualification Data Packages (EQDPs), it was discovered that Buchanan Model 0241 terminal blocks installed in the drywell had been qualified to a temperature profile which did not bound the worst case postulated environmental conditions. Subsequent inspections of Environmentally Qualified (EQ) components in the drywell revealed noncompliance with the EQDPs. Based on the results of these inspections, a review of the Cooper Nuclear Station (CNS) EQ Program was conducted. This review identified specific splice and terminal block nonconformances which were determined to place the plant in a condition outside the design basis. In addition, the review identified weaknesses in the implementation of the EQ Program at CNS. The individual root causes of these nonconformances were determined to be (1) a technical error made in August 1985, (2) a deficiency in the overall process of translating EQ information to the field, and (3) EQ programmatic weaknesses in that existing EQ Program standards and expectations were not effectively communicated, implemented, and enforced. Immediate corrective actions were taken to ensure field installation reflects EQ Program requirements and to correct technical deficiencies associated with the EQ Program. Additional corrective actions are being taken to resolve the weaknesses that resulted in the EQ Program deficiencies noted during the EQ Program review.
2982000009 | Cooper Station | 06/28/2000 | 07/27/2000 | ML00373661 | <strong>Failure to Recognize Entry Condition for Limiting Condition for Operation 3.4.5 Condition D Causes Plant Operation in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2000, it was noted that the Drywell Floor Drain Sump Flow Transmitter (EIIS Code: IJ) had been made inoperable for the performance of a routine surveillance at the same time that the Drywell Atmospheric Monitoring System was inoperable. Contrary to Technical Specification (TS) 3.4.5 Condition D, "All required leakage detection systems inoperable," which requires immediate entry into LCO 3.0.3, TS 3.4.5 had been entered separately for each system. All Drywell leakage monitoring systems were inoperable for 69 minutes while a scheduled routine loop channel calibration was completed. Drywell Atmospheric Monitoring System, RMV-RR-2 (EIIS Code: FQT), was inoperable during this period due to sample pump failure. With both instrumentation systems inoperable, this results in entering the LCO 3.4.5 Condition D and immediate entry into LCO 3.0.3, Action shall be initiated within 1 hour. The cause was determined to be procedural inadequacy. Operations management has provided procedural intent clarification to all Control Room personnel. Station documents will be revised to detail the requirement to complete an independent verification of LCO entries prior to beginning work.
2982000010 | Cooper Station | 09/15/2000 | 11/15/2000 | ML00377104 | <strong>Engineered Safety Feature Actuation - Control Room Emergency Filter System</strong><br /><i>Abstract:&nbsp;</i>On September 15, 2000, at 0446 Central Daylight Time (CDT), the plant was in Mode 1 at approximately 100% steady state power, when the control room received an annunciator for Control Building Gas Activity High and the Control Room Emergency Filter System (CREFS) automatically actuated. At 0450 CDT, the radiation alarm cleared and at 0459 CDT, the CREFS was restored to standby status. The root cause evaluation concluded the event was not a human performance issue, was not caused by natural phenomenon or man-made radioactivity, but was most likely the result of a malfunction of the Control Building Gaseous Radiation Monitor. Immediate corrective action was to confirm if a temperature inversion was present during the event. A followup action was completed by the Radiological Protection department which confirmed it was unlikely that the alarm and CREFS actuation occurred as a result of natural or man-made radioactivity. Long term corrective action is to replace the ratemeter for the gaseous channel of the Control Building Radiation Monitor. This event is being reported voluntarily based on the lack of a definitive cause. It appears the actuation was caused by a malfunction of the Control Building Radiation monitor. Other credible causes have been eliminated. Given that this CREFS actuation was most likely caused by an equipment malfunction it would be an invalid Engineered Safety Feature (ESF) actuation and not reportable.
2982000011 | Cooper Station | 10/14/2000 | 11/13/2000 | ML00376988 | <strong>Automatic Reactor Scram Due to Actuation of Generator to Transformer Differential Phase C Relay</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2000 at approximately 3:24 Central Daylight Time (CDT), a phase 'C' differential current trip (87/GT relay) [EIIS:87] resulted in a Main Generator [EIIS:GEN] trip and automatic reactor scram. All rods inserted. Reactor Pressure Vessel (RPV) pressure initially rose to 1068 psig which is below the lowest Safety Relief Valve setpoint of 1080 psig and then was controlled by the Digital Electro-Hydraulic control system. RPV level initially lowered due to shrink and caused Group 2 (Primary Containment), Group 3 (Reactor Water Cleanup), and Group 6 (Secondary Containment) isolations. The Alternate Rod Insertion (ARI) signal initiated on low RPV level; however, level recovered prior to ARI tripping the Reactor Recirculation Motor Generator field breakers. Reactor Feed Pump turbines tripped on high RPV water level swell following the scram. The RPV swell dampened the RPV pressure transient. A normal cooldown was commenced and the plant was placed in Mode 4, Cold Shutdown, at 17:48 CDT on October 14, 2000. The cause of the event was vibration induced insulation wear in a current transformer (CT) [EIIS:XCTI lead wire [EIIS:CBL2] associated with the main power transformer [EIIS:XFMR] which resulted in a short to ground. The worn insulation has been repaired, and a spare CT in the transformer has been used to replace the CT with the damaged leads. The CT with the damaged leads has been spared in place.
2982000012 | Cooper Station | 12/18/2000 | 01/17/2001 | ML01023017 | <strong>Human Error Results in Automatic Engineered Safety Features Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2000, at 14:36 Central Standard Time (CST), with the plant operating at 100% power, a personnel error was made in performing the Division I undervoltage logic surveillance procedure relay calibration that resulted in the load shedding of the Division I 4160V Critical Bus 1F. Service Water (SW) pump C tripped causing low pressure isolation of the non-critical header, Control Rod Drive pump A tripped, and several Motor Control Centers were lost resulting in the trip of Reactor Recirculation Motor Generator A, Reactor Water Cleanup pump B, Off-Gas Dilution Fan A, Reactor Building Exhaust Fan 1 A, and the loss of Elevated Release Point radiation monitoring. The plant stabilized at approximately 65% power in single-loop operation. Reactor Pressure Vessel level and pressure responded as expected. A detailed review of the electrical system response indicated that the trip circuits for Division I Emergency Core Cooling System pumps were energized by the load shedding event, thus preventing their operation for a period of approximately four minutes. In addition, during recovery from the event SW Pump B started, tripped, and would not re-start on operator demand. At 14:40 CST on December 18, 2000, SW header pressure was returned to normal. The plant was restored to two loop operation at 21:25 CST on December 18, 2000, and 100 percent power was achieved at 08:00 CST on December 19, 2000. This event is attributed to a management failure to reinforce standards and expectations which resulted in inadequate supervision, and the resultant personnel error, during the performance of a Division I undervoltage surveillance procedure.
3012000001 | Point Beach 2 | 01/03/2000 | 02/02/2000 | ML00368165 | <strong>Replacement of Charging Pump Control Power Fuse Outside Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 2, 2000, while evaluating Appendix R safe shutdown analyses and fire scenarios, Wisconsin Electric engineering personnel identified that the PBNP Unit 2 2P-2C charging pump may require replacement of a control circuit fuse for the pump to be available following a postulated fire event in either of Fire Zones 142 or 187. Replacement of a fuse or fuses, per guidance from the NRC, is considered a maintenance activity. Maintenance activities are not permitted to meet the Appendix R hot safe shutdown performance goals. Corrective actions will be taken to maintain the availability of the 2P-2C charging pump independent of the status of the control power fuse. Due to the availability of alternate means for RCS inventory control, the safety significance of this event was minimal. This event was reported in accordance with 10 CFR 50.72 as a condition outside the Appendix R design basis for the plant.
3012000002 | Point Beach 2 | 04/13/2000 | 05/11/2000 | ML00369426 | <strong>Redundant Channels of Steam Generator Pressure Indication and Source Range Nuclear Instrumentation Not Routed Independent of Common Fire Zone</strong><br /><i>Abstract:&nbsp;</i>While conducting a revalidation and reverification project for the Point Beach Nuclear Plant 10 CFR 50 Appendix R fire protection programs, the licensee discovered that several cables necessary to provide plant parameters required to be monitored for an Appendix R safe shutdown locations were not routed independent of fire zones containing cables for redundant equipment. Specifically we discovered on April 13, 2000 that the power supply for steam generator (SG) pressure transmitter 2PT-469 would not be available for a postulated fire event in the north section of the 26' Primary Auxiliary Building. Cabling for the redundant SG pressure transducer, 2PT-483, already has its cable routed in this same fire zone. We also determined on April 17, 2000, that the redundant power supply to Source Range Monitor 2N-32 may not be available for a fire in the 8' PAB. Alternate Source Range Monitors 2N-31 and 2N-40 would already be considered unavailable because their signal cables are in the same fire zones. In accordance with plant procedures a twice per shift fire round has been established for these fire zones pending correction of the cable routing. These events were reported to the NRC in accordance with 10 CFR 50.72 as conditions outside the Appendix R design basis for the plant.
3012000003 | Point Beach 2 | 11/01/2000 | 11/30/2000 | ML00377511 | <strong>Failure to Comply with LCO Action Statement to Start Redundant Standby Emergency Power Supply</strong><br /><i>Abstract:&nbsp;</i>On November 1 during a review of the station log, the licensee discovered that contrary to the action statement of Technical Specification (TS) LCO 15.3.7.B.l.g, the standby emergency power to Point Beach Nuclear Plant Unit 2 Train "A" safeguards bus had been out of service for a period of more than 24 hours without starting of the redundant standby emergency power supply within 24 hours before or after entering the LCO. This is a condition prohibited by the TS and reportable pursuant to 10 CFR 50.73. The apparent cause of the condition was incomplete tracking of the LCO conditions. A complete evaluation of the root cause for this event is in progress. Unit 2 was shutdown and defueled at the time of this event.
3012000004 | Point Beach 2 | 11/05/2000 | 12/05/2000 | ML00377637 | <strong>Unplanned Emergency Safety Features Actuation During Safeguards Bus Restoration</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2000, an inadvertent Engineered Safety Features (ESF) actuation resulted in the start of the G03 Emergency Diesel Generator (EDG). This actuation occurred while restoring power to 4.16 KV busses 2A04 and 2A06 following a bus maintenance outage. The signal was generated when the fuses for the under voltage relays were installed. With the 2A06 bus still deenergized, the under voltage relays energized and generated a fast start signal to the G03 EDG. G03 started but did not sequence on to, and energize, the 2A06 bus since its output breaker to that bus was in pull out in accordance with the bus maintenance tag out. At the time of this event Point Beach Nuclear Plant Unit 2 was shutdown and defueled for a scheduled refueling and maintenance outage. The EDG was secured in accordance with plant procedures. An evaluation has been initiated to establish the contributing factors and root cause for this event. Based on the plant conditions at the time and the proper functioning of equipment following the ESF actuation, the safety significance of this event was minimal.
3012000005 | Point Beach 2 | 11/10/2000 | 12/11/2000 | ML00377797 | <strong>Unplanned Emergency Safety Features Actuation During Calibration and Testing of Safeguards Bus Relays</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2000, an inadvertent Engineered Safety Features (ESF) actuation resulted in the start of the G03 and G04 Emergency Diesel Generators (EDGs). This actuation occurred during the calibration and testing of the protective relays associated with the PBNP Unit 2 Train "B" 4160 V safeguards bus. The process was being conducted in accordance with approved plant procedures. During this calibration and testing an under voltage signal was created at a procedural step which checks the continuity across two test points. This signal energized an auxiliary relay which caused the normal bus 2A06 supply breaker to open and resulted in the fast start of the G03 and G04 EDGs. The loss of voltage sensing circuitry then sequenced the G04 EDG onto, and re-energized, the 2A06 bus. At the time of this event Point Beach Nuclear Plant Unit 2 was shutdown and defueled for a scheduled refueling and maintenance outage. After appropriate response to these conditions, the EDGs were secured. The immediate cause of this event was an incorrectly written step in the calibration and testing procedure. A thorough evaluation has been initiated to establish the contributing factors and root cause for this event. Based on the plant conditions at the time of this actuation and the proper functioning of equipment, we have determined that the safety significance of this event was minimal.
3012000006 | Point Beach 2 | 12/14/2000 | 01/12/2001 | ML01022044 | <strong>Failed Fuse in Intermediate Range Nuclear Detector Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2000, Point Beach Nuclear Plant (PBNP) Unit 2 tripped as a result of a failed control power fuse in the intermediate range (IR) nuclear instrumentation Channel 2N35. The trip occurred with the reactor critical at approximately 10E4 counts per second in the source range, well below the actual IR trip set point. PBNP Unit 2 was in the process of starting up following a refueling shutdown and had reached criticality at 0543 at normal temperature and pressure. There were no other failures or system operating abnormalities resulting from this trip. The NRC was notified pursuant to 10 CFR 50.72(b)(2)(i) at 0740. In accordance with plant procedures a post trip review and incident examination were completed. The control power and instrument power fuses in both IR instrument circuits were replaced. Following a review of the event by senior plant management, permission was granted for a unit restart at 1624. Unit 2 achieved criticality at 2112 on December 14 and commenced low power physics testing in accordance with the normal startup procedures. No further problems were experienced with the nuclear instrumentation during the escalation to normal power operations.
3012000007 | Point Beach 2 | 12/20/2000 | 01/18/2001 | ML01029004 | <strong>Fault Associated with "C" Phase Main Step-up Transformer Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2000, the Point Beach Nuclear Plant (PBNP) Unit 2 experienced a turbine generator and reactor trip while raising power following completion of the unit's refueling outage. The trip occurred with reactor power at approximately 63% power. The cause of the trip was initially identified as a ground overcurrent relay actuation on the main step up transformer. Subsequent investigation determined the trip was due to the 2-51N neutral overcurrent relay detecting a phase current imbalance; however, no evidence of an actual overcurrent condition was identified. Further investigation determined that the trip resulted from the opening of the current transformer circuit for the "C" phase input to the 2-51N relay. The open circuit occurred due to the failure of a manufacturer's crimp connection. The circuit was repaired and the connections in the current transformer for the other phases were checked and found to be satisfactory. The unit was returned to service on December 21st.
3022000001 | Crystal River 3 | 01/12/2000 | 02/09/2000 | ML00368505 | <strong>Surveillance Requirement Was Not Performed Within The Required Time Frame of Improved Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2000, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 99.9 percent RATED THERMAL POWER. FPC personnel discovered that a Surveillance Requirement (SR) was not performed within the required time frame of Improved Technical Specifications (ITS). ITS 3.6.3, "Containment Isolation Valves (CIVs)," provides the Conditions and Required Actions necessary to maintain the CIVs OPERABLE. ITS SR 3.6.3.3 requires verification every 31 days that each containment isolation manual valve and blind flange located outside containment is closed. Makeup and Purification Valve MUV-520 became a CIV as a result of a plant modification installed during Refuel 11 but was not added to the CIV surveillance procedure until January 11, 2000. The cause was a weakness in the technical review process. MUV-520 was verified to be in the correct position. There was no decrease in protection of the health and safety of the public.
3022000002 | Crystal River 3 | 03/03/1994 | 07/13/2000 | ML00373455 | <strong>Inadequate Identification of Components Required for Operability Results in Exceeding a Limiting Condition for Operation</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2000, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 99.9 percent RATED THERMAL POWER. Prior to performing a maintenance activity, FPC personnel recognized that certain electrical buses required to be operable by Improved Technical Specifications (ITS) were not clearly identified. The activity would have removed a breaker from service that provides one source of emergency electrical power to the pressurizer heaters. FPC conducted an evaluation to determine if a Limiting Condition for Operation (LCO) of ITS had previously been exceeded. The evaluation determined that an ITS LCO had been exceeded one time in 1994. Various tools used by the work control process to identify equipment required for operability did not clearly reflect the relationship between the electrical buses and the pressurizer heater emergency power supply. There was no reduction in protection of the public health and safety. Corrective actions include a revision to the ITS Bases, a change to the CR-3 Configuration Management System and a revision to an operating procedure.
3022000003 | Crystal River 3 | 09/11/2000 | 10/10/2000 | ML00376155 | <strong>Reactor Coolant Pump Trip Criteria May Cause Peak Fuel Clad Temperature to Exceed 10 CFR 50.46 Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2000, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) at 0 percent Rated Thermal Power. CR-3 was informed by Framatome Technologies Inc. (FTI), that the preliminary results of a revised Small Break Loss of Coolant Accident (SBLOCA) analysis for a Core Flood (CF) line break indicated that the peak fuel clad temperature could exceed the 10 CFR 50.46 (b) limit of 2200 degrees Fahrenheit if the Reactor Coolant Pumps (RCPs) are not assumed to be tripped until two minutes following loss of subcooling margin. Current CR-3 licensing/design basis analyses assumes that with offsite power available, RCPs are shut down no sooner than two minutes after a loss of subcooling margin. On September 15, 2000 at 1038, FPC notified the NRC of this event as a design basis issue under 10 CFR 50.72(b)(1)(ii)(B) and 10 CFR 50.46(a)(3)(ii). The causes were failure to include an analysis of a CF line break with offsite power available in the validation of the two-minute RCP trip criteria for Babcock and Wilcox (B&W) plants, and the use of non-conservative modeling techniques in the current approved CF line break analysis. Corrective actions included determining an acceptable RCP trip window based on the revised analysis and ensuring that current operator response to a loss of subcooling margin supports the new RCP trip criteria.
3052000002 | Kewaunee | 03/10/2000 | 04/10/2000 | ML00370343 | <strong>Failure to Perform Second Level Review Results in Train B of the Shield Building Ventilation System Being Incorrectly Returned to Service</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2000, while the plant was operating at full power, a second level review of surveillance data determined that train B of the shield building ventilation (SBV) system had incorrectly been returned to service. Train B could not be verified operable using the surveillance procedure test data last performed on July 27, 1999. Using the recorded data, train B of the SBV system was outside the test acceptance criteria (+ l- 10 percent) for fan flow by 2.5 percent. SBV train B was declared out of service at 1620 hours Central Standard Time (CST) and the 7-day Limiting Conditions for Operation (LCO) of Technical Specification 3.6.b.1 was entered. On March 11, 2000, SBV train B was retested and determined operable. Two problems were identified concerning this event: 1) failure to identify unacceptable test results on July 27, 1999, and 2) a delay in performing a required technical review of the test results. Causes include: procedure design problems, administrative directive problems, attention to details issues, testing methodology changes, and communication challenges. Corrective actions taken or in progress include: retesting SBV train B to verify it is operable and procedure reviews and revisions.
3052000003 | Kewaunee | 03/16/2000 | 04/17/2000 | ML00370628 | <strong>Unplanned ESF Actuation Caused By Radiation Monitor R-15 Detector Failing</strong><br /><i>Abstract:&nbsp;</i>The following event is reportable as an unplanned actuation of steam generator blowdown isolation valves which are engineered safety features (ESF) equipment. On March 16, 2000, while the plant was operating at full power, radiation monitor system channel R-15, "Condenser Air Ejector Gas Radiation Monitor" failed. As a result, inadvertent blowdown isolation occurred. R-1 5 failed due to a failed radiation detector. The detector was replaced and tested. The monitor was returned to service within two hours of failure. The consequence of the failure was that steam generator blowdown and blowdown sample isolation actuated as designed. During the short term of the monitor's unavailability the normal continuous steam generator tube leakage monitoring capability was inhibited. Compensatory actions were initiated in accordance with requirements. Since the design function of the system was fulfilled and compensatory actions were initiated, there were minimal safety consequences to this event. The blowdown isolation (motor operated) valves were not adversely challenged by the additional operation caused by the failure.
3052000004 | Kewaunee | 04/15/2000 | 07/31/2000 | ML00373851 | <strong>Unplanned ESF Actuation Caused by Radiation Monitor R-15 Detector Failing - Repeat Occcurrence</strong><br /><i>Abstract:&nbsp;</i>The following event is reportable as an unplanned actuation of steam generator blowdown isolation valves which are engineered safety features (ESF) equipment. On April 15, 2000, while the plant was operating at full power, radiation monitor system channel R- 15, "Condenser Air Ejector Gas Radiation Monitor," failed. As a result, inadvertent blowdown isolation occurred. R-15 failed due to a failed radiation detector. The detector was replaced and tested. The monitor was returned to service when the detector was replaced and tested on April 16, 2000 at 1430. The consequence of the failure was that steam generator blowdown and blowdown sample isolation actuated as designed. During the monitor's unavailability the normal continuous steam generator tube leakage monitoring capability was inhibited. Compensatory actions were initiated in accordance with requirements. Since the design function of the system was fulfilled and compensatory actions were initiated, there were minimal safety consequences to this event. The blowdown isolation (motor operated) valves were not adversely challenged by the additional operation caused by the failure. This event is a repeat occurrence. A previous detector failure occurred on March 16, 2000. The cause of these failures has not been conclusively determined. Initial evaluations of the failures suspected moisture intrusion as the cause. However, manufacturer testing could not isolate the failure mechanism to moisture intrusion. Therefore, the definitive cause remains unknown.
3052000005 | Kewaunee | 04/22/2000 | 05/22/2000 | ML00371880 | <strong>Main Steam Isolation Valve Exceeds Technical Specification Acceptance Criteria and Design Basis for Valve Closure Time</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2000, while the plant was in intermediate shutdown condition, during the performance of surveillance procedure (SP) 55-167-8, "Hot/Intermediate Shutdown Valve Tests - IST", the as found closing time for the main steam isolation valve for the B steam generator (MS-1B) exceeded the test acceptance criteria. Technical Specification 4.7 requires that the valve close within 5 seconds. The valve actually closed in 6 seconds. The valve was immediately declared out of service. A root cause investigation was initiated to determine the cause of the event. The cause is believed to be excess friction associated with aging of the valve packing. The valve packing was replaced with an improved design. The valve was tested to ensure it met all requirements prior to being returned to service.
3052000007 | Kewaunee | 05/19/2000 | 06/19/2000 | ML00372518 | <strong>Alternate Service Water Supply Piping Obstructed</strong><br /><i>Abstract:&nbsp;</i>During a routine inspection on May 19, 2000 at about 1400, while the plant was in the refueling shutdown mode, contracted divers determined that a 30 inch diameter circulating water recirculation line was obstructed with silt and debris. The line was plugged for most of the 200 foot length up to the valve that isolates the forebay. Approximately 40 feet of pipe downstream of the valve was partially blocked. The line had been designated as an alternate supply to the service water pumps should the main intake system become completely plugged. The safety consequences of this event are minimal because complete failure of the intake system is not credible. The line was cleaned and returned to service at 1600 on May 31, 2000, before returning the plant to service following the 2000 refueling outage. A design change that will prevent debris from entering the recirculation line has been installed. The procedure that governs underwater inspections will be modified to require periodic inspection of the line.
3052000008 | Kewaunee | 05/26/2000 | 06/20/2000 | ML00372719 | <strong>High Head Recirculation Outside Design Basis of Plant</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2000, while the plant was in the Refueling Shutdown condition, it was determined that the as-built condition of the plant did not meet its current design basis. The condition involves the Residual Heat Removal (RHR) Heat Exchanger to Safety Injection (SI) pump motor operated valves. These valves receive an open-permissive signal from the RHR system on low pressure. This signal circuitry was found not to meet the requirements of the Institute of Electrical and Electronic Engineers (IEEE)-279 standard. The pressure signal prevents the valves from opening when RHR pressure is greater than the design pressure of the SI suction piping. This permissive was designed to prevent the valves from being inadvertently opened when RHR is in its cooldown line up. Its post-accident function is to allow the valves to open. Original documentation from plant construction and discussions with the Nuclear Steam Supply System vendor, indicated that the original design did not require meeting IEEE-279. However, the Kewaunee Updated Safety Analysis Report does not appear to reflect this design philosophy. As this event dates from original construction the cause is unknown. To ensure these valves can be operated from the control room a jumper has been installed to remove the open-permissive from the valve control circuitry. With the jumper installed the motor operated valve circuitry meets IEEE-279 standards.
3052000009 | Kewaunee | 06/06/2000 | 07/06/2000 | ML00372675 | <strong>Manual Reactor Trip Initiated - Failure of Reactor Coolant Pump Temperature Indication Required Action to Trip the Pump</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2000, while operating at 37% power, a manual trip was initiated in response to an abnormal high temperature indication of the A Reactor Coolant Pump (RXCP). At the time of the trip, the plant was in a chemistry hold at reduced power following a recently completed refueling outage. The indicated increased temperature was on the RXCP bearing water outlet temperature that would be indicative of a RXCP radial bearing related problem. Plant procedures prohibit operating the RXCP with bearing temperature indication in excess of 225 degrees F. Subsequent to the Operators noting temperature indication exceeding 225 degrees, the reactor and affected pump were tripped. The cause of the increased temperature indication was a failed resistance temperature detector (RTD). The plant response to the trip was normal. All systems operated as designed.
3052000010 | Kewaunee | 06/12/2000 | 11/27/2000 | ML00377390 | <strong>Testing and Evaluation Determine the Service Water System has a Lower Design Basis Temperature Than Previously Believed</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2000, during the review of service water system testing performed during the 2000 refueling outage, it was determined that both emergency diesel generators were out of service for a short period of time in 1991 due to elevated lake temperatures. Additionally, both trains of local area fan coil units located on the fan floor and mezzanine levels in the auxiliary building were out of service at separate times. The fan coil units maintain post accident environmental conditions to ensure safety related equipment located in these areas remain operable. Prior to commencing power operation after refueling, compensatory actions were taken to ensure operability of all equipment. After the outage, design changes were implemented to increase the SW flow to safety related components. Additional design changes are being evaluated to further increase the flow to the emergency diesel generators. These modifications are scheduled for the 2001 refueling outage.
3052000011 | Kewaunee | 06/13/2000 | 07/14/2000 | ML00373486 | <strong>Target Band Alarm Setpoint Not Updated with the Current Target Delta Flux Difference Value as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2000 at 1942 hours, the Nuclear Control Operator (NCO) received TLA-3, "Start Outside Target Band." The target flux difference was set at 1.0%. The indicated axial flux difference was 2.3%. Investigations determined that the current target flux difference was not entered into the Plant Process Computer as required. This is a violation of TS 3.10.b.13. Subsequent to the Operators receiving the alarm, the target flux difference was entered into the plant process computer and the alarm cleared at 2001. A review of the axial flux difference history verified that the plant was operated within the target flux difference. Procedural changes will be made to prevent reoccurrence of this event in the future. Due to administrative oversight, this LER is being submitted one day late.
3052000012 | Kewaunee | 06/14/2000 | 07/14/2000 | ML00373595 | <strong>Failure to Expand Scope to Test Additional Relief Valves as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2000, it was discovered that, during a recent refueling outage, additional relief valves were not tested as required by Technical Specifications when one relief valve setpoint could not be determined. The valve tested may have had seat leakage greater than the capacity of the test pump that prevented determining an exact setpoint, rather than a low setpoint. This condition should have been conservatively treated as a test failure and additional valves tested. The cause of the event was determined to be inadequate guidance in plant procedures on actions to take if seat leakage prevented exact determination of a relief valve setpoint. Corrective actions taken included testing of additional relief valves. Personnel involved in relief valve testing have been advised of the actions to take when seat leakage prevents determination of an exact setpoint. Additionally, this guidance will be added to plant procedures governing relief valve testing. The process for reviewing KAP problem reports will be reviewed and revised as necessary.
3052000013 | Kewaunee | 07/21/2000 | 08/18/2000 | ML00374372 | <strong>Condition Prohibited by Technical Specifications Inadvertently Entered Due to Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2000, while operating at full power, contrary to Kewaunee Nuclear Power Plant's (KNPPs) Technical Specifications (TS), a containment penetration line had an automatic containment isolation valve declared out-of-service (OOS) without the penetration being isolated by a closed valve. The condition lasted for 23 minutes. BT-32B, "Steam Generator "B" Blowdown Sample Isolation Valve," was declared OOS when air was isolated to the valve to repair an air leak on the air regulator. Following rebuild and bench setting of the air regulator in the Instrument and Control (I&C) shop, the regulator was re-installed in BT-3213's air supply line. The air isolation valve was then opened and BT-32B was opened from the control room, to allow the I&C technician to check for leaks. At this time the Control Room Supervisor questioned if BT-32B required a timing test to return the valve to service. This question caused the operating crew to identify that BT-32B Containment Isolation function and TS requirements were not satisfied due to the redundant penetration isolation valve, BT-31B, being open. At no time, during the 23 minutes, was the physical ability to isolate containment compromised. This was confirmed by the satisfactory performance test of BT-32B.
3052000014 | Kewaunee | 08/21/2000 | 01/22/2001 | ML01030019 | <strong>All Three Auxiliary Feedwater Pumps Declared Inoperable Due to the Potential to Plug Their Suction Strainers</strong><br /><i>Abstract:&nbsp;</i>At 1415 hours on August 21, 2000, with the plant at 96 percent power, all three auxiliary feedwater (AFW) pumps were declared inoperable. The pumps were declared inoperable when it was determined that the strainers in the suction of each pump had smaller diameter holes (1/16 inch versus 1/8 inch) than previously believed. As a result, there was no analysis of record that could conclusively demonstrate the strainers would not become blocked during a design basis accident. Upon declaring the AFW pumps inoperable, actions were taken as required by Technical Specification (TS) 3.4.b.4. The TS states to initiate immediate action to return at least one train to service and suspend all limiting conditions of operation (LCO) requiring mode changes until one AFW pump is returned to operable status. The pumps were subsequently returned to operable status at 2047 hours on August 21, 2249 hours on August 21 and 1209 hours on August 22 after the strainers were removed from the suction of each pump. Additional analyses using both probabilistic and deterministic methods were performed. The deterministic analysis demonstrates the pumps were operable in the as found condition. The probabilistic analysis, which did not credit the deterministic analysis, determined that the event would have had a minor impact on safety.
3052000015 | Kewaunee | 11/09/2000 | 03/12/2001 | ML01079045 | <strong>Service Water Traveling Water Screens Not Sealed As Per USAR</strong><br /><i>Abstract:&nbsp;</i>During a review of the Kewaunee Nuclear Power Plant (KNPP) Updated Safety Analysis Report (USAR) a question arose concerning the status of access covers on the intake traveling water screens. The USAR states that these covers are to be gasketed, sealed, and strengthened to accommodate high water levels that may develop due to a seiche on Lake Michigan. Contrary to the statement in the USAR, the covers have historically been left open to allow visual inspection of the screens during operator rounds. Open access covers also provide an additional means of flushing the screens of excessive aquatic debris during unusual lake conditions. Current lake low-level conditions preclude the onset of the design basis seiche and its potential consequences. The traveling water screens have been closed.
3052000016 | Kewaunee | 12/19/2000 | 01/18/2001 | ML01025006 | <strong>Inadvertent ESF Actuation Caused by Unanticipated Temperature Control Switch Response During Testing</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2000, while the plant was operating at 96% power, an inadvertent steam generator blowdown isolation occurred as a result of personnel manually actuating a temperature control circuit that provides a closure signal to steam generator blowdown isolation. The consequence of this event was that steam generator blowdown actuated as designed. Operating personnel recovered from the event, with blowdown being reestablished approximately 45 minutes subsequent to the event. The motor-operated steam generator blowdown isolation valves were not adversely challenged by the additional operation. The event was caused by the failure of personnel to recognize the inter-relationship of the temperature control circuit for the steam generator blowdown tank outlet (a non-ESF) system and the closure circuit for the steam generator blowdown isolation valves (an ESF system).
3062000001 | Prairie Island 2 | 04/28/2000 | 05/30/2000 | ML00368506 | <strong>(Blank)</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2000, Unit 2 was undergoing an orderly shutdown in preparation for refueling. During the course of the shutdown, at approximately 2240, the unit tripped from 22% power. The reactor trip was initiated by a turbine trip which was initiated by a Hi Hi Level signal from 23B Feedwater Heater. The unit remains shutdown for refueling.
3062000002 | Prairie Island 2, Prairie Island 1 | 05/02/2000 | 03/13/2001 | ML01082017 | <strong>Discovery that PORV/Block Valve Cable in Containment Does Not meet Appendix R Separation Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2000, while Unit 2 was in a refueling outage, plant personnel inspected cable routing in Unit 2 containment for Appendix R separation requirements and determined that cables associated with the Unit 2 PORV's and block valves were not separated by twenty feet. Prairie Island has exemptions from Appendix R Section III.G.2 for both Unit 1 and Unit 2 containments (Fire Areas 01 and 71). Those exemptions are based in part on the separation of redundant shutdown equipment, with the exception of Pressurizer Level Channel Cabling, by a minimum of 20 ft. The Pressurizer PORVs and opposite train PORV Block Valves are considered redundant equipment. The lack of twenty feet of separation between affected cables constitutes a condition outside the exemption bases. The affected Unit 2 PORV cables in containment have been rerouted in individual conduits such that the lack of separation is no longer a concern. In December of 2000, the Unit 1 containment was inspected to determine whether a similar condition existed for Unit 1. A series of inspections revealed that Unit 1 PORV/Block Valve Cables either met the separation requirements of the existing exemption (greater than 20 feet) or met the requirements of 10 CFR 50, Appendix R, Section III.G.2 (separated by a radiant energy shield).
3112000001 | Salem 2, Salem 1 | 09/30/2000 | 10/26/2000 | ML00376454 | <strong>Historical Non-Compliance with Technical Specification 3.3.3.9 Action 36</strong><br /><i>Abstract:&nbsp;</i>This licensee event report is being submitted to report a historical non-compliance with Technical Specification 3.3.3.9 Table 3.3-13 action 36, which became evident on September 30, 2000. On September 30, 2000, at approximately 2041 the Unit 2 control room operators received an alarm indicating that the Radiation Monitoring System {IL} 2R41A-D channels had failed. This failure caused the 2R45 skid to bypass the continuous iodine and particulate monitors. The R41s and R45s detectors, which serve as back up to each other, monitor the effluent through the plant vent. Immediately following the overhead alarm, the control room operators entered Technical Specification 3.3.3.9, and requested Chemistry department to set up the alternate sampling of particulate and iodine in accordance with Action 36. However, because the alternate skid is not permanently installed literal compliance with Action 36 is not possible. The apparent cause of this event is an inappropriate interpretation of the Technical Specification. A contributing factor was the inability to meet the action requirements whenever a failure of these detectors occurred. Amendment 234 and 215 issued on August 24, 2000, relocated the radiological effluents of Technical Specifications to the Off-Site Dose Calculation manual, therefore this report is being submitted due to a historical non-compliance with Technical Specification 3.3.3.9 Table 3.3-13 action 36 in accordance with 10 CFR 50.73(a)(2)(I)(B).
3112000002 | Salem 2, Salem 1 | 10/27/2000 | 11/22/2000 | ML00377353 | <strong>Engineered Safety Feature Actuation due to 2R11A "Containment Particulate Monitor" Alarm</strong><br /><i>Abstract:&nbsp;</i>On Friday, October 27, 2000, at 2228 hours, the containment particulate radiation monitor, 2R11A, spiked into alarm resulting in a containment ventilation isolation signal being generated. This ventilation isolation function is identified as an Engineered Safety Feature (ESF) actuation in the Salem Technical Specifications. The 2R11A monitor settled at approximately 3830 cpm following the spike. Earlier on the same day, at 1955 hours, licensed control room operators (ROs) commenced draining the refueling cavity in accordance with normal operating procedures. At 2026 hours, Operations personnel performed a containment pressure relief evolution. At 2150 hours, PSEG Maintenance personnel defeated the airlock's interlock and opened both 100-foot elevation containment doors to begin containment demobilization. At 2228 hours, the containment particulate radiation monitor, 2R11A, spiked into alarm due to radon gas daughter products. All containment ventilation isolation valves {IK/V} were already closed prior to the isolation signal generation; therefore, no equipment repositioned as a result of this isolation signal. The root cause was attributed to naturally occurring radon gas and its daughter products. Corrective actions taken were: (1) Air samples taken by health physics personnel were analyzed and showed concentrations less than 1% of the DAC values in 10CFR20, (2) The R11A setpoint was changed in accordance with procedures to account for the higher background and avoid unnecessary isolation signals (3) Management was notified of the event and a notification was issued in accordance with the corrective action program, and (4) The circumstances surrounding this event will be included in the lessons learned planned for future outages.
3112000003 | Salem 2 | 11/07/2000 | 12/07/2000 | ML00377764 | <strong>Engineered Safety Feature - Feedwater Isolation Due to High Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>At approximately 1504 hours on 7 November 2000, with Salem Unit 2 operating in Mode 4 (Hot Shutdown), Main Feedwater Regulating Valves 21 BF 19 {SJ/FCV} automatically closed on a 21 Steam Generator High-High level. The cause of this event was human error. The Steam Generators were being fed using the Condensate pumps. Controls technicians, working on the position indication for the 21 BF19 (Main Feedwater Regulating Valve to the 21 Steam Generator) {SJ/FCV} to repair erratic indication, stroked the valve full open. The operators did not adequately anticipate the impact of the work being performed or anticipate the erratic levels that would accompany the 21 BF19 work. The level in 21 Steam Generator rose to the P-14 (2/3rd Level on 1 out of 4 Steam Generators) setpoint and produced an Engineered Safety Feature Actuation, a Feedwater Isolation signal The operators promptly restored feedwater level control to steam generators. Other corrective actions included evaluation of work control during plant transition periods, the addition of licensed personnel to the control room to control the activities in progress until the end of the outage, and a re-emphasis on the requirement for face-to face briefings. Additionally, personnel involved will be held accountable in accordance with PSE&G procedures and policies. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv), required for "any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF)..." A four-hour notification was made to the NRC in accordance with 10CFR 50.72 (b)(2)(ii) on November 7, 2000 at 1655.
3112000004 | Salem 2, Salem 1 | 10/31/2000 | 11/30/2000 | ML00377514 | <strong>Main Steam Safety Valves Failed Lift Set Test</strong><br /><i>Abstract:&nbsp;</i>During the 2R11 refueling outage at Salem Unit 2, three Main Steam Safety Valves {SB/RV} (MSSV) were tested in accordance with the requirements of Technical Specifications and the ASME Operational and Maintenance Code. Valves 23MS11, 21MS13 and 23MS14 were tested during 2R11 outage. Two out of the three valves tested (23MS11 and 23MS14) failed to meet the Technical Specification required acceptance criteria, as established in Technical Specification Table 3.7-4. The apparent cause of the valves failing to meet the acceptance criteria was attributed to excessive seat leakage, as indicated by steam cutting of valve disc and nozzle. From a process point of view, there were no processes or program deviations that contributed to this event. A set point variance of greater than ± 1.0% but less than ± 3.0% is not unusual for these valves, as described in AEOD/S92-20. Corrective actions taken were; (1) The valves were disassembled, refurbished, adjusted and retested to ensure compliance with the ± 1 % Technical Specification, and (2) A license change request to increase the set point tolerance from ± 1 % to ± 3% was submitted to the NRC. This event is reportable in accordance with 10 CFR 50.73 (a) (2) (i).
3132000001 | Arkansas 1 | 01/14/2000 | 02/10/2000 | ML01040016 | <strong>Reactor Building Atmosphere Sample Not Taken As Required By Technical Specifications Due to Personnel Errors During Review and Approval of Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications (TS) allow the unit to continue power operation for 72 hours with both the Reactor Building (RB) atmosphere particulate and gaseous detectors inoperable providing two other means of reactor coolant leak detection remain operable and RB atmosphere samples are taken and analyzed shiftly. Otherwise, the unit must be in Hot Shutdown within the following six hours. At approximately 1030 on January 13, 2000, both leak detection radiation monitors were taken out of service to facilitate maintenance on their associated RB isolation valves. The 72 hour TS action statement was entered at that time. At approximately 0830 on January 14, it was identified that the required sample was not taken on the previous shift. A six hour shutdown action statement was entered at that time and actions were initiated to take the sample. At 0918, acceptable sample results were verified and the six hour action was exited. The root cause of this event was personnel errors by several individuals involved in the planning and approval of the maintenance activity. Lessons learned training will be developed and provided to appropriate personnel.
3132000003 | Arkansas 1 | 02/15/2000 | 03/16/2000 | ML00369384 | <strong>Reactor Coolant System (RCS) Hot Leg Level Instrument Nozzle Welds Cracked Due To Primary Water Stress Corrosion Cracking Resulting From the Use of Alloy 182 Weld Metal Exposed to RCS Water In A Highly Restrained Weld Joint That Was Not Stress Relieved</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2000, with the plant in cold shutdown conditions for a scheduled outage, a weld in a Reactor Coolant System (RCS) hot leg level instrumentation nozzle was found to have been leaking as indicated by boron buildup. Cracked welds were later found on the other six hot leg level instrumentation nozzles of similar design. One weld crack was subsurface. The root cause was determined to have been using Alloy 182 weld metal exposed to RCS water in a highly restrained weld joint that had not been stress relieved, resulting in Primary Water Stress Corrosion Cracking (PWSCC). Six of the nozzles were replaced in accordance with Section XI of the ASME Code using an improved design that included different materials with more resistance to PWSCC. The seventh nozzle was repaired using alternate criteria approved by the NRC because a Section XI repair would have required core offload. This nozzle will receive a Section XI repair during the next refueling outage. The particular nozzle design was used only in these seven locations and is not believed to be installed in any other B&W design operating unit.
3132000004 | Arkansas 1 | 03/14/2000 | 04/10/2000 | ML00370412 | <strong>Manual Reactor Trip Initiated In Response To the Rapid Closure of the Main Turbine Steam Supply Valves Which Resulted From Failure of the Electro-Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2000, at approximately 0005, the reactor was manually tripped following a component failure in the main turbine electro-hydraulic control system. During plant startup, the main turbine steam supply valve position limits were set at 100 percent to allow full travel of the valves. When reactor power reached 82 percent during power escalation, the turbine operator identified an alarm on the plant computer alarm display indicating that the valve position limit was slightly greater than 100 percent. The operator attempted to clear the alarm by depressing the "lower" pushbutton on the panel. The third time the pushbutton was depressed, the valve position limit decreased and continued to rapidly decrease after the button was released. The decreasing valve position limit caused the main turbine steam supply valves to rapidly close and the main steam safety valves began lifting. The reactor was manually tripped and all control rods inserted into the core well within their expected drop times. The cause of this event was determined to be a stuck contact on the valve position limit pushbutton. The switch was replaced prior to plant startup.
3132000005 | Arkansas 1 | 10/18/2000 | 11/16/2000 | ML00377043 | <strong>Deficient Reactor Protection System Surveillance Tests Due to Inadequate Procedure Verification Resulted in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Deficient monthly surveillances have been performed on the 4 channels of the Reactor Protection System (RPS). The 18 month channel calibration tests were performed in accordance with their schedules with the understanding that the required elements of the monthly tests were encompassed by the calibration tests. Consequently, the monthly tests were not performed during months when the calibration was scheduled. However, it was subsequently discovered that one parameter, required to be tested during the monthly surveillance, was not included in the 18 month calibration test. The affected parameter is the Reactor Coolant System total flow amplifier scaled output voltage. The output signal of this amplifier is used by a function generator to establish the plateau of the Power/Imbalance/Flow curve, which becomes the setpoint for the Power/Imbalance/Flow RPS trip bistable. When it was determined that this omission resulted in deficient surveillances affecting each RPS channel, the applicable steps of the channel monthly tests were performed and test results demonstrated that all channels were operable.
3152000001 | Cook 1, Cook 2 | 09/02/1999 | 02/21/2000 | ML00368706 | <strong>Stress Loads for the Ice Condenser Basket Assembly Greater Than Allowed by Safety Analysis Report</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1999, during re-evaluation of the structural design analyses for the ice condenser ice baskets, Westinghouse determined that the vertical dynamic load factor of 1.0 used in the original design analyses for the ice baskets was non-conservative. Specifically, the analyses did not consider dynamic load forces that could be imparted on the slotted clevis bracket configuration during a Design Basis Accident (DBA) and Design Basis Earthquake (DBE) event. Upon completion of the evaluation of this condition for other ice condenser plants, Westinghouse issued a Nuclear Safety Advisory Letter (NSAL) on January 17, 2000, regarding the clevis bracket gap effects. Subsequent review of the NSAL by Donald C. Cook Nuclear Plant determined this condition to be reportable to the NRC on January 24, 2000. As previously reported in LERs 315/98-007 and 015, individual occurrences of gross ice basket weights of less than 800 pounds had been found in both Unit 1 and Unit 2. Because these ice baskets were resident in the ice condenser during periods when the Units were operating, this LER is being submitted in accordance with 10CFR50.73(a)(2)(ii)(B) for a condition outside the design basis of the plant. The apparent cause is lack of design documentation control by Westinghouse during the initial design of the ice condenser system and components. A non-conforming condition evaluation will be performed to document the acceptability of the change in the design requirements in accordance with plant procedures. No physical hardware changes are required as a result of this condition because the Technical Specification minimum ice weight per basket is greater than the minimum ice weight required by the Westinghouse analysis. The potential safety significance of this condition is bounded by the analysis described in LER 315/98-006-02. The reanalysis performed by Westinghouse concluded that the ice condenser structure would prevent any basket from exiting the ice condenser. Therefore, the load effect on the slotted ice basket bottom brackets has minimal safety significance.
3152000004 | Cook 1, Cook 2 | 07/19/1999 | 07/03/2000 | ML00373183 | <strong>Circuit Design Could Result in Failure of Emergency Diesel Generators to Load Properly after Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>During the Expanded System Readiness Reviews a concern arose that a "sneak circuit" existed in the Safety Injection circuitry which could prevent proper sequencing of the Essential Service Water pumps, the Non-Essential Service Water pumps, the Component Cooling Water pumps and the Motor Driven Auxiliary Feedwater pumps onto the Emergency Diesel Generators (EDGs) during a Loss of Coolant Accident with a concurrent Loss of Offsite Power (LOCA/LOOP) event. The existence and effect of the circuit were confirmed, and on June 5, 2000, this condition was determined to be reportable in accordance with 10CFR50.73(a)(2)(ii) as a condition outside the design bases. The apparent cause was an original design error. A design change has been installed for Unit 2 to correct the condition, and a similar design change will be installed on Unit 1 prior to Mode 4. Multiple scenarios involving the affected pumps were evaluated as well as the procedures for coping with the effects of the sneak circuit. It was found that the procedures and operator response times were adequate to preclude damage to operating equipment necessary to mitigate the vent. Based on the evaluated scenarios and the proceduralized guidance provided for coping with the effects of the sneak circuit, the safety significance of this condition is low.
3152000005 | Cook 1, Cook 2 | 06/04/2000 | 06/30/2000 | ML00373122 | <strong>Control of Auxiliary Building Crane Main Load Block Over Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1999, the Spent Fuel Pool (SFP) ventilation system was declared operable, but degraded because the system cannot react quickly enough to a high radiation signal to close the charcoal filter bypass dampers and prevent radioactive gases from a fuel handling accident from being released to atmosphere without passing through the charcoal filters. To maintain the system in an operable status, compensatory actions were required. These actions included placing the SFP ventilation system in the charcoal filter mode of operation prior to movement of fuel or any load within or over the SFP, and procedure changes. On June 4, 2000, during performance of crane interlock testing, the east Auxiliary Building crane was operated over the SFP without the SFP ventilation system in the charcoal filter mode of operation as required by the compensatory actions, and without the main load block de-energized as required by Technical Specification (TS) 3.9.12 footnote. On June 5, 2000, this condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by TS. The apparent cause for this event is the failure to establish adequate administrative controls for the degraded condition, with a contributing cause of an operator knowledge weakness. The crane interlock verification procedure will be revised, training will be provided to Operations personnel relative to the requirements of TS 3.9.12, and a license amendment request will be submitted to delete the TS 3.9.12 footnote. Because the Auxiliary Building cranes are now single failure proof, under the provisions of NUREG-0612 the load blocks need not be considered heavy loads. Based on the single failure proof design of the cranes, the "+" footnote is no longer appropriate, and the event had no safety significance.
3152000006 | Cook 1, Cook 2 | 08/04/2000 | 08/31/2000 | ML00374810 | <strong>Emergency Diesel Fuel Oil Technical Specification Surveillances Not Met Verbatim</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2000, during the revision process for a Technical Specification (TS) surveillance procedure, it was discovered that procedure 12 THP 6020.CHM.307, "Emergency Diesel Fuel Oil," did not meet the verbatim surveillance requirement of TS 4.8.1.1.2.c.3. The surveillance requires verification, "... in accordance with the test specified in ASTM D4176-82 and prior to adding new fuel to the storage tanks, that the sample has a clear and bright appearance with proper color." Contrary to the TS and the American Society for Testing and Materials (ASTM) standard, proper color has not been verified or documented during the performance of the clear and bright test for new fuel oil shipments since the TS surveillance was implemented in 1989. During the investigation of the condition, five other fuel oil TS surveillance procedures were determined to not meet TS requirements - kinematic viscosity, flash point, specific gravity, clear and bright, and particulate contamination. All five procedures lacked sufficient detail to ensure verbatim compliance with the appropriate ASTM, as required by TS. This LER is submitted in accordance with 10CFR50.73(a)(2)(i)(B) for a condition prohibited by the plant's TS. The cause of the missed surveillance was the failure to recognize the phrase "with proper color" as a surveillance criteria. Caution tags were placed on the fill standpipes for both Emergency Diesel Generator (EDG) fuel oil tanks. Results from a sampling of fuel oil analyses were reviewed to verify acceptable results, including offsite analyses for water and sediment. New fuel oil will be purchased clear, not colored or dyed, and the ASTM color will be determined for all new fuel shipments prior to fuel offloading. The diesel fuel oil analysis procedures have been reviewed and are being revised as appropriate to ensure verbatim compliance with TS. Technician qualification for fuel oil color analysis is in progress. Based on the performance of other field and laboratory analyses and Technician training and qualification programs that ensure high quality fuel is used for the EDGs, there is minimal safety significance to the failure to verify proper color of new diesel fuel oil or provide explicitly detailed procedures for performance of ASTM requirements.
3152000007 | Cook 1, Cook 2 | 09/19/2000 | 08/02/2001 | ML01220000 | <strong>ESF Ventilation System Inoperable due to Technical Specification Surveillance Test Methodology</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to include the cause and corrective actions and replace the original submitted LER in its entirety. On September 19, 2000, Donald C. Cook Nuclear Plant (CNP) completed an Operating Experience (OE) evaluation regarding INPO OE11256, "Control Room Emergency Filtration Inoperable due to Testing Method." The OE identified an event at Shearon Harris Nuclear Power Plant where both control room emergency filtration system units were inoperable due to the system's test configuration during performance of Technical Specification (TS) surveillance testing. CNP evaluated OE11256 to determine applicability to CNP plant ventilation systems. During the performance of ESF ventilation system surveillance testing at CNP, the system is aligned such that the fan for the filter unit being tested is not running, and the fan in the other train is running. The evaluation determined that opening the access door to the train being tested made the tested unit inoperable because it would be unable to meet the TS 4.7.6.1 surveillance requirement of 25,000 cubic feet per minute (cfm), plus or minus 10 percent if auto-started by an accident signal. Additionally, opening the filter unit access door allowed air to flow backward through the filter unit inlet damper to the common inlet suction to the operating train. This backflow could potentially reduce the amount of airflow drawn from the Emergency Core Cooling System pump room cubicles. As such, on September 19, 2000, this condition was determined to be reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) for a condition prohibited by TS, since both ESF ventilation trains were rendered inoperable during operating modes which require the system to be operable. The cause of the TS noncompliance was determined to be an inadequate testing procedure. This procedural inadequacy was discovered during the review of industry operating experience. Corrective actions included the installation of informational placards on the applicable ventilation doors and the placement of the applicable testing procedures on administrative hold until the identified procedural inadequacies can be corrected. The implementation of these corrective actions has been reviewed and deemed adequate to prevent recurrence.
3152000008 | Cook 1, Cook 2 | 03/16/2000 | 12/07/2001 | ML02022028 | <strong>Failure to Test Essential Service Water Valves in Accordance with Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide additional information concerning the event analysis, cause, and corrective actions and replaces the original submittal in its entirety. On March 16, 2000, during development of the new Essential Service Water (ESW) flow balance procedure, it was discovered that the Component Cooling Water (CCW) Heat Exchanger Essential Service Water (ESW) outlet valves for Unit 1 (1-WMO-733 and 1-WMO-737) and Unit 2 (2-WMO-734 and 2WMO-738) had not been fully tested in accordance with Technical Specification 3/4.7.4.1.b. Specifically, on a refueling outage basis the valves are required to be demonstrated to actuate to their correct position on a Safety Injection (SI) signal. However, the previous procedure only required the valves to be demonstrated to reposition to their intermediate position from the fully open position. Since these valves may be closed during normal operation when the opposite CCW train is the only train in service, repositioning to the intermediate position from the fully closed position on a SI signal is a design basis scenario and should have also been demonstrated. This condition was reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause of the event was weaknesses within the Surveillance Test Program, involving program management, programmatic infrastructure, and training. As corrective actions, the ESW valves were tested to demonstrate the valves would reposition to the intermediate position from the fully open and fully closed positions on March 31, 2000 for Unit 2 and on November 01, 2000 for Unit 1. The procedures for testing these ESW valves have been revised. The Surveillance Test Program was restructured to ensure that adequate training, procedures, and management oversight are in place. Testing performed subsequent to discovery of this condition with the valves in the fully closed and fully open position has demonstrated little difference in flow values; therefore, it is reasonable to assume that in the past the valves would have performed their safety function per the design basis as required. Thus, this condition is considered to be of minimal safety significance.
3152000009 | Cook 1 | 12/06/2000 | 01/08/2001 | ML01017035 | <strong>Failure to Perform Technical Specification Valve Position Surveillance on Leak-off Valves</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2000, during performance of the procedure used to satisfy Technical Specifications (TS) containment integrity surveillance requirement (SR) 4.6.1.1.a.1, it was determined that a missed TS surveillance had previously occurred. It was determined that, prior to the 1997 extended shutdown, the surveillance procedure failed to include position verification for two Emergency Core Cooling System test connection isolation valves. The two residual heat removal (RHR) system test connection valves, 1-RH-110E and 1-RH-11 OW, are the stem leak-off isolation valves for the normally closed containment recirculation sump isolation valves. These test connection valves provide a boundary to maintain containment integrity during operating modes 1 (Operation) through 4 (Hot Shutdown), and are required to be verified in their correct positions at least once every thirty-one days. Failure to verify the position of these test connection valves since their installation is a violation of TS. As such, this LER is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS. The apparent cause for this condition was the failure to adequately control plant modifications and supporting documentation. The Unit 2 containment recirculation sump isolation valves were verified to not have leak-off valves. The extent of condition is limited to this containment penetration due to its unique configuration. This condition is not applicable to Unit 2. The leak-off valves had been verified to be in their correct positions prior to each plant startup; access to these leak-off valves is very limited during normal plant operation; the leak-off piping is capped; and, the valve enclosure tanks are closed and monitored for leakage. Based on the above, the safety significance of the condition is minimal.
3162000001 | Cook 2 | 01/17/2000 | 03/16/2000 | ML01081021 | <strong>Retraction - Through-Liner Hole Discovered In Containment Liner</strong><br /><i>Abstract:&nbsp;</i>This LER is being retracted. In November 1999, during the Coatings Assessment and Inservice Program inspection of the Unit 2 containment liner, an indication was found that appeared to be a weld repair of the liner plate. Surface preparation to allow for further inspection dislodged repair material exposing an approximately 3/16-inch circular through-liner hole. An LER was submitted in accordance with 10 CFR 50.73(a)(2)(ii)(A). The liner hole appears to have resulted from an inadequate repair of a hole drilled through the liner in error during plant construction. A design change has restored the containment structure to its original configuration. The containment liner plate and concrete repair along with the necessary examination, inspection, and testing was completed in accordance with the ASME Section XI Repair / Replacement Plan. The Containment Inspection Program and the Safety Related Coatings Program will contribute to the identification of conditions on the liner that are adverse to quality. The most recent 10 CFR 50 Appendix J Integrated Leakage Rate Testing (ILRT) performed on the Unit 2 containment was conducted in May 1992. The test results of the as-found condition of the liner showed the as-found leakage to be well within the maximum allowable leak rate and the performance of the liner as tested is judged to reasonably reflect its performance during accident conditions. Therefore, it is concluded that no serious degradation of the principal safety barrier occurred as was originally reported and this LER is being retracted.
3162000002 | Cook 2 | 05/14/1997 | 06/21/2000 | ML00372719 | <strong>Operation Outside Design Bases and Entry Into Technical Specification (TS) 3.0.3 Due to Non-Conservative TS</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1997, with Unit 2 in Mode 3 and Unit 1 defueled, the Unit I Essential Service Water (ESW) system was removed from service to facilitate Unit 1 forebay cleaning without the ESW crosstie valves to Unit 2 being closed. On May 1, 2000, a new Administrative Technical Requirement (ATR) was approved for implementation in accordance with the guidance provided In NRC Administrative Letter 98-10, "Dispositioning of Technical Specifications That Are Insufficient to Assure Plant Safety". The ATR for ESW requires that the ESW crosstie valves be closed when a pump is inoperable. On May 24, 2000, it was determined that operation In the past, such as from March 14 to 17,1997 with the ESW crosstie valve open when the associated pump was inoperable, constituted a condition outside the design basis, reportable in accordance with 10CFR50.73(a)(2)(ii). Additionally, applying the criteria of the current ATR, the event was also reportable in accordance with 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specification (TS). The apparent cause was failure to recognize that ESW TS 3.7.4.1 was potentially non-conservative and the system could be operated outside the design bases while still meeting the requirements of the TS. The ESW ATR was implemented on May 1, 2000. A TS amendment request for TS 3.7.4.1 will be submitted by August 18, 2000. A review was performed of other shared systems to determine if adequate control is maintained over the associated system crosstie valves. No additional issues were identified. A familiarization session on NRC Administrative Letter 98-10 was conducted with the Regulatory Compliance personnel normally involved with the evaluation of potentially reportable conditions. Due to the low probability for scenarios involving maximum flow conditions, in conjunction with the existing procedural guidance and training received by the operators, this event had minimal safety significance.
3162000003 | Cook 2, Cook 1 | 05/29/2000 | 11/20/2000 | ML05103002 | <strong>Containment Internal Concrete Structures Do Not Meet Design Load Margins</strong><br /><i>Abstract:&nbsp;</i>This LER is revised as marked in the margin to incorporate Unit 1 containment structure information. On May 29, 2000, during an evaluation of concrete structures inside the Donald C. Cook Nuclear Plant (CNP) Unit 2 containment, it was determined that a condition outside the design basis of the plant existed in that some containment internal concrete sub-compartment structural elements, specifically walls and floors, did not meet the design pressure load factor margin of 1.5 as described in the CNP Updated Final Safety Analysis Report (UFSAR). A revised Nuclear Steam Supply System (NSSS) vendor transient mass distribution (TMD) containment analysis prompted new calculations which showed that a number of containment internal concrete structural elements did not meet the 1.5 design pressure load factor margin. On October 26, 2000, during an extent-of-condition review prompted by the Unit 2 condition described above, completed calculations identified that similar conditions existed on the Unit 1 containment structural elements. This LER is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) for a condition outside the design basis of the plant. The apparent cause for this event was the failure to adequately control design basis calculations and supporting documentation. For Units 1 and 2, critical calculations were reconstituted or evaluations performed for the subject concrete structural elements, and some structural grout repairs made on one Unit 2 wall with noted degradation. Presentations were made to the U.S. Nuclear Regulatory Commission (NRC) to provide information related to the design and licensing basis for the concrete structures and discrepancies found. A plan and schedule for long-term corrective and preventive actions for both units have been developed. The results of the Unit 1 and 2 calculations and evaluations show that the internal containment concrete structural elements were capable of withstanding the revised TMD accident pressures without loss of function. There is minimal safety significance associated with the failure to maintain a 1.5 design pressure load factor margin for internal containment structures.
3162000004 | Cook 2, Cook 1 | 06/08/2000 | 07/07/2000 | ML00373183 | <strong>Partial Loss of Offsite Power Results in Start of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2000, at 0931 hours EDT, with Unit I defueled and Unit 2 in Mode 4, reserve power to the Train A busses on both units was lost during switching operations in the 34.5 kV switchyard. The Unit 1 and Unit 2 CD Emergency Diesel Generators (EDGs) started and picked up load as expected. The Spent Fuel Pool (SFP) Cooling pump in service tripped, but was restored at 0953 hours following a 1 degree Fahrenheit (F) temperature rise in the SFP. All 4 Reactor Coolant Pumps (RCPs) on Unit 2 tripped as designed. While on natural circulation, the Reactor Coolant System cooled down approximately 20 degrees F due to low decay heat and increased auxiliary feedwater flow. Two RCPs were returned to service by 1159 hours. This LER is submitted in accordance with 10CFR50.73(a)(2)(iv), any event that resulted in an automatic actuation of any Engineered Safety Feature, and in accordance with 10CFR50.73(a)(2)(i)(B), for failure to complete the surveillance requirement of Technical Specification 3.8.1.1 .a, "AC Power Sources", within 1 hour. The root cause of this event was personnel error. The Interface Agreement between Donald C. Cook Nuclear Plant and American Electric Power's Western Transmission Region will be revised to require concurrent verification of switching operations in the switchyard by operations department personnel. The missed surveillance was due to failure of the responsible crew members to complete an evaluation of the event for its impact on compliance with TS requirements in a timely manner due to the plant transient response. Training will be developed for the operators to reinforce the expectations regarding 1-hour TS action statement requirements. The safety significance of this event was evaluated and found to be minimal. All expected actions for a loss of power to a bus occurred, including load shed, start of the EDGs on both units and sequencing of loads onto the EDGs.
3162000005 | Cook 2 | 06/15/2000 | 07/14/2000 | ML00373122 | <strong>Auxiliary Feedwater Pump Inoperable Due to Incorrect Flow Retention Valve Settings</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2000, during evaluation of the test data from the surveillance used to verify operability of all three auxiliary feedwater pumps (AFPs), it was determined that the as-left settings for the mid-position limit switches of the turbine driven AFP (TDAFP) steam generator supply valves were not adequate to protect the pump from damage due to run-out flow conditions. Technical Specification (TS) 3.7.1.2, “Auxiliary Feedwater System,” allows verification of operability of the TDAFP following entry into Mode 3. The TDAFP had been surveillance tested and was determined to be operable within the 72-hour allowed outage time limit of the TS 3.7.1.2 action statement Upon further review, it was determined that the valves were set incorrectly, and the TDAFP was again declared inoperable, 88 hours after Unit 2 entered Mode 3. During post-event review, it was conservatively decided that the TDAFP had been inoperable for a total of more than 98 hours, which was greater than the 72 hours allowed by the action statement of TS 3.7.1.2. This LER is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. The apparent cause for this condition was inadequate documentation. Immediate corrective actions were to declare the TDAFP inoperable, verify both motor driven AFPs (MDAFPs) operable, and reset the TDAFP steam generator supply valve intermediate limit switches. The Technical Data book was verified to provide the correct reference points for other valves. A sampling was performed of past limit switch adjustments to verify correct performance. A reference point for the valve limit switch settings will be included in the Technical Data book for all the AFP steam generator supply valves. At the time of the event, there was negligible decay heat present in Unit 2, well within the heat removal capability of a single MDAFP. The safety significance of the condition of incorrect settings of the TDAFP steam generator supply valve limit switches is therefore minimal.
3162000006 | Cook 2 | 06/28/2000 | 07/24/2000 | ML00374810 | <strong>Failure to Comply with Requirements of Technical Specifications for Nuclear Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2000, low power physics testing commenced for Unit 2. Testing was performed using the special test exception of Technical Specification (TS) 3.10.3, "Physics Tests," which requires that thermal power not exceed 5 percent of rated thermal power (RTP), and the intermediate range and power range neutron flux low trip setpoints are set at less than or equal to 25 percent RTP. The trip setpoints were adjusted to 25 percent. On June 26, 2000, it was determined that the setpoints for all intermediate and power range instruments had been greater than 25 percent during low power physics testing, based on actual detector response. Additionally, the requirements of TS 2.2.1 and 3.3.1.1, which govern the setpoints and operability requirements during Modes 1 and 2, were not met, resulting in an unrecognized entry into TS 3.0.3. This LER is submitted in accordance with 10CFR50.73(a)(2)(i)(B), for a condition prohibited by TS. The apparent cause for this event was the failure to recognize the need to apply uncertainty in the analysis that projects detector current versus thermal power and the conservatisms that will be required to maintain trip setpoints less than 25 percent RTP. All intermediate and power range instrument setpoints were adjusted to meet TS requirements. Prior to Unit I entering Mode 2, industry practice on conservatism used in determining these setpoints will be benchmarked and appropriate preventive actions developed, the vendor will be asked to validate detector current calculation inputs, and adequate conservatisms will be incorporated into the setpoint calculations. An expanded extent of condition will be performed to determine if other nuclear instrumentation setpoints were established without considering appropriate conservatisms. Reactor power was continuously monitored and never exceeded 5 percent RTP, as required by the TS. The safety analysis assumes the trip from an event during low power physics testing occurs at 35 percent power, without fuel damage and without credit taken for the intermediate range instruments. Although greater than 25 percent, the setpoints on all 4 power range instruments were less than 30 percent, therefore, the safety significance for this event is minimal.
3162000007 | Cook 2, Cook 1 | 06/28/2000 | 07/27/2000 | ML00373720 | <strong>Technical Specification 3.0.3 Shutdown Initiated Due to Inoperable Rod Position Indications</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2000, at 2224 hours, with Unit 2 at 79.6 percent rated thermal power (RTP), a Technical Specification (TS) 3.0.3 shutdown was initiated due to failure to meet the requirements of TS Limiting Condition for Operation (LCO) 3.1.3.2, and the associated LCO action statements. Two Individual Rod Position Indicators (IRPIs) for control rods in control bank D, group 2, deviated from the group step counter demand by 18.5 steps, which exceeded the 18-step deviation limit of TS 3.1.3.1 (rod group height). The two IRPIs were declared inoperable, and TS LCO 3.1.3.2 (rod position indication) was entered. The action statements for TS 3.1.3.2 allow for a maximum of one rod position indicator channel per group to be inoperable; therefore, a TS 3.0.3 shutdown was initiated. Additionally, the Rod Position Deviation Monitor alarm failed to annunciate when the 18-step limit was reached due to a software error, subsequently found to exist on both units. The monitor should therefore have been historically inoperable. Failure to perform 4-hour rod position deviation readings throughout this period constitutes a violation of TS surveillance requirement 4.1.3.2. A non-emergency 1-hour NRC notification was made in accordance with 10CFR50.72(b)(1)(i)(A), for the initiation of a plant shutdown required by the plant's TS. This LER is submitted in accordance with 10CFR50.73(a)(2)(i)(B) for a condition prohibited by TS. The cause of the event was human error, a non-conservative decision to delay adjustment of the IRPI circuits. The IRPI channels were readjusted to within TS limits in accordance with plant procedures and declared operable, TS 3.0.3 was exited, and, at 2250 hours, the shutdown was terminated at 78.9 percent RTP. Prior to Unit 1 restart, the error in the Unit 1 Rod Position Deviation Monitor software will be corrected. A review of the issues identified in this LER will be performed in the upcoming cycle of continuing Operator Training, and a training course will be provided to operators to reinforce conservative decision-making principles. The condition was limited to temperature-related drift of the rod position indication system only; therefore, there was no safety significance to this event. There was also no safety significance to the missed 4-hour rod deviation surveillances.
3162000008 | Cook 2 | 06/30/2000 | 07/31/2000 | ML00377870 | <strong>Erroneous Plant Process Computer Input Data Resulted in Power Range Trip Setpoints Above TS Limit</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2000, during performance of procedure 12 EHP 4030 STP.219, "Thermal Power Measurement and Reactor Coolant System Flow Rate," it was identified that the Neutron Flux High trip setpoints for the Power Range Nuclear Instrumentation (PRNI) were above the Technical Specification (TS) 2.2.1 (reactor trip system setpoints) allowable value of 110 percent of Rated Thermal Power (RTP). Higher than expected feedwater temperatures due to intermittent circuit card contacts resulted in an indicated power level lower than actual power. PRNI 109 percent trip setpoints were adjusted based on the lower than actual indicated power level. A subsequent calorimetric calculation required an adjustment of indicated power upward by two percent, resulting in the PRNI trip settings exceeding the TS limit of 110 percent. With all four PRNIs inoperable, the requirements of TS 3.3.1.1 (reactor trip system instrumentation) were not met and an unrecognized entry into TS 3.0.3 occurred. This LER is submitted in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by TS. The cause for the PRNI Neutron Flux High trip setpoints being set above the TS limit was due to an inadequate TS surveillance procedure. The loose PPC FW temperature reference card contacts were tightened, and PRNI settings reset to 109 percent. Unit 1 and 2 plant procedures will be revised to include specific acceptance criteria regarding error tolerances for calorimetric plant parameters. As an interim preventive action, reactor engineering will perform a calorimetric calculation at 50 percent power during any restart following a Unit 2 plant trip. An expanded extent of condition evaluation will be performed to determine whether engineering EHP procedures have appropriate acceptance criteria for the functions they test. An investigation will be performed regarding multiple unrecognized entries into TS 3.0.3 from this and recent other events. Plant accident analyses bound the condition identified in this LER; therefore, there was minimal safety significance.
3162000009 | Cook 2 | 07/05/2000 | 08/07/2000 | ML01017035 | <strong>Common-Cause Ventilation Failure Results in Inoperable Auxiliary Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2000, during routine operator rounds, it was observed that the Unit 2 Turbine Driven Auxiliary Feedwater Pump (TDAFP) room cooler was not operating properly as indicated by a room temperature of approximately 100 degrees Fahrenheit (F). It was determined that normal lake water debris capable of passing through the Essential Service Water (ESW) strainer mesh was limiting flow through the room cooling system. The TDAFP was declared inoperable in accordance with Technical Specification (TS) 3.7.1.2, "Auxiliary Feedwater System." On July 7, 2000, reduced cooling flow to the East Motor Driven Auxiliary Feedwater Pump (MDAFP) room cooler was observed, and it was also declared inoperable. The design and installation discrepancies identified were considered a common-cause failure mechanism. This LER is submitted in accordance with 10CFR50.73(a)(2)(vii) for a condition that caused two independent trains to become inoperable in a single system. The apparent cause was determined to be human error, specifically, a lack of attention to the detail of the design requirements for the modification that installed the Auxiliary Feedwater Pump (AFP) room cooler units. The ESW valves for the AFP room coolers have been repositioned. Operations will periodically monitor ESW flow to all AFP room coolers and flush as required. The Unit 2 AFP room cooler flow blockage issue will be resolved by December 15, 2000, such that the compensatory actions are no longer necessary. The potential for flow blockage in Unit 1 will be resolved prior to the completion of the installation of the cooler modification. A "lessons learned" memorandum will be developed and issued to Design Engineering personnel detailing the causes and consequences of this type of oversight in the design process. Based on the evaluations performed, the potential common cause failure of the AFP room coolers due to design inadequacies has minimal safety significance.
3162000012 | Cook 2 | 08/11/2000 | 05/18/2001 | ML01150041 | <strong>Failure to Perform Increased Frequency Surveillance on 2 East Containment Spray Pump</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2000, it was determined that the required surveillance frequency for the Unit 2 East Containment Spray (CTS) pump had not been met. Vibration results in the Alert range from the previous performance of 2 East CTS pump surveillance in June 2000 required an increased surveillance frequency. The next surveillance should have been performed no later than July 20, 2000, but was not performed until August 11, 2000. This condition is a violation of Technical Specification (TS) 4-0.5, and was reportable in accordance with 10CFR50.73(a)(2)(i)(B), for a condition prohibited by TS. This supplement incorporates the root cause investigation results. The root cause of the missed surveillance was attributed to programmatic deficiencies within the IST Program that allowed a single human error to cause a program failure. The programmatic deficiencies were: absence of a tracking system, inadequate prompt communication with interface organizations, and an informal process for distribution/review of test results. The IST program procedure, EHI-5071 "Inservice Testing Program Implementation," was revised to require that the IST Program Coordinator provide written notification to the Surveillance-Scheduling Group when an IST component enters the Alert range and the associated surveillance frequency must be increased. Procedural enhancements were made to Operations procedure OHI-4016,"Conduct of Operations Guidelines," and Plant Manager Procedure PMP-4030-EXE-001 to provide additional barriers to prevent recurrence. The failure to test on an increased frequency was evaluated for safety significance. It was determined that the event was of minimal safety significance, as the 2 East CTS pump was operable.
3162000014 | Cook 2 | 09/15/2000 | 07/27/2001 | ML01218017 | <strong>Reactor Trip Signal Not Verified as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This supplement is being issued to provide the root cause and corrective actions associated with this event and replaces the original LER in its entirety. On September 15, 2000, during review of corrective actions for Licensee Event Report (LER) 315/98-051-00 (Reactor Trip Signal from Safety Injection Not Verified as Required by Technical Specification Surveillance), it was discovered that the requirements of Technical Specification (TS) 4.3.2.1.1, Table 4.3-2, Item 9.a were not met during startup from the extended outage. The TS requires, in part, that the Reactor Trip breakers be demonstrated operable for Modes 1, 2, 3, and 4 at least once every refueling interval by verification of Reactor Trip breaker actuation upon a manual Safety Injection (SI) signal. Contrary to this requirement, Unit 2 entered Mode 4 on June 6, 2000, and Mode 3 on June 12, 2000, without verifying operability of the manual SI Reactor Trip breaker actuation function. This condition is a violation of TS 4.3.2.1.1 and is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. The function was tested while in Mode 3 on June 13, 2000. During the surveillance procedure adequacy review performed in 1998, it was identified that TS 4.3.2.1.1, Table 4.3-2, Item 9.a "Reactor Trip breaker actuation on manual SI initiation" had not been performed in accordance with TS. This condition was previously documented in Condition Report (CR) 98-06496 and reported in LER 50-315/1998-051-00. The corrective actions from CR 98-06496 to update the Surveillance Matrix were signed off as complete in the hard copy condition report but in fact were not updated nor was a Recurring Task (RT) Job Order established at that time. As a result of the failure to implement the corrective actions identified in the Corrective Action Program, the applicable procedures were not revised, nor was the TS Surveillance Requirement Matrix updated, as intended. The TS Surveillance Requirement Matrix has been revised and a RT Job Order has been established. This has minimal safety significance since testing was completed prior to energizing the control rods.
3162000015 | Cook 2 | 10/19/2000 | 08/17/2001 | ML01234011 | <strong>Containment Airlock Door Seals Not Tested At Frequency Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This supplement is being issued to provide the cause and corrective actions associated with this event and replaces the original LER in its entirety. On October 19, 2000, during evaluation of a field observation from the Performance Assurance department, it was determined that Technical Specifications (TS) surveillance requirement 4.6.1.3.a to test the containment airlock door seals within seven days following airlock entry was not performed. On July 27, 2000, at 0315 hours, an operator entered the Unit 2 containment 612-foot (ft) elevation airlock to perform a surveillance test line-up. The airlock was not entered again until August 10, 2000, at 0200 hours. No testing of the 612 ft elevation airlock door seals occurred during that period. Failure to test the containment airlock door seals within seven days following the entry was determined to be a violation of TS. This LER is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B), for a condition prohibited by the plant's TS. The cause of this event was misinterpretation of the requirements in Section 10.2.2.1 of NEI 94-01, "Industry Guideline for Implementing Performance-Based Option of 10 CFR Part 50, Appendix J," by plant personnel during the development and review of plant test procedures. A contributing cause was the over reliance on a single individuals expert opinion during the review and approval process. A review of the containment entry log since Unit 2 restart in June 2000 was performed to ensure no other cases of missed airlock door seal surveillance tests have occurred. Plant procedures have been revised to meet the requirements of NEI-94-01 Based on the successful surveillance leak-test history, containment integrity was not compromised during the period when the 612 ft elevation airlock was not tested in accordance with TS and NEI 94-01, and the condition was of no safety significance.
3172000001 | Calvert Cliffs 1 | 01/14/2000 | 02/11/2000 | ML00368442 | <strong>Reactor Trip Due to Motor Generator Local Voltage Adjust Handswitch Failure</strong><br /><i>Abstract:&nbsp;</i>At 0950 on January 14, 2000, Calvert Cliffs Unit 1 tripped from 100 percent power due to a failure of the No. 11 Motor Generator (MG) Local Voltage Adjust Handswitch. Contacts closed on the handswitch causing No. 11 MG Voltage Regulator to raise the output voltage, increasing the voltage on the reactor trip bus. The output voltage increased to the setpoints of both the Nos. 11 and 12 MG sets' Overvoltage Relays, opening the output contactors of both MG sets. With both MG output contactors open, the reactor trip bus had zero voltage, causing control element assemblies to insert into the core. Operators responded appropriately and primary plant systems functioned as designed. The plant was brought to a safe shutdown condition. Number 11 MG's Local Voltage Adjust Handswitch and Voltage Regulator card was replaced. Both MG sets were meggered, bridged, and load tested. The three remaining voltage control handswitches on Unit 1 were inspected and no wear similar to that of the failed handswitch was found. The unit was restarted January 15, 2000.
3172000002 | Calvert Cliffs 1 | 01/28/2000 | 02/28/2000 | ML00368783 | <strong>Emergency Core Cooling Pump Room Ventilation Surveilance Test Failure</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2000, during performance of a surveillance test, a condition was discovered at Calvert Cliffs that could have prevented the Emergency Core Cooling System (ECCS) Pump Room Exhaust Filtration System (PREFS) from fulfilling its safety function to control the release of radioactive material during the recirculation phase of a Loss-of-Coolant Accident. Specifically, during an in-place test of the ECCS PREFS charcoal adsorber to show a penetration and system bypass less than or equal to 1.0 percent, the test showed a penetration and system bypass greater than 50 percent. The test failed due to loose nuts holding in the ECCS charcoal trays. The test was repeated with satisfactory results after the nuts were tightened. The ECCS PREFS could have been incapable of performing its safety function since the last time it was tested on November 8, 1999, a period of 82 days.
3172000003 | Calvert Cliffs 1, Calvert Cliffs 2 | 02/29/2000 | 03/30/2000 | ML00369939 | <strong>Incomplete Channel Calibration Procedure Leaks to Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 29, 2000, the reactor coolant system manager determined that a discrepancy in the scope of a surveillance test procedure (STP) led to a failure to properly complete channel calibration of the pressurizer power-operated relief valve (PORV) actuation circuitry in accordance with Technical Specification (TS) Surveillance Requirement (SR) 3.4.12.6. The STP did not include the sensor portion of the PORV actuation channel, consisting of four temperature elements (TEs). Each TE is a resistance temperature detector (RTD). After discovering the discrepancy, we determined that the PORV actuation channel RTDs had not been tested since 1991. The balance of the channel was properly tested. The cause of this event was personnel error in failing to maintain the RTDs in a testing procedure. The RTDs were improperly deleted from the scope of an STP in 1992. The Calvert Cliffs Unit 1 PORV actuation channels were recently tested and verified operable before we entered low temperature overpressure protection (LTOP) conditions during the 2000 refueling outage. The Unit 2 PORV actuation channels will be tested prior to the next planned entry into LTOP conditions. Corrective actions include correcting the procedure and matrixing the RTDs to the TS SRs they implement. All TS surveillance channel calibrations of channels with RTDs or thermocouples will be reviewed to ensure TS SRs are being consistently implemented properly.
3172000004 | Calvert Cliffs 1 | 03/31/2000 | 04/28/2000 | ML00370982 | <strong>Containment Radiation Signal Bypassed During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2000, during core alterations, a condition was discovered at Calvert Cliffs that is prohibited by Technical Specifications. Specifically, during Unit 1 core alterations, it was discovered that one containment radiation monitor sensor module was bypassed. The Technical Specifications require that if one radiation monitor sensor module or associated measurement channel is inoperable, the affected sensor module shall be placed in the trip condition within four hours. Core alterations were suspended in accordance with the Technical Specifications when the condition was discovered. The sensor module was restored to operable status before re-commencement of core alterations. Corrective actions included an immediate procedure change to require a check of the bypass switches for these sensors and a description of this event has been distributed to all licensed operators for required reading.
3172000005 | Calvert Cliffs 1 | 09/10/2000 | 10/05/2000 | ML00375890 | <strong>Reactor Trip Due to Spurious Main Steam Isolation Valves Closing</strong><br /><i>Abstract:&nbsp;</i>At 2123 on September 10, 2000, Calvert Cliffs Unit 1 tripped from 100 percent power due to a spurious signal from Channel A of the Engineered Safety Features Actuation System Steam Generator Isolation Signal. A logic module in the Steam Generator Isolation Signal produced a spurious signal that closed the Main Steam Isolation Valves. The closed Main Steam Isolation Valves created shrink in both steam generators and the Unit 1 reactor tripped on low steam generator water level. Operators responded appropriately and primary plant systems functioned as designed. The plant was brought to a safe shutdown condition. The suspect Channel A Steam Generator Isolation Signal logic module was replaced and the new module was post-maintenance tested satisfactorily. The suspect logic module was sent to the vendor for testing and destructive analysis. The unit was restarted September 12, 2000. A detailed root cause analysis is in progress to determine causal factors, generic implications, and establish additional corrective actions, as required.
3172000006 | Calvert Cliffs 1 | 11/10/2000 | 02/27/2001 | ML01064012 | <strong>Number 12 Containment Spray Pump Circuit Breaker Failed to Close</strong><br /><i>Abstract:&nbsp;</i>During surveillance testing on November 10, 2000, at 0200, the Asea Brown Boveri, Inc. 4-kV Vacuum Circuit Breaker for 12 Containment Spray Pump failed to close upon the receipt of an auto-start signal. Troubleshooting revealed the breaker tripped free. This same breaker failed to close during similar surveillance testing on October 12, 2000, and subsequent testing indicated the breaker was operating satisfactorily. The breaker was replaced with a General Electric Magne-Blast circuit breaker. The General Electric breaker was satisfactorily tested and 12 Containment Spray Pump was declared operable November 10, 2000, at 1800. Unit 1 was in Mode 1, operating at 100 percent power at the time of the event, the event had no affect on the operation of the unit. The breaker failed to close because the breaker was not inserted fully into the cubicle, allowing the trip-free interlock to contact the interlock cam on the cubicle.
3212000001 | Hatch 1, Hatch 2 | 01/07/2000 | 01/31/2000 | ML00368173 | <strong>Improperly Sized Differential Pressure Instruments Lead to Missed Technical Specifications Action Statements</strong><br /><i>Abstract:&nbsp;</i>On 1/7/2000 at 1201 EST, Unit 1 was in the Run mode at 2763 CMWt (100 percent rated thermal power) and Unit 2 was in the Run mode at 2706 CMWt (97.9 percent rated thermal power). At that time, licensed personnel in the control room were notified that certain items of instrumentation required by both units' Technical Specifications were inoperable. The instruments were water level sensors in the suppression pool whose function is to initiate a signal on high water level to realign the suction source of the high pressure coolant injection system from the condensate storage tank to the suppression pool. These instruments were declared inoperable because of a design and installation error that resulted in their being calibrated contrary to the vendor's specifications. This condition actually occurred when the instruments were installed under a design change in April, 1997. It was discovered when engineering personnel were looking for records of an evaluation that was performed as a corrective action for LER 50-366/1998-001. Licensed personnel re-aligned the suction source for the high pressure coolant injection system to the suppression pool as required by the Technical Specifications. This event was caused by personnel error and an omission from a procedure. Personnel did not recognize that installation of an internal jumper was necessary for initial setup of the replacement transmitters. This was due to the subtle change associated with the range which the transmitters would monitor for this application. An inadvertent procedure omission occurred in that the instructions for calibrating the pressure transmitter were not adequate, which contributed to the decision to change the pressure transmitters to a different, and incorrect, pressure range. Corrective actions for this event were replacing the affected transmitters, revising calibration procedures, and training personnel.
3212000002 | Hatch 1, Hatch 2 | 01/26/2000 | 03/09/2001 | ML01079031 | <strong>Reduction in Reactor Feedwater Flow Results in Automatic Reactor Shutdown on Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On 01/26/2000 at 0653 EST, Unit I was in the Run mode at a power level of 2763 CMWT (100% of rated thermal power) when the reactor shut down automatically, and the Group 2 Primary Containment Isolation Valves (PCIVs) closed on low water level. Water level decreased when feedwater flow was reduced following the unexpected closure of an inlet valve to a feedwater heater. Following shutdown, water level continued to decrease due to a void collapse from the rapid reduction in power, resulting in closure of the Group 5 PCIVs and automatic initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) systems. The secondary containment dampers automatically isolated, and all trains of the Unit I and Unit 2 Standby Gas Treatment systems automatically started on low water level. Water level reached a minimum of 54 in. below instrument zero. The Reactor Feedwater Pumps, RCIC, HPCI, and Control Rod Drive systems restored level to > 40 in. above instrument zero within 40 sec of the shutdown. Pressure decreased from its normal value of 1030 psig to a minimum of 746 psig approximately 2 min following shutdown. At that time, the main steam line isolation valves (MSIVs) were closed because water level was approaching the main steam line nozzles. MSIV closure caused pressure to increase to a maximum of 1085 psig approximately 17 min following shutdown. Pressure was reduced and controlled using manual and automatic safety/relief valve actuation. The feedwater heater inlet valve closed upon receipt of an apparent spurious signal from its control switch. The inlet valve closure was most likely the result of a slight jarring of either the control switch or its panel. Switches of this type have been known to actuate with very little movement of the control mechanism. The delay of the HPCI system to trip automatically at its high level setpoint resulted in water level reaching the main steam line nozzles. Testing of the level transmitters, trip units, relays, and logic system revealed no reason for the delay in tripping. Corrective actions include replacing control switches, reviewing the type and frequency of logic system testing, and additional operator training.
3212000003 | Hatch 1 | 01/29/2000 | 02/22/2000 | ML00369007 | <strong>Failed Relay Coil Results in Unexpected Actuations of Engineered Feature Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 1/29/2000 at approximately 1530 EST, Unit 1 was in cold shutdown with the residual heat removal shutdown cooling system in service. At that time, a relay coil failed, resulting in opening a fuse in the reactor protection system power supply to the primary containment isolation system control logic. The open fuse caused several engineered safety features to actuate. Several valves in the Group 1 and Group 2 primary containment isolation system closed automatically, and the mechanical vacuum pump tripped, as well as the steam packing exhaust blower. Licensed personnel verified the actuations by procedure. The fuse was subsequently replaced, and the affected valves were returned to their pre-event configurations. The cause of this event was a failed relay coil. When the relay coil developed a short circuit, the fuse in its power supply experienced high current and opened as expected for high current. The cause of the failed relay coil appears to be related to problems experienced previously with this type of relay, a General Electric CR120A. The relay is installed in an application where it is continuously energized. After many years of this service, the windings of the coil began to short circuit turn-to-turn, leading to overheating and eventual failure. Corrective actions for this event included replacing the fuse and the failed relay. In addition, the SNC response to General Electric Services Information Letter 229 will be reviewed by 8/31/2000.
3212000004 | Hatch 1 | 07/10/2000 | 08/04/2000 | ML00374270 | <strong>Component Failure Causes Turbine Trip and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 07/10/2000 at 1050 EDT, Unit 1 was in the Run mode at a power level of 2754 CMWT (99.7 percent rated thermal power). At that time, the reactor scrammed and the reactor recirculation pumps tripped automatically on turbine stop valve fast closure caused by a turbine trip. The turbine tripped when the vibration instrument on the #10 bearing failed causing a false high vibration trip signal to be generated. Following the reactor scram, water level decreased due to void collapse from the rapid reduction in power. However, the reactor feedwater pumps maintained water level higher than seventeen inches above instrument zero. Consequently, no safety system actuations on low level were received nor were any required. Pressure reached a maximum value of 1128 psig; nine of eleven safety/relief valves lifted to reduce reactor pressure. Pressure did not reach the nominal actuation setpoints for the remaining two safety/relief valves. The temperature in the vessel bottom head region decreased by more than the Technical Specification allowed 100 in one hour before a recirculation pump could be re-started. This event was caused by component failure. The vibration instrument on the #10 bearing failed, generating a false high vibration signal. The high vibration signal caused the main turbine to trip, producing a reactor scram on turbine stop valve fast closure per design. The failed vibration instrument was replaced. The vibration instruments on the remaining bearings were checked resulting in the replacement of the shaft rider probe on the #6 bearing. No other instrument problems were found.
3212000005 | Hatch 1 | 08/16/2000 | 09/15/2000 | ML00375170 | <strong>Failure of Turbine Stop Valve to Close Renders High Pressure Coolant Injection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 08/16/2000 at 0030 EDT, Unit 1 was in the Run mode at a power level of approximately 2763 CMWT (100 percent rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was declared inoperable when its turbine stop valve failed to close as required during the performance of a routine weekly test. Operations personnel had started the HPCI system auxiliary oil pump as required by step 7.9.7 of surveillance procedure 34SV-SUV-019-1S, "Surveillance Checks," and Operating Order OO-01-0200S, "Weekly HPCI Auxiliary Oil Pump Exercise." The turbine stop valve opened as expected when the auxiliary oil pump was started. Operations personnel then depressed the manual HPCI turbine trip pushbutton as required by the Operating Order in order to verify proper operation of the HPCI turbine trip solenoid-operated valve and turbine stop valve. The turbine stop valve failed to close as expected when the trip pushbutton was depressed. Operations personnel declared the HPCI system inoperable as required by Condition C of Unit 1 Technical Specifications Limiting Condition for Operation 3.5.1. This event was the result of turbine stop valve binding caused by galling of the disc guide surfaces. The valve bonnet guide and disc guide ring surfaces were found to be galled to the extent that less than the minimum required clearance existed between the disc and guide. This resulted in valve binding. The cause for the galling could not be determined conclusively. The bonnet guide was machined, the valve was reassembled, and the HPCI system operability test was completed satisfactorily on 08/18/2000.
3212000006 | Hatch 1 | 08/31/2000 | 09/25/2000 | ML00375661 | <strong>Failed Relay Results in Unplanned Actuation of Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On 8/31/2000 at 1600 EDT, Unit I was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, Operations personnel found post-accident sampling system return isolation valve 1E41-F122 closed. This valve had been opened previously during the performance of logic system functional test procedure 34SV-SUV-027-1S, "Reactor Building Isolation LSFT." Valve 1E41-F122 is an air-operated, primary containment isolation valve (PCIV); therefore, its closure was an unplanned actuation of an engineered safety feature. Operations personnel declared the valve inoperable and initiated Required Action Sheet 1-00-205 as required by Unit 1 Technical Specifications Limiting Condition for Operation 3.6.1.3, Required Action A.1, and plant procedures. The cause of this event was a failed solid-state relay located in relay control panel No.3, 2P33-P211. Specifically, one of the four pins on the solid-state relay broke at the base of the relay. Failure of this relay de-energized another relay, K1R2. When the coil on the K1R2 relay de-energized, its contact located in the Reactor Coolant Sample Primary Containment Isolation circuit opened. The opened contact resulted in a loss of power to the energized solenoid-operated pilot valve for PCIV valve, 1E41-F122. The PCIV valve is designed to close upon loss of power. Therefore, when the relay failed resulting in a loss of power to the solenoid circuit, the primary containment isolation valve closed as designed to its "Fail-Safe Position." Maintenance personnel replaced the failed relay per Maintenance Work Order 1-00-02758. Operations personnel returned the valve to an operable status on 9/7/2000 at 0405 EDT following the successful completion of procedure 34SV-SUV-008-1S, "Primary Containment Isolation Valve Operability."
3212000007 | Hatch 1 | 09/08/2000 | 09/27/2000 | ML00375688 | <strong>Component Failure Resulting in Erratic Flow Signal Renders HPCI System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 09/08/2000 at 1514 EDT, Unit 1 was in the Run mode at a power level of approximately 2744 CMWT (99.3 percent rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was declared inoperable when Operations personnel noted that the flow rate indications on flow controller 1E41-R612 were exhibiting erratic behavior. Specifically, the indications, a vertical bar graph and a digital window display, were oscillating between zero gallons per minute and greater than 500 gallons per minute with the HPCI system in standby. Operations personnel initiated Required Action Sheet 1-00-215 as required by Unit 1 Technical Specifications Limiting Condition for Operation 3.5.1, Condition C, and plant procedures. Maintenance personnel investigating the problem with the flow controller found the controller input signal resistor to be degraded. This resistor converts a flow rate transmitter output current signal to a controller input voltage signal. The degraded resistor caused the voltage signal to fluctuate and the flow controller indicators to oscillate. Maintenance personnel replaced the controller input signal resistor. Operations personnel then completed satisfactorily the HPCI system operability test and returned the system to an operable status on 09/09/2000 at 0502 EDT.
3212000008 | Hatch 1 | 09/11/2000 | 10/02/2000 | ML00375920 | <strong>Inadequate Procedure Results in Unplanned Actuation of Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On 9/11/2000 at 1020 EDT, Unit 1 was in the Run mode at a power level of 2716 CMWT (98.3 percent rated thermal power). At that time, excess flow check valve 1B21-F051C, a primary containment isolation valve, closed unexpectedly during the performance of procedure 34SV-SUV-026-1S, "Primary Containment Isolation Valves LSFT"' when Post-Accident Sampling System inlet isolation valves were opened as required by the procedure. These valves were opened in order to verify their closure on a simulated isolation signal at a later point in the test. However, reactor coolant flowed into the Post-Accident Sampling System to fill and pressurize the inlet tubing when the valves were opened. The flow created when the inlet valves were opened was sufficient to actuate excess flow check valve 1B21-FO51C on high flow and the valve closed as designed. Because valve 1B21-F051C is a primary containment isolation valve, its automatic closure represented an unplanned actuation of an engineered safety feature system. The cause of this event was an inadequate surveillance procedure. Procedure 34SV-SUV-026-1S did not alert licensed Operations personnel to the possibility that excess flow check valve 1B21-F051C could isolate when the Post-Accident Sampling System inlet isolation valves were opened nor did it contain steps to prevent the rapid filling and pressurizing of the sampling system tubing. Operations personnel re-opened the excess flow check valve. Procedure 34SV-SUV-026-1S will be revised prior to its next performance.
3212000009 | Hatch 1 | 09/20/2000 | 10/16/2000 | ML00376194 | <strong>Component Failure Results in Failure of Engineered Safety Feature to Actuate</strong><br /><i>Abstract:&nbsp;</i>On 9/20/2000 at 1215 EDT, Unit 1 was in the Run mode at a power level of 2695 CMWT (97.5% rated thermal power). At that time, inboard primary containment isolation valve 1G31-F001 failed to close as expected during the performance of surveillance procedure 34SV-G31-001-1S, "Reactor Water Cleanup Automatic Isolation LSFT." Specifically, the valve failed to close upon injection of a simulated isolation signal on high equipment room temperature/high differential temperature/high differential flow. Operations personnel declared inoperable the primary containment isolation function of valve 1G31-F001 and initiated Required Action Sheet 1-00-228 as required by Unit 1 Technical Specifications Limiting Condition for Operation 3.6.1.3, Condition A, and plant procedures. Outboard primary containment isolation valve 1G31 F004 was closed and de-activated under Clearance 1-00-0761 per Unit 1 Technical Specifications Limiting Condition for Operation 3.6.1.3, Required Action A.1. The cause of this event was component failure. The normally-closed set of contacts in primary containment isolation logic relay 1A71-K26 failed to close when the relay coil de-energized upon receipt of the simulated isolation signal. This set of contacts must close in order to close valve 1G31-F001; therefore, its failure to close prevented valve 1G31-F001 from closing. The sliding contact arm on the relay was replaced; valve 1G31-F001 was verified to close on a simulated isolation signal per procedure 34SV-G31-001-1S; and the valve was returned to an operable status on 9/22/2000 at 1638 EDT.
3212000010 | Hatch 1 | 09/27/2000 | 10/18/2000 | ML00376243 | <strong>Personnel Error Results in a Condition Prohibited by the Plant's Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 09/27/2000 at 1015 EDT, Unit 1 was in the Run mode at a power level of approximately 2620 CMWT (approximately 94.8 percent rated thermal power). At that time, the "B" loop of the Core Spray system was rendered inoperable when contract personnel mistakenly removed a power cable to the motor operator for Core Spray pump minimum flow valve 1E21-F031B. This prevented the valve from closing when pump discharge flow reached a set value thereby creating a flow diversion path sufficiently large to prevent the required system flow from reaching the reactor. The "A" loop of the low pressure coolant injection (LPCI) function of the Residual Heat Removal (RHR) system previously had been rendered inoperable for scheduled logic system functional testing. With one loop of Core Spray and one loop of the LPCI function of RHR inoperable, the plant entered Condition F of Unit 1 Technical Specifications Limiting Condition for Operation (LCO) 3.5.1 which required the plant to enter LCO 3.0.3. At 1037 EDT, the "A" loop of the LPCI function of RHR was restored to an operable status, exiting LCO 3.0.3. This event was caused by cognitive personnel error. Contract personnel as part of pre-outage activities were instructed to disconnect the wires from an air flow switch located in the same area as minimum flow valve 1E21-F03 1B. They instead disconnected a power cable to the valve, rendering inoperable the "B" loop of the Core Spray system. The power cable was restored, and the valve was functionally tested and returned to service. Responsible personnel were issued a written reprimand.
3212000011 | Hatch 1 | 09/29/2000 | 10/17/2000 | ML00376238 | <strong>Trip of Reactor Feedwater Pump Results in Low Reactor Water Level and Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 09/29/2000 at 1357 EDT, Unit 1 was in the Run mode at a power level of approximately 1520 CMWT (55 percent rated thermal power). At that time, the reactor was scrammed manually following a trip of the operating Reactor Feedwater Pump (RFP) and a decrease in water level. Personnel inserted the scram in anticipation of an automatic scram on low water level. Following the scram, level continued to decrease due to void collapse from the rapid reduction in power and the trip of the RFP resulting in closure of the Group 2 and Group 5 Primary Containment Isolation Valves as designed. Level reached a minimum of approximately 40 inches below instrument zero causing automatic initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) systems. Secondary containment automatically isolated and all four trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low level. The RCIC and HPCI systems recovered level; an RFP was placed into service to maintain level. Pressure decreased immediately following the manual scram; no Safety/Relief Valves lifted nor were any required to lift. Pressure was controlled automatically by the Main Turbine Bypass Valves. This event was caused by component failure. During the implementation of a clearance to isolate a condensate pump, air was introduced into the condensate pump suction header through a leaking pump suction isolation valve. The presence of air led to the trip of the operating RFP on low suction pressure. The valve will be repaired or replaced as necessary during the refueling outage that began on 09/29/2000.
3212000012 | Hatch 1 | 11/06/2000 | 12/01/2000 | ML00377662 | <strong>Water Level Transient Following Manual Reactor Scram Causes Group 2 PCIS Isolation</strong><br /><i>Abstract:&nbsp;</i>On 11/06/2000 at 1540 EST, Unit 1 was in the Run mode at an approximate power level of 442 CMWT (16 percent rated thermal power). At that time, Operations personnel manually scrammed the reactor per procedure 34GO-OPS-013-1S, "Normal Plant Shutdown," to allow plant personnel to isolate and repair condensate demineralizer outlet header isolation valve 1N21-F253. Following the manual scram, water level decreased due to void collapse from the rapid reduction in power, reaching a minimum of approximately three inches above instrument zero (about 161 inches above the top of the active fuel). The decrease in water level resulted in receipt of a Group 2 Primary Containment Isolation System (PCIS) isolation signal and closure of the Group 2 Primary Containment Isolation Valves per design. The operating Reactor Feedwater Pump restored level to its desired value. Personnel reset the Group 2 isolation signal and restored the isolation valves to normal per procedure 34AB-C71-001-1S, "Scram Procedure." This event was the result of the expected water level decrease from void collapse and proceduralized operator action following a reactor scram. Operations personnel increased water level to approximately 44 inches above instrument zero, about seven to nine inches above the normal operating level, in anticipation of the level decrease. Nevertheless, water level decreased to a point approximately equal to the Group 2 PCIS isolation setpoint. Personnel actions, procedural instructions, and equipment operation were appropriate for the situation; therefore, no corrective actions are required.
3232000001 | Diablo Canyon 2 | 01/26/2000 | 02/24/2000 | ML00368689 | <strong>Technical Speciation 3.4.8 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2000, at 1753 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.4.8, "Specific Activity," was not met. TS 4.4.8, Table 4.4-4, item 1 of the table and the applicable notation require that gross activity analysis be done at least once per 72 hours in Modes 1, 2, 3, and 4 and that the sample analysis be completed within 2 hours. Contrary to the requirement, the sample analysis was not completed for 2 hours and 32 minutes. This condition was discovered by a supervisory review of sampling results. The condition was caused by personnel error. The responsible technician was delayed after taking the sample but also believed, incorrectly, that Technical Specification 4.0.2 could be applied to the sample period. The involved individual was counseled. Other personnel were advised of the condition and procedure requirements during a departmental tailboard. Although unrelated to the cause of the condition, a conflict between the governing procedure and the TS requirement for sample analysis completion time was identified and corrected. A review of past samples was done to determine the number and effect of late analyses. The review indicated that previous samples were unaffected by this condition.
3232000002 | Diablo Canyon 2 | 03/07/2000 | 04/06/2000 | ML00370210 | <strong>Technical Specification 3.4.4 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2000, at 1416 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, the limiting condition for operation for Technical Specification 3.4.4, "Reactor Coolant System Relief Valves," was not met when the block valve for an inoperable power operated relief valve (PORV) was reenergized and opened. This condition was discovered by a utility licensed operator. The condition was caused by a personnel error (cognitive). The shift foreman failed to recognize the requirement for a post maintenance test prior to the full removal of a clearance. Corrective actions included adding administrative controls for PORV maintenance to separate the maintenance activities from the operator's TS compliance activities.
3232000003 | Diablo Canyon 2 | 04/06/2000 | 10/26/2000 | ML00376456 | <strong>Technical Specification 3.6.5 Not Met Due to the Unanticipated Failure Mode of the Containment Average Air Temperature Indicator</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2000, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, the Limiting Condition for Operation of Technical Specification (TS) 3.6.5, "Containment Air Temperature," was not met when the containment average air temperature indicator (TI-26) failed as-is and went undetected during subsequent daily surveillances. Consequently, the containment average air temperature had not been verified. On September 26, 2000, a utility licensed operator, while performing the daily surveillance test procedure (STP), determined TI-26 was inoperable when the digital temperature indicator did not recalculate when different temperature elements were selected. The cause of the TS violation was an unanticipated failure mode of TI-26. On September 26, 2000, at 2207 PDT, operators declared the TI-26 inoperable, entered TS surveillance requirement 3.0.3 and calculated the average containment temperature directly from the functioning temperature elements. On September 27, 2000, at 1749 PDT, operators satisfied the surveillance requirement by confirming the containment temperature was less than the 120 degrees Fahrenheit. On September 28, 2000, after TI-26 was replaced, operators declared it operable. Corrective actions to prevent recurrence include revising STP I-1 B to verify TI-26 is functioning while verifying the indicated temperature is within limits.
3232000004 | Diablo Canyon 2 | 10/23/2000 | 11/22/2000 | ML00377202 | <strong>Engineered Safety Features Actuation, Diesel Generators Started When Startup power Was Lost Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2000, at 1637 PDT, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Emergency Diesel Generators (EDGs) 2-1, 2-2, and 2-3 started as a result of loss of power to the startup power system. A clearance had been issued for the Unit 1 startup transformer, authorizing the opening of the switch to disconnect the startup transformer from the 230kV system during Mode 6 (Refueling) for scheduled maintenance. However, due to personnel error, the Unit 2 disconnect switch was opened. This resulted in actuation of 4kV startup undervoltage relays, which started all three EDGs. Within three minutes, the Unit 2 disconnect switch was reclosed, and startup power to Unit 2 was restored. The EDGs responded as designed and were secured. This event is an engineered safety feature actuation, and a 4 hour nonemergency report was made on October 23, 2000 at 1825 PDT per 10 CFR 50.72(b)(2). The vital buses remained energized from the auxiliary power system throughout the event. Therefore, the EDGs were not required to supply power to the buses and no other systems were affected. The root cause of the event is personnel error due to lack of attention to detail. Corrective actions include adding color-coded signs to the switches and coaching the individuals on self-verification.
3242000001 | Brunswick 2 | 01/07/2000 | 02/07/2000 | ML00368388 | <strong>Operation Prohibited by Technical Specifications Due to Inoperable Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2000, at approximately 1300 hours, it was determined that a malfunction of the Division 1 Nitrogen Backup subsystem pressure control valve (2-RNA-PCV-5248) which existed from August 28, 1999, to December 3, 1999, resulted in the inoperability of the Division 1 Nitrogen Backup subsystem for the same time period. The inoperability of the subsystem resulted in the Division 1 Reactor Building-to-Suppression Chamber vacuum breaker being inoperable for a time that exceeded required action completion times of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.5, "Reactor Building-to-Suppression Chamber Vacuum Breakers." Additionally, during the time the vacuum breaker was inoperable, Mode changes were made, which were prohibited by TS LCO 3.0.4. The cause of this event is attributed to an inadequate level of knowledge, on the part of plant personnel, regarding operability criteria for the Nitrogen Backup subsystems. This resulted in the failure to recognize and correct deficiencies in a timely manner. The safety significance of this event is minimal. Pressure control valve 2-RNA-PCV-5248 was repaired by replacing internal components. Documentation used for determining and verifying operability of the Nitrogen Backup subsystems and Reactor Building-to-Suppression Chamber vacuum breakers will be enhanced. Training on this event will be provided to the appropriate plant personnel during future scheduled training intervals.
3242000002 | Brunswick 2 | 09/22/2000 | 10/20/2000 | ML00371951 | <strong>Main Transformer Fault Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2000, at 0340 hours, the Brunswick Steam Electric Plant (BSEP) Unit No. 2, was operating at 100 percent rated thermal power, when the Unit 2 B phase of the Main Power Transformer (U2 B MPT) experienced a fault resulting in a generator load reject and subsequent turbine trip and reactor scram. In addition, Primary Containment Isolation System Groups 2, 6, and 8 valve isolations/signals initiated as expected. The transformer fault was caused by a loss of cooling. The loss of cooling system is attributed to the tripping of an electrical breaker, which provided alternate power to the transformer cooling components (i.e., 480 V distribution panel 2-HB4 circuit breaker #7). The cause of the breaker tripping has not been conclusively determined. At the time of the event, the U2 B MPT auxiliaries were being powered from the alternate 480 V source due to maintenance that was being performed on the normal source. The causes of the event include the unexplained trip of the 2-HB4 circuit breaker #7 and the failure to establish adequate compensatory measures during the maintenance activity. Corrective actions include replacement of the U2 B MPT and 2-HB4 circuit breaker #7. In addition, enhancements to the work control process, procedure revisions, and event review with appropriate site personnel will be performed to preclude recurrence. The safety significance of this event is minimal since off-site power remained available throughout the event and all emergency diesel generators were operable.
3252000001 | Brunswick 1, Brunswick 2 | 03/03/2000 | 04/03/2000 | ML00370185 | <strong>Loss of Offsite Power During Refuel Outage</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2000, at 0931 hours, with Unit 1 in a refuel outage and Unit 2 at 100 percent rated thermal power, a switch positioning error, made during switchyard relay trip test activities, resulted in a loss of offsite power (LOOP) for Unit 1, and initiation of numerous Engineered Safety Feature (ESF) actuations including a shutdown cooling isolation. At approximately 1200 hours, the failure of emergency Diesel Generator 2 (DG2) excitation system power potential transformer (PPT) resulted in a loss of power to emergency bus E2, which caused a Technical Specification Limiting Condition for Operation 3.0.3 entry for Unit 2, another initiation of numerous ESF actuations on Unit 1, and the actuation of the halon system in the Diesel Generator Building, which caused an actuation of the Control Room Emergency Ventilation system in the chlorine protection mode. The root cause of the LOOP event is personnel error; inadequate self-checking and attention to detail on the part of the transmission maintenance technicians performing and verifying the relay trip testing in the switchyard relay house. The root cause of the PPT failure is a short between turns of the secondary winding. The switch positioning error was corrected and offsite power restored to the site on March 3, 2000, at 1147 hours. The DG2 excitation system PPT was replaced and DG2 declared operable on March 8, 2000. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(iv), and 10 CFR 50.73(a)(2)(v)(D).
3252000002 | Brunswick 1, Brunswick 2 | 04/28/2000 | 05/25/2000 | ML00371951 | <strong>Control Room Emergency Ventilation System Actuation During Chlorination System Venting</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2000, at 1630 hours, with both units operating at rated power, the Control Room Emergency Ventilation (CREV) system actuated and aligned to the chlorine protection mode. At the time of the occurrence, maintenance personnel were venting nitrogen gas containing residual chlorine from the chlorination system following the performance of scheduled system maintenance. By 1802 hours, venting of the chlorination system was completed and the CREV system was restored to its normal configuration. The cause of this occurrence is attributed to an external factor. Specifically, the prevailing wind direction abruptly changed during the venting of the chlorination system. Residual chlorine gas, vented from the system, actuated the chlorine detectors located at the chlorine loading area resulting in the CREV system actuation. Due to the nature of this event, corrective actions are not warranted. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(iv) in that the condition resulted in the automatic actuation of an engineered safety feature.
3252000003 | Brunswick 1, Brunswick 2 | 06/09/2000 | 07/07/2000 | ML00373122 | <strong>Control Room Emergency Ventilation System Actuation During Chlorination System Breach</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2000, at 1651 hours, with both units operating at rated power, the Control Room Emergency Ventilation (CREV) system actuated and aligned to the chlorine protection mode of operation. At the time of the occurrence, maintenance personnel were performing work that involved breaching the chlorination system. The cause of the occurrence is attributed to a small amount of residual chlorine gas escaping from the chlorination system when the maintenance personnel were removing piping components. Although the chlorination system had been purged with nitrogen, small amounts of residual chlorine can remain in piping crevices and trapped in corrosion products. When the system was opened, this residual chlorine, in the form of gas, escaped and was sensed by the chlorine detectors. Due to the required sensitivity of the chlorine detection instrumentation and the nature of maintenance activities, which require a system breach, additional measures to minimize the actuation of the CREV system in the chlorine protection mode are not considered to be practical or prudent. The actuations have minimal impact on the CREV system equipment reliability, and have minimal nuclear or industrial safety significance. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(iv) as a condition that resulted in the automatic actuation of an engineered safety feature.
3272000002 | Sequoyah 1 | 03/14/2000 | 04/10/2000 | ML00370416 | <strong>Loss of Pressurizer Level as a Result of a Relief Valve Failing to Reseat</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2000, at approximately 2350 Eastern standard time (EST), Operations personnel began venting the residual heat removal (RHR) discharge hot leg injection piping with one RHR pump in service. Operations personnel observed a decreasing pressurizer level and realigned the RHR pump to the normal cold leg injection flow path. As the pressurizer level continued to decrease, Operations personnel initiated additional actions based on applicable abnormal operating procedures. At approximately 0035 EST, Operations personnel initiated a manual Phase A and containment ventilation isolation. A relief valve on the RHR pump discharge piping had opened to relieve pressure in the system and did not reseat. Operations personnel reduced the reactor coolant system (RCS) pressure and stabilized the pressurizer level. The RHR relief valve relieves to the pressurizer relief tank. The root cause of the event was an inadequate procedure revision. The procedure is being revised to provide an appropriate method of venting the RHR discharge piping. Also, the relief valve was replaced.
3272000003 | Sequoyah 1 | 03/21/2000 | 04/19/2000 | ML00370826 | <strong>Reactor Trip Caused from a Detected Loss of Excitation Field to the Main Generator Because of a Design Error</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2000, at 0440 Eastern standard time (EST), Unit 1 experienced an automatic reactor trip. The reactor trip was initiated by a turbine trip which was caused by a detected loss of excitation field to the main generator. The turbine trip signal was caused by the actuation of two protective relays that were installed during the refueling outage. A wiring error contained in the design change package resulted in improper installation in the field. The wiring error resulted in actuation of the relays during unit restart when a loss of excitation condition did not exist. The root cause of the design error was an error by the package preparer that was not detected by the barriers in place to prevent the design deficiency. The design change checking, design verifications, and reviews were not completed to the proper level. The design error was corrected. A standdown meeting, to clarify expectations for design checkers and design verifiers, was held with Design Engineering personnel. A training letter, addressing expectations for design checkers and design verifiers, was issued to the SQN Design Engineering personnel.
3272000004 | Sequoyah 1 | 09/25/2000 | 10/23/2000 | ML00376453 | <strong>Reactor Trip on Low-Low Steam Generator Level as a Result of the Loss of a Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2000, at 1033 Eastern Daylight Time, Unit 1 experienced an automatic reactor trip on low-low steam generator level. The reactor trip was preceded by a turbine runback because main feedwater pump (MFP) 1A tripped on low control oil pressure. Following the 1A MFP trip and turbine runback, the remaining MFP (1B) was not able to provide sufficient feedwater flow to maintain steam generator level, resulting in the automatic reactor trip. The root cause for the turbine runback was lower motor bearing failure on the lA MFP main oil pump, resulting in the motor tripping on thermal overload. The root cause of the reactor trip was incorrect adjustment of the 1B MFP turbine governor, resulting in a lower control signal output and inability of the pump to provide sufficient feedwater flow. The lA MFP turbine main oil pump motor bearing was replaced, the motor tested and returned to service. Calibration methodology of the MFP turbine governor was changed to ensure that during a transient, where one MFP is required to pickup load, the governor valve will open to provide adequate steam flow to run the pump near its maximum speed.
3282000002 | Sequoyah 2 | 01/26/2000 | 02/25/2000 | ML00368650 | <strong>Inoperability of Both Safety Injection Pumps as a Result of Personnel Error During Performance of a Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2000, at 2023 Eastern standard time (EST), Operations entered Limiting Condition for Operation (LCO) 3.5.2.a for removing the 2A-A safety injection pump (SIP) from service for maintenance activities. As part of the maintenance activity, the oil for the 2A-A SIP motor was to be changed out. On January 26, 2000, at approximately 0220 EST, Operations was notified that Maintenance personnel had changed out the oil in the 2B-B SIP motor. Operations personnel entered LCO 3.0.3 (effective at 0039 EST) for both trains of emergency core cooling subsystems being inoperable at the same time. During the time of the oil change out, both SIPs were considered inoperable. The cause of the oil change on the wrong SIP motor was human performance error. There was a lack of self checking, as well as a lack of peer checking, to ensure that the correct component was identified prior to performance of work. The involved individuals were coached and counseled on the failure to perform self checking, as well as a lack of peer checking.
3282000003 | Sequoyah 2 | 11/09/2000 | 12/08/2000 | ML00378078 | <strong>Missed SI - Failure to Perform Containment Sump Level Instrument Channel Functional Tests (CFTs) on Containment Sump Level Channels</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2000, with Unit 2 in a refueling outage, it was discovered that the four surveillance instructions (SIs) for the Containment Sump Level Instrument CFTs had not been performed as required by Technical Specifications 4.3.2.1.1. These SIs were erroneously entered as "complete" in the SI Program database on June 8, 2000. This inadvertent status change resulted in removal of the CFTs from the daily schedule for the August 21, 2000 work week. This updated daily schedule was used to determine which SIs were to be performed. The CFT SIs were immediately performed upon identification. Each Containment Sump Level Instrument Channel performed satisfactorily and was determined to be operable. The root cause of this event was a personnel error resulting in an inadvertent status change of four scheduled SIs to "complete". The involved individual was coached and counseled. The SI database was reviewed and the review did not identify any other missed surveillances. The SI Program database was modified to ensure a SI schedule date cannot be inappropriately changed.
3282000004 | Sequoyah 2 | 11/17/2000 | 12/15/2000 | ML00378061 | <strong>Reactor Trip Resulting from a Fault in a Main Transformer Caused by a Failed Bushing</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2000, at 0842 Eastern standard time (EST), Unit 2 experienced an automatic reactor trip. The reactor trip was initiated by a turbine trip, which was caused by the actuation of the sudden pressure relays on the `C' phase main transformer. The main control room operators took appropriate actions to stabilize the reactor in hot standby (Mode 3). An inspection of the main transformer revealed that a fault had occurred in the transformer. The electrical fault in the transformer was caused by a failure of a 24-kV bushing. A spare main transformer was placed in service for the faulted transformer, and the unit was returned to service.
3312000001 | Duane Arnold | 01/05/2000 | 02/04/2000 | ML00368158 | <strong>Automatic Reactor Scram While Restoring Level Transmitter to Service</strong><br /><i>Abstract:&nbsp;</i>On January 5, 2000, with the plant operating at 100% power, an automatic scram occurred when technicians attempted to restore a level transmitter to service after calibration. All control rods inserted, and primary containment isolations (Groups 2, 3 and 4) occurred as expected. A partial Group 5 isolation also occurred. Reactor water level control following the scram was complicated by a positive bias on a feedwater regulating valve and a recirculation motor generator runback failure, but vessel level and pressure were maintained within safe operating limits. There were no emergency core cooling system actuations and no safety relief valve openings. The plant was restarted on January 9, 2000. This event had no effect on the safe operation of the plant. The scram signal resulted from a false low level signal generated due to an inadequate instrument restoration process. Corrective actions will include enhancements to training and calibration practices, and procedure revisions.
3312000002 | Duane Arnold | 06/23/2000 | 05/25/2001 | ML01150014 | <strong>Turbine Trip and Reactor Scram Due to Main Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2000 at 1616, with the reactor operating at 100% power, the Duane Arnold Energy Center (DAEC) experienced a main generator lockout which caused a turbine trip and reactor scram. The plant and control room operator responses were as expected. The safety consequences were minimal. The cause of the event was a main generator backup lockout due to a unit differential current trip. Initial testing on the associated current transformers did not indicate the existence of equipment malfunction. Other potential causes of the transient, including lightning strike, were investigated and additional equipment walk downs and testing were performed. No definitive cause was determined. During the subsequent plant startup the generator output current transformer, which provides an input to the unit differential current relay, failed approximately 30 minutes after the generator was synchronized to the grid. Apparently, a loose connection on one of the current transformer secondary leads caused an increased voltage potential, which resulted in an arc that destroyed the lead.
3312000003 | Duane Arnold | 07/18/2000 | 08/17/2000 | ML01289041 | <strong>Actuation of Engineered Safety Feature, Primary Containment Isolation, From a Planned Fuse Removal</strong><br /><i>Abstract:&nbsp;</i>On 7/18/2000 at approximately 1212, during preplanned maintenance activities on the 'B' standby gas treatment system (SBGTS) logic, an unexpected, invalid ESF actuation occurred. The plant was at 100% power operation, 1658 MWth, and Limiting Conditions for Operation (LCO) were in place for 'B' SBGTS and CARDOX. Specifically, a planned fuse removal resulted in an unexpected isolation of a containment nitrogen makeup valve, CV4311, and the 'B' recirculation mini-purge valve, CV1804B, in response to a Primary Containment Isolation System (PCIS) actuation. All isolations performed as designed. The Group III isolation was reset at 1541 on 7/18/2000 and the isolated valves were subsequently re-opened. The cause of this event was inadequate planning of the work activity. Corrective actions will include a review of the planning process for work orders that involve plant manipulations. This event had no effect on the safe operation of the plant.
3332000001 | FitzPatrick | 01/06/2000 | 02/03/2000 | ML00368145 | <strong>Missed Surveillance Requirement due to Error in Reading the Surveillance Test Schedule</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2000 at 0400, with reactor power at 100 percent, it was determined that Surveillance Test (ST)-29C, "Reactor Protection System (RPS) Channel Switch Functional Test" had not been performed within the test frequency required by the plant's Technical Specifications. ST-29C had been completed successfully on January 6, 2000 at 0303. The cause of this event was an inconsistency in the way surveillance test frequency requirements were translated from a surveillance test tracking database to a work scheduling database, and reviews of reports from these databases failed to identify the discrepancy. Corrective actions include a review of all scheduled surveillance activities to verify that no other scheduled surveillance activities had exceeded their required due dates, a formal critique with lessons learned and a change to the procedure used by the Work Week Manager to provide direction regarding what data sources are to be used to check work schedule surveillance test due dates.
3332000003 | FitzPatrick | 04/01/2000 | 04/28/2000 | ML00371030 | <strong>Reactor Scram Due to Manual Trip of the Main Turbine</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2000, with the reactor at approximately 25 percent power an automatic scram occurred due to a manual trip of the main turbine. Planned maintenance was in progress to repair a small main steam drain line pipe leak, which required the condenser air ejector recombiner to be removed from service. At approximately 17:04 when the recombiner was removed from service, the recombiner bypass valve, 01-107AOV-104, failed closed, isolating the condenser off gas system from the main condenser. This caused a lowering trend in condenser vacuum. Operators entered the associated Abnormal Operating Procedure AOP-31. At approximately 17:31 condenser vacuum had degraded to the "manual turbine trip region" contained in Figure 1 of AOP-31. The CRS assumed the reactor protection system turbine trip scram was bypassed, based on current power level, ordered a manual trip of the turbine. Upon initiation of the turbine trip an automatic reactor scram occurred from the turbine trip scram logic. The associated transient is bounded by analysis contained in the Final Safety Analysis Report. Corrective actions included repair of the failed valve, an Equipment Failure Evaluation, and evaluations of additional training required to improve some identified personnel performance errors.
3332000005 | FitzPatrick | 04/13/2000 | 05/15/2000 | ML00371667 | <strong>One of Two 115KV Reserve Power Lines Inoperable Concurrent With One Emergency Diesel Generator Train Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2000 at 08:25 hours, with Emergency Diesel Generator (EDG) System train "B" inoperable due to scheduled maintenance on the "B" train of the Emergency Service Water (ESW) System, a Niagara Mohawk Power Corporation (NMPC) worker inadvertently opened an off site 115KV breaker which resulted in rendering inoperable one of two auxiliary 115KV supply lines to FitzPatrick. The concurrent condition of one train of the EDG System inoperable, and one incoming 115KV emergency AC supply power line inoperable meets the provisions of Technical Specifications (T.S.) section 3.0.C, requiring that the plant be placed in COLD SHUTDOWN within the following 24 hours. The error was promptly identified by NMPC, the breaker closed, and power restored to the reserve line within 4 minutes. At the time of the event, FitzPatrick was operating at approximately 96 percent rated power with the mode switch in the RUN position. The cause for the event was insufficient knowledge of the requirements for manipulation of the breaker by an NMPC worker, as identified by NMPC. Corrective actions included prompt restoration of power to the 115KV line and counseling of the worker involved. Both actions were completed by NMPC. No specific corrective actions were taken by the Authority.
3332000006 | FitzPatrick | 06/26/2000 | 07/26/2000 | ML00373723 | <strong>RPS Motor Generator Voltage Regulator Failure Causes Loss of "A" RPS Bus and ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 06/26/2000 at 23:21 with the reactor at approximately 100 percent power, the "A" Reactor Protection System (RPS) bus was de-energized due to an unplanned loss of power. The Electrical Protection Assembly (EPA) breakers that supply the RPS bus were found in a tripped condition. This condition re-occurred on July 3, 2000, with the same half scram and isolations. In both events Operations transferred the RPS bus to the alternate transformer supply, and reset the half scram and isolations. Isolations and initiations as a result of the loss of power consisted of reactor building isolation, standby gas treatment initiation, reactor water cleanup isolation, isolation of primary containment drains, and containment vent and purge isolation. Troubleshooting revealed that RPS motor-generator voltage regulator instability caused the output voltage to dip below the EPA breaker undervoltage trip setting. The safety significance was minimal, a plant transient did not occur and the plant equipment responded as designed.
3332000007 | FitzPatrick | 07/27/2000 | 08/24/2000 | ML00374564 | <strong>Failure to Satisfy Technical Specification Table 4.2.8 Torus Bulk Water Temperature Calibration Requirement Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2000 at 1205, with reactor power at 100 percent, it was determined that the most recent performance of Instrument Surveillance Procedure (ISP)-28, "SUPPRESSION POOL TEMPERATURE CALIBRATION", conducted on September 11, 1998, did not satisfy Technical Specification requirements. The procedure permitted performing a calibration check of torus (a.k.a., suppression pool) bulk water temperature instrumentation at normal torus operating temperature in lieu of performing a calibration over the entire range of operability of the instrumentation. The cause of this event is a procedural inadequacy, in that a procedure step permitted skipping the calibration section of the procedure if the calibration check was satisfied. A contributing cause was inadequate change management in that an editorial change to ISP-28 introduced the wording that permitted skipping a critical part of the procedure. ISP-28 was revised, eliminating the wording that allowed skipping the calibration section of the procedure and incorporating additional analog subcomponents identified during evaluation of this event. The torus bulk water temperature instrumentation was calibrated using the revised ISP. Additional corrective actions include a review of analogous ISP's for similar conditions, and discussion of this event with I&C personnel.
3332000008 | FitzPatrick | 07/28/2000 | 10/02/2000 | ML00375739 | <strong>Reactor Water Recirc Speed Control Mechanical Stops Set Higher Than Value Assumed in Core Operating Limits Report</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2000, with the reactor at approximately 100 percent power, it was discovered that the mechanical stop setting for the "A” Reactor Water Recirculation (RWR) pump speed limiter exceeded the value assumed in the calculation for the flow dependent Minimum Critical Power Ratio (MCPR) contained in the Core Operating Limits Report (COLR). On July 29, the "B" RWR pump mechanical stops were also discovered to be set above 102.5 percent. If a RWR pump transient such as a runaway RWR flow from a low flow condition is postulated, the flow dependent MCPR may be exceeded. This could result in exceeding the Safety Limit MCPR. This condition could have put the plant outside of its design bases and is being reported per lOCFR50.73(a)(2)(ii)(B). Review of plant operating history determined that the plant had not operated in a condition that would have resulted in exceeding Operating Limit MCPR and thus would not have exceeded the SLMCPR. Therefore, the safety significance was determined to be minimal. The cause was determined to be inadequate post work testing due to failure of the post work testing determination process and poor communications between work groups. Corrective actions include: resetting and verifying the mechanical stops set at 102.5 percent, completion of the Root Cause Anal sis, planned revision to the Instrument Maintenance Procedure, and reinforcement of expectations with regard to ensuring all affected functions are checked during post-work testing following corrective maintenance.
3332000009 | FitzPatrick | 08/23/2000 | 09/22/2000 | ML00375377 | <strong>HPCI and A&B Core Spray Systems Inoperable Due to Lack of Proper Environmental Qualification on Minimum Flow Valve Control Circuits</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2000 the plant was operating at 100% power. At 1615, both (A & B) divisions of the Core Spray (CSP) system and the High Pressure Coolant Injection (HPCI) system were declared inoperable when it was determined that certain wire and wire terminations of unknown environmental qualification (EQ) were installed in the control circuits for the minimum flow valves for the A & B CSP pumps as well as the HPCI pump. The condition was corrected by replacing the unqualified wire and wire terminations in the effected circuits with properly qualified wire and wire terminations. The A & B CSP systems were declared operable at 0246 on August 24, 2000 and the HPCI system was declared operable at 1000 on August 26, 2000.
3332000010 | FitzPatrick | 08/27/2000 | 09/26/2000 | ML00375687 | <strong>Departure From Technical Specifications to Facilitate Controlled Shutdown Under Notice of Enforcement Discretion (NOED)</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2000 the plant was operating at approximately 50% power with the B Reactor Feed Pump (RFP) out of service. At approximately 0930 a leak on a hydraulic control oil fitting on the Electro-Hydraulic Control (EHC) system for the main turbine was identified. Concurrent with this hydraulic oil leak, but apparently unrelated, a steam leak had developed at the weld joint on the instrument line for the A RFP suction flow meter. A controlled plant shut down was initiated due to these plant conditions. Enforcement Discretion was requested to allow transitioning from the Run Mode to the Startup mode without certain neutron monitoring instrumentation operable due to lack of required surveillance testing. Enforcement Discretion was granted and a proposed amendment to the Technical Specifications was submitted.
3332000011 | FitzPatrick | 08/28/2000 | 02/28/2001 | ML01066019 | <strong>Shutdown Cooling Suction Valve Isolation When Securing Reactor Recirculation Pumps</strong><br /><i>Abstract:&nbsp;</i>This report is provided as a supplement to previously submitted LER-00-011. This event is not reportable under the current requirements. At 0840 hours on August 28, 2000, the plant was shut down with a cooldown in progress. Shutdown cooling suction piping had been filled and vented, and shutdown cooling suction valves (10MOV-17 and 10MOV-18) were open in preparation for entering shutdown cooling. At 0851 hours, shortly after securing recirculation (RWR) [AD] pumps, 10MOV-17 was observed to have closed. Investigation revealed tripped relays associated with a shutdown cooling isolation for the 10MOV-17 valve. Analogous relays for 10MOV-18 were not tripped and 10MOV-18 remained open. Reactor pressure was confirmed to be approximately 2 psig. No annunciators or indications were received which would indicate a shutdown cooling isolation. The isolation was attributed to a pressure transient associated with securing RWR pumps. The isolation signal was reset, 10MOV-17 was reopened, and the plant placed in shutdown cooling without further incident. The reason the isolation only occurred for the 10MOV-17 and not also for the 10MOV-18 valve is discussed under Analysis of the Event.
3332000012 | FitzPatrick | 09/14/2000 | 02/28/2001 | ML01066023 | <strong>Failed Primary Containment Isolation System Relay Resulting in Drywell Sump Isolation Valve Closure (Isolation)</strong><br /><i>Abstract:&nbsp;</i>This report is provided as a supplement to previously submitted LER-00-012. The event is not reportable under current requirements. At 2333 hours on September 14, 2000, with the plant operating at 100% power, control room annunciator alarms were received indicating ESF isolation of Drywell Equipment Drain Isolation Valve 20MOV-94 and Drywell Floor Drain Isolation Valve 20MOV-82. Investigation determined that the cause of the isolation was failure of relay 16A-K61. Isolation closure of the subject valves does not permit pumping drywell sumps, rendering the Primary Containment Sump Monitoring System inoperable and placing the plant in a 24 hour LCO Action, as required by Technical Specification 3.6.D.5. At 1038 hours on September 15, 2000, a temporary modification was installed, allowing valves 20MOV-94 and 20MOV-82 to be opened under administrative controls to permit pumping drywell sumps, restoring Primary Containment Sump Monitoring System operability. LCO Action 3.6.D.5 was exited at 1955 hours. The coil for relay 16A-K61 was subsequently replaced and the temporary modification removed. An Equipment Failure Evaluation (EFE) performed on the failed relay coil determined the cause to be an open circuit due to age related failure.
3332000013 | FitzPatrick | 10/02/2000 | 10/30/2000 | ML00376700 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Closed Steam Supply Valve</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2000 the plant was at 100% power. An engineering review determined that the steam supply inboard isolation valve (23MOV-15) for the High Pressure Coolant Injection System (HPCI) may not have fully closed against design basis differential pressure (dP). The HPCI steam supply inboard isolation valve was declared inoperable as a containment isolation valve and manually closed in accordance with Technical Specification 3.7.D.2 at 1220 on October 2, 2000. This action rendered the HPCI system inoperable. This event therefore constituted a condition (lack of steam to HPCI) that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. Subsequent engineering review of test data taken in 1995 for this valve indicated that the valve was in fact, operable. The HPCI system was therefore declared operable at 1547 on October 2, 2000. Corrective actions include procedure revisions, an operating experience notification and preparation of an Engineering Design Standard.
3332000014 | FitzPatrick | 10/13/2000 | 11/13/2000 | ML00377045 | <strong>Failure to Meet Standby Gas Treatment System Technical Specifications Required Action Statement Test Interval Requirement</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2000, at 0905 hours, with reactor power at 0 percent and the mode switch in the REFUEL position, it was determined that Surveillance Test Procedure ST-7C, "One Circuit of Standby Gas Treatment System Inoperable Test" had not been performed within the interval required by the plant Technical Specifications (TS). Specifically, on October 12, 2000, at approximately 0130 hours, Standby Gas Treatment (SGT) System train B was removed from service. In preparation for its removal, operators satisfied the TS Required Action Statement for SGT System train A by successfully completing ST-7C at 0115 hours. TS 4.7.B.2 requires when one SOT System train becomes inoperable, the operable train shall be verified to be operable immediately and daily thereafter. ST-7C was not completed again until 0918 hours on 10/13100. The TB required test interval requirement (including the allowable 25 percent extension) was exceeded by approximately 2 hours. The cause of this event was personnel error. This non-routine surveillance test had not been added to or included in the operator's daily surveillance checks. Corrective actions included counseling the individuals involved, completing a review of all routine STs and active Limiting Conditions for Operation SLCOs) to ensure there were no other overdue surveillance tests, and Operations Management reviewing this event with the operating shifts.
3332000015 | FitzPatrick | 10/18/2000 | 07/01/2002 | ML02191037 | <strong>Containment Leakage Rate Exceeds Authorized Limits</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2000, following completion of Local Leak Rate Testing (LLRT) of valves 29AOV-80D (inboard) and 29AOV-86D (outboard) Main Steam System isolation valves (MSIVs), it was determined that the Primary Containment Type B and Type C as-found running total minimum-pathway leakage rate had exceeded the maximum allowable limit of 320 standard liters per minute (SLM) specified in Technical Specifications (TS) Section 6.20. When leak tested in combination (applied test pressure between the inboard and outboard MSIV), test results demonstrated seat leakage in excess of 320 SLM. At the time of the testing, the mode switch was in the REFUEL position while the plant was conducting Refuel Outage 14. The excessive leakage rate of inboard MSIV 29AOV-80D was attributed to valve disc to seat misalignment. The excessive leakage rate of outboard MSIV 29AOV-86D was attributed to seat scoring in the valve seat area, as a result of debris caught between the sealing surfaces. The failed valves were repaired and retested satisfactorily prior to plant startup. An equipment failure evaluation was performed for the valves that failed testing. An operability review was performed to support operation through the remainder of the operating cycle. Additional valve modifications and improvements, and improved outage work management controls are being planned to enhance MSIV performance and test accuracy.
3332000016 | FitzPatrick | 11/20/2000 | 08/03/2001 | ML01225022 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Water in Turbine Exhaust Piping</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2000, at 2310 hours, with reactor power at approximately 72 percent, it was discovered that the High Pressure Coolant Injection (HPCI) System turbine exhaust drain pot level switch 23LS-98 was inoperable. Prior to the level switch failure, HPCI turbine steam supply isolation valve 23MOV-14 was experiencing valve seat leakage. These concurrent conditions resulted in water accumulation in the HPCI turbine exhaust line and rendered the HPCI System inoperable. Immediate corrective actions included repairing level switch 23LS-98 and returning it to an operable condition, successfully completing Surveillance Testing of the HPCI System, and returning the HPCI System to an operable status. Post event analysis determined the mechanistic cause of the event to be a combination of corrosion and misalignment in the level switch float coupled with loss of (permanent) magnetism in one of the internal switch components. This analysis also identified a staff knowledge deficiency regarding the details of the switch internal component configuration and theory of operation. A contributing cause of the event was inadequate compensatory measures to assure HPCI operability given the 23MOV-14 seat leakage.
3342000001 | Beaver Valley 1, Beaver Valley 2 | 01/21/2000 | 02/17/2000 | ML00368691 | <strong>Inadequate Guidance Proivided to Operators Regarding Post-DBA operation of SLCRS</strong><br /><i>Abstract:&nbsp;</i>During the evaluation of a separate Condition Report involving the Beaver Valley Power Station (BVPS) Unit 1 Supplemental Leak Collection & Release System (SLCRS), it was discovered that the control room operators did not have sufficient guidance for ensuring that the safety related SLCRS would be operating following an accident. SLCRS operation post-DBA ensures that Engineered Safety Features (ESF) leakage following the postulated DBA LOCA will not cause the total calculated dose to exceed 10CFR100 limits and also provides post-DBA cooling air flow for the ESF pump motors. Thus post-DBA SLCRS operation is needed to maintain plant design basis conditions. Though SLCRS exhaust fan operation is credited post-DBA, operator guidance did not ensure that SLCRS would be available in all conditions where SLCRS flow is required following a DBA. This lack of sufficient administrative controls would potentially not ensure adequate post-DBA SLCRS operation, when required. This is a condition beyond the plant design basis. Operation of BVPS Unit 1 and Unit 2 in a condition which is beyond the design basis of the plant is reportable pursuant to 10CFR50.73(a)(2)(ii)(B). A cause of this event is a failure to translate design requirements for the BVPS Units 1 and 2 SLCRS into appropriate administrative controls (e.g., Emergency Operating Procedures, EOPs) to ensure mitigation of a DBA. The root cause for this event is a lack of understanding regarding the design bases and the time required for SLCRS to meet design bases analytical assumptions. EOP E-0 for BVPS Unit 1 and Unit 2 have been revised to ensure at least one SLCRS fan is running during DBA conditions.
3342000002 | Beaver Valley 1 | 02/08/2000 | 04/27/2000 | ML00371202 | <strong>Condition Outside Design Basis for One Train of River Water System Inoperable</strong><br /><i>Abstract:&nbsp;</i>During a routine surveillance on the BVPS Unit No. 1 Reactor Plant River Water (RPRW) System B Train pump at 1209 on 2/8/2000, the pump unexpectedly tripped approximately three seconds after a start signal due to an overcurrent condition. Technical Specification 3.7.4.1 was entered due to having only one River Water System pump operable. RPRW pump WR-P-1C (swing pump) was then aligned to the B train and started at 1716 on 2/8/2000. This pump also tripped approximately three seconds after a start signal due to an overcurrent condition. A subsequent evaluation determined that the two overcurrent trip conditions on the RPRW pumps were a result of physical contact between the rotating element (impeller) and the lower casing liner of the pumps. The cause of this condition was due to differential thermal expansion between the pump shaft and the pump casing as a result of an elevated seal injection water temperature. This delta temperature elongated the pump shaft to the point of physical binding. Normally the RPRW Pumps' seal water is supplied by the Filtered Water System at approximately the same temperature as the Ohio River. At the time of the condition, the seal water was being supplied by the Filtered Water System, which was in an abnormal configuration that created the elevated water temperature. This condition is reportable pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition that is outside the design basis of the plant because one train of a two train safety related system (required to be operable per Technical Specification 3/4.7.4.1) was incapable of performing its design safety function for an extended period of time during operation. This seal water supply design defect had the potential to render non-operating RPRW pump(s) inoperable. Therefore this design defect could create a safety hazard, and is also reportable pursuant to 10 CFR 21 requirements. This report satisfies the notification and reporting requirements of 10 CFR Part 21 per the provisions of 10 CFR 21.2(c). An additional material condition that occurred on 3/3/2000 provided further basis that the BVPS Unit 1 seal water design for the RPRW Pumps may not have been sufficient to meet the design basis of the plant.
3342000003 | Beaver Valley 1 | 03/23/2000 | 04/24/2000 | ML00370891 | <strong>Failure to comply with Technical Specifications Due to Inoperbility of One Subsystem of the Containment Recirculation Spray System</strong><br /><i>Abstract:&nbsp;</i>On 3/23/2000 while in Mode 5 during refueling outage 1R13, ASME Section XI in-service testing (IST) of BVPS Unit 1 Inside Containment Recirculation Spray Pump RS-P-1A revealed that the pump discharge pressures and flows were below the minimum test acceptance criteria. Slightly higher than normal pump motor amperage and vibration were also noted. The pump was not required to be operable during Mode 5. The pump was disassembled and an inspection revealed two 2" X 4" wooden blocks (each approximately 6" long) on the bottom of the pump suction well and a fragmented piece of wood (approximately 6" long) in the pump second stage impeller. This event is reportable per 10CFR50.73(a)(2)(i)(B). The root cause of the wood in the pump suction well and impeller is inadequate foreign material exclusion (FME) control during installation of a design change package in February 1982. The wood was removed and two pump wear rings and one shaft bushing were replaced due to damage. Additional pump components were also replaced as part of good maintenance practices. The pump suction well of the other inside containment recirculation spray (RS) pump and the suction piping of the outside RS pumps and the low head safety injection pumps were inspected. Subsequent testing of RS-P-lA showed the pump met IST acceptance criteria and it was determined to be operable. The BVPS Unit 2 Containment sump and suction piping will be inspected during the next refueling outage (2R08).
3342000004 | Beaver Valley 1 | 03/30/2000 | 04/27/2000 | ML00371202 | <strong>Inadvertent ESF Actuation Due to Loss of Power to 4KV Emergency Bus</strong><br /><i>Abstract:&nbsp;</i>At 1204 on March 30, 2000, an 18 month automatic-load sequencing operating surveillance test was being conducted on the No. 1 Emergency Diesel Generator (EDG) during a refueling outage at the BVPS Unit No. 1. The power to the 4KV 1AE Emergency Bus was being supplied by the operating No. 1 EDG and the 4KV 1AE Emergency Bus was separated from the offsite power sources. Checks of the EDG local alarms were in progress. The EDG output breaker 1E9 unexpectedly tripped open and reclosed three times before the breaker remained open, keeping the 4KV Emergency Bus 1AE de-energized. The opening(s) of the EDG breaker caused the 4KV 1AE Emergency Bus to be de-energized. This produced a valid automatic Engineered Safety Features (ESF) actuation signal of the No. 1 EDG, even though the EDG had already been running. The Control Room operators entered the Abnormal Operating Procedure for loss of a 4KV Emergency Bus and took appropriate immediate actions. Technical Specification (TS) 3.4.1.3 was entered due to Residual Heat Removal System Train A being inoperable. The redundant train's Residual Heat Removal System cooling and spent fuel pool cooling remained available for service. The reactor coolant and spent fuel pool temperature remained constant. At 1228, power was restored to the 4KV 1AE Emergency Bus from the off site power source. With the normal power for Residual Heat Removal System Train A restored, TS 3.4.1.3 was exited. The receipt of a valid automatic actuation of an EDG start signal is an automatic ESF train actuation and is being reported pursuant to 10CFR50.73(a)(2)(iv) as an automatic actuation of an ESF. The cause of this event was inadequate human performance. This was concluded based on the system operation and EDG/output breaker response matching an incorrect landing of the test jumper lead on Terminal No. 18 rather than on Terminal No. 19 in the EDG local alarm cabinet. There were minimal safety implications to the health and safety of the public.
3342000005 | Beaver Valley 1 | 04/17/2000 | 05/16/2000 | ML00371783 | <strong>Manual Reactor Trip in Response to Degraded Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>At 1309 hours on April 17, 2000, the Unit 1 reactor was manually tripped from approximately 100% power due to degrading condenser vacuum. The degraded condenser vacuum was caused by inadequate steam supply to the condenser air ejectors due to the malfunctioning of auxiliary steam pressure control valve PCV-1AS-100. The Unit was manually tripped after reaching the condenser vacuum low-low alarm setpoint. Unit response to the reactor trip and Unit recovery were uncomplicated. PCV-lAS-100 was repaired, tested, and returned to service. As part of corrective actions to this event, an evaluation of I&C task analysis documentation, and maintenance documentation of as found and as-left conditions will be performed. Performance of a manually initiated reactor trip constitutes a manual actuation of an engineered safety feature and is reportable per 10 CFR 50.72(b)(2)(ii), and 10 CFR 50.73 (a) (2)(iv). The calculated risk associated with this event is small.
3342000006 | Beaver Valley 1 | 07/05/2000 | 02/16/2001 | ML01058028 | <strong>Reactor Trip/Turbine Trip Due to Turbine EH Loss of Control Power</strong><br /><i>Abstract:&nbsp;</i>At 1305 on July 5, 2000, Beaver Valley Power Station (BVPS) Unit 1 experienced a reactor trip from 100% power due to the four (4) Main Turbine throttle valves going closed. There were no turbine related activities ongoing at the time. The Sequence of Events recorder indicated a momentary loss of DC control power (18 milliseconds) to the Analog Electrohydraulic (AEH) control system associated with the Main Turbine. One second later, a computer point indicated that a Throttle Valve/Governor Valve transfer had occurred. All four Main Turbine throttle valves closed between 10 and 13 seconds after the momentary loss of DC power. Following initiation of the automatic reactor trip signal, all control rods fully inserted and the Unit was stabilized in mode 3 with decay heat being removed via the normal post-reactor trip method of using the steam bypass system into the Main Condenser. There were no radiological releases. The throttle valve mixing amp 3 card was the only failed component found in the AEH control cabinet. Though initially thought to be the cause, subsequent evaluation showed this failure was not responsible for the turbine trip. A new mixing amp 3 card was installed and tested satisfactorily with the original DC power supplies. It is known that the reactor trip was caused by a failure in the AEH control cabinet, though no specific cause has been identified.
3342000007 | Beaver Valley 1 | 08/28/2000 | 10/20/2000 | ML00376537 | <strong>Technical Specification Non-Compliance Due to Misinterpretation of Containment Isolation Valve Requirements for GDC 57 Penetrations</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2000, at the Beaver Valley Power Station (BVPS) Unit No. 1, routine maintenance work was performed on a containment isolation valve (CIV) in a River Water System line for approximately 30 hours. This containment isolation valve is on a penetration where the inside boundary is a closed system (pursuant to General Design Criteria 57). This work intermittently removed the control room's capability to remotely operate this valve. Therefore, the valve was declared inoperable and the CIV technical specification's action entered. Based on operations and Licensing review of a docketed NRC correspondence for a similar situation at another facility, the Action statement was interpreted to require flow be terminated through the closed system boundary to make it completely passive. It was subsequently determined that the NRC correspondence was misapplied and that, although the Updated Final Safety Analysis Report and Licensing Requirements Manual referred to the inside containment isolation valve as the closed system, the closed system could not be considered an automatic valve with regard to meeting the CIV Technical Specification's Action statement. Thus, this action constituted a condition prohibited by Technical Specifications since the Action statement was not fulfilled during the maintenance work and is reportable pursuant to 10 CFR 50.73 (a)(2)(1)(B). The safety significance for this event was small.
3352000001 | St. Lucie 1, St. Lucie 2 | 03/09/2000 | 04/07/2000 | ML00370343 | <strong>Outside Design Bases Appendix R Hi-Lo Pressure Interface and Separation Issues</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2000, St. Lucie Units 1 and 2 were in Mode 1 operation at 100 percent reactor power. As part of the continuing resolution of fire protection program issues identified during a follow-up Fire Protection Functional Inspection at St. Lucie in December 1999, FPL performed a review of certain Appendix R circuit separation and protection issues for the Unit 1 & 2 containments. The identified issues include hi-lo pressure interface issues with power operated relief valves and the Unit 2 shut down cooling valves and lack of separation or protection to prevent loss of function of redundant components during a fire. FPL determined that the affected systems, structures, and components were operable in accordance with the guidance provided in Generic Letter 91-18. Where appropriate, additional compensatory measures were implemented to enhance safe shutdown capability. Long term corrective actions include correcting the licensing basis and/or physical modification to the plants.
3352000002 | St. Lucie 1 | 03/30/2000 | 04/25/2000 | ML00371085 | <strong>Missed Surveillance and Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2000 St. Lucie Unit 1 was at 100 percent power. Operations personnel determined that a required weekly surveillance was not performed within the appropriate grace time. The subject surveillance verifies that the safety related 4160 volt buses are aligned to or capable of receiving power from off-site power sources via the associated startup transformer. The review of the chronological logs indicated the surveillance was performed satisfactorily at 0230 on April 1, 2000, in preparation for an unrelated 1A emergency diesel generator code run. However, the previously recorded performance of this weekly surveillance was on March 21, 2000. With the addition of the 25% grace period, this surveillance should have been conducted no later than March 30, 2000. This event was caused by personnel error when procedural requirements were not met due to inattention to detail by the control room staff. Immediate corrective actions included the issuance of a night order to reinforce management expectations. This event is under consideration for inclusion into the continuing operator training program.
3352000003 | St. Lucie 1, St. Lucie 2 | 10/25/2000 | 11/22/2000 | ML00377188 | <strong>Technical Specification Control Room Minimum Staffing Level Not Met</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2000, St. Lucia Units 1 and 2 were in Mode 1 at approximately 100 percent reactor power. St. Lucia determined that the nuclear watch engineers did not meet the proficiency watch 10 CFR 55 requirements for maintaining an active license. Historically, when the assistant nuclear plant supervisor performed duties outside of the control room, the nuclear watch engineer temporarily relieved the assistant nuclear plant supervisor and assumed command and control functions for the shift. The cause of this event was a lack of proper understanding of the application of 10 CFR 55.53e as it applies towards maintaining active operator licenses. Corrective actions included placing nuclear watch engineers and senior reactor operators that are not assigned specific technical specification shift staffing positions in non-qualified status for SRO duties. Additionally, all licensed operators must document the required shift watches on Appendix B of AP 0005720, "Licensed Operator Requalification Program."
3352000004 | St. Lucie 1 | 11/15/2000 | 12/15/2000 | ML00377953 | <strong>Pressurizer Level Instrumentation Conduit Separation Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2000, St. Lucie Unit 1 was in Mode 1 at approximately 100 percent reactor power. FPL completed a reanalysis of fire protection separation requirements for all circuits required for post-fire safe shutdown in containment. The only components identified with separation issues that had the potential to lose a post-fire safe shutdown function, was pressurizer level instrumentation. Inadequate separation for the pressurizer level circuits exists between radius lines 1 and 3 at the end of the containment annulus area. The cause of this event is that the design basis for conduit separation was not adequately translated to the field during the original Appendix R plant backfit modification activities. FPL determined that this 10 CFR 50 Appendix R noncompliance does not adversely affect the reasonable assurance of safety conclusions for the fire protection program. FPL will either design and implement modifications for the pressurizer level instrumentation conduit to resolve the separation issue or initiate a licensing action to resolve this discrepancy.
3362000001 | Millstone 2 | 01/27/2000 | 02/24/2000 | ML00369055 | <strong>Manual Reactor Trip Due to Secondary System Transient</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2000 at approximately 1427 hours with the unit in Mode 1 at 100 percent power, a manual reactor trip was initiated due to a rapid decrease in the "B" Steam Generator (SG) level to approximately 57 percent and the trip of a SG feedwater pump. The plant response was uncomplicated with safety systems performing as expected. The plant was stabilized at normal post trip parameters (Mode 3) and operating shift personnel reacted appropriately. Operators manually initiated the auxiliary feedwater system to restore SG water levels. It was determined that this event was caused by the loss of all heater drain flow to the suction of the SG feedwater pumps as a result of bulk flashing in the heater drain tank. As event precursors, it was determined that the transient was initiated due to the restoration of the 2A feedwater heater's sight glass causing oscillations in the feedwater control system that adversely affected the systems' ability to recover from the transient. Also, it was concluded that the heater drain tank vent control valve 2-HD-104 control logic wiring did not permit the valve to function properly in order to mitigate the consequences of a loss or rapid reduction of extraction steam pressure on the heater drain tank. Completed corrective actions include optimizing the feedwater heater system performance by improving the stroke time for the level controller valve, and correcting the control logic for 2-HD-104 such that the valve will close to prevent depressurization of the heater drain tank.
3362000002 | Millstone 2 | 02/08/2000 | 03/07/2000 | ML00369386 | <strong>Technical Specification Surveillance Requirement of Cask Crane Was Not Performed</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2000 at 1130, it was discovered that the Technical Specification Surveillance Requirement (SR) for Technical Specification (TS) 3.9.7, "Crane Travel - Spent Fuel Storage Pool Building," was not performed. A prerequisite of the Spent Fuel Pool Handling Operations procedure called out testing of Cask Crane Interlock within 72 hours prior to initiation of irradiated fuel handling operations. This prerequisite was not performed. Subsequent to this event, TS 3.9.7 was relocated to the Technical Requirement Manual upon receiving the Nuclear Regulatory Commission's approval on February 10, 2000. The cause of the event was a deficiency in the TS. The TS Applicability and SR did not meet the intent of the TS. As a result of this event, the Technical Requirement corresponding to "Crane Travel - Spent Fuel Storage Pool Building" in the Technical Requirement Manual will be revised specifically to address the Cask Crane, clarify Applicability, and remove the conflict between Applicability and SR. Additionally, an interim administrative control was implemented to ensure that the Technical Requirement is satisfied.
3362000003 | Millstone 2 | 02/11/2000 | 03/10/2000 | ML00369427 | <strong>Manual Reactor Trip After Two Control Element Assemblies Unexpectedly Drop into the Core</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2000 at approximately 1346 hours with the unit in Mode 1 at 96 percent power, a manual reactor trip was initiated during Control Element Assembly (CEA) insertion testing after the second of two CEAs unexpectedly dropped into the core. Immediately prior to the trip, Operators were reducing power in accordance with Technical Specification Action Statement 3.1.3.1(e) after the first CEA had dropped into the core. During this power reduction action, the second CEA dropped into the core approximately 17 minutes after the first. As directed by procedure, the Operators then manually tripped the reactor immediately after the second CEA inserted at which time all remaining CEAs inserted completely into the core. The Auxiliary Feedwater System automatically initiated as a result of the trip and other appropriate safety systems operated as expected. The plant was stabilized in hot standby (Mode 3) at normal post trip parameters and Operating shift personnel reacted appropriately throughout the trip event. The apparent cause of the first CEA failure was determined to be a ground in the circuit between the interposing cabling and the coil stack. In addition, the apparent cause of the second CEA failure was determined to be failed relays in the assembly's upper gripper circuit. As a contributing factor, it was determined that there were deficiencies in the CEA's preventive maintenance program. Prior to unit restart, several corrective actions were performed to both test and replace suspect equipment. In addition, a preventive maintenance program for periodic refurbishment of power switch modules will be established by September 1, 2000.
3362000004 | Millstone 2 | 02/14/2000 | 03/15/2000 | ML00369608 | <strong>Failure to Perform Channel Check for Wide Range Logarithmic Neutron Flux Monitor</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2000, at approximately 1400 hours, it was identified that a channel check for the Wide Range Logarithmic Neutron Flux Monitors was not performed on February 14, 2000 as required by the facility Technical Specifications (TS). The cause of this event was a misjudgment by Operations shift personnel. This was caused by the Control Operators (CO) and the Shift Manager (SM) misinterpreting the TS mode applicability and failing to perform the required surveillance. The wording of the TS mode applicability contributed to the CO and SM reaching their conclusion. To correct this deficiency, a briefing shall be performed on Technical Specification LCO applicability and applying "Not Applicable" in procedural steps. Additional corrective action include revising the applicable surveillance procedure to clarify when a channel check is required.
3362000005 | Millstone 2 | 02/16/2000 | 03/16/2000 | ML00369436 | <strong>Failure to Assure Containment Integrity for Certain Locked or Sealed Valves Located Inside Containment Prior to Entering Mode 4 from Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2000, during preparations to conduct the next scheduled performance of Technical Specification (TS) Surveillance Requirement (SR) 4.6.1.1(a) which verifies primary containment integrity, it was discovered that the last performance of this surveillance may have been inappropriately credited when the unit transitioned from Mode 5 to Mode 4 on February 16, 2000, at 0857 hours. It was later revealed that SR 4.6.1.1(a) was last conducted on January 20, 2000 with the unit in Model. In this Mode, certain containment penetrations located in containment are not required to be surveilled under SR 4.6.1.1(a) although the SR does require that these penetrations be verified closed prior to entering Mode 4 from Mode 5 if not performed within the previous 92 days. Since these containment penetrations had not been verified closed during the past 92 days, it was determined that containment integrity had not been assured during the February 16, 2000 Mode change. The root cause of this condition was determined to be a deficiency in the plant's heat-up procedure such that there was insufficient information to cue the user that the Mode needs to be considered in determining whether the surveillance is still current. As corrective actions, appropriate Operations department personnel were briefed on the specifics of this condition and prior to May 26, 2000, the plant's heat-up procedure will be revised to ensure compliance with Technical Specification Surveillance Requirement 4.6.1.1(a).
3362000006 | Millstone 2 | 03/07/2000 | 04/05/2000 | ML00370362 | <strong>Historical Condition: Remote Fire Detector Panel Supervisory Circuits not Tested in Accordance with Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2000, it was discovered that the supervisory circuitry for certain fire detection instruments may not have been historically inspected in accordance with Technical Specification (TS) surveillance requirements. TS surveillance requirements stated that the circuitry associated with the supervision of the fire detection instruments be demonstrated OPERABLE on a periodic basis not to exceed six months. Upon further review of this condition, it was determined on March 8, 2000 that from March, 1978, to November, 1995, a small segment of the instrumentation was not regularly or fully tested to the specific TS requirement. The cause of the event was failure to properly incorporate Technical Specification surveillance requirements into plant surveillance procedures. As a result of this condition the circuitry for the fire detectors that had not been historically inspected was tested satisfactorily to the proper surveillance requirements. Further corrective actions will be addressed by the Millstone Corrective Action Plan.
3362000007 | Millstone 2 | 04/22/2000 | 05/19/2000 | ML00371959 | <strong>Shutdown Cooling System Isolation Valve Does Not Comply With Appendix R Requirements Due To Error In Configuration Management</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2000, while shutting down in Mode 3 for a planned refueling outage, it was discovered that a shutdown cooling system isolation valve, 2-SI-651, was not disabled as required by the facility Appendix R Compliance Report for Modes 1, 2, and 3. It was determined on April 28, 2000, that this condition could have resulted in an inability to achieve and maintain cold shutdown per the requirements of Appendix R if a design basis fire-induced hot short of this valve had occurred. The Appendix R Compliance Report credits disabling this valve to ensure that a fire-induced hot short would not result in the valve damaging itself such that it could not be opened as needed to initiate Shut Down Cooling in the event of certain postulated fires. The cause of this event is that the operating procedures lacked sufficient verification to ensure that the desired outcome of disabling 2-SI-651 had been accomplished. The corrective action to prevent reoccurrence is to revise the heatup and cooldown procedures to 1) add steps that validate that 2-SI-651 will not operate from the Control Room after the opening and closing coils are removed and 2) ensure that the procedures contain proper validation that any other equipment required to be electrically disabled has been accomplished.
3362000009 | Millstone 2 | 06/01/2000 | 06/30/2000 | ML00373127 | <strong>Entry into an Operational Mode While in the LCO 3.6.5.2 Action Statement is a Violation of Technical Specification 3.0.4</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2000, at 1300 hours, with the unit in Mode 2 at 0 percent power, two (2) exterior doors located in an Auxiliary Building stairwell were blocked open for ventilation purposes in support of painting activities. These doors are part of the Enclosure Building Filtration System (EBFS) boundary and while opened, resulted in an untested EBFS boundary configuration. As a result, the EBFS boundary integrity was compromised and the Action Statement for Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.5.2 should have been entered but was not. On May 31, 2000, at 1434 hours, the unit entered Mode 3 from Mode 2 in order to troubleshoot control element assembly drive system problems. On June 1, 2000, at 0459 hours, a TS 3.0.4 violation occurred when the unit reentered Mode 2 from Mode 3 while the LCO Action Statement was in effect. This condition existed for approximately twenty-one (21) hours before EBFS boundary integrity was restored on June 1, 2000, at 0953 hours. The root cause of this condition is attributed to inadequate interface among organizations. Specifically, the work order to paint the stairwell was incomplete in that it did not contain necessary details with regards to EBFS ventilation pathway considerations, or that stairwell doors may need to be blocked open during the performance of the work. This inadequacy was neither identified nor questioned during the work order review and approval processes and the painting was allowed to be added and performed late in the outage schedule without appropriate consideration given to the pending unit mode changes. As corrective actions, a briefing will be conducted for appropriate Operations personnel and enhancements made to applicable sections of the station work control procedure to address this condition.
3362000010 | Millstone 2 | 06/04/2000 | 06/30/2000 | ML00373126 | <strong>Reactor Trip During Testing of Turbine Power-Load Unbalance Circuit</strong><br /><i>Abstract:&nbsp;</i>At 0012 on June 4, 2000 with the plant in Mode 1 at 65 percent (%) power, a reactor trip occurred during the performance of the weekly test of the Main Turbine Generator Power-Load Unbalance (PLU) circuit by operations personnel. This test was being performed in accordance with the applicable plant procedure (SP-2651T, "Power to Load Unbalance (PLU) Circuitry Test"). In accordance with this procedure, the power load unbalance pushbutton was pressed to initiate the test. However, the turbine control valves were not disabled and as a result the turbine control valves received a fast closure signal. The fast closure signal dumped disk pressure from the control valves which in turn processed a reactor protection trip from the low turbine trip fluid pressure switches. This event resulted in the Control room receiving annunciation of a turbine trouble followed by a reactor trip and plant equipment responded as expected following the initiation of the turbine control valves fast closure signal. This event was reported in accordance with 10CFR50.72(b)(2)(ii) on June 4, 2000 and is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event or condition that resulted in a manual or automatic actuation of an engineered safety feature (ESF), including the reactor protection system (RPS). The root cause for this event was determined to be an inadequate circuit design which, along with other corrective actions, is being addressed via the Millstone Corrective Action Program.
3362000011 | Millstone 2 | 07/12/2000 | 08/09/2000 | ML00374047 | <strong>Technical Specification Action Statements Exceeded for Electrical Busses When Vital Switchgear Ventilation Equipment Taken Out of Service</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2000 and again on July 17, it was determined that, with the Unit in Mode 1 at 100% power, Technical Specification (TS) action statements for electrical busses were exceeded when vital switchgear ventilation equipment was removed from service without implementing compensatory cooling measures. TS 3.8.2.1 requires both trains of emergency AC load centers be operable in Modes 1 through 4 and provides for an eight hour allowed outage time to restore the bus or be in cold shutdown in 36 hours. Motor control center enclosure (MCC B61) supports AC load center 22F. When the cooler for MCC B61 was tagged out of service, existing guidance directed either initiation of compensatory cooling measures, or entry into TS 3.8.2.1. Neither action occurred. Later, on July 17, 2000, it was discovered that TS action statement 3.8.2.3 for 125-volt DC bus trains was likewise exceeded when the ventilation chiller that supports Train "B" switchgear cooling was tagged out of service for routine maintenance. TS 3.8.2.3 requires both trains of DC busses be operable in Modes 1 though 4 and provides for a two hour allowed outage time to restore the bus or be in cold shutdown in 36 hours. Upon discovery of these conditions, appropriate action was taken to restore the equipment to operable status. In both instances, the redundant train was protected and operable during the maintenance outages, the switchgear rooms did not exceed their design basis temperatures, and no loss of safety function occurred. The cause of these two events was determined to be a lack of organizational awareness of vital switchgear room operability requirements.
3362000012 | Millstone 2 | 07/24/2000 | 02/20/2001 | ML01058042 | <strong>Historical LER: Work on Non-Vital Chiller Caused Vital Chillers to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2000, with the unit in Mode 1 at 100% power, restoration from a maintenance activity on a non-vital chiller introduced air into the vital chilled water system. The air migrated through the system and caused the pumps for the vital chillers to become air-bound. The vital chillers provide necessary cooling for the two DC switchgear rooms during accident situations. This condition went undetected until April 23, 2000, at which time the unit was in Mode 5 for refueling. The DC busses were administratively inoperable for 80.5 hours in Modes 1 through 4. Therefore, the limiting condition for operation for TS 3.8.2.3, which requires both trains of DC busses be operable in Modes 1 though 4, was not met. The vital chillers X169A/B were discovered air-bound during routine surveillance testing. The vital chillers were restored to operable status prior to entry into Mode 4 from the refueling outage. On July 24, 2000, during a regulatory review, it was determined that this was a reportable condition. The cause of this event was determined to be inadequate restoration from work performed on non-vital chiller X196B on April 19, 2000, in conjunction with a system piping arrangement conducive to air entrapment.
3362000013 | Millstone 2 | 07/31/2000 | 08/29/2000 | ML00374935 | <strong>Failure to Calculate Azimuthal Power Tilt As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 31, 2000, at 0800, with the plant in Mode 1 at 100 percent (%) power, it was determined that the incore monitoring computer software program (INPAX) had not automatically run the required calculation for Azimuthal Power Tilt (Tq) for a period exceeding 12 hours during the period from July 1 to July 2, 2000, and again during the period from July 29 to July 31, 2000. The surveillance requirement to calculate the tilt at least once per 12 hours was not met and this condition existed for a period of time that exceeded the allowed timeframe. Therefore, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition prohibited by the plant's Technical Specifications". The root cause of this event was historically inadequate expectations by the management of the Information Technology (IT) group for use of procedures when working on critical software. Upon discovery, the affected subroutine of the INPAX program was recompiled, thereby eliminating the condition which caused the INPAX program to fail to run. Subsequently, the INPAX program was run successfully and all required core parameters were determined to be within TS required limits. Additionally, a review of the data confirmed that core parameters remained within acceptable limits.
3362000014 | Millstone 2 | 08/03/2000 | 08/31/2000 | ML00374894 | <strong>Low Oil Level in "C" HPSI Outboard Bearing</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2000 with the plant in mode 1 at 100% power, during the routine surveillance of the "C" High-Pressure Safety Injection (HPSI) pump a determination was made that the outboard bearing housing was lacking the appropriate amount of oil. At the time of discovery, the pump was considered the operable HPSI pump for one of the Emergency Core Cooling Systems (ECCS). Per Technical Specification (TS) 3.5.2, two independent and separate ECCS subsystems are required to be OPERABLE, and to meet this requirement, each subsystem is required to have one OPERABLE HPSI pump. The follow-up investigation determined that the condition existed for the previous 28 days. With the reduced oil level in the outboard bearing, the "C" HPSI pump would not have been capable of performing its safety function for more than approximately 24 hours. The pump would potentially need to operate for significantly longer if its associated design basis accident did occur. Upon discovery, the "C" HPSI pump was removed from service, and the "B" HPSI pump (swing pump) was lined up to the associated ECCS subsystem to bring the plant into compliance with the TS. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3362000015 | Millstone 2 | 10/25/2000 | 11/20/2000 | ML00377209 | <strong>Failure to Comply with Technical Specification Action Statement for One Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 25, 2000 with the Unit in Mode 1 at 100% power and one emergency diesel generator (EDG) inoperable due to planned EDG testing, Operations personnel failed to perform verification of offsite power sources within one hour as required by Technical Specification (TS) 3.8.1.1, action b.1. The action to verify offsite power sources is met by completion of surveillance requirement 4.8.1.1.1 which calls for verification of correct breaker alignment and indicated power available for each required offsite circuit. This condition has been attributed to personnel error on the part of the licensed Control Operator who was performing the "B" EDG testing and the root cause was determined to be that the required procedures were not used. The corrective action was to provide coaching and counseling for Control Operator responsible for personnel error. Upon discovery of this condition, approximately 3.5 hours into the diesel testing, appropriate action was taken to complete the missed verification activity required by TS 3.8.1.1, action b.1, and the required offsite power sources were determined to be available. At no time during the EDG testing were any indications received that the required offsite power sources were unavailable.
3382000001 | North Anna 1, North Anna 2 | 02/21/2000 | 03/16/2000 | ML00369606 | <strong>Control Rod Deviation Monitor Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2000, at 0755 hours, with Unit 2 in Mode 1 operating at 100% power, the Individual Rod Position Indicator (IRPI) for rod E-5 on shutdown bank "B" drifted high. The Plant Computer System (PCS) rod deviation monitor alarm did not actuate when the IRPI for rod E-5 exceeded 12 steps above the bank demand position of 229 steps. The Technical Specification (TS) action was entered to verify the IRPI was within 12 steps of the bank demand position once every four hours. The IRPI was calibrated and returned to service. Subsequently, it was determined the PCS Rod Position Deviation Monitor would not provide alarm capability above 235 steps. The cause of the event is attributable to personnel error. Test procedures used to implement the PCS TS monitoring function did not ensure the Rod Position Deviation Monitor was operable above 235 steps. The software database has been corrected for both units. This event posed no significant safety implications since the shutdown bank control rods were able to perform their safety function throughout the event and the ability to move control rods was never compromised. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the TS.
3382000002 | North Anna 1, North Anna 2 | 04/04/2000 | 04/27/2000 | ML00371092 | <strong>Conditions Prohibited by TS and Outside Design Basis with EDGs Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2000, at 1145 hours, the "C" reserve station service transformer unloaded (refer to Licensee Event Report (50-339/2000-02-00). The 1H and 2J emergency busses lost power and then the 1H emergency diesel generator (EDG) did not start. It was determined that the 1H EDG became inoperable on March 22, 2000, at 1710 hours. On March 22, 2000, at 2329 hours, the 1J EDG was removed from service. TS 3.8.1.2 requires an operable EDG during movement of irradiated fuel assemblies when no fuel assemblies are in the reactor vessel. Irradiated fuel assemblies were moved in the spent fuel pool without an operable EDG. Also, with both Unit 1 EDGs inoperable, two Service Water pumps were inoperable for greater than the 72 hours allowed outage time specified in TS 3.7.4.1. Therefore, this is reportable pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(ii)(B). The reason for the 1H EDG not starting was that the number 3 cylinder was hydraulically locked due to being full of oil because of low lube oil temperatures that occurred during a bus outage. This event posed no significant safety implications since offsite power sources were operable and the SBO diesel was available to supply power to safety related equipment. Also, the control room emergency ventilation system was capable of performing its design basis function.
3382000003 | North Anna 1, North Anna 2 | 04/27/2000 | 05/25/2000 | ML00371986 | <strong>Multiple Safeguards Ventilation Damper Test Failures Due To System Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2000, with Units 1 and 2 in Mode 1 operating at 100% power, it was determined that the Safeguards Exhaust Ventilation System (SAVS) had been in a condition which could have prevented fulfillment of its safety function. Degraded conditions with the Unit 1 and 2 SAVS fan discharge dampers resulted in surveillance test failures between March 23, 2000 and April 27, 2000. Test results indicated instrument air leakage in the safety related seismic air supply for the fan discharge dampers. Inadequate test procedures did not ensure the dampers would remain open for 30 days following a design basis accident. A four hour non-emergency report was made to the NRC Operations Center at 1647 hours on May 1, 2000, pursuant to 10 CFR 50.72(b)(2)(iii)(B) and (C). This event posed no significant safety implications since a design basis accident did not occur and compensatory measures were established to adequately monitor the condition and promptly restore Safeguards area exhaust. LER 50-338/1999-00600 identified a degraded ventilation damper that had the potential to cause a portion of the SAVS flow to bypass the charcoal filter prior to release to the environment following a design basis accident. Engineering is pursuing a change in damper design to prevent recurrence.
3392000001 | North Anna 2 | 04/03/2000 | 04/25/2000 | ML00371094 | <strong>Automatic Reactor Trip Due To Loss of the Station Service Transformer</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2000, at 0857 hours, with Unit 2 in Mode 1 operating at 100% power, an automatic reactor trip occurred as a result of actuation of the 2C Station Service Lockout Relay resulting in a Turbine trip-Reactor trip. Actuation of the 2C Station Service Lockout Relay was due to a fault on a secondary feeder cable from the 2C Station Service Transformer to the 2C Station Service Bus. Control Room personnel responded to the reactor trip in accordance with emergency procedure E-0, Reactor Trip or Safety Injection. Initially, Reactor Coolant System (RCS) pressure decreased to 1985 psig, pressurizer level decreased to 23 percent, and RCS temperature decreased to approximately 542 degrees F. Pressurizer pressure, level and RCS temperature returned to their normal programmed values. All Engineered Safety Feature (ESF) equipment responded as designed. This event posed no significant safety implications because the reactor protection system and ESF systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
3392000002 | North Anna 2 | 04/04/2000 | 04/25/2000 | ML00371094 | <strong>MANUAL REACTOR TRIP DUE TO LOSS OF A REACTOR COOLANT PUMP</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2000, at 1146 hours, with Unit 2 in Mode 1 operating at approximately 7% power, a manual reactor trip was initiated to comply with Technical Specification 3.4.1.1 due to the loss of the "C" reactor coolant pump. While preparing to install the potential transformer fuses for recovery of the 2C Station Service Bus (SSB), the drawer for the "F" emergency transfer bus was opened. This caused the "C" Reserve Station Service Transformer (RSST) to unload, deenergizing the 1 H and 2J emergency busses and also both Unit's "C" SSBs. The "C" Reactor Coolant Pumps on both units tripped due to the loss of the "C" SSBs. Both unit's SSB power was being provided from the RSST busses at this time. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(A) and (a)(2)(iv). The loss of the emergency busses was the result of personnel error when the incorrect potential transformer fuse drawer was opened. This event posed no significant safety implications because the Unit's Reactor Protection System and ESF systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event. Non-emergency one and four hour reports were made at 1225 hours on April 4, 2000, pursuant to 10 CFR 50.72(b)(1)(i)(A) and (b)(2)(ii).
3412000001 | Fermi 2 | 01/07/2000 | 02/07/2000 | ML00368384 | <strong>Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCI) System Delcared INoperable due to Loss of Power to the Division I LPCI Inboard Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2000, at 0829 hours, the Division I Low Pressure Coolant Injection (LPCI) Inboard Isolation Valve, El150-F015A, lost power. The Fermi 2 Accident Analysis takes credit for the operation of the E1150-F015A valve with the initiation of "LPCI Loop Select Logic" during a Loss of Coolant Accident (LOCA). In the event of a break in one of the two reactor recirculation system loops, "LPCI Loop Select Logic" is provided to sense the broken loop and to inject coolant flow into the unbroken loop. Thus, the flow from the two LPCI system loops are interconnected by valving. With the E1150-F015A valve inoperable, both divisions of LPCI were declared inoperable. Technical Specification 3.5.1, Action J, was invoked and Limiting Condition for Operation (LCO) 3.0.3 was immediately entered. At 0837 hours on January 7, 2000, power was restored to the E1150-F015A valve and LCO 3.0.3 was exited, terminating the event. The cause of the loss of power to the E1150-F015A valve was determined to be a human performance error that most likely resulted from a contract employee inadvertently contacting the Motor Control Center (MCC) 72C-F Position 2C switch while erecting scaffolding in the MCC area. This event will be discussed at the next Fermi 2 human performance stand down day to be conducted prior to the Seventh Refueling Outage (RFO7).
3412000002 | Fermi 2 | 02/29/2000 | 03/29/2000 | ML00369985 | <strong>Damaged Terminal Blocks for Division 1 Core Spray Test Line Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On February 29, 2000, during performance of a work request for thrust testing of E2150-F015A, Division 1 Core Spray Test Line Isolation Valve, five damaged terminals of a terminal block assembly were discovered. The plastic barriers between terminal blocks 17 through 21 of Motor Control Center (MCC) 72B-3A position 3B were broken creating a potential for a short circuit between terminals. An evaluation of the damaged terminals determined it was possible that adjacent leads in the E2150-F015A valve MCC position could come in contact causing a short circuit under seismic conditions and, with a design basis accident signal present, render Division 1 Core Spray incapable of performing its Emergency Core Cooling System function and the E2150-F015A valve incapable of performing its primary containment isolation function. Because this condition was conservatively determined to exist since July 6, 1999, a period exceeding that permitted by Technical Specifications, this event is considered to be a condition prohibited by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B). The cause of the event was determined to be excessive stress on the terminal block divider plates due to the weight of the cable run connected to these terminals. The damaged terminal blocks were replaced and cables lengthened.
3412000003 | Fermi 2 | 03/15/2000 | 04/14/2000 | ML00370630 | <strong>High Pressure Coolant Injection System Inoperable due to High Reactor Water Level Trip During Channel Functional Test</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2000, at approximately 1036 hours, during performance of a surveillance procedure for the High Pressure Coolant Injection (HPCI) system [BJ] high reactor water level trip logic, an unexpected HPCI system high water level (Level 8) trip signal was generated. The HPCI Level 8 trip logic requires both the division 1 and division 2 Level 8 signals to complete the trip. The surveillance test in progress produced a division 2 level 8 signal. An apparently momentary division 1 Level 8 trip signal, completed the HPCI Level 8 trip logic. Because HPCI was not operating the Level 8 trip had no effect on HPCI system valves or components. Except for the short period of time both the division 1 and 2 Level 8 signals were present, a HPCI initiation on low reactor water level would have overridden the unexpected Level 8 trip allowing HPCI to perform its intended function. The surveillance procedure was exited, HPCI conditions monitored, Level 8 signals verified clear, and the Level 8 trip logic reset. Subsequent investigation was unable to conclusively determine a cause or duration of the division 1 Level 8 signal. Consequently, it must be conservatively assumed that both the division 1 and division 2 Level 8 signal were present until reset. Because a HPCI initiation signal could not override the completed Level 8 trip logic, HPCI was considered inoperable during this period. Since HPCI is a single train system this event is reportable in accordance with 10CFR5 0.73 (a)(2)(v)(D) as any event or condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
3412000004 | Fermi 2 | 04/01/2000 | 04/27/2000 | ML00370996 | <strong>Unplanned Manual Reactor Scram Following Recirculation Pump Trip During Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2000 at 1200 hours, a planned shutdown began for the seventh refueling outage. At 1815 hours, operators lowered the Reactor Recirculation Pump (RRP) speed to 30 percent. At that time, the "A" RRP speed oscillated between approximately 24 and 30 percent speed. This type of RRP speed oscillation is due to the hydraulic characteristics of RRP Motor Generator [MG] set fluid coupling and is expected near the 24 to 28 percent RRP speed range. The "A" MG fluid coupler scoop tube was locked in an attempt to maintain "A" RRP speed constant. The scoop tube apparently did not lock and the "A" RRP speed increased rapidly. The "A" RRP was immediately tripped as required by plant procedures. In single loop operation, procedures require the remaining ("B") RRP speed be maintained at greater than 50 percent. This could not be achieved because at the low power condition that existed at the time, RRP speed is limited to 31.5 percent speed. Lacking specific procedural guidance for the conditions that existed, reactor operators decided to manually trip the reactor. At 1915 hours, with reactor power at approximately 24 percent the mode switch was placed in shutdown, initiating a manual scram. Troubleshooting of the scoop tube and its controls could not duplicate or determine the cause for the scoop tube not locking. Additional post maintenance testing is planned during restart from the refueling outage. Corrective actions include development of appropriate procedural guidance for single loop operation at low power conditions.
3412000005 | Fermi 2 | 04/07/2000 | 05/08/2000 | ML00371468 | <strong>Pressure Isolation Valve Leak Test Failure</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2000, leak testing of Pressure Isolation Valve (PIV) E1100F050A, Division 1 Residual Heat Removal (RHR)/Low Pressure Coolant Injection (LPCI) System injection line inboard isolation check valve, was performed in accordance with Technical Specification (TS) Surveillance Requirement SR 3.4.5.1. The resultant leak rate was determined to be in excess of the specified leakage criteria of 10 gpm. The valve was disassembled and inspected. The cause of the failure was determined to be degradation of the elastomer soft seat. The soft seat was replaced and the valve was successfully leak rate tested. The opposite division counterpart, E110OF050B, successfully passed its as-found leak test; however, it was disassembled, inspected, and its soft seat was replaced, because of the degree of degradation observed for E1100F050A. With new soft seats, historical performance indicates that both valves would be expected to pass the as-found leak rate tests at the end of the next operating cycle. Further corrective actions relating to this event to obviate the need for periodic soft seat replacement are being considered, and will be developed and implemented commensurate with established priorities and processes of the Fermi 2 corrective action program.
3412000006 | Fermi 2 | 04/17/2000 | 05/12/2000 | ML00371561 | <strong>ESF Actuation: Invalid Automatic Closure of E1150F008 Resulting in Shutdown Cooling Interruption</strong><br /><i>Abstract:&nbsp;</i>At 0251 hours on April 17, 2000, the reactor was in Mode 5 with the vessel head removed, the reactor cavity filled with water, and the fuel pool gates removed. While removing Division 2 Core Spray from service for planned maintenance, operators removed power fuses to deenergize instrument power supply inverter E21K601B as directed by Safety Tagging Record (STR) 2000-000501. This inverter feeds one of two paralleled DC power supplies in panel H21 P081. However, inverter R31 K004, which feeds the other DC power supply, had previously been deenergized to support other activities. Therefore, when E21K601B was shutdown, the associated Division 2 instrumentation was deenergized, including the Reactor Steam Dome Pressure instrument loop which initiates the Shutdown Cooling System Isolation on Reactor Steam Dome Pressure - High. Deenergization of this loop initiated the automatic closure of E1150F008, Residual Heat Removal (RHR) Division 1 and 2 Shutdown Cooling Outboard Containment Isolation Valve, causing a trip of the operating RHR pump and a brief interruption of shutdown cooling. Once the cause of the isolation and pump trip was confirmed, power fuses for E21K601B were reinstalled and shutdown cooling was returned to operation. Shutdown cooling was interrupted for 21 minutes due to this isolation, however no change in reactor temperature was observed. This event occurred because proper power supply verification was not performed prior to shutting down inverter E21K601B.
3412000007 | Fermi 2 | 04/12/2000 | 05/12/2000 | ML00371564 | <strong>Failure of Isolation Valves to Meet Secondary Containment Bypass Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>Local leak rate testing of the main steam line drain valves was conducted during the Seventh Refueling Outage. Secondary containment bypass leakage through penetration X-8 exceeded the 0.04 La allowed by Technical Specification Surveillance Requirement 3.6.1.3.11. The leakage through B2103-F016, Main Steam Line Drain Inboard Isolation Valve, was not quantifiable. The leakage through B2103-F019, Main Steam Line Drain Outboard Isolation Valve, was 232.7 standard cubic feet per hour. Conservatively, the as found minimum path leakage value for penetration X-8 was determined to be 232.7 scfh. For the B2103-F016, the valve disc was found to provide an improved fit when it was rotated 180 degrees. Refurbishment work during the sixth refueling outage had left the B2103-F019 valve seats with insufficient margin. There was no evidence of steam cutting on the seating surfaces for either valve indicating that there was no active leakage through this pathway during the last operating cycle. Lapping and polishing of the valve seats was performed during the current outage. The B2103-F019 in body valve seats were lapped and polished and a build up was performed on the valve disc to restore the valve to an acceptable condition. Both valves subsequently passed their local leak rate tests.
3412000008 | Fermi 2 | 04/22/2000 | 05/22/2000 | ML00371715 | <strong>ESF Actuation: Invalid Automatic Closure of E1150F009 Resulting in Shutdown Cooling Interruption</strong><br /><i>Abstract:&nbsp;</i>At 1428 hours on April 22, 2000, the reactor was in Mode 5 with the vessel head removed, the reactor cavity filled with water, and the fuel pool gates removed. While attempting to deenergize solenoid valve T50F451 to remove it from service for maintenance, an operator (utility, non-licensed) removed the wrong fuse. Removal of this fuse deenergized part of the circuit involved in the Group 4 (Residual Heat Removal Shutdown Cooling and Head Spray) isolation signal. This initiated the automatic closure of E1150F009, Residual Heat Removal (RHR) Division 1 and 2 Shutdown Cooling Inboard Containment Isolation Valve, causing a trip of the operating RHR pump and a brief interruption of shutdown cooling. Once the cause of the isolation and pump trip was confirmed, the fuse was reinstalled and shutdown cooling was returned to operation. Shutdown cooling was interrupted for approximately 48 minutes due to this isolation, and a one degree Fahrenheit increase in reactor coolant temperature was observed. This event resulted from human performance errors caused by inattention to detail during the preparation, review, and implementation of the Safety Tagging Record (STR) associated with T50F451 maintenance activities. This event had minimal safety significance and did not impact the health and safety of the public. This event is being reported under 10CFR50.73(a)(2)(iv) as an Engineered Safety Feature Actuation.
3412000009 | Fermi 2 | 05/08/2000 | 06/07/2000 | ML00372283 | <strong>Emergency Diesel Generator Inoperable Due to Low Viscosity Oil in the Alternator Bearings</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2000, a review of past preventive maintenance activities determined that Emergency Diesel Generator (EDG) 11 had been inoperable for a period which exceeded the limiting applicable Technical Specifications (TS) allowed outage time of 7 days per TS 3.8.1, "AC Sources - Operating." EDG 11 was removed from service on March 1, 2000 for preventive maintenance. Maintenance activities were completed on March 4, 2000; however, subsequent evaluation determined that EDG 11 remained inoperable until April 2, 2000, when the Reactor was placed in Mode 4. During that time no TS Limiting Condition of Operation (LCO) was invoked because it was believed that EDG 11 was restored to its standby operation mode on March 4, 2000. The cause of this event was a human error that resulted in filling both EDG 11 alternator bearings with low viscosity oil that did not meet the required oil specification. With the low viscosity oil, it could not be assured that EDG 11 would fulfill its design basis requirements. The use of the wrong oil was a result of less than adequate self-checking and error detection practices, and less than adequate labeling and controlling of oil containers on site.
3412000010 | Fermi 2 | 11/24/2000 | 12/20/2000 | ML01002014 | <strong>ESF Actuation of a Suppression Chamber to Drywell Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>On November 24, 2000, at approximately 1236 hours, one of twelve suppression chamber to drywell vacuum breakers opened for approximately four minutes. The drywell pressure reduction and subsequent vacuum breaker opening was the result of P42-F400, Reactor Building Closed Cooling Water (RBCCW) Temperature Control Valve (TCV), controlling General Service Water (GSW) flow to the RBCCW Heat exchangers, failing in the open position. This resulted in a drywell temperature and pressure reduction and subsequent opening of the suppression chamber to drywell vacuum breaker. This is being reported in accordance with 10CFR50.73(a)(2)(iv), because the cycling of a suppression chamber to drywell vacuum breaker is considered to be an Engineered Safety Feature (ESF) actuation. The cause of this event was a previous misdiagnosis of a similar failure of the TCV positioner. This event is considered a Maintenance Rule Functional Failure. The air operator for the P42-F400, RBCCW TCV, was disassembled and the capscrew for the air operator shaft was torqued to the correct value and locktite was applied to prevent future loosening. P42-F400 was returned to service on December 5, 2000.
3462000001 | Davis-Besse | 09/26/1998 | 02/21/2000 | ML00369162 | <strong>Failure to Perform Technical Specification Action With Switchyard Circuit Inoperable Due To Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2000, with the unit in Mode 1 at approximately 100 percent power, a past condition was identified and determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. This past condition occurred on September 26, 1998, when switchyard breakers were opened while synchronizing the main generator to the grid. In this switchyard configuration, only one qualified circuit exists, rather than two as required by the Technical Specifications. On September 26, 1998, the appropriate actions of the Technical Specifications with only one qualified circuit operable were not performed within the one hour time frame specified. The apparent cause of this event is that previous reviews of the switchyard configuration and fault relaying did not address that opening these breakers could result in only one qualified circuit remaining operable. This condition would not have prevented safe shutdown of the plant because onsite power sources were unaffected by this condition. Appropriate procedures relating to switchyard operation will be changed to include steps to alert operators of conditions that may require entry into Technical Specifications when opening switchyard breakers.
3462000002 | Davis-Besse | 03/29/2000 | 05/24/2001 | ML01156001 | <strong>Main Steam Safety Valve Setpoints Greater Than Technical Specification Allowable Values</strong><br /><i>Abstract:&nbsp;</i>On March 27 and March 28, 2000, with the unit in Mode 1 at approximately 94 percent power, setpoint testing was conducted on the Main Steam Safety Valves (MSSVS). All 18 installed MSSVs were tested. Three of the tested MSSVs had a setpoint more than three percent above the desired setpoint, which exceeded the ASME Code allowable value, rendering the valves inoperable in accordance with the Technical Specifications. The setpoint of each MSSV was adjusted to within one percent of the desired setpoint upon discovery, as necessary. Based on the as-found lift setting pressures, the Main Steam System pressure would not have exceeded previously evaluated values during any anticipated overpressure transients. Six of the tested MSSVs, including the three that had a setpoint above the allowable value, were removed and replaced with valves less susceptible to sticking/ galling. The stainless steel valve seats of all 18 MSSVS will be replaced over the next four refueling outages with inconel valve seats to eliminate sticking/galling that is causing the high lift phenomenon. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3462000003 | Davis-Besse | 04/12/2000 | 05/11/2000 | ML00371623 | <strong>Loss of Auxiliary Feedwater Pump Turbine Main Steam Supply Train Separation Due to Check Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2000, at 0115 hours, with the Davis-Besse Nuclear Power Station in Refueling Mode 6, a Condition Report was initiated that identified that two check valves in the main steam supply to the Auxiliary Feedwater Pump Turbines (AFPT) had failed reverse flow testing. The two check valves that failed, AFPT 1 Main Steam Minimum Flow Line Check Valve (MS145) and AFPT 2 Main Steam Minimum Flow Line Check Valve (MS146), provide train separation between the two AFPT steam supplies. Simultaneous failure of these check valves due to abnormal wear resulted in loss of train separation between the steam line break detection pressure switches for each AFPT. Failure of these valves is a high-energy line break concern but has no impact on the operability of the Auxiliary Feedwater System. These valves were installed with a modification performed during the previous refueling outage. The apparent cause of occurrence is misapplication of the check valves due to the original design being inadequate. Due to the as found condition of the valves, it was concluded that the steam line break pressure switches were inoperable and potentially incapable of detecting a steam line break. This condition existed for a time period longer than allowed by the required Action for Technical Specification (TS) 3.7.1.2 and is reportable as operation prohibited by the plant's TSs in accordance with 10CFR50.73 (a) (2) (i) (B).
3462000004 | Davis-Besse | 04/22/2000 | 05/20/2000 | ML00371944 | <strong>Personnel Error During Bus Transfer Testing Results In Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2000, with the reactor defueled, a loss of offsite power occurred during performance of the Off-Site AC Sources Bus Transfer Test. Due to the test configuration, all station loads were powered from a single offsite source via Startup Transformer 01. When the Startup Transformer 02 lockout alarm automatically cleared during testing, the cause of the unexpected alarm response was investigated. The electrician checking the status of the lockout relays mistakenly checked the relays on the wrong side of the electrical panel, which were for the main generator instead of Startup Transformer 02. While checking the status of the relays, a main generator protection relay was actuated, which locked out the only available offsite AC power source, resulting in the loss of offsite power. Both emergency diesel generators started and loaded onto their respective essential buses. Offsite power was restored in ten minutes, and an Unusual Event was declared due to the loss of offsite power. This event is being reported in accordance with 10CFR50.73(a)(2)(v) as an event or condition that alone could have prevented the fulfillment of a safety function.
3462000005 | Davis-Besse | 06/08/2000 | 07/07/2000 | ML00373301 | <strong>Main Steam Drain Valve Left Open Rendering Auxiliary Feedwater Pump Turbine Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2000, with the plant in Mode 1 operating at 100 percent power, valve Main Steam (MS) 750, Auxiliary Feedwater Pump Turbine (AFPT) 1 Trip Throttle Valve Above Seat Drain, was found one turn from full open. The valve MS 750 along with nine other valves (five valves for AFPT 1 and 2 each) are operated once per week to drain condensate from the Main Steam supply piping to the AFPTs. Valve MS 750 is required to be closed in order to maintain the operability of AFPT 1. Investigation of the event concluded that MS 750 was last operated on June 1, 2000, during the weekly drain evolution. Valve MS 750 was apparently not closed after draining the condensate from the Main Steam piping. Because the valve was out of position for one week, exceeding the 72 hour Action requirement of Technical Specification 3.7.1.2, the plant was in violation of the Technical Specification. A procedure change which requires signoffs and independent verifications on the restoration for each of these ten valves required for draining the AFPT steam supply lines has been completed. This condition is reportable as operation prohibited by the plant's Technical Specifications in accordance with 10CFR50.73(a)(2)(1)(B).
3482000001 | Farley 1, Farley 2 | 02/19/1999 | 02/23/2000 | ML00368700 | <strong>Non-Conservative Main Steam Line Break Offsite Dose Calculation</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1999, it was determined that the limiting main steam line break (MSLB) offsite dose analysis for Farley Nuclear Plant (FNP) Units 1 and 2 may have assumed a non-conservative value for letdown flowrate which affected the iodine source term (dose equivalent iodine or DEI) used in the analysis. This event is being reported voluntarily. This condition was discovered due to evaluation of a similar condition discovered at Beaver Valley and reported on a Nuclear Network entry dated February 9, 1999. The cause of the non-conservatism was that the dose calculation assumed flows lower than the actual flows of the letdown system. This discrepancy between the assumed and actual flow rates resulted in a nonconservative offsite dose calculation such that with postulated worst case operating conditions and a postulated MSLB, offsite dose limits may have been exceeded. Reactor coolant system (RCS) DEI was below worst case postulated conditions. On February 19, 1999, a correction factor was applied to the measured DEI to ensure that the current TS limit and MSLB offsite dose analysis assumptions would remain bounding with respect to increased letdown flow rates. On February 4, 2000, Southern Company Services determined that use of a nominal flowrate does represent a non-conservatism in the FNP dose analyses. SNC is currently considering a number of options such as revising the accident analyses, reducing steam generator alternate repair criteria allowable leakage, or requesting a TS change to the DEI limit. This event does not represent a Safety System Functional Failure.
3482000002 | Farley 1 | 03/04/2000 | 03/29/2000 | ML00371336 | <strong>Unplanned Auxiliary Feedwater Actuation Upon Shutdown of Both Steam Generator Feed Pumps</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2000 at 0018, during the shutdown of FNP Unit 1 for refueling, an unplanned emergency safeguards actuation of the Auxiliary Feedwater System (AFW) occurred upon the planned shutdown of both Steam Generator Feedwater Pumps (SGFP). Thus automatic signal caused the 1B Motor Driven Auxiliary Feedwater (MDAFW) pump to start, AFW flow control valves to open fully and Steam Generator Blowdown to isolate. The 1A MDAFW pump was already running. The cause of this event was personnel error in that a step in the unit operating procedure to block the autostart of the AFW system on trip of both SGFPs was missed. When the turbine was secured, a leaking Main Feed Regulating Valve (MFRV) caused a rapid rise in steam generator (SG) water level. In an effort to stop the rapid rise in SG water level, the crew acted expeditiously to secure the second SGFP. During these efforts, the step to block the AFW autostart was missed. Additionally, the operating crew was aware that the MFRV was suspected of leaking but failed to proactively question and address the problem. Licensed personnel and Engineering Support personnel have been provided information on the proper use of and the need to adhere to "continuous use" procedures and to question and investigate abnormal indications. Troubleshooting and repair on the lB MFRV has been completed. The SGFP operating procedure has also been changed to include a "Caution" statement regarding trip of the second SGFP.
3482000003 | Farley 1 | 03/15/2000 | 04/13/2000 | ML00370417 | <strong>Penetration Room Filtration Automatic Start During Fuel Sipping</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2000 at 2051, with Unit 1 defueled, a valid high radiation alarm occurred on spent fuel pool (SFP) ventilation radiation monitor, R-25B. The alarm resulted in an automatic start of the B-train penetration room filtration system (PRF), an Engineered Safety Feature (ESF) actuation. It also resulted in an automatic shutdown of the normal SFP ventilation system. Per system design, the shutdown of the SFP ventilation system resulted in an automatic start of the A -train PRF system. The high alarm was caused by radioactive gases released from a fuel sipping activity being performed to identify leaking fuel assemblies. The PRF system functioned as designed and no abnormal offsite radioactive release was indicated. The cause of this event was procedural inadequacy in that the procedure being used for the leak detection did not contain sufficient provisions needed to prevent the auto start of the PRF system during release of radioactive gases into the SFP area. Small releases of radioactive gas are expected when sipping a fuel assembly with leaking pins. Appropriate plant procedures will be revised to require starting the PRF system before performing activities with the potential to release radioactive gases into the SFP area. The appropriate personnel will be trained on this event. These actions will be completed by June 30, 2000.
3482000004 | Farley 1 | 03/23/2000 | 04/20/2000 | ML00370740 | <strong>Three Spent Fuel Assemblies in Spent Fuel Pool Locations Not Allowed by Technical Specification 3.7.15</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2000 at 0830, it was determined that Unit 1 had been operated in a condition contrary to Technical Specification (TS) 3.7.15, in that three spent fuel assemblies were loaded in the Spent Fuel Pool in configurations contrary to TS Figures 4.3-1 through 4.3-5. This condition first occurred during the core offload for the current refueling cycle on March 13, 2000 at 1449. Manual verification of the acceptability of proposed offload configuration on March 11, 2000 failed to identify that three assemblies had insufficient burnup for their planned storage locations. On March 23, 2000, while Reactor Engineering personnel were loading the fuel location data into a Special Nuclear Materials tracking software package being developed for use, three fuel assemblies that did not meet the Technical Specification storage configuration requirements were identified. On March 23, 2000 at 0933, relocation of the three affected assemblies into acceptable locations was completed. This event was caused by personnel error in that personnel responsible for developing, performing, and verifying the SFP configuration failed to assure that three fuel assemblies met the Technical Specification configuration requirements. Contributing causes were lack of detail in the procedure, experience level of personnel performing this evolution, and insufficient independent review in the verification process. The procedure will be changed to provide sufficient detail to ensure correct configuration determinations. Responsible personnel will be trained on revisions to this procedure and the independent review requirements prior to moving fuel.
3482000005 | Farley 1 | 04/09/2000 | 05/08/2000 | ML00371467 | <strong>Loss of Offsite Power While Defueled due to Loss of 1A Startup Transformer</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2000 at 10:00 with the reactor defueled, Farley Nuclear Plant Unit 1 experienced a Loss of Offsite Power (LOSP), resulting in an Engineered Safety Feature (ESF) actuation. This occurred due to a trip of the operating lA Startup Transformer (SUT) which was supplying both trains of emergency AC busses from offsite power. As designed, the A Train emergency diesel generators (EDG) started and reenergized the A train emergency busses within approximately 12 seconds. Spent fuel pool cooling, which was deenergized at the initiation of the event, was restored at 10:18, and at 10:19 offsite power was restored to B Train emergency busses. The plant's electrical power systems were subsequently returned to normal alignment by 10:55. A root cause investigation concluded that the cause of the event was an inadvertent short circuit across one of the 1 A SUT protection relays to the trip bus circuits. Panel cleaning activity in progress when the event occurred was not appropriate for the plant electrical alignment in place. The cleaning, begun earlier, had been inappropriately allowed to recommence after conditions changed. The cause of this inappropriate activity was a failure in work coordination in that work was recommenced with neither Shift Supervisor awareness of the activity, nor worker awareness of current plant conditions. The maintenance procedure for cleaning the Metering and Relay Panels has been revised to require notification to the Shift Supervisor for each shift. Appropriate operating procedures for evolutions in which one train of equipment is removed from service, leaving only a single train available, will be revised to establish positive controls to protect the availability of the remaining train by July 31, 2000. The Operations Shift Foreman involved has been coached and shift personnel have been trained on this event. The shift operating crew erroneously determined that this event was a 4 hour report vs. a NOUE. Licensed personnel have received training on proper classification of LOSP events.
3482000006 | Farley 1 | 05/28/2000 | 06/27/2000 | ML00372871 | <strong>Reactor Trip from 4% Power Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2000 at 0545, with the reactor at 4% power, Unit 1 experienced an automatic reactor trip due to steam generator (SG) level reaching the low-low (lo-lo) level trip setpoint. At 0259 with the reactor at 14% power, the main turbine was manually tripped as part of planned maintenance to perform balancing. The turbine did not stop rolling as expected, and the decision was made to cycle the main turbine governor valves (GVs) to attempt to stop the turbine. The GVs were opened slightly in Turbine Manual mode, and then manually tripped. Following the turbine trip, low electrohydraulic (EH) control fluid pressure resulted in the only running steam generator feed pump (SGFP) losing speed and providing insufficient flow. The EH system is common to the SGFP turbines and the main turbine. Auxiliary feedwater (AFW) pumps were started and reactor power was rapidly reduced in accordance with plant procedures. SG levels had been stabilized with reactor power at 4% when cooldown caused the steam dumps to close. The resulting SG level shrink caused an automatic reactor trip on to-lo SG level. This event was caused by personnel error in that: 1) the governor valve cycling evolution was performed with inappropriate procedural guidance selection and use of Turbine Manual mode when Operator-Auto mode was the appropriate method; and 2) a prior software change to the turbine control system was prepared with inadequate documentation of its operational impact, leading to an inadequate procedure for operation in Turbine Manual mode. The event will be discussed with all licensed personnel, and all licensed personnel will be retrained on procedure use expectations by July 31, 2000. Personnel responsible for the digital electrohydraulic control (DEHC) system and software will be trained on expectations for software change package documentation by July 31, 2000. Applicable operating procedures have been changed to reflect the changed response of the EH system to a turbine trip when in Turbine Manual mode. Recent changes to DEHC software have been reviewed for additional operational impact and appropriate procedure changes have been made.
3522000001 | Limerick 1 | 04/07/2000 | 05/05/2000 | ML00371441 | <strong>ESF automatic actuation of PCIV's due to failed fuse.</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2000 at 10:56 hours, Unit 1, while in Mode 5 for refueling outage 1R08 , experienced an Engineered Safety Features (ESF) actuation (Channel D) which isolated six primary containment isolation valves (Drywell Chilled Water supply & return loops and Containment Instrument Gas supply). The isolation was a result of a blown fuse. The fuse was replaced and the valves were returned to service on April 8 at 15:54 hours. The most probable cause of the blown fuse was testing in progress on the affected equipment.
3522000002 | Limerick 1 | 05/01/2000 | 08/04/2000 | ML00373893 | <strong>Scram due to generator lockout following failure of a main transformer bushing connection</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2000 at 03:07 hours, an automatic scram occurred on Unit 1 due to a phase-to-phase fault which caused a generator lockout and resultant turbine trip. This automatic shutdown was the result of a faulty electrical connection at the 220 kV main transformer "C" phase bushing. This was due to inadequate administrative controls for assembly of the connection following maintenance on the main transformer. Standards and procedures will be created to ensure proper assembly, independent verification, and post maintenance testing of the electrical connection.
3522000003 | Limerick 1 | 06/12/2000 | 07/07/2000 | ML00373295 | <strong>Twelve Main Steam System Safety Relief Valves (SRV) Failed to Meet 1% Setpoint Tolerance due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 06/12/00, Engineering was informed that as-found test results for 12 of 14 Main Steam Safety Relief Valves (SRVs) did not meet the 1% setpoint tolerance of Tech Spec 3.4.2. The 14 SRVs were replaced during the 8th Unit 1 refueling outage (1R08) in April 2000. The condition of the 12 SRVs resulted in more than 2 independent trains in a single safety system becoming inoperable from a common cause. The consequences were minimal since no challenges to the overpressure protection system occurred. The 1R08 SRV setpoint drifts have been evaluated and found to be acceptable. This conclusion is based on an analysis performed to support installation of the three stage SRVs on Unit 1. The analysis assumed two (2) failed SRVs and incorporated data from a GE parametric study. The plant overpressure analysis was met. The SRVs are Target Rock Corp. Model 7567F pilot operated two-stage valves. The setpoint drift primarily resulted from corrosion induced bonding between the pilot disc and seat. All fourteen (14) Unit 1 SRVs were replaced with three-stage Target Rock SRVs prior to restart.
3522000004 | Limerick 1 | 10/18/2000 | 11/27/2000 | ML00377367 | <strong>Deficient Surveillance tests Identified by Internal SSFI on High Pressure Coolant Injection (HPCI) System</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2000, an internal Safety System Functional Inspection (SSFI) for the High Pressure Coolant Injection (HPCI) System identified two conditions that resulted in conditions prohibited by Technical Specifications (TS). On October 24, 2000, six cells in the Unit 1 Division III safeguard 125 VDC battery were measured to be at or below the electrolyte level minimum indication mark. Surveillance test deficiencies allowed acceptance of battery electrolyte level at a value that was less than the TS minimum. The battery electrolyte level was restored to normal and test procedures have been revised. Also, as part of the SSFI, it was identified that HPCI full flow surveillance test (ST) procedures did not specify the proper pump discharge pressure required by TS. Several tests had been performed at a pump discharge pressure that did not satisfy TS testing requirements. The most recent HPCI STs have been performed at a pump discharge pressure that satisfied TS requirements. HPCI ST procedures have been revised.
3532000001 | Limerick 2 | 01/08/2000 | 02/07/2000 | ML00368303 | <strong>Generator Lockout and SCRAM due to a Ground on the BOP DC 222 Bus</strong><br /><i>Abstract:&nbsp;</i>At approximately 16:30 hours on January 8, 2000 Unit 2 scrammed on a main generator lockout/turbine trip from a positive ground on the Balance of Plant (BOP) 222 plant services transformer alarm circuit. The shutdown was normal with all rods in and the reactor was stabilized. The trip was determined to be caused by a voltage transient as a result of ground on the non-safeguard DC distribution system resulting from closure of a knife switch while investigating a ground on the BOP DC System. The ground was caused by an exposed spare wire on the transformer low liquid level switch. The voltage transient caused the failure of two main generator differential relays. Additionally, a controlled process was not used in the search for the ground which has been addressed by management directives. The unit was returned to service on January 10, 2000.
3532000002 | Limerick 2 | 02/02/2000 | 03/03/2000 | ML00369152 | <strong>Automatic Depressurization System (ADS) long term gas supply valve mispositioning</strong><br /><i>Abstract:&nbsp;</i>On 02/02/00 at 21:05 hours, an Operations Supervisor discovered the manual shutoff valve on the 2A Automatic Depressurization System (ADS) long term gas supply was in the closed position. At 21:19 hours, the manual shutoff valve on the 2B ADS long term gas supply was determined to be in the closed position. At 21:25 hours, both valves were restored to the open position as required. This condition resulted in both trains of the ADS long term gas supply being inoperable. ADS ECCS operability was not affected. The last known correct alignment of these valves was determined to be during the previous refueling outage (2R05) in May 1999. This condition was discovered during performance of the ADS long term gas supply low pressure alarm calibration surveillance test (ST-2-059-400-2). A licensed operator's observation of loss of header pressure during this test led to the discovery of two valve mispositionings during the subsequent troubleshooting activity. One similar event was reported in LER 1-99-004 regarding two occasions when one train of the ADS long term gas supply was removed from service to perform maintenance. Retraction of this prior LER will be evaluated due to the conclusions of this event investigation.
3532000003 | Limerick 2 | 08/29/2000 | 09/22/2000 | ML00375654 | <strong>Failure of Suppression Pool Suction Valve Resulting in HPCI Inoperability</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2000 at 03:15 hours, the outboard suppression pool suction valve for the High Pressure Coolant Injection (HPCI) System failed to open on the first attempt during its surveillance test. The HPCI System was declared inoperable because of the inability of the suppression pool suction valve to take suction from the suppression pool (TS 3.5.1.c). This limit seated butterfly valve was subsequently closed, retested and stroked successfully within the acceptable time requirements. High pressure injection capability was available through the HPCI system from the Condensate Storage Tank. The cause of the valve inoperability was due to the valve operator spring pack being out of tolerance combined with a recent change to the torque switch setting. The spring pack for this valve was replaced with a calibrated spring pack. Other limit seated valves were reviewed, and valve setup criteria notes for these valves were developed. The motor operated valve (MOV) specification will be revised for limit seated valves to test the spring pack when torque values or spring packs are changed. This report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(v)(D).
3532000004 | Limerick 2 | 11/07/2000 | 12/01/2000 | ML00377558 | <strong>High Pressure Coolant Injection System Isolation Due to Failed Temperature Element Module</strong><br /><i>Abstract:&nbsp;</i>On Nov 7, 2000 at 02:31 hours, Unit 2, while operating at 100% power, experienced an Engineered Safety Features (ESF) actuation which isolated four primary containment isolation valves in the High Pressure Coolant Injection (HPCI) System. The isolation signal was a result of a failed temperature element module in the Steam Leak Detection system. The HPCI system was declared inoperable and a 14 day Limiting Condition of Operation (LCO) was entered in accordance with Technical Specification 3.5.1. A four hour notification was made to the NRC at 05:30 hours on November 7, 2000 pursuant to 10CFR50.72(b)(2)(ii). The failed module for the temperature element was replaced, and the isolation was reset on November 7, 2000 at 13:30 hours. The HPCI system was declared operable at 15:15 hours on November 7, 2000. The cause of the failure was identified as a random failure of a single isolation amplifier which resulted in signal fluctuations.
3542000001 | Hope Creek | 01/03/2000 | 02/02/2000 | ML00368387 | <strong>Technical Specification Prohibited Condition - Failure To Meet Technical Specification Surveillance Requirements To Verify Vital Bus Load Shedding During A Loss of Power and a Loss of Power/Loss of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>This LER reports the operation of Hope Creek in a condition prohibited by Technical Specification (TS) 3/4.8.1, A. C. Sources. Specifically, TS 3/4.8.1 requires verification at least once per 18 months that during a loss of offsite power, and during a loss of offsite power in conjunction with an Emergency Core Cooling System (ECCS) actuation signal, that the emergency buses are de-energized and that unnecessary loads are shed from those buses. Because of an error in Hope Creek procedure HC.OP-ST.KJ-0008(Q), Integrated Emergency Diesel Generator 1DG400 Test - 18 Months, the pre-test configuration of the B Radwaste Supply Fan was listed as "off". With the B Radwaste Supply Fan off during the test, the load shed of the B Radwaste Supply Fan was not verified. The apparent cause of this occurrence was human error during the development and review of the test table in procedure HC.OP-ST.KJ-0008(Q) that specifies the pre-test lineup. A review of procedures used to perform the 18-month integrated emergency diesel generator test on the remaining Emergency Diesel Generators was performed and no similar errors were identified. To prevent recurrence, procedure HC.OP-ST.KJ-0008(Q) will be revised to verify the B Radwaste Supply Fan to be in service prior to the next performance of the surveillance. The operability of the B Radwaste Supply Fan to trip upon a loss of power was verified through performance of a 36-month preventive maintenance test performed on May 27, 1998. This test will be completed prior to March 1, 2000 to maintain the operability of the B Radwaste Supply Fan load shed until the next 18-month surveillance can be performed. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by TS.
3542000002 | Hope Creek | 02/27/2000 | 03/27/2000 | ML00372283 | <strong>Technical Specification Prohibited Condition - Failure to Meet Technical Specification Surveillance Requirements to Perform Channel Check of Main Steam Isolation Valve Sealing System Instrumentation</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.6.1.4.d.1 requires that the operability of the Main Steam Isolation Valve Sealing System control instrumentation be verified at least once per 24 hours by performance of a CHANNEL CHECK. On February 26, 2000, the log documenting performance of this surveillance was omitted from the pre-prepared log package for that day. The error was not identified by station personnel until the required surveillance interval and the allowed grace period for the surveillance were exceeded. The apparent cause of this occurrence was personnel error in the preparation and review of the surveillance log package. Upon discovery of this condition, on February 27, 2000, the CHANNEL CHECK of the Main Steam Isolation Valve Sealing System control instrumentation was satisfactorily performed. To prevent recurrence of this event, management expectations regarding page checking of log packages by log users and reviewers were communicated to the operating crews, with emphasis on the need for attention to detail. Additionally this event will be evaluated as a part of a common cause evaluation of human performance errors.
3542000003 | Hope Creek | 05/04/2000 | 06/05/2000 | ML00375654 | <strong>As Found Values for Safety Relief Valve Lift Setpoint Exceed Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2000, the results of the Safety Relief Valve (SRV) setpoint testing were received. The testing revealed that, following Cycle 9, 2 of the 14 SRVs experienced setpoint drift outside of the Technical Specification limit of +/3%. One of the failures was of a valve with a pilot disc that was modified with platinum ion implantation. The drift for this valve appears to have been caused by friction on the sliding surfaces resulting from poorly controlled maintenance performed by the valve vendor. These practices have been addressed via a NUPIC audit. Corrective actions have been proposed and their effectiveness is being monitored. The cause of the drift for the other valve is corrosion bonding of the pilot disc to the pilot seat. The SRVs were inspected, refurbished and satisfactorily re-tested at a test facility. SRV drift in two-stage Target Rock valves is being addressed generically by the Boiling Water Reactor Owners Group. Platinum ion implantation has now been implemented on all 14 SRVs. The ion implantation process has resulted in a marked reduction of setpoint drift and will continue to be the primary solution for pilot disc to seat corrosion bonding.
3542000004 | Hope Creek | 05/06/2000 | 06/05/2000 | ML00372282 | <strong>Reactor Scram with Reactor Defueled Due to Scram Discharge Volume High Level</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2000, a SCRAM signal was generated as a result of high level in the Scram Discharge Volume (SDV). At the time of the event, the reactor was in a refueling outage with the core completely offloaded to the fuel pool, all control rods were inserted and the control rod drive hydraulic system was isolated. Work was being performed that required isolating air to the scram discharge volume vent and drain valves, resulting in these valves being closed. With the plant in this configuration Control Rod Drive leakage is directed to the scram discharge volume. Water level continued to rise in the discharge volume until the high scram discharge volume level scram setpoint was reached. This event resulted from an inadequate partial release of a tagout and untimely action to drain the SDV. Corrective action is to perform a review of tagouts in order to identify enhancements that will prevent recurrence of this type of event. This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an "event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS), .... "
3542000005 | Hope Creek | 05/07/2000 | 06/05/2000 | ML00372308 | <strong>Reactor Water Cleanup Isolation Following a Standby Liquid Control Initiation Signal</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2000, a reactor water cleanup system (RWCU) isolation occurred due to an inadvertent standby liquid control (SLC) initiation signal during surveillance testing. A maintenance technician was performing two surveillance tests (STS) in parallel for the Redundant Reactivity Control System (RRCS). Also, a SLC surveillance test was still in the restoration process. The simultaneous performance of these three tests resulted in the initiation logic being completed for the RRCS system to provide an initiation signal to the SLC system and isolate the RWCU system. Injection of SLC to the vessel did not occur due to the alignment of the SLC system valves in support of its surveillance testing. The apparent cause of the event was procedures that did not include adequate precautions and prerequisites. Contributing causes included the SLC flow test remaining in the restoration phase for an extended period of time and an error in judgment by the maintenance technician. Corrective actions taken included counseling of the technician. Actions to be taken include roll-out of the event to Maintenance personnel and procedure revisions to ensure that adequate precautions and prerequisites are included. This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an event or condition that resulted in the actuation of an Engineered Safety Feature (ESF).
3542000007 | Hope Creek | 05/13/2000 | 06/12/2000 | ML00372562 | <strong>Unplanned Scram During Post-Maintenance Testing While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2000, a Reactor Protection System (RPS) scram occurred due to high level in the scram discharge volume (SDV) during post-maintenance testing of one of the Alternate Rod Insertion (ARI) valves. The SDV high level scram signal was generated as a result of a manually initiated ARI scram. This event is reportable as an actuation of an Engineered Safety Feature in accordance with the requirements of 10 CFR 50.73 (a) (2)(iv) since the SDV high level scram was not expected to occur as a result of the test. The apparent cause for this event was personnel error. Both the ARI manual initiation and the SDV high level scram functioned as designed; however, based upon an incorrect understanding of the ARI manual initiation logic, personnel performing the test planned to close the ARI valves before the SDV high level scram setpoint was reached. By design, the manual ARI initiation signal seals in and can be reset only after a thirty second time delay. There were no actual safety consequences associated with this event. Corrective actions included resetting the ARI manual initiation and the SDV high level scram in accordance with plant procedures and communicating lessons learned from this event to Operations personnel.
3542000011 | Hope Creek | 11/21/2000 | 12/20/2000 | ML00378186 | <strong>Entry into Technical Specification 3.0.3 Due to Loss of Two Independent Control Room Emergency Filtration Systems</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2000, at 1027 hours, the A Control Room Chiller had been tagged and made inoperable for scheduled work on the Hot Gas Bypass valve temperature control setpoint. On November 21, 2000, at 1308 hours, the B Control Room Chiller and associated fans tripped on an apparent high bearing oil temperature condition. As a result of the trip of the B chiller, Technical Specification (TS) 3.0.3 was entered due to the loss of both trains of control room emergency filtration units. The apparent cause of the B chiller trip has been attributed to a high bearing oil temperature signal caused by the failure of the high thrust bearing temperature switch. A loose wire connected to the common power supply input to these modules was also detected. When the old module was bench tested it was found failed open in the tripped condition and required numerous cycling of the test equipment to get the switch to re-close. Corrective Actions taken were: the failed RobertShaw module was replaced with a new module; the loose wire was tightened and all others checked prior to installing the new module; the remaining RobertShaw modules on the A and B chillers will be replaced at the next opportunity.
3612000001 | San Onofre 2, San Onofre 3 | 01/20/2000 | 02/17/2000 | ML00368535 | <strong>Inadequate Design-SWC Pump Control Circuits Do Not Meet Fire Protection Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2000, at 1431 PST, SCE notified (NRC Log No. 36608) that some cables in the Saltwater Cooling pipe tunnel were missing a portion of their fire wraps required to meet 10CFR50, Appendix R, Section III.G. On January 25, 2000, subsequent engineering investigation determined that a design change was implemented in circa 1987, which was intended to eliminate the need to wrap these cables. However, this design change for the SWC Pump control circuits did not provide an isolation fuse as intended. Consequently, SCE is reporting this condition as outside the design basis of the plant in accordance with 10 CFR 50.73 (a)(2)(ii)(B). The cause is attributed to design error by a contract engineering firm (non-utility, non-licensed). SCE immediately ensured that an hourly fire watch was posted in the SWC pipe tunnel and in each Unit's SWC pump room. SCE will modify the affected circuits to eliminate the potential vulnerability discussed above. The condition had minimal safety significance.
3612000002 | San Onofre 2, San Onofre 3 | 01/27/2000 | 02/16/2000 | ML00368505 | <strong>Loss of Regulatory Guide 1.75 Separation - Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>The SONGS Units 2 and 3 UFSAR states, in part, "Non-Class 1E circuits and devices shall be electrically isolated from Class 1E circuits." During a review of elementary drawings, SCE observed that the Class 1E control circuits for Boric Acid Makeup Pumps (P174 and P175) contained unisolated contact inputs from non-Class 1E components. A follow up review identified other Class 1 E circuits with unisolated inputs from non-Class 1E circuits and devices as follows: a) 2/3V0227B Volume Control Tank Outlet Valve; b) 2/3V0227C Refueling Water Storage Tank Outlet to Charging Pump Suction Valve, and c) Units 2 and 3 Loss of Voltage Signal (one of four channels on both Trains A and B). SCE concluded that this deviation was reportable as a condition "outside the design basis of the plant." On 1/27/2000, at 1613 PDT, SCE reported this condition in accordance with 10CFR50.72(b)(1)(ii)(B). SCE is providing this 30-day follow-up report in accordance with 10CFR50.73(a)(2)(ii)(B). Due to the passage of time, SCE was not able to determine the cause of this occurrence. SCE will install appropriate isolation devices in the affected circuits to restore the design basis requirements described in the UFSAR. Because there are no credible initiators of non-Class 1E circuit faults which could affect the Class 1E circuits, the safety significance of this condition is minimal.
3612000003 | San Onofre 2, San Onofre 3 | 04/06/2000 | 05/04/2000 | ML00371237 | <strong>CREACUS Boundary Leakage--Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 4/3/2000, SCE performed a visual inspection of control room (CR) cabinet area normal and emergency A/C units. During the inspection, SCE discovered the condensate drain lines to both normal A/C units were not capped and would have provided a pathway for unfiltered air to enter the control room envelope. Upon discovery, SCE capped the drain lines. Subsequently, on 4/5/2000, after removal of insulation, SCE inspected the CR cabinet area normal A/C units and discovered one or more tears in an expansion boot. SCE immediately initiated actions to repair this damage. On 4/6/2000, based on engineering judgment, SCE concluded that when combined, the uncapped drain lines and the expansion boot tears could have caused aggregate unfiltered air inleakage into the control room from these sources to exceed the 10 scfm assumed in the UFSAR. Consequently, SCE is reporting this occurrence as a condition that was outside the design basis of the plant. Due to the passage of time, SCE did not identify the cause of the uncapped drain lines. The worn expansion boot appears to be a result of wear against an internal support member. Even though 10 scfm inleakage might have been exceeded for a few hours, the actual dose received by control room operators during postulated accidents remained within the criteria provided in GDC 19; therefore, the safety significance was minimal.
3612000004 | San Onofre 2, San Onofre 3 | 04/20/2000 | 05/15/2000 | ML00371522 | <strong>ECCS Rooms Outside the Design Basis Due to Missing Piping Insulation</strong><br /><i>Abstract:&nbsp;</i>On 4/19/2000, during an NRC inspection, it was noted that portions of the ECCS piping were not insulated as assumed in design calculations. Without insulation, the heat loading into ECCS pump rooms would be greater than assumed in the design calculations. Consequently, room temperatures could be above the 104 degrees F design limit during a Loss Of Coolant Accident or normal shutdown that uses the Shutdown Cooling system. A 1-hour non-emergency notification was made in accordance with 10CFR50.72(b)(1)(ii)(B). This report is provided in accordance with 10CFR50.73(a)(2)(ii)(B). Due to the passage of time, the cause of the missing insulation was not determined. Temporary insulation was installed on portions of the piping to increase thermal margin. SCE will install permanent insulation as required and revise calculations as needed to match the as-installed insulation configuration. SCE concludes that the condition has minimal safety significance. The lack of insulation did not result in a Safety System Functional Failure and was evaluated as GREEN using the latest draft of the Reactor Safety Significance Determination Process.
3612000005 | San Onofre 2, San Onofre 3 | 04/24/2000 | 05/23/2000 | ML00371873 | <strong>Electrical Power Alignment May Place CREACUS Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2000, in response to questions raised during the NRC Safety System Design and Functional Inspection, SCE realized that an interlock (intended to prevent backflow of unfiltered air into the control room) will not function as intended unless both the supply fan and recirculation fan are powered from the same Unit. Following a review of plant operating records, on April 24, 2000 (event date) SCE confirmed that there have been several instances in the past where both fans in a CREACUS train were not aligned to the same unit's ESF bus. As a result, one ventilation supply fan could have potentially introduced more than 10 cfm of unfiltered outside air into the control room during a postulated design basis event. At the time of discovery, the supply and recirculation units of each CREACUS train were aligned to the same power supply. Therefore, SCE is reporting this condition in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that was outside the design basis of the plant. The condition was caused by a design error by a contract engineering firm. When first identified, SCE immediately verified that the supply and re-circulation fans were aligned to the same unit supply bus in each CREACUS train. SCE also implemented an operating restriction to require that the fan alignment be maintained. The condition reported herein was evaluated by SCE as GREEN using the latest draft of the Reactor Safety Significance Determination Process (SDP).
3612000006 | San Onofre 2 | 04/26/2000 | 05/26/2000 | ML00372026 | <strong>Inoperable Salt Water Cooling Valve Causes Violation of Technical Specification 3.7.8, "Salt Water Cooling System"</strong><br /><i>Abstract:&nbsp;</i>Recently, SCE questioned the ability of the SWC valves and certain valves to remain in their safety related position if the instrument air system were to become inoperable. The focus of our efforts was a phenomenon (flow-induced hydrodynamic torque) which could cause certain types of butterfly valves to self-close under flow conditions. Subsequently, SCE determined that for 11 of the 12 valves affected, internal forces that resist closure were greater than the induced hydrodynamic torque, except for one SWC valve (2HV6202). SCE has blocked this valve open. TS 3.7.8, "Saltwater Cooling" requires two trains of saltwater cooling to be operable. If one train is inoperable, it must be restored within 72 hours, or the plant must be in Mode 3 in 6 hours and Mode 5 in 36 hours. Because there have been times in the past when SCE credited 2HV6202 for compliance with TS 3.7.8, it is possible that we did not comply with the actions required by TS 3.7.8 and SCE is reporting in accordance with 10 CFR 50.73(a)(2)(i). SCE violated TS 3.7.8 because SCE was not aware that 2HV6202 should have been considered inoperable. SCE has not yet been able to determine the cause of this valve's anomalous behavior. The safety significance was small; this condition screens as "Green".
3612000007 | San Onofre 2, San Onofre 3 | 06/01/2000 | 06/23/2000 | ML00372656 | <strong>Valve Position Verification Required for Surveillance 3.6.6.1.1 Not Implemented as Specified in TS Bases</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2000 (event date), while preparing to perform the containment spray monthly surveillance, an Assistant Control Room Operator (ACO) questioned the adequacy of the method of valve position verification. The surveillance procedure (SO23-3-3.13) did not include specific guidance for performing the verification. A review of the Bases to SR 3.6.6.1.1 noted the requirement of verification "through a system walkdown." However, procedure (SO123-O-23.1) allows verification of valve position by a control board indicator walkdown. Subsequently, SCE concluded that "through a system walkdown" could be interpreted to require a local verification at the valve's physical location. Consequently, even though this discrepancy is administrative in nature, and it could not impact the operability of the system, SCE is reporting this condition in accordance with 10 CFR 50.73(a)(2)(i)(B) as a Technical Specification violation. The phrase "through a system walkdown" was apparently inadvertently added in the Standard Technical Specifications and during the conversion to Technical Specification Improvement Program, SCE did not recognize the distinction between field walkdown and control room alignment walkdown. SCE immediately conducted a field verification of valve positions (on both Units) including valves with remote position indication. The Bases to TS 3.6.3 and 3.6.6.1 were revised to delete the statement "through a system walkdown." Using the NRC's current Significant Determination Process, this issue "screens-out" as an administrative issue not affecting operability, and consequently has "no color".
3612000008 | San Onofre 2, San Onofre 3 | 06/11/2000 | 07/10/2000 | ML00373159 | <strong>Radiography Causes Control Room Isolation Signal (CRIS) Actuation</strong><br /><i>Abstract:&nbsp;</i>On 6/11/2000, SCE was performing radiography on the 56-foot elevation of the Unit 2 Turbine Building when the Control Room Isolation Signal (CRIS) Train B radiation monitor actuated. A few minutes later, the CRIS Train A radiation monitor actuated. The Train A and B Control Room Emergency Air Cleanup System actuated as expected. During the pre job briefing, or tailboard, site personnel discussed the possibility for a CRIS actuation as a result of radiography. However, the actual equivalent dose rate (compared to the setpoint) was not known by the personnel attending the tailboard. Therefore, several shots were deferred to preclude a potential CRIS actuation until additional information became available. Contrary to management expectations, site personnel proceeded while still uncertain of the correlation between the source and the detector setpoint. The personnel involved considered it acceptable to proceed with the radiography based on historical data from previous radiography. SCE has suspended radiography within the Turbine Building until appropriate corrective actions are implemented. Because no actual airborne radioactive contamination was present, this event has no safety significance.
3612000009 | San Onofre 2, San Onofre 3 | 08/11/2000 | 09/08/2000 | ML00374903 | <strong>Missed Technical Specification Surveillances on Loss of Voltage Signal (LOVS) Relays</strong><br /><i>Abstract:&nbsp;</i>On 8/11/2000, during an NRC Inspection, it was identified that the testing procedures for timing the Loss of Voltage Signal (LOVS) circuitry did not include the 127F1X1 relay in the circuit. SCE realized that the procedures, as written, did not adequately ensure compliance with Surveillance Requirement (SR) 3.3.7.3 and SR 3.3.7.4. SCE declared a missed surveillance on both Units 2 and 3 Emergency Diesel Generators (EDGs), and entered the appropriate SR 3.0.3 24-hour action statement at 1440 PDT on 8/11/2000. SCE began efforts to test each of the Unit 2 and 3 EDGs; all EDGs were tested and declared operable by 2315 PDT on 8/11/2000 (within the 24 hours allowed by TS SR 3.0.3). This event was caused by an unclear definition of a LOVS channel which resulted in the omission of 127F1X1 from the test procedures. The safety significance of the missed LOVS circuit surveillances is negligible.
3612000010 | San Onofre 2, San Onofre 3 | 09/01/2000 | 09/27/2000 | ML00375612 | <strong>Control Room Emergency Cleanup System Not Seismically Qualified</strong><br /><i>Abstract:&nbsp;</i>On 8/31/2000, workers discovered a cracked weld where the electrical power supply conduit coupling is attached to the sheet metal junction box for the CREACUS Train B recirculation fan. On 9/1/2000, Southern California Edison (SCE) determined the cracked weld might fail during a Design Basis Earthquake (DBE), and cause the fan unit to fail by cutting or shorting the wiring. SCE could not determine when the weld failed, but it is likely CREACUS Train B was inoperable (not seismically qualified) longer than the 7-day out-of-service time allowed by TS 3.7.11. Consequently, SCE is providing this report in accordance with 10CFR50.73(a)(2)(i). Due to the passage of time, SCE did not identify the cause of the cracked weld. CREACUS Train A was inspected for similar weld defects. None were found. The inadequate weld on CREACUS Train B was repaired. SCE evaluated the safety significance of this condition using site specific criteria, including IPEEE considerations. This condition would not have impacted the ability of the control room operators to take appropriate accident mitigation actions. SCE concludes that there is no increase in calculated Core Damage Frequency or Large Early Release Frequency. This occurrence is categorized "Green" using the latest draft of the Reactor Safety Significance Determination Process (SDP).
3612000011 | San Onofre 2 | 09/17/2000 | 10/12/2000 | ML00376044 | <strong>Manual Start of a Containment Emergency Cooler, ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2000, at about 0620 PDT, non-1E containment normal chiller (2ME201) tripped on low oil pressure. Plant operators attempted to start the other containment normal chiller (2ME202) but stopped when the pre-start checks indicated low Freon level. Because containment temperatures were slowly increasing, the Emergency Containment Cooler units (ECU) were placed in service and an additional containment dome air circulator was started. The containment emergency coolers and dome air circulator operated as designed. On September 18, 2000, at 1258 PDT, Southern California Edison (SCE) made a 4-hour telephone notification to the NRC Operations Center (Log No. 37343) in accordance with 10CFR50.72(b)(2)(ii) for a manual actuation of an Engineered Safety Feature (EFS) component, even though the ECUs were not performing an ESF function during this event. SCE is providing this 30-day follow-up report in accordance with 10CFR50.73(a)(2)(iv). Normal containment cooler 2ME201 was repaired. A small amount of Freon was added to normal containment cooler 2ME202 as a conservative measure. This event had no safety significance.
3612000012 | San Onofre 2, San Onofre 3 | 10/06/2000 | 11/02/2000 | ML00376720 | <strong>Common boration flow path closed During Mod 4 - Potential non-conformance with TS 3.1.9 "Boration Systems - Operating"</strong><br /><i>Abstract:&nbsp;</i>While discussing CVCS check valve testing for the Unit 2 Cycle 11 refueling outage (which began on 10/7/00), SCE recognized that 2HV9200 had been closed when Unit 2 was in Mode 4 and below 400 psia during its Cycle 10 refueling outage shutdown, without first aligning an alternate boration flow path. (3HV9200 had also been closed under similar conditions during the Unit 3 cycle 10 refueling outage.) TS 3.1.9 had been interpreted to allow this action. Nevertheless, SCE recognizes there is a more conservative interpretation of TS 3.1.9. Because 2HV9200 is common to both charging header boration flow paths, if 2HV9200 was closed, neither train would respond to a SIAS. Although automatic SIAS is not required in Mode 4, manual SIAS is required in Mode 4. Therefore, on October 6, 2000 (discovery date), SCE conservatively concluded that closing 2HV9200 during the cycle 10 refueling outage with the plant in Mode 4 below 400 psia with SIAS disabled may not have maintained the two boration flow paths required by TS 3.1.9. SCE is submitting this report in accordance with 10CFR50.73(a)(2)(i). Prior to starting the shutdown for the current refueling outage, SCE revised the applicable procedure to require an alternate flow path to be aligned before closing 2HV9200 in Mode 4. Therefore, when 2HV9200 was closed on October 8, 2000 with the plant in Mode 4 below 400 psia, plant Operators first aligned an alternate boron injection flow path through the HPSI header. There is minimal safety significance to this issue. Closing 2HV9200 without first aligning an alternate boration flow path would not prevent operators from initiating boron injection in Mode 4 if it had been required. Additionally, the current NRC approved Standard Technical Specifications for Combustion Engineering Plants do not have a TS for boration flow paths.
3612000013 | San Onofre 2 | 10/08/2000 | 11/03/2000 | ML00376767 | <strong>Missed RCS Cooldown Rate TS Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 1018/2000, San Onofre Unit 2 was entering its refueling outage. As a part of this process, Operators secured the reactor coolant pumps and transitioned to Shutdown Cooling to remove decay heat. During this transition, for two 30 minute periods, the Reactor Coolant System (RCS) cooldown was not monitored as required by the Technical Specifications. Southern California Edison is reporting this event in accordance with 10CFR50.73(a)(2)(i). The cause of this event was Operator error in monitoring RCS cooldown. Proper RCS cooldown monitoring was established at 1450 PDT on October 8, 2000. An engineering determination that the RCS is acceptable for continued operation was completed on October 26, 2000, bring the unit into full compliance with the TS LCO. Operator training and procedure guidance on the process of controlling cold leg temperature and monitoring that parameter during this unique transition period will be improved prior to the Unit 3 shutdown for its scheduled refueling outage (January 2001). This event had minimal safety significance.
3612000014 | San Onofre 2, San Onofre 3 | 11/03/2000 | 02/02/2001 | ML01038033 | <strong>Missed IST for Safety Injection Tank Nitrogen Valves</strong><br /><i>Abstract:&nbsp;</i>On 11/03/2000 (discovery date), Southern California Edison (SCE) determined that the Safety Injection Tank (SIT) nitrogen supply check valves should have been included in the In Service Testing (IST) program but were not, and that the valves had not undergone periodic testing. As originally submitted, this Licensee Event Report (LER) indicated the missed IST constituted a missed Technical Specification (TS) Surveillance Requirement (SR) and was reportable to the NRC in accordance with 10CFR50.73(a)(2)(i). Subsequent review concluded that this omission did not cause a TS to be violated because there is no applicable TS LCO governing the SIT nitrogen supply check valves. Nevertheless, SCE is voluntarily providing this LER. Even though the SIT nitrogen supply check valves had not been tested in accordance with the IST program, these valves were functional and therefore, would not have prevented the SITs from performing their intended safety function. Consequently, this occurrence is categorized "Green" using the latest draft of the Reactor Safety Significance Determination Process (SDP).
3612000015 | San Onofre 2, San Onofre 3 | 11/17/2000 | 12/14/2000 | ML00377774 | <strong>Missed Technical Specification Surveillances on Post-Accident Monitoring Instrumentation (PAMI) Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>At SONGS Units 2 and 3, Technical Specifications (TS) Surveillance Requirement (SR) 3.3.11.4 requires, in part, that SCE "perform CHANNEL CALIBRATION" every 18 months on Post Accident Monitoring Instrumentation (PAMI) containment isolation valves. On 11/17/2000, SCE discovered that the surveillance frequency of 18 month (plus 25 percent) was exceeded. SCE is providing this LER in accordance with 10CFR50.73(a)(2)(i). In August 1996, TS SR 3.3.11.4 was added as a result of Improved Technical Specifications (TSIP). During the implementation of the TSIP SRs, SCE did not incorporate the new TS requirements in site SR procedures. SCE verified that the requirements of TS SR 3.3.11.4 had been met for all of the PAMI containment isolation valves. This was completed on 11/9/2000. SCE modified the IST procedure to credit the IST as performing a "CHANNEL CALIBRATION" in accordance with TS SR 3.3.11.4. In addition, SCE will modify the scheduling program for the PAMI containment isolation valves to 18 months. This issue was evaluated using NRC Manual Chapter 0610* (dated 10/6/00), and using the initial assessment of inspection observations for Significance Determination Process (SDP) entry (Attachment 0609.02), the issue would be a minor one without color.
3612000016 | San Onofre 2 | 12/31/2000 | 01/22/2001 | ML01025003 | <strong>Manual Start of a Containment Emergency Cooler, ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2000, at about 0130 PST, non-1E containment normal chiller (2ME201) shutdown on high chilled water temperature. Plant operators stopped 2ME201 and began preparations to start the other containment normal chiller (2ME202). During this time, operators were concerned that an increase in containment pressure and temperature could accelerate Reactor Coolant Pump seal degradation. In response to this concern, operators decided to place the ECU's in service until a normal containment chiller was returned to service. On December 31, 2000, at 0333 PST, Southern California Edison (SCE) made a 4-hour telephone notification to the NRC Operations Center (Log No. 37641) in accordance with 10CFR50.72(b)(2)(ii) for a manual actuation of an Engineered Safety Feature (EFS) component, even though the ECUs were not performing an ESF function during this event. SCE is providing this 30-day follow-up report in accordance with 10CFR50.73(a)(2)(iv). A drift in the low chilled water temperature switch setpoint caused the shutdown of normal containment cooler 2ME201. 2ME202 was placed in service at 0220 on December 31, 2000 and provided cooling to containment normal coolers. The temperature switch for 2ME201 was re-calibrated, and 2ME201 was returned to service on January 1, 2001. This event had no safety significance.
3622000001 | San Onofre 3, San Onofre 2 | 02/18/2000 | 03/14/2000 | ML00368535 | <strong>Inoperable Post Accident Monitoring Instrument</strong><br /><i>Abstract:&nbsp;</i>On 2/18/2000, SCE determined that on 3/5/98, Unit 3's RCS Hot Leg Wide Range Temperature recorder 3TR0911X1 was declared inoperable and was not corrected until April 15, 1998 (greater than the 30 days allowed by TS 3.3.11 Action A.1). Because the specified action time was not met, this Special Report is being submitted in accordance with TS 3.3.11 Action B.1 and in accordance with 10CFR50.73(a)(2)(i). The cause of 3TR0911X1 being declared inoperable in March 1998 was the take up spool upper retaining plate return tension spring was broken. The broken spring had the potential to affect the required trending capability of the recorder. The cause of the broken spring was not determined in March 1998, and, due to the passage of time, was not determined at this time. A Special Report, as required by TS 3.3.11 Action B.1, was not submitted in 1998 due to a procedure error. SCE repaired recorder 3TR0911X1 and returned it to operable status on April 15, 1998. SCE corrected the procedure error on February 18, 2000. The safety significance of this event was minimal.
3622000002 | San Onofre 3 | 02/01/2000 | 06/01/2000 | ML00372033 | <strong>Missed RCS Leak Rate Surv. - Y2K Error Inattention to Detail</strong><br /><i>Abstract:&nbsp;</i>On 5/3/2000 (discovery date), an NRC Resident Inspector questioned a discrepancy noted in the data used for calculating the 2/1/2000 (event date) Reactor Coolant System leakage surveillance for Unit 3 and further questioned if SCE may have violated a Technical Specification Surveillance Requirement. Southern California Edison (SCE) determined that the data were in fact incorrect. Consequently, this event is considered to be a missed surveillance and is being reported in accordance with 10CFR50.73(a)(2)(i). The cause of the data error was a latent Y2K related problem with the way a computer program handled Year 2000 dates. For the event reported herein, both the initial and final data were incorrect and identical. The operator who performed the surveillance did not recognize these details in the surveillance results. Consequently, the surveillance was missed. SCE replaced the software. This event had no safety -significance because the TS LCO would have been met on 2/1/2000, had the correct data been used. SCE evaluated this event GREEN using the latest draft of the NRC's Reactor Safety Significance Determination Process (SDP).
3622000003 | San Onofre 3 | 10/01/2000 | 10/23/2000 | ML00371237 | <strong>Inoperable Containment Dome Air Circulator</strong><br /><i>Abstract:&nbsp;</i>During Technical Specification (TS) surveillance tests on 8/15/2000, the feeder breaker for a Containment Dome Air Circulator fan was slow to trip. The breaker was overhauled, and returned to service on 8/26/2000. On 10/1/2000 (discovery date), while attempting to start the fan, its feeder breaker tripped on over-current. Because the fan motor is not accessible during power operation, Southern California Edison (SCE) has not been able to determine the exact cause of the trip. Nevertheless, SCE considers that fan may have been inoperable longer than the TS out of service time limit of 30 days. Consequently, SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). The cause of this occurrence is under investigation. On 10/6/2000, SCE revised the Bases of TS 3.6.8 and the UFSAR in accordance with 10CFR50.59 to allow operation with one operable fan unit per train, bringing the unit into full compliance with TS 3.6.8. The fan will be repaired during the upcoming Unit 3 refueling outage, currently scheduled to begin in January 2001. This event had minimal safety significance.
3642000002 | Farley 2 | 03/25/2000 | 04/21/2000 | ML00370884 | <strong>TS 3.0.3 Entered due to RCS Leak Detection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 25, 2000, with Unit 2 operating at 100% power, it was determined that at isolated times beginning on May 11, 1998 until March 25, 2000, Farley Nuclear Plant Unit 2 was operated in a condition prohibited by Technical Specifications (TS). TS 3.4.15 specifies that the containment particulate radiation monitor, R-11, and either the containment gaseous radiation monitor, R-12, or one of the containment cooler condensate level monitors (CCLM) be operable. All four CCLMs were determined to have previously been inoperable. Three of the CCLMs were inoperable due to improperly positioned drain valves and the fourth CCLM was periodically inoperable due to spurious alarms and maintenance. There was one occurrence in April 1999 and seven occurrences in the first quarter of 2000 (and possibly others which were not identified) where all CCLMs and both R-11 and R-12 were inoperable and resulted in Unit 2 operating in a condition prohibited by TS requiring entry into TS 3.0.3. The cause of this event is that plant design documents did not specify the unique flow restriction requirements of the CCLM drain valves. The CCLM drain valves are grouped in the bill of material with other common 3/8" drain valves allowing the selection of other replacement drain valves for use that did not have identical flow characteristics. This resulted in maintenance and planning controls allowing a valve of different flow characteristics to be installed without assuring operations procedures for throttling the valves were revised. Two of the mispositioned drain valves were properly repositioned on March 25, and the third was properly repositioned on March 26, 2000. Operating procedures have been revised to have operators determine the valve model and position the valves as directed by a table in the procedure. The bill of material will be revised to specify the design requirement of the CCLM drain valves per a unique identification number that will include the unique flow requirements of these valves. The plant component database will be revised to include complete information on containment cooler drain valves. These actions will be completed by June 30, 2000.
3642000003 | Farley 2 | 08/13/2000 | 09/08/2000 | ML00374981 | <strong>Pressurizer Pressure Protection Channel Not in Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2000, at 1000, it was determined that Unit 2 had been operated contrary to Technical Specification (TS) Table 3.3.1-1 item 8.a. The pressurizer low pressure reactor trip setpoint on one channel was found to have been incorrectly set. The surveillance procedure requires one of two calibration thumbwheels on the applicable circuit card to be repositioned for performance of the surveillance. It was concluded that another thumbwheel was inadvertently returned to the normal operating position for the first thumbwheel at the completion of the previous surveillance test on June 24, 2000. This resulted in the low pressurizer reactor trip setpoint being approximately 1757 psig with a 1 second time constant instead of a required 1865 psig with a 10 second time constant. Other functions based on pressurizer pressure from this channel, and the other two pressurizer pressure channels, were unaffected by this condition. Root cause investigation concluded the cause of this event was personnel error in that the technician, who performed the surveillance on June 24, 2000, repositioned the incorrect thumbwheel. Also, a second technician incorrectly performed verification and therefore failed to identify the error. The affected card was returned to the correct alignment, and the channel tested satisfactorily. Technicians involved have been coached. Maintenance personnel will be retrained and expectations reinforced on self checking and independent verification requirements by October 31, 2000.
3642000004 | Farley 2 | 11/16/2000 | 12/12/2000 | ML00378078 | <strong>Reactor Trip Due to Degraded Main Feedwater Regulating Valve Transient Response</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2000, at 0323, Unit 2 experienced an automatic reactor trip resulting from a turbine trip from high steam generator (SG) water level in the 2A SG. At 0318, approximately 5 minutes prior to the event, both Steam Generator Feedwater Pumps (SGFP) had decreased to minimum speed due to a failure in the master speed control circuit. The operator manually recovered speed control, but due to sluggish response of the 2A SG main feedwater regulating valve (MFRV), too much water was supplied to the 2A SG and the high level turbine trip was actuated. The turbine trip provides a direct reactor trip signal at power greater than 35%. All safety systems functioned as designed following the trip. The transient leading to the trip was initiated by a failed card (failed soldier joint) in the feedwater pump speed control circuit. Nevertheless, had the 2A MFRV responded normally, a trip should not have occurred. The sluggish response of the 2A MRFV was due to the air bleed path filter within the positioner being clogged as a result of inadequate preventive maintenance on the positioner. Feedwater isolation, the safety function of this valve, was unaffected by this condition. The 2A MFRV positioner was replaced. The 2B and 2C MFRV positioner air bleed paths were verified clear, and the positioners were setup to preclude the valves from going into saturation. The failed feed pump speed control circuit card was replaced. To prevent recurrence, preventive maintenance practices for the MFRV will be revised to provide adequate guidance by February 24, 2001. The Unit 1 MFRVs were verified to have a positioner type not susceptible to this type failure.
3662000001 | Hatch 2 | 02/27/2000 | 03/27/2000 | ML00370049 | <strong>High Pressure Coolant Injection System Inoperable Due to Water In Lubricating Oil System</strong><br /><i>Abstract:&nbsp;</i>On 02/27/2000 at 1615 EST, Unit 2 was in the Run mode at a power level of approximately 2708 CMWT (98 percent rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was declared inoperable after water was discovered in its lubricating oil. During the performance of procedure 34SV-E41-002-2S, "HPCI Pump Operability," personnel noted water spraying from the area of the main pump outboard mechanical seal. As a result, personnel shut down the HPCI pump. Maintenance personnel subsequently found the seal cavity full of water and its drain line clogged. Personnel unclogged the line, allowing the water to drain. When personnel returned the HPCI system to standby status, they noted the oil level was above the high level mark. Personnel obtained an oil sample from the bottom of the oil reservoir and found the sample to contain approximately fourteen percent water. Operations personnel declared the HPCI system inoperable at 1615 EST upon being notified of the water in the oil. This event was the result of water standing in the outboard mechanical seal cavity caused by a clogged drain line. The water, coming from a small leak in the mechanical seal, apparently entered the oil system by flowing past the thrust bearing oil deflector. The deflector forms one of the seal cavity walls and is not designed to keep standing water out of the bearing housing. The oil system was drained and cleaned, filters were replaced, and new oil was added to the reservoir. The HPCI system was returned to operable status on 02/28/2000 at 1714 EST after successful performance of procedure 34SV-E41-002-2S.
3662000002 | Hatch 2 | 03/14/2000 | 04/11/2000 | ML00370424 | <strong>Unclear Drawing Results in Unplanned Actuation of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 3/14/2000 at 1318 EST, Unit 2 was in the refuel mode with the reactor vessel disassembled and flooded to accommodate refueling operations. At that time, a local leak rate test (LLRT) was being performed which resulted in inadvertently applying air pressure to a sensor that detects high pressure in the drywell. As a result of this signal, several engineered safety features associated with high drywell pressure were actuated, including the drywell floor drain isolation valve in the primary containment isolation system. The event was caused by misleading notes on drawings which resulted in two conflicting equipment clearances being established simultaneously. The effect of these two clearances was to open the valve in the instrument line leading to the drywell pressure instrument. With this valve open, the air pressure applied to the valve for the LLRT was sensed in the instrument, resulting in the trip of the associated logic. Corrective actions for this event will include revising the appropriate drawings, reviewing drawings for similar conditions, and revising the LLRT procedure to require that relay logic downstream of the affected pressure sensor be disabled before performing a leak rate test. These actions will be completed on both operating units before the next scheduled refueling outage.
3662000003 | Hatch 2 | 03/23/2000 | 04/18/2000 | ML00370680 | <strong>Inadequate Procedure Results in RPS Actuation on Scram Discharge Volume High Water Level</strong><br /><i>Abstract:&nbsp;</i>On 03/23/2000 at 2140 EST, Unit 2 was in the Refuel mode with fuel in the vessel, the refueling cavity flooded, and refueling outage activities in progress. At that time, personnel were performing subsection 7.11 of surveillance procedure 42SV-C71-001-2S, "Reactor Protection System LSFT," when an unplanned full reactor protection system actuation occurred on high water level in the scram discharge volume. The actuation occurred after the scram discharge volume high water level scram bypass switch had been moved from "bypass" to "normal" as required by procedure 42SV-C71-001-2S. All control rods were inserted fully and the control rod drive system was out of service; therefore, the reactor protection system actuation resulted in no appreciable rod movement. This event was the result of an inadequate testing procedure. Procedure 42SV-C71-001-2S required a manual scram to be inserted; this action closed the scram discharge volume vent and drain valves allowing the volume to fill. Following testing, the procedure required the scram to be reset and the bypass switch to be moved to the "normal" position. However, the procedure did not require personnel to wait for the volume to drain before moving the switch. Therefore, a reactor protection system actuation was received when the bypass switch was repositioned before the volume had drained. Corrective actions include revising procedure 42SV-C71-001-2S to require personnel to verify the scram discharge volume high level alarm has cleared before placing the bypass switch to the "normal" position.
3662000004 | Hatch 2 | 03/27/2000 | 04/25/2000 | ML00370736 | <strong>Excessive Leakage Identified on Secondary Containment Bypass Valves</strong><br /><i>Abstract:&nbsp;</i>On 3/27/2000 at 0800 EST, Unit 2 was in the Refuel mode with the reactor vessel head in place with the head bolts not yet tensioned. At that time, the plant engineer responsible for local leak rate testing (LLRT) on primary containment isolation valves (PCIVs) determined that two secondary containment bypass valves, 2G11 F003 and 2G11-F004, had failed their associated LLRT. Both valves are located in the same penetration which exits the drywell floor drain sump. The valves are classified as secondary containment bypass valves as the drain piping is routed to the Radwaste Building which is not inside the secondary containment and, consequently, not served by the standby gas treatment system. The cause of the failure of valve 2G11-F004 was foreign material intrusion. A nylon tie-wrap and a piece of paper were found on the valve seat upon disassembly. The cause of the failure of 2G11-F003 could not be conclusively determined. The possibility could not be ruled out that foreign material also caused the failure of 2G11-F003. Corrective actions for this event included removing the foreign material from 2G11-F004, adjusting the pneumatic operator on 2G11-F003, re-testing the valves, and performing cleaning and inspections to ensure that measures taken for foreign material exclusion were as effective as possible to preclude further intrusion of objects which could affect operation of the PCIVs.
3662000005 | Hatch 2 | 04/02/2000 | 04/21/2000 | ML00370737 | <strong>Blown Fuse Results in Unplanned Actuation of Engineered Safety Feature System</strong><br /><i>Abstract:&nbsp;</i>On 4/2/2000 at 0030 EST, Unit 2 was in the Cold Shutdown mode. At that time, fuse 2A71B-F21A in main control room panel 2H11-P622 blew while licensed personnel were re-opening primary containment isolation valves 2G11-F003 and 2G11-F019. These valves, the only ones powered through fuse 2A71B-F21A, had closed as expected during the performance of surveillance procedure 42SV-R43-008-2S, "Diesel Generator 2A LOCA/LOSP LSFT," when the bus powering these valves was de-energized momentarily as part of the surveillance. While personnel were restoring valves 2G11-F003 and 2G11-F019 to their pre-test position, fuse 2A71B-F21A blew unexpectedly, causing the valves to close again on loss of power. The blown fuse was replaced and the valves were re-opened without further incident. The cause of this event was a blown fuse. These valves are designed to close upon loss of power. Therefore, when the fuse in their power supply circuit blew, the valves closed as designed. The reason the fuse blew was not identified. However, it may have been the result of a weak fuse since no problems, such as a ground, were evident when the valves were re-opened following fuse replacement. Corrective actions for this event included replacing the blown fuse and re-opening valves 2G11-F003 and 2G11-F019.
3662000006 | Hatch 2 | 04/06/2000 | 05/02/2000 | ML00371282 | <strong>Improper Coordination of Outage Activities Results in Unplanned Actuation of ESF System</strong><br /><i>Abstract:&nbsp;</i>On 04/06/2000 at 1000 EDT, Unit 2 was in the Cold Shutdown mode with the main condenser at atmospheric pressure and the main turbine in the tripped condition. At that time, a Group 1 primary containment isolation system signal on low condenser vacuum was received when the turbine was reset. Reactor water sample line isolation valves 2B31-F019 and 2B31-F020 closed as designed. Investigation revealed that the turbine "1800 rpm" speed select pushbutton was illuminated instead of the expected "all valves closed" pushbutton. When the turbine was reset with the "1800 rpm" speed select pushbutton illuminated, the stop valves opened per design, removing the low vacuum isolation signal bypass and generating a Group 1 isolation signal. The cause of this event was a lack of proper coordination between two outage activities. Contributing to this event was a failure of personnel to note that the "1800 rpm" speed select pushbutton was illuminated. As a result, the turbine was reset when logic systems were configured to open the stop valves, generate a low condenser vacuum isolation signal, and close the open Group 1 primary containment isolation valves. Corrective actions for this event include identifying this event as an outage lesson learned; adding administrative controls on the turbine reset button; and including this event in requalification training.
3662000007 | Hatch 2 | 04/07/2000 | 04/27/2000 | ML00371083 | <strong>Blown Fuse Results in Unplanned Actuation of Engineered Safety Feature System</strong><br /><i>Abstract:&nbsp;</i>On 04/07/2000 at 1615 EDT, Unit 2 was in the Cold Shutdown mode. At that time, a nonlicensed electrician replacing a divisional separator cover damaged wire insulation with a cover screw, grounding a logic power circuit and causing fuse 2A71B-F22 in main control room panel 2H11-P623 to blow. The resulting loss of power caused certain Group 1 and Group 2 primary containment isolation system valves to close per design. The fuse and wire were replaced per Maintenance Work Order 2-00-1352. Personnel returned affected valves and systems to service by 2154 EDT on 04/07/2000. The cause of this event was poor human factors. The covers on divisional separation wiring trays typically are attached with screws; however, once the cover is in place, it cannot be determined if the screw will contact wires within the tray, nor can actions be taken to prevent a screw from damaging wire insulation. In this event, a screw damaged wire insulation. The exposed wire contacted the metal tray, creating a ground path and blowing fuse 2A71B-F22. When the fuse blew, the various Group 1 and Group 2 primary containment isolation system valves closed as designed. Corrective actions for this event include replacing the blown fuse and damaged wire, returning affected valves and systems to service, and reviewing the method for attaching separator covers in panels containing engineered safety feature system logic and/or power circuit wiring.
3662000008 | Hatch 2 | 09/04/2000 | 09/27/2000 | ML00375688 | <strong>Trip of 600-Volt Supply Breaker Causes Loss of RPS Power Supply and Unplanned ESF System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 09/04/2000 at 1416 EDT, Unit 2 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, the supply breaker to Unit 2 Reactor Protection System (RPS) bus "2A" power supply tripped. Logic systems powered by the RPS bus include the RPS trip logic, the Main Control Room Environmental Control System (MCRECS) initiation logic, Primary Containment Isolation System (PCIS) trip logic, and Steam Packing Exhauster trip logic. All affected systems responded per design on the loss of power, producing a half scram signal, several PCIS valve isolations, MCRECS pressurization mode initiation, and other actuations. Licensed personnel verified the proper plant response to the initiating signal and, by 1441 EDT, had energized the affected RPS bus from its alternate supply. Affected systems subsequently were returned to their normal lineups. The cause of the supply breaker trip could not be determined conclusively; however, a likely cause appears to be actuation of the breaker control switch when personnel inadvertently bumped the control switch panel. Checks of the breaker and its trip unit, cables, motor starter contactor, and motor windings revealed no faults or other problems that could have caused the supply breaker to trip. Corrective actions for this event include the aforementioned checks, temporary monitoring of the 600-volt bus, and considering the possible addition of panel covers.
3662000009 | Hatch 2 | 11/22/2000 | 12/19/2000 | ML00378184 | <strong>Low Station Service Battery Room Temperatures Result in Entry Into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 11/22/2000 at 0930 EST, Unit 2 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, personnel performing daily rounds discovered the temperatures in the 2A and 2B station service battery rooms were below their minimum limit of 65°F. The temperature in the 2A battery room was 60°F and the temperature in the 2B battery room was 63°F. The Unit 2 Technical Specifications require the battery cell electrolyte temperature to be = 65°F. Operations personnel assumed conservatively that the cell electrolyte temperature was approximately the same as the room temperature and therefore below the minimum required temperature. At 1500 EST, personnel declared the batteries inoperable, effective at the time of the initial recording of the room temperatures. With both batteries inoperable, personnel entered Condition E of Unit 2 Technical Specifications Limiting Condition for Operation (LCO) 3.8.4, which, in turn, required entry into LCO 3.0.3. At 1530 EST, the batteries were declared operable and Condition E and LCO 3.0.3 were exited after the cell electrolyte temperatures were determined to be greater than 65°F. The cause of this event was inadequate procedures. Procedures did not require the heating coil for the battery room ventilation system to be placed into service during cold weather. Personnel placed the heating coil into service causing temperature in the battery rooms to increase to greater than 70°F by 0544 EST on 11/23/2000. The procedures will be revised. The Unit 1 station service battery room heating system is of a different design; therefore, no similar corrective actions are required.
3682000001 | Arkansas 2 | 07/30/2000 | 08/29/2000 | ML00374769 | <strong>Pressurizer Heater Sleeves and a Reactor Coolant System Hot Leg Resistance Temperature Detector Nozzle Were Leaking Due to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2000, with the plant in cold shutdown conditions for a Steam Generator tube inspection outage, twelve Pressurizer heater sleeves and one Reactor Coolant System (RCS) hot leg resistance temperature detector nozzle were found to have been leaking. Leakage was indicated by boric acid accumulation. The root cause evaluation concluded that the failure mechanism was primary water stress corrosion cracking of Alloy 600 material. Inspections were performed at other RCS and Pressurizer locations containing potentially susceptible material. No other leakage was found. Inspections of base material in the area of the leakage revealed no degradation. The leaks were repaired with an ASME Code-qualified process. The repairs were qualified for a limited service life until at least the refueling outage scheduled to begin in September 2000.
3682000002 | Arkansas 2 | 09/14/2000 | 10/16/2000 | ML00376197 | <strong>As-Found Lift Settings of Three Main Steam Safety Valves Were Below Technical Specifications Requirements Due to Different Methods for As-Found and As-Left Tests, As-Left Setpoint Bias, and Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Prior to a scheduled refueling outage, in situ testing revealed that as-found lift settings of three of the ten Main Steam Safety Valves (MSSVs) were more than three percent below their setpoints. The testing was conducted with a Crosby Set Pressure Verification Device (SPVD). MSSVs that were not within one percent of their setpoint were adjusted and re-tested until repeatable lifts were within tolerance. During the previous refueling outage, as-left setpoint verification was conducted using steam at a vendor's facility. Lift points were left in the low part of the allowable tolerance band based on experience that their as-found values were more often high at the end of the operating cycle. A potential failure mode analysis determined that the most probable causes were a difference in results from using the two test methods, the setpoint bias from the previous as-left tests, and setpoint drift. Collection and evaluation of information to improve MSSV performance will continue during future operating cycles.
3682000003 | Arkansas 2 | 11/16/2000 | 12/14/2000 | ML00377937 | <strong>Overload Cut-Off Limits for the Refueling Machine Were Not Set As Required by Technical Specifications Due to An Incorrect Dummy Fuel Assembly Weight Being Used for Calibration</strong><br /><i>Abstract:&nbsp;</i>At the start of core reload during a scheduled refueling outage, Refueling Machine underload indications were received. Fuel movement was suspended. Investigations revealed that the actual weight of the dummy fuel assembly used to calibrate the signal condition unit of the Refueling Machine was approximately 104 pounds heavier than the value that had been used since 1994. Calibration was performed with the revised weight and underload setpoints were adjusted before resuming fuel loading. A subsequent evaluation determined that the incorrect dummy fuel assembly weight had also affected Refueling Machine overload limits and resulted in their not being set as required by Technical Specifications. Inspections conducted during the outage confirmed that the condition had not resulted in damage to the fuel, core internals, or Reactor Vessel. The cause of the weight discrepancy in 1994 is attributed to use of a load cell with a large span to conduct the measurement. Applicable procedure changes were performed to incorporate the revised dummy fuel assembly weight.
3692000001 | McGuire 1 | 01/07/2000 | 02/07/2000 | ML00368385 | <strong>Failure to meet temperature requirements of Technical Specification Action Statement when more than one centrifugal charging pump or safety injection pump was capable of injecting into the Reactor Coolant system</strong><br /><i>Abstract:&nbsp;</i>Unit Status: On October 30, 1999, Unit 1 was in Mode 5 at 0% power. Event Description: At 16:24, on 10/30/99, Technical Specification Action Statement A.2.2.2 was entered when the 1A Safety Injection (NI) pump was racked in to fill and vent the NI piping inside containment. Reactor Coolant System fill was in progress with charging of 120 gpm to the 1A cold leg and reactor coolant pump seals with letdown of approximately 20 gpm. The Residual Heat Removal (ND) System was aligned and flowing at 1300 gpm to the 1C and 1D cold legs. The ND heat exchanger discharge temperature was approximately 119°F. Technical Specification 3.4.12, Action Statement A.2.2.2 requires that cold leg temperature be maintained >107°F when in this condition. No reactor coolant pumps were in operation. In this condition, Reactor Coolant (NC) cold leg temperature indication used during normal operation does not provide reliable indication of cold leg water flow to the core. As such, during this time, operators used decay heat removal discharge temperature as indication of "cold leg temperature." The temperature measured at the outlet of this heat exchanger met the Technical Specification limit at all times. This practice was questioned by the Resident Inspectors from a literal compliance perspective and a non-cited violation was issued on January 7, 2000 (discovery date). Event Cause: Incomplete guidance document for interpretation of Technical Specification 3.4.12. Corrective Action: Duke Energy will document a Technical Specification Bases change to reflect the use of decay heat removal temperature for the purposes of meeting this Technical Specification requirement.
3692000002 | McGuire 1, McGuire 2 | 02/04/2000 | 03/06/2000 | ML00369161 | <strong>McGuire Units 1 and 2 in a condition outside design basis of plant due to Refueling Water Storage Tank level channels in a trip condition for an indefinite period of time</strong><br /><i>Abstract:&nbsp;</i>Unit Status: On February 4, 2000, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 1 at 65% Power. Event Description: McGuire Technical Specifications (TS) allow for the option of placing an inoperable channel of Refueling Water Storage Tank (FWST) level instrumentation in the trip condition. McGuire has identified past instances where this option was invoked. Since the TSs allowed operation in this trip condition for an indefinite period of time, this condition cannot be considered as the design basis single failure during a design basis accident. Consequently, with one channel of FWST level instrumentation in the trip condition, a single failure of another channel coincident with a design basis Loss of Coolant Accident (LOCA) could have resulted in premature swapover of the Residual Heat Removal (ND) pumps to the Containment Sump. If premature swapover were to occur, both trains of ND pumps could fail due to insufficient Containment Sump water level. This could result in a loss of post-accident cooling functions. Event Cause: Deficiency in McGuire Technical Specification 3.3.2 - Engineered Safety Feature Actuation System (ESFAS) Instrumentation. Corrective Action: Duke Energy will submit a TS amendment to provide limitation on the time an FWST level channel can be in a trip condition.
3692000003 | McGuire 1, McGuire 2 | 03/02/2000 | 03/30/2000 | ML00370164 | <strong>Non-Conservatism in Spent Fuel Pool Criticality Calculation</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Both Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power at the time of discovery. Event Description: Modeling methods used to perform spent fuel pool criticality analysis have been determined to be non-conservative. Specifically, certain assumptions may result in Keff in excess of 0.95 for postulated off-normal conditions with 0 ppm boron concentration in the fuel pool. The design basis of the plant requires that fuel stored in the fuel pool remain = 0.95 Keff when fully flooded with unborated water. Event Cause: This event is the result of an original design condition. Corrective Action: Technical Specifications will be revised to include additional conservatism to account for uncertainties associated with modeling assumptions.
3692000004 | McGuire 1 | 05/25/2000 | 06/26/2000 | ML00372883 | <strong>McGuire Unit 1 Reactor Trip Resulting in an Unplanned Valid Actuation of an Engineered Safety Feature (ESF) and the Reactor Protection System (RPS)</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the ESF/RPS actuation, both Unit 1 and Unit 2 were in Mode 1 at 100% Power. Event Description: On May 25, 2000, Unit 1 experienced a failure of the output switch on vital inverter 1EVIA. This failure caused a loss of Channel 1 vital instrumentation and control power resulting in a false low Channel 1 steam generator (S/G) level input to the S/G Water Level Control System, commencing a feedwater system transient. Upon placing S/G water level control in Channel 2, the feedwater system transient continued in a manner which resulted in a trip of the 1A CF Pump due to high discharge pressure, followed by a Unit 1 reactor trip due to 1C S/G Low-Low Level. Upon receipt of subsequent Low-Low S/G Level inputs, the 1B Motor Driven Auxiliary Feedwater (CA) Pump and the Turbine Driven CA Pump auto-started. The lA Motor Driven CA Pump was manually started, as it did not auto-start since its control circuitry is supplied power from Channel 1 vital control power, which was lost. In addition, post-trip operator actions resulted in the auto-alignment of the CA pumps suction to the assured source when the normal non-safety related water supplies were isolated. Event Cause: Mechanical related failure of the 1EVIA inverter output switch. Failure to correctly follow procedure when aligning CA pump suction sources. Corrective Action: Replaced vital inverter switches as needed. Future modifications will eliminate switches of this design. Plant procedures revised to preclude inadvertent alignment of CA pump suction to the assured source. Operator training (RO only) will be reviewed to examine proficiency in the use of 2 column format procedures as related to this event.
3702000001 | McGuire 2 | 10/10/2000 | 11/08/2000 | ML00376932 | <strong>Inadvertent Start of the Turbine Driven Auxiliary Feedwater Pump During Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 3 (Hot Standby) at 0% Rated Thermal Power at the time of occurrence. Event Description: On October 10, 2000, there was an inadvertent start of the Unit 2 Turbine Driven Auxiliary Feedwater (TDCA) Pump. The start occurred during performance testing of the turbine driven pump. The testing procedure provides for installation of electrical jumpers to prevent the start of the pump during performance of the test. Personnel performing the test failed to correctly install all of the required jumpers. As a result, when the pump switch was placed in the start position, per the test procedure, the pump started and ran for approximately 3 minutes injecting water into all four Steam Generators. Event Cause: Personnel Error due to Deficient Communications and Inappropriate Procedure Use and Adherence. Corrective Action: Individualized coaching of the individuals involved on the importance of effective communications and the importance of strict procedure adherence during testing of plant equipment.
3732000001 | LaSalle 1, LaSalle 2 | 02/17/2000 | 03/17/2000 | ML00369466 | <strong>Inadequate Implementation of Technical Specification Surveillance Requirements Results in Missed Surveillance on Reactor Core Isolation Cooling Time Delay Relays</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2000, Units 1 and 2 were in Operational Mode 1 at 100% power. At 1600 hours, based on a review of all safety-related time delay relays listed in procedure LTP-100-6, "Time Delay Relay (TDR) Calibration Program," it was concluded that the quarterly Technical Specification surveillance channel calibration for the Reactor Core Isolation Cooling (RCIC) steam line high flow isolation logic did not include time delay relays 1(2)E51A-K47 and 1(2)E51A-K48. The associated pressure switch is calibrated quarterly and the time delay relay is calibrated each refueling cycle. Since the time delay relay is part of the instrument channel, it should have been calibrated quarterly. Corrective actions were to calibrate the RCIC steam line high flow isolation logic time delay relays and to revise the instrument surveillance procedures. The safety significance of the event was minimal. The operability of the Emergency Core Cooling Systems was not challenged. When tested, the time delay relays were found within calibration tolerances.
3732000002 | LaSalle 1 | 04/26/2000 | 05/26/2000 | ML00372325 | <strong>Inadvertent Reactor Water Cleanup System Isolation During System Startup Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2000, Unit 1 was in Operational Mode 1 at 100 percent power. The Reactor Water Cleanup System (RT) [CE] was being placed in service in accordance with procedure LOP-RT-02, "Reactor Water Cleanup System (RWCU) - Startup and Pump Transfer." At 1318 hours, the inlet isolation valve (1G33-F004) was opened, and an Engineered Safety Feature (ESF) isolation of the RT system occurred on high suction flow. The RT system was walked down to verify that there was no system leakage, and the RT system was subsequently placed in service. The causes of this event were personnel error and defective procedures. Licensed control room operators failed to follow the procedural requirements of procedure LOP-RT-02 verbatim, and the procedure was also deemed to be inadequate. Corrective actions include training and procedure enhancements. The safety significance of the event was minimal. The RT isolation valves operated as designed, there was no leakage from the system, and operation of the reactor was not directly or immediately affected by isolation of the system during a return to service.
3732000004 | LaSalle 1, LaSalle 2 | 07/17/2000 | 08/16/2000 | ML00373661 | <strong>Inadequate Channel Functional Testing of Reactor Protection System due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2000, it was determined that procedure LOS-RP-Q3, "Main Steam Isolation Valve (MSIV) Scram Functional Test," did not include all the steps necessary to perform a complete channel functional test (CFT) as required by Technical Specification (TS) 3.3.1, "Reactor Protection System Instrumentation." The procedure only verified that at least one of the two limit switches on each MSIV would provide a position signal to the reactor protection logic. At 1625 hours on July 17, 2000, a 24-hour shutdown time clock was entered per TS 4.0.3, on both Units 1 and 2. LOS-RP-Q3 was revised to correct the deficiency, and the CFT was acceptably performed on both Units. The time clocks were exited at 0150 hours on July 18, 2000 for Unit 2, and 0515 hours on July 18, 2000 for Unit 1. The cause of the event was a pre-existing procedure deficiency that was due to insufficient rigor in the procedure preparation and review process. Corrective actions included revising the affected procedure, and communicating the event to all technical procedure writers. The safety significance of the event was minimal. Successful performance of the corrected procedure demonstrated that the MSIV limit switches would have performed their intended safety function.
3742000001 | LaSalle 2 | 02/09/2000 | 03/10/2000 | ML00369466 | <strong>2B Diesel Generator Unavailable for Restart Due to Diode Failure</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2000, at 1212 hours the 2B Diesel Generator (DG) start logic control power fuses blew prior to the conclusion of the monthly operability run during an unexpected reverse power trip of the diesel. This rendered the 2B DG unavailable for subsequent restart. The 2B DG provides the emergency power to the High Pressure Core Spray (HPCS) System. Troubleshooting determined that the unexpected DC power failure in the diesel start logic was the result of a shorted diode installed in parallel with the output breaker permissive relay. The shorted diode resulted in the blowing of the two start logic control power fuses. The diode and fuses were replaced and the 2B DG was returned to service at 0804 on February 10, 2000. The safety significance of the event was minimal. The HPCS was still available with normal power. The operability of the redundant Emergency Core Cooling Systems was not challenged.
3742000002 | LaSalle 2 | 02/17/2000 | 03/17/2000 | ML00369612 | <strong>Clerical Errors During Construction Result in Missed Augmented Weld Examinations for Residual Heat Removal System Welds RH-2005-28 and 29</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2000, Commonwealth Edison Company (ComEd) determined that two Category D welds on Unit 2 had not been inspected per the schedule provided in Generic Letter 88-01, "NRC Position on IGSCC in BWR Austenitic Stainless Steel Piping," dated January 25, 1988. These inspections are augmented inspection requirements of the LaSalle County Station Inservice Inspection (ISI) program, and a requirement of Technical Specification 4.0.5.f. Since one weld was examined during the seventh refueling outage, it currently meets its surveillance requirement. A Notice of Enforcement Discretion was requested and approved on February 18, 2000, for the missed surveillance on the other weld. An exigent Technical Specification amendment was docketed on February 22, 2000, in order to defer inspection of the missed weld until the next refueling outage. The root cause of the missed weld inspections is human error in the form of clerical errors in 1983. Corrective actions included performance of deterministic and probabilistic evaluations, which demonstrated that the structural integrity of the affected systems was not adversely impacted by these missed weld inspections.
3742000003 | LaSalle 2 | 06/22/2000 | 07/24/2000 | ML00373661 | <strong>Scram on Low Reactor Water Level Due to Los of 2A Turbine Driven Reactor Feed Pump Flow</strong><br /><i>Abstract:&nbsp;</i>At 0728 hours on June 22, 2000, LaSalle Unit 2 experienced an automatic reactor scram due to low reactor water level. The low reactor water level was caused by a loss of flow from the 2A turbine driven reactor feed pump (TDRFP). The root cause of the event was the intrusion of wear products into the high pressure control oil pressure regulating relief valve (2FW199A). The wear products became lodged between the relief valve seat and disk, which allowed the oil system pressure to be relieved. This caused the 2A TDRFP control valve to close, and the loss of flow from the 2A TDRFP. The resulting reactor water level transient led to the automatic scram. The corrective action was to install duplex oil filters on the 2A and 2B TDRFP high pressure control oil systems. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The Emergency Core Cooling Systems were not challenged.
3742000004 | LaSalle 2 | 09/01/2000 | 10/02/2000 | ML00374518 | <strong>Reactor Core Isolation Cooling (RCIC) Isolation Due to RCIC High Steam Flow Indication</strong><br /><i>Abstract:&nbsp;</i>At 1420 hours on September 1, 2000, LaSalle Unit 2 was preparing to return Reactor Core Isolation Cooling (RCIC)(BN) to service in accordance with procedure LOP-RI-05, "Preparation for Standby Operation of the Reactor Core Isolation Cooling System." Fifteen seconds after opening the RCIC Warm-up Bypass valve 2E51-F076, a RCIC Steam Line Differential Pressure alarm was received and valve 2E51-F076 closed automatically due to a RCIC High Steam Flow containment isolation signal. The root cause of the event was the presence of water on the upstream side of valve 2E51-F076. The water flashed into steam when valve 2E51-F076 was opened, resulting in a momentary high steam flow signal, which resulted in a containment isolation signal. Procedure LOP-RI-05 will be revised to isolate the steam flow instrumentation from service until valves 2E51-F076 and RCIC Steam Line Outboard Isolation valve 2E51-F008 have both been opened. The safety significance of this event was minimal. The Emergency Core Cooling Systems were not challenged and were fully operational.
3742000005 | LaSalle 2, LaSalle 1 | 09/13/2000 | 10/13/2000 | ML00376047 | <strong>Inadvertent Start of 2A Diesel Generator Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2000, during performance of procedure LOS-RH-Q1 Attachment 2E, "Unit 2B RHR Service Water Operability and Inservice Test," the Unit 2 licensed Reactor Operator (RO) inadvertently started the 2A Diesel Generator (DG) when he intended to start the Diesel Generator Cooling Water Pump (2DG01P). The cause of this event was personnel error on the part of the Unit 2 RO, in not performing an adequate self check and not obtaining an adequate peer check. Corrective actions included a review of verification techniques with all operating crews and issuance of a Daily Order re-emphasizing the requirement for peer check of control room manipulations. The safety significance of this event was minimal. The 2A DG remained operable during the event, as did the normal AC power sources and the 0 DG and 2B DG.
3742000006 | LaSalle 2 | 12/01/2000 | 01/02/2001 | ML01009028 | <strong>Unit 2 Scram on Turbine Control Valve Closure Due to High Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2000, at 1105 hours, during power ascension from refuel outage L2R08, operators were placing the 2B Turbine Driven Reactor Feedwater Pump (TDRFP) on line. A reactor water level transient occurred that resulted in an automatic high level trip of the main turbine and an associated reactor scram. All equipment operated as expected during the post-trip plant response. The investigation has identified two root causes for this event. There was a human performance component, primarily related to inadequate evolution preparation including failure to perform a Heightened Level of Awareness (HLA) briefing. The second root cause is poor design combined with materiel conditions in the Feedwater and Reactor Level Control system that results in sluggish response of the control system leading to an increased operational challenge. Corrective actions include revising the TDRFP startup procedure, requiring a High Level Activity brief as part of the Reactor Feedwater start up procedure, and a review of the system design and material condition for improvements. The safety consequences of this event were minimal. All systems operated as expected. A turbine trip is an analyzed condition of moderate frequency. The reactor was safely shut down and recovery performed without incident.
3822000001 | Waterford 3 | 01/05/2000 | 02/04/2000 | ML00368172 | <strong>An Appendix R Non-Compliance Outside Design Basis Condition Involving An Inoperable Sprinkler System</strong><br /><i>Abstract:&nbsp;</i>On January 5, 2000, with the plant operating in Mode 1 at 100% reactor power, it was determined, during reviews of sprinkler system hydraulic calculations, that a fire protection sprinkler system (FPM-1 8) was inoperable due to system demand exceeding fire pump capability in Fire Area RAB 6. Compensatory measures (continuous fire watches) were established in the Fire Area. Electrical cables for both trains of reactor safe shutdown equipment are routed through the fire area. It was determined that the sprinkler system did not meet original design requirements. Initially, it was believed that actual fire loading in the affected fire area was less than the one hour protection provided by the cable raceway fire enclosures installed on essential Train `B' raceways in that area. However, during subsequent reviews, it was determined on January 6, 2000 that fire loading in that area actually exceeded one hour. At that point, it was recognized that the condition was outside the design bases and a one-hour notification was made to the NRC. No actual fire event occurred. The condition was determined to be due to an inadequate original design configuration. Corrective measures are being addressed under the plant corrective action program. The condition did not compromise the health and safety of the general public. This event is not considered a Safety System Functional Failure (SSFF).
3822000002 | Waterford 3 | 03/03/2000 | 04/03/2000 | ML00370070 | <strong>Technical Specification Violations Due to Plant Mode Changes WIth Inoperable Steam Generator Snubbers</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2000, with the plant operating in Mode 1, at approximately 100% reactor power, it was determined that the plant had changed modes, during two plant outages between Refuel 8 and Refuel 9 and during cooldown for entry into Refuel 9, with an inoperable Steam Generator (#1). Both Steam Generators were required by Technical Specifications. The Steam Generator became inoperable when three of four snubbers on the Steam Generator became inoperable during plant cooldown / heatup mode changes in Modes 3 and 4. Leaks in snubber reservoir hoses or hose connections had resulted in loss of fluid level to just above the control valve on each of the three snubbers, allowing air to enter the snubber during cooldown / heatup. An operability review (performed on March 3, 2000) indicated that, based on the level of fluid remaining, the snubbers would not have functioned properly in Modes 3 and 4. The condition was not reported during Refuel 9 due to a human performance error associated with the original operability calculation. The condition no longer existed when the hoses were replaced and fluid levels were restored during Refuel 9. The condition is hereby being reported for past operability considerations for violation of Technical Specifications. There were no actual seismic events associated with the condition. The affected Steam Generator was determined to have been operable during Modes 1 and 2 plant operations. This condition is not considered a Safety System Functional Failure (SSFF). The condition did not compromise the health and safety of the general public.
3822000003 | Waterford 3 | 03/06/2000 | 04/05/2000 | ML00370368 | <strong>Shutdown Per TS LCO 3.0.3 Due to Cracked Weld Which Rendered the Charging System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 3/6/00, Waterford 3 was shut down per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 due to a weld crack adjoining a hydrostatic test connection on the Charging Pump A suction line. Since the cracked weld was unisolable from the Charging header, all three Charging Pumps were declared inoperable. Technical Specification LCO 3.1.2.4 requires at least two Charging Pumps to be Operable and does not contain Actions for three Charging Pumps inoperable. Therefore, TS LCO 3.0.3 was entered. On 3/6/00, at approximately 0715, an Auxiliary Operator discovered boric acid buildup on the socket weld adjoining a hydrostatic test connection on Charging Pump A suction piping. Subsequent investigation by Engineering and Maintenance resulted in identifying visual indication of leakage (approximately one drop every two minutes) through an approximate 1/4 inch full penetration crack. Since the crack cannot be isolated from the Charging header, all three Charging Pumps were declared inoperable and TS LCO 3.0.3 was entered at 1145. There is no safety significance associated with this event. The Charging System remained capable of performing its design function (emergency boration and coolant injection) throughout the event. This event had no adverse affects on health and safety of the general public. This event is not considered a Safety System Functional Failure (SSFF).
3822000004 | Waterford 3 | 04/13/2000 | 05/15/2000 | ML00371713 | <strong>Potential Degradation of Feedwater Isolation Valves due to Design Basis Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 3/21/00, with Waterford 3 operating at 100% power, it was identified that both Feedwater Isolation Valves (FWIVs) may have closed faster than the 1.5 second design basis limit. A new calculation methodology and the latest stroke time data were used to make this determination. On 4/13/00, an evaluation determined that within the last two years there were seven occasions in which the percent increase in fast valve closure load caused by waterhammer from quicker stroke times exceeded the values provided to maintain operability. These forces may have exceeded the capability of piping supports, which could have resulted in the subsequent loss of the containment isolation function. This is reportable under 10CFR50.73(a)(2)(ii)(B) as a condition that was outside the design basis of the plant. Based on an evaluation of the present conditions and immediate actions, it was determined that the FWIVs and their associated penetrations could perform their required safety functions. The root cause of this condition was Entergy's acceptance of vendor analysis without adequate review and insufficient awareness of the impact of actions on safety/reliability. Corrective actions are being addressed under the plant corrective action program. This event did not compromise the health and safety of the public.
3822000005 | Waterford 3 | 04/27/2000 | 05/26/2000 | ML00371985 | <strong>Operating in a Condition Prohibited by Technical Specification 3.6.2.2 Due to and Inoperable Containment Fan Cooler</strong><br /><i>Abstract:&nbsp;</i>On 4/24/00, at 22:16 hours, Containment Fan Cooler (CFC) "C" tripped and was declared inoperable. The action statement of Technical Specification (TS) 3.6.2.2 was entered that required CFC "C" to be restored to operable status within 72 hours. A visual inspection of CFC "C" found evidence that the fan blades had rubbed against the shroud and the fan blade edges were damaged. An on-line repair was not feasible within 72 hours. The other three CFCs were inspected and tested to provide assurance that a similar condition did not exist. On 4/26/00 Entergy verbally requested the NRC Staff to exercise discretion not to enforce compliance with TS 3.6.2.2 Limiting Condition for Operation, to remain in effect until Technical Specification Change Request NPF-38-224 (requests approval to allow one operable CFC per train) is approved or an outage of sufficient duration occurs to accommodate repair of the CFC. The NRC orally issued the Notice of Enforcement Discretion (NOED) on 4/27/00 and confirmed NOED 00-6-006 in writing on 5/1/00. On 4/27/00 at 22:16 hours, Waterford 3 exceeded the allowed outage time of TS 3.6.2.2. There is no safety significance associated with this event. The Containment Cooling System remains capable of performing its design function. This event had no adverse affects on the health and safety of the public and is not considered a Safety System Functional Failure.
3822000006 | Waterford 3 | 05/11/2000 | 06/12/2000 | ML00372438 | <strong>Both Channels of Chlorine Detectors Found Outside Technical Specification (2 ppm) Limits</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2000, with the plant operating in Mode 1, at approximately 100% reactor power, it was determined that the plant had apparently operated, in April of 1999, with both chlorine monitor channels outside of the Technical Specification (2 ppm) limit for setpoint / alarm actuation. This condition was observed during reviews of surveillance test records associated with a related plant condition (condition report CR-2000-0282). Test results indicate that both chlorine monitors had apparently drifted outside the Technical Specification limit. This condition is considered a multiple test failure and, therefore is an indication that the condition developed overtime, beyond the allowed outage time of Technical Specification 3.3.3.7.1. The discovered condition was entered into the plant corrective action program (CR-2000-0400). Both chlorine monitor sensors were replaced at the time of calibration in April of 1999. The condition is being reported here on the basis of past operability. The monitors are tested monthly and had acceptable test results in the two months preceding the subject failed tests. A review by Engineering determined that both of the two monitors would have functioned within the required time to protect the Control Room Operators if the worst case Chlorine leak had occurred during the month of April 1999. This event is not considered a Safety System Functional Failure (SSFF). The condition did not compromise the health and safety of the general public.
3822000007 | Waterford 3 | 08/24/2000 | 09/21/2000 | ML00375516 | <strong>Technical Specification Action Not Met Due to an Invalid Sample for an Inoperable Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On 8/24/2000, it was discovered that the eight-hour grab samples taken for an out of service radiation monitor did not meet the intent of the Technical Specification Action Statement. This condition was discovered when plant personnel questioned the validity of the samples being taken from the Component Cooling Water (CCW) system to comply with the Technical Specification (TS) 3.3.3.1 Action Statement. The causal factor was determined to be the omission of relevant information in plant procedures. A valid sample was taken upon discovery of this condition, and data from the operable CCW A and B monitors was reviewed. The data did not indicate a higher trend in activity. This event did not threaten the health and safety of the public or plant personnel, and the safety significance of this event is negligible. This event is not considered a Safety System Functional Failure (SSFF).
3822000008 | Waterford 3 | 09/14/2000 | 10/13/2000 | ML00376050 | <strong>Operating in a Condition Prohibited by TS 3.3.1 due to an Inoperable Core Protection Calculator Channel</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2000, at approximately 0100 hours, I&C Technicians performed a Technical Specification Surveillance on Core Protection Calculator (CPC) channel "B". They failed to recognize that the inputs were out of tolerance and made no adjustments as required by procedures. The channel was erroneously placed back in service and declared operable. The error was caught during the I&C Supervisor's review at approximately 0648 hours the same day. A condition report was generated and Operations was notified. CPC channel B was declared inoperable, and TS 3.1.1 was entered. Rework was commenced to re-perform the calibration. The channel was declared operable at 1225 hours the same day. This condition is being reported as a condition prohibited by Technical Specifications since the channel should not have been declared operable and taken out of "bypass". There is no safety significance associated with this event. Although there was one CPC channel inoperable, the remaining 3 channels remained operable and provided the required plant protection. This event is not considered a Safety System Functional Failure (SSFF).
3822000009 | Waterford 3 | 09/18/2000 | 10/18/2000 | ML00376275 | <strong>Potential for Loss of Safe Shutdown Equipment by a Fire in Either of Two Separate Fire Areas</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2000, with the plant operating in Mode 1, at approximately 100% reactor power, it was determined that a condition existed wherein an Appendix R fire in Fire Area RAB 2 could conceivably render safe shutdown equipment (Essential Chillers / RAB HVAC AH-13 / E-41 Fans) inoperable. During review of the Waterford 3 safe shutdown analysis, it was observed that six designated, essential cables were not listed as requiring one hour fire wrap and were not wrapped in the field. Later, while reviewing for other similar cases, it was discovered that cables associated with other equipment (Charging Pumps) required for cold shutdown were also not properly provided with one-hour wrap in fire area RAB 39. The conditions have primarily existed since initial construction (1984 time frame) and resulted from original design inadequacies in Waterford 3's safe shutdown analysis. In one case, the condition was caused by an inadequate design change (1992 time frame). The conditions are being reported as being outside the design basis of the fire protection program. The cables and conduits were immediately identified as impaired and compensatory actions were established (hourly fire watches). The condition was entered into the plant corrective action program (CR-WF3-2000-1088 and -1169). There was no actual fire involved. The condition did not compromise the health and safety of the general public. This condition is not considered a Safety System Functional Failure (SSFF).
3822000010 | Waterford 3 | 09/25/2000 | 10/25/2000 | ML00376453 | <strong>Non-conservative Essential Chiller Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 9/25/00, while re-evaluating the setpoints of the essential chiller, Design Engineering discovered that the 42 °F chiller outlet water temperature value in Technical Specification (TS) Surveillance Requirement (SR) 4.7.12.1 b was not protecting an assumption in a design basis calculation. A design calculation, 5T, "Essential Chilled Water", assumed a chiller outlet water temperature of 41.5 °F, so the SR value of 42 °F causes the SR to be non-conservative. When the past SR data was reviewed, it was discovered that there were occasions when the chiller outlet water temperature was higher than the design calculation assumed. The intent of the SR was not met for these instances and is reportable as a condition prohibited by plant TS per 10 CFR 50.73(a)(2)(i)(B). The root cause was not adequately communicating changes to the design calculation. The chiller outlet water temperature was verified to be within the new limit to protect the design calculation assumption, including instrument uncertainty. This event did not compromise the health and safety of the public. This event is not considered a Safety System Functional Failure (SSFF).
3822000011 | Waterford 3 | 10/17/2000 | 11/16/2000 | ML00377050 | <strong>RCS Pressure Boundary Leakage Due to PWSCC and Leaking MNSA Clamps</strong><br /><i>Abstract:&nbsp;</i>This LER documents three separate cases of Reactor Coolant System (RCS) pressure boundary leakage discovered during Waterford 3's Refuel 10 outage. The first case of leakage was discovered during inspections on October 17, 2000 and involved evidence of leakage at a Pressurizer heater sleeve (F-4). The other two cases of leakage were discovered during inspections on October 19, 2000 and involved evidence of leakage at two of the three MNSA clamps that had been installed during the Refuel 9 outage as temporary repairs of leaking RCS nozzles. The conditions are being reported as violations of Technical Specification 3.4.5.2a, which allows no RCS pressure boundary leakage. Although it cannot be determined exactly when the leakage actually occurred, in one case, it is believed to have occurred sometime after a planned outage conducted during June 2000. Inspections (with insulation on) conducted during that earlier outage did not identify MNSA clamp leakage. The three leakage cases were due to 1) Primary Water Stress Corrosion Cracking (PWSCC), 2) a MNSA clamp flange not being flat against the pipe and 3) a MNSA clamp seating itself, respectively. These conditions have been corrected by plugging the pressurizer heater sleeve, and by removing the MNSA clamps and making permanent weld repairs on the nozzles. The leakage did not compromise the health and safety of the general public. The conditions are not considered Safety System Functional Failures (SSFF).
3822000012 | Waterford 3 | 11/13/2000 | 12/13/2000 | ML00377839 | <strong>Mode Change in Violation of Technical Specifications Due to a Mispositioned Control Panel Switch</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2000, with the plant shut down in Mode 5 and starting up from the Refuel 10 outage, a plant mode change was made from Mode 5 to Mode 4 with the control switch for Charging Pump B in the "off” position. Technical Specification 3.1.2.4 requires two operable Charging Pumps to make this mode change. Operable, in this case, means that the pump is capable of starting in response to a safety injection actuation signal. Therefore, Charging Pump B was inoperable when the mode was changed, since the switch being in the off position prevented the pump from being capable of an automatic start. The event is being reported as a violation of plant Technical Specifications. The condition was discovered approximately 8 hours after the mode change was made. The mode change checklist does not provide an organized method of verifying that control panels are configured as required for mode changes. Contributing causes included Operator fatigue and supervisory distractions due to administrative burden. The condition did not compromise the health and safety of the general public. Corrective measures are currently being evaluated in the Corrective Action Program (CR-WF3-2000-1515). In the interim, Operator awareness is being heightened via required reviews of the associated root cause analysis. The condition is not considered a Safety System Functional Failure (SSFF).
3822000013 | Waterford 3 | 11/16/2000 | 12/18/2000 | ML00378099 | <strong>Technical Specification Violation Due to Failure to Perform Surveillance Required for Mode Change</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2000 at 0519, the plant entered mode 1 while coming out of a refueling outage. OP-903-001, Technical Specification (TS) Surveillance Logs, Attachment 11.1 was completed on November 17, 2000 at 0410 for a planned power ascension to mode 1. Under TS 4.0.4, an entry into an operational mode or other specified condition shall not be made unless the Surveillance Requirement(s) associated with the Limiting Condition for Operation have been performed within the stated surveillance interval or as otherwise specified. TS Surveillance 4.2.5 is applicable in mode 1 and states that "the actual Reactor Coolant System total flow rate shall be determined to be greater than or equal to the above limit [148.0 x106 Ibm/h] at least once per 12 hours." This surveillance was not performed prior to entry into mode 1; therefore, the plant did not operate in compliance with TS 4.0.4. The cause of this event was determined to be personnel work practice in that an intended verification was not performed. A contributing cause to this was the physical layout and format of the instructional steps. Operations personnel will be briefed on this event, and the procedures involved in this event will be revised. This event did not compromise the health and safety of the general public. This event is not considered a Safety System Functional Failure (SSFF).
3872000001 | Susquehanna 1, Susquehanna 2 | 02/02/2000 | 03/03/2000 | ML00369159 | <strong>Inadequate System Design Documentation Leads to Missed 10CFR50 Appendix J Testing.</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2000 with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100% power, engineering personnel (utility, non-licensed) discovered that testing required by 10CFR50 Appendix J had not been performed for piping and panels in the Hydrogen-Oxygen (H202) Analyzer system and the gas sampling portion of the Post Accident Sampling System (PASS). The affected system components will be called the Containment Atmosphere Monitoring (CAM) system in this report. Testing had been performed to NUREG 737 requirements, but it had not been recognized that 10CFR50 Appendix J requirements applied to this system as an extension of containment. The root cause of this event is that the documentation provided for the CAM system was inadequate to clearly identify the system as a closed boundary that is an extension of containment that requires 10CFR50 Appendix J leak rate testing. Several causal factors were also identified in the areas of organizational responsibility, multiple design configurations and corrective actions. Corrective actions include development and performance of required testing, comprehensive review of containment design documentation, enhancements to the Corrective Action Program, and to update and provide training on primary containment systems. This event is reportable per 10CFR50.73(a)(2)(i)(B), operation or condition prohibited by the plant's Technical Specifications. The safety significance of this event is low, and the health and safety of the public was not compromised.
3872000002 | Susquehanna 1 | 03/24/2000 | 04/21/2000 | ML00371051 | <strong>Main Steam Isolation Valve Total Leakage Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 0445 hours on March 24, 2000, with Unit 1 in its eleventh refueling and inspection outage (Mode 5, Refueling, 0% power), an evaluation of data from the scheduled Main Steam Line (MSL) penetration Local Leak Rate Testing (LLRT) determined that the "as-found" maximum pathway leakage for the Main Steam Isolation Valves (MSIV) was in excess of the limit of Technical Specification 3.6.1.3 for the MSL containment penetration maximum pathway leakage of 300 standard cubic feet per hour (SCFH). The total "as-found" maximum pathway leakage could not be determined since one of the MSIVs was unable to be pressurized. However, the total "as-found" minimum pathway leakage was only 135 SCFH. The evaluation determined that the MSIV LLRT excess "as-found" maximum pathway leakage was reportable pursuant to 10CFR50.73(a)(2)(ii). The cause was determined to be that two (2) MSIVs had excessive leak rates. This excessive leakage was due to a misalignment of the poppet to body seat on the "C" inboard MSIV and due to a metal piece embedded in the upper guide surface of the poppet in the "A" outboard MSIV. The corrective actions included reworking of the MSIVs and retesting them to ensure they were left below the Technical Specification limits. Since the leakage (the minimum path leak rate - 135 SCFH) that would have actually reached the main condenser is below the 300 SCFH analyzed in the dose calculations, there were no safety consequences or compromises to public health and safety as a result of this event.
3872000003 | Susquehanna 1, Susquehanna 2 | 03/23/2000 | 04/24/2000 | ML00371204 | <strong>Multiple Test Failures of Suppression Chamber-to-Drywell Vacuum Breakers</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2000 with Unit 1 in Mode 5 (Refueling) and Unit 2 in Mode 1 (Power Operation) at 100% power, five of ten Unit 1 Suppression Chamber-to-Drywell Vacuum Breakers (vacuum breakers) failed the opening setpoint surveillance test, required by Surveillance Requirement 3.6.1.6.3. The acceptable band for the opening setpoint is 0.250 to 0.525 psid. The five valves which failed had opening setpoints of 0.526 to 0.540 psid, due to setpoint drift. With implementation of Improved Technical Specifications (ITS), the setpoint band was widened from 0.475-0.525 psid to 0.250-0.525 psid, however, the last adjustments to Unit 1 vacuum breakers were made prior to ITS implementation. Corrective actions include adjustments to the opening setpoint for all vacuum breakers and revision of the maintenance procedure for vacuum breaker adjustment. This event is reportable per 10CFR50.73(a)(2)(i)(B), operation or condition prohibited by the plant's Technical Specifications, based on the example provided in NUREG-1022, Revision 1 concerning multiple test failures. The safety significance of this event is low, and the health and safety of the public was not compromised.
3872000004 | Susquehanna 1 | 03/27/2000 | 04/26/2000 | ML00371187 | <strong>Actuation of Reactor Water Cleanup High Differential Flow Isolation Logic During RWCU System Draining</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2000, at 1734 hours, with Unit 1 in Condition 5 (Refueling) at 0 percent power for the Unit 1 Eleventh Refueling and Inspection Outage, an Engineered Safety Feature (ESF) actuation occurred when the Reactor Water Cleanup (RWCU) System's isolation logic actuated for its inboard and outboard primary containment isolation valves. The isolation logic actuated due to a valid high differential flow signal that was generated when water was inadvertently drained from the reactor vessel to the RWCU Filter Demineralizer Backwash Receiving Tank (BWRT) during system draining. The Unit 1 reactor vessel cavity was flooded and cross-tied to the Unit 1 and Unit 2 Spent Fuel Storage Pools. The event allowed approximately 1,100 gallons of water to flow from this reservoir into the BWRT. The inboard and outboard primary containment isolation valves did not move from the open to the closed position during the event because the high flow and high differential flow isolation actuation logic for the valves had been bypassed in accordance with procedure. The event was terminated by closing isolation valves to the RWCU filter demineralizer. The event had an insignificant impact on nuclear safety and did not compromise public health or safety. The cause of the event was attributed to less than adequate drain procedure use by Operations personnel. The event was reviewed with applicable Operations personnel, emphasizing the importance of procedure adherence. There were also several causal factors associated with this event and other corrective actions, which include reviewing other drain procedures for adequacy and establishing a policy to verify system isolation boundaries for all system draining just prior to work.
3872000005 | Susquehanna 1 | 03/29/2000 | 04/28/2000 | ML00371190 | <strong>CRD Seismic Island Check Valves Did Not Meet Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2000, at 0200 hours, with Unit 1 in Condition 5 (Refueling) at 0 percent power, both of the in-series Control Rod Drive System (CRD) Seismic Island Check Valves (non 10CFR50, Appendix J, Option B valves) failed their leakage acceptance criteria. Both check valves had leakage past the valve seat that was not quantifiable. The valves were disassembled. The cause of failure for the check valves is believed to have been due to oxide buildup on the valve body bore and the disc. This buildup resulted in the valve disc sticking in the lifted position. The valves were replaced with in-line check valves. A leak test was performed successfully on each of the new valves. Since no design basis accident occurred, there were no safety consequences or compromise to the public health or safety as a result of the check valves not passing their leak test.
3872000006 | Susquehanna 1, Susquehanna 2 | 04/07/2000 | 05/08/2000 | ML00371441 | <strong>Invalid Local Leak Rate Tests For Testable Spectacle Flanges</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2000 with Unit 1 in Mode 5 (Refueling) and Unit 2 in Mode 1 (Power Operation) at 100% power, maintenance and engineering personnel (utility; non-licensed) determined that Local Leak Rate Tests (LLRT) performed on Unit 1 and 2 Residual Heat Removal system (EIIS Code: BO) testable spectacle flanges may not be valid due to the presence of an additional o-ring on each flange face that is not per design. The configuration of Unit 1 flanges was corrected and required testing was satisfactorily performed. It was concluded that Unit 2 was not in compliance with Technical Specification Surveillance Requirement 3.6.1.1.1, and a Request for Enforcement Discretion was submitted to the NRC and approved on April 8, 2000. The cause of the event is inadequate technical detail to maintain design configuration in the work plan. Corrective actions include correction of the flange reassembly work plans and enhancements to the work planning technical review process. This event is reportable per 10CFR50.73(a)(2)(i)(B), operation or condition prohibited by the plant's Technical Specifications, based on the failure to adequately perform Surveillance Requirement 3.6.1.1.1. The safety significance of this event is low because the presence of the third o-ring does not affect the pressure-retaining capability of the flange, actual leakage is significantly less than maximum allowed leakage, and any leakage through the seals would be treated prior to its release to the environment. The health and safety of the public was not compromised.
3872000007 | Susquehanna 1 | 04/14/2000 | 05/15/2000 | ML00371619 | <strong>Multiple Test Failures of Main Steam Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2000 with Unit 1 in Mode 5 (Refueling), five of eight Main Steam Relief Valves (MSRV) that were tested failed their as-found actuation pressure surveillance test required by Technical Specification Surveillance Requirement 3.4.3.1. The acceptable band for the as-found actuation pressure is plus or minus 1% of the nameplate setpoint pressure. Four of the five MSRVs that failed had as-found actuation pressures below the lower limit of minus 1% of the nameplate setpoint pressure. The remaining failed MSRV as-found setpoint was greater than the upper limit of plus 1%, but below the reactor vessel design pressure. The cause of the as-found actuation pressure surveillance MSRV failures is due to expected drift of the actuation pressures after exposure to in-service operation. Corrective actions include replacing all eight MSRVs removed for testing with refurbished MSRVs that have opening setpoints within plus or minus 1% of the nameplate setpoint pressure. This event is reportable per 10CFR50.73(a)(2)(i)(B), operation prohibited by the plant's Technical Specifications, based on the guidance provided in NUREG-1022, Revision 1, concerning multiple test failures. The safety significance of this event is low, and the health and safety of the public was not compromised.
3872000008 | Susquehanna 1 | 07/15/2000 | 08/24/2000 | ML00374556 | <strong>Operation Prohibited by Technical Specifications Due to Inoperable Reactor Vessel Level Switch</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2000, at 0400 hours with Unit 1 in Mode 1 at 100% power, Reactor Vessel Water Level Emergency Core Cooling System Actuation Switch LIS-B21-1 N031A was found with moisture inside its faceplate and determined to be operable. On July 17, 2000 two of the micro-switches within LIS-B21-1 N031A that provide input to the High Pressure Coolant Injection (HPCI) and the Reactor Core Isolation Cooling (RCIC) were found outside of Technical Specification allowable values. LIS-B21-1 N031A was replaced and returned to operable on July 18, 2000 at 0545 hours. On July 26, 2000, after an in-depth investigation, a follow-up engineering evaluation determined that LISB21-1 N031A had been inoperable from July 15, 2000 at 0400 hours until July 17, 2000 at 2115 hours without the applicable Technical Specification action statements met. The micro-switch failures are due to a minor external water leak into the instrument housing, which developed at the high pressure process connection following recent replacement of LIS-B21-1N031A. All similar in-service instruments were verified to be free from moisture. The cause for non-compliance with required LCO actions is that actions beyond Operations initial investigation were not immediately pursued. Applicable Operations personnel will review the event and the actions to be taken for similar instrument problems and other equipment problems. This event will be reviewed with applicable Instrumentation and Control personnel discussing the moisture induced micro-switch failures and potential impacts from defective process connections. The instrument will be shipped to a vendor for failure analysis. There was no compromise to the health and safety of the public due to this event since redundant instrumentation was operable.
3872000009 | Susquehanna 1, Susquehanna 2 | 08/10/2000 | 09/11/2000 | ML00375107 | <strong>Primary Containment Boundary Valves Not Checked Per Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>While Unit 1 and Unit 2 were operating at 100% power on August 10, 2000, engineering personnel identified that 87 Unit 1 and 85 Unit 2 primary containment boundary valves (instrument line vent and drain valves, and test connections on containment side of inboard primary containment isolation valves) had not been included in required surveillance testing. Decisions made previously to exclude the subject valves from surveillance requirements were based on a narrow definition of the terms associated with containment boundary components. Systems which are extensions of containment require any penetrations on that system to be included in surveillance requirements for containment penetrations. These events are reportable per 10CFR50.73(a)(2)(i)(B), Technical Specification Prohibited Operation or Condition, in that all valves required to be surveilled per Technical Specification 3.6.1.3 were not included in surveillance activities. All subject valves were surveilled and no leakage paths were identified. The valves have historically been controlled by administrative means and are infrequently operated. The significance of the event is low, and the health and safety of the public was not compromised. Corrective actions include revising Unit 1 and Unit 2 surveillance procedures to include the subject valves, clarifying the definitions associated with the Technical Specifications pertaining to primary containment components and a comprehensive review of containment boundary components and applicable surveillance requirements.
3872000010 | Susquehanna 1, Susquehanna 2 | 08/24/2000 | 09/25/2000 | ML00375514 | <strong>Operation of Control Room Smoke Removal Fans Causes Both Trains of Control Room Energency Outside Air Supply To Be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 24, 2000, with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100% power, control room operators observed the control structure at a negative differential pressure due to the operation of the Control Room Smoke Removal system. The smoke removal system was in service to exhaust odors resulting from welding associated with modification activities on ventilation ducts that were generated the previous day. It was later recognized that operation of the smoke removal system rendered both trains of the Control Room Emergency Outside Air Supply System (CREOASS) inoperable, which are required to maintain a positive pressure in the control structure in accident scenarios. The root cause of this event is personnel error, for failing to implement appropriate design changes or administrative controls on smoke removal system operation when the condition was identified in 1980. Corrective actions include revising the smoke removal system operating procedure to identify the impact on CREOASS operability, review of all control structure ventilation systems to verify no other adverse interaction exists between ventilation components, operator training and a design basis review to ensure control room habitability envelope and fire protection program requirements are satisfied. This event is reportable per 10CFR50.73(a)(2)(v), 10CFR50.73(a)(2)(i)(B), and 10CFR50.73(a)(2)(ii). There were no adverse consequences to the health and safety of the public at any time during this event.
3882000001 | Susquehanna 2 | 04/23/2000 | 05/22/2000 | ML00371882 | <strong>Entry Into Technical Specification 3.0.3 for LOCA/LOOP Logic Testing</strong><br /><i>Abstract:&nbsp;</i>At 1731 hours on April 23, 2000, Unit 2 entered Technical Specification (TS) 3.0.3 while in Mode 1 (Power Operation) at 100% power, in order to perform 24 month surveillance test SE-124-107, "Unit 1 Division I Diesel Generator LOCA/LOOP Test " for the electrical system on Unit 1, which was in Mode 5 (Refueling) at 0% power. At 1310 hours on April 27, 2000, Unit 2 again entered TS 3.0.3 while in Mode 1 (Power Operation) at 100% power, in order to perform 24 month surveillance test SE-124-207, "Unit 1 Division II Diesel Generator LOCA/LOOP Test" on Unit 1, which was in Mode 4 (Cold Shutdown) at 0% power. Each test placed one control structure chiller in "STOP" and the 4.16 kV Engineered Safeguards System Bus supplying power to the other control structure chiller was de-energized for approximately 10 seconds. Application of the Safety Function Determination Process (SFDP) at that time rendered both control structure chillers inoperable for approximately 10 seconds during each test. TS 3.7.3 and 3.7.4 require entry into TS 3.0.3 when both control structure chillers are inoperable. Both tests were successfully completed and TS 3.0.3 was exited prior to the need to commence a unit shutdown. All safety-related systems associated with the testing responded as required. These surveillance test procedures will be evaluated for revision to prevent entry into TS 3.0.3 and similar procedures will be reviewed to ensure all TS actions are accurately identified. The safety significance of this event is low, and the health and safety of the public was not compromised.
3882000002 | Susquehanna 2 | 04/24/2000 | 05/22/2000 | ML00371881 | <strong>Inadvertent Valve Closure In Containment Radiation Monitor System During Mainentance Activities</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2000 with Unit 2 in Mode 1 (Power Operation) at 100% power, the `B' channel Containment Radiation Monitor Inboard Primary Containment Isolation valves inadvertently closed. Maintenance activities were in progress to replace a relay for the 'A' channel Containment Radiation Monitor Inboard Isolation valves. The cause of the event was loose wiring terminations. Corrective actions include tightening of terminations, updating of design documentation to indicate the interrelationship of 'A' and 'B' channel components, and review of this event and corrective actions with maintenance personnel. This event is reportable per 10CFR50.73(a)(2)(iv), as an unplanned actuation of an Engineered Safety Feature. The safety significance of this event is low, and the health and safety of the public was not compromised.
3882000003 | Susquehanna 2 | 07/04/2000 | 08/02/2000 | ML00373858 | <strong>Inadvertent ESF Actuation Caused by Loss of RSP Power Supply</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power on July 4, 2000, Susquehanna Unit 2 experienced a half scram and Containment isolations due to an unexpected loss of the 'B' Reactor Protection System (RPS) bus. The loss of power was caused by a voltage transient on the output of the RPS Motor-Generator (MG), which resulted in a trip of the RPS MG output breaker. All Engineered Safety Feature (ESF) actuations occurred as intended per plant design. The cause of the event was a failure of the RPS MG voltage regulator, causing generator output voltage to decrease. Corrective actions include replacement of the failed voltage regulator, failure analysis of the failed component, revision of the preventive maintenance replacement frequency for all four RPS MG voltage regulators installed at Susquehanna, and an evaluation of design changes to improve reliability of the components. This event is reportable as an inadvertent invalid actuation of an ESF per 10CFR50.73(a)(2)(iv). The safety significance of this event is low, and the health and safety of the public was not compromised.
3882000004 | Susquehanna 2 | 07/17/2000 | 08/16/2000 | ML00374341 | <strong>Technical Specification Interpretations Incorrect - Operations Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2000 at 1500 hours, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, it was determined that interpretations of the plant's Technical Specifications for the actions to be performed, should a primary containment isolation barrier in the H202 Analyzer penetrations become inoperable, contained a non-conservative statement. The non-conservative statement directed that no Limiting Conditions for Operation (LCO) need be taken when one of the two Primary Containment Isolation Valves (PCIVs) becomes inoperable, since the isolation function of the two PCIVs was backed-up by a closed system. A subsequent review of work documents for the H2O2 Analyzer penetrations' PCIVs showed that from April 11, 2000 to April 14, 2000 one PCIV in a Unit 2 H202 Analyzer penetration had been inoperable and no LCOs were entered when required, due to the TSI. The root causes were attributed to (1) the FSAR not clearly reflecting the required design basis of the penetration and (2) human error in that at the time the TSI was developed, the preparer did not thoroughly research the licensing basis for the H2O2 Analyzer penetrations. The Technical Specification Interpretations (TSIs) for both units were revised to eliminate the non-conservatism. The remaining six (6) TSIS (3 on each unit) were reviewed to ensure that they did not contain non-conservative statements. The review concluded that these other TSIs did not contain any non-conservative statements. Actions are being implemented to eliminate the eight (8) existing TSIs (4 on each unit). Also, a Technical Specification change has been submitted to the NRC. Corrective actions remaining to be completed include (1) the deletion or revision of the procedure for processing TSIs and (2) revising of the FSAR to reflect the approved design of the penetration. There were no safety consequences or compromises to public health and safety since two of the three isolation barriers remained operable during this time period.
3882000005 | Susquehanna 2 | 12/05/2000 | 03/25/2003 | ML03092007 | <strong>ESF Actuations Due to RPS EPA Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>At 07:00 on December 5, 2000 with Unit 2 in Mode 1 at 100% power, the primary power supply to the "B" Reactor Protection System (RPS) power distribution panel was lost when the downstream Electrical Protection Assembly (EPA) breaker tripped. This resulted in Primary Containment Isolation System actuations and other automatic system initiations. RPS as well as other plant systems and components functioned properly in response to the event. The "B" distribution panel was swapped to alternate power while investigation of the event took place. There were no indications of abnormalities and all isolation signals were reset by 08:15. The investigation resulted in replacement of the downstream EPA logic card. The primary power source EPA breakers were reset and aligned to the "B" distribution panel at 18:11 on 12/9/00. The suspect faulty downstream EPA logic card was returned to the manufacturer to determine cause of failure. Manufacturer testing did not reveal any functional problems with the card. It has now been concluded (by virtue of an observed high resistance across the EPA Calibration/Test switch in-line contacts) that the power source signal to the EPA logic card was degraded thus causing the EPA breaker trip. The event is reportable under 10 CFR50.73(a)(2)(iv)(A) in that unplanned actuations of Engineered Safety Features occurred. Since all Engineered Safety Feature (ESF) systems and components functioned properly and per design, there were no safety consequences or compromises to the health or safety of the public.
3892000001 | St. Lucie 2 | 04/16/2000 | 05/14/2000 | ML00370343 | <strong>Cycle 11 Main Steam Safety Valves Surveillance Outside Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2000, St. Lucie Unit 2 was in Mode 1 at 68 percent power and the main steam safety valves were being lift tested in accordance with procedure 2-MSP-08.07, "Main Steam Safety Valve Setpoint Surveillance." During the surveillance testing the tested main steam safety valves lifted outside the ± 1 percent Technical Specifications (TS) limits. Three of the tested valves were adjusted and successfully retested in the field. One valve was left out of service since the as-found lift setting exceeded 3 percent low and will be removed, overhauled, retested, and reinstalled during the ongoing SL2-12 refueling outage. The cause of this event was determined to be setpoint drift. There was no impact on the out of specification lift settings on the St. Lucie accident analyses. Additionally, FPL recently submitted a license amendment to expand the range of allowed as found code safety valves lift setpoints consistent with the St. Lucie accident analyses.
3892000002 | St. Lucie 2 | 04/24/2000 | 05/24/2000 | ML00371953 | <strong>Valve V3523 Not Fully Closed Results in Operation of Facility Outside TS</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2000, St. Lucie Unit 2 was shutdown in Mode 6 during the SL2-12 refueling outage. Valve V3523, a motor operated valve (MOV) for 2B hot leg injection, was being worked to investigate the reason why the valve would not fully close. FPL discovered that the cause of the inability of V3523 to close was the presence of foreign material inside the valve. FPL concluded that past operation of St. Lucie Unit 2 between December 4, 1998, and December 16, 1998, when compensatory measures were implemented to maintain valve V3523 in its throttled position, was in a condition prohibited by Technical Specifications. The valve was reworked and placed back in service.
3892000003 | St. Lucie 2 | 07/08/2000 | 08/07/2000 | ML00374265 | <strong>TSP Surveillance Methodology Differed From Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 8, 2000, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. FPL determined that differences between surveillance procedure 2-COP-07.07, "Analysis of Unit 2 Trisodium Phosphate (TSP) for pH and Volume Requirements," and St. Lucie Unit 2 Technical Specification Surveillance 4.5.2.e.4. constituted a literal non-compliance with the Technical Specifications. However, on July 8, 2000, a TSP basket was sampled and analyzed in accordance with Technical Specification requirements and compliance was established. The cause of this event was personnel error in that the Technical Specification surveillance method was not correctly translated into the implementing procedure. Procedure 2-COP-07.07 was revised to comply with the literal wording of the Technical Specification requirements. Other chemistry procedures that implement Technical Specification surveillances were reviewed for verbatim compliance and no other issues were identified. This event had no impact on the health and safety of the public.
3892000004 | St. Lucie 2 | 08/16/2000 | 09/14/2000 | ML00375129 | <strong>As Found Cycle 11 Pressurizer Safety Valve Setpoints Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2000, St. Lucie Unit 2 was in Mode 1 at approximately 100 percent reactor power. Wyle Labs informed FPL of unsatisfactory test results for two of the three code pressurizer safety valves removed during the cycle 12 refueling outage. Wyle Labs was contracted to perform the offsite pressurizer safety valve testing and the testing was conducted within the required time restraints. Technical Specification 3.4.2.1 requires the PSVs to lift at 2500 psia (+/-1 percent). The as found settings of two St. Lucie Unit 2 pressurizer safety valves were 1.51 and 2.98 percent high, outside the Technical Specification tolerance limit of +/- 1 percent. The cause of the failed pressurizer safety valve tests was due to mechanical setpoint drift over the operating cycle. There is no past or present operability concern as the subject pressurizer safety valves were removed and replaced with pre-tested valves during the St. Lucie Unit 2 cycle 12 refueling outage. There was no affect on the health and safety of the public during past St. Lucie Unit 2 cycle 11 power operations because the limiting overpressure analyses remain bounding for the as-found condition.
3902000001 | Watts Bar 1 | 02/22/2000 | 03/23/2000 | ML00369605 | <strong>Response Time Testing of Train B Turbine Solenoid Valve (1-FSV-47-027-B)</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2000, with unit 1 in Mode 1 operating at approximately 100 percent reactor power, engineering personnel identified for solenoid valve 1-FSV-47-027-B that required response time testing was not performed when the valve was replaced on April 4, 1999. The testing is required by Surveillance Requirement (SR) 3.3.2.10. The cause of this event was determined to be a lack of knowledge on the part of the personnel that developed the maintenance instruction that was used for the replacement of the valve. Also contributing to the event was that WBN had not developed a matrix or other appropriate documents which identified the components for which response time testing is required. Without a document of this nature, each individual had to interpret the Technical Specifications (TS), the Final Safety Analysis Report (FSAR) and other relevant documents like the System Descriptions, to determine the appropriate scope of a test. The principal corrective actions include; the development of an NOED with subsequent approval by NRC, development of a TS amendment, the planning of a WO which will be implemented when the turbine is next removed from service and perform the required response time testing, and development of a list of components that are part of the response time testing program. This condition is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B).
3902000002 | Watts Bar 1 | 05/25/2000 | 06/26/2000 | ML00372868 | <strong>Entry Into LCO 3.0.3 Due to Both Trains of the Control Room Emergency Ventilation System Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2000, with Unit 1 in Mode 1 and operating at approximately 100 percent reactor power, maintenance was initiated on Main Control Room (MCR) isolation valve 0-FCV-31-003. This ventilation valve is part of the Control Room Emergency Ventilation System (CREVS). As part of the planned maintenance, Train A control room isolation (CRI) was initiated by a licensed operator. Once isolated, the differential pressure between the MCR and adjacent plant areas was less than the required positive pressure of = 0.125 inches water gauge. Therefore, Action A of LCO 3.7.10 was entered for one train of CREVS being inoperable. During troubleshooting of the CREVS, an access door for damper 0-ISD-31-4627 was found to be open. The door was closed and subsequently, the MCR pressure returned to normal. A review of the design drawings for the ventilation system indicated that the access door being open affected both Train A and Train B of the system. Therefore, LCO 3.0.3, was entered. The root cause was determined to be a change in the scope of a corrective action document which was implemented without appropriate reviews and approvals. The corrective actions include: 1) A walkdown of seismic Category I, TVA Class S (primary safety-related), pressurized rectangular duct located in the Auxiliary Building, Diesel Building and Control Building to identify those duct access doors which need a positive closure mechanism, 2) Modifications to secure the duct access doors identified by the walkdown, 3) Issuance of a memorandum to engineering personnel to address the lessons learned.
3902000003 | Watts Bar 1 | 08/31/2000 | 10/02/2000 | ML00375757 | <strong>Discovery of a Missed Response Time Test for Reactor Trip Breakers</strong><br /><i>Abstract:&nbsp;</i>On August 31, during a review of post maintenance tests scheduled for the upcoming Unit 1 Cycle 3 refueling outage, it was discovered that no documented evidence could be found that a reactor trip breaker response time test had been performed for reactor trip breaker B during the Unit 1 Cycle 2 refueling outage. At 1555 on August 31, Surveillance Requirement (SR) 3.0.3 was entered which provides 24 hours for completion of the missed test. The response time test was successfully completed and the results accepted on September 1, 2000, at 1523. The cause was determined to be an inadequate work order which only notified another group to perform the response time test and did not verify completion. Corrective actions included performance of the missed test and a revision to the upcoming Unit 1 Cycle 3 work orders to include a verification of test completion.
3902000004 | Watts Bar 1 | 09/10/2000 | 10/10/2000 | ML00376049 | <strong>Inadvertent Actuation of the Turbine Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>Work Order 99-015140-000 directed the installation of jumpers in relay rack 1-R-73 on relays BVA and AFA. This action was required by Section 6.2.1 of chemistry and sampling procedure CM 6.60 and was necessary so that the steam generator blowdown sample valves could be opened while the auxiliary feedwater (AFW) pumps were running. The turbine driven AFW (TDAFW) pump receives an engineered safety feature start signal from Train A via relay RAS and from Train B via relay RBS. For relay RAS, actuation is initiated by relay RA2 (1-R-73). Relay RA2 also initiates an actuation signal for the turbine driven level control valves (LCVs). Relays AFA and BVA are located in Row F of the relay rack (1-R-73) in slots four and five. Relay RA2 is located in slot five of Row G of 1-R-73, immediately below relay BVA. Relay RA2 is a Westinghouse AR440 relay with a contact operating bar on the front of the relay. Based on steam flow and LCV actuation data obtained from the Integrated Computer System (ICS), the TDAFW pump started at approximately 01:59. This indicates that the inadvertent starting of the pump occurred during the period the jumper installation was ongoing in the relay rack. The cause of the event is considered to be the inadvertent operation (bumping) of the contact bar of relay RA2. The circumstances associated with this event will be developed into a briefing document. This document will specifically address the sensitivity of Westinghouse AR Relays and the need for extreme care when working around the relays. The briefing document will be provided to affected maintenance organizations to reinforce the cause of this event.
3902000005 | Watts Bar 1 | 10/06/2000 | 11/06/2000 | ML00376926 | <strong>Main Feed Pump Turbine Trip Due to a Condenser Vacuum Transient</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2000, at 19:22, WBN Unit 1 entered Mode 1 following the completion of the Unit 1 Cycle 3 refueling outage. Reactor power reached approximately 13 percent power at 19:39 and steam generator (SG) level was being maintained by the 1 B turbine driven main feedwater pump (TDMFP). The 1A TDMFP was not in service at this time but the condenser for the 1A pump was operational. As part of the routine start-up activities, the Operations staff was preparing to roll the main turbine. However, at this time, low condenser vacuum was experienced on the 1B TDMFP. The condenser transient caused the 1B pump to trip and this satisfied the logic for the starting of the auxiliary feedwater (AFW) pumps as an Engineered Safety Feature. The AFW system functioned properly to maintain the water level of the steam generators. In addition to this, the Operations staff entered Abnormal Operating Instruction 16, "Loss of Normal Feedwater," and started the standby main feedwater pump. Due to these actions the reactor power was maintained at 13 percent. The condenser vacuum transient was caused by the improper control or modulation of FCV-2-35, the condensate short cycle recirculation valve. This was attributed to the flow controller for FCV-2-35 not being adjusted appropriately to respond to plant conditions. Corrective actions included; 1) The calibration of FCV-2-35 and its instrument loop was verified, 2) Revision of a setpoint and scaling document.
3952000001 | Summer 1 | 01/07/2000 | 04/06/2000 | ML00370366 | <strong>Missed Surveillance on Control Room Evacuation Panel 'B' Steam Generator Wide Range Level Indicator (ILI00487B)</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2000, the task tracking system prompted generation of a Surveillance Test Task Sheet (STTS) for the Control Room Evacuation Panel (CREP) 'B' Steam Generator level indicator (surveillance test procedure STP0345.056) with a "need date" of October 25, 1998. This surveillance has an 18-month frequency and was last performed on April 27, 1997. This surveillance should have been performed on October 25, 1998. It was determined that, during the rollover from an old tracking system database (CHAMPS RMS) to a new database (CHAMPS RDB) in March 1997, a database algorithm created an error in some due date calculations. The verification and validation process for the database upgrade failed to detect this discrepancy. The STTS for the April 27, 1997 performance of STP0345.056 had been generated prior to the database rollover, and therefore, was not affected by the rollover. Subsequent to the rollover, errors were detected in due date calculations for some tasks, and corrected. None of these other calculation errors resulted in missed surveillances. It could not be determined if the subject surveillance due date error was detected at this time and invalid data was then entered while attempting to correct the problem, or if it remained undetected until January 7, 2000. In response to the above condition, the required surveillance was completed on January 7, 2000, the test due date for the subject surveillance was corrected, and the CHAMPS RDB system was thoroughly tested and determined to have no additional errors.
3952000003 | Summer 1 | 01/29/2000 | 02/15/2000 | ML00368585 | <strong>Missed Surveillance Test for Penetration Overcurrent Protection Technical Specification</strong><br /><i>Abstract:&nbsp;</i>This report is made due to a missed Technical Specification (TS) surveillance test. On January 19, 2000, at 1600 hours, the Limiting Condition for Operations (LCO) for TS 3.8.4.1 was entered due to a missed surveillance test for Electrical Equipment Protection Devices. During a procedure review of Surveillance Test Procedure (STP) 502.001, it was identified that one set of overcurrent protection relays required to be tested by the FSAR was missing from this procedure. This condition was found to have existed since the original version of the procedure. Condition Event Report (CER) 0-C-00-0080 was initiated to address immediate corrective actions. These actions included verification that the relay testing was completed as a preventive maintenance task, a visual verification of the control circuit wiring, appropriate continuity checks, and performance of an operability evaluation. These actions were completed and the LCO was exited on January 20, 2000 at 2000 hours.
3952000004 | Summer 1 | 03/01/2000 | 03/30/2000 | ML00370187 | <strong>Potentially Outside Design Bases Due to a Deficiency in Facility Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2000 at 12:15 hours, following evaluations performed in response to McGuire Station Notification (event # 36659), Virgil C. Summer Nuclear Station (VCSNS) concluded that there existed a single failure vulnerability which may have existed during past plant operation. The specific condition is a deficiency in the current Limiting Condition for Operation (LCO) for Engineered Safety Feature Actuation System (ESFAS) instrumentation. For one inoperable channel in the Emergency Feedwater suction swap-over on low suction pressure, Refueling Water Storage Tank (RWST) to Reactor Building Sump Swap-over on to-lo level, and Containment Spray actuation on Hi-3 building pressure, The Technical Specification (TS) requirement is to place the channel in bypass. There is no completion or restoration time specified. During a design basis accident, a single failure involving a loss of power to the opposite train instrumentation, while one or more of these functions were in bypass would prevent the safety function from automatically occurring. Currently all 4 channels for each function are operable. A preliminary PRA evaluation shows the change in Core Damage Frequency to be insignificant. Administrative controls are in place to limit the time a channel can be in bypass until a TS change request can be submitted and approved. This change is expected to be submitted by 12/2000.
3952000005 | Summer 1 | 06/16/2000 | 07/14/2000 | ML00373453 | <strong>Voluntary Report: Initiation of Plant Shutdown due to Inoperable Feedwater Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted as a Voluntary Report because the condition was corrected before plant shutdown was completed. A low accumulator air pressure alarm for "C" Feedwater Isolation Valve (FWIV), XVG01611C was received at 1459 hours on June 13, 2000. Plant personnel observed air escaping from the top exhaust port on the actuation air assembly for the valve. The valve was subsequently declared inoperable at 1545 hours and V.C. Summer Nuclear Station (VCSNS) entered the 72 hour action statement for Technical Specification (TS) 3.7.1.6, Feedwater Isolation Valves. When one feedwater isolation valve is inoperable, power operation may continue in Mode 1 provided that the inoperable valve is restored within 72 hours; otherwise be in Hot Standby within the next 6 hours and in Hot Shutdown within the following 6 hours. The NRC was notified at 2210 hours on June 15 in accordance with the requirements of 10 CFR 50.72(b)(1)(i)(A) that VCSNS was initiating the plant shutdown. The plant was taken off line at 0503 hours on June 16 and maintained in Mode 2. With the plant in Mode 2 and the FWIV closed, TS 3.7.1.6 allows continued operation without going to Hot Standby (Mode 3). The actuation assembly for XVG01611C was replaced and the valve verified to be operable at 1949 hours on June 16. A plant restart was then initiated with Mode 1 entry at 1220 hours on June 17. VCSNS returned to approximately 100% power at 1900 hours on June 19, 2000. The cause of this event is attributed to a failure of the #7 poppet seal on the #3 poppet valve. A piece of the viton poppet seal was found missing. No operability concerns currently exist, as post maintenance testing of the "C" Feedwater Isolation Valve actuator was satisfactory.
3952000006 | Summer 1 | 09/21/2000 | 10/18/2000 | ML00376238 | <strong>Turbine Driven Emergency Feedwater Pump Discharge Valve Found Isolated</strong><br /><i>Abstract:&nbsp;</i>On 9/21/00 at 0600, during the performance of a scheduled surveillance test on the Turbine Driven Emergency Feedwater Pump (TDEFP), it was discovered that the TDEFP discharge valve, XVG-1036, had been inappropriately locked in the closed position. XVG-1036 had not been manipulated as part of this particular surveillance test; however, the stem on the valve was positioned such that it appeared different from other similar valves in the area. The duty shift supervisor (DSS) with the assistance of the shift engineer (SE) immediately opened and locked the valve in the correct position. A one hour notification was made to the NRC at 0651. Subsequent review of plant surveillance test records revealed that the valve had been mispositioned on 8/4/00 during the quarterly performance of surveillance test procedure STP-1 20.004 for emergency feedwater valves. As a result of the mispositioned valve, the TDEFP was inoperable. This condition is contrary to the requirements of Technical Specifications. The cause of this event is attributed to human error. First, the valve was not opened, per procedure, prior to placing the locking chain on the valve handwheel. Second, the independent verification was not properly performed. Therefore, an opportunity to correct the mis-positioning was missed. Since an initiating event did not occur during the time that the condition existed, the TDEFP was not required to function and there were no adverse consequences to the public health and safety, plant personnel, or plant equipment.
3952000007 | Summer 1 | 10/09/2000 | 11/08/2000 | ML00376929 | <strong>Main Steam System Support Found Missing</strong><br /><i>Abstract:&nbsp;</i>On 8/15/00, during a reanalysis of the Reactor Coolant System and Main Steam System inside the Reactor Building, plant engineering personnel identified a concern that a discrepancy existed between the pipe analysis and the documentation of a tie - back support for the 3/4" vent to XVT12803/12804. The analysis performed for snubber reduction under Modification Request Form 22494B takes credit for the existence of the tie-back support on the "B" Main Steam header. Condition Evaluation Report (CER-O-C-00-1019) was written to document this apparent discrepancy. Because the area was inaccessible, a visual inspection of the main steam line was planned to be performed during the upcoming refueling outage (RF) 12 to determine whether or not the tie-back support existed. On 10/9/00, at 2045 hours, plant personnel visually verified that the tie-back support did not exist on the "B" main steam line in the Reactor Building. Condition Evaluation Report (CER-O-C-00-1359) was written to document the reportability of this condition. Evaluation of the condition revealed that the plant was outside the design basis. Immediate notification was not required per 10 CFR 50.72 since the condition was found while the plant was shutdown, but a 30 day written report was required per 10 CFR 50.73(a)(2)(ii)(B). The cause of this event was personnel error. To correct this condition, a tie-back support for the 3/4" vent to XVT12803/12804 will be installed prior to restart from RF 12.
3952000008 | Summer 1 | 10/12/2000 | 03/15/2001 | ML01079045 | <strong>Reactor Coolant System Pressure Boundary Degradation</strong><br /><i>Abstract:&nbsp;</i>On 10/7/00 plant personnel identified an accumulation of boric acid near the "A" loop of the reactor vessel. Subsequent inspections revealed small amounts of boron buildup on the weld between the vessel nozzle and the hot leg pipe. Within hours, the suspect area was cleaned and a dye penetrant (PT) examination of the pipe identified a 4 inch indication at the weld approximately 3 feet from the vessel between the hot leg piping and the reactor vessel nozzle. The indication was located about 17 inches from the top of the pipe. This pipe has a nominal inside diameter of 29 inches and is approximately 2.5 inches thick. Subsequent ultrasonic examination from the inside diameter identified an axial flaw less than 3 inches long. The same examination determined that the original indication was not the source of the leak. The PT indications were later determined to be steam cutting/boric acid corrosion at the nozzle butter to nozzle interface. The axial flaw was determined to have resulted from the extensive repairs performed during initial installation which created high welding residual stresses in the material, combined with a material susceptible to stress corrosion cracking, and an environment known to cause primary water stress corrosion cracking. The welding technology of the codes, standards and processes in use during initial installation did not account for the extent of repairs required on the weld. Weld repairs were completed on February 9, 2001. All safety issues are satisfied. Several long term corrective actions are being tracked in the plant Corrective Action Program. Any additional actions will be addressed through industry response to EPRI and NRC developed initiatives.
3952000009 | Summer 1 | 10/16/2000 | 11/15/2000 | ML00377043 | <strong>Technical Specification Prohibited Operation - Fuel Handling Building Ventilation Outside Required Range</strong><br /><i>Abstract:&nbsp;</i>The V.C. Summer Nuclear Station shut down for its 12th refueling outage on October 7, 2000. Fuel transfer from the reactor building to the Spent Fuel Pool commenced on October 15th. On October 16th, a plant operator questioned the Fuel Handling Building (FHB) differential pressure (AP). Per plant design and TS Surveillance Requirement 4.9.11.d.3, the spent fuel pool area should be maintained at a negative pressure of greater than or equal to one eighth (1/8) inch water gauge relative to the outside atmosphere during Spent Fuel Pool Ventilation system operation. The system is required to be operable whenever irradiated fuel is being moved in the spent fuel pool and during crane operation with loads over the pool. The building negative pressure with the existing configuration of running fans was between 0.09 and 0.10 inches water column as indicated on local instrument IPS 09688. Maintenance personnel utilizing a field standard test instrument confirmed this condition. The remote alarm per the Annunciator Response Procedure (ARP-016) should have been set to alarm at -0.185 inches with a minimum of -0.125 inches for fuel handling evolutions. All fuel-handling activities were immediately suspended upon discovery while a more effective ventilation configuration was established and tested. The alarm was found to be out of calibration and was recalibrated prior to resumption of fuel movement. The reduced negative pressure was attributed to reduced flow at the FHB exhaust plenum due to the Auxiliary Building and FHB ventilation systems configuration and characteristics.
3952000010 | Summer 1 | 10/18/2000 | 11/17/2000 | ML00377196 | <strong>Inadequate ASME Code Visual Examination for Pressure Retaining Components</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2000, South Carolina Electric & Gas Company (SCE&G) personnel identified an inadequate surveillance for visual leakage inspection of components with pressure retaining bolted connections. The inspection of bolted components, in systems borated for the purposes of reactivity control, requires insulation to be removed during the inspection in accordance with ASME Section XI, 1989 Edition, Article IWA-5242(a). Plant personnel, involved in the visual inspection of Code Class 1 components in the Inservice Test (IST) program, questioned why several check valves were not included. A review of plant drawings found that there were five (5) Code Class 1 check valves that had not been previously identified as having bolted connections covered with insulation. SCE&G considers the failure to inspect the bolted connections with insulation removed to be a procedure development error. There were no adverse consequences resulting from the failure to inspect these valves with the insulation removed. VCSNS performs a walkdown of areas in the containment each outage looking for degradation that would be indicated by leakage from a borated system. Additionally, the identified components received a visual inspection with the insulation on and the system at rated pressure during each required pressure test for Code Class 1 or 2 systems. Plant personnel are reviewing design documents to verify that all bolted connections for Class 1 and 2 systems are identified. Any Class 1 surveillance program errors will be corrected prior to the pressure test scheduled at the end of the current refueling outage (RF-12). All Class 2 component inspection errors will receive a visual inspection with insulation removed and the system depressurized prior to the end of RF-12. The applicable surveillance procedures for Code Class 2 components will be corrected by March 1, 2001.
3952000011 | Summer 1 | 10/19/2000 | 11/18/2000 | ML00377199 | <strong>Diesel Generator Fuel Oil Storage</strong><br /><i>Abstract:&nbsp;</i>On 10/19/00 plant engineering personnel determined that design calculations for the Emergency Diesel Generator (EDG) Fuel Oil Storage requirements do not consider the "optional" loads that would be loaded per the plant Emergency Operating Procedures (EOPs) following a loss of coolant accident (LOCA) coincident with a loss of offsite power (i.e., starting of instrument air compressors, etc.). This impacts fuel storage calculations. This event would place the plant outside of its design basis. VC Summer Station is committed to compliance with Regulatory Guide (RG) 1.137, Revision 1, 10/79 which includes calculating the minimum required volume of EDG fuel oil In accordance with ANSI N195-1976 using the time dependent load method. Original design calculations performed to determine the minimum required volume of EDG fuel oil made non-conservative assumptions that under-stated the optional loads placed on the EDGs. Technical Specification (TS) 3.8.1 is based on these calculations, and requires that the EDG Fuel Oil Systems contain a minimum volume of 47,100 gallons of fuel oil which includes a 10 per cent (%) margin in Modes 1 through 4 and 33,200 gallons in Modes 5 and 6. The TS specified minimum volume for the EDG day tank is 300 gallons in Modes 1 through 6. Calculations have been performed which Identify and evaluate the optional loads that may be placed on the EDGs. The minimum fuel oil volume including a 10% margin that is needed to support operation in Modes 1 through 4 is 50,680 gallons. For Modes 5 and 6, the minimum fuel oil volume to support operation for seven days plus at least 10% is 42,500 gallons. The revised minimum required contained volume for the day tank is 360 gallons in Modes 1 through 6. There were no adverse consequences resulting from this discrepancy. Additional fuel oil is available locally within 24 hours of determining needs and the system design allows for fuel oil transfer from the redundant EDG fuel oil storage tank via a normally closed cross-tie line between the tanks Engineering has initiated appropriate TS and FSAR revisions based on the revised calculations.
3972000001 | Columbia | 02/01/2000 | 03/01/2000 | ML00369002 | <strong>Condition that could have allowed fulfillment of a safety function beyond the Technical Specifications allowable limit</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2000 with the plant in mode 1 at 100% power it was determined that the Main Steam Isolation Valves (MSIVs) [JM] would not have closed automatically in response to a condenser low vacuum condition within the value allowed by the Technical Specifications. This condition was discovered after performance of a channel functional test of main condenser vacuum-low instrumentation that functions to generate a signal to close the MSIVs. The setpoints for two pressure switches that monitor condenser vacuum were found to be out of tolerance in a non-conservative direction that exceeded the Technical Specifications allowable value of greater than or equal to 7.2 inches of mercury (Hg) vacuum. A review of the condition determined that the switches had been misadjusted during a previous calibration on November 10, 1999 and had remained out of tolerance since that time. Upon discovery of this condition, the pressure switches were adjusted to the nominal setpoint and the automatic MSIV closure on low condenser vacuum function was restored to actuate at the required value. This condition would have required the control room operators to manually close the MSIVs, according to procedure, when the automatic function did not occur at the expected condenser pressure. Considering the misadjusted setpoint, the automatic closure of the MSIVs would have occurred at 2.8 inches of Hg vacuum. Initiation of automatic MSIV closure at that pressure would have been adequate to prevent condenser over-pressurization. A positive condenser pressure could rupture the diaphragm that is installed to protect the turbine exhaust hood and prevent a potential radiation leakage path following an accident. Condenser vacuum has been maintained within the normal operating range throughout the current operating cycle.
3972000003 | Columbia | 06/26/2000 | 07/26/2000 | ML00373662 | <strong>Unit Trip and Reactor Scram due to Protective Relay Control Circuit Failure</strong><br /><i>Abstract:&nbsp;</i>At 0825 hours PDT on June 26, 2000, with the plant in Mode 1 at 100% power, WNP-2 experienced a Unit Trip. This resulted in the tripping of the 500 kV power circuit breakers and exciter breaker, tripping the station auxiliary breakers, closing of the breakers to supply offsite power from the startup transformer and tripping of the main turbine. The turbine trip in turn initiated a reactor SCRAM. The unit trip was initiated by a signal from the Main Generator and Transformer Overall Differential protection relaying. Immediately after the reactor SCRAM, two main steam relief valves (MSRV) automatically opened on high pressure. Emergency operating procedures were entered on Reactor Pressure Vessel (RPV) low level (+13"), RPV Pressure High (1060 psig), Suppression Pool Level High, and subsequently Suppression Pool Temperature High. Main Steam Bypass Valve #1 (MS-V-160D) temporarily remained open causing the reactor pressure to decrease to approximately 500 psig. The reactor water level increased to level 8 resulting in a trip of the main feedpumps. The pressure decrease was controlled by operator action to close the Main Steam to Auxiliaries Isolation Valve (MS-V-146). The reactor cool down rate limit was not exceeded. Operators restored reactor level to within the normal shutdown limits by a controlled condensate booster pump injection and maintained subsequent reactor vessel level and pressure with the Start-up RPV Level Controller and MSRVs. The cause of the Main Generator and Transformer Overall Differential protection relay trip was a short to ground in an unused tap of one of the 500 kV current transformer's (CT) secondary control circuit wiring. This caused an unbalanced phase current signal to be sent to the relay causing it to actuate.
3972000005 | Columbia | 06/27/2000 | 08/01/2000 | ML00373845 | <strong>Failure to Completely Bypass the Low Condenser Vacuum Trip Caused an ESF Signal to be Generated That Resulted in the Closure of all Eight MSIVs While the Plant Was Shutdown</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2000 at 1529 with the plant in Mode 4, plant operators were performing a reactor cooldown. The reactor cooldown procedure requires four low condenser vacuum isolation logic keylock switches to be placed in the bypass position prior to breaking condenser vacuum. An operator was directed to bypass the low vacuum trip and placed only the C and D logic channels in bypass, leaving channels A and B in the normal position. When the main condenser vacuum was broken, a nuclear steam supply shutoff system (NSSSS) isolation signal was generated, closing all eight main steam isolation valves (MSIVs). There were no safety consequences associated with this event. The contributing cause of this event is procedure noncompliance. The operator assigned to bypass the low condenser vacuum trip placed only the C and D logic channels in bypass, leaving channels A and B in the normal position. When the main condenser vacuum was broken, an NSSSS isolation signal was generated, closing all eight MSIVs. The root cause of this event is ineffective oversight to consistently reinforce standards and expectations for this operating crew. There were no safety consequences associated with this event. The Operations Manager and or the Operations Crew Manager reviewed this event and its underlying causes with management from each operating crew. The personnel directly involved in this event are being remediated.
3972000006 | Columbia | 09/13/2000 | 12/06/2000 | ML00377634 | <strong>Plant Outside Design Basis for Control Room Emergency Filtration System Unfiltered In-Leakage Based Upon Tracer Gas Testing</strong><br /><i>Abstract:&nbsp;</i>During September 8 through 11, 2000, a series of special tests, using a tracer gas decay methodology, were performed to determine the total in-leakage into the control room and the associated impact on control room dose. These tests were performed in support of a proposed Technical Specification amendment request that is being developed for removal of main steam leakage control system testing requirements and resolution of a long-standing issue pertaining to secondary containment/standby gas treatment system performance, using alternative source term methodology. On November 29, 2000, final test results were received and an assessment showed that the maximum combined train measured unfiltered in-leakage (plus the measurement uncertainty) for the control room emergency filtration system was 218 cfm. This is two cfm less than that which was reported in the original LER (the September 13, 2000 preliminary test results showed a value of 220 cfm), but is still in excess of the current licensing and design basis limit of 10.55 cfm. The impact of the unfiltered in-leakage increase on control room dose was evaluated and it was determined that the design basis thyroid dose of 30 rem to the control room operators would have been exceeded during post-accident conditions. An operability assessment was prepared which concluded that the as-found in-leakage did not render the control room emergency filtration system inoperable. In addition, a follow-up interim compensatory measure included direction regarding the administration of potassium iodide, in accordance with requirements contained in abnormal operating procedures, to reduce the calculated control room thyroid dose below the 30-rem limit in the event of a design basis accident. Final resolution of this issue will be addressed by implementation of alternative source term methodology. A feasibility study, using alternative source term methodology, has shown that in-leakage rates in excess of 218 cfm (approximately 300 cfm) would result in control room doses below the regulatory limit. This is a design basis analysis issue and no plant hardware changes are required. The safety consequences associated with this event were minimal.
3972000007 | Columbia | 09/18/2000 | 10/17/2000 | ML00376245 | <strong>Manual Reactor Scram Due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2000 at 1425 control room operators received an offgas condenser low-level alarm, and noticed a rapid increase in condenser offgas flow while reactor power was at 100%. In response to increasing turbine back pressure, the operators began lowering reactor power. At 1509, with reactor power at 65% and condenser vacuum at 24 inches Hg, control room operators manually scrammed the reactor as directed by plant procedures. A turbine trip occurs automatically at a condenser vacuum of 20 inches Hg. Plant systems responded as expected following the manual reactor scram. Immediate actions included stabilizing the plant in Mode 3 then commencing a plant cooldown to Mode 4 to investigate the cause of the event. The reason for the loss of condenser vacuum was determined to be a broken turbine "slop" drain line. A four-hour event notification phone call was made to NRC headquarters per the requirements of 10 CFR 50.72(b)(2)(ii).
3972000008 | Columbia | 12/14/2000 | 01/12/2001 | ML01022041 | <strong>Unexpected Low Pressure in the Containment Instrument Air System Results in Actuation of Safety Related Bottled Nitrogen Source to Maintain Operating Pressure for the Automatic Depressurization System</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2000 the plant was at 100% power. Containment Instrument Air (CIA) system quarterly sampling was in progress. The pressure in CIA header 'A' and header 'B' began to decrease at approximately 2051. At approximately 2128 the pressure in the CIA system dropped to approximately 160 psig and caused the generation of a valid isolation signal to the 'B' CIA supply valve, CIA-V-39B, and the valve closed. This isolated the 'B' CIA header from the normal non safety-related nitrogen supply portion of the system. The closure of the isolation valve, in combination with the low pressure in the system, caused the safety-related portion of the CIA system to initiate and supply nitrogen gas to the system from the associated bank of nitrogen bottles. The pressure in header 'B' increased to 184 prig (normal) within 3 minutes. This engineered safety feature (ESF) actuation provided the pneumatic supply to maintain operating pressure for the 'B' nitrogen supply header for the Automatic Depressurization System. No other plant safety features were affected. The CIA system pressure dropped to a minimum pressure of approximately 156 psig. The 'A' CIA header did not isolate as the supply valve. CIA-V-39A, did not close when the system reached 160 psig. The as-found closure setpoint for CIA-V-39A was 154 psig. Subsequent to the event, the CIA quarterly sampling procedure was successfully completed. The cause regarding the failure of the non safety-related portion of the system to maintain system nitrogen supply and pressure has not been identified. Additional component testing is planned. Failures of the non safety-related portions of the system have minimal safety significance and will not cause plant transients. The ESF portion of the system actuated and maintained the pneumatic supply and pressure as designed. There were no safety consequences associated with this event.
4002000001 | Harris | 02/22/2000 | 03/23/2000 | ML00369669 | <strong>Control Room Emergency Filtration System Technical Specification violation.</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2000, with the Harris Nuclear Plant (HNP) at 100% reactor power, a duct access panel for the Control Room Emergency Filtration System (CREFS) ventilation boundary was removed to facilitate surveillance testing of the charcoal in the filtration unit. This access panel is located at the common suction line for the two redundant CREFS units, R-2A and R-2B. During the time (approximately five minutes) that the access panel was removed and the test panel installed, the CREFS could not achieve and maintain a positive pressure as required by Technical Specifications (TS) surveillance requirement 4.7.6.d.3. This condition caused both of the CREFS units to become inoperable. Harris Nuclear Plant (HNP) TS do not provide an action when both CREFS are inoperable. Additionally, there is no action, in TS 3.7.6, for an inoperable CREFS ventilation boundary. Thus, opening the CREFS duct work during performance of the surveillance test required entry into TS 3.0.3. Cause of this event: Inadequate review of plant procedures which affect control room ventilation boundaries. Corrective actions include: (1) Reviewing plant procedures to ensure that passive barriers which may be opened do not violate CREFS pressure boundary requirements. (2) Install signs on applicable ventilation duct access panels instructing plant personnel to contact the main control room prior to removal of the associated duct access panel.
4002000002 | Harris | 04/13/2000 | 09/22/2000 | ML00375370 | <strong>Technical Specification Violation Due To Inoperable Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2000, with the Harris Nuclear Plant (HNP) at 100% reactor power, an investigation determined that the Containment Reactor Coolant Leakage Detection System Radiation Monitor, REM-OILT-3502ASA, Particulate Channel was inoperable longer than allowed by HNP Technical Specifications (TS). The REM-01LT-3502ASA was inoperable due to the filter paper moving too fast resulting in a nonconservative signal being sent to the radiation monitor indication and alarm circuitry. Investigation determined that the filter paper was moving too fast because the slip-clutch on the take-up reel was not adjusted to the correct torque and was not lubricated as recommended by the vendor. This condition existed in excess of 30 days resulting in a violation of HNP TS 3.3.3.1.1.c.l. "Radiation Monitoring", and TS 3.4.6.1.c.a. "Reactor Coolant System Leakage Detection Systems". Cause of this event: Inadequate preventative and corrective maintenance. Corrective actions: Placed the Particulate Channel of REM-01LT-3502A in the fixed filter mode of operation. In this mode of operation the filter paper does not move.
4002000003 | Harris | 05/04/2000 | 06/01/2000 | ML00372105 | <strong>Inadvertent Safety Injection Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2000 at approximately 1324, with the Harris Nuclear Plant HNP)in Mode 5 at 0% reactor power, an inadvertent Safety Injection (SI) was generated by a Pressurizer Low Pressure SI signal. The signal was generated when Instrument Bus S-III, which provides power to Channel 3 instruments, was de-energized to return it to its normal power supply concurrent with plant procedure MST-10604, Time Response Test for Channel I Pressurizer Pressure being in progress. Since the same pressure channels supply the Low Pressurizer Pressure SI Block Permissive (P-il), the block feature was lost and SI actuated. The Boron Injection Tank outlet valves were closed and de-energized in preparation for OST-1826, which prevented ECCS discharge to the RCS. Other equipment operated as required in response to the SI signal. Cause of this event: (1) Failure to validate or verify information upon which key decisions were made. (2) Less than adequate sensitivity to activities that may cause an SI actuation during shutdown conditions. Corrective actions include: (1) Formally incorporate the "sensitive activity" work control, scheduling, and associated expectations for pre-job briefs and oversight into a plant procedure. (2) Counsel involved operators. (3) Provide training to applicable operators to reinforce actions when faced with complex knowledge challenges.
4002000004 | Harris | 05/12/2000 | 06/12/2000 | ML00372368 | <strong>Technical Specifications violation due to inoperable Power Range Nuclear Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On 5/12/00 at 00:15 hours with Harris Nuclear Plant (HNP) performing a reactor startup following a refueling outage, the Excore Nuclear Instrumentation power range channel N44 failed to indicate as expected. Reactor power was increased to the point of adding heat when power range channel N44 was observed to have an indication of zero on the percent power meter and zero on both the upper and lower detector current meters. At this time the other power range channels were indicating 1.4 to 1.5% reactor power with detector currents readings of 1.8 microamperes to 2.7 microamperes. The malfunction was determined to be the result of a failed high voltage cable connector at the high voltage power supply. This condition was most likely caused when the drawer was pulled out and the cable jacket hooked on the sharp edge of another cable connector resulting in the center pin being pulled from the high voltage power supply connector. Entry into Mode 2 occurred at 10:36 on 5/11/00 at 10:36 hrs. The failure was identified on 5/12/00 at 00:15 hrs. No work has been identified on N-44 after entry into Mode 2. Therefore, HNP has determined that N-44 was inoperable longer than the six hours allowed by Technical Specification 3.3.1 Action 2 without placing the channel in the trip condition. (1) Cause of this event: Inadequate self-checking and inattention to detail during the opening of the N44 drawer. Corrective actions include: (1) N-44 high voltage cable connector was repaired. (2) Review of this Condition Report with Crews working with Nuclear Instrumentation System. (3) Revise applicable procedures associated with the power range excore nuclear instrumentation to have a signoff for additional personnel assigned at the cabinet to ensure the cables are positioned properly.
4002000005 | Harris | 06/20/2000 | 07/20/2000 | ML00373487 | <strong>Manual Reactor Trip due to a Reduction in Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2000 at 1631 hours with Harris Nuclear Plant (HNP) at 100% power, control room operators initiated a manual reactor trip in response to lowering level in the "A" Steam Generator (SG). The cause of the lowering level in "A" SG was due to the unexpected closure of the "A" Main Feedwater Isolation Valve (MFIV). The low water level in "A" SG resulted in an automatic actuation of both motor-driven auxiliary feedwater pumps. The control room operators restored "A" SG water level following the reactor trip. There were no other structures, systems, or components that were inoperable at the start of the event and that contributed to the event. Cause of this event: A random manufacturing defect of a diode in a solenoid valve for the "A" MFIV actuator. Corrective actions include: The defective solenoid valve for the "A" MFIV was replaced.
4002000007 | Harris | 05/15/1999 | 12/03/2001 | ML02016038 | <strong>Technical Specifications Violation Due to Inoperable Charging Safety Injection Pump</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2000 with Harris Nuclear Plant (HNP) at approximately 100% reactor power, HNP determined that the "C" Charging Safety Injection Pump (CSIP) was inoperable for a period of time longer than that allowed by Technical Specifications. These periods occurred between May 15, 1999 through June 4, 1999, November 13, 1999 through December 18, 1999 and between January 3, 2000 through January 7, 2000. On June 19, 2000, the "C" CSIP was disassembled for scheduled mechanical seal replacement. Upon removal of the bearing housing, the outboard thrust bearing shoes were found to have significant damage. HNP determined that the "C" CSIP was inoperable due to this condition after further evaluation and discussions with the vendor. I Cause of this event: Potential causes include partial loss of lubricant flow to the outboard thrust bearing (most probable cause) or improper fill and vent of the "C" CSIP. Corrective actions include (l)Repaired the "C" CSIP with vendor support using the vendor manual in conjunction with plant procedures.(2)Reinforced expectations to Operations personnel that describe the consequences of an improper fill and vent with regard to the CSIP. (3)Established oil analysis criteria for components that would result in further analysis for the increased particulate count and actions as appropriate. (4)Reinforced expectations to individuals involved for timely disposition of abnormal indications. (5)Increased CSIP lube oil sampling frequency to a quarterly interval. (6)Reviewed the system configuration for venting, and revised the operating procedure to specify the minimum volume of water to be collected to ensure proper fill and vent. (7)Revised the maintenance procedure associated with CSIP reassembly (CM-M0019) with lessons learned from vendor guidance. (8)Implement a design modification to install temperature detectors on the CSIPs, which allow for improved monitoring and failure detection of the CSIPs.
4102000001 | Nine Mile Point 2 | 01/12/2000 | 02/11/2000 | ML00368556 | <strong>Missed Response Time testing of the High Pressure Core Spray Initiation Signals and the Main Steam Flow Channels as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2000, while at 100 percent power, Niagara Mohawk Power Corporation identified that response time testing for the high pressure core spray initiation signals (from high drywell pressure and low reactor water level) and the main steam flow channels were not being tested within the frequency required by Technical Specifications Surveillance Requirements 4.3.2.3 and 4.3.3.3. The cause was a lack of standardized guidance on the philosophy and methodology for maintaining and changing the surveillance test database. The high pressure core spray system and the main steam line flow channels were declared inoperable until the required channels were satisfactorily tested. All response time testing surveillance frequencies were reviewed. Procedural guidance on the methodology for establishing the coding frequency in the surveillance test database will be issued, and all procedures with variable or staggered type frequency codes will be reviewed for proper database entry.
4102000003 | Nine Mile Point 2 | 03/03/2000 | 03/31/2000 | ML00376621 | <strong>Pre-outage Review of Previous Outage Inspection Data on Feedwater Nozzle to Safe-End Weld Revealed an Indication</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2000, the ultrasonic data recorded during Refueling Outage 6 (RFO6) (1998) inservice inspection (ISI) on feedwater nozzle (N4D) to safe end weld (2RPV-KB20) was reanalyzed using improved analysis software. An indication had been identified in the safe-end butter of that weldment for three outages (RFO1, RFO4 and RFO6). The RFO6 indication had been evaluated as a conforming condition according to criteria established by American Society of Mechanical Engineers (ASME) Section XI, 1989 Edition, IWB3640, and was believed to be an original fabrication defect because of its location. The reanalyses of the RFO6 data identified another recordable indication immediately above the known indication. Code rules for proximity required that a combined size of the two indications be analyzed as a single defect. The new combined size exceeded the acceptance requirements given in ASME Section XI, 1989 Edition, IWB-3640, Appendix C 3320 which required the indication to be defined as a non-conforming condition. The cause for the inspection results difference was the application of new previously unavailable technology to analyze digital ultrasonic test data. Nine Mile Point, Unit 2 was shutting down for RFO7 at the time the indication was discovered. A weld overlay repair was designed and implemented to restore full structural margins to the component. The component operability was evaluated in terms of design margins for the component with full consideration for potential growth by intergranular stress corrosion cracking during the time interval between RFO6 and RFO7. It was determined that the component maintained ASME Section XI Code safety factor margins even with a conservative estimate for the indication to have grown through-wall. The use of improved inspection technology is considered a proactive approach to safety, but always presents a finite potential for discovery of new indications.
4102000004 | Nine Mile Point 2 | 03/15/2000 | 04/14/2000 | ML00370631 | <strong>Division I Diesel Generator Special Report and Two Service Water System Isolations</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2000, during surveillance testing while the plant was shutdown, the Division I Diesel Generator failed to control voltage. As required by Technical Specification 4.8.1.1.3, Niagara Mohawk Power Corporation is providing a special report for a non-valid failure of the diesel generator. In addition, on March 17 and March 21, 2000, the service water system isolated the non-essential portions of service water, which is an automatic engineered safety feature actuation. The cause of the diesel generator high voltage condition was the lack of procedural guidance for the re-assembly of the Potential Transformer (PT) fuse carriage linkage. The PT fuse carriage linkage was re-assembled and tested satisfactorily. The re-assembly of the PT fuse carriage was proceduralized. The cause of the first service water isolation was that the control room operators did not effectively assimilate and use available information to determine the condition of plant equipment. The circuit was repaired and tested satisfactorily. Static and/or simulator training will be enhanced to improve operator recognition of abnormal annunciator and alarm indications and clarifications to the watch standing policy will be developed. The cause of the second service water isolation was that a supervisor stepped out of the supervisory role and became part of the task execution. The blown fuse and relay were replaced and the supervisor involved was counseled on oversight expectations. The Manager-Maintenance will reinforce his expectations on maintaining a supervisory role under all conditions.
4102000006 | Nine Mile Point 2 | 04/04/2000 | 04/27/2000 | ML00371283 | <strong>Division I Service Water System Isolation of the Non-Essential Portions</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2000, while the plant was shutdown, the Division I Service Water System isolated the nonessential portions of service water, which is an automatic engineered safety feature actuation. The investigation team for the service water isolation could not identify any cause or failure. The investigation team determined that the most probable cause was an intermittent failure of at least one of three specific components. Non-intrusive testing was performed in an effort to identify possible causes for the service water isolation. The investigation team identified and interviewed personnel that where in the relay room and the Division 2 Emergency Switchgear Room prior to the service water isolation. All three components suspected as a possible cause were replaced and each will undergo failure analysis.
4102000007 | Nine Mile Point 2 | 04/13/2000 | 05/09/2001 | ML01135018 | <strong>Plant Outside Design Basis due to Single Failure Susceptibility of Service Water and Emergency Core Cooling Systems</strong><br /><i>Abstract:&nbsp;</i>April 13, 2000, the plant was shutdown for refueling in Mode 4. A review of the service water pumps' low discharge flow trip setpoint uncertainty and its impact on the service water system concluded that a single failure of the High Pressure Core Spray (HPCS) diesel, the onsite power source to Division III Emergency Core Cooling Systems (ECCS), to start following a Loss of Offsite Power (LOOP), could result in a low flow demand for service water and consequently, loss of all service water pumps due to the setting of the low flow trip. This is contrary to the criteria stated in General Design Criteria 44. The loss of all service water results in the loss of all ECCS. The review also concluded that a single failure of the HPCS diesel to start following a Loss of Coolant Accident (LOCA) concurrent with a LOOP, could result in the loss of one train of service water, leaving one train of service water and one train of ECCS operable. Subsequently, in October 2000, it was determined that the failure of the HPCS diesel to start following a LOCA concurrent with a LOOP could also result in the loss of all service water and all ECCS. The cause was that the original design of the service water system did not consider all possible low flow conditions that may contribute to the tripping of the service water pumps. A temporary modification was implemented that provided additional service water flow by throttling flow through the Division I and Division II Residual Heat Removal heat exchangers. A corrective action was implemented that modified the service water pumps' control logic such that the pumps no longer trip on low discharge flow.
4102000008 | Nine Mile Point 2 | 04/18/2000 | 05/17/2000 | ML00371783 | <strong>Unanalyzed Environmental Qualification Areas</strong><br /><i>Abstract:&nbsp;</i>In 1995, Niagara Mohawk Power Corporation modified the containment atmospheric monitoring system by installing standpipes to remove excess moisture from the sample lines. Following a loss of coolant accident, these standpipes could fill with reactor coolant. On April 18, 2000, Niagara Mohawk Power Corporation identified that the effect of this condition was not fully evaluated when the modification was developed. The cause of this condition has been determined to be inadequate change management. The personnel involved in the preparation of the change did not identify or evaluate the potential for the standpipes filling with reactor coolant following a loss of coolant accident. Contributing to the cause were inadequate independent reviews. Immediate corrective actions included the relocation and closure of the standpipe isolation valves to minimize the volume that could potentially be filled with reactor coolant, and the installation of temporary shielding. The design change and design change review process has been substantially enhanced since this error was made. To provide assurance that the radiological assumptions and consequences have been properly assessed, an evaluation of Nine Mile Point Unit 1 and Unit 2 modifications that affected either standpipes or lines that remove containment atmosphere from the containment following a LOCA will be performed.
4102000009 | Nine Mile Point 2 | 04/20/2000 | 05/22/2000 | ML00371881 | <strong>Violation of Technical Specification Due to Design Deficiency of Off Gas Grab Sample System</strong><br /><i>Abstract:&nbsp;</i>Off gas grab samples taken on April 20, 2000 through 0056 on April 21, 2000, during plant startup from a refueling outage, were not representative of conditions in the off gas stream. Grab samples were being taken to satisfy Technical Specification 3.3.7.10 action requirements, because installed off gas radiation monitors and hydrogen monitors were inoperable. By procedure grab samples could be collected using either the grab sample pump and the radiation monitor sample pump in parallel or by using the grab sample pump alone. These samples were being collected using only the grab sample pump. After reviewing sample analyses, chemistry concluded that grab samples collected with the grab sample pump alone were not representative of the off gas process stream and therefore, did not satisfy the Technical Specification requirement. The cause was that the original design validation calculation for pressure drop through the system incorrectly left out the smaller diameter tubing associated with Grab Sample Skid 2OFG-SMPV13. A contributing cause was inadequate post modification testing. Corrective actions include verifying the capability of the off gas grab sample system, modifying the grab sample procedure and reviewing other sampling procedures for adequacy.
4102000010 | Nine Mile Point 2 | 04/25/2000 | 05/25/2000 | ML00372094 | <strong>Technical Specification Requirement Not Performed for the Reactor Core Isolation Cooling System High Steam Flow Instrumentation Due to an Inadequate Work Package</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2000, with the plant at 100 percent power, Niagara Mohawk Power Corporation declared the reactor core isolation cooling system high steam flow instrumentation inoperable due to erratic indication. During the refueling outage, maintenance was performed on both divisions of the high steam flow instruments which inadvertently rendered them inoperable by introducing air into the lines. Technical Specification 3.3.2.c requires the reactor core isolation cooling system to be isolated from the steam supply within one hour with both high steam flow instruments inoperable in Operational Condition 1 2 and 3. The plant was placed in Operational Condition 2 on April 18, 2000 and the reactor core isolation cooling system steam supply valves were subsequently opened. The system remained unisolated until April 23, 2000. Once the system was isolated, the system could no longer automatically fulfill the safety function to remove residual heat. The causes were inadequate work package revision and inadequate worker knowledge and skills. The reactor core isolation cooling system was isolated from the steam supply until the high steam flow instrumentation was restored to operability by backfilling and removing the entrapped air. Operations personnel involved in the approval of the revised work order will be counseled in accordance with the human resource department policy. Operations personnel will be briefed on the development and review of changes to existing work orders. In addition, this event will be reviewed with instrumentation and control personnel.
4102000011 | Nine Mile Point 2 | 05/12/2000 | 06/12/2000 | ML00372481 | <strong>Missed Technical Specification for Primary Containment Integrity Due to a Failure to Revise a Surveillance Procedure After Issuing an Engineering Change Notice</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2000, with the plant at 100 percent power, Niagara Mohawk Power Corporation identified that since initial plant startup, the Primary Containment Isolation Valve 2RHS*V192 was not being verified closed every 31 days as required by Technical Specification Surveillance Requirement 4.6.1.1 .b. Not performing the surveillance requirement resulted in not meeting Technical Specification 3.6.1.1, which requires that primary containment integrity be restored within 1 hour or be in at least hot shutdown within the next 12 hours and in cold shutdown within the following 24 hours. The cause was that an engineering change notice was not implemented into all affected documents (i.e., the surveillance procedure). An opportunity was missed to identify and correct the deficiency when Niagara Mohawk Power Corporation did not properly address a recommendation from a General Physics audit of containment penetrations. Valve 2RHS*V192 was verified locked closed, and the surveillance procedure was revised to include the valve. Also, a General Physics audit of containment penetrations was reviewed for any other additional containment integrity issues.
4102000014 | Nine Mile Point 2 | 09/17/2000 | 10/17/2000 | ML00376212 | <strong>Reactor Trip on Turbine Trip Due to High Vibrations</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2000, at 1520 hours, while starting up from a planned outage for Noble Metal Chemical Addition, Nine Mile Point Unit 2 experienced a turbine trip and subsequent reactor trip from approximately 70% power as a result of high vibration sensed by turbine bearing number 8 instrumentation. The cause of the high vibration was oil whip/whirl. Oil whip/whirl is the movement of the oil wedge that is present between the turbine shaft and bearing sleeve. This oil movement caused high vibration. The corrective action was to revise procedures to direct operating the turbine oil system at a higher temperature. Additional turbine instrumentation was installed to monitor turbine vibration while placing the plant back into service.
4102000015 | Nine Mile Point 2 | 10/19/2000 | 11/17/2000 | ML00377216 | <strong>Failure to Enter Technical Specification Action Statement at the Correct Point in an Electrical Breaker Switching Sequence, Results in Exceeding Action Statement Allowed Time Frame</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2000, at approximately 0130, Nine Mile Point Unit 2 initiated activities to remove 115 KV offsite power source, Line b, from service for maintenance. Operators recognized that entry into the Action Statement of Technical Specification 3.8.1.1 was required. However, there was an incorrect understanding of which point in the evolution entry into the Action Statement would occur. This resulted in failing to enter the Action Statement at the appropriate point in the evolution which led to exceeding the time frame allowed for completion of the Action Statement requirements. Failing to meet the Action Statement requirements is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The cause of the event was poor work practices in that the relevant documents were not used or followed correctly. A contributing cause was inadequate managerial oversight. Corrective actions included procedure modifications and briefings of operations personnel.
4102000017 | Nine Mile Point 2 | 11/22/2000 | 12/22/2000 | ML01002014 | <strong>Inadequate Test Methodology Used for Reverse Flow Testing of Check Valve in Low Pressure Core Spray, Minimum-Flow Recirculation Line</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2000, with the plant at 100 percent power, Niagara Mohawk Power Corporation identified that the methodology for reverse flow testing Low Pressure Core Spray System Check Valve 2CSL*V9 was inadequate. Technical Specification 4.0.5 requires inservice testing of all American Society of Mechanical Engineers (ASME) Code Class 1, 2, and 3 components in accordance with Section XI of the ASME Boiler and Pressure Vessel Code. Section XI of the ASME Boiler and Pressure Vessel Code requires a quarterly surveillance to reverse flow test Low Pressure Core Spray System Check Valve 2CSL*V9. The surveillance procedure did not establish a condition that would properly reverse flow test the check valve. Failing to properly reverse flow test 2CSL*V9 is a violation of Technical Specification 4.0.5. The cause was the responsibility for ensuring that the test method actually worked was not clearly assigned. A contributing cause was the absence of written standards or guidance for validating that a test procedure actually performed the intended test, resulting in a lack of rigor in the validation process. Corrective actions include: revising the surveillance procedure and retesting Valve 2CSL*V9, clearly assigning roles and responsibilities within selected programs, and developing a validation checklist to establish effectiveness of pump and valve test methods.
4122000001 | Beaver Valley 2 | 09/23/2000 | 10/20/2000 | ML00376537 | <strong>ESF Actuation of Feedwater Isolation While Shutting the Plant Down For Refueling</strong><br /><i>Abstract:&nbsp;</i>At 00:37 on September 23, 2000, Beaver Valley Power Station (BVPS) Unit 2 experienced an automatic Feedwater Isolation resulting from indicated high steam generator water level. This occurred while shutting the plant down for refueling. All plant equipment properly responded as expected. The operating crew then transitioned to the operating procedure to reset feedwater isolation signal and to restore the secondary system to normal. The automatic initiation of a Feedwater Isolation signal and the resultant automatic initiation of the Auxiliary Feedwater System due to the tripping of the Main Feedwater Pumps following the Feedwater Isolation constitutes an automatic actuation of an Engineered Safeguards Feature. This requires NRC reporting within four hours of the occurrence, pursuant to the reporting criteria of 10 CFR 50.72(b) (2) (ii), and LER reporting within 30 days of the occurrence, pursuant to the reporting criteria of 10 CFR 50.73(a) (2) (iv). The cause was the lack of procedural clarity combined with simulation training not being consistent with actual plant response. As a result of the inadequate procedure clarity, the initial water inventory in all steam generators was inappropriately high.
4122000002 | Beaver Valley 2 | 10/15/2000 | 11/10/2000 | ML00376944 | <strong>Failure to Verify Spent Fuel Pool Boron Concentration Prior to Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2000, a spent fuel assembly in the Beaver Valley Power Station (BVPS) Unit 2 Spent Fuel Pool (SFP) was moved to perform ultrasonic testing of the fuel assembly. Later that day it was determined that the SFP soluble Boron concentration was not verified in accordance with Technical Specification Surveillance Requirement (SR) 4.9.14.2.a, which requires verifying the SFP soluble Boron concentration to be greater than or equal to 1050 PPM soluble Boron within 8 hours prior to and at least once per 24 hours during movement of fuel in the SFP. This condition was found to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Inadequate communication between the Refueling Engineer and Nuclear Shift Supervisor (NSS) caused the NSS to believe that work in the fuel building involved the movement of ultrasonic testing equipment, but not fuel. Also, the procedure used for fuel movement was inadequate in that it did not contain an NSS signoff that would have alerted him that fuel was to be moved. Subsequently, the NSS verified all of the requirements for the movement of loads above the SFP, but not the soluble Boron concentration required for fuel movement. Upon discovery of the event the SFP was sampled and the soluble Boron concentration was determined to be 2096 PPM, well above the required 1050 PPM. An Operations procedure containing prerequisites for using the SFP Bridge Crane was written and Refueling procedures were revised to require the performance of this new procedure as a prerequisite. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
4122000003 | Beaver Valley 2 | 12/11/2000 | 01/10/2001 | ML01019016 | <strong>Reactor Coolant System Leak Initiates Plant Shutdown and Declaration of an Unusual Event</strong><br /><i>Abstract:&nbsp;</i>On December 11, 2000, at 0320 hours, the Beaver Valley Power Station (BVPS) Unit No. 2 control room operators received indications of a Primary System leak in the Reactor Containment Building. The rate of leakage was noted to be in excess of the Technical Specification 3.4.6.2 limit of one gpm for unidentified leakage. A plant shutdown at 2 percent a minute was initiated at 0412 hours. At 0536 hours, the Reactor Coolant System (RCS) unidentified leak rate was estimated to be between 12 and 20 gpm based on charging/letdown mismatch and an Unusual Event was declared. Plant cool down and depressurization of the RCS continued and Mode 5 was entered at 1357 hours. The Unusual Event was terminated at 1405 hours. This condition is being reported pursuant to 10CFR50.73 (a) (2)(i)(A) as the completion of any nuclear plant shutdown required by the plant's Technical Specifications. The cause of the RCS leakage into the containment building was an abrupt packing leak on a motor-operated (MOV) drain isolation valve on the RCS. The direct cause of the packing leak was a failure of one the valve's two stainless steel gland stud eyebolts. The gland stud eyebolts on the RCS primary loop fill and drain valves were replaced with a more stress corrosion resistant material. Since this actual event did not result in a plant trip, there was no increase in any analyzed initiating event frequency, and hence no increase in the core damage frequency.
4132000001 | Catawba 1 | 02/13/2000 | 03/14/2000 | ML00369383 | <strong>Reactor Trip Caused by a Pin to Pin Short Circuit within an Electrical Connector on the Turbine Electrical Connector on the Turbine Electrical Trip Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2000 at 1831 hours with Catawba Unit 1 operating in Mode 1 "Power Operation" at 100% power, a reactor trip occurred. The cause of the reactor trip was actuation of the turbine trip instrumentation inputs to the Solid State Protection System (SSPS) logic. This was due to an electrical short within an electrical connector on the normally energized Turbine Electrical Trip Solenoid Valve (ETSV). This caused the normally energized ETSV to de-energize and dump Emergency Trip System (ETS) pressure, resulting in the pressure switches on the ETS header sensing pressure dropping below their set point and thus sending a signal that the turbine was tripped to the SSPS. The SSPS then initiated a reactor trip. All systems responded as designed to shut down the reactor and maintain it in a safe shutdown condition. This event is being reported as an automatic actuation of the reactor protection system. Corrective Actions included replacing the failed connector. A failure analysis performed on the connector determined that the root cause of the problem was a misapplication of the connector insert insulating material, which is made of neoprene. This connector will be replaced with a high temperature model.
4132000002 | Catawba 1, Catawba 2 | 02/10/2000 | 03/13/2000 | ML00369386 | <strong>Bypassed Compensatory Action on ECCS Pump Area Sump Pumps Caused Plant to be in a Condition Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2000 plant personnel determined that a condition outside the design basis of the plant had occurred on Unit 1 & Unit 2 due to defeating part of a compensatory action for monitoring potential emergency core cooling system (ECCS) leakage outside containment. The compensatory action was initiated because of an interlock that was not installed during the original construction of the plant as described in LER 413-98-016. The interlock was supposed to trip the residual heat removal and containment spray sump pumps upon receipt of a safety injection signal and allow the pumps to start on high-high sump level, with an accompanying Control Room alarm. This interlock was to facilitate leak detection from ECCS components outside containment following a loss of coolant accident. This compensatory action was found defeated on February 10 and 16, 2000. Subsequent reviews found another 7 times that the compensatory action was defeated. The root cause was that compensatory actions are not reviewed and integrated into appropriate processes to ensure communications and coordination takes place to maintain compliance with the requirements. Interim corrective action consisted of restoring the compensatory action to service and increasing the approval authority to allow defeating this compensatory action. Planned corrective actions include a review and revision of the compensatory action program to preclude recurrence.
4132000003 | Catawba 1, Catawba 2 | 03/08/2000 | 04/07/2000 | ML00370162 | <strong>Use of Control Room Pressure Boundary Compensatory Action Caused Control Room Ventilation System to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>In February 1998, the NRC questioned the use of a control room pressure boundary compensatory action to maintain Control Room Ventilation System (VC) operability. The compensatory action was developed to maintain the VC system operable during the performance of maintenance activities that compromised the control room pressure boundary. The compensatory action document specified that measures would be taken to restore the control room area pressure boundary within five minutes of a condition that could potentially challenge control room habitability. The compensatory action was based on engineering calculations for an operability evaluation of the time required to restore control room pressure. The compensatory action was deleted on May 21, 1999. On March 8, 2000 the NRC determined that reliance on the compensatory action (in lieu of declaring the VC system inoperable) was a violation of Pre-Improved Technical Specifications (Pre-ITS) 3.7.6 and 3.0.3. Corrective actions will include a TS change to allow the VC System to remain operable with a compromised pressure boundary for maintenance activities up to 24 hours.
4132000005 | Catawba 1 | 11/10/2000 | 12/07/2000 | ML00377762 | <strong>Engineered Safety Feature Actuation - 1B 4160 Volt Bus De-Energized Due to 1B Emergency Diesel Generator Potential Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2000, Operations was performing "B" train engineered safety feature (ESF) testing per plant procedures. During the blackout/LOCA section, a non-licensed operator at the 1B diesel generator (DG) notified the control room that smoke was coming out of the 1B DG generator control panel. The 1B DG was immediately shutdown and operations entered abnormal procedure, (AP) AP/l/A/5500/007, Loss of Normal Power, to remove control power from the 1B DG and reenergize the ESF bus 1ETB from offsite power. At the time of this event, the 1B DG was the only power source to ESF bus 1ETB. The shutdown on the 1B DG resulted in a loss of voltage to ESF bus 1ETB and actuation of its undervoltage relays. This is an ESF actuation and is reportable pursuant to 10 CFR 50.73 (a) (2)(iv). The cause of this event was a failure of the 1B DG voltage regulator potential transformer. The apparent cause of the failure of the potential transformer was a turn - to - turn fault in one phase. Engineering performed a common mode failure analysis and determined that no common mode failure existed. The failed transformer was replaced and the 1B DG successfully tested and returned to service on November 13, 2000. Additional testing and inspections on the remaining DG voltage potential transformers (1A, 2A, & 2B DGs) will be conducted to determine if any additional corrective actions are required.
4132000006 | Catawba 1 | 11/10/2000 | 12/07/2000 | ML00377763 | <strong>Invalid Engineered Safety Features Actuation Occurred During Calibration of Pressurizer Pressure Instrumentation Channels as a Result of a Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2000, at 1107 hours, an invalid safety injection signal was generated on a two-out-of-four pressurizes pressure channels "low" condition. At the time, Unit 1 was in Mode 6 in its End-of-Cycle 12 Refueling Outage. Personnel were in the process of performing calibration work on channel 3 of the pressurizes pressure instrumentation. Channel 2 of the pressurizes pressure instrumentation had failed earlier in the outage and was in a tripped condition. When channel 3 was taken out of service for calibration, the required logic was satisfied. No actual Emergency Core Cooling Systems (ECCS) injection into the Reactor Coolant System (RCS) occurred, since the ECCS was isolated from the RCS at the time. A root cause analysis of this event determined that it occurred as a result of a defective calibration procedure. The procedure did not require the operating status of the other three instrumentation channels to be ascertained prior to performing the calibration. Corrective action from this event includes revising the affected procedure to include this requirements.
4142000001 | Catawba 2, Catawba 1 | 02/29/2000 | 03/30/2000 | ML00369886 | <strong>Failure of Diesel Generator Output Breaker Renders 2B Diesel Generator Inoperable for Longer than Technical Specifications Allow</strong><br /><i>Abstract:&nbsp;</i>On February 29, 2000 during the performance of the Operability Performance Test (PT/2/A/4350/002B) on diesel generator (DG) 2B, Operations was unable to close the DG Output Breaker (2ETB-18) when attempting to parallel the DG to the bus. DG 2B was secured by operations and declared inoperable. Troubleshooting revealed that the most probable root cause was loose contact parts inside the control device that prevented closure of one of the contacts in the breaker close coil circuit. Examination of the failure mode determined that the breaker was most likely in this condition since the last time it had been operated during testing on 2/7/00. Therefore, DG 2B had been inoperable since 2/7/00. During this period routine maintenance activities resulted in equipment on both units being taken out of service. DG 2B and other required features supported by DG 2B being inoperable resulted in noncompliance with TS which is reportable as a condition prohibited by TS, 10 CFR 50.73 (a)(2)(1)(B), and TS LCO not met, 10 CFR 50.36(c)(2). The failed control device was replaced and breaker 2ETB-18 successfully tested. The vendor of the failed breaker is being requested to provide recommendations on further corrective actions. Since no event occurred during this time that required the use of DG 2B, the health and safety of the public were not affected by this event.
4142000002 | Catawba 2 | 04/29/2000 | 07/19/2001 | ML01207014 | <strong>Inoperable Ignitors on Both Trains of the Hydrogen Ignition System Due to a Common Cause Failure Mode of Non-Safety Related Equipement Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2000, during Mode 1 operation, it was discovered that 22 of 35 ignitors of Train B of the Hydrogen Ignition System (HIS) had failed and were inoperable. 34 ignitors were replaced on Train B (one ignitor was inaccessible due to its location beneath the reactor vessel missile shield). Following replacement of the Train B ignitors, Train A of the HIS was tested on April 29, 2000, and 2 of 35 ignitors failed. 34 Train A ignitors were replaced (the inaccessible ignitor beneath the missile shield was not replaced). The cause of this event was lack of a process to ensure that new production lots of ignitors were tested to ensure that the design basis for their applicability could be met. Catawba retroactively determined that multiple ignitors on each HIS train were inoperable due to a common cause failure mode. An emergency Technical Specification (TS) amendment was subsequently requested and approved to exclude the ignitors beneath the missile shield from the HIS TS requirements on a temporary basis. A new procedure has been developed to perform proper testing of ignitors after receipt to ensure they can perform their design function. For this event, the overall hydrogen mitigation function was maintained as a result of the remaining ignitors and other hydrogen mitigation equipment. Therefore the health and safety of the public was unaffected.
4162000001 | Grand Gulf 1 | 06/28/2000 | 07/25/2000 | ML00373573 | <strong>Failure to Comply with Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2000 between 1410 to 1424, for a period of 14 minutes, operators did not recognize the need to take the Required Actions of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.7, specifically Required Action F. Entry into LCO 3.4.7, Required Action F is required if there is no operable Reactor Coolant System (RCS) Leakage Detection Instrumentation. LCO 3.4.7 Required Action F requires immediate entry into LCO 3.0.3 which requires a shutdown to be initiated within one hour. Failure to perform the Technical Specification LCO actions was not discovered until June 29, 2000 at 1745 at which time a Condition Report (CR-GGN-2000-0931) was written and root cause investigation was initiated. The requirements of TS 3.4.5 for Reactor Coolant System (RCS) Operational Leakage were met throughout the event since the remainder of the calculation process for drywell floor drain sump inleakage remained operable throughout this event. The described condition has no effect on core damage frequency as it does not impact potential core damage initiators or any of the systems that would be utilized for mitigation following potential initiators.
4162000002 | Grand Gulf 1 | 12/09/2000 | 01/22/2001 | ML01025023 | <strong>Plant Outside Design Basis (Kaowool)</strong><br /><i>Abstract:&nbsp;</i>GGNS uses Kaowool to satisfy commitments for me ting 10CFR50, Appendix R, Section III.G.2 safe shutdown separation requirements, as a nominal 1-hour fire barrier and as a radiant energy shield inside containment. GGNS also uses Kaowool to satisfy Regulatory Guide 1.75 electrical separation requirements. During resolution of concerns promulgated in SECY 99-204, GGNS developed a re-qualification plan to establish the fire resistive rating and overall acceptability of Kaowool. Limited installation instructions and documentation necessitated the need to destructively examine representative samples of GGNS Kaowool raceways. The examinations revealed deficiencies that compromised the ability of Kaowool to perform as designed. Based on the nature of the deficiencies identified, the results of the examinations were generically applied to all Kaowool installations. Subsequent evaluations concluded that the only area where redundant safe shutdown capability may have been compromised during a postulated fire was the Division II ESF Switchgear Room. The fire barrier in this area is augmented with early warning smoke detection, heat detection, and automatic suppression capability. This area is being monitored by an hourly fire patrol. Regulatory Guide 1.75 electrical separation requirements are unimpaired by these deficiencies.
4162000003 | Grand Gulf 1 | 06/15/2000 | 09/01/2000 | ML01040006 | <strong>Use of Inaccurate Meteorological Data Units</strong><br /><i>Abstract:&nbsp;</i>Meteorological data is required to calculate atmospheric dispersion of a radiation release. Plant staff supplied meteorological data to an end user with inconsistent units of measure. This resulted in calculation of inaccurate dispersion coefficients. The dispersion coefficients were not used for actual release calculations but were used as the basis for some changes to the plant. Dose calculations that applied these values were used as inputs for secondary containment relaxation during a refueling outage. Technical Specification changes based on these calculations were approved in License Amendment 139. Other dose calculations using these values have also been submitted to the NRC as part of the GGNS full scope alternative source term application. Both of these sets of calculations were performed conservatively. Using met data previously submitted by GGNS, a NRC staff reviewer identified inconsistencies in the alternative source term application and requested additional information. These questions facilitated the identification of the inaccurate data. Plant personnel determined the deficiency in the units of measure used for the calculations. A condition report was issued and a root cause investigation initiated. Acting conservatively, a 10CFR50.9 notification was made to the NRC Region IV Administrator on June 15, 2000. Engineering re-calculated the dispersion coefficients using accurate and more recent data. The described condition has no effect on the public health and safety as the new calculations using the correct units are within the bounds of previously analyzed acceptance criteria. This voluntary LER addresses the referenced 10CFR50.9 notification.
4162000004 | Grand Gulf 1 | 09/07/2000 | 09/29/2000 | ML01040027 | <strong>Inadvertent Reactor Core Isolation Cooling Isolation Due to Failure to Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2000, the Reactor Core Isolation Cooling (RCIC) system isolated while technicians were performing area high temperature calibrations. Procedural steps to place the logic bypass switch to the bypass position were not performed. This resulted in the closure of the RCIC Steam Supply Drywell Outboard Isolation when the leads were disconnected from the trip unit. With RCIC isolated, the plant entered a Technical Specification limiting condition for operation (LCO) which requires immediate operability verification of the High Pressure Core Spray (HPCS) system and the return of RCIC to service within 14 days. Immediate action was taken to enter the required LCO and verify HPCS operable. The surveillance was completed correctly and RCIC was returned to service in 41 minutes, which was well within the LCO requirement. Interim corrective actions included a human performance evaluation which determined the root cause of the event to be failure to follow the procedure. Counseling of the technicians Involved was conducted as part of the interim corrective actions. Additionally, I&C supervisors will also discuss this event and Its Implications with all I&C technicians. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
4162000005 | Grand Gulf 1 | 09/15/2000 | 10/13/2000 | ML00377704 | <strong>Automatic Reactor Scram Due to Offsite 500 KV Circuit Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On 9/15/00 at approximately 0630 hours, while operating at steady state conditions, a reactor scram occurred. The scram was the result of a reactor protection system actuation from a turbine control valve fast closure signal. This signal was the result of a generator load transient caused by failure of a 500 kV circuit breaker located in an offsite switchyard which directly feeds the GGNS switchyard. A generator load reject was sensed due to the grid voltage transient, causing generator load demand to automatically switch off. A turbine control valve fast closure was sensed as Turbine Control Valves (TCVs) closed. However the generator stayed online and, due to the speed demand signal that was still present, the TCVs did not go full closed. The reactor scrammed but the End of Cycle Recirculation Pump Trip (EOC-RPT) did not occur. This issue is being addressed in Licensee Event Report 200-00600. No major equipment was out of service except for Engineered Safety Feature Transformer 12 to 17AC bus feeder breaker, which was tagged out of service. All control rods inserted and all other equipment responded as expected. Reactor Core Isolation Cooling initiated and began injecting into the vessel, however no ECCS initiated. Additionally, due to the low grid voltage, the Division III diesel generator started on undervoltage as designed, tied to and provided power to the 17AC bus.
4162000006 | Grand Gulf 1 | 09/18/2000 | 10/13/2000 | ML01031021 | <strong>Unanalyzed Condition - Turbine Control Valves May Move in Excess of Design Assumptions</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2000, during evaluation of the data from a recent reactor scram that occurred on September 15, 2000, an unanalyzed condition was identified. Specifically, a main generator partial load reject can actuate a circuit contained in the turbine controls that may cause Turbine Control Valve (TCV) motion in excess of design assumptions and may not always actuate a reactor scram/recirculation pump downshift as assumed by analysis. No End of Cycle / Recirculation Pump Trip (EOC/RPT) initiation occurred with the TCV fast closure. It appears that the EOC/RPT logic was not satisfied. During this event, both the direct scram and the bypass valves functioned as designed. Although there was some limited reactor pressurization (as seen by the secondary pressure scram signal), this transient is bounded by the assumptions in the analysis due to the slower TCV closure rate and bypass function experienced in this event. Therefore all operating margins were protected during the event and the health and safety of the public was not affected. This event is being reported pursuant to 10CFR50.73(a)(2)(ii).
4162000007 | Grand Gulf 1 | 10/26/2000 | 11/22/2000 | ML01031022 | <strong>Plant Outside of its Design Basis with Respect to Appendix R</strong><br /><i>Abstract:&nbsp;</i>The Kaowool fire wrap system is used in certain plant areas as a nominal 1-hour fire barrier to satisfy GGNS' License Condition to meet 10CFR50, Appendix R, Section III.G.2.c commitments. While performing plant walkdowns as part of the GGNS effort to address Kaowool issues in SECY 99-204, deficiencies were identified with the as-installed fire barrier configuration. The initial evaluation identified a condition that may prevent the fire barrier from providing adequate protection for raceways containing Division I and II circuits for ESF Switchgear Room Coolers which support the operation of redundant Division I and II SSD components. Loss of Coolers may potentially affect Division I and II SSD capability. The affected area was under an hourly fire watch. Early warning fire detection and automatic fire suppression are available in this area. Review of the GGNS IPEEE Fire Model confirms that due to the location of the SSD raceways and the projected flame spread of a fire, a transient or fixed fire in this area is not expected to damage these cables. Additionally, there is an alternative method of actuating the affected Coolers locally. Therefore, in the event of a fire in the affected area, the ability of the plant to shutdown and maintain shutdown condition would be maintained. However, the event is being reported pursuant to 10CFR50.73(a)(2)(ii).
4232000001 | Millstone 3 | 01/21/2000 | 02/17/2000 | ML00368506 | <strong>Ultimate Heat Sink Below Minimum Design Temperature</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2000, with the plant in Mode 1, the inlet temperature of the service water system (SWP), as determined by the circulating water inlet temperature, decreased below the 33 degree F design basis minimum and a prompt report was made pursuant to 10CFR50.72(b)(1)(ii)(B). The Ultimate Heat Sink (UHS) for the service water system is Niantic Bay, Long Island Sound. On multiple occasions subsequent to this event, as detailed in this report, the UHS again dropped below 33 degrees F. The SWP provides cooling water for plant safety-related systems during normal and accident conditions. Operability Determination MP3-004-00 provides justification for continued operation with SWP temperature below 33 degrees F and above 29 degrees F. Compensatory actions were put in place to run safety injection pump cooling system (CCI) at SWP temperatures below 33 degrees F to prevent potential freezing of stagnant freshwater CCI fluid in the shell side of the CCI heat exchanger, while cold SWP passes through the tube side. Throughout the event, safety systems and components remained operable and continued to function as designed. The condition of potential operation outside design basis with SWP temperatures below 33 degrees F had previously been identified by the station Corrective Action Program in 1998. The cause of the event on January 21, 2000, was determined to be a failure to appreciate the operational significance of this condition and to assign adequate priority to its resolution prior to seasonal cold temperatures. The corrective action is to align the existing design basis SWP lower limit with the historically lower temperatures observed by December 15, 2000. This condition is reportable pursuant to 10CFR50.73(a)(2)(ii)(B) as an event or condition that resulted in the nuclear plant being in a condition that was outside the design basis of the plant.
4232000002 | Millstone 3 | 07/18/2000 | 08/14/2000 | ML00374355 | <strong>Technical Specification 3.0.3 Entry with both Hydrogen Recombiner Trains Inoperable Due to a Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On July 18, 2000, at 2003 hours with the plant in MODE 1 at 100 percent power and the A train Hydrogen Recombiner out of service for planned maintenance a trouble alarm indicated that the B train radiation monitor had gone off line. At 2030 hours the monitor was confirmed to be inoperable. As the monitor is interlocked with the Hydrogen Recombiner fan as well as the supply and exhaust dampers, the B train Recombiner was also declared inoperable. An inspection of the radiation monitor determined that the failure was caused by water intrusion. With both trains of the Hydrogen Recombiner out of service the Technical Specification Limiting Condition for Operation could not be met and Technical Specification 3.0.3 was entered. Therefore, this condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause for the failure of the B train radiation monitor was water intrusion due to condensation leaking through the floor from an air conditioning unit on the floor above. The water draining from the floor above was diverted and the radiation monitor cabinet was dried out. The power supply was replaced and the circuit boards were tested satisfactorily. In addition, other corrective actions are being addressed via the Millstone Corrective Action Program. These corrective actions include sealing the cracks in the floor above the monitor and installing new conduit fittings with gaskets on top of the monitor enclosure to prevent water from entering.
4232000003 | Millstone 3 | 09/28/2000 | 10/26/2000 | ML00376710 | <strong>Cable Routing for 3CHS*P3B Does Not Meet Fire Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2000, with the plant in mode 1 at 100% power, it was discovered that the 4160V power cable for charging pump, 3CHS*P3B was not installed in the Auxiliary Building as identified by the MP3 BTP 9.5-1 Compliance Report. It was determined that this condition could have significantly challenged the ability to achieve and maintain cold shutdown per the requirements of CMEB BTP 9.5-1 if a design basis fire occurred in the area and the pump cable was damaged as a result of this fire. The MP3 BTP 9.5-1 Compliance Report credits this pump to provide Reactor Coolant Pump (RCP) seal cooling, Reactor Coolant System (RCS) inventory make-up, and RCS boration functions in the event of a postulated fire in an area of the Auxiliary Building where a fire could potentially damage all Reactor Plant Closed Cooling Water (RPCCW) pumps. The RPCCW pumps provide an alternate means of cooling the seals and are assumed to be lost in such a fire. The cause of this condition is that the reviews performed historically failed to correctly identify the location of the power cable for the charging pump 3CHS*P3B relative to the water curtain which has been credited as a barrier between two methods of safe shutdown. Interim compensatory actions as outlined in the Technical Requirements Manual were immediately implemented, and remained in effect until compliance with the Compliance Report was achieved. The power cable for the 3CHS*P3B Pump has been relocated to place the plant in compliance with the MP3 BTP 9.51 Compliance Report.
4242000001 | Vogtle 1 | 02/25/2000 | 03/21/2000 | ML00369602 | <strong>Auxiliary Feedwater Pump Inoperable Longer Than Allowed by the Tech. Specs.</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2000, a monthly turbine driven auxiliary feedwater pump (TDAFWP) operability test was performed. The test determined that the pump differential pressure was below the minimum acceptance criterion of 1662 psid. The TDAFWP speed control was adjusted, and the pump was re-tested satisfactorily and returned to service. A review of pump test data found that the previous month's testing on January 27, 2000, had also displayed inadequate pump differential pressure; however, no corrective action had been taken at that time. This constituted firm evidence that the pump was inoperable for 29 days until the discovery of this condition on February 25, 2000. Although other auxiliary feedwater pumps were available to perform the system safety function, the unit had operated in a condition prohibited by the Technical Specifications. The causes of this event were speed controller instrument drift and a cognitive personnel error. The personnel responsible for performing and reviewing the testing of January 27, 2000 did not recognize the unacceptable test results and initiate corrective actions. The responsible personnel have been counseled and routine preventive maintenance has been established for speed controllers.
4242000002 | Vogtle 1 | 06/05/2000 | 06/27/2000 | ML00372890 | <strong>Manual Reactor Trip Following Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2000, at 1140 EDT, the main steam isolation valve (MSIV) for steam generator (SG) #4 closed. Control room operators observed the valve's trouble alarm and also observed the water level decreasing in SG #4. The reactor operator manually tripped the reactor and all rods fully inserted. The unit was stabilized in mode 3 (hot standby). The direct cause of the reactor trip was the closure of the MSIV which was the result of a blown fuse. The investigation into the cause of the blown fuse found no electrical ground in the circuit or evidence of an overcurrent condition. The area around the valve was also checked for signs of water, loose connections or visible damage, with none found. Therefore, the cause of the fuse failure is unknown. The blown fuse and other fuses were replaced and the unit was returned to service. Other actions including component testing and evaluations are planned to determine the cause and prevent recurrence.
4242000003 | Vogtle 1 | 09/17/2000 | 10/12/2000 | ML00376082 | <strong>Safety Injection System Rendered Inoperable with Unit in Hot Standby</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2000, safety injection system (SI) Train A was inoperable for planned testing and isolated from the reactor coolant system (RCS) cold legs and SI Train B. During the testing, a motor operated valve had to be manually closed. Testing was completed and Train A was unisolated from the RCS cold legs and SI Train B. Shortly thereafter, control room personnel stroked a Train A valve that had been manually operated during the test in order to restore the valve to operability. Prior to the valve stroke, the SI Train A pump was placed in pull-to-lock to prevent inadvertant starting and runout. However, this open valve created a condition in which the Train B SI pump was susceptible to runout had it been started following a large-break LOCA. Therefore, during the time of the valve stroking, both SI pumps were inoperable. This is a condition that could have prevented the fulfillment of the SI system safety function and also represents operation of the unit in a condition prohibited by the Technical Specifications. The causes of this event were a lack of procedural guidance to address precautions to be taken in the event of valve anomalies, and personnel errors by those conducting the testing for not ensuring system operability. Corrective actions are described herein.
4242000004 | Vogtle 1 | 12/09/2000 | 01/04/2001 | ML01009021 | <strong>Procedure Inadequacy Leads to Reactor Trip During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2000, plant personnel were conducting a test of the solid state protection system (SSPS), Train B, per procedure 14421-1, "Solid State Protection System And Reactor Trip Breaker Train B Operability Test." The Balance of Plant operator (BOP) proceeded through the procedure steps in an orderly fashion to section 5.3. When the BOP performed step 5.3.1, "PLACE the MEMORIES Switch to Position 9," an automatic reactor trip occurred at 1015 EST. The root cause of this event was a procedure inadequacy. A recent change to procedure 14421-1 had moved a portion of the testing from procedure section 5.8 to section 5.3. However, this change bypassed a procedure step to place the Input Error Inhibit switch in the "Inhibit" position, which had previously been performed prior to beginning the section 5.8 testing. The failure to place this switch into "Inhibit" allowed the reactor trip test signals to enter SSPS trip logic and complete an actual reactor trip. Procedure 14421-1 was revised to move the section 5.3 testing back to section 5.8 and testing was completed satisfactorily.
4402000001 | Perry | 01/13/2000 | 02/14/2000 | ML00368551 | <strong>Potential for Inadequate Suppression Pool Make-Up for the Emergency Core Cooling Systems</strong><br /><i>Abstract:&nbsp;</i>During an engineering review of the Inclined Fuel Transfer System (IFTS) blind flange removal at power, the Emergency Core Cooling System (ECCS) was determined not to meet the design criteria due to a potential for insufficient Suppression Pool Make-Up (SPMU). A recent license amendment allowed removal of the blind flange and subsequent testing of IFTS at power. The blind flange is part of the upper pool boundary for water volume required for the Loss of Coolant Accident (LOCA) analysis. The boundary to maintain upper pool volume, with the blind flange and IFTS gate in the upper containment pool removed, is either the upper or bottom IFTS valve. These valves are not safety related. The safety analysis report credits only safety-related equipment I for accident mitigation, and, therefore, these valves are not assumed to prevent water loss during a LOCA. The reduced water inventory would be less than that required for SPMU. The resultant reduced suppression pool volume and increased temperature could potentially result in the loss of all ECCS pumps due to a lack of adequate suction pressure. On March 25, 1999, the IFTS blind flange and the IFTS pool gate were removed at power prior to achieving cold shutdown on March 27, 1999, for refueling outage seven. This condition was reported in accordance with 10 CFR 50.72 (b)(1)(ii)(B) for the plant having been outside of the design basis on January 13, 2000 (ENF # 36588). This Licensee Event Report is submitted in accordance with 10 CFR 50.73 (a)(2)(ii) for the plant having been outside of the design basis. The cause of this condition was attributed to inadequate internal reviews and insufficient procedural barriers.
4402000002 | Perry | 03/01/2000 | 03/31/2000 | ML00370157 | <strong>Inadequate Data Validation Checks Result in Missed Power Distribution Limits Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2000, reactor engineering personnel identified that the parameters on 3D Monicore reports, listing thermal limits and other plant parameters, were not varying as expected. The 3D Monicore was determined to be using static (historical) data instead of current plant data to calculate the thermal limits. This condition existed since an Integrated Computer System (ICS) reset was performed on February 28, 2000. This condition was corrected on March 1, 2000. The Technical Specification (TS) Power Distribution Limits Surveillance Requirements (SRs) verify that plant parameters are within the specified limits once per 24 hours. During the interval that static data was being used, these SRs were not satisfied. Failure to perform these SRs and to restore 3D Monicore configuration within the required completion time is a condition prohibited by TS and, therefore, a Licensee Event Report is required by 10 CFR 50.73 (a)(2)(i)(B). Subsequently, reactor engineering personnel evaluation concluded with a high degree of confidence that plant parameters were within TS thermal limits during this interval. Two primary causes for this condition were identified, both attributed to inadequate software design. A parameter validation check is being performed by operations during the conduct of the SRs to ensure current plant data is being utilized to calculate thermal limits. The ICS software is scheduled to be modified by April 6, 2000.
4402000003 | Perry | 02/19/1999 | 04/19/2000 | ML00370745 | <strong>Battery Age Determination Results in Tecnical Specification Violation of Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1999, an operability determination was performed for the Division 3 Unit 1 battery based on a question regarding installation dates. Testing frequency for the battery to meet Surveillance Requirements is determined by the age of the battery. This battery was installed in November 1984, and was assumed to be at 72 percent of a 20-year service life. Further investigation indicated that the battery cells had been stored on trickle charge since January 11, 1978, and many of the original individual cells had been replaced. This information was used in determining the service life of the batteries. Based on the engineering analysis performed, the overall life of the Division 3 Unit 1 battery was determined to be 9.7 years by calculating the arithmetic average of the age of the individual battery cells, and also by battery curve comparisons and performance test results. The Division 3 Unit 1 battery was concluded to be OPERABLE, and the required surveillances were continued at the less restrictive frequency (60 months vice 18 months). The Senior Resident Inspector questioned the approach used for calculation of battery age, and referred this to Office of Nuclear Reactor Regulation staff for evaluation. The staff concluded that this approach for calculating battery age was not acceptable, and stated that the more restrictive surveillance frequency should have been observed. A Non-Cited Violation was issued in Inspection Report 50-440/99015, dated March 19, 2000. Therefore, this event is being reported under 10 CFR 50.73 (a)(2)(i) as a condition prohibited by Technical Specifications.
4402000004 | Perry | 05/15/2000 | 06/13/2000 | ML00372481 | <strong>Technical Specification 3.0.3 Entered Due to Inoperability of Both Trains of Annulus Exhaust Gas Treatment System</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2000, the Perry Nuclear Power Plant performed routine sampling of activated carbon from the B train of the Annulus Exhaust Gas Treatment System. The B train had been declared inoperable on May 15, 2000, to facilitate this work activity. A surveillance instruction had been commenced on the A train of the system on May 14, 2000. This included a noninvasive test to verify airflow, which was deferred until May 15, 2000, when Engineering support personnel were available. During the surveillance, it was discovered that the airflow for the A train was high outside of the specified band. As a result, the A train was declared inoperable at 1155 hours on May 15, 2000. This resulted in both subsystems inoperable, and entry into Technical Specification 3.0.3 was required by the governing Technical Specification Condition. The airflow on the A train was adjusted to within the required operating band, and was returned to operability at 1607 hours on May 15, 2000. With one train restored to operability, the plant exited Technical Specification 3.0.3 without performing power changes. The B train was restored to operability shortly thereafter at 1702 hours on May 15, 2000. The apparent cause of this event was a flow anomaly resulting from a combination of factors, including design or operating characteristics affecting system pressure control. A contributing cause was the release of a surveillance activity on the redundant system train. Corrective actions will include increased monitoring and additional guidance for statusing of Divisional systems. Entry into Technical Specification 3.0.3 is reportable under 10 CFR 50.73(a)(2)(i) as a condition prohibited by Technical Specifications.
4402000005 | Perry | 11/01/2000 | 06/28/2001 | ML01187002 | <strong>Unrecognized Design Requirement for Emergency Service Water Resulted in Operation Outside the Design Bases</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2000, at approximately 1300 hours, the Perry Nuclear Power Plant (PNPP), Unit No. 1, was operating at 98.5 percent rated thermal power, when it was identified that a condition had existed that resulted in operation outside of the plant's design basis. With the Emergency Service Water (ESW) alternate intake sluice gates open, recirculated discharge water would raise the ESW suction temperature above the design-input value resulting in potential inadequate cooling during a Design Basis Accident (DBA). The condition was discovered during an investigation related to opening the ESW sluice gates. A detailed engineering calculation, has since been completed as a corrective action to a sluice gate issue documented in the plant's corrective action program, validating that the gates should not be opened without aligning the ESW discharge to the surface drainage (swale). This condition has existed since the initial operation of the plant, during which the sluice gates have been opened on limited occasions to support maintenance of the gates. The detailed engineering calculation was also utilized to determine operator response time for restoration of the ESW system had it been required to perform its safety function. The calculation results demonstrated that adequate time was available to realign the system to the swale during a DBA. The apparent cause of this condition was inadequate initial ESW design. There was no engineering design information provided by the Architect Engineer that could have allowed the understanding that opening the sluice gates at low lake temperature without realignment to the swale would result in exceeding the design inlet temperature for ESW during a DBA. This condition is a latent error that has existed since the initial operation of the plant. The condition was entered in the plant corrective action program and administrative controls were put into place to ensure the ESW system discharge is aligned to the swale prior to opening the sluice gates. Corrective actions to incorporate the final calculation results into the plants design basis have been completed. Additionally, permanent procedure controls have been implemented that reflect the design. This License Event Report is submitted in accordance with 10 CFR 50.73(a)(2)(ii), plant outside its design basis.
4432000001 | Seabrook | 01/19/2000 | 02/18/2000 | ML00368690 | <strong>Non-Compliance With Technical Specification 4.8.4.2 Due to Inadequate Breaker Scheduling Guidance</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2000, with the plant operating at 100% power (operational mode 1), it was determined that the performance of a Technical Specification (TS) required surveillance was not fully met prior to the start-up from refueling outage 5 (OR05) (May/June 1997). TS 4.8.4.2.a.2 requires testing of 5 Type FJ circuit breakers, (10% of the total population of 42) and should a circuit breaker be found inoperable during functional testing, an additional representative sample of at least 10% of all circuit breakers of the inoperable type shall be functionally tested until no more failures are found or all circuit breakers of that type have been functionally tested. Contrary to the requirement of TS 4.8.4.2.a.2, testing on 5 additional Type FJ circuit breaker was not performed per TS. Out of a total population of 42 Type FJ circuit breakers, 25 breakers had been tested while 16 of the remaining available 17 breakers were inappropriately considered unavailable for testing due to preconditioning, (removed from their cabinets and manually exercised) and one breaker was inadvertently left off the list of available breakers, thus the requirements of TS 4.8.4.2.a.2 were not met. This event is reportable pursuant to the requirements of 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant Technical Specifications. The cause of the event was the lack of a formal program to ensure TS 4.8.4.2.a.2 was met. Corrective actions have been identified to formalize the program to improve scheduling guidance for TS 4.8.4.2.a.2 breaker selection.
4432000002 | Seabrook | 02/04/2000 | 03/03/2000 | ML00369168 | <strong>Inadequate Surveillance Testing of the Spent Fuel Pool Bridge and Hoist Interlock</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2000 with the plant operating at 100% power, it was determined by Operations Department personnel that the requirements of Technical Specification Surveillance Requirement (SR) 4.9.7 were not met. SR 4.9.7 requires the interlocks that prevent crane (spent fuel pool bridge and hoist) travel with loads in excess of 2100 pounds over the fuel assemblies be demonstrated operable within 7 days prior to crane use and at least 7 days thereafter during crane operation. SR 4.9.7 was met utilizing station procedure OX1415.04 "Spent Fuel Bridge Assembly Weekly Operational Test." During a review of OX1415.04, it was determined that inconsistencies existed between the surveillance procedure acceptance criteria and SR 4.9.7. Since the spent fuel pool bridge and hoist travel interlock and the overload protection device were not set to meet the requirements of SR 4.9.7, this is a condition prohibited by the Technical Specifications and is reportable pursuant to the requirements 10 CFR 50.73(a)(2)(i)(B). This event resulted from a misunderstanding of the relationship of the spent fuel pool bridge and hoist interlocks as they pertain to the requirements of SR 4.9.7. The safety consequences of this event are minimal. Two corrective actions have been identified to prevent recurrence.
4432000003 | Seabrook | 05/29/2000 | 06/16/2000 | ML00372529 | <strong>Shutdown Bank Rods Mis-alignment During Quarterly Rod Operability Surveillance</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2000, North Atlantic determined that a mis-alignment of two of the four Shutdown Bank E rods occurred during the quarterly rod operability surveillance performance. This resulted in a condition prohibited by plant's Technical Specifications (TS) as the two mis-aligned rods were found to be not fully withdrawn. This condition is prohibited by TS 3.1.3.5 and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B). The root cause of this event has not yet been determined. Based on discussions with the Control Rod Drive Mechanisms (CRDM) vendor and review of other similar types of events at other utilities, two potential root causes were identified, one electrical and one mechanical. The postulated electrical cause is a one-time or intermittent degradation of portions of the rod control system circuitry such that when out motion was demanded by the system, the control rod drive mechanism gripper timing was off and the rods slightly descended into the core. The postulated mechanical cause is physical sluggishness that also would affect timing of the moveable and/or stationary grippers on the rods due to increased friction acting on moving parts or physical interference due to the temporary presence of debris in the vicinity of the CRDM grippers. Subsequent movement of the rods would have likely facilitated dislodging the debris. Additional troubleshooting to explore the root cause will be performed prior to the startup from the seventh refueling outage.
4432000004 | Seabrook | 06/26/2000 | 07/26/2000 | ML00373666 | <strong>Manual Reactor Trip and ESF Actuation Due to a Steam Generator Low-Low Level Indication</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2000 at approximately 1851 with the reactor operating at 100 percent power (mode 1), the "A" Main Feedwater Pump (1FW-P-32A) tripped. The trip of 1FW-P-32A resulted in a setback to 55 percent power. Approximately 1 minute and 25 seconds after the trip of 1FW-P-32A, plant operators received a low level alarm on the "C" steam generator due to the inability of the "B" Main Feedwater Pump (1FW-P-32B) to maintain feed water inventory to the steam generators in proportion to the reactor power level. Shortly thereafter, a manual reactor trip was initiated by plant operators as steam generator levels approached the low-low level trip setpoint. This event (Event Number 37117) was initially reported to the Nuclear Regulatory Commission on June 26, 2000 at 1923 pursuant to the requirements of 10 CFR 50.72(b)(2)(ii). This event is additionally reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(iv). 1FW-P-32A tripped as a result of a momentary steam generator High-High level signal originating from the solid state protection system (SSPS). A number of corrective actions have been completed and identified. There were no adverse safety consequences as a result of this event. Plant equipment functioned as designed and operator actions were determined to be appropriate. This is the first event of this type reported within the past two years.
4432000005 | Seabrook | 07/10/2000 | 08/09/2000 | ML00374169 | <strong>Control Room Emergency Makeup Air and Filtration System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2000 at approximately 1148, with the reactor operating at 100 percent power (mode 1), Seabrook Station entered TS 3.0.3 due to having both trains of Control Room Emergency Makeup Air and Filtration System (CBA) inoperable. The "A" train Emergency Cleanup Filter Unit (CBA-F-38) was placed into the emergency filter recirculation mode for its 18 month TS filter flow testing. The "B" train Emergency Cleanup Filter Unit, (CBA-F8038) was operating in the normal makeup mode and was the operable unit, per Technical Specification 3.7.6.1. At 1148, while CBA-F-38 was still isolated, the "Control Room Train B Emergency Makeup Filter Moisture High" alarm (A0098) was received. The alarm is an indication that the "B" train makeup air relative humidity has increased to 60% relative humidity. In response to the Visual Alarm System (VAS) procedure, the Control Room operators identified "B" train Emergency Cleanup Filter Unit heater, (CBA-H-372) as being in the tripped position. With CBA-H-372 tripped, the "B" train was declared inoperable and TS 3.0.3 was entered. At 1152, CBA-H-372 high temperature cutout switch was reset and the "B" train was returned to service and TS 3.0.3 was exited. This event is reportable pursuant to the requirements of 10CFR 50.73(a)(2)(i)(b). The most probable cause of this event has been determined to be CBA-H-372 heater high temperature cutout switch actuation due to personnel inadvertently bumping the switch housing during filter testing. Warning tape to identify switch sensitivity was placed on the switches and a design change to prevent recurrence is being pursued. This is the first event of this type reported by Seabrook Station.
4432000006 | Seabrook | 10/20/2000 | 11/30/2000 | ML00377515 | <strong>Main Steam Safety Valve Lift Pressure Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2000, with the unit in Mode 1 at approximately 65 percent power, the as-found set pressure for one Main Steam Safety Valve (MSSV) was found to be outside the setpoint tolerance allowed by Technical Specification (TS) 3.7.1.1. The MSSV was subsequently tested two more times and the lift set pressures were satisfactory. No repairs or adjustments to the valve were necessary. All other tested valves met the TS acceptance criteria. There were no adverse safety consequences as a result of this event as the as-found lift setpoint of the valve would not have resulted in secondary system pressures exceeding the Condition II (Events of Moderate Frequency) pressure limit (110 percent of design pressure)for the secondary system during the most limiting event. The cause of this condition cannot be conclusively determined given an insufficient amount of data associated with the setpoint of only one MSSV being out of tolerance. However, the most probable cause is component aging. Corrective actions for this event include gathering additional information during future MSSV testing that will aid in further understanding the cause of MSSV setpoint deviations and increased testing frequency of MS-V6 and the other MSSVs that utilize the same style disc insert.
4432000007 | Seabrook | 11/02/2000 | 04/11/2001 | ML01107026 | <strong>Over Pressure Protection System Relief Valve Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2000 with the unit in Mode 6, defueled, the as-found set pressure for the "A" Train Residual Heat Removal (RHR) suction relief valve 1-RC-V-24, was found to be outside the tolerance allowed by Technical Specification (TS) 3.4.9.3. This condition was identified during testing conducted in accordance with TS 4.0.5 and Appendix I of the ASME Operation and Maintenance (0 &M) Code-1995. 1-RC-V-24 is one of two relief valves used to provide overpressure protection of the Reactor Coolant System (RCS) and the RHR System while in Modes 4, 5, and 6. In response to the requirements of the ASME O&M Code for a valve test failure, the one remaining valve in the same test group, the "B" Train Residual Heat Removal suction relief valve 1-RC-V-89 was tested and actuated at 452.5 psig or 2.5 psig above its allowed TS value of 450 psig. There were no adverse safety consequences as a result of this event. Should 1-RC-V-24 lift prematurely, this is a condition that is addressed in North Atlantic's Abnormal Procedures. In the event 1-RC-V-89 was required to actuate, with the RHR System design pressure at 600 psig, there would be sufficient margin to ensure that RHR System integrity would be maintained. The cause of this condition for 1-RC-V-24 has been determined to be associated with the recent changes in the testing methodology. The cause of this condition for 1-RC-V-89 has been determined to be associated with 1-RC-V-89 being inadvertently jarred prior to as-found testing. 1-RC-V-24 and 1-RC-V-89 were replaced with pre-tested spare valves.
4432000008 | Seabrook | 11/01/2000 | 12/29/2000 | ML01009029 | <strong>Voluntary LER for Emergency Diesel Generator Failure During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2000 at 1726, Control Room operators initiated an emergency shutdown of Diesel Generator (DG) 1B upon the receipt of high crankcase pressure and high vibration alarms. The DG was approximately four hours into a 24-hour surveillance run. While coasting down, the engine experienced a crankcase explosion that lifted the crankcase relief cover assemblies and displaced the crankcase exhauster hose. Subsequent investigation revealed damage to the DG's number seven piston and cylinder. The cylinder liner was scuffed/scored and it revealed heavy bonding of aluminum from the piston skirt. The most significant causes of this event have been determined to be due to a combination of the following factors: fast engine starts, rapid loading, high loading, and inadequate cylinder liner surface finish caused by carbon polishing of the cylinder liners. There were no adverse safety consequences as a result of this event since DG-1B was already out of service and the opposite train DG remained operable. Significant corrective actions include inspecting and rebuilding both DGs, changing loading profiles, increasing keep-warm system temperatures, and revising maintenance procedures to address cylinder liner surface condition requirements. A Technical Specification change request will be submitted to propose modifications to DG testing requirements.
4452000001 | Comanche Peak 1, Comanche Peak 2 | 01/21/2000 | 02/22/2000 | ML00368711 | <strong>Technical Specifications Limiting Condition for Operation (LCO) 3.7.3, Feedwater Isolation Valves (FIVS) and Associated Bypass Valves Were Exceeded</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1999, it was discovered that the hydraulic pump for 1-HV-2136, SG 1-03 Feedwater Isolation Valve (FIV 1-03), was not maintaining its prime due to air inleakage. Maintenance personnel were able to re-prime the pump on several occasions, but for long term reliability, maintenance and engineering recommended replacement of the hydraulic pump at power. The Limiting Condition for Operation (LCO) 3.7.3, Feedwater Isolation Valves (FIVs) and Associated Bypass Valves, requires, in part, that four FIVs and associated bypass valves be OPERABLE in Modes 1, 2, and 3. With one or more FIVs inoperable, the action to be taken is to close or isolate the FIV within 4 hours. Operating at power with one FIV inoperable would require a significant reduction in power or placing the unit in Mode 3, Hot Standby. TXU Electric requested that the NRC exercise enforcement discretion to not enforce compliance with LCO 3.7.3 Required Action A.1, A Close or Isolate the FIV within 4 hours, if maintenance activities to repair FIV 1-03 were to take longer than 4 hours. This report is being issued to document that the Completion Time allowed by LCO 3.7.3, Required Action A.1, A was exceeded by 1 hour and 52 minutes. No corrective actions are warranted, since the enforcement discretion to not enforce compliance with LCO 3.7.3 was requested and granted.
4452000002 | Comanche Peak 1, Comanche Peak 2 | 11/19/2000 | 12/11/2000 | ML00377793 | <strong>Some Technical Specification Surveillances Were Not Adequately Documented as Required Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2000, while performing an administrative review and verification of the November 19, 2000 completed shift Surveillance, Operations staff personnel (Utility, Non-licensed) identified that entries on page 6 of 9 of the "Operations Shiftly Routine Tests" logs/forms were not annotated. Following the discovery, it was immediately verified that the missed surveillances were current and satisfactory on November 20, 2000. TXU Electric's evaluation of the event deemed that less than adequate self-verification in recording of the data, and less than adequate review by the Supervisor of the completed surveillances led to this event. Management's expectations with respect to attention to detail and compliance with the Technical Specifications were reemphasized to the cognizant personnel. A Lessons Learned with respect to this event will be promulgated to the individuals who perform and review these type of surveillances.
4462000001 | Comanche Peak 2, Comanche Peak 1 | 12/29/1999 | 01/27/2000 | ML00367945 | <strong>18 Month Surveillance Testing for the Molded case Circuit Breakers was Exceeded Due to Less Than Adequate Scheduling Coordination</strong><br /><i>Abstract:&nbsp;</i>The Comanche Peak Steam Electric Station (CPSES) Technical Requirements Manual (TRM) section pertaining to subject molded case circuit breakers (TRS 13.8.32.2) requires functional testing of at least 10 percent of each type of applicable circuit breakers to be performed on a rotating basis with an 18-month frequency. On December 29, 1999, during a review of the work orders pertaining to the circuit breakers, it was discovered that certain breakers had exceeded the surveillance interval of 18 months in the past when this requirement was a part of the CPSES Technical Specifications (TS). Nevertheless, the up to date surveillances for both units were deemed to be within required Technical Requirements Manual (TRM) or the TS which were applicable at that time, hence, no immediate corrective actions were warranted. The probable cause of the missed surveillance was deemed to be less than adequate surveillance scheduling process(s). Surveillance scheduling practices are being reviewed to determine enhancements to these practices.
4462000002 | Comanche Peak 2, Comanche Peak 1 | 01/07/2000 | 02/04/2000 | ML00368164 | <strong>Loss of Offsite Power to Transformer XST1 Caused Uint 2 Blackout Sequencer Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2000 at approximately 6:07 p.m., Comanche Peak Steam Electric Station (CPSES) experienced a loss of power to transformer XST1, which is the preferred offsite power sources to CPSES Unit 2 class 1E busses. CPSES Unit 2 temporarily lost power to Train A and Train B safeguard busses due to automatic transfer to the alternate offsite power source. This loss of power to XST1 caused a signal to be sent to the Train A and Train B Blackout Sequencer to realign the engineered safety feature equipment. The cause of the loss of the transformer XST1 (EIIS: (XMER)(EB)) was due to a directional ground relay that had its directional contact out of adjustment so that it was in the closed position. With the directional contact closed, CPSES breakers 7030 and 7040 opened prematurely due to a ground fault on an incoming feeder line, deenergizing XST1. The ground fault was cleared, and the Unit was aligned properly.
4462000003 | Comanche Peak 2, Comanche Peak 1 | 10/13/2000 | 11/10/2000 | ML00376944 | <strong>Core Alterations Had Continued While a Required Technical Specification Source Range Monitor was Inoperable</strong><br /><i>Abstract:&nbsp;</i>Following reactor shutdown as a part of the fifth refueling outage of Unit 2 (2RF05), on September 30, 2000 it was discovered that Source Range Neutron Flux Monitor 2-N-0031 (EIIS: (CHA)(JC)) read lower than source range neutron flux monitor 2-N-0032 (EIIS: (CHA)(JC)). Troubleshooting was performed and the affected monitor was deemed operable. On October 8, 2000 core alterations began. On Octoberl3, 2000, at approximately 2:41 p.m., an analysis of data extracted from the plant computer determined that Source Range Neutron Flux Monitor 2-N-0031 may not have provided valid neutron indication prior to commencing core alterations as required by the Comanche Peak Steam Electric Station's Technical Specification. The troubleshooting identified a degraded connector. The degraded components were replaced and the Source Range Neutron Flux Monitor 2-N-0031 was declared operable. The specific cause of the degraded connector was not identified.
4542000001 | Byron 1, Byron 2 | 02/02/2000 | 03/03/2000 | ML00369213 | <strong>Inservice Testing Not Performed on Several Values Due to Inadequate Program Scope Development</strong><br /><i>Abstract:&nbsp;</i>As part of an effort to enhance the quality of the Inservice Testing (IST) Program, Commonwealth Edison (ComEd) Company conducted a design basis review of components in the IST programs at the five ComEd sites, including Byron Station. The purpose of the review was to re-evaluate the ComEd IST Programs based on current guidance and determine and document components that should or should not be in the scope of the IST Program. This review began at Byron Station in May of 1999, with a final draft report being provided in December of 1999. The subsequent acceptance review of components proposed for inclusion in the IST Program was completed on February 2, 2000. This review indicated that several valves needed to be added to Byron Station IST Program and that acceptable surveillance tests on several of these additional valves could not be verified. Previous scoping efforts were ineffective in properly applying ASME code requirements to plant components. At the time of the previous scoping efforts there were insufficient controls in place to ensure the IST engineer had the proper knowledge to make all the scoping decisions. The safety significance of this issue is minimal. All missed testing requirements were performed with acceptable results. This event is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B), for an action or condition prohibited by Technical Specifications.
4542000002 | Byron 1, Byron 2 | 06/15/2000 | 09/29/2000 | ML00375688 | <strong>Acceptance Criteria for the Control Room Ventilation System Train Monthly Surveillance Not Met Due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2000, it was discovered that the June 15, 2000, performance of the Control Room Ventilation System (VC) Train OB Monthly Surveillance was inappropriately approved without meeting the required acceptance criteria of a continuous fan run time of 10 hours. A licensed operator performing the surveillance procedure made a subtraction error in beginning and ending clock times recorded in the procedure. The end time recorded was actually 50 minutes less than the minimum time required. The subsequent supervisor review of the procedure failed to identify the error. The VC fan was not shut down until well after the recorded end time; however, a search for other means to verify the exact stop time of the VC fan was unsuccessful. Consequently, the surveillance requirement could not be objectively verified. The root causes were determined to be a human performance error on the part of the licensed operator and a failure by operations management to establish clear expectations for supervisory review of completed surveillance procedures. Contributing causes include poor self-checking and incomplete turnover information. Corrective actions include counseling the individual and providing clear expectations for performing the supervisory review of surveillances. Other corrective actions include improvements in turnover information, and better utilization of the department surveillance coordinator. There were no adverse safety consequences with this event. This event is reportable to the NRC in accordance with 10 CFR 50.73 (a) (2)(i)(B) as a condition prohibited by Technical Specifications.
4542000003 | Byron 1 | 10/08/2000 | 03/28/2001 | ML01093006 | <strong>Unintentional Violation of Low Temperature Over Pressure Protection System Technical Specification Due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>Byron Station Technical Specification 3.4.12, "Low Temperature Over Pressure Protection (LTOP) System," contains requirements for both adequate pressure relieving devices and controls to prevent mass addition into the RCS. The mass addition controls include, in part, requiring the Safety Injection (SI) pumps to be incapable of injecting into the RCS. One method of ensuring this condition is to have two independent means to prevent a mass addition. On October 8, 2000, Byron Station Unit 1 was in Mode 5 and preparing to fill the SI Accumulators using the lA SI pump. The operating procedure used to perform this evolution contained an approved change to allow flexibility in LTOP compliance requirements. At 2125 hours, the licensed operator performing the procedure improperly restored an isolation valve being used for LTOP compliance to the open position. This action violated the two independent means of mass addition criterion. This situation was recognized approximately 4 hours later and immediately corrected. The causes of the event were the inappropriate application of human performance error reduction techniques used by the operator and that operators' fundamental practices relax during outage periods. Several other contributing causes were identified such as an inadequate pre-job briefing and weak operator knowledge of LTOP requirements. Corrective actions include removing the operator from shift duties pending remediation, operator training to improve fundamental practices and redefining key on-shift Operations Management roles and responsibilities during unit outages. There were no adverse safety consequences with this event. The control switch for 1A SI pump was always in the pull to lock position. All the relief devices required by the LTOP Technical Specification were operable and fully capable of mitigating an inadvertent mass addition from the 1A SI pump. This event is reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(i)(B).
4552000001 | Byron 2 | 01/13/2000 | 02/10/2000 | ML00368574 | <strong>Automatic Reactor Trip System Actuation Due to Off-Site Power LIne Fault and Failed Air Circuit Breaker Load Rejection Contact</strong><br /><i>Abstract:&nbsp;</i>At 0059 hours on January 13, 2000, Byron Station Unit 2 received an offsite transmission line 0622 trip alarm due to a phase B fault. A static line from another offsite line fell onto phase B of line 0622 causing the fault and direct transfer trip. As designed, the direct transfer trip opened oil circuit breakers (OCBs) 11-12 and 12-13 to isolate the line fault in the Byron Station switchyard. Unit 2 next received an unexpected main generator load rejection trip signal. The load rejection circuit provided a signal to actuate a main generator lockout relay, which opened air circuit breaker (ACB) 10-11 and tripped the Unit 2 turbine and reactor. The turbine and reactor trip occurred as designed and the unit was safely shut down. ACB 10-11 was closed at the time of the load rejection alarm which indicated one of the ACB 10-11 auxiliary contacts must have been closed at that time to complete the required load rejection trip logic. It was verified during subsequent troubleshooting that the ACB 10-11 phase A load rejection 'b' contact was found closed when the breaker was closed. The 'b' contact should have been open. The root cause of the switch failure is unknown. The immediate corrective action was to replace the defective contacts and verify proper operation. Also, a preventive maintenance activity will be developed to test these switches for both Byron Station Units. There were no actual safety consequences impacting plant or public safety. At 0155 hours on January 13, 2000, a NRC Emergency Notification System telephone call was initiated in accordance with 10 CFR 50.72.
4552000002 | Byron 2 | 07/26/2000 | 08/25/2000 | ML00374554 | <strong>Automatic Reactor Trip System Actuation From Low Steam Generator Level Caused by an Inappropriate Operator Response to a Failed Circuit Card in the Feedwater Flow Control Circuitry</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2000, at 1833 hours, Byron Station, Unit 2 experienced a reactor trip due to Steam Generator 2C low level. The low level was caused by a Protection and Control Instrumentation Rack NTD circuit card failure in the Main Feedwater (FW) Regulating Valve (FRV) circuitry and inappropriate licensed operators' response to the card failure causing the FRV to close. Following the reactor trip, the circuit card was replaced and the unit returned to power operations. A Company wide task force has been formed to evaluate control circuit card issues in an effort to reduce failures. The inappropriate operator actions include not using alternate indications to validate their diagnosis, switching the FW control from automatic to manual, switching back to manual after returning to automatic control, and the delay in identifying the need to initiate a manual reactor trip which resulted in the automatic reactor trip. Procedural and training improvements will be made to help the operator better diagnose and respond to control circuit failures. Operations Management will reinforce the expectation to validate information and to manually trip the reactor prior to exceeding an automatic trip setpoint. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv).
4562000001 | Braidwood 1, Braidwood 2 | 02/08/2000 | 03/30/2000 | ML00369985 | <strong>Manual Actuation of the Main Control Room Ventilation System (VC) Due to Conservative Decision Making Based on Environmental Conditions</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2000, the Main Control Room (MCR) received "alert alarms" on two radiation monitors for the MCR Ventilation System outside air intake. The Unit 1 Unit Supervisor (US) directed the Unit 1 Nuclear Station Operator to place the MCR Ventilation System in the makeup mode with the charcoal absorbers in service per the appropriate Station procedure. The US believed a temperature inversion was occurring and made the decision to realign the ventilation system based on the meteorological tower indications and trends on the radiation monitors. During a temperature inversion, the concentration of naturally occurring radon will increase causing an increase in radiation levels and a resultant increase on radiation monitors. The US believed it was a conservative decision. Neither MCR radiation monitor reached the "high alarm" setpoint, which would have caused the ventilation system to automatically swap to the makeup mode. The US did not believe the actions taken constituted a valid actuation of an Engineered Safety Feature System. It was subsequently determined that the original evaluation was incorrect. The root cause of the event was the conservative decision made by the US and his misunderstanding of the potential reportability.
4562000002 | Braidwood 1 | 03/15/2000 | 04/13/2000 | ML00371302 | <strong>Main Steam Safety Valves (MSSVs) tested in exccess of required setpoint due to bonding between the disc and nozzle seat</strong><br /><i>Abstract:&nbsp;</i>During setpoint verification testing of Unit One Main Steam Safety Valves (MSSVs), 8 valves lifted in excess of their setpoints by greater than the 30 Technical Specification (TS) tolerance. For each case where the MSSV lifted greater than the 3% tolerance, the appropriate TS Condition was entered. The valves were tested sequentially, so only one valve was known to be inoperable at any time. The valves were adjusted as necessary and retested to place them in the required tolerance range prior to exiting the TS Condition. The root cause for 7 of the 8 MSSV test failures was bonding between the disc and nozzle seats. The cause of the failure of the other MSSV was setpoint drift. Corrective actions included replacement of the discs and refurbishing the nozzle seating surfaces in the 7 MSSVs exhibiting bonding. An evaluation of the safety consequences concluded that the acceptance criteria for the applicable Updated Final Safety Analysis Report (UFSAR) accident scenarios were not exceeded. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4562000003 | Braidwood 1 | 04/17/2000 | 05/17/2000 | ML00371712 | <strong>Missed Technical Specification Surveillance on the 1B Diesel Generator due to Personnel Error due to Poor Supervisory Control</strong><br /><i>Abstract:&nbsp;</i>At 0718 on April 17, 2000, Condition B for Technical Specification (TS) 3.8.1, "AC Sources-Operating" was entered for the 1B Diesel Generator (DG) being inoperable due to the 1B DG Vent Fan being Out of Service. Per Required Action B.1 of this TS, Surveillance Requirement (SR) 3.8.1.1 was to be performed within one hour (by 0818) to verify the required qualified circuits were available. At 1154 on April 17, 2000, the Unit 1 Unit Supervisor (US) identified the failure to perform SR 3.8.1.1 within the required timeframe. The SR was started and Condition F of TS 3.8.1 was entered at 1155 due to the failure to meet the Completion Time requirements of Required Action B.1. The SR was completed and Condition F was exited at 1204. The safety consequences associated with this event were minimal. The SR verifies the required qualified sources of offsite AC power are available. During this timeframe, activities were being performed in the switchyard but none of these activities would have affected the availability of these power sources. The cause of the event was poor supervisory control by the Unit 1 US. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4572000001 | Braidwood 2 | 03/30/2000 | 05/01/2000 | ML00371191 | <strong>2A Essential Service Water Pump Inoperable for more than the Technical Specification Allowed Outage Time Resulting from Inadequate Testing Criteria due to a Design Deficiency and Inadequate Methodology for the Return to Service</strong><br /><i>Abstract:&nbsp;</i>At 1900 on March 26, 2000, the 2A Essential Service Water (SX) Pump was taken Out of Service for planned maintenance. The appropriate Required Actions of the Technical Specifications (TS) were entered. Upon completion of the maintenance, Operations personnel performed post maintenance testing of the system. At 1241 on March 29, the pump was declared operable. At 1206 on March 30, 2000, the 2A SX Pump was started and showed indications of inadequate flow when the 2B SX Pump was secured. The 2A SX Pump was declared inoperable and the Required Actions of the TS were again entered. Significant quantities of entrained air were found in the 2A SX Pump piping. Additional venting activities were conducted and the 2A SX Pump was declared Operable at 1045 on April 1, 2000. As a result of inadequate design of the SX suction headers and knowledge deficiencies of the system configuration, the 2A SX Pump was prematurely declared Operable. The safety significance of the event was minimal. The plant would have been fully capable of coping with the design basis accident on Unit 2, even with the additional single failure of the 2B SX Pump. The required cooling functions of the SX System could have been maintained, and the impact of the additional period of unavailability of 2A SX Pump was not risk significant. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4572000002 | Braidwood 2 | 04/15/2000 | 05/12/2000 | ML00371712 | <strong>Automatic Reactor Trip on Power Range Neutron Flux High Negative Rate Due to Stationary Gripper Fuse FU15 Failure for Control Rod P10 Causing the Rod to Drop into the Core</strong><br /><i>Abstract:&nbsp;</i>On 4/15/2000 at 1714 hours, Unit 2 was operating at 99.9 percent power when it experienced a trip on Power Range Neutron Flux High Negative Rate. Following the trip, a low Steam Generator (SG) level Engineered Safety Features (ESF) actuation signal started Auxiliary Feedwater and a high SG level ESF actuation P-14 signal was processed. The rapid power decrease was traced to the failed Stationary Gripper fuse and blown fuse indicator (telltale) for Control Rod P10 causing the rod drop. Troubleshooting verified that circuits were not shorted and had not caused an overcurrent condition. The blown fuse and telltale were removed for analysis and replacements installed. Unit start-up commenced on 4/16/2000 at 0414 hours, but was aborted due to Digital Rod Position Indication problems. The cause of the trip was the opening of fuse FU15 and telltale which led to the rod drop and subsequent high neutron flux negative rate. The fuse was blown due to an indeterminate overcurrent condition believed to be an isolated failure. Analysis revealed that the fuse had apparently failed prior to the trip and that the telltale had been carrying the load current. Thermography scans will be performed as predictive maintenance to look for "hot" telltales indicative of such fuse failures and the circuits will be reviewed to verify the adequacy of design. Because the negative rate trip may not be necessary, possible elimination of this trip will be reviewed. This event is being reported pursuant to 10 CFR 50.73 (a) (2)(iv).
4572000003 | Braidwood 2 | 04/16/2000 | 06/15/2000 | ML00372517 | <strong>Manually Opened Trip Breakers Due to Detector / Encoder Card Failure In Digital Rod Position Indication System</strong><br /><i>Abstract:&nbsp;</i>While withdrawing Shutdown Bank B rods during a Braidwood Unit 2 restart on 4/16/2000, the operator noted Digital Rod Position Indication (DRPI) for rod G13 jump from 18 to 210 steps. With the plant in Mode 3 and with the reactor trip breakers closed, the operator declared DRPI for rod G13 inoperable and immediately opened the reactor trip breakers. Investigation of the problem determined that either the Data A or Data B Detector/Encoder Card for rod G13 was the source of the problem. Instrument Maintenance Department (IMD) personnel replaced both cards and a partial DRPI operability surveillance was run to verify rod G13 was operable. Corrective actions included replacing the Data A Detector/Encoder Card a second time for rod G13, and re-performance of the operability surveillance prior to Unit start-up. Other Corrective actions to be taken include: review of TRM requirements for possible changes in the requirements for opening the reactor trip breakers, scheduling of periodic DRPI Dynamic Card Testing and conduct of an Effectiveness Review.
4582000001 | River Bend | 01/22/2000 | 02/22/2000 | ML01022039 | <strong>Automatic Isolation of the Reactor Core Isolation Cooling System During Surveillance Testing Due to Procedure Implementation Error</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2000, with the plant in Mode 1 (Power Operation) at 31 percent power, an automatic isolation of the reactor core isolation cooling (RCIC) system occurred during surveillance testing. The purpose of the regularly scheduled surveillance test was to perform a channel functional test of the automatic isolation of the Division I steam supply isolation valve in the RCIC system as would occur with a low pressure condition in the steam supply line. The test technician misread a procedure step, which caused him to omit instructions to lift a circuit lead in order to block the isolation signal to the motor operated steam supply valve. When subsequent steps were performed, an isolation signal generated by the trip unit being tested was sent to the valve, which responded as designed. The isolation signal was reset, and the RCIC system was restored to its normal standby status approximately twenty-six minutes after the event. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of an engineered safety feature. The RCIC steam supply valve is a primary containment isolation valve. The RCIC steam supply valve responded as designed to the isolation signal. The high pressure core spray system was operable at the time. This event had minimal effects on the health and safety of the public.
4582000002 | River Bend | 03/16/1999 | 02/23/2000 | ML00368918 | <strong>Inoperability of High Pressure Core Spray Diesel Generator due to Closure of Division I Service Water Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1999, with the plant in Mode 1 at approximately 80 % power, the isolation valve (SWPMOV77A)(*ISV*) for the Division I service water supply to the Division III, High Pressure Core Spray (HPCS), these generator (DG) was closed. SWP-MOV77A was closed in excess of the maximum allowed outage time in the River Bend Station (RBS) technical specifications (TS) for this condition. Exceeding the allowed outage time constitutes operation prohibited by TS and is reportable according to 10 CFR 50.73(a)(2)(i)(B). Site personnel understood that closing SWP-MOV77A did not impact the operability of the Division III DG. This misconception supported the contingency action of closing SWP-MOV77A instead of declaring the system inoperable and entering the applicable LCO. An Operations Department Standing Order was issued that requires entry into technical specification LCOs if the service water supply or return valve for the Division III DG for either division is closed. The significance of this condition was a reduction of systems available to mitigate accidents analyzed in the River Bend USAR.
4582000003 | River Bend | 03/04/2000 | 04/03/2000 | ML00370128 | <strong>Inoperable Division 3 Battery Caused by an Incorrectly Assembled Terminal Following Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At approximately 3:00 a.m. on March 4, 2000, with the plant shutdown in a refueling outage, a connection having a high resistance reading was discovered on the Division 3 125-volt DC battery during surveillance testing. Troubleshooting found that a washer was installed between the battery terminal plate and a battery cable lug. Other connections on the battery had the washer correctly installed on the opposite side of the cable lug, between the lug and the hex nut. The connection was reassembled in the same configuration as the other terminals. The resistance of the connection was measured and found to be acceptable in accordance with the surveillance test. The incorrect configuration of the connection and the resultant high resistance caused the battery to not meet the surveillance requirements of River Bend Technical Specifications. A review of plant records concluded that this condition had existed since April 1999. This exceeds the allowable outage time of the applicable Technical Specifications. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications. An engineering review determined that the battery was capable of performing its safety function during the period that the incorrect connection configuration existed. Therefore, this event was not significant with respect to the health and safety of the public.
4582000004 | River Bend | 12/27/1999 | 04/13/2000 | ML00370418 | <strong>Automatic Standby Gas Treatment System Actuation Due to Annulus Exhaust Radiation Monitor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1999, an unplanned automatic actuation of the standby gas treatment and annulus mixing systems occurred. The initiating signal originated in radiation monitor RMS-RE11B, which monitors the reactor building annulus for gaseous activity. The redundant RMS-RE11A radiation monitor and grab samples of the annulus atmosphere indicated normal radioactive levels. The filter cartridge in the RMS-RE11B radiation monitor was changed and its indication returned to normal. The standby gas treatment and annulus mixing systems were returned to their normal standby configuration. This LER is required in accordance with 10CFR50.73(a)(2)(iv) due to automatic actuation of an ESF system. An investigation of the event determined that the filter cartridge in the RMS-RE11B radiation monitor was incorrectly installed, such that sample flow could bypass the filter. It is postulated that particulate matter bypassed the filter element and was detected by the radiation monitor. This event was not significant with respect to the health and safety of the public.
4582000005 | River Bend | 03/21/2000 | 05/24/2000 | ML00371945 | <strong>Incorrectly Connected Motor Leads for the 'B' Primary Containment Unit Cooler Service Water Supply Valve</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2000, with the plant in Mode 5 (Refueling), the motor operator breaker for the 'B' containment unit cooler service water supply valve was discovered to be incorrectly wired. This wiring error caused the valve's motor operator to move the valve in the closed direction upon receipt of an open signal. It was subsequently determined that this valve had been inoperable since the performance of its associated breaker overload functional test on February 9, 2000, when the plant was in Mode 1 (Power Operation). Since the plant was shutdown on March 4, 2000, a time limit specified by Technical Specification 3.6.1.7 was exceeded. The 'A' primary containment unit cooler was continuously operable during this timeframe. This condition is being reported in accordance with 10CFR50.73(a)(2)(i) as operation prohibited by the plant's Technical Specifications. The root cause of this event is personnel error. The 'B' containment unit cooler service water supply valve was returned to an operable condition prior to plant startup. The failure of this valve had minimal safety or risk significance.
4582000006 | River Bend | 04/08/2000 | 05/08/2000 | ML00371467 | <strong>Noncompliance With Technical Specifications During Control Rod Scram Time Testing Due to Procedure Implementation Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2000, with the plant at approximately 10% power, a reactor control rod was withdrawn without meeting the applicable requirements of River Bend Technical Specifications (TS) and station procedures. Specifically, the TS requires a control rod drop accident (CRDA) analysis for such testing when it is performed below 20% rated reactor power. The control rod was undergoing a scheduled scram time surveillance test following a plant startup from a refueling outage. The control rod was out of its approved position for approximately six minutes before being fully reinserted into the core. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications. The cause of this event was inadequate procedure implementation by the personnel performing the test. Procedure requirements were not correctly followed in that a specific CRDA analysis for this test was not performed or obtained prior to test performance. Subsequent analysis found that a postulated rod drop accident for the control rod being tested was bounded by a previous vendor analysis which demonstrated that assumptions in the River Bend Updated Safety Analysis Report would have been met. This event had minimal potential to affect the health and safety of the public.
4582000008 | River Bend | 05/11/2000 | 06/12/2000 | ML00372488 | <strong>Unplanned Automatic Isolation of Reactor Water Cleanup System During System Configuration Change Due to Mispositioned Manual Valves</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2000, at approximately 8:18 a.m., an unplanned automatic actuation of the primary containment isolation valves in the reactor water cleanup system occurred. The system configuration was being shifted at the time, as operators were attempting to place one of the system's demineralizers In service. When the demineralizer inlet and outlet valves were opened, a high differential system flow alarm actuated. Following a built-in time delay, the differential flow condition actuated the isolation control circuitry and caused the containment isolation valves to close. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a condition which caused the automatic actuation of an engineered safety feature. The cause of the high differential flow condition was mispositioned manual strainer backwash valves, which allowed part of the system flow to be diverted to the demineralizer backwash receiving tank. Due to degradation of the valve travel stops, the operator was led to believe the valves were closed when they were actually partially open. The operator relied on the travel stops to determine valve position. Other than the primary containment isolation valves, the RWCU system does not perform an active safety function. Its removal from service had no immediate adverse effect on plant operation, and it was restored to service later the same day. The diverted system flow was contained within the demineralizer backwash receiving tank. This event had minimal potential to affect the health and safety of the public.
4582000009 | River Bend | 05/19/2000 | 06/19/2000 | ML00372680 | <strong>Noncompliance with Technical Specifications for Drywell Purge Valve Configuration During Power Operations Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2000, at approximately 0357 hours, plant operators discovered that four air-operated valves (AOV's) in the drywell ventilation system were not sealed shut as required by Technical Specification Surveillance Requirement 3.6.5.3.1. The AOV's are part of the drywell pressure boundary, and are required to be sealed shut by Technical Specifications (TS) and plant procedures when the plant is not in cold shutdown. The valves were closed, but were not sealed as defined by the TS bases. The plant was started up on April 8, 2000, without meeting this requirement, and a subsequent surveillance test intended to verify the valves are isolated did not discover the noncompliance. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications. The cause of this event was inadequate communications between a shift superintendent and the control room supervisor implementing the plant startup procedure. Although the requirements of the Technical Specification were not satisfied, the administrative controls established by tagging the valve control switches and locking the actuator handwheels provided sufficient barriers to prevent inadvertent operator actuation of the valves. Additionally, the operating procedure for the drywell purge system contains a precaution that prohibits opening of the drywell purge valves when the plant is not in cold shutdown. Therefore, this event had minimal potential to affect the health and safety of the public.
4582000010 | River Bend | 07/05/2000 | 08/04/2000 | ML00373848 | <strong>Unplanned Automatic Isolation of the Reactor Core Isolation Cooling System During Surveillance Testing Due to Hydraulic Perturbation in Instrument Lines</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2000, at 0920 hours with the plant in Mode 1 (Power Operation) at 100 percent power, an unplanned automatic isolation of the Division II steam supply valve to the reactor core isolation cooling (RCIC) system occurred during scheduled surveillance testing. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of an engineered safety feature. The Division II isolation signal was caused by a hydraulic perturbation in the common sensing lines while the Division I transmitter was being removed from service. Evaluation of recorded data indicates that a small pressure drop occurred in the common low pressure side sensing line when the equalizing valve was opened. This caused a momentary increase in differential pressure. The technicians performed the instrument valve manipulations in accordance with their training and procedural requirements. The Division II RCIC steam supply containment isolation valve responded as designed. The high pressure core spray (HPCS) system was operable at the time, and remained so for the period that the RCIC system was out of service. The RCIC system was restored to its normal standby alignment approximately four hours after the event. This event had minimal potential to affect the health and safety of the public.
4582000011 | River Bend | 08/11/2000 | 09/11/2000 | ML00375147 | <strong>Secondary Containment Inoperable Due to Failure of Auxiliary Building Door Opening Device</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2000, at 2250 hours with the plant in Mode 1 (Power Operation) at 100 percent power, a secondary containment door leading into the auxiliary building became blocked open such that it caused secondary containment to be inoperable for a short period of time. This event is being reported in accordance with 10CFR50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of a safety function needed to control the release of radioactive material. Three secondary containment doors used for routine personnel access into the auxiliary building are equipped with assist devices that ease the opening of the door against the differential pressure created by operation of the standby gas treatment system (GTS). The door involved in this event was opened for routine access while the GTS system was running for a surveillance test. The door assist device malfunctioned, causing the door to be blocked open approximately eight inches. The door remained in this condition for approximately eighteen minutes before the assist device was reset to allow the door to be closed. During the period the door was blocked open, the plant continued to operate normally. There was no actual safety significance to the health and safety of the public. If a design-basis accident had occurred while the door was blocked open, evaluations have shown that the exclusion area boundary thyroid dose would have remained within the limits defined by 10CFR100.
4582000012 | River Bend | 08/21/2000 | 09/20/2000 | ML00375428 | <strong>Manual Reactor Scram Initiated in Response to Decreasing Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2000, at 1531 hours, with the plant operating at 81 percent power, the operating crew initiated a manual reactor scram in response to a decrease in main condenser vacuum. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a condition that resulted in the actuation of an engineered safety feature. Before the event, the plant was operating at 100 percent power. Troubleshooting activities were in progress on the main condenser offgas system in an effort to clear a low flow alarm. Instructions in the alarm response procedure directed the initiation of an air purge of the system. When the air purge was started, the air flow rate was apparently too high, causing excessive backpressure at the discharge of the main condenser air ejector. Condenser vacuum began to decrease, and operators began reducing power in accordance with procedure. Condenser vacuum could not be recovered prior to reaching the point at which a manual reactor scram is directed by operating procedures. Following the scram, the transient in reactor water level actuated the Level 3 setpoints, causing the actuation of an engineered safety feature in the suppression pool cooling (SPC) system. The SPC system was operating in the suppression pool cooling mode at the time. The containment isolation valves in the SPC system closed as designed. All plant responses to the scram were as expected. This event was of minimal potential consequence to the health and safety of the public.
4582000013 | River Bend | 09/14/2000 | 10/13/2000 | ML00376045 | <strong>Standby Liquid Control System Inoperable Due to Foreign Material in the Storage Tank</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2000, at 0936 with the plant in Mode 1 (Power Operation) at 100 percent power, a chemistry technician sampling the Standby Liquid Control (SLC) system (**BR**) storage tank (**TK**) found plastic material on the sampling apparatus when the apparatus was removed from the tank. A thorough inspection of the SLC storage tank internals was performed using an underwater camera. No material was found in the pump suction line. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(A) as a condition that alone could have prevented the fulfillment of a safety function needed to shutdown the reactor and maintain it in a safe shutdown condition. While obtaining the monthly sample of the Standby Liquid Control (SLC) solution, part of a plastic bag approximately 10 inches square was retrieved with the chemistry sampling apparatus. Subsequent inspection of the SLC storage tank revealed approximately 20 pieces of plastic floating on the surface that ranged in size from two square feet to 1/2 inch square and appeared to be part of a trash bag. Three pieces were attached to components in the lower portion of the tank. Due to the foreign material attached to the tank components, both SLC subsystems were declared inoperable on 9/14/00 at 1422 in accordance with Technical Specification 3.1.7. Since inoperability of both SLC pumps results in a loss of safety function, this event was reported to the NRC on 9/14/00 at 1652. Based on the removal of the foreign material, the subsequent SLC tank inspections, and an engineering evaluation of potential trace amounts of plastic remaining in the tank; both SLC subsystems were declared operable on 9/14/00 at 2059. A risk assessment that assumed the inoperability of SLC system for a period of one year determined that the condition was non-risk significant. Based on this information, the safety significance of this event is minimal.
4582000015 | River Bend | 10/12/2000 | 11/13/2000 | ML00376986 | <strong>Inadequate Surveillance Test Procedure Results in Failure to Fully Perform Required Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2000, at 1535 with the plant in Mode I (Power Operation) at 100 percent power, a system engineer determined through post-maintenance review of documentation for both emergency diesel generators (EDG) (**DG**) that all diesel start functions were not verified for Logic System Functional Test (LSFT) surveillance purposes during RF-8. On April 1, 2000, while performing surveillance testing during RF-09, a system engineer questioned the response of the starting air system (**LC**). An investigation determined that one set of Loss of Coolant Accident (LOCA) contacts did not function as required. This was corrected and the surveillance was successfully completed, and is not reportable. During the same testing, the Loss of Power (LOP) portion of the test was also observed and both tanks successfully reduced in pressure as expected. Therefore, the LOP contacts performed as required and the surveillance requirements were met in RF-09. In a subsequent review of the LOP/LOCA test data, it was realized that for the LOP portion of the test, the LOP contacts were not directly monitored and a failure of a contact to close would not have been detected without the previously described monitoring of the air banks (*"ACC*"). Further review revealed that there was no data to substantiate that the LOP contacts performed correctly in RF-08. The absence of this provision in the procedure resulted in a failure to adequately perform the required surveillance. However, the technical specification surveillance requirements for LOP functions were satisfactorily performed on March 24, 2000 for Division II and on April 5, 2000 for Division I. The LOP related circuits operated satisfactorily and would have performed their safety function. The safety significance of the reported procedure inadequacy is minimal.
4582000016 | River Bend | 12/17/2000 | 01/22/2001 | ML01031018 | <strong>Automatic Actuation of Primary Containment Isolation Valve in Suppression Pool Cooling System Due to Test Switch Failure</strong><br /><i>Abstract:&nbsp;</i>At approximately 0823 hours on December 17, 2000, with the plant at 100 percent rated power, an unplanned automatic closure of a primary containment isolation valve in the suppression pool cooling system occurred during surveillance testing. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of an engineered safety feature. This event occurred during scheduled surveillance testing of the residual heat removal pump room high temperature isolation function. Test switches are used during the procedure to bypass the isolation function, allowing initiation of a high temperature trip signal without actually causing closure of the isolation valves. In this case, a failure of a test switch caused the isolation circuitry to remain active such that the trip signal initiated during the procedure was not bypassed. The isolation valve closed as designed in response to the simulated high temperature trip signal. The SPC system does not perform a safety related function. The isolation valve is designed to protect the integrity of primary containment during a postulated line break, and it functioned as designed. The failure mode of the switch was such that it could not cause an isolation signal to the isolation valve to be bypassed. The safety function of the isolation circuitry and valve was thus unaffected by the switch failure. This event was of no significance with respect to the health and safety of the public.
4612000001 | Clinton 1 | 05/17/2000 | 06/14/2000 | ML00372562 | <strong>Operation of Mislabeled Switch While Performing Preventive Maintenance on a Circuit Breaker Results in Loss of 4160 Volt 1B Bus, Reactor Water Level Transient and Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2000, the plant was in Mode 1, at approximately 100 percent power. Functional testing of over current relays for the reserve feeder breaker to the 4160 Volt (V) 1B Bus (non-safety) was in progress. While inputting a simulated over current condition to test the over current relays on the reserve feeder breaker, the main feeder breaker to the 4160 V 1B Bus tripped unexpectedly resulting in a loss of power to the 4160 V 1B Bus. The resulting loss of power caused a loss of feedwater flow and reactor vessel level transient. In response to the level transient, a manual reactor scram was initiated and the reactor shut down. The cause of this event was incorrect labeling of a test switch on the 4160 V 1B Bus. The corrective actions for this event include performing walkdowns of other electrical busses to identify labeling problems, briefing maintenance personnel on this event, and incorporating a Labeling Validation Form in Electrical Maintenance work packages.
4612000002 | Clinton 1 | 02/28/2000 | 03/01/2001 | ML01071000 | <strong>Out-of-Phase Synchronization Results in Damage to Division 3 Emergency Diesel Generator and Inadequate Design of Static VAR Compensator Freeze Circuit Results in Overvoltage of Class 1E Divisional Bus</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2000, while paralleling the Division 3 Emergency Diesel Generator (EDG) to an offsite source, an out-of-phase synchronization occurred that damaged the Division 3 EDG stator windings. A Static VAR Compensator (SVC) responded to the out of phase synchronization in a way not intended by design, resulting in an overvoltage condition on the Division 3, Class 1E, electrical distribution system. Subsequent evaluation of the overvoltage condition determined the overvoltage condition did not adversely affect components supplied by the Division 3 electrical distribution system. The out-of-phase synchronization was caused by a combination of synchronization technique weaknesses. The cause for the SVC not responding as intended by design was determine to be a failure to account for an inherent time delay in the SVC freeze circuitry during the design process of the SVC freeze function. Corrective actions for this event include ;repair of the Division 3 EDG, improving guidance for paralleling EDGs, installing syncronizing check relays, revising the EDG reverse power relay settings, performing routine preventive maintenance on synchroscopes, and providing training on this event.
4612000003 | Clinton 1 | 08/31/2000 | 10/02/2000 | ML00375921 | <strong>Failure to Follow Procedure While Performing Fire Detector Testing Results in Inoperable Division III DG Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2000, Clinton Power Station (CPS) was in Mode 1, at approximately 100 percent power. At approximately 1420 hours, during restoration from testing fire detectors in the Division III Diesel Generator (DG) room, DG ventilation fans tripped unexpectedly. At approximately 1747 hours, during investigation into this condition, it was determined that the DG ventilation fan trips were due to a problem with a relay in the Division III DG fire protection supervisory circuit that was activated during the testing of the fire detectors in the Division III DG room. It was also determined that this relay problem adversely affected the operability of the Division III DG room ventilation. In response to this determination, operations declared the Division III DG inoperable and entered the Technical Specification (TS) Limiting Condition for Operation (LCO) action statements for the Division III DG being inoperable. The cause for this event was inadequate job preparation which led to a failure to follow procedure requirements. The corrective actions for this event included implementation of an improved pre-job briefing form, counseling the technicians involved, and performing a two-day stand down in the Maintenance Department to reinforce expectations concerning procedure adherence.
4612000004 | Clinton 1 | 09/15/2000 | 10/14/2000 | ML00376154 | <strong>Inability to Restore from Technical Specification Limiting Condition for Operation Due to Inadequate Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 15, 2000, Clinton Power Station (CPS) requested, and the NRC granted, enforcement discretion to allow restoring the Emergency Reserve Auxiliary Transformer (ERAT) Static Var Compensator (SVC) to service without meeting the Limiting Condition for Operation for the associated SVC protection system. The ERAT SVC is provided with two redundant protection subsystems ("A" and "B"). The enforcement discretion allowed restoring the ERAT SVC to service with the ERAT SVC "A" protection subsystem inoperable. (The Technical Specifications (TS) require both protection subsystems to be operable prior to returning the ERAT SVC to service.) This enforcement discretion was requested to avoid an undesirable plant transient (i.e., shutdown). The cause for the inability to restore the ERAT SVC "A" protective subsystem to an operable status was lack of system knowledge. Corrective actions associated with this event include providing training for key personnel on SVC operation and maintenance and correcting procedure deficiencies associated with performance of SVC protection system testing.
4612000005 | Clinton 1 | 10/22/2000 | 11/20/2000 | ML00377198 | <strong>Losses of Secondary Containment Integrity During Movement of Irradiated Fuel Due to Unauthorized Opening of Boundary Doors and Failure to Adequately Verify Local Leak Rate Test Boundary Valve Position</strong><br /><i>Abstract:&nbsp;</i>Four times during the recent refueling outage Secondary Containment was breached during movement of irradiated fuel. On two occasions contract employees opened both doors of Secondary Containment boundary airlocks for a few minutes to transport scaffolding through the doors. The causes of the events were incorrect assumption of permission to open both doors based on assignment of work, and inadequate corrective action to prevent recurrence. Corrective action includes briefing work crews, coaching the involved individuals, informing site personnel about the event, and evaluating a more effective means to control a Secondary Containment airlock. On two occasions operators failed to ensure a boundary isolation valve for local leak rate testing was closed. The air-operated valve involved in both events had its air supply isolated and control power fuse removed. Operators were unaware of the fuse removal due to an error in the valve identification in the clearance that removed the fuse. This resulted in the valve being open when operators believed they had repositioned the valve to the closed position. The valve identification error was the cause of the event. Corrective actions include providing lessons learned to Operations personnel, and verifying valve position in the field when indicating lights are not lit.
4612000006 | Clinton 1 | 10/16/2000 | 11/15/2000 | ML00377052 | <strong>Lack of System Response Characteristics Knowledge Results in Failure to Identify Consequences of Re-Energizing Power Supplies and Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>While re-energizing two power supplies following replacement in the Alternate Rod Insertion (ARI-1) System, the ARI-1 system automatically initiated. Annunciators alarmed in the Main Control Room and operators observed the Scram Discharge Volume (SDV) vent and drain valves closing. With SDV water level increasing, operators initiated a manual scram to prevent an automatic scram on high SDV water level. An investigation identified that the technician performing the work considered that an ARI-1 logic initiation was not possible upon reenergizing the power supplies since normally the circuit must be energized for a trip to occur. Therefore, no precautions were taken for the restoration activity. The most likely cause of the ARI-1 initiation signal was the logic sensed a low reactor water level and initiated the trip. The cause of this event was a failure of Maintenance Planning, I&C technicians, and Operations personnel to identify the consequences of energizing the power supplies due to a lack of knowledge of system response characteristics. Corrective action for this event includes revising the work documents, providing lessons learned briefing/training, performing a training task analysis, and revising a procedure.
4612000007 | Clinton 1 | 12/18/2000 | 06/26/2002 | ML02191001 | <strong>Unknown Division 1 Logic Circuit Card Failure Goes Undetected During Division 2 Surveillance Test Due to Inadequate Procedure and Completes Actuation Logic Resulting in Main Steam Line Containment Isolation and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>A Containment Main Steam Line isolation (Group 1) and subsequent reactor scram from 100 percent reactor power occurred during a Division (Div) 2 Main Steam Line tunnel ambient temperature channel functional test. The logic for the isolation was completed when a Div 2 channel functional test signal combined with a pre-existing Div 1 trip signal. The Div 1 trip signal was a result of a circuit card failure and was unknown at the time of the test. The isolation initiated a Reactor Scram. During recovery from the event, an additional scram occurred on low reactor water level. While reestablishing the main condenser as a heat sink, a deficient procedure lacked provisions for opening both the inboard and outboard main steam isolation valves and an at risk revision of the procedure was initiated. During the revision process, poor command and control allowed reactor pressure to increase and water level to decrease to the scram setpoint. The cause of the Group 1 and scram was inadequate indication/annunciation for the technician to detect a pre-existing fault in an alternate channel. The cause of the additional scram was poor command and control. Corrective action for this event includes changing circuit design, revising procedures, counseling the main control room crew, providing remedial training, and developing a comprehensive corrective action plan to address the operator performance issues.
4612000008 | Clinton 1 | 10/26/2000 | 11/20/2000 | ML00377198 | <strong>Failure to Meet Technical Specification Requirements for Reactor Cavity Upper Containment Pool Water Level During Refueling Operations</strong><br /><i>Abstract:&nbsp;</i>In early 1997, a generic concern was identified that certain acceptance criteria in Technical Specification (TS) surveillance procedures may not be adequate to assure compliance due to uncertainties in measuring plant process parameters. To address this issue, a review of plant parameters associated with TS Surveillance Requirements was performed. During the review, station engineers identified a potential discrepancy in the reactor cavity upper containment pool level during refueling operations. Further review of this potential discrepancy found that CPS had failed to meet the TS required minimum upper containment pool water level of 23 feet above the reactor pressure vessel (RPV) flange during previous refueling outages. The cause for this condition was a failure to account for as-built construction inaccuracies during the original TS development. The corrective actions for this event include performing an analysis to support refueling operations with an upper containment pool water level less than 23 feet above the RPV flange; revising the TS to change the required upper containment pool water level to 22 feet, 8 inches above the RPV flange; and revising operating procedures to reflect the TS change.
4822000001 | Wolf Creek | 02/10/2000 | 03/13/2000 | ML00369603 | <strong>Surveillance Method Results in Low NaOH Level in the Spray Additive Tank</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2000, while reviewing an NRC inspector's concern associated with a calibration calculation, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel determined that the method used to measure Sodium Hydroxide (NaOH) level in the spray additive tank could result in the level in the tank being lower than that allowed by Technical Specifications. On February 10, 2000, WCNOC personnel checked the tank level and determined that the level was approximately 100 gallons lower than required by Technical Specification Surveillance 3.6.7.2. The condition had existed for longer than the allowed out of service time, and thus is reportable in accordance with 10 CFR 50.73 (a) (2)(i)(B) and NUREG-1022, Revision 1. WCNOC personnel subsequently determined that a 1985 engineering recommendation providing guidance for proper instrumentation to be used to determine level indication was not incorporated into operating procedures. The root cause of not incorporating the guidance is indeterminate due to the historical nature. The surveillance procedure has been corrected to ensure the proper instrumentation (sight glass) is used to determine tank level, and other engineering documents providing recommendations during the time period in question were reviewed to ensure that no similar conditions existed. Although the level was low, the tank volume was sufficient to ensure design bases functions were met. Therefore, the event was not considered a safety system functional failure and the safety significance is minimal.
4822000002 | Wolf Creek | 05/24/2000 | 08/11/2000 | ML00374262 | <strong>Loss of Containment Total Unidentified Leak Rate Computer Point Operability</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2000, Wolf Creek Generating Station (WCGS) operators identified that the Nuclear Plant Information System (NPIS) computer point LFU0769, "Containment Total Unidentified Leak Rate," had been inoperable since April 2, 2000, at 0300 Daylight Savings Time (DST), following the change to DST. This condition violated the Limiting Condition of Operation (LCO) requirements and actions of WCGS post Amendment 123 Technical Specification (TS) 3.4.15. Investigation determined that the condition had also occurred historically, violating pre-amendment 123 TS 3.4.6. Review also identified an April 17, 1995, entry into the conditions of LCO 3.0.3 that was not previously recognized, identified, and reported. These events are reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) and NUREG-1022, Revision 1, "Event Reporting Guidelines 10 CFR 50.72 and 10 CFR 50.73." An error in vendor supplied software caused leak rate calculations to be suspended whenever a DST change occurred, and both vendor and WCGS Acceptance Tests did not verify that leak rate calculations were unaffected by DST-related time changes. Inadequate use of the Qualification, Validation, and Verification (QV&V) process by the WCGS NPIS Project Team members is a root cause of this failure. Corrective actions include evaluation of NPIS software, investigation of the classification and grading of software, and a review of the potential concurrent inoperability of systems. There was minimal impact on safety from this condition, as safety function was not lost.
4822000003 | Wolf Creek | 09/04/2000 | 10/04/2000 | ML00375926 | <strong>Unit Trip Due to a Failure of the Unit Auxiliary Transformer and Accompanying Fire Caused by a Squirrel; Engineered Safety Function Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2000, at 1132, Wolf Creek Generating Station (WCGS) experienced afire on the Unit Auxiliary Transformer. This resulted in a momentary degraded condition for the station service loads. The "C" and "D" Reactor Coolant Pumps (RCP) tripped on under voltage, which resulted in a reactor trip. A turbine trip then followed. The fire on the transformer was extinguished by installed plant fire suppression equipment, and was declared "out" at 1143. The plant was stabilized at 2235 psig in the Reactor Coolant System. Other actuations were feedwater isolation and actuation of both motor and turbine driven auxiliary feed pumps due to low steam generator water level. These actuations were expected, and safety equipment performed as designed. The fast bus transfer to the start-up transformer source performed consistent with its design. Immediate investigation revealed what appeared to be a dead squirrel below the Transient Recover Voltage (TRV) Capacitor Bank associated with the PA02 side of the Unit Auxiliary Transformer. The root cause is that the Unit Auxiliary Transformer was not designed to be resistant to small animal intrusion. Corrective actions include installing insulating materials on the Unit Auxiliary Transformer and its TRV capacitor banks, and installing insulating material on the Startup Transformer and capacitor banks. On September 4, 2000, at 1424, a separate Feedwater Isolation Signal occurred. The root cause of this subsequent event was a misleading procedure step, which will be clarified.
4822000004 | Wolf Creek | 11/07/2000 | 12/06/2000 | ML00377636 | <strong>Failure to Satisfactorily Perform Technical Specification Surveillance Requirement 3.8.1.3</strong><br /><i>Abstract:&nbsp;</i>Technical Specification Surveillance Requirement (SR) 3.8.1.3 states, "Verify each [Diesel Generator] DG is synchronized and loaded and operates for >1= 60 minutes at a load of >1= 5580 kW and <1= 6201 kW." This SR is modified by a Note which states: "Momentary transients outside the load range do not invalidate this test." The Frequency of this SR is every 31 days. During a recent review of data from surveillance tests between September, 1999, and September, 2000, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel noted that on May 11, 2000, and on September 14, 2000, the load on the "A" DG was not within the acceptable kW band specified for a consecutive period of 60 minutes. Although several excursions occurred, the longest single time the DG load was outside the band was approximately 15 minutes during the surveillance on May 11, 2000. All load transients outside the specified full load band were within the load ratings of the DG for the duration of those transients. Although all performance requirement of the surveillance were not met (i.e., not having more than momentary transients) the intent of the surveillance was met, in that the surveillance demonstrated the ability of the DG to perform its safety function. The root cause was inadequate procedural guidance concerning test acceptance standards. A contributing cause was a degraded governor which caused difficulty in controlling the DG during testing. The procedures will be revised to clarify test performance acceptance standards. The governor was replaced during Refuel XI (October, 2000).
4822000005 | Wolf Creek | 11/23/2000 | 01/04/2001 | ML01009022 | <strong>Failure to Perform Technical Specification Surveillance Requirement 3.7.16.1</strong><br /><i>Abstract:&nbsp;</i>Wolf Creek Nuclear Operating Corporation (WCNOC) Chemistry personnel identified on December 8, 2000, that the fuel storage pool boron concentration reported on November 23, 2000, was performed on a sample of the Refueling Water Storage Tank (RWST) instead of the fuel storage pool. Fuel storage pool samples taken on November 16, 30, and December 7, 2000, indicated that the results were within the required limits. Technical Specification Surveillance Requirement (SR) 3.7.16.1 states, "Verify the fuel pool boron concentration is within limit." The frequency of this SR is every seven (7) days. The Technical Specification Bases indicate that the boron concentration is required to be greater than or equal to 2165 parts per million (ppm). The root cause was human error/inappropriate action in that the technician failed to use the continuous use sampling procedure as required. Employee discipline was administered. No procedural or programmatic changes are planned. The event carried minimal safety significance since the fuel storage pool was subsequently found to be within limits and was not outside limits during this time.
4832000001 | Callaway | 10/28/1999 | 03/08/2000 | ML00369151 | <strong>Technical Specification 4.6.4.2.b Violation - 'A' Hydrogen recombiner Thermocouple Inoperable for Over 30 Days Due to Swapped Leads.</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.6.4.2.b requires Channel Calibration of all Hydrogen Recombiner System instrumentation to prove operability. On 2/7/00, Utility Operations personnel discovered that thermocouple (T/C) #2 for the 'A' Hydrogen Recombiner had incorrect temperature indication. It was determined that leads for T/C #2 were swapped at a junction box. The leads were re-landed at their correct locations and restoration was independently verified. The T/C leads were last terminated on 10/28/99. The swapping of leads is attributed to failure to follow procedure. With direction being provided by a task director in the control room, the craft in containment did not have the procedure. The craft went to the wrong electrical box. The junction box is electrically the same as the correct terminal box, but more cramped and difficult to work in. The retest was not adequate to identify the swapped leads. Procedures will be revised to refer to maps for correct locations and restoration. Independent Verification will be required to be performed at the terminal box, which requires the procedure to be with the craft. A retest has been created to ensure operability is verified following termination of the T/C leads. The individuals involved were coached on attention to detail. This event will be added to industry event/operating experience for retraining and future pre job briefs.
4832000002 | Callaway | 02/13/2000 | 05/01/2000 | ML00371277 | <strong>Automatic Reactor Trip Initiated by Reactor Coolant Pump Trip Caused By Motor Current Imbalance Due to External Transmission System Disturbance</strong><br /><i>Abstract:&nbsp;</i>At 07:34 on February 13, 2000, automatic actuation of the reactor protection system (RPS) was initiated due to a low reactor coolant flow condition. This condition resulted when a reactor coolant pump (RCP) motor's protective relay sensed an electrical disturbance occurring on the transmission system, subsequently tripping the pump. The cause of the disturbance was attributed to a transmission line breaker failing to operate due to a defective electrical connection within the neighboring electric cooperative's protective relaying scheme. This resulted in an eight-minute system disturbance. At the time of the event, the plant was operating in Mode 1 at 100 percent power. Upon receiving the RPS actuation, all safety-related and nonsafety-related systems functioned per design. Ameren took corrective action to review the adequacy of their transmission system and RCP protective relaying setpoints. Completion of this review determined that Ameren's transmission system and RCP relay setpoints were adequate in the level of protection they provided and that the relays functioned per designed during the event. Ameren is also monitoring corrective actions of the electric cooperative, which has committed to installing backup relaying at the affected substation.
4832000003 | Callaway | 02/23/2000 | 03/21/2000 | ML00369613 | <strong>Pressurizer Safety Valve Setpoint Drift Outside Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>During Callaway Plant refuel ten outage in October, 1999, the three pressurizer safety valves (PSV) BB 801OA, BB8010B and BB8010C, were removed from the system and delivered to a vendor to test set pressure in accordance with Technical Specification (T/S) 4.4.2.2. These valves were replaced with pre-tested spare valves during the refueling outage. On 2/23/2000, with the Plant at 100% power, Callaway was informed by the vendor that the set pressure test results were outside of the Technical Specification as-found acceptance criteria. T/S 3.4.2.2 specifies a set pressure criteria of 2485 psig plus/minus one percent (2461 psig to 2509 psig). The as-found set pressures for BB8010A, BB8010B, and BB8010C were 2441 psig (-1.77%), 2544 psig (+2.37%), and 2522 psig (+1.49%) respectively. No material deficiencies were identified during the testing and inspection. The inspection revealed no abnormal wear and verified critical tolerances were acceptable. The valves were inspected by the vendor and set pressure reset. Based on inspections, no definitive cause was identified for the setpoint drift. Vendor testing of the PSVs will continue in the future. Set pressure will be verified within the T/S tolerance band before return as a spare.
4832000004 | Callaway | 04/06/2000 | 06/30/2000 | ML00373125 | <strong>Design Error Results in Containment Isolation Valve Inoperability in Excess of Technical Specification Limitations</strong><br /><i>Abstract:&nbsp;</i>From 04-06-2000 to 06-02-2000, valve EGHV0061 (Component Cooling Water from Reactor Coolant Pump Thermal Barrier Outer Containment Isolation Valve) was not able to automatically close upon receipt of a Phase B containment isolation signal (CISB). On 06-02-2000 Instrument and Control Technicians were performing surveillance testing on phase B slave relays. During this surveillance, it was determined that the automatic control circuit for valve EGHV0061 was not properly terminated to allow the valve to close on a CISB signal. This termination had been modified on 04-06-2000 to resolve NRC Information Notice 92-18 concerns for fire induced shorts within motor operated valve control circuits. The termination error was attributed to a design error by the utility design engineer, a failure to discover the error by the utility reviewing engineer and inadequate post modification testing. The design for valve EGHV0061 was reviewed and corrected to restore the automatic control function. The valve was retested appropriately and returned to service. The circuits for all valves with similar modifications were reviewed with no other discrepancies identified. Future modifications to resolve NRC IN 92-18 concerns will be evaluated for post modification retest adequacy. Additional evaluations are being performed to identify opportunities to enhance the design and retest programs.
4832000005 | Callaway | 09/07/2000 | 10/09/2000 | ML00376050 | <strong>Technical Specification Bases Inadequacy Results in Technical Specification Surveillances Not Being Performed on BNHV8812A/B Since Plant Startup</strong><br /><i>Abstract:&nbsp;</i>From plant start-up through 2000/09/07, surveillance testing was not performed on Refueling Water Storage Tank (RWST) to Residual Heat Removal (RHR) pumps suction isolation valves (BNHV8812A/B) as required by Technical Specification SR 3.5.2.5. On 2000/09/07, plant management determined that surveillances as required by technical specification had not been performed because Technical Specification Bases were inadequate and did not include BNHV8812A/B. Original Technical Specification SR 4.5.2.e.1 failed to include BNHV8812A/B as automatic valves in the flow path for flow path switchover by electrical interlock from EJHV8811 A/B RHR containment sump isolation valves upon receipt of a SI or RWST Level Low-Low 1 coincident with an SI signal. Technical Specification Bases and the related testing procedure will be revised to include BNHV8812A/B. Nuclear Engineering determined Maintenance testing had satisfied technical specification surveillance requirements for BNHV8812B. Delinquent surveillance testing for BNHV8812A will be performed per NOED 00-06-010 and License Amendment 140 dated 10/6/00.
4832000006 | Callaway | 09/14/2000 | 10/13/2000 | ML00376046 | <strong>Macrofouling in the 'A' train Motor Driven Auxiliary Feed Pump Room Cooler Results in Inoperability of the Pump in excess of the timje allowed in the Callaway Plant's Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2000 the A train Motor Driven Auxiliary Feed Pump (MDAFP) was determined to have been inoperable in excess of the 72 hour limit allowed by the Callaway Plant's Technical Specifications. This was due to degraded Essential Service Water (ESW) flow through its respective room cooler (SGF02A). On September 14, 2000 Engineering Personnel were performing flow verification for the 'A' train ESW system. The flow verification was part of an investigation concerning Asiatic clams that were found in another safety related room cooler during maintenance. During the flow testing, flow to the "A" MDAFP room cooler was determined to be below the limit required to support operability of the "A" MDAFP. The cause of low flow was macrofouling by Asiatic clamshells that were conservatively estimated to have infested the system as early as September 5, 2000. The outlet valve for this room cooler was repositioned from 1 7/8 turns open to 3 turns open to reestablish the required flow to this cooler. Clamshells were cleaned out of the Water Treatment Plant clearwell, and the clearwell was chemically treated to eliminate living Asiatic clams. Plant components utilizing Service Water and Essential Service Water were monitored and flushed as required. A formal root cause analysis will determine further actions.
4832000007 | Callaway | 10/03/2000 | 10/30/2000 | ML00376719 | <strong>Unplanned Emergency Diesel Generator Actuation Resulting from Inadvertent Actuation of the local emergency start device</strong><br /><i>Abstract:&nbsp;</i>At 2055 on October 3, 2000, an unplanned actuation of the A Train Emergency Diesel Generator (EDG) occurred following an inadvertent actuation of the local emergency start controls by a non-licensed Assistant Equipment Operator (AEO). This actuation occurred during an informational walkdown while the AEO was reviewing procedures associated with locally starting this EDG. Upon locating the local emergency start device, the AEO contacted the glass cover on this device with his index finger. Due to the thickness of this cover, and the relative movement of the glass cover within this device, the glass cover broke resulting in the actuation of the EDG. The EDG subsequently achieved rated speed and voltage, however, no electrical loads were transferred to the EDG since the offsite power supply was not affected. The human performance error precursor of "Inaccurate Risk Perception" was determined to be applicable in explaining the actions taken by the AEO during this event. This was based on an unrecognized risk associated with the design of the emergency start device which allowed the glass cover to be broken without excessive force. As a result, operating experience training will be provided to Operations personnel regarding this specific event, and the generic implications of this event to other plant systems/components.
4982000001 | South Texas 1 | 02/18/2000 | 03/23/2000 | ML00369610 | <strong>Failed Engineered Safety Feature instrument channel not placed in the tripped position within the required Technical Specification allowed time</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2000, Unit 1 was in Mode 1 at 96% power conducting plant coast down operations in preparation for a refueling outage. At 2130 hours on February 18, 2000, a "PCC PROT SET DOOR OPEN/PWR SPLY FAIL" alarm was received in the Unit 1 control room. An inspection of the Protection Set III cabinets concluded that the source of the alarm was a power supply failure. At approximately 0530 hours on February 19, 2000, a walk down of the diagnosed power supply failure was conducted. The LED for solid state protection system process comparator card PB-0204A was observed to be extinguished. It was determined that the "PCC PROT SET DOOR OPEN/PWR SPLY FAIL" alarm, received the previous day, was caused by a failure of the alarm card in the Charging Header Pressure - Low channel. This failed alarm card resulted in the Charging Header Pressure - Low instrument being declared inoperable at 0600 hours on February 19, 2000. The failed channel was placed in the tripped condition at 0615 hours and had been inoperable for a period of 8 hours and 45 minutes before the one hour Technical Specification required action was taken. The cause of this event was the use of ineffective problem solving to resolve the alarmed condition and the lack of control board indications or the annunciator response procedure identifying this failure as a one-hour Technical Specification action. Corrective actions include replacing and calibrating the failed card, revising the annunciator procedure and reinforcing station expectations for effective problem solving.
4982000002 | South Texas 1 | 03/02/2000 | 04/03/2000 | ML00370162 | <strong>Operability of Technical Specification Equipment Incorrectly Determined Resulting in Noncompliance with Technical Specification Action Statements</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2000, Unit 1 was in Mode 5, Cold Shutdown. Between 1415 hours on March 1, 2000 and 2208 hours on March 2, 2000, South Texas Project incorrectly determined the operability of the Source Range Nuclear Instrumentation (NI) NI-31 and Extended Range NI-45. As a result, the appropriate Technical Specification Limiting Condition For Operations (LCO) action statements of Technical Specification 3.8.2.2 and 3.8.3.2, regarding suspension of positive reactivity changes, were not complied with when control rods were withdrawn during rapid refueling rod holdout operations. The incorrect condition was identified at 1245 on March 2, 2000 and the required Technical Specification actions taken. This event resulted in a non-compliance with Technical Specification actions, which is a condition prohibited by Technical Specifications per 50.73 (a)(2)(i)(B); and a 24-hour notification is required by section 2G of the Operating License. During this same timeframe, South Texas Project also incorrectly determined the operability of "A" Train Pressurizer Power Operated Relief Valve (PORV); however, this was recognized before Technical Specification 3.4.9.3 LCO was exceeded and the Reactor Coolant System (RCS) was depressurized and vented within the allowed timeframe of the LCO. The root cause of the event was a failure to develop administrative documents to support the changes to Technical Specifications 3.8.2.2 and 3.8.3.2. Corrective actions include development of administrative tools to specify and verify the electrical power needs for equipment in Modes 5 and 6.
4982000003 | South Texas 1 | 06/08/2000 | 07/08/2000 | ML00373297 | <strong>Inoperable Battery Event</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2000, with Unit 1 at 100% power, it was determined that from May 15 through May 30, the E1A11 battery was inoperable. On May 15, 2000, a surveillance test was performed on the E1A11 battery. During the surveillance the electrolyte level in cell #18 was recorded as + t/4 inch above the high level line on the cell which exceeded the acceptance criterion as stated in the procedure. The acceptance criterion, as stated in the surveillance procedure, for the electrolyte level is "Highest electrolyte level is < +1/4 inch..." The acceptance criterion was misread and understood to mean less than or equal to +1/4 inch. This condition was not recognized during review of surveillance data. Tech Spec Surveillance 4.8.2.1.b.1 allows 7 days to restore electrolyte level within the Category B limits or declare the battery inoperable. The LCO for an inoperable battery, which is 2 hours to restore to operable or be in hot standby within 6 hours, was not met. This was a violation of Technical Specification 3.8.2.1.a. which is reportable to the Nuclear Regulatory Commission in accordance with Operating License Condition 2.G. The condition was corrected on May 30, 2000. The root cause for this event is workers' lack of attention to detail while reviewing the acceptance criteria. Corrective actions include reviewing the event with Electrical Maintenance personnel, and addressing personal accountability issues with the Maintenance personnel involved in accordance with site policies.
4982000004 | South Texas 1 | 03/10/2000 | 04/06/2000 | ML00370358 | <strong>Noncompliance with Technical Specification 3.9.9 Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2000, with Unit 1 in Mode 6, a temporary modification was installed in Class lE Load Center E1B to provide temporary power to Spent Fuel Pool Pump 1A in support of an up-coming Train B electrical outage. It was not adequately communicated that this rendered Load Center E1B inoperable. Subsequently, the Containment Ventilation Isolation System powered by Train B was not declared inoperable, and the normal containment purge penetration was not closed. Contrary to Technical Specification 3.9.9 requirements, core alterations (core off-load) were performed, with containment normal purge in operation. The incorrect condition was identified on March 8, 2000, and at 2247 on March 8, core alterations were suspended and the containment normal purge system was secured. After all core alteration requirements were re-verified, core off-load was re-commenced on March 8, 2000 at 2355. This event resulted in a non-compliance with Technical Specification actions, which is a condition prohibited by Technical Specifications per 50.73 (a)(2)(i)(B); and a 24-hour notification was required by section 2G of the Operating License. The root cause of the event was that special circumstances or conditions associated with installation of the temporary modification in Modes 5 and 6 were not recognized during outage planning. It was incorrectly understood that the components powered from a functional, but inoperable, Load Center E1B would remain operable. Corrective actions include development of administrative tools to specify and verify the electrical power needs for equipment in Modes 5 and 6, and development of guidance on determining whether functional attendant equipment is adequate to support operable equipment in Modes 5 and 6.
4982000005 | South Texas 1 | 07/20/2000 | 08/17/2000 | ML00374524 | <strong>Reactor Operator Assumes Control Room Watch with Inactive License</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2000, with Unit 1 at 100% power, it was determined that a Licensed Reactor Operator assigned to day staff incorrectly assumed the watch in the Unit 1 control room. This individual has a valid NRC Reactor Operator's license but did not meet the requirements for maintaining his license "Active" in accordance with 10CFR55.53, and NUREG-1262. This is a violation of Technical Specification 6.2.2.a Table 6.2-1. Technical Specifications Control Room staffing requires that each on-duty shift shall be composed of at least two Licensed Reactor Operators in the control room when in modes 1, 2, 3 and 4. This requirement was not maintained in that a Reactor Operator with an inactive license was assigned to fill one of the two required Reactor Operator positions in the Unit 1 control room for a short period of time (< 2 hrs). The root cause of the event was the lack of questioning attitude on the part of the Reactor Operator and the Unit Supervisor to validate qualification concerns. Corrective actions for this event include correcting the "Active License List" in both control rooms and discussing this event in Operator Requalification training. In addition, the procedure for Operator License Maintenance will be revised to require a copy of the signed original "Active License List" be posted in the main control rooms.
4982000006 | South Texas 1 | 08/21/2000 | 09/20/2000 | ML00375470 | <strong>Two Trains of Essential Chilled Water System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2000 at 0346, C Train Essential Chilled Water was secured in preparation for scheduled maintenance. Essential Chiller 12A was started at 0512 and verified to be running normally. Essential Chiller 12C was removed from service (declared inoperable) at 0400 on August 21, 2000. On August 21, 2000 at about 0645, Essential Chiller 12A was observed to be spraying oil from the top of the purge unit. The oil level in Essential Chiller 12A was found to be abnormally low. The Control Room immediately secured the chiller and declared it inoperable. Technical Specification 3.7.14 has no provisions for Mode 1 operation with two trains of Essential Chilled Water inoperable; therefore, Technical Specification 3.0.3 was entered at 0645. Since no maintenance on Essential Chiller 12C had started, the unit was restored to operable status at 0754 on August 21, 2000 and Technical Specification 3.0.3 was exited at 0754. The root cause of this event was concurrent failure of the level control system due to debris induced mechanical binding of the upper float assembly and failure of the float check valve. Corrective actions include restoring Essential Chiller 12C to operable status, replacing defective parts in Chiller 12A, and developing and scheduling Preventive Maintenance activities for each of the 300-ton chillers.
4982000007 | South Texas 1 | 12/16/2000 | 01/15/2001 | ML01023007 | <strong>Manual Unit Trip with Safety Injection</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2001 at 2300, a manual reactor trip was initiated when all main turbine governor valves closed during preparations to perform the monthly main turbine valve testing surveillance. During the ensuing transient an automatic safety injection occurred due to lowering reactor coolant system pressure resulting from a pressurizer spray valve control anomaly. Plant pressure decrease was terminated when partially open pressurizer spray valves shut and auxiliary feedwater flow was throttled. The highest reactor coolant pressure achieved during this transient was 2310 psig which is 75 psig above the normal operating value. Adequate subcooling was maintained and the reactor head area remained full during the transient. Maximum pressurizer level during the transient was approximately 63.8% which is below the high level alarm setpoint. Reactor coolant system pressure reached a minimum of 1480 psig during the transient due to partially open pressurizer spray valves. The cause of the main turbine governor valves shutting was a failure a logic card in the analog electro-hydraulic controller. The cause of the pressurizer spray valves anomaly was a calibration shift of the spray valve UP converters. Corrective actions included replacement of the gate logic card, calibration of spray valve I/P converters, and planned replacement of the pressurizer spray valve I/P converters with an improved model.
4992000001 | South Texas 2 | 02/09/2000 | 03/09/2000 | ML00369392 | <strong>Engineered Safety Feature Actuation Due to Anticipated Transient Without Scram Mitigation System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2/9/00 at 1546, with the reactor at 32% power, Unit 2 experienced an Anticipated Transient Without Scram Mitigation System Actuation Circuitry (AMSAC) actuation. AMSAC actuated in response to actual plant conditions, as opposed to equipment malfunction, spurious signal, or inappropriate actions by the operating crew. The plant conditions that caused the actuation were within normal bands for power ascension, indicating that reduced operating margin existed in the AMSAC design. AMSAC initiated in response to plant conditions causing a Turbine trip, Auxiliary Feedwater actuation, Steam Generator Blowdown and Sampling isolation. The Auxiliary Feedwater actuation started all the Auxiliary Feedwater pumps and began feeding all Steam Generators. The event was caused by a modification that introduced insufficient operating margin into the AMSAC design. The modification reduced the arming setpoint for turbine impulse pressure from 40% to 30%, and in doing so created a corresponding reduction in the operating margin. Corrective actions include verifying AMSAC and associated inputs (e.g. feedwater flow instruments) were operating as designed, and revising the modification process to ensure the impact on operating margin is properly addressed. In addition, procedures for Plant Shutdown and Plant Startup were revised to direct the bypassing of AMSAC once reactor power is reduced below 40% and prior to increasing above 38%.
4992000002 | South Texas 2 | 04/07/2000 | 05/09/2000 | ML00371516 | <strong>Reactor Overpower Event</strong><br /><i>Abstract:&nbsp;</i>On Friday April 7, 2000 at 1014, with Unit 2 at 100% power, a Nuclear Mixing Amplifier card was removed from the 7300 Solid State Protection System instrument racks during performance of a preventive maintenance activity in order to calibrate the deaerator storage tank 2A level channel. With the Nuclear Mixing Amplifier card removed the main steam to deaerator valves began to modulate open, drawing additional steam from the steam generators into the deaerator. The increase in steam flow from the steam generators caused a decrease in Reactor Coolant System average temperature and an increase in reactor power to a peak of 103.7% by average Reactor Coolant System Delta-T indication. The duration of the excursion was approximately four minutes. Exceeding rated thermal power limits is reportable to the Nuclear Regulatory Commission in accordance with Operating License Condition 2.G for a violation of the requirements contained in Section 2.C of the license. The root cause for this event is that management expectations for pre job preparation on tasks that are perceived as low risk are not well defined and have not been adequately reinforced to ensure consistent, successful task performance. Corrective actions include defining management expectations for pre job preparation in station procedures and developing a plan for reinforcing the expectations by periodic measurement of job preparation work practices.
4992000003 | South Texas 2 | 06/28/2000 | 07/28/2000 | ML00373854 | <strong>Reactor Containment Building Penetration M-85 Not Properly Isolated</strong><br /><i>Abstract:&nbsp;</i>While performing a surveillance test on December 25, 1999 with Unit 2 at 100% power, the Reactor Coolant System Hot Leg Sample Line Inside Reactor Containment Isolation Valve, PS-FV-4454, failed to properly stroke closed. In order to comply with Technical Specifications PS-FV-4454 was tagged closed and de-energized. On June 12, 2000, Equipment Clearance Order 9071 was revised to move the boundary to the Outside Containment Isolation Valve PS-FV-4456 to allow for troubleshooting on PS-FV-4454. This revision (Rev.1) did not meet the Technical Specification requirements since Reactor Coolant System Sample to Post Accident Sampling System Outside Containment Isolation Valve AP-FV-2455 was not included on the equipment clearance order. On June 13, 2000, Equipment Clearance Order 9071 Rev. 2 restored power to PS-FV-4454 which resulted in the improper isolation of penetration M-85. This condition was not discovered until June 28, 2000 at which time Equipment Clearance Order 9071 was revised to comply with Technical Specifications. The cause of this event is failure to meet management expectations associated with work practices. Corrective actions include reinforcing management expectations regarding roles and responsibilities, Technical Specification compliance, peer checking and the use of error reduction tools.
4992000004 | South Texas 2 | 08/29/2000 | 10/05/2000 | ML00375929 | <strong>Circuit Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2000, at 0038 hours (CDT), Unit 2 was at 100% power when it experienced a loss of power to one train due to tripping of the feeder breaker for a Class lE 480V motor control center. The incident occurred while restoring the associated standby diesel generator to service, causing the circuit breaker to trip due to an apparent overload condition. The circuit breaker was found to have an incorrect current transformer installed, and a new breaker with the correct current transformer was installed by 1737 hours on August 29, 2000. The failed breaker had been in operation since the last Unit 2 refueling outage in October 1999. Equipment powered from the motor control center was determined to have been inoperable since October 23, 1999, because opening of the breaker would have interrupted the ability of the equipment to perform its design function. The duration of the inoperability exceeded the Technical Specification allowed outage time, which is reportable to the Nuclear Regulatory Commission pursuant to 10CFR50.73(a)(2)(i). The root cause for this event was less than adequate work instructions in the work order used to change out the current transformers in 1992. Corrective actions include replacing the current transformer for this circuit breaker, revising the breaker maintenance procedure to perform a primary injection test if the breaker has been overhauled, discussing lessons learned with Electrical planners and Electrical Maintenance personnel, and incorporating the lessons learned in continuing training for Electrical Maintenance personnel.
5282000001 | Palo Verde 1 | 03/05/2000 | 03/31/2000 | ML00370181 | <strong>Missed Shiftly Channel Check Causes Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2000, at 2003 mountain standard time (MST), Unit 1 was at approximately 100 percent power when a containment vent was commenced to lower containment pressure. At 2200 MST, during the containment vent, control room personnel were informed that shiftly channel checks had not been maintained current for the power access purge area radiation monitors as required by Technical Specification (TS) 3.3.8. Radiological monitoring department personnel had promptly completed a channel check of RU-37 at 2140 MST upon recognizing the shiftly channel checks were not current. However, the shiftly channel check exceeded the TS surveillance testing interval by approximately 75 minutes. Subsequent channel check testing of RU-37 and RU-38 demonstrated there was no loss of quality or functional capability and therefore, there were no safety consequences as a result of this event. Likewise, this event does not represent a safety system function failure because the condition alone did not prevent, or would not have prevented, the fulfillment of a safety function of structures or systems.
5282000002 | Palo Verde 1 | 03/08/2000 | 04/07/2000 | ML00370365 | <strong>Degraded Solder Joint Causes Inoperability of Channel D Plant Protection System</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2000, at approximately 2327 mountain standard time (MST), Unit 1 was operating at approximately 100 percent power when control room personnel received multiple pre-trip alarms on channel "D" variable overpower trip (VOPT) in the reactor protection system (RPS). Upon discovery, control room personnel placed channel "D" RPS in bypass to comply with Technical Specification (TS) LCO 3.3.1, REQUIRED ACTION A.1. The cause of the alarms was determined to be a broken solder connection (cold solder joint) on the excore linear calibrate switch which supplies a linear signal to channel "D" RPS. A review of plant process data revealed firm evidence to suggest that RPS VOPT channel "D" had been inoperable for approximately 32 hours and 1 minute. As a result, compliance with TS LCO 3.3.1 REQUIRED ACTION A.1 was not met. There was no loss of a safety function in that 3 out of 4 RPS VOPT channels remained operable.
5282000003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 06/08/2000 | 07/08/2000 | ML00373298 | <strong>Inappropriate Procedure Setting in VOPT Channels Results in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2000 at approximately 1103 MST, with Units 1, 2, and 3 in Mode 1 (power operation) at approximately 100 percent power, Unit 1 control room personnel determined that the variable overpower trip (VOPT) channels (4) had an inappropriate setting. The VOPT is part of the reactor protective system and is required to be operable in Modes 1 and 2. The inappropriate setting only affected the VOPT channels at power levels less than 0.3 percent rated thermal power (RTP) and had the effect of increasing the VOPT trip setpoint slightly above the technical specification (TS) Allowable Value for Band. It was also determined that the setting had no effect on VOPT operation while operating at power levels greater than 0.3 percent RTP. The condition affected all VOPT channels in all three Units. The cause of this condition is attributed a surveillance test procedure that contained an inappropriate value for the minimum setpoint trip. The minimum value setting has been reduced below the TS Allowable Value for Band on all VOPT channels. The safety analysis setpoint limit for the VOPT was not exceeded therefore no loss of safety function occurred.
5282000004 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 11/29/2000 | 12/28/2000 | ML01008035 | <strong>Technical Specification Violation Due to Deficient Test Procedure for Refueling Purge Valves</strong><br /><i>Abstract:&nbsp;</i>On November 29, 2000, engineering personnel discovered surveillance procedures for testing refueling purge containment isolation valves were deficient, which resulted in a condition prohibited by the technical specifications. On November 30, 2000, the applicable surveillance test procedures were revised to include quantification of stem packing leakoff which is then factored into the total penetration leakage rate. By December 1, 2000, Unit 1 and 3 inboard refueling purge containment isolation valves CPAUV2B and CPBUV3A had been tested and had met revised surveillance test requirements. There have been no previous similar events reported in the last three years.
5292000001 | Palo Verde 2 | 08/26/2000 | 09/21/2000 | ML00375467 | <strong>Reactor trip due to unexpected closure of main steam isolation valves</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2000, at approximately 1539 Mountain Standard Time, Unit 2 was in Mode 1 (POWER OPERATION), when a loss of power to an "A" train logic control cabinet occurred causing all four main steam isolation valves (MSIVs) and the "A" train feedwater isolation valves (FWIVs) to close. An automatic reactor trip was initiated and the primary plant was stabilized in Mode 3 (HOT STANDBY) in forced circulation with both steam generators used for heat removal via the atmospheric dump valves. Subsequent to the reactor trip, one of the two 13.8 kV electrical distribution buses failed to complete a fast bus transfer which resulted in a loss of power to two of the four reactor coolant pumps. Operations personnel successfully cross-connected the electrical loads normally supplied by this bus to an available power source. In addition, reactor coolant system activity was monitored and acceptable operational limits were not exceeded. The event did not adversely affect the safe operation of the plant or the health and safety of the public. In the past three years there have been no similar events reported where a failed power supply caused the closure of MSIVs.
5292000002 | Palo Verde 2 | 08/29/2000 | 09/27/2000 | ML00375688 | <strong>Main Steam Safety Valve Lift Pressures Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2000, after a Unit 2 plant trip (LER 50-529/2000-02-00), lift pressure verification testing was completed on the main steam safety valves (MSSVs) per the PVNGS corrective action program. The testing revealed that as-found lift pressures for five of the twenty Unit 2 MSSVs were below the Technical Specification limits of +/- 3 percent of design lift pressure. The five MSSVs are assumed to have drifted out-of-tolerance after the MSSVs lifted during a plant trip and the completion time for technical specification limiting condition for operation (LCO) 3.7.1 B.2 was not met. APS engineering has determined that a low out of tolerance condition may occur after MSSVs lift and has implemented corrective actions to reset MSSVs after lifts occur to preclude plant operation with low MSSV setpoints. Previous similar events have been reported in LERs 50-529/1999-002, 50-530/1998-003, 50-528/1998-004, 50-529/1997-001, and 50-530/1997-003.
5292000003 | Palo Verde 2 | 07/23/2000 | 09/27/2000 | ML00375688 | <strong>ECCS Surveillance Requirement Not Met Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 23, 2000 with Unit Two operating in MODE 1, Power Operation, at approximately 100 percent power, shift operations personnel were venting the B train high pressure safety injection (HPSI) system to meet a technical specification (TS) surveillance requirement (SR). During the venting it was discovered the system contained an unusual amount of gas. Subsequent evaluation determined the B train had been partially voided by nitrogen due to safety injection tank (SIT) water leaking past HPSI injection valves. Since the SIT is maintained with a nitrogen cover gas at approximately 600 psig, the water became saturated with nitrogen which came out of solution when the water leaked past the HPSI valves into the lower pressure piping upstream of the cold leg injection valve. The SR verifies every 31 days that the system is full of water. However, the HPSI valves had been leaking and it is believed the B train experienced nitrogen voiding that was not completely vented every 31 days. Engineering personnel determined the B train remained capable of performing its safety function in the partially voided condition. The cause of this condition has been attributed to an inadequate surveillance test procedure when SIT backleakage occurs. Corrective actions include more frequent venting of the B train and a procedure change to require more extensive venting if gas is observed during the performance of the surveillance test. PVNGS has not reported similar events in the last three years.
5292000004 | Palo Verde 2 | 10/04/2000 | 11/01/2000 | ML00376854 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Degraded Alloy 600 Pressurizer Heater Sleeve</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2000, at approximately 2300 mountain standard time (MST), Unit 2 was in Mode 4, Hot Shutdown, cooling down for a refueling outage when engineering personnel discovered a small accumulation of boric acid residue on a reactor coolant system pressurizer heater sleeve. The condition was identified during a routine boric acid walkdown of the reactor coolant system hot legs. Subsequent eddy current testing confirmed a linear indication in the sleeve. Visual inspections of other RCS Alloy 600 hot leg components did not identify other degraded components. An ENS notification was made on October 5, at 1248 MST to report the condition. The sleeve has been repaired and testing will be completed during startup (Mode 3) at normal operating pressure and temperature. A previous similar event was reported in LER 50-528/1999-006-00.
5292000005 | Palo Verde 2 | 10/27/2000 | 05/14/2001 | ML01143004 | <strong>Safety Injection Discharge Check Valve Back-leakage Causes Degraded Safety Injection Flow</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2000, at approximately 1600 Mountain Standard Time, Palo Verde Unit 2 was in Mode 6 (REFUELING) when surveillance testing of the "B" train high pressure safety injection (HPSI) pump discharge check valve (2PSIBV405) revealed back-leakage in excess of surveillance test acceptance criteria. Further investigation revealed the cause of the back-leakage was due to a defective manufacturer's weld that caused the valve disk to become cocked. APS engineering has determined that while 2PSIBV405 was in this condition the HPSI system minimum flow requirements would not have been met by the redundant "A" train HPSI system during certain events when the "B" train HPSI pump was not operating. The internals of the check valve were replaced and the valve was returned to operable status on November 3, 2000. A previous similar event was reported in LER 50-528/1998-006-01.
5292000006 | Palo Verde 2 | 11/03/2000 | 05/01/2002 | ML01143004 | <strong>Safety Injection Tank Outlet Check Valve Back-Leakage Causes Degraded Safety Injection Flow</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2000, at approximately 1636 Mountain Standard Time (MST), Palo Verde Unit 2 was in Mode 3 (HOT STANDBY) when safety injection tank 2B pressure increased during boration of the cold leg safety injection lines. Operations personnel diagnosed the condition and determined that the safety injection tank 2B outlet check valve (2PSIEV225) was not seated. Since back-leakage through 2PSIEV225 could affect both trains of the high pressure safety injection system, operations personnel entered Technical Specification Limiting Condition for Operation (LCO) 3.0.3. Safety injection tank inventory was used to flush 2PSIEV225 and then reverse flow was used to seat the valve. LCO 3.0.3 was exited at 2352 MST after 2PSIEV225 was returned to an operable status and the HPSI system was returned to its normal alignment. The root cause was a lack of Preventive Maintenance (PM) activities sufficient enough to prevent the unacceptable accumulation of contaminants around the spherical bearing and hinge pin. Corrective actions include changing the check valve PM program to periodically inspect the safety injection tank outlet check valves. Previous similar events involving safety injection check valves have been reported.
5292000007 | Palo Verde 2 | 11/18/2000 | 12/15/2000 | ML00378090 | <strong>Reactor Trip Due to Licensed Operator Cognitive Error</strong><br /><i>Abstract:&nbsp;</i>On November 18, 2000 at 1147 Mountain Standard Time (MST), Unit 2 was in MODE 1 (Power Operation), at approximately 45 percent rated thermal power when a reactor protection system actuation tripped the plant. Prior to the reactor trip, at approximately 1058 MST, Unit 2 had experienced a generator/turbine trip followed by a reactor power cutback. The turbine trip was the result of failed on-line maximum excitation limit and field current regulator circuit boards. The cause of the reactor trip was licensed operator cognitive error. There have been no previous similar events reported in the last three years.
5292000008 | Palo Verde 2 | 12/10/2000 | 01/10/2001 | ML01018017 | <strong>Pressurizer Safety Valve As-Found Lift Pressures Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2000, lift pressure verification testing was completed on pressurizer safety valves (PSVs) that had been removed during the Unit 2 ninth refueling outage. The testing revealed that as-found lift pressures for two of the four Unit 2 PSVs were outside the Technical Specification limits of +3/-1 percent of design lift pressure. The out of tolerance as-found PSV condition appears to be the result of setpoint drift. An analysis of the safety consequences of the Unit 2 as-found PSV testing results is being conducted in accordance with PVNGS procedures. Based on past PSV as-found setpoints, APS does not anticipate the analysis will produce unbounded results. Previous similar events have been reported in the last three years.
5292000009 | Palo Verde 2 | 09/21/2000 | 02/16/2001 | ML01057007 | <strong>Main Steam Safety Valve Lift Pressure Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2000, during the performance of a pre-outage surveillance test, lift pressure verification testing was completed on the main steam safety valves (MSSVs). The testing revealed that as-found lift pressure for one of the twenty Unit 2 MSSVS was above the Technical Specification limits of +/-3 percent of design lift pressure. The MSSV is believed to have experienced the phenomenon called "sticking" when the MSSV lifted during the surveillance testing. The out of tolerance as-found condition appears in some cases to be the results of the valve disc bonding with the nozzle seat. Previous similar events have been reported in LERs 50-529/1999-002, 50-530/1998-003, 50-528/1998-004, 50-529/1997-001, and 50-530/1997-003.