## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192003001 | Oyster Creek | 04/15/2003 | 05/12/2003 | ML03140055 | <strong>License Violation Due to Security Officers Inattentive to Duty</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2003, at approximately 4:50 A.M. the Oyster Creek Operations Director arrived at the station and was appropriately processed by the Outer Owner Controlled Area (OCA) checkpoint. He proceeded to the Inner OCA checkpoint where he noticed that the security guards did not immediately exit the guardhouse to verify his identification and check his vehicle. He proceeded to the Guardhouse where he observed the guards, apparently asleep. An immediate search of the Inner OCA was conducted to ensure that no unauthorized vehicles had entered. The Inner OCA checkpoint is monitored by a surveillance camera. A review of the videotape revealed that no vehicles entered the Inner OCA during this period. This information was corroborated by an interview with the Outer OCA guard. Both guards were relieved from all duties. Two new guards manned the Inner OCA post. Both guards were "For Cause" Fitness for Duty tested. All readings were negative. All required NRC and Exelon notifications were made. Security reinforced management expectations to all Security Personnel on attentiveness to duty.
2192003002 | Oyster Creek | 05/20/2003 | 07/17/2003 | ML03205006 | <strong>Completion of Reactor Shutdown Required by Tech Specs Due to a Cable Fault</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2003, at 0030 hours, 4160 VAC bus 1 C locked out due to a ground fault. The plant continued operating at full power. Due to the equipment made inoperable by the loss of power to bus 1 C, Technical Specifications required the reactor to be placed In the COLD SHUTDOWN CONDITION. The reactor was manually scrammed at 0943 hours. The COLD SHUTDOWN CONDITION was reached at 1913 hours. The safety significance of this event is considered minimal. The redundant 4160 VAC bus remained in service and redundant safety-related equipment remained operable. The plant remained within Technical Specification limits and achieved SHUTDOWN and COLD SHUTDOWN within the allowed time limits. Previous experience has shown this type of cable is subject to accelerated degradation from water at the site of any defects In the insulation. All cables in this run were replaced with cables of a different manufacture. Corrective action included confirming that all buried cable powering safety-related equipment was not of the type that failed.
2192003003 | Oyster Creek | 08/14/2003 | 09/26/2003 | ML03281018 | <strong>Actuation of Reactor Protection System Due to Grid Transient</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, an electrical disturbance in the off-site electrical power grid caused an overexcitation condition in the main generator. This resulted in a main generator lockout, turbine trip, and reactor scram from 100% power. The reactor shut down as designed. Plant cooldown to cold shutdown was required due to the trip of all five recirculation pumps (three auto trip and two manual trip). Off-site power was available throughout the event. The safety significance of this event is considered minimal. The plant responded as designed for this type of event. Technical Specification limits were maintained. There was no radioactive release. Off-site power was not lost Operator response was appropriate.
2192003004 | Oyster Creek | 08/22/2003 | 09/29/2003 | ML03281019 | <strong>Actuation of Reactor Protection System Due to Instrument Malfunction.</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2003, a Turbine Trip was caused by a spurious actuation of Moisture Separator Hi-Hi Level switch, LS-4-691. This resulted in a Reactor Scram from 100% power. The reactor shut down as designed. Plant cooldown to cold shutdown was required due to the trip of all five recirculation pumps. The safety significance of this event is considered minimal. The plant responded as designed for this type of event. Technical Specification limits were maintained. There was no radioactive release . All safety systems were fully operable. Off-site power was available. Operator performance was satisfactory. All four level switches were replaced and a root cause is in progress.
2202003001 | Nine Mile Point 1 | 04/22/2003 | 06/23/2003 | ML03188001 | <strong>Technical Specification Cooldown Rate Exceeded During Required Cooldown for a Failed Solenoid Actuated Pressure Relief Valve</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2003, Nine Mile Point Unit 1 (NMP1), having recently ended a refueling outage, was at low power preparing for technical specification (TS) required testing of six solenoid-actuated pressure relief valves (also referred to as Electromatic Relief Valves or ERVs). At 2117 with power approximately 23 percent, solenoid-actuated pressure relief valve, ERV-111, failed to open during testing. TS 3.1.5.a requires that all six ERVs be operable whenever the reactor coolant pressure is greater than 110 psig. At 2117 the action statement of TS 3.1.5.b was entered. After the remaining five ERVs were satisfactorily tested, NMPl began a shutdown at 2230. The reactor was subcritical at 0055 on April 22, 2003. NMPI exited the action statement at 0250. During the cooldown, the TS cooldown limit of 100 degrees Fahrenheit (F) in one hour was marginally exceeded (101 degrees F in one hour) for approximately three minutes in two of four loops. An engineering evaluation of the cooldown concluded that Appendix G requirements were not violated and that the structural Integrity of the reactor pressure vessel was not compromised. The ERV-111 failure was due to high resistance in Its associated solenoid cut-out switch contacts. An inadequate preventive maintenance (PM) procedure did not specify measuring the contact resistance, hence the contact resistance increased unnoticed until the failure. Exceeding the cooldown limit occurred because the shutdown procedure did not adequately identify steam loads that should be secured to prevent exceeding the cooldown limit when decay heat values are low. Corrective actions for the ERV failure include replacing the solenoid valve for ERV-111, modifying the PM procedure, and testing the resistance of the cut-out switch contacts on the remaining five ERVs. The corrective actions to address exceeding the cooldown rate are modifying the shutdown procedure and providing training on the event. The test failure of ERV-111 is reportable in accordance with 10 CFR 50 .73(a)(2)(i)(a), in that the failure resulted in a TS required shutdown. Exceeding the TS cooldown limit of 100 degrees F in one hour is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the technical specifications.
2202003002 | Nine Mile Point 1 | 08/14/2003 | 01/23/2004 | ML04029060 | <strong>Reactor Scram Due to Electric Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003 at approximately 1611 hours, Nine Mile Point Unit 1 automatically scrammed from 100% rated thermal power when the turbine tripped on a load rejection. A large disturbance in the electric grid had caused the turbine to trip. Both emergency diesel generators (EDGS) automatically started and supplied the emergency buses. The electric grid disturbance ultimately led to the loss of the reactor recirculation pumps, condensate pumps, and circulating water pumps. Reactor pressure and water level were maintained using the electromatic relief valves (ERVs), emergency condensers, and the control rod drive injection system. At 1633 hours an Unusual Event (UE) was declared due to grid instability. After grid stability had been established the EDGs were secured. EDG 103 was secured at 2339 hours on August 14, 2003 and EDG 102 was secured at 0018 hours on August 15,2003. The UE was terminated at 0120 hours on August 15, 2003. The cause of the event was the severe disturbance on the northeast electric grid. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) because of the critical reactor scram, and because of the automatic start of the EDGs.
2202003003 | Nine Mile Point 1 | 11/13/2003 | 01/12/2004 | ML04021079 | <strong>Automatic Initiation of Emergency Diesel Generator 103 due to Momentary Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2003 at 2149 hours, Emergency Diesel Generator (EDG) 103 automatically initiated due to a momentary loss of offsite 115 kV power source Line #4 and an abnormal plant configuration. Nine Mile Point Unit I receives 115 kV service from two offsite power sources, Line #1 and line #4. Line #1 and Line #4 supply power to 4160 V emergency power boards (PB) #102 and #103, respectively. The two offsite sources are connected through a 115 kV reserve bus and a normally closed disconnect switch MDS-8106. The reserve bus, with a closed disconnect switch, allows one offsite power source to feed both emergency PBs. In the event offsite power is unavailable, each PB can be supplied power from its associated EDG which automatically initiates on a low voltage condition. The apparent cause of the event was 1) high wind conditions which resulted in a momentary loss of Line #4 together with 2) the abnormal configuration of failed switch MDS-8106 (i.e.,open) to facilitate required maintenance activities. With MDS-8106 In the normally closed position, the loss of Line #4 would not have affected PB 103 and EDG 103 would not have automatically initiated. Immediate actions Included verification of proper plant response and entry into appropriate operating procedures. Reserve bus disconnect switch MDS-8106 has been repaired. The automatic initiation of EDG 103 Is reportable in accordance with 10 CFR50.73(a)(2)(iv)(A).
2202003004 | Nine Mile Point 1 | 08/13/2003 | 01/26/2004 | ML04034034 | <strong>Unplanned Inoperability of Emergency Cooling System Caused by Inadequate Review of Clearance for Replacement of Instrumentation Relay</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2003, at approximately 0430 hours with the plant operating at 100 percent power, fuses were pulled in accordance with Clearance N03-13-004 to support the replacement of Emergency Cooling (EC) system initiation logic time delay dropout (TDDO) relay 11 K62A. Removal of these fuses de-energized 125 VDC battery power to EC solenoid valves 39-05G and 39-06G, which inhibited the capability of the solenoid valves to actuate (energize) to close their respective EC condensate return isolation valves in response to an EC system high steam flow isolation signal. On November 26, 2003, plant management determined that both EC systems (loops) had been inoperable on August13, 2003 for a period of approximately one hour and eight minutes as a result of this event without having initiated a reactor shutdown within one hour as required by Technical Specification (TS) 3.1.3.e. Compliance with TS 3.1.3.e was restored when the clearance was removed at approximately 0538 hours on August 13, 2003. The cause of this event is inadequate performance of the plant and TS impact reviews for the clearance supporting the replacement of the EC system initiation logic TDDO relay. A contributing cause is inadequate corrective actions for a non-reportable similar previous event. Corrective actions include removal of Clearance N03-13-003, a written briefing for Operations describing this event and the resolution, reinforcement of the proper attributes for performing clearance impact reviews, and written guidance and training for Operations personnel regarding the EC instrumentation logic and compliance with TS Table 3.6.2c.
2372003001 | Dresden 2, Dresden 3 | 05/19/2003 | 07/18/2003 | ML03211043 | <strong>Electromatic Relief Valve (ERV) Pressure Switches Drift Greater than Estimated</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2003, instrument maintenance department (MD) personnel performed a quarterly surveillance for the five Unit 3 relief valve pressure switches (3-0203-3A thru E). Of those five pressure switches, two were above the Technical Specification Allowable Values (AV) (3B & 3D), and of these two, one was above its Analytical Limit (AL) (3B). On May 21, 2003, the same quarterly surveillance was performed on the five Unit 2 relief valve pressure switches (2-0203-3A thru E). Two pressure switches (3B & 3C) were found above both their Technical Specification AV and AL. As a pressure switch was found out of tolerance, it was reset to within its as-left tolerance specifications. The investigation identified two root causes associated with this event. The first root cause was ineffective implementation of previous corrective actions. The second root cause is an error in a calculation prepared as part of the Improved Technical Specification (ITS) project. The corrective action to prevent recurrence for both root causes is to implement an appropriate setpoint change. An additional corrective action is to confirm or revise the setpoint based on testing on Barksdale pressure switches to measure the effect of changes in relative humidity.
2372003002 | Dresden 2 | 07/10/2003 | 09/08/2003 | ML03258045 | <strong>HIGH PRESSURE COOLANT INJECTION ROOM COOLER BEARING DEGRADATION</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2003, Operations personnel observed excessive noise and vibration from the Unit 2 High Pressure Coolant Injection (HPCI) room cooler. The room cooler was secured, restarted later for troubleshooting, secured again and taken out of service. On July 11, 2003, personnel replaced the inboard and outboard fan shaft bearings, performed post maintenance testing and declared the system operable. The rotating equipment component engineer examined the removed bearings. The outboard bearing was found to be in good condition. The inboard bearing, though still round, was severely worn and pitted on the entire surface of each ball indicating inadequate lubrication. The root cause for the event was that the lubrication frequency for the HPCI room coolers was incorrectly changed in 1996 from quarterly to every two years, which resulted in inadequate bearing lubrication. The corrective action to prevent recurrence is to revise the frequency of bearing lubrication for the Unit 2 and Unit 3 HPCI room coolers back to quarterly from two years. Additionally, the root cause determined that at the time the frequency was changed, there were inadequate controls in place in the preventative maintenance program to prevent this event from occurring, whereas the current program has adequate controls in place to prevent this type of event.
2372003003 | Dresden 2 | 09/30/2003 | 12/01/2003 | ML03343038 | <strong>Unit 2 Reactor Feedwater Pump Trip and Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2003, at 2014 hours (CDT), an automatic reactor scram occurred due to a low reactor water level scram signal. The low reactor water level was the result of the trip of the 2C Reactor Feedwater Pump. The 2C Reactor Feedwater Pump trip occurred due to a valid over current ground relay actuation from a fault in the B phase power cable to the 2C Reactor Feedwater Pump. The root cause of the cable fault was indeterminate as the section of the cable which contained the fault could not be retrieved. Testing of retrievable cable sections did not identify the failure mechanism. The cable was replaced. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The loss of feedwater flow is an analyzed transient and is classified as a moderate frequency event in the Updated Final Safety Analysis Report. There were no subsequent major equipment malfunctions .
2372003004 | Dresden 2 | 10/06/2003 | 12/05/2003 | ML03346038 | <strong>Unit 2 HPCI System Inoperable Due To Leaking Gland Seal Leak off Pump Check and Regulating Valves</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2003, a High Pressure Coolant Injection System (HPCI) Torus High Level switch was discovered inoperable during the functional testing of the switch. The Technical Specifications allow HPCI to remain operable with an inoperable Torus High Level switch if the HPCI pump suction is aligned to the suppression pool. When the HPCI pump suction was aligned to the suppression pool from the Condensate Storage Tank (CST), the HPCI Gland Seal Leak Off System (GSLO) pump unexpectedly operated due to high water level in the GSLO condenser. This required the realignment of the HPCI pump suction back to the CST. On October 6, 2003, at 2215 (CDT), the Unit 2 HPCI was declared inoperable due to the high water level in the GSLO condenser and the operation of the HPCI GSLO pump that prevented continued alignment of the HPCI to the uppression pool. The above-described events would not have prevented manual operation of HPCI from the control room and the Isolation Condenser System was operable during this event. The unexpected high water level in the GSLO condenser and the operation of the HPCI GSLO pump was due to leaking pump discharge check and regulating valves. The root cause of the leaking valves was the preventive maintenance performed on the valves did not adequately assess or test the leak tight condition of the valves. A new procedural requirement to perform periodic seat leakage testing for the Unit 2 and 3 HPCI GSLO pump discharge check and regulating valves will be prepared.
2372003005 | Dresden 2 | 10/19/2003 | 12/18/2003 | ML03363058 | <strong>Unit 2 Main Steam Isolation Valve Leakage Exceeds Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2003, at 1658 hours (CDT), with Unit 2 shutdown for Refueling Outage D2R18, it was discovered that the combined leak rate for all Main Steam Isolation Valve leakage paths exceeded the Technical Specification Surveillance Requirement 3.6.1.3.10 allowed value of 46 standard cubic feet per hour. The root cause of the Main Steam Isolation Valve leak rate was determined to be a loss of line contact at the valve seat/disk interface . The valves were repaired and the as-left leakage was within Technical Specification limits. The corrective actions to prevent reoccurrence are: (1) inspect all Main Steam Isolation Valves and if required, repair with the single point cutting tool method within two operating cycles, and (2) the Main Steam Isolation Valve repair procedure will be updated to require machining valve seats instead of lapping. The safety significance of this event was minimal. The total as-found primary containment leakage including Main Steam Isolation Valve leakage was 209 .7 scfh and is below the total allowable leakage of 432.3 scfh assumed in accident analyses. Thus, the total as-found primary containment leakage would have resulted in exposures during a postulated Design Basis Accident that did not exceed 10 CFR 100 limits for offsite dose or General Design Criteria 19 limits for control room dose .
2372003006 | Dresden 2 | 11/10/2003 | 12/31/2003 | ML04014036 | <strong>Unit 2 Torus Purge Valve Open In Conjunction with the Drywell Purge Valve in Mode 2</strong><br /><i>Abstract:&nbsp;</i>On October 10, 2003, at 0720 hours (CST), with Unit 2 in Mode 2, it was discovered during control panel monitoring, that the Torus Purge and Drywell Purge valves were both open. Technical Specification 3.6.1.1, "Primary Containment," and Technical Specification 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)," require one of these valves to be closed in Modes 1, 2, and 3. The Torus Purge Valve was immediately closed. The condition existed for a period of time that exceeded Technical Specifications allowed Completion Time for this alignment. The root cause of having the Torus Purge Valve and the Drywell Purge Valve open was determined to be inadequate procedures. The corrective actions to prevent reoccurrence are to revise procedures DGP-01-S1, "Startup Checklist," and DOS 0040-12, "Penetration Flow Path PCIV Position Channel Check." The safety significance of this event was minimal. The reactor pressure was approximately 135 pounds per square inch gauge when the Torus Purge valve was closed. The Drywell Purge and Torus Purge valves would have closed within approximately 10 seconds during a postulated Design Basis Accident. An engineering evaluation was performed that demonstrated that with either of the valves in the closed position within 10 seconds of a postulated Design Basis Accident, the calculated maximum Primary Containment and Torus pressures would be within design limits.
2372003007 | Dresden 2 | 12/11/2003 | 02/09/2004 | ML04049066 | <strong>Unit 2 Manual Scram Due To High Stator Water Cooling System Temperature</strong><br /><i>Abstract:&nbsp;</i>On December 11, 2003, at 2335 hours (CST), with Unit 2 at 96 percent power in Mode 1, a manual scram was inserted as the result of the plant's response to high Stator Water Cooling System temperature. The high Stator Cooling Water System temperature was due to a failed temperature controller to the Stator Water Cooling System temperature control valve. The plant responded as expected to the manual scram. The root cause of the temperature controller failure was attributed to historical foreign material intrusion resulting from inadequate processes for maintenance on the instrument air system. The foreign material caused an internal temperature controller pneumatic relay valve to stick and not respond properly. The identified foreign material was 5 to 10 micron aluminum oxide particles from the instrument air system. The corrective actions to prevent reoccurrence are to establish equirements for a post maintenance flush of instrument air lines and to incorporate the requirements into maintenance work planning documents. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the manual scram. There were no subsequent major equipment malfunctions.
2442003001 | Ginna | 04/02/2003 | 05/23/2003 | ML03155036 | <strong>Inadequate Consideration of System Interactions for Bus Tie Breaker Maintenance Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2003, the plant was in Mode 1 at approximately 100% steady state reactor power. At approximately 0930 EST, it was discovered that over the last three years, on two separate occasions (June 8, 2000 and January 16, 2002), maintenance activities associated with non-safety-related bus tie breakers 52/BTA-A and 52/BTB-B had rendered the Main Feedwater Pump Discharge Valves (MFPDVs) inoperable with respect to the Ginna Station Technical Specifications. This inoperability was not recognized by plant staff at the time of the maintenance. As a result, LCO 3.7.3 Condition A was not entered and the Required Action Completion Time of 24 hours was not met. Since these were previous occurrences, no immediate actions were required. The cause of operating in a condition prohibited by Technical Specifications was plant staff not recognizing the impact of removing the bus-tie breaker's from service and their impact on the MFPDVs due to inadequate consideration of system interactions. Corrective action to prevent recurrence is listed in Section V.B.
2442003002 | Ginna | 08/14/2003 | 10/09/2003 | ML03289044 | <strong>Major Power Grid Disturbance Causes Loss of Electrical Load and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, the plant was in Mode 1 at approximately 100% steady state reactor power. At approximately 1611 EDST, a major electrical grid disturbance occurred, affecting the Northeastern United States and areas of Southern Canada. The disturbance caused a complete loss of electrical load and an automatic Reactor Trip. The Shift Supervisor conservatively declared an Unusual Event at 1646 EDST based on Emergency Action Level 6.1.1, "Loss of ability to supply power to the safeguard trains from offsite circuits 751 and 767 for greater than 15 minutes," and exited the Unusual Event at 2108 EDST. The cause of the Reactor Trip was 2/4 Over Temperature Delta T (OTDT) channels reaching their setpoints due to the load rejection and ensuing Reactor Coolant System transient.
2442003003 | Ginna | 09/18/2003 | 11/10/2003 | ML03321014 | <strong>Containment Sump As-Found Condition not in Accordance with Design Requirements</strong><br /><i>Abstract:&nbsp;</i>This information is reported voluntarily appropriate to the guidance provided in NUREG 1022, "Event Reporting Guidelines 10 CFR 50.72 and 50.73," revision 2, section 2.7 "Voluntary Reporting." On September 18, 2003, with the reactor in Mode 5 for a refueling outage, investigations determined that potential flow paths existed larger than allowed by design basis (greater than 1/4-inch openings) into the containment Sump B that bypass the sump inner screen. Upon initial evaluation, it was postulated that debris generated by a design basis loss of coolant accident inside containment could have potentially bypassed the emergency sump inner screen and affected both independent Emergency Core Cooling System (ECCS) trains, due to both trains requiring suction from the emergency sump during the recirculation phase of operation. This had the potential to prevent both trains of ECCS from removing residual heat from the reactor. Also, further investigations determined an existing limited amount of debris inside containment Sump B and a question regarding the size of the openings in the inner screen. However, since that time, RG&E has performed an extensive evaluation and determined that equipment required to mitigate the event, though found to be in a degraded condition, would perform their required functions. Corrective actions included modifications to the containment Sump B to restore it to design conditions and enhancements to the containment inspection procedure, including training of involved personnel.
2442003004 | Ginna | 10/12/2003 | 12/11/2003 | ML03352019 | <strong>Auxiliary Feedwater Flowpath Inoperable During Mode Changes, Due to Personnel Error, Resulted in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2003, at approximately 2300 EDST, the plant was in Mode 2 at approximately 2% steady state reactor power. Surveillance testing was in progress as part of a return to power following a refueling outage. It was discovered that one of two turbine driven auxiliary feedwater (TDAFW) flowpath was isolated, and had been inoperable during the transition from Mode 4 to Mode 3 on October 12, 2003 at 1320 and from Mode 3 to Mode 2 on October 14, 2003 at 0446. This condition is contrary to Ginna Station Improved Technical Specifications Limiting Condition for Operation 3.0.4. The conditions initiating this event were traced to the performance of procedures utilized for the filling of the steam generators during shutdown, which invalidated the auxiliary feedwater system lineup previously performed. Corrective action was immediately taken to restore the TDAFW flowpath to operable status, and further procedural and process controls will be implemented to prevent recurrence.
2442003005 | Ginna | 10/15/2003 | 12/11/2003 | ML03352020 | <strong>Manual Reactor Trip Resulting From Loss of Off-Site Power Circuit 751</strong><br /><i>Abstract:&nbsp;</i>During start-up from the 2003 Refueling Outage (RFO) on October 15, 2003, high wind conditions resulted in the loss of off-site Circuit 751. With the electrical system in the normal start-up alignment, the loss of Circuit 751 resulted in the loss of the bus powering the B Reactor Coolant Pump (RCP). Following the loss of the BRCP, the operators manually tripped the reactor as required by Abnormal Operating Procedure AP-RCS.2, Loss of Reactor Coolant Flow. Safeguards busses 16 and 17 were also lost due to the loss of Circuit 751, but were subsequently re-energized by the B Emergency Diesel Generator (EDG) as designed. The A and B Motor Driven Auxiliary Feedwater Pumps started as designed. The plant was stabilized in Mode 3 using the appropriate procedures. Corrective action to prevent recurrence is outlined in Section V.B.
2442003006 | Ginna | 11/13/2003 | 01/09/2004 | ML04014032 | <strong>Emergency Diesel Generator Start Resulting From Loss of Off-Site Power Circuit 751</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2003, high wind conditions resulted in the loss of off-site Circuit 751. With the electrical system in the 50/50 alignment, the loss of Circuit 751 resulted in the loss of safeguards busses 16 and 17. The B Emergency Diesel Generator (EDG) started automatically and re-energized the safeguards busses as designed. Corrective action to prevent recurrence is outlined in Section V .B.
2472003001 | Indian Point 2 | 02/06/2003 | 04/02/2003 | ML03097009 | <strong>Plant in an Unanalyzed Condition Due to Cable Routing - Non-Compliance With Appendix R Separation Criteria</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2003, IPEC, Programs & Components Engineering (P&CE), determined that the routing of Charging Pump (CHP) control cables did not meet the cable separation criteria specified in Appendix R Section III.G. On February 12, 2003, P&CE further identified that the routing of the power supply cables for the six Service Water Pumps (SWP) did not meet the separation criteria of Appendix R, Section III. G. These conditions were discovered during the validation and re-baselineing of the Appendix R safe shutdown analysis. In the case of the CHPs, the control functions for all three CHPs were determined to be vulnerable to damage by a single fire event in Fire Area F, specifically the Primary Auxiliary Building (PAB), elevation 80 ft. In the case of the SWPs, the normal and alternate power supply cables for all six SWPs were determined to be vulnerable to damage by a single fire in Fire Area J, specifically the Turbine Building (TB), elevation 15 ft. The apparent cause was the lack of rigor applied in the engineering analysis that developed the Appendix R safe shutdown analysis. The Appendix R analysis lacks sufficient detail and/or support documentation to justify the original design configuration. The corrective actions taken were to complete the re-baselineing of the Appendix R analysis and develop procedures or modifications to resolve non-compliance with Appendix R. Upon discovery of these conditions, IPEC initiated fire protection impairment actions in accordance with Station Administrative Order SAO-703," Fire Protection Impairment Criteria and Surveillance," and interim compensatory measures were implemented. These conditions had no significant effect on the health and safety of the public.
2472003002 | Indian Point 2 | 04/22/2001 | 05/20/2003 | ML03143034 | <strong>Plant in a Condition Prohibited by Technical Specification Due to Unavailability of Boric Acid Storage for More than 48 Hours</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2003, at 1600 hours, with steady state reactor power at 100%, System Engineering determined that the both trains of the boric acid storage system (BASS) had been inoperable for 102.3 hours from April 22 to April 26, 2001. Technical Specification (TS) 3.2.B.3 requires one flow path from the BASS to the reactor coolant system (RCS) and TS 3.2.C.2 allows this flow path to be inoperable for a period of up to 48 hours before going to hot shutdown. This placed the plant in a condition prohibited by TS for 54.3 hours. The event was identified on March 21, 2003 during an extent of condition review of an event where the inability to verify a boric acid flow path to the core occurred. A 2-inch manual Grinnell Saunders diaphragm valve had failed due to the incorrect (upside down) installation of the fingerplate in the bonnet assembly in March 2001 and prevented design flow from the 22 Boric Acid transfer pump to the blender. The event was the only time both flow paths were unavailable for more than 8 hours since the valve work. The apparent cause was human error. Corrective action included valve repair, visual inspection of 5 similar valves and upgrade of the maintenance procedure. There was no safety significance since the BASS is not required for any plant accident.
2472003003 | Indian Point 2 | 04/28/2003 | 06/27/2003 | ML03182016 | <strong>Automatic Reactor trip initiated by a main turbine trip on auto stop oil .</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2003 at 1648 hours Indian Point Unit 2 experienced an automatic reactor trip with all control rods fully inserting. The trip was initiated by a main turbine trip on auto stop oil. The auto stop oil turbine trip was caused by a trip of the over frequency relays actuated by a disturbance associated with the 345kV North Ring Bus at the Buchanan Substation and the Consolidated Edison 138kV system. Following the grid disturbance breakers 11 and 7 opened followed by a Phase A ground fault on breaker F7. When Consolidated Edison attempted to re-close breaker 11, a relay [EIIS:FK:681] malfunction occurred causing Unit 2 output breaker 9 to open resulting in a turbine trip. The resultant trip placed the plant in natural circulation with 480-volt buses 2A and 3A de-energized as per design. All three Emergency Diesel Generators (EDGs) started and buses 2A and 3A were manually energized by 22 EDG, this was an expected response. 480-volt buses 5A and 6A remained energized from offsite sources during this event. No steam generator or pressurizer safety valves lifted and actuation of the Safety Injection System was not required. No radioactive release to the environment occurred as a result of this transient.
2472003004 | Indian Point 2 | 08/03/2003 | 10/02/2003 | ML03279015 | <strong>Automatic Turbine Trip / Reactor Trip Due to 345 kV Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2003, at approximately 0430 hours, Indian Point Unit 2 experienced an automatic reactor trip event (JE) initiated by a main turbine trip on auto stop oil . The auto stop oil turbine trip was caused by an electrical disturbance associated with the 345kV North Ring Bus at the Buchanan Substation. Subsequent failure of a carrier power supply {JX} prevented the generation of a transfer block signal, which would have prevented the occurrence of this event. Prior to this event, Indian Point Unit 2 was operating at 100 percent, steady-state power conditions. During the unit trip the internal 6.9kV buses were de-energized resulting in a loss of all four (4) reactor coolant pumps (RCP). This placed the plant in natural circulation. The loss of the internal 6.9kV buses resulted in the loss of 480V buses 2A and 3A as per plant design. All three (3) emergency diesel generators (EDG) {EK) started and buses 2A and 3A were manually energized by 22EDG. No steam generator or pressurizer safety valves lifted and actuation of the safety injection system was not required. No radiological releases or adverse safety implications to the public occurred as a result of this event. In accordance with 10 CFR 50 .72 (b)(3)(iv)(A), the NRC was notified (Event Number 40045) of this event at 1110 hours on August 3, 2003. This report is submitted pursuant to 10 CFR 50 .73 (a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system.
2472003005 | Indian Point 2 | 08/14/2003 | 10/14/2003 | ML03289022 | <strong>Automatic Reactor Trip Due to Reactor Coolant Pump Trip on Under-Frequency Caused by a Degraded Off-Site Grid</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, at approximately 1611 hours during 100% steady state power, Indian Point Unit 2 experienced an automatic reactor trip initiated as a result of low reactor coolant loop flow due to the trip of the 22 Reactor Coolant Pump (RCP) breaker. The 22 RCP breaker tripped due to electrical supply bus under-frequency caused by an unstable off-site power grid (Northeast blackout). Off-site power was lost and all three Emergency Diesel Generators started and energized their assigned safety buses. Main feedwater isolated and the Auxiliary Feedwater (AFW) pumps automatically started. A Notification of Unusual Event (NUE) was declared at 1625 hours, in accordance with the Emergency Plan when off-site power was unavailable for greater than 15 minutes. The NUE was terminated on August 15, at 0210 hours, when off-site power was restored. The cause of the event was a loss of off-site power due to an unstable power grid. Corrective actions to address the cause of the event included a post trip review, root cause evaluation and plant assessment. There were no nuclear safety concerns exhibited during the event and all fission product barriers remained intact. There was no impact on the health and safety of the general public.
2492003001 | Dresden 3 | 10/23/2002 | 10/27/2003 | ML03309006 | <strong>Drywell Radiation Monitor Detector Not Fully Inserted</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2003, at approximately 1300 hours (CDT), an Instrument Maintenance Department Technician confirmed that Unit 3 Drywell Radiation Monitor detector 3B was approximately 23.5 inches from full insertion. The functions of the Drywell Radiation Monitors are to provide a primary containment isolation signal due to high radiation per Technical Specification (TS) 3.3.6.1, "Primary Containment Isolation Instrumentation," and post accident radiation monitoring capability to control room operators during potential accident situations per TS 3.3.3.1, "Post Accident Monitoring (PAM) Instrumentation." Engineering performed an evaluation and determined that the Unit 3 detector 3B could not perform its TS functions in the as-found partially inserted condition. This condition had existed since October 23, 2002. The investigation identified the root cause as inadequate procedural direction in the placement of the detector in its penetration. The corrective action to prevent recurrence was to revise Dresden procedure DIS-1700-16, "Drywell High Radiation Monitor Group 2 Isolation Functional and Calibration Tests," to clarify that the detector be fully inserted into the penetration until the detector is in contact with the inner surface of the penetration.
2502003002 | Turkey Point 3 | 01/27/2003 | 08/15/2003 | ML03239003 | <strong>Manual Reactor Trip Due to Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2003, with the unit operating at approximately 100% reactor power, Unit 3 was manually tripped due to low steam generator level on the 3C steam generator. The low steam generator level was caused by a momentary loss of running instrument air compressors. The degraded instrument air pressure affected the air-operated main feedwater control valves, causing them to drift closed. The Control Room Operator took prompt procedurally driven actions to reduce power in response to the transient and to manually load the diesel driven instrument air compressors. Steam generator levels decreased, with the 3C steam generator level reaching approximately 12 percent, when the Unit 3 Control Room Operator initiated the manual trip of the unit. Following the manual reactor trip, all three turbine-driven auxiliary feedwater pumps started as expected and instrument air was restored. All control rods fully inserted. The plant was stabilized in Mode 3. This event is reported per the requirements of IOCFR50.73(a)(2)(iv)(A). The cause of this event was a failure of the 4CM motor driven instrument air compressor, with the 3CM compressor out of service for maintenance. A contributing cause was the failure of the 3CD and 4CD diesel-driven compressors to autostart. Corrective actions included the installation of temporary instrument air compressors. Evaluation of the 4CM motor driven compressor failure and the 3CD and 4CD diesel-driven instrument air compressors failure to autostart was completed and corrective actions were implemented.
2502003003 | Turkey Point 3, Turkey Point 4 | 03/11/2003 | 03/26/2003 | ML03093064 | <strong>Unescorted Access Inappropriately Approved Due to Falsified Pre-Access Information</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2003, at 2115 hours, Florida Power and Light's Turkey Point Unit 3 was defueled, and Unit 4 was in Mode 1 (Power Operation) operating at 100 percent power. At this time, FPL access authorization and Fitness for Duty personnel determined that a contractor employee had provided false information during pre-employment screening to gain unescorted access to the protected area. Access authorization and Fitness for Duty personnel concluded that the individual would not have been granted unescorted access had the information been disclosed. On March 11, 2003, at 2148 hours, FPL completed a one-hour notification to the NRC, in accordance with 10 CFR 73.71(d) and with the safeguards reporting guidelines contained in Generic Letter 91-03, Reporting of Safeguards Events. The individual's access was denied. FPL judged that the individual falsified the background information to obtain employment and not to perform acts to impact plant safety, i.e., there was no malevolent intent. This event report is being submitted pursuant to 10 CFR 73.71(d).
2502003004 | Turkey Point 3 | 02/27/2003 | 04/25/2003 | ML03126038 | <strong>As-Found Cycle 19 Main Steam Safety Valve Setpoints Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2003, Turkey Point Unit 3 was in mode 1 and holding at approximately 60 percent reactor power while performing Technical Specification surveillance testing of the Main Steam Safety Valves setpoints. Three Main Steam Safety Valves lifted outside the Technical Specification limits of +/- 3% due to micro-bonding between the valve and the disc. In each case, the unit entered then exited the applicable Technical Specification 3.7.1.1.b Action Statement as the valves were removed from service, then returned to service within the Technical Specification allowed outage time of 4 hours. A fourth Main Steam Safety Valve lifted outside the Technical Specification Limit due to a misalignment of the valve yoke rod and nut and could not be returned to service. The plant entered the Action Statement for Technical Specification 3.7.1.1.b and reactor power was reduced below 53 percent. During the planned unit refueling shutdown which commenced on March 1, 2003, all four valves were disassembled, repaired, and returned to service prior to unit restart. Operation of the facility with the Main Steam Safety Valves as-found settings was within analytical bounds; therefore, this event had no impact on the health and safety of the public.
2502003005 | Turkey Point 3 | 03/01/2003 | 04/29/2003 | ML03126069 | <strong>Disabling Both Auxiliary Feedwater Trains Inadvertently During Mode 3</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2003, Turkey Point Unit 3 was in Operational Mode 3 in accordance with the planned reactor shutdown for the Cycle 20, Refueling Outage. A clearance executed for planned maintenance activities on the Rod Control system opened two DC breakers, which disabled both trains of Reactor Protection Relay Racks. This was an expected condition. However, it also disabled both trains of Auxiliary Feedwater (AFW) automatic actuation logic and relays from the Steam Generator water (SG) water level low-low signal. This was not expected. Two Technical Specifications (TS) for the AFW actuation logic and actuation relays Item 6.a of TS Table 3.3-2 and TS 3.7.1.2 for the AFW steam supply valves are applicable in Modes 1-3. This condition was discovered in Mode 5 when no TS applied. There was no recognition that TS action statements applied during the transition to Mode 5. As a result, the TS actions while in Mode 3 were not performed. No operability concerns existed at the time of discovery. Unit 3 continued to Mode 6 for refueling activities. The root cause of this event is a latent organizational weakness in the level of detail contained in the vital DC load list drawing. A contributing cause is the inherent design of the SG water level low-low signal circuitry. It was determined that the health and safety of the public were not affected by this event. This event is reportable in accordance to 10 CFR-50.73(a)(2)(i)(B).
2502003006 | Turkey Point 3 | 04/28/2003 | 06/26/2003 | ML03188082 | <strong>Technical Specification Required Shutdown Due to Inoperable Containment Isolation Valve CV 3-200B</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2003, at 1600 hours, with Unit 3 in Mode 1 at 100 percent rated thermal power, letdown containment isolation valve, CV-3-200B, was determined to be inoperable due to excessive seat leakage. A management decision was made to shutdown Unit 3 in order to effect the required repairs, and TS 3.6.4, Action Statement d. was entered. On April 28, 2003, at 21:09 hours, in accordance with plant operating procedures, a manual trip of the unit was performed from approximately 22 percent power. Following the manual reactor trip, all three turbine-driven auxiliary feedwater pumps started and all control rods fully inserted. The plant was stabilized in Hot Standby (Mode 3). A decision was made to remain in Mode 3, isolate CV-3-200B and comply with TS 3.6.4 Action Statement c. On April 29, 2003, at 0105 hours, CV-3-200B was isolated and Technical Specification Action Statement c. was met. CV-3-200B was repaired and declared operable on April 30, 2003, at 1925 hours, and TS 3.6.4 was exited. This event is reported per the requirements of 1OCFR50.73(a)(2)(i)(A). The cause of this event was due to leakage through the letdown isolation valves CV-3-200 A, B, and C due to wear of the valve stems, cages and plugs. Corrective actions included the repair of CV-3-200 A, B, and C letdown isolation valves. In addition, the Preventive Maintenance program will be reviewed and revised to improve the reliability of CV-3-200A, B and C valves. The health and safety of the public were not affected by this event.
2502003007 | Turkey Point 3 | 03/15/2003 | 07/02/2003 | ML03197047 | <strong>Containment Spray Pump Failed During Mode 5 Refueling Outage Testing</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2003, Turkey Point Unit 3 was in Mode 5, returning to power following the planned reactor shutdown for the Cycle 20, refueling outage. During the Train B Engineered Safeguards Integrated Testing, when the 3B Containment Spray Pump (CSP) [BE:P] was started, the field Operator heard unusual noises emanating from the pump and detected an electrical odor around the motor. The 3B CSP was secured. Investigations to determine pump failure, discovered that the pump casing wear ring was fused to the impeller wear ring and that there was a discoloration on the wear rings indicating that they had overheated. The pump was overhauled successfully, tested and returned to service on March 20, 2003. After event analysis on May 7, 2003, it was concluded that the 3B CSP was considered to have been inoperable since the last successful Inservice Testing (IST) performed in Mode 1 on February 6, 2003. Based on that conclusion, the failure of the 3B CSP is reportable under the requirements of 1OCFR50.73 (a)(2)(i)(B) for operation or condition prohibited by Technical Specifications. The root cause for the 3B CSP failure was a loss of internal pump clearance, due to the large amount of diametrical clearance between the pullout assembly to pump casing rabbet fit. The pump was overhauled successfully, tested and returned to service on March 20, 2003. It was determined that the health and safety of the public were not affected by this event.
2502003008 | Turkey Point 3 | 05/20/2003 | 07/17/2003 | ML03212066 | <strong>Manual Reactor Trip to Repair Shutdown Bank B Rod Control System Logic Failure</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2003, Florida Power and Light's (FPL) Turkey Point Unit 3 was operating in Mode 1 at 100% power. At 09:16 hours during the performance of the quarterly surveillance Rod Cluster Control Assembly Periodic exercise, Group 1 Shutdown Bank B did not move out with demand for withdrawal and an urgent failure alarm [AA:JD] was received from rod control [AA:ROD] power cabinet 1 BD [JD:CAB, JC]. Group 1 of the Shutdown Bank B was declared inoperable. Operations entered the Off Normal Operating Procedure for Reactor Control System Malfunction and Technical Specifications (TS). In accordance with TS 3.1.3.5, Shutdown Rod Insertion Limit, and 3.0.3, the reactor was manually tripped from 30% power at approximately 15:43 hours. The inability to move the Shutdown Bank B was caused by a Rod Control System failure due to a loss of the logic UPSPX signal on the 1 BD Movable Slave Cycler Decoder Card A41 1, pin 24. During the shutdown, all Unit 3 control rods properly inserted into the reactor core. As such, they performed their design basis function of inserting into the reactor core on demand. The health and safety of the public were not affected by this event. This event is reported under the requirements of 10 CFR 50.73 (a) (2) (i) (A) for the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
2502003009 | Turkey Point 3 | 07/18/2003 | 09/17/2003 | ML03269094 | <strong>Component Cooling Water System COnfiguration Outside Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 6, 2003, in preparation for performing the Unit 3 "C" Component Cooling Water (CCW) Pump In-service Test (IST), it was questioned as to whether or not the CCW system configuration used for IST, conforms to the allowable Technical Specification (TS) 3 .7.2, "Component Cooling Water System" requirements. Due to the Turkey Point CCW system configuration, whenever the 3C CCW pump IST is performed, the CCW system headers are split and the 3B CCW pump control switch is placed in pull-to-lock. This configuration is necessary in order to establish the required IST test flow rate for the 3C CCW pump. This renders the 3B CCW pump out-of-service (inoperable) for the duration of the 3C CCW pump IST. The Operating Procedure for the CCW System requires that, whenever the 3B CCW pump is inoperable, its breaker must be racked out and the 3C CCW pump must be electrically aligned to the 3B 4160 volt electrical bus. This action enables an interlock for the 3C CCW pump to receive the 3B pump's auto-start signals. The IST procedure does not take this into account. Thus, for the 3C CCW pump IST, the CCW system configuration for postulated accident mitigation can only be credited with one (1) CCW pump/heat exchanger serving one CCW header for the duration of the IST. This is less than the minimum required per TS 3.7.2, and is therefore reportable under IOCFR50.73(a)(2)(v)(B). The cause of this event was due to a procedural deficiency resulting in unacceptable CCW system testing configurations. The procedural deficiencies have been corrected. The health and safety of the public were not affected by this event.
2502003010 | Turkey Point 3 | 09/16/2003 | 11/13/2003 | ML03328048 | <strong>Operation With Two Charging Pumps Inoperable In Excess of Technical Specifications Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2003, with Turkey Point Unit 3 operating at 100% power, and the 3A Charging Pump out of service for maintenance, when the 3C Charging pump was placed in service, the pump tripped. After the second unsuccessful attempt to restart the 3C Charging Pump, it was declared inoperable. Technical Specification 3 .1 .2.3 Limiting Condition of Operation requires that at least two of the three charging pumps be operable in Mode 1. With only one Charging Pump operable, TS 3.1.2.3, Action Statement requires that at least two charging pumps be restored to operable status within 72 hours or be in cold shutdown within the next 30 hours. It was discovered that valve 3-280H, the isolation valve for the interlock pressure control switch was mispositioned closed. Since the time of valve 3-280H closure could not be determined, the 3C Charging Pump was considered inoperable since the performance of the last surveillance on August 24, 2003 at 11:56. The 3A Charging Pump had been out-of-service for maintenance since August 26, 2003 at 04:45, leaving one operable charging pump. The 3C Charging Pump was declared operable on August 29, 2003 at 16:55, following valve 3-280H alignment and verification of proper pump operation. Therefore, two charging pumps (3A and 3C) were considered inoperable for a total of 84 hours and 10 minutes, exceeding the 72 hour TS Action Statement 3.1.2.3. This event is reportable as a condition prohibited by technical specifications in accordance with 10 CFR 50.73(a)(2)(i)(B). The valve mispositioning was corrected. The health and safety of the public were not affected by this event.
2512003001 | Turkey Point 4 | 04/10/2003 | 06/12/2003 | ML03170048 | <strong>Channel Failure of Qualified Safety Parameter Display System</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2003 at 2:50 AM, Unit 4 was operating at 79 percent reactor power while performing a power reduction for turbine valve testing. Operations personnel observed that the 4A Core Exit Thermocouple Subcooling Margin Monitor of the Qualified Safety Parameter Display System was not responding as expected to the power reduction. The instrument channel was subsequently reset and it began to respond as expected to the unit power reduction. Investigation revealed that some inputs to the 4A Channel of the Qualified Safety Parameter Display System had stopped responding to actual plant conditions. It was determined that this condition existed since March 22, 2003 at approximately 6:40 PM. During the time that these inputs were inoperable, the unit had inadvertently exceeded the 7-day Technical Specification Action Statements 31 and 37 of Accident Monitoring Technical Specification 3.3.3.3 for inoperability of the 4A In-Core Thermocouples, and the Reactor Vessel Level Monitoring System. This event was determined to be reportable on April 15, 2003, under the criteria of 10 CFR 50.73 (a)(2)(i)(B). The apparent cause of the failure is a sticking input relay on one of the thermocouple input boards on Chassis number 2 of the 4A Channel of the Qualified Safety Parameter Display System. Corrective actions include increased monitoring and trending of QSPDS. This event did not compromise the health or safety of plant personnel or the general public.
2512003002 | Turkey Point 4 | 10/02/2003 | 12/03/2003 | ML03346038 | <strong>AS-FOUND CYCLE 20 MAIN STEAM SAFETY VALVE SETPOINT OUTSIDE TECHNICAL SPECIFICATION LIMITS</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2003, Turkey Point Unit 4 was in mode 1 and holding at approximately 49 percent (%) reactor power, while performing Technical Specification (TS) surveillance testing of the Main Steam Safety Valves (MSSV) setpoints, just prior to the Unit 4 Cycle 21 Refueling Outage. The Unit 4 "A" Steam Generator (SG) MSSV, RV-4-1400, as found lift pressure was 1128.5 psig, which was greater than the TS allowable setpoint pressure of ±3% of 1085 psig (1052.5 psig - 1117.5 psig). RV-4-1400 was declared inoperable and the plant entered TS action statement 3.7.1.1.b. Reactor power was at 49%, which is below the 53% reactor power required per TS 3.7.1.1.b. RV-4-1400 was subsequently tested at 1097.9 psig, or 1.19% above the setpoint . Per ASME Operation and Maintenance (OM), Part 1, Section 1.3.4.1(e)(2), RV-4-1400 remained out of service, pending cause and corrective action determination. The cause of the high lift pressure for RV-4-1400 was determined to be micro-bonding of the nozzle and disc. An adjustment was made of 1 flat of the adjusting nut to restore the valve to within 1% of the setpoint pressure and the plant exited TS action statement 3.7.1.1.b. The valve was subsequently overhauled and tested twice more, with the results within 1% of the required setpoint pressure the valve was placed back in service. Operation of the facility with the as-found setting was within analytical bounds; therefore, this event had no impact on the health and safety of the public.
2542003001 | Quad Cities 1 | 05/20/2003 | 07/21/2003 | ML03212051 | <strong>Reactor Shutdown Due to Reactor Heat Vent Steam Leak Constituting Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2003, at approximately 0240 hours, a small (approximately 12" plume) steam leak was identified on the Unit 1 Reactor Head Vent line. At the time that the leak was identified, the reactor was subcritical in Mode 2 with a planned shutdown in progress and all Emergency Core Cooling ECCS) systems operable. The leak was identified during the initial drywell entry for the reactor shutdown. The Reactor Head Vent is utilized to vent non-condensable gases from the reactor vessel head during operation. The vent line attaches to the vessel head at a 4" flanged connection and reduces to a 2" line constructed of A106 Grade B carbon steel, schedule 80, piping with socket welded fittings. The leak was located adjacent to an original construction weld in the 2" section of piping inboard of the isolation valves. The root cause of this event was inadequate verification of weld quality. The significance of the event was minimal. The leakage rate was low and all ECCS systems were operable. Also, the consequences of a postulated worse case failure of this pipe are within analyzed limits. Corrective actions included replacement of a section of piping and inspection of additional welds on Unit 1 and Unit 2.
2542003002 | Quad Cities 1 | 05/29/2003 | 02/09/2004 | ML04057051 | <strong>Mode Change with Core Spray Loop Inoperable due to Failure to Properly Fill and Vent</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2003, at 0114 hours, during the monthly verification of fill for the 1B Core Spray loop, air was observed from the high-point vent in excess of procedural acceptance criteria. Investigation determined a fill and vent had not been performed following a local leak rate test (LLRT) of the 1B Core Spray isolation valves on May 21, 2003. The system was inoperable from the time that the LLRT was performed until the air in the piping was removed. On May 29, 2003, at 0353 hours, Unit 1 entered Mode 2, and at 1947 hours Unit1 entered Mode 1. This event was originally reported as operation prohibited by TS Limiting Condition for Operation 3.0.4 and Surveillance Requirement 3.0.4 due to the mode changes made while Core Spray, was inoperable. Revision 1 is being submitted to include additional system venting events in the "Previous Occurrences" section. The root cause of this event was inadequate procedure adherence and coordination of work activities due to miscommunication and inadequate turnover. The safety significance of this event was minimal. The IA loop of Core Spray and the Low Pressure Coolant Injection mode of Residual Heat Removal were operable throughout the time that the 1B Core Spray loop was required to be operable. Corrective actions include a procedure revision to verify fill each time a mode of applicability is entered.
2542003003 | Quad Cities 1 | 11/17/2003 | 01/16/2004 | ML04023065 | <strong>Failure of Reactor Main Steam Relief Valve Actuator due to Vibration Following Failure of the Pilot Valve Vent line</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2003, with Unit 1 in refuel mode, it was determined that the 3B Main Steam relief valve actuator had excessive wear. Testing determined that the actuator would not have functioned. The actuator failure was determined to be due to increased vibrations as a result of failure of the pilot valve vent line. The pilot valve vent line failed due to cold spring force in the line. The safety significance of this event was minimal. The other three Main Steam relief valves and the combined Main Steam safety/relief valve were all operable. Corrective actions include replacement of the actuator and replacement of the pilot valve vent line, revision to the ERV installation procedure to include evaluation for cold spring, and installation of a tie-back modification to preclude ERV solenoid actuator failure due to excessive vibration.
2552003001 | Palisades | 01/15/2003 | 03/10/2003 | ML03077044 | <strong>Inoperable Steam Generator Low-Level Channels</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2003, at 2015 hours, with the plant in Mode 1, it was determined from a review of surveillance procedure basis information, that all four steam generator (SG) reactor protection system (RPS) low-level trip setpoints in each SG were set such that the trip could occur below the allowable value specified in Technical Specification (TS) 3.3.1. The SG low-level trip setpoints were declared inoperable. It was determined that this condition had existed since 1998. TS 3.3.1 requires four associated instrument channels, for the SG low-level RPS trip functions, to be operable in Modes 1 and 2, and in Modes 3, 4 and 5 when more than one full-length control rod is capable of being withdrawn and the primary coolant system boron concentration is less than refueling boron concentration. TS 3.3.1 does not provide a condition for four SG level instrument channels being inoperable. Therefore, TS 3.0.3 was entered. Nuclear Management Company, LLC, (NMC), requested enforcement discretion to extend the completion times in TS 3.0.3 by an additional 36 hours to avoid a plant shutdown. The Nuclear Regulatory Commission Staff verbally exercised discretion on January 16, 2003 at 0017 hours. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2552003002 | Palisades | 03/11/2003 | 05/06/2003 | ML03133035 | <strong>Incomplete Surveillance of Fuel Handling Area Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2003, in conjunction with performance of fuel handling area ventilation system (FHAVS) [VG] surveillance testing prior to the 2003 refueling outage, it was determined that the FHAVS was not being tested in full accordance with the ventilation filter testing program specified by Technical Specification (TS) 5.5.10. Review of the previous three years revealed that surveillance testing of the FHAVS specified by TS SR 3.7.12.1 had not fully met the ventilation filter testing program when the FHAVS was required to be operable during the April-May 2001 refueling outage. Pursuant to TS SR 3.0.1, failure to have met TS SR 3.7.12.1 is a failure to have metTS LCO 3.7.12 requirements for an operable FHAVS for core alterations and movement of irradiated fuel assemblies that occurred during the 2001 refueling outage. This occurrence is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications. The surveillance procedure was revised and the surveillance requirements successfully completed prior to entering the applicable conditions of TS LCO 3.7.12 for the 2003 refueling outage in March 2003.
2552003003 | Palisades | 03/25/2003 | 05/20/2003 | ML03148057 | <strong>Loss of Shutdown Cooling and Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On March 25, 2003, at 1116 hours, with the plant in Mode 6, a loss of offsite power occurred while installing a signpost. The signpost penetrated a buried conduit, damaging a control power cable associated with both offsite power feeds. As a result, the safety-related and non-safety related buses de-energized, which caused a loss of shutdown cooling flow. The emergency diesel generators started and loaded safety-related buses, as expected. An Alert was declared at 1126 hours. Shutdown cooling flow through the core was restored in approximately 20 minutes. The Alert was downgraded to an Unusual Event at 1231 hours. The Unusual Event was exited on March 27, 2003, at 1737 hours, when offsite power was fully restored. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(v)(B) as an event that prevented the fulfillment of the safety function of a system needed to remove residual heat, and in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in automatic actuation of the emergency AC electrical power system.
2552003004 | Palisades | 07/01/2003 | 08/28/2003 | ML03255035 | <strong>INOPERABLE TRAIN OF CONTAINMENT COOLING-CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2003, at 0414 hours, with the plant in mode 1, containment air cooler recirculation fan V-4A tripped unexpectedly and was declared inoperable, causing its associated containment cooling train to also become inoperable. Technical Specification (TS) 3.6.6, condition A, requires that with one or more containment cooling trains inoperable, restore the train(s) to operable status within 72 hours. Condition B of TS 3.6.6 requires that if condition A cannot be met, be in mode 3 within 6 hours and in mode 4 within 30 hours. Nuclear Management Company, LLC, requested, and was granted, enforcement discretion from the NRC to not enforce compliance with the required actions of condition B for up to an additional 100 hours to avoid a plant shutdown that would impose an unnecessary plant transient without a significant offsetting safety benefit. V-4A was subsequently returned to operable status on July 6, 2003, at 1404 hours. Since the 72-hour completion time of TS 3.6.6 condition A was exceeded, this occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2552003005 | Palisades | 08/14/2003 | 10/12/2003 | ML03288075 | <strong>Emergency Diesel Generators Start on Low Voltage Condition</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, at approximately 1607 hours EDT, with the plant operating at 100% power, an electrical power grid disturbance occurred, resulting in a momentary lowering of voltage on both 2400 volt safety related buses 1C and 1D. The reduced voltage on the 2400 volt buses caused both emergency diesel generators to start. However, the 2400 volt safety related buses remained energized from offsite power throughout the event . Local grid conditions stabilized within approximately five minutes. The diesel generators were secured at 1650 hours EDT. The plant remained at full power throughout the event. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of the emergency AC electrical power system.
2602003001 | Browns Ferry 2 | 02/24/2003 | 04/24/2003 | ML03115050 | <strong>Automatic Scram resulting from low reactor water level furing reactor cooldown</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2003, during the Unit 2 reactor cooldown evolution following its shutdown to begin the cycle 12 refueling outage, at 1117 hours CST an automatic actuation of the reactor protection system (RPS) occurred as a result of a low reactor water level condition. Reactor water level control was being transferred from operation of a single turbine driven reactor feed pump (RFP) to the motor-driven condensate/condensate booster pumps via the reactor feedwater startup level control valve. Difficulties in closing the RFP discharge valve and subsequent slow operation of the startup level control valve allowed reactor water level to drop slightly below the scram setpoint of 2 inches. The lowest reactor water level observed was 1.6 inches. Reactor water level was immediately recovered to the normal operating range by increased make-up flow through the feedwater startup level control valve. No control rod motion occurred as a result of the RPS actuation, since all control rods had previously been fully inserted via the manual scram which had commenced the earlier, planned reactor shutdown. All expected system responses were received, including the actuation of primary containment isolation system groups 2, 3, 6, and 8 due to the same low reactor water level condition. The cause of the event was off-normal RFP discharge valve operation combined with a slow response of the feedwater startup level control valve. Corrective actions include maintenance on the discharge valve, evaluation of the design of the control scheme, and additional operator training on the system response.
2602003002 | Browns Ferry 2 | 03/16/2003 | 05/13/2003 | ML03141065 | <strong>High Pressure Coolant Injection (HPCI) Inoperability Due to Loss of Turbine Speed Feedback Signal</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2003, Operations personnel were performing a surveillance procedure on the High Pressure Coolant Injection (HPCI) system. At 0525 hours CST, during conduct of this procedure, an automatic Primary Containment Isolation System (PCIS) Group 4 actuation occurred upon startup of the HPCI system. The isolation occurred because of an actual high HPCI system steam flow which was above the steam flow isolation setpoint of 200% nominal steam flow. This high flow rate was detected by sensors which input to the PCIS, and the PCIS logic actuated to isolate the system by closing the inboard and outboard HPCI steam line isolation valves. The isolation signal also resulted in a HPCI turbine trip. The HPCI turbine overspeed trip setpoint was not reached. Following the isolation event, a failed connector in the turbine speed feedback circuitry was identified and repaired. Subsequent to the necessary post-maintenance testing and completion of the appropriate surveillance procedures, the HPCI system was declared operable at 1405 hours CST on March 17, 2003. Connector failure due to age, excessive wear, and vibration was the event root cause. Corrective actions included repair of the connector, establishment of improved post-maintenance testing methods, and establishment of preventive maintenance activities to ensure connector integrity. Because this event involved a condition that could have prevented the fulfillment of the HPCI system safety functions of removing residual heat and mitigating the consequences of an accident, it is reportable in accordance with 10 CFR 50.73(a)(2)(v)(B) and (D).
2602003003 | Browns Ferry 2 | 03/26/2003 | 05/23/2003 | ML03156062 | <strong>Manual Scram of Unit 2 Resulting from the 2B Reactor Recirculation Pump Trip with OPRM Function Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2003, at 0018 hours, the 2A reactor recirculation pump tripped as a result of an invalid output ground fault indication in its variable frequency drive (VFD) . Operations entered into Technical Specification (TS) LCO 3.4.1 Action A. The reactor power was reduced to approximately 63 percent. At 0244 hours, the 2B reactor recirculation pump also tripped as a result of an invalid output ground fault indication in its VFD. Due to an inoperable Oscillation Power Range Monitor (OPRM) function, TS .3 .3 .1 .1-I was in effect at the time of the event . Abnormal Operating Instruction 2-AOI-68-1B implemented the conditions of TS 3.3.1.1-I, and required Operations personnel to manually scram the reactor when both reactor recirculation pumps tripped. The root cause of this event was spiking in the neutral voltage signals in the VFDs . The cause of the spiking has not been determined. Contributing factors were: lack of a pre-trip alarm, and knowledge about the VFD control function was not available to TVA Engineering personnel. Corrective actions include: (1) The ground fault trip function of the VFDs was changed to an alarm function, (2) Ground fault alarm setpoint was increased, (3) Investigation is ongoing to determine the cause of the voltage signal spiking, (4) Single point failure analysis design standard will be revised to address pre-trip alarms, and (5) Procedural guidance for post-modification testing (PMT) will be revised to address expectations of PMTs.
2602003004 | Browns Ferry 2, Browns Ferry 3 | 07/07/2003 | 09/05/2003 | ML03248097 | <strong>Cable Separations Design Error Related to Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>During review and validation of Appendix R-related calculations associated with the restart of BFN Unit 1, it was noted that some associated circuits of certain 4 kV electrical distribution boards and loads were not adequately evaluated in the Unit 2 and Unit 3 calculations. As physically configured, control power cables which affect power circuit breaker control are routed within 20 feet of the power cables being fed by these same breakers. The plant loads affected are the Unit 2 variable frequency drives and the Unit 3 recirculation motor-generator sets which provide power to drive the reactor recirculation pumps. As a result of this cable routing, fires in certain zones of the BFN plant could result in electrical faults on power cables which could not be de-energized by automatic breaker operation. Such faults could result in cable insulation fires being initiated in fire areas other than the area where the original fire occurred, thus creating an associated circuit of concern. The apparent cause was a historical design error. Compensatory measures were implemented in accordance with the fire protection plan. The plant will be modified to correct the condition.
2602003005 | Browns Ferry 2, Browns Ferry 3 | 08/10/2003 | 10/08/2003 | ML03290097 | <strong>Unplanned Start of DG A and DG B from Momentary Board Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2003, 4 kV Shutdown Bus (SB) 1 alternate supply breaker 1622 failed to automatically close when normal supply breaker 1612 was manually opened during electrical board switching activities. The operator performing the switching recognized that breaker 1622 had failed to close, and normal supply breaker 1612 was then reclosed. SB 1 was de-energized for less than 5 seconds . SB 1 is the normal power supply to 4 kV Shutdown Boards A and B, and relays on these boards sensed the undervoltage condition and automatically started Diesel Generators (DGs) A and B. Because of the actions by the operator to quickly reclose the normal supply breaker and restore off-site power to SB 1, and thereby to 4 kV Shutdown Boards A and B, it was not necessary for the DGs to connect to their respective boards . The temporary de-energization of 4 kV Shutdown Boards A and B resulted in the actuation of additional equipment. No turbine trip or reactor trip setpoints were approached. The root cause was the existence of a faulty breaker internal connection . Corrective actions include improved plant staff training and evaluation of the connection style for improvements.
2612003001 | Robinson 2 | 02/24/2003 | 04/24/2003 | ML03115003 | <strong>Failure to Complete Technical Specifications Required Action Within the Allowed Time</strong><br /><i>Abstract:&nbsp;</i>At 0000 hours on February 24, 2003, with the unit operating at full power, Technical Specifications (TS) Limiting Condition for Operation (LCO) Applicability requirement 3.0.3 was entered based on failure to meet the required actions of TS LCO 3.1.7. Upon discovery that the required actions of TS LCO 3.1.7 were not met, appropriate action was taken and the required actions were subsequently satisfied at 0043 hours. Safe operation of the plant was not affected by this event. The required action in effect at the time was associated with Condition A, Required Action A .1, which provides actions for inoperability of an analog rod position indication (ARPI). The cause of the event was determined to be operator error. The day-shift operator responsible for performing Required Action A.1 failed to recognize that the recorder had been halted during the February 23, 2003, 0800 hours observation and that this condition continued during the 1600 hours observation . Corrective actions for the event have been completed. The failure to meet the required actions associated with TS LCO 3.1.7 is a condition prohibited by the plant's Technical Specifications. Therefore, this condition is reportable based on 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition prohibited by the plant's Technical Specifications."
2612003002 | Robinson 2 | 06/05/2003 | 07/31/2003 | ML03213043 | <strong>Failure of Automatic Containment Ventilation Isolation During Containment Pressure Relief</strong><br /><i>Abstract:&nbsp;</i>At approximately 19:49 hours on June 5, 2003, during a planned source check of containment radiation monitor R-11 with a routine containment pressure relief in progress, the containment pressure relief isolation valves would not close automatically. The valves were closed by use of the control switch in the control room to stop the pressure relief of the containment at the time of the automatic isolation failure. The source check should have caused the valves to close automatically by the initiation of a containment ventilation isolation signal. The penetration was isolated at 20:47 hours by the use of a closed and de-activated automatic isolation valve. The cause of the failure was determined be a failure of the control switch that controls the valves for the containment pressure relief penetration. The control switch was repaired at approximately 14:13 hours on June 6, 2003, and the system was restored to operable status at that time. A planned and monitored gaseous release from the containment was in progress at the time of this event using the containment pressure relief system. No release limits were exceeded. If plant conditions had required isolation of the penetration, alarms and indications in the control room would have alerted the operators to the condition and the applicable operating procedures direct the operators to manually isolate the penetration. Investigation of the event determined that an inappropriate design change occurred in about 1980, which when coupled with the switch failure, caused the loss of safety function. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) and (D).
2612003003 | Robinson 2 | 11/19/2003 | 01/20/2004 | ML04022049 | <strong>Discovery of Two New Appendix R Safe Shutdown Vulnerabilities</strong><br /><i>Abstract:&nbsp;</i>During the development and review of an Engineering Change involving Appendix R Analysis, two postulated fire-induced transient conditions were identified. These conditions if not mitigated, could result in an unrecoverable condition. If a postulated fire were to occur causing specific circuit damage, operator actions to mitigate the transient would have to be taken in less than 10 minutes from the onset of circuit damage. Based on current analysis criteria, operator mitigating actions taken outside the Control Room and required in less than 10 minutes are not used due to the limited amount of time that the Control Room Staff would have to detect an equipment malfunction, determine its effect, and take mitigating actions. The fire-induced transient conditions identified include: 1) a postulated fire event that causes the spurious operation (closing) of the Volume Control Tank outlet isolation valve and loss of function for the Refueling Water Storage Tank Emergency Makeup to Charging Pump Suction isolation valve, and 2) a postulated fire event that causes the operation of both Pressurizer Power Operated Relief Valves concurrently. These transient conditions could occur due to a fire of sufficient magnitude in one of the following two fire zones: Fire Zone 19. Unit 2 Cable Spread Room. or Fire Zone 20, Emergency Switchgear Room. Immediate corrective action included revising plant procedures to direct prompt operator actions. Long-term corrective actions will be determined and planned for upcoming refueling outages. This event is being reported in accordance with 10 CFR50.73(a)(2)(v)(A) and (B).
2632003001 | Monticello | 03/13/2003 | 05/11/2003 | ML03140064 | <strong>Degraded Fire Barrier Penetration Discovered During a Walkdown</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2003 during a walkdown of fire barrier penetration FZ-4900 in the upper 4KV room it was discovered that a portion of a penetration seal was degraded allowing the upper and lower 4KV rooms to communicate with each other. The barrier was declared inoperable and a continuous fire watch was established. In accordance with 10 CFR 50.72(b)(3)(ii), an 8-hour event notification was made. The Updated Fire Hazards Analysis was reviewed to identify other locations where gypsum board assemblies are used as penetrations. No other penetrations were found to be inoperable as a result of this walk-down. On March 15, 2003 the barrier was repaired and declared operable.
2652003001 | Quad Cities 2 | 01/09/2003 | 03/10/2003 | ML03077068 | <strong>Failure to Reset Residual Heat Removal Injection Valve Containment Isolation Signal Due to Inadequate Procedural Development and Review</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2003, at 0540 hours, with Unit 2 in Mode 1 at 100% power, a Residual Heat Removal (RHR) injection valve failed to stay open during a valve test. It was determined that a containment isolation signal for that valve was sealed in. The isolation signal was reset and the valve was satisfactorily tested. The isolation signal for the injection valve in the other Unit 2 RHR loop was also found sealed in, and was reset. The 'seal in' condition for these relays is not annunciated nor are there any other secondary indications available for monitoring this portion of the RHR logic. The root cause of the event was inadequate procedural development and review. A revision made to a logic test procedure in 1999 failed to ensure that the isolation signal was reset at the end of the test. The logic test had last been performed on December 18, 2002. Corrective actions included revising the procedure to verify that the isolation signal has been reset. The safety significance of this event was minimal. Although the injection valves would not operate automatically, the isolation signal could be reset from the control room. Also, the Core Spray system was operable and capable of post-accident low pressure injection.
2652003002 | Quad Cities 2 | 04/16/2003 | 06/12/2003 | ML03175061 | <strong>Self-Actuation of Main Steam Relief Valve Due to Excessive Leakage Through Pilot Valve Seat</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2003, at 1322 hours, the Unit 2 3B Main Steam Relief Valve (RV) selfactuated. The operators initiated the appropriate procedures for an open RV, including initiation of suppression pool cooling, a manual reactor scram, removal of the control power fuses to the 3B RV, and closure of the main steam isolation valves to slow the reactor cooldown rate. At 1359 hours, the suppression pool temperature reached 110F and an Alert was declared in accordance with the Exelon Emergency Plan. The Alert was exited at 2251 hours. The safety significance of this event was minimal. The opening of the 3B RV did not affect the capability of the relief valves to protect against high reactor pressure. At the time of the event, the Emergency Diesel Generator was out of service for planned maintenance. All other mitigating systems were available. Therefore, both emergency and non-emergency sources of injection to the vessel were available to make up for the coolant being relieved through the RV to the suppression pool. The root cause was excessive leakage past the 3B RV pilot valve seat, which allowed the RV closure force to diminish and the RV to open. Corrective actions included replacement of the 3B RV, improvements in RV tailpipe temperature monitoring, and removal of the requirement to perform on-line test actuations of the RV.
2652003003 | Quad Cities 2 | 03/24/2003 | 08/18/2003 | ML03238055 | <strong>Low Pressure Coolant Injection Differential Pressure Instrument Inoperable Due to Misposition of Instrument Valve</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2003, a differential pressure instrument isolation valve was found isolated, rendering the instrument inoperable. The other three differential pressure switches that provide the one-out-of-two-twice logic to direct injection of the Low Pressure Coolant Injection system to the intact reactor recirculation pipe during a loss of coolant event were verified to be operable. The surveillance in progress was completed, the switch was tested satisfactorily and the manifold valves were returned to the in-service position. A work history review identified that the valve was left closed following a March 24, 2003, surveillance. A search of the work history involving the individuals that performed the March 24 2003, surveillance did not identify any discrepancies. The safety significance of this event was minimal. The remaining three switches were operable and capable of providing the required logic signal. Therefore, there was no loss of safety function associated with this event. The root cause for this event is a breakdown in the use of human performance tools. Corrective actions include a revision to Human Performance training and development of a human performance improvement program for the Instrument Maintenance Department.
2652003004 | Quad Cities 2 | 06/12/2003 | 08/22/2003 | ML03246117 | <strong>Reactor Shutdown Due to Degraded Reactor Steam Dryer as a Result of Increased Steam Velocities from Extended Power Uprate</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2003, after evaluation of indications of a degraded steam dryer, Unit 2 was shut down to allow inspection and repair of the steam dryer. On June 12, 2003, inspections identified cracking in the steam dryer. Failure analysis and repairs to the Unit 2 dryer were completed over the following 18 days and the reactor was returned to service. The root cause of the failure of the steam dryer has been determined to be the high cycle fatigue cracking caused by the increased vibration loadings created by high steam velocities. The safety significance of this event was minimal. The dryer is a non-safety related component whose only safety function is to remain intact such that it will not prevent a safety related component from performing its function. At the time of discovery, all dryer components remained constrained within the dryer/separator envelope. This report is being submitted as a voluntary report.
2652003005 | Quad Cities 2 | 07/17/2003 | 09/15/2003 | ML03267113 | <strong>Technical Specification Allowable Value Exceeded for Main Steam Flow Switches Due to Inadequate Drift Allowance Used in Setpoint Calculation</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2003, at 1059 hours, during performance of the Unit 2 Division II Main Steam Line High Flow Switch Calibration and Functional Test, two main steam flow instruments were determined to have as-found setpoints that exceeded the Technical Specification (TS) Allowable Value. The instruments were calibrated to be within the TS allowable range. A total of 16 switches, four per steam line, are installed on the Unit 2 Main Steam Lines. The switches feed into the Primary Containment Isolation System, with one out of two twice' logic. The root cause of this event was the use of inadequate drift allowance in the associated setpoint calculation. The safety significance of this event was minimal . The instruments would have provided the trip signal within the analytical values assumed in the accident analysis. Corrective actions include a drift analysis and replacement of the instruments with an improved model.
2662003001 | Point Beach 1, Point Beach 2 | 04/06/2003 | 06/05/2003 | ML03164011 | <strong>As Found Condition of Degraded Grid Voltage Relays Not Within Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>This report discusses the discovery that the Point Beach Nuclear Plant was operated for an extended period with the set points for the degraded voltage relays less than the Technical Specification setting. This was a condition prohibited by the Technical Specifications and is reportable under 10 CFR 50.73. The set points were incorrectly set because the surveillance procedures for the relays had been revised to specify a test instrument with an accuracy tolerance greater than the accuracy tolerance of the test instrument assumed in the set point calculation. The cause of this event was that the Nuclear Management Company (NMC) staff did not adequately consider and evaluate the differences in accuracy tolerance of the measuring instruments. Upon identification of the potential for this event, the surveillances for the degraded grid relays were declared to be missed and the surveillances were redone using the proper test Instruments. Although all of the degraded grid voltage relay set points were found to be less than the Technical Specification limit of 3937 volts, only two of the 12 relays were found with set points potentially less than the analytical limits. These relays were both on the 1A-05 bus. The limiting equipment potentially impacted by these relays were an emergency diesel generator exhaust fan and a standby swing battery charger. A PRA risk assessment of the delay in performing the degraded voltage relay surveillance determined that the surveillance delay was not risk significant.
2662003002 | Point Beach 1 | 07/15/2003 | 09/12/2003 | ML03267106 | <strong>Reactor Trip Due to Rod Drive Motor-Generator Set Failure</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2003, at approximately 1340 CDT, Point Beach Nuclear Plant (PBNP) Unit 1 experienced an automatic reactor trip from full power followed by a loss of Feedwater/Turbine Trip due to the reactor trip and main feedwater regulating valve closure. The cause of the trip was a failure of the 1G-06 Control Rod Drive Motor Generator set. The first out indication for the trip was an over temperature delta T signal. This trip also resulted in an automatic actuation of the Auxiliary Feedwater System. An operator was dispatched to the Unit 1 Rod Drive Room and identified smoke coming from the Voltage Regulator cabinets. Actions were taken to de-energize both Rod Drive Motor Generator (MG) Sets. Operators continued with follow-up actions to stabilize the unit in Mode 3. An event notification (EN# 39996) was made to the NRC at 1429 CDT. An investigation concluded that the voltage regulator failure was caused by the failure of a surge suppresser component in the power and feedback circuit. The 1G-06 MG set was repaired and a modification to the circuitry to improve voltage regulator reliability was completed in both the 1G-06 and 1G-07 motor generator sets. Systems and equipment necessary to mitigate the consequences of this equipment failure and subsequent reactor trip functioned as designed and the plant was maintained in a stable hot shutdown condition during the troubleshooting and repair of 1G-06. The safety and welfare of the public and the plant staff was not impacted by this event and the safety significance was minimal.
2692003001 | Oconee 1, Oconee 2, Oconee 3 | 06/04/2003 | 08/04/2003 | ML03225012 | <strong>Design Oversight Results in Appendix R Control Cable Separation Issue</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2003, with Oconee Units 1 and 2 operating in Mode 1 at 100% Rated Power and Unit 3 in Mode 5 (start-up after refueling), an engineering evaluation identified a cable routed contrary to 10CFR 50, Appendix R separation criteria. Consequently, a low probability hot short due to a hypothetical fire could spuriously operate any one of six (6) valves in each Unit . Depending on the location of the design basis fire, one, two, or all three Oconee Units could be affected. This was considered a previously unanalyzed condition. A fire watch patrol has been established on a once per 6 hour frequency and will remain in place until appropriate permanent corrective actions are in place to mitigate this condition. The apparent cause of this event is an unanalyzed condition resulting from a historic design deficiency. Engineering risk assessment concludes that the likelihood of the actual spurious actuation of these valves is low. This event is considered to have minimal safety significance with respect to the health and safety of the public.
2692003002 | Oconee 1 | 09/23/2003 | 10/27/2003 | ML03309048 | <strong>Apparent Reactor Coolant System Leakage from Three Reactor Vessel Head Penetrations</strong><br /><i>Abstract:&nbsp;</i>Oconee Nuclear Station Unit 1 (ONS-1) entered its scheduled end-of-cycle 21 refueling outage on September 20, 2003. On September 23, 2003, a visual inspection of the bare reactor vessel head was performed while bolted to the vessel in order to determine if reactor coolant system leakage had occurred during the previous operating cycle. This bare head visual inspection was performed looking through the nine access ports in the service structure support skirt on the reactor vessel head. Results of the visual inspection identified two (2) control rod drive mechanism (CRDM) nozzles and one (1) thermocouple (T/C) nozzle that exhibited similar leakage characteristics as was found from previous nozzle inspection and repair campaigns. Consequently, these nozzles were conservatively classified as leaking. The total leakage from the nozzles did not exceed Technical Specification limits for unidentified reactor coolant system inventory loss. At no time during the operating cycle did the reactor building or area radiation alarms actuate as a result of this event. The small amount of boric acid deposits observed around the nozzles caused no visible head material loss (wastage) from erosion or corrosion. The apparent root cause of the CRDM nozzle leaks is most likely primary water stress corrosion cracking. The minor leakage observed around the previously repaired T/C nozzle is most likely attributed to a welding defect. This reactor vessel head will be retired from service and replaced with a new reactor vessel head prior to unit restart. For this event, the overall safety significance of this event was minimal and there was no actual impact on the health and safety of the public.
2712003001 | Vermont Yankee | 09/27/2003 | 11/19/2003 | ML03332005 | <strong>Reactor Shutdown Completed for an Increase in Unidentified Leakage Located Inside Primary Containment from a Reactor Head Vent Valve Packing Gland Due to Lack of Sufficient Documented Guidance for Repacking Manual Valves</strong><br /><i>Abstract:&nbsp;</i>On 09/27/03 at 0440 with the reactor at 100 percent power, a change in drywell temperature led operators to the discovery of an increase in unidentified leakage inside the Primary Containment. The leakage was determined to have risen by 3.6 gallons per minute (gpm), exceeding the Technical Specification (TS) limit for an increase in unidentified reactor coolant leakage of greater than 2 gpm within a 24 hour period [TS 3.6.C.1.b.]. As directed by the TS Limiting Conditions for Operation, an orderly shutdown was initiated to place the reactor in a cold shutdown condition within twenty-four hours. On 09/28/03, a walk-down of the drywell identified that valve V2-19 was the source of the leakage. V2-19 is a two inch, manually operated, normally open globe valve, located in the reactor head vent piping that is closed only during refuel outages. Visual inspection indicated that the valve was leaking past the stem packing. An investigation revealed that the gland nuts were hand-tight, thereby indicating minimal radial load on the packing material. The packing volume was visually intact and V2-19 was not back-seated. The primary cause of this event was determined to be inadequate document provisions that caused improper assembly of the valve packing while performing preventative maintenance during November of 1999. Specifically, the packing procedure for this valve did not provide complete instructions for the consolidation of packing during installation. This event posed no increased risk to the health and safety of the public due to the relatively small size of the leak as compared to the analyzed event for a Design Basis Loss of Coolant Accident.
2722003001 | Salem 1 | 05/23/2003 | 12/01/2003 | ML03343034 | <strong>Plant Operation for Greater Than 72 Hours With 13 AFW Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2003, during the performance of surveillance testing on the 13 Turbine Driven Auxiliary Feedwater (TDAFW) pump {BA/-}, the TDAFW pump tripped. During the start of the 13 TDAFW pump, the steam admission valve (1MS132) valve popped open. The popping open of the 1MS132 valve caused an in rush of steam and mechanical agitation (shaking and vibration) of the steam line. This mechanical agitation resulted in the unlatching of the steam trip valve (1MS52) for the 13 TDAFW pump causing the pump to trip. The cause of the 13 TDAFW pump trip is attributed to the popping open of the 1MS132 steam valve due to the split block being loose, which created a mechanical agitation of the steam line that led to the unlatching of the 1MS52 trip valve. Corrective actions consist of the tightening of the split block for the 1MS132 valve and satisfactory re-test of the valve, and changes to the maintenance procedure for the MS132 valves regarding the tightening of split blocks. This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "any operation or condition which was prohibited by the plant's Technical Specification" and 10CFR50.73(a)(2)(v)(B) & (D), "any event or condition that could have prevented the fulfillment of the safety structures that are needed to : remove residual heat and mitigate the consequences of an accident."
2722003002 | Salem 1 | 07/29/2003 | 09/24/2003 | ML03275142 | <strong>Reactor Trip Due to Turbine Trip Caused by a 500KV Switchyard Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On July 29, 2003 at 1329 Salem Unit 1 reactor tripped automatically due to generator protection and turbine trip. The cause of this event was an indicated ground fault on the 500KV 1-5 breaker which caused protective relaying to actuate which resulted in isolating the Unit 1 generator causing a generator and turbine trip which lead to a reactor trip. In addition, loss of bus section 1 caused the loss of the 14 station power transformer (SPT) which was feeding the 1B and 1C vital busses. The 1B and 1C vital busses transferred as designed to the 13 SPT, which was feeding the 1A vital bus. In addition, three of the Circulating Water (CW) pumps transferred to the 13 SPT as designed. As a result of the event, the 4KV vital bus voltages dropped below the second level undervoltage setting of 95.1%. Voltage on the Salem Unit 1 4KV vital busses did not recover to the reset setpoint before the relay timeout caused the relay logic to separate the vital busses from offsite power. The Emergency Diesel Generators (EDG) started and loaded as expected and all systems responded as designed. Salem Unit 2 responded as expected throughout the transient. An Unusual Event (UE) was declared at 1401 due to a loss of offsite power for greater than 15 minutes to the vital busses. The UE was exited at 2201 after restoring normal power to the Unit 1 vital busses. Troubleshooting of the 1-5 breaker "Breaker Failure Scheme" circuitry found a shorted cable. The "Breaker Failure Scheme" circuitry was repaired using spare conductors to restore the 1-5 breaker to service. The automatic transfer of Circulating Water busses was temporarily disabled to permit plant restart.
2722003003 | Salem 1 | 10/15/2003 | 12/05/2003 | ML03351008 | <strong>Shutdown Required By Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2003, at approximately 0316, the Salem Unit 1 nuclear control operator (NCO) (licensed operator) noticed that the 14BF19 (main feedwater regulating valve) {JB/FCV} was not moving with changing demand (both in automatic and manual). The valve appeared to be approximately 71 % open. Initial local inspection of the valve and prior experience indicated that the problem with the valve was the actuator and not the feedwater isolation function, thus the valve was still operable. Further investigation confirmed the valve to be immovable. Technical Specification 3.0.3 was entered and a plant shutdown was initiated in accordance with procedures. After the plant shutdown, the valve was opened and inspected. Foreign material was found lodged between the valve plug and the inside diameter of the cage. This resulted in the valve not being able to move. As a result of the inspection a level one condition report was initiated to evaluate the root cause of this and other issues with the foreign material control program. The level one root cause is in progress and corrective actions will be taken as necessary to enhance the foreign material control program. An extent of condition evaluation concluded that the other feedwater valves were not affected. This event is reportable per the requirements of 10 CFR 50.73 (a)(2)(i)(A), completion of any nuclear plant shutdown required by the plant's Technical Specifications.
2722003005 | Salem 1 | 12/21/2003 | 03/24/2005 | ML05096049 | <strong>Condition Prohibited by Technical Specifications : Auxiliary Building Ventilation System Fire Damper Found Out of Position 5. EVENT DATE 6. LER NUMBER T. REPORT DATE B. OTHER FACILITIES INVOLVED</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2004, as part of a troubleshooting activity to determine the cause of high differential pressure in Salem I Auxiliary Building, it was identified that two fire dampers, 1ABF13 and 1ABF15, inside the ECCS room flow damper exhaust ductwork were found closed. Additionally, High Energy Break Analysis (HEBA) excess 1ABS8 was found dosed. Further review indicated that this condition might have existed since December 21, 2003when high differential pressure was first noted. This condition is contrary to Technical Specification 3.7.7.1. The above dampers were subsequently reopened to their normal open position and the airflows were returned to normal.There were no actual safety consequences associated with this event.This is being reported under the requirement of 10CFR50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications and 1 OCFR50.73(a)(2)(v)(D), any event or condition that at the that are time of discovery could have prevented the fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident.
2752003001 | Diablo Canyon 1 | 10/09/2003 | 12/04/2003 | ML03344041 | <strong>Technical Specification 3.8.1, Action B.1, Not Met Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2003, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.8.1, "AC Sources - Operating," Action B.1, was not met when operators failed to perform an offsite circuit check within one hour upon declaring an emergency diesel generator inoperable to support exhaust stack slide bearing replacement. After the shift turnover briefing following completion of the slide bearing replacement, the unit shift foreman (SFM) determined that the conditional surveillance had been required and concluded two independent circuits between the off-site transmission network and the on-site distribution system were operable. The root cause of the event was personnel error. The Unit 1 SFM did not recognize the necessity to perform the conditional surveillance nor did he adequately communicate the change in plant status with the control room crew. Additionally, recent changes in the work control process placed work authorization responsibilities with the work control shift foreman, including the responsibility to communicate changes in plant status to the Unit 1 SFM. Corrective actions to prevent recurrence include briefing all operating crews on effective control room communication and modifying the TS tracking module to require a sign-off that any required conditional surveillances are being implemented upon declaring equipment inoperable.
2772003001 | Peach Bottom 2 | 04/12/2003 | 05/23/2003 | ML03149037 | <strong>Outboard Main Steam Isolation Valve Instrument Air Line Failure Results in Scram on Reactor High Pressure</strong><br /><i>Abstract:&nbsp;</i>At 1847 hours on 4/12/03, Unit 2 scrammed as a result of a high reactor pressure condition. The high pressure condition resulted from the closure of the 'D' Outboard Main Steam Isolation Valve (MSIV). The MSIV closed as a result of a failed instrument air line that provides control air to the valve control manifold. Primary Containment Isolation System (PCIS) Group II and III isolations were received, as expected, as a result of reaching the Level 3 reactor water level set point. There were no significant equipment issues that adversely affected Operations personnel response to the event. The plant was maintained in the hot shutdown condition (Mode 3) until the mode switch was placed in the Startup position (Mode 2) on 4/13/03 at 1545 hours. Analysis of this event determined that the event was not risk significant. The cause of the broken air line is primarily due to less than adequate supporting of the instrument air line that allowed the instrument air line to experience a fatigue failure. The instrument air line was replaced and additional supports were added to the line. Supports for other similar instrument lines on other Outboard MSIVs were upgraded. Similar instrument lines on Unit 3 Outboard MSIVs are planned to be upgraded. Other pneumatic lines will be inspected for enhancements. There were no previous similar events.
2772003002 | Peach Bottom 2, Peach Bottom 3 | 11/28/2002 | 07/17/2003 | ML03212055 | <strong>Condition Prohibited by Technical Specifications Due to Inoperability of Standby Gas Treatment Filter Train</strong><br /><i>Abstract:&nbsp;</i>On 5/28/03 at approximately 1100 hours, licensed operators were notified that approximately 4 inches of water (~170 gallons) was discovered in the bottom of the 'A' Standby Gas Treatment (SBGT) filter plenum during the performance of an annual surveillance. Further evaluation determined that a condition prohibited by Technical Specifications existed since this water intrusion resulted in the 'A' SBGT subsystem being inoperable between the worst-case time period of 11/21/02 until 12/18/02. The Technical Specification Required Action times for an inoperable subsystem were exceeded on 11/28/02. The water in the 'A' SBGT filter plenum was promptly removed subsequent to discovery and appropriate filters were replaced. There were no actual safety consequences as a result of this condition. The 'B' SBGT subsystem remained operable throughout the worst-case time period that the 'A' SBGT subsystem was inoperable. The cause investigation concluded that the most probable cause is human error that caused water intrusion into the 'A' SBGT plenum during the performance of a fire deluge system surveillance test for the 'A' SBGT filter plenum on 11/21/02. Surveillance tests for SBGT fire system deluge functionality did not contain adequate concurrent verification by a second operator and will be revised. There were no previous events identified.
2772003003 | Peach Bottom 2 | 07/22/2003 | 09/16/2003 | ML03273055 | <strong>Generator Bus Ground Caused by Foreign Material Results in Automatic Scram</strong><br /><i>Abstract:&nbsp;</i>At approximately 1345 on 7/22/03, Unit 2 automatically scrammed as a result of a fast closure of the Main Turbine Control Valves. This was a result of a Main Generator lockout due to a generator neutral high voltage ground fault. Control rods fully inserted and Primary Containment Isolation System (PCIS) Group II / III isolations were received, as expected. At approximately 1358 hours, a Main Steam Line Isolation valve closure occurred due to a Group I PCIS actuation. The actuation was a result of high area temperatures in the vicinity of the main steam lines caused by a loss of normal ventilation due to the Group II / III isolations. A reactor scram signal was also received as a result of the Group I isolation. The Reactor Core Isolation Cooling (RCIC) system controller was observed to have an inappropriate response while controlling reactor water level in that the RCIC system flow was oscillating (a condition that was subsequently determined to be a Technical Specification inoperable condition). A reactor scram occurred at approximately 1615 hours during transition to reactor level control using the feedwater / condensate system. The generator bus fault occurred when foreign material in the isophase bus duct came in contact with a bus conductor. This foreign material was identified as remnants of failed isophase bus cooling fan belts that had previously failed. The foreign material was removed, thereby resolving the bus ground. Design changes are in progress to add isophase bus fan belt debris guards.
2772003004 | Peach Bottom 2, Peach Bottom 3 | 09/15/2003 | 11/07/2003 | ML03323032 | <strong>Units 2 and 3 Automatic Scrams Resulting from an Off-Site Electrical Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>At approximately 0132.on 9/15/03, Units 2 and 3 automatically scrammed and received Primary Containment Isolations as a result of an interruption of power to the Reactor Protection System (RPS) and the Primary Containment Isolation System (PCIS) logic circuits. This interruption of power was caused by a brief loss of two, of the three PBAPS off-site power sources caused by an electrical grid disturbance approximately 35 miles away from the site. The disturbance was the result of failure of off-site protective relaying during a lightning storm. The Emergency Diesel Generators (EDGs) started and provided on-site power. On Unit 3, one Safety Relief Valve (SRV) remained Open, after actuation. It subsequently closed, when reactor pressure was reduced. At approximately 0235 hours, the E-2 EDG tripped on low, jacket coolant pressure. A discretionary Unusual Event was declared by the Shift Manager as a result of the E-2 EDG trip combined with the off-site grid concerns. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems were used to provide reactor water level control. Safety Relief Valves were used for reactor pressure control. The Suppression Pool cooling system was used for containment heat removal. Normal power was restored to the on-site emergency busses and the Unusual Event was terminated at 1046 hours. The cause of the event was due to less than adequate maintenance and testing on protective relaying on the off-site electrical distribution system. Appropriate maintenance, testing and other upgrades are being pursued.
2772003005 | Peach Bottom 2 | 12/10/2003 | 01/30/2004 | ML04044031 | <strong>Loss of High Pressure Coolant Injection System Function as a Result of Less Than Adequate Check Valve Condition</strong><br /><i>Abstract:&nbsp;</i>On 12/10/03, at approximately 1040 hours, during the performance of a routine Logic System Functional Test for the High Pressure Coolant Injection (HPCI) system, Operations personnel detected an unexpected condition when a Suppression Pool high water level alarm was received. Based on engineering reviews, it was subsequently determined at approximately 1800 hours that the HPCI check valve 61 in the system suction path from the Suppression Pool was not properly closed. This resulted in the HPCI system possibly not being capable of performing its intended restart design function for certain design bases events. For these events, with HPCI aligned to the Suppression Pool, the HPCI system piping could be voided while the system is not operating resulting in water hammer conditions if the HPCI system would need to restart after performing its design function. There were no actual safety consequences or water hammer events associated with this event. The cause of the HPCI suction check valve 61 not closing properly was attributed to the valve disc not seating properly. This was caused by excessive clearances of certain check valve internal components due to maintenance procedures not containing adequate criteria concerning component clearances and alignment of the valve disc to the seat. In body repairs were made to the HPCI Suction Check Valve 61 and HPCI was returned to a fully operable condition by approximately 1445 hours on 12/12/03. Maintenance procedures will be upgraded.
2782003001 | Peach Bottom 3 | 05/05/2003 | 07/01/2003 | ML03190004 | <strong>Loss of Capability of the Unit 3 10CFR 50 Appendix R Alternate Control Station</strong><br /><i>Abstract:&nbsp;</i>On 5/14/03, at 0410 hours, an operability evaluation performed by a shift supervisor determined that the Unit 3 High Pressure Coolant Injection (HPCI) Alternate Control Station (ACS) for Fire Safe Shutdown was inoperable. This inoperability was due to the fact that multiple instruments were de-energized as a result of a failed wire on a power supply. This resulted in Operations personnel not having the capability to implement actions required for plant safe shutdown from the ACS if a 10CFR 50 Appendix R fire were to occur. The HPCI ACS is required if a significant fire were to occur in the Cable Spreading Room, Main Control Room or the Main Control Room Fan Room. Repairs to the broken wire were promptly made and the ACS was restored to an operable status on 5/14/03 by 1030 hours. There were no actual safety consequences as a result of this event. Investigation determined that the broken wire occurred during previous maintenance activities on 5/5/03. Further review of the post maintenance testing performed on 5/6/03 revealed that the I&C technicians involved with the work did not perform sufficient post maintenance testing as required. The involved I&C technicians have been counseled and expectations for strict compliance with the work order requirements have been reinforced. There were no previous similar events identified.
2802003001 | Surry 1 | 01/14/2003 | 03/14/2003 | ML03083037 | <strong>Manual Reactor Trip Due to Degraded Conditions on "C" Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>At 0137 hours on January 14, 2003, Surry Unit 1 Reactor was manually tripped from 100% power due to degrading conditions on the Reactor Coolant Pump (RCP) 'C'. The operating crew received alarms indicating elevated shaft vibrations with the RCP 'C' motor followed by indications of increased lower radial bearing temperatures. In accordance with approved procedures, the operating crew manually tripped the reactor and secured the RCP 'C'. Automatic actuations occurred as expected, including Turbine Trip by Reactor Trip, Auxiliary Feedwater initiation, Main Generator Trip, and AMSAC initiation. The motor lower radial bearings on RCP 'C' were replaced and the unit was returned to service. A root cause evaluation was initiated to determine the cause of the high bearing temperatures and high shaft vibrations and to address actions to preclude recurrence. This is a reportable event pursuant to 10CFR50.73(a)(2)(iv)(A) since the event resulted in manual actuation of the reactor protection system and the initiation of the Auxiliary Feedwater system.
2802003002 | Surry 1 | 01/25/2003 | 11/25/2003 | ML03336065 | <strong>Manual Steam Generator Level Control Results in Power Ascension Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2003, at 0700 hours a Unit 1 automatic reactor trip occurred during startup at 27% reactor power due to low-low level in "B" steam generator (SG). Automatic actuations occurred as expected, including Turbine Trip by Reactor Trip, and Main Generator Trip. The Turbine Driven Auxiliary Feedwater Pump (TDAFWP) started automatically, but tripped on overspeed. A root cause evaluation (RCE) determined that the difficulties with manual control of SG water levels at low power and the subsequent Unit 1 reactor trip were due to inadequate modification of the main feedwater regulating valves. An RCE for the overspeed trip of the TDAFWP was performed, however no single root cause was identified. The probable causes were inadequate margin between the overspeed trip setpoint and nominal speed, sluggish response of the governor at low temperatures, steam supply line water condensation, and inability of the governor valve to go fully closed. The TDAFWP governor was replaced and post maintenance testing completed on January 28, 2003. Training was provided to the operating shift responsible for the unit restart. Unit 1 was restarted and achieved 100% reactor power on January 31, 2003 at 0755 hours. This report is being submitted in accordance with 10CFR50.73(a)(2)(iv)(A).
2802003003 | Surry 1 | 06/13/2003 | 08/11/2003 | ML03230047 | <strong>Control Rod Electrical Connector Pin Defect Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2003 at 0535 hours a Unit 1 manual reactor trip occurred while the reactor was critical during startup physics testing. The manual reactor trip was initiated due to a control rod misalignment that resulted from an electrical connector pin which was partially recessed and not making a good connection. At the time of the manual trip, the reactor was in startup physics testing below the point of adding heat, and reactor power was approximately 1 x 10-8 amps. The operating staff acted promptly and appropriately to stabilize the unit at hot shutdown at 0555 hours. All required systems functioned as designed during the trip. Following repositioning of the connector pin, post maintenance testing and startup physics testing were completed satisfactorily. The unit was taken critical and placed on line on June 17, 2003 at 0419 hours. The male connector pins for the movable, lift and stationary coils for all control rod drive mechanisms on Unit 1 and Unit 2 will be inspected, and repaired as necessary, no later than the next refueling outage for each unit. This report is being submitted in accordance with 10CFR50.73(a)(2)(iv)(A) for the manual trip of the reactor.
2802003004 | Surry 1, Surry 2 | 09/18/2003 | 12/30/2003 | ML04014033 | <strong>Manual Reactor Trips Due to Loss of All Circulating Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2003, with Surry Power Station Unit 1 at 79% reactor power and Unit 2 at 100% reactor power, a manual reactor trip was initiated on Unit 1 at 1728 and on Unit 2 at 1732 due to the loss of the '1 G' and '2G' buses which supply power to all eight circulating water pumps for both units. Automatic actuations occurred as expected, including Turbine Generator Trip, Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) initiation, and Auxiliary Feedwater (AFW) initiation. As a result of the loss of the circulating water (CW) pumps, the emergency service water (ESW) pumps weree started. After start, 2 of the 3 ESW pump diesel engines tripped on cooling water high temperature. The ESW pumps were restarted successfully. At 1845, the 2G bus was energized, CW pumps were started and the ESW pumps were secured. Root cause evaluations determined the cause of the loss of all AC electrical power to the CW pumps and tripping of the two ESW pumps were design issues. There were no significant safety consequences or implications for this event. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) since the event resulted in manual actuation of the reactor protection system and the initiation of the AFW system and 10CFR50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications.
2802003005 | Surry 1 | 11/03/2003 | 12/17/2003 | ML03364049 | <strong>Unanalyzed Condition Related To Loss of RCP Seal Cooling During an Appendix R Fire Event</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2003, it was determined that assumption of the RCP seal leakage model from WCAP-1 5603, Rev. 1-A would result in the inability to maintain pressurizer level during plant shutdown, thus not satisfying 10CFR50 Appendix R. This condition could result from a loss of RCP seal cooling due to postulated fire damage in certain Unit 1 emergency switchgear room fire scenarios. The charging pump cross-connect was considered inoperable with respect to Appendix R due to these circumstances, and the appropriate actions required by the Technical Requirements Manual (TRM) were entered. An eight-hour non-emergency report to the NRC was made in accordance with 10CFR50.72(b)(3)(ii)(B). Along with establishing the TRM-required fire watch, additional interim measures were implemented on November 4, 2003. A justification for continued operation, which reestablishes compliance with Appendix R, was implemented on November 10, 2003 and will remain in place until permanent resolution is implemented. This condition occurred because WCAP-15603, Rev. 1-A was recognized as being appropriate to consider for probabilistic risk assessment modeling, but was not viewed as applicable to Appendix R analyses. There were no significant safety consequences or implications associated with this condition. This report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(B).
2802003006 | Surry 1, Surry 2 | 12/12/2003 | 02/09/2004 | ML04048059 | <strong>Steam Generator AFW Isolation Unanalyzed Condition from Original Design</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2003, at 0900 hours with Units 1 and 2 at 100% power, it was determined that for both Unit1and Unit 2, an unanalyzed condition existed with the alignment configuration of the normally open auxiliary feedwater (AFW) motor operated valves (MOVs). The AFW system isolation function assumed by the accident analysis was not capable of being performed during a steam generator tube rupture event concurrent with the loss of one emergency bus. The root cause for this condition was design configuration/ analysis in that the unanalyzed condition was not considered during initial plant design. Unit 1 and Unit 2 AFW systems were declared inoperable at 1119 hours on December 12, 2003 and a 6-hour clock to hot shutdown was entered for both Units. It was determined that maintaining four of the six AFW MOVs closed and two AFW MOVs open would return the unit to an analyzed condition. When the AFW MOVs were placed in this alignment, both Units 1 and 2 exited the 6-hour clock at1341 hours on December 12, 2003. There were no significant safety consequences associated with this condition. Stop check valves will be installed to prevent back flow though the AFW MOVs. This report is being submitted in accordance with 10CFR 50.73(a)(2)(i)(B) and 10CFR 50.73(a)(2)(ii)(B).
2812003001 | Surry 2, Surry 1 | 01/25/2003 | 03/26/2003 | ML03092021 | <strong>Electrical Conduit Bushing Failure Results in a Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2003 at 1414 hours with Unit 2 at 100% power, the reactor tripped due to turbine trip from a main generator trip. The main generator trip was due to Main Transformer and Generator Leads current differential lockout. The differential lockout resulted from a shorted main generator current transformer (CT) lead. Emergency systems functioned as required for the Unit 2 trip. At the time of the Unit 2 reactor trip, Unit 1 was off-line. Load shed occurred on the Unit 1 station service busses as designed. The Unit 1 `B' Main Feed Pump tripped, and since the Unit 1 'A' Main Feed Pump had previously been shut down, a start signal was initiated to both Unit 1 Motor Driven Auxiliary Feedwater Pumps (MDAFWPs) at approximately 1414 hours. The damaged CT leads were repaired. Inspection of like components on Units 1 and 2 was performed, and repairs made as necessary. The automatic actuation of the Unit 2 reactor trip, the actuation of Unit 2 Auxiliary Feedwater, and the automatic actuation of Unit 1 Auxiliary Floodwater are reportable in accordance with 10CFR50.73(a)(2)(iv)(A).
2812003002 | Surry 2 | 09/23/2003 | 11/24/2003 | ML03336069 | <strong>Inside Recirculation Spray Pump Breaker Failed to Close Due to Mechanical Binding</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2003, while performing a surveillance test with Unit 2 in cold shutdown, Inside Recirculation Spray (ISRS) pump 1B breaker 24J-4 failed to close when a simulated automatic closure signal was generated. At the time of the failure, Unit 1 was at 100% reactor power. The breaker is considered to have been inoperable since its previous successful test on April 3, 2002. The root cause evaluation (RCE) determined that the cause for the failure is mechanical binding due to interference between the moving parts of the breaker 24J-4 operating mechanism. A spare breaker was refurbished with a retrofit upgrade repair kit and installed as breaker 24J-4. The retrofit upgrade repair kit improves the design by reducing the inherent gaps in the operating mechanism. Other safety related Unit 1 and Unit 2 breakers have been or will be refurbished with the retrofit upgrade repair kits. A probabilistic risk assessment due to ISRS pump 1B inoperability determined that the integrated risk for this event was of low significance. This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B), any operation or condition, which was prohibited by the plant's Technical Specifications.
2822003001 | Prairie Island 1 | 03/24/2003 | 05/23/2003 | ML03153037 | <strong>Residual Heat Removal Valve CV-31236 Positioner Linkage Found Broken</strong><br /><i>Abstract:&nbsp;</i>A wrench, left in the vicinity of the Unit 1 Train B Residual Heat Removal (RHR) heat exchanger outlet control valve during the November/December 2002 Unit 1 refueling outage, eventually became lodged in the valve operator. Subsequent operations of the valve with wrench interference caused the feedback linkage of the valve operator to fail. The position of the wrench and nature of the valve operator failure allowed this condition to be undetected until a system inspection on March 3, 2003. Upon discovery of the failed valve linkage on March 3, 2003, Technical Specification (TS) 3.5.2, Condition A was entered and valve repair was performed within the TS required Completion Time. The RHR control valve was found, with the wrench lodged in the operator, in the open safeguards position and the Control Room Operators could control the valve from the full open to full close positions, but could not modulate (throttle) the valve. An investigation determined that if the wrench became dislodged from the valve operator, the valve would have closed. A system status light would have alerted the Control Room Operators that the valve changed position but they may not have been able to reposition the valve to its open position. Valve operator air supply failure or isolation would have opened the valve. On March 24, 2003, with both units operating at 100% power, a Nuclear Management Company (NMC) evaluation determined that the misplaced wrench caused the RHR control valve to be inoperable.
2822003002 | Prairie Island 1, Prairie Island 2 | 03/26/2003 | 05/23/2003 | ML03153036 | <strong>Appendix R Safe Shutdown Analysis Issues</strong><br /><i>Abstract:&nbsp;</i>In August 2002, a Nuclear Management Company (NMC) evaluation of potential flow diversion (an ongoing assessment of the extent of a similar condition reported in LER 1-98-15) was in progress. At this point in the evaluation, NMC identified (as a conservative measure prior to completing the detailed evaluation) interim actions to preclude the potential for adversely affecting safe shutdown. Before the interim actions were implemented the potential existed for adverse effects on safe shutdown. On March 26, 2003, with both units operating at 100% power, the completed evaluation determined that, absent compensatory measures, the ability to safely shutdown could have been adversely affected in two cases. In the first case, a fire postulated in certain Fire Areas could result in a spurious start of a containment spray (CS) pump and spurious opening of its associated discharge motor-operated valve (MOV), which would divert the sole credited source of reactor coolant system (RCS) makeup - the refueling water storage tank (RWST) - into containment. In the second case, the scavenging and combustion air dampers for the diesel-driven emergency cooling water pumps (which are required to open when the associated pump operates) were found to be vulnerable to postulated fires in certain Fire Areas. Upon completing the evaluation, the interim actions implemented in August 2002 were assessed and found to be effective compensatory measures until corrective actions are completed.
2822003003 | Prairie Island 1, Prairie Island 2 | 09/10/2003 | 10/31/2003 | ML03317017 | <strong>Unauthorized Entry Into A Protected Area</strong><br /><i>Abstract:&nbsp;</i>On September 10, 2003 at 1458 CDT with both units operating at 100% power, an outage worker was granted unescorted access. At 1502 the worker entered the Prairie Island protected area in an unescorted status. At 1730 information in the worker's access authorization file was discovered that warranted denial of unescorted access. At 1743 the worker was removed from the protected area. The individual made no keycard entries into vital or security-controlled areas. An evaluation of the cause of this event attributed this event to: the NMC Site Access Specialist not correctly interpreting information received from the psychological services provider; and similarity in format of favorable/unfavorable communications from the psychological services provider. Corrective actions to prevent recurrence have been entered into the NMC corrective action process.
2852003001 | Fort Calhoun | 03/06/2003 | 05/05/2003 | ML03134047 | <strong>Lack of Guidance Results in Noncompliance with Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>During the week of March 3, 2003 an evaluation to determine the adequacy of the Fort Calhoun Station (FCS) boric acid program was conducted. As part of the evaluation, one of the evaluation team members requested information on the results of the VT-2 inspections on the lower portion of the reactor vessel. A review of the inspection results indicated that the VT-2 examination had not been accomplished which is not in compliance with Section XI of the ASME Boiler and Pressure Vessel Code as required by Technical Specification section 3.3.1.a. The most probable cause of this event is lack of procedural guidance, caused by poor human factors in the FCS procedure that is used to inspect the rest of the reactor coolant system. There appears to have been a mind set among individuals that the room housing the reactor vessel was then, and had always been, inaccessible because of radiological dose considerations. Further, there appears to be a mind set that "inaccessible" because of radiological dose considerations is equivalent to "inaccessible" as defined in the code. FCS will perform the examination as required by the code if the relief request submitted for processing prior to the2003 refueling outage is delayed or denied.
2852003002 | Fort Calhoun | 07/07/2003 | 08/28/2003 | ML03252140 | <strong>Inadequate Testing of Diesel Generators Due to Air Start Systems Unique Design</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2003 NRC Resident Inspectors discussed diesel generator (DG) surveillance testing with the DG system engineer. A Condition Report (CR) was generated as a result of that discussion. On June 11, 2003, the NRC notified the Nuclear Licensing Department that they believed there was a concern with surveillance testing of the DGs at Fort Calhoun Station (FCS). Another CR was generated to investigate the concern. On July 7, 2003, the NRC informed FCS that, following review of this item, the NRC believed FCS to be in violation of technical specification (TS) 3.0.5 (missed surveillance TS). An additional CR was generated as a result of the last discussion. FCS entered TS 3.0.5 and completed the required actions. On July 7, 2003, a review of the reportability of this event was completed and it was determined to be reportable. The root cause analysis determined that this is a historical issue, and that the DGs have been tested in much the same manner for the life of the plant. Therefore, it is not possible to determine the root cause of this inadequate test of the DGs. The DGs were tested in accordance with the 184 day frequency "full start" TS requirement on July 7, 2003. The surveillance tests have been modified to ensure that all monthly testing is performed on the primary air start system. The operability guidance for the DGs has also been modified to credit only the primary air start system for operability of the DGs.
2852003003 | Fort Calhoun | 09/12/2003 | 11/11/2003 | ML03325033 | <strong>Reactor Trip During Plant Shutdown due to Inadequate Preparation</strong><br /><i>Abstract:&nbsp;</i>During a reactor shutdown in preparation for a refueling outage, the power reduction was stopped because the operators were unable to maintain the axial shape index (ASI) within the expected band. In order to minimize the operational challenge, management provided two reactor trip criteria. At 2037, with the power reduction close to a nominal 15 percent power, it was noted that ASI might not be maintained within the required margin if the shutdown continued. At 2055 on September 12, 2003, Operations determined that a reactor trip was required because one of management's reactor trip criteria was about to be met. The reactor operators were directed to trip the reactor using the manual push button. A four (4) hour non-emergency report was made to the NRC Operations Center at 0010 CDT on September 13, 2003, pursuant to 10CFR 50.72(b)(2)(iv). This report is being made pursuant to 10CFR50.73(a)(2)(iv). No formally approved written guidance was provided to the operator and therefore this event is reportable. Management failed to recognize that a manual trip of the reactor without a change to the shutdown procedure would be reportable. Appropriate procedural revisions to allow the flexibility in plant procedures to allow a manual reactor trip from power levels greater than 2 percent are being processed.
2862003001 | Indian Point 3 | 01/13/2003 | 03/11/2003 | ML03076029 | <strong>Manual Reactor Trip Due to High Differential Pressure Between Condenser Sections</strong><br /><i>Abstract:&nbsp;</i>On January 13, Operations manually tripped the reactor in accordance with Off Normal Operating Procedure ONOP-C-1 due to high differential pressure (dp) between sections of the main condenser. The high dp was due to a loss of circulating water in one condenser section as a result of the trip of the 35 circulating water pump (CWP) while the 36 CWP was tagged out of service for planned maintenance. All control rods fully inserted. The plant was stabilized in hot standby with decay heat being removed by the main condenser. Offsite power remained available and the emergency diesel generators did not start. The auxiliary feed water (AFW) system automatically started. The cause of the event was a high dp between condenser sections. The apparent cause of the 35 CWP trip was a failure of the positive DC exciter lead terminal lug that connects the exciter rotor to the main rotor of the pump motor. The failure was a result of the lead rubbing against the motor dust cover due to improper cable position during a previous maintenance activity. Corrective actions included troubleshooting and repair of the 35 CWP, testing and repair of the CWP Standby drive, and return to service of the 36 CWP. A discussion of the event and management expectations on human performance was communicated to the maintenance department and site population. Maintenance procedure MTR-004-CWP was revised to provide a caution regarding motor exciter leads and assembly details. Procedure PMP-052-CWS will be revised to include a requirement to open and inspect CWP motors brought on site from a vendor. The event had no effect on public health and safety.
2862003002 | Indian Point 3 | 04/29/2003 | 06/25/2003 | ML03183034 | <strong>Manual Reactor Trip for Fire in Main Turbine Insulation Due To Bearing Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2003, during power ascension from refueling outage 3R12, the reactor was manually tripped due to a fire at the south end of the high-pressure turbine located at 53 ft. elevation of the Turbine Building. The fire was caused by the heat of the turbine casing igniting turbine lubricating oil that had leaked and soaked several of the high-pressure turbine insulating pads. The oil leak was from an improperly installed oil deflector for turbine bearing no. 2 during refueling outage 3R12. A Notice of Unusual Event (NUE) was declared at 0313 hours due to the fire exceeding 15 minutes. The fire was extinguished in approximately 15 minutes and declared out approximately 30 minutes later following verification of no reflash. The NUE was terminated at 0521 hours. Fire fighting foam and the C02 system were used to put the fire out. No damage to any equipment or personal injury occurred and no Engineered Safety Feature actuation was required as a result of the manual reactor trip. As immediate corrective actions, the oil deflector was repaired and the oil soaked insulation pads were replaced with new pads. The event had no effect on public health and safety. This event was entered into the Entergy Corrective Action Program under CR-IP3-2003-2795.
2862003003 | Indian Point 3 | 06/22/2003 | 08/21/2003 | ML03239006 | <strong>Automatic Turbine Trip/Reactor Trip Due to Fault in 345kV Generator Output Breaker 3</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2003, at approximately 1742 hours, following completion of maintenance activities on the 345kV Buchanan distribution system {FK}, Indian Point Unit 3 experienced an automatic turbine / reactor trip event {JE}. Prior to this event, Indian Point Unit 3 was in Mode 1, operating at 100 percent, steady-state power conditions. Generator output breaker No. 3 had been opened earlier at approximately 1654 hours to support maintenance activities on 345kV offsite feeder W-98 {FDR}. Indian Point Unit 3 remained in service utilizing generator output breaker No. 1. While attempting to close breaker No. 3, a fault occurred which resulted in the tripping of both generator output breakers No. 1 and 3. The cause for this event was attributed to a ground fault on Phase B of generator output breaker No. 3 {EL}. Control room personnel immediately entered Emergency Operating Procedure (EOP) E-0, "Reactor Trip or Safety Injection" to initiate plant recovery. No radiological releases or adverse safety implications to the public occurred as a result of this event. In accordance with 10 CFR 50.72(b)(2)(iv)(B), the NRC was notified (Event Number 39955) of this event at 2118 hours on June 22, 2003. This report is submitted pursuant to 10 CFR 50.73 (a) (2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system.
2862003004 | Indian Point 3 | 08/04/2003 | 10/01/2003 | ML03279016 | <strong>Plant in a Condition Prohibited by Technical Specifications Due to Late Recognition of Inoperable Battery as a Result of Improper Document Use</strong><br /><i>Abstract:&nbsp;</i>At about 1045 hours on August 4, 2003, cell 26 on the 31 Battery failed a surveillance test. An operability evaluation concluded the battery was operable and did not recognize that the Technical Specification (TS) limit on the cell voltage was not met. The error was identified at 1010 hours on August 5, 2003, and the TS action statement for the 31 Battery was entered. The TS action statement for two inoperable Emergency Diesel Generators (EDG) was also entered because the 31 Battery was required for 33 EDG field flashing and the 31 EDG was out of service for maintenance. The battery was restored to service and the TS action statements were exited prior to a required plant shutdown. The cause of this event was work practices - document use practices - documents not followed correctly. The Shift Manager did not directly consult the TS and did not follow the surveillance procedure requirement to take required TS action. Corrective action includes performance of future operability determinations by Senior Reactor Operators (SRO) or Shift Technical Advisors (STA) with peer review approval by the Shift Manager, training on this event, and further evaluation of the condition of the degraded battery cell. This event had no significant effect on the public health and safety.
2862003005 | Indian Point 3 | 08/14/2003 | 10/14/2003 | ML03289022 | <strong>Automatic Reactor Trip Due to Reactor Coolant Pump Trip on Under-Frequency Caused by a Degraded Off-Site Grid</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, at approximately 1611 hours, during 100% steady state power, Indian Point Unit 3 experienced an automatic reactor trip initiated as a result of low reactor coolant loop flow due to the trip of the 34 Reactor Coolant Pump (RCP) breaker. The 34 RCP breaker tripped due to electrical supply bus under-frequency caused by an unstable off-site power grid (Northeast blackout). Off-site power was lost and all three Emergency Diesel Generators started and energized their assigned safety buses. Main feedwater isolated and the Auxiliary Feedwater (AFW) pumps automatically started. A Notification of Unusual Event (NUE) was declared at 1623 hours, in accordance with the Emergency Plan when off-site power was unavailable for greater than 15 minutes. The NUE was terminated on August 15, at 0210 hours, when off-site power was restored. The cause of the event was a loss of off-site power due to an unstable power grid. Corrective actions to address the cause of the event included a post trip review, root cause evaluation and plant assessment. There were no nuclear safety concerns exhibited during the event and all fission product barriers remained intact. There was no impact on the health and safety of the general public.
2872003001 | Oconee 3 | 05/02/2003 | 05/19/2003 | ML03149004 | <strong>Apparent Reactor Pressure Vessel Head Leakage From a Control Rod Drive Nozzle</strong><br /><i>Abstract:&nbsp;</i>Unit 3 entered its scheduled end-of-cycle 20 refueling outage on April 26, 2003. On May 2, 2003, a visual inspection of the bare reactor vessel head (RVH) was performed. Results of the visual inspection revealed two (2) control rod drive (CRD) mechanism (CRDM) nozzles that were suspected of leakage. Of these, CRDM No. 4 was observed to contain a very thin white coating on the nozzle and CRDM No. 7 appeared to have a small accumulation of boron on the head adjacent to the annulus region. In addition, approximately 6 to 8 CRDMs could not be visually inspected as they were masked by deposits from a Component Cooling (CC) system leak above the RV head. Subsequent evaluation of the prior refueling outage RVH inspection videotape showed that the CRDM No. 7 deposits were not associated with a new leak but rather were remnants from a prior refueling outage leak and repair campaign where the boron residue had not been completely removed from the RVH during the wash down process. The CRDM No. 4 boron deposit appeared fresher, exhibited characteristics similar to prior RVH leaks and as such, was conservatively identified as a leak. The apparent root cause of the nozzle leak is primary water stress corrosion cracking. This RVH will be retired from service and replaced with a new RVH prior to unit restart. For this event, the overall safety significance of this event was minimal and there was no actual impact on the health and safety of the public.
2892003001 | Three Mile Island 1 | 06/24/2003 | 08/20/2003 | ML03239061 | <strong>Control Room Habitability Boundary Ventilation Access Panel Found Open Due To Latching Mechanisms Not Properly Closed</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2003, at approximately 0630 hours while TMI-1 was operating at 100 percent power, an access panel in the Control Building Ventilation system was discovered in the open position. This condition would have resulted in not meeting the design basis requirement of maintaining a positive pressure inside the Control Building Envelope (CBE) following a design basis accident. This condition was determined to be reportable in accordance with 10 CFR 50.72 (b)(3)(ii)(B) and 10CFR 50.72 (b)(3)(v)(D). The NRC Operations Center was notified on June 25, 2003 at 1945 hours. The access panel was promptly closed, and the latching mechanisms were verified to be properly closed. The System Engineer walked down 45 accessible access panels within the Control Building. Two additional panels were found with one of the two latches loose (access panels were still closed). The loose latches were properly closed. The cause of this event has been determined to be that the spiral cam-type latching mechanisms were not properly closed. There were no adverse safety consequences associated with this event, since the Control Building Ventilation system was not required to be placed in the emergency recirculation configuration at any time while the access panel was open. Surveillance and Maintenance procedures for safety related ventilation systems that require access panels in safety related ventilation systems to be periodically opened will be revised. The revision will add steps to verify the latching mechanisms are properly closed.
2892003002 | Three Mile Island 1 | 10/28/2003 | 12/18/2003 | ML03358062 | <strong>Reactor Building Polar Crane Hoist Operation over the Fuel Transfer Canal During Movement of Fuel Due To Inadequate Understanding of Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2003, at approximately 1950 hours while TMI-1 was in the T1R15 refueling outage, the Reactor Building polar crane hoist operated over the Fuel Transfer Canal during movement of a fuel assembly. The cause of this event was a lack of a process for Outage Services personnel to review and implement local station rules and restrictions prior to refueling outages. This condition was determined to be reportable in accordance with 10 CFR 50.72 (a)(2)(i)(B), "Operation or Condition Prohibited by Technical Specifications." Further Polar Crane operation over the Fuel Transfer Canal was stopped until the Polar Crane operators were provided specific training on the proper use of the Polar Crane over the Fuel Transfer Canal when fuel is being moved. Corrective actions include implementing a process for Outage Services to review and implement local station rules and restrictions prior to refueling outages. Additionally, the TMI site-specific Polar Crane training will be revised using a performance based training approach. There were no adverse safety consequences associated with this event, since the Reactor Building Polar Crane hoist operation did not result in any dropped loads.
2892003003 | Three Mile Island 1 | 11/04/2003 | 12/18/2003 | ML03358062 | <strong>Reactor Coolant System Pressure Boundary Leakage Due To Degradation of an Alloy 600 Pressurizer Heater Bundle Diaphragm Plate</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2003, at approximately 10 AM, during the TMI Unit One 15th (T1R15) refueling outage, an inspection of the Pressurizer Heater Bundle (PHB) was completed. This inspection identified a primary system leak at the lower Pressurizer Heater Bundle Diaphragm Plate. Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.1.6.4 does not allow any leakage through a nonisolable RCS strength boundary. Therefore, the discovery of leakage from the PHB Diaphragm Plate was considered a degradation of a principal safety barrier. Three Mile Island Unit One was already in Refueling Shutdown and the conditions of the LCO were already satisfied. The identified condition existed during plant operation and is being reported under 10CFR50.73(a)(2)(i)(B), and 10CFR50.73(a)(2)(ii)(A). This condition does not represent a reduction in the public health and safety. The cause of the leakage was attributed to primary water stress corrosion cracking (PWSCC) of the Alloy 600 PHB Diaphragm Plate. Subsequent VT-2 examinations of the two other pressurizer heater bundles revealed no indication of leakage. The lower Pressurizer Heater Bundle Assembly including the PHB Cover Plate was replaced with a new heater bundle assembly. This new PHB Diaphragm Plate is constructed of Type 304 austenitic stainless steel. The new PHB Diaphragm Plate was seal welded to the pressurizer using Alloy 52 weld material. A previous PWSCC condition was reported in LER 50-289/2001-002-00.
2932003001 | Pilgrim | 02/21/2003 | 04/17/2003 | ML03113049 | <strong>Manual Scram and Completion of a Required Shutdown Due to Recirculation Motor-Generator Trip and Runback</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2003 an unplanned manual reactor scram was initiated during a controlled shutdown while at 22% reactor power. The resulting scram was the completion of a required shutdown that was initiated as a result of a trip of the recirculation loop 'A' motor-generator (MG) set/pump on February 20, 2003. The direct cause of the shutdown was the trip and lockout of the recirculation loop 'A' MG set/pump that was due to a mechanical-type failure of one of two rotor field slip ring copper studs on the generator portion of the MG set. The root cause was improper installation of the generator collector slip ring assembly in the 1991 timeframe. Corrective action taken included replacement of the loop 'A' MG set generator rotor and inspection and testing of the loop 'B' MG set generator. The manual scram was directed as a result of a runback of the recirculation loop 'B' MG set/pump on February 21, 2003. The root cause of the runback was a difference between the actual total feedwater flow and the conditioned signal sent to the feedwater level control system. Corrective action taken included adjustments to improve the response of the feedwater regulating valves, and tuning the overall gain of the feedwater level control system. The events posed no threat to public health and safety.
2932003002 | Pilgrim | 05/19/2003 | 07/17/2003 | ML03205006 | <strong>Unplanned Automatic Closing of the Main Steam Isolation Valves and Resultant Scram Due to Licensed Operator Error During Startup</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2003 an unplanned automatic closing of the main steam isolation valves (MSIVs) occurred while at about 2.5% reactor power, during startup from the 2003 refueling outage. The closing of the MSIVs resulted in a designed automatic scram signal and scram. The scram resulted in the insertion of the control rods and consequent isolation signals due to an expected decrease in the reactor water level. The root cause was licensed operator error. In response to an alarm, the operator operated a control switch that opened the turbine steam bypass valves instead of operating a switch to increase the steam pressure setting. The opening of the bypass valves resulted in decreased pressure in the reactor vessel and main steam lines. The pressure decrease resulted in a reactor water level increase that resulted in the closing of the MSIVs per design. Corrective action taken Included an Operations human performance stand down and an INPO Assist visit. Corrective actions planned include coaching the responsible operator in the proper use of human performance tools, and implementation of an Operations Human Performance improvement action plan. The event posed no threat to public health and safety.
2932003003 | Pilgrim | 06/01/2003 | 07/29/2003 | ML03218073 | <strong>Automatic Scram Resulting from Load Rejection at Full Power Due to Transformer Fault</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2003 an unplanned automatic scram occurred while at 100% reactor power. The scram was the result of a load rejection. Automatic responses included the insertion of all withdrawn control rods, transfer of the source of electrical power for Pilgrim's 4.16 kV auxiliary power distribution system (APDS), closure of the turbine steam control and stop valves, trip of the turbine, opening of the turbine steam bypass valves, and opening of main steam relief valves for pressure relief. The direct cause of the scram was the automatic closing of the turbine control valves. The direct cause of the event was an electrical fault in the unit auxiliary transformer (UAT) that was powering the APDS at the time of the event. The fault was the result of the failure of a conductor within the low voltage portion of the UAT (X-winding). Corrective actions taken included a temporary alteration for powering the APDS during power operation. Corrective actions planned include the repair or replacement of the unit auxiliary transformer. The event posed no threat to public health and safety.
2932003004 | Pilgrim | 08/29/2003 | 10/27/2003 | ML03309004 | <strong>HPCI System Declared Inoperable During Surveillance Test Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2003 at 1350 hours, the high pressure coolant injection (HPCI) system was declared inoperable. This action was taken as a result of two successive automatic turbine trips and resets that occurred about 25 minutes after the HPCI turbine-pump was started for routine surveillance testing required by Technical Specifications. The root cause of the automatic turbine trips and resets was inadequate guidance in the procedure for inspecting and testing the HPCI turbine mechanical-hydraulic overspeed trip and reset device. Corrective action taken included the adjustment of the spring setting in the manual trip and reset device. Corrective action planned includes revising the procedure used for inspecting and testing the HPCI overspeed trip device. This event posed no threat to public health and safety.
2932003005 | Pilgrim | 09/06/2003 | 11/03/2003 | ML03318044 | <strong>HPCI and RCIC Systems Inoperable Due to De-Energized Train "A" Electrical Loads Caused by Circuit Breaker Current Transformer Malfunction</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2003 at 1151 hours, the safety-related train 'A' 480-volt load center and the related motor control centers (MCCs) powered from the load center de-energized. The event resulted in several systems including the high pressure coolant injection and the reactor core isolation cooling systems becoming inoperable. The train 'B' 480-volt load center and related MCCs were unaffected. The affected load center and related MCCs were re-energized by 0022 hours and the affected systems were returned to service by 1000 hours on September 7, 2003. The direct cause of the event was the unplanned trip of the circuit breaker that powers the load center. The root cause investigation revealed the circuit breaker tripped due to a malfunction of one of the breaker's three current transformers. Corrective action included the replacement of the circuit breaker. Corrective action planned includes analysis of the current transformer malfunction and related actions to preclude recurrence. The event posed no threat to public health and safety.
2932003006 | Pilgrim | 10/01/2003 | 11/24/2003 | ML03336073 | <strong>Reactor Coolant Pressure Boundary Leakage Due to Reactor Vessel Nozzle Weld Crack Propagation</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2003 at about 0430 hours, a reactor coolant pressure boundary leak from a reactor vessel nozzle-to-cap weld was discovered during a planned visual inspection of the Drywell. The inspection was a planned activity to identify the source(s) of Drywell leakage. The leak was caused by an incipient crack or crevice condition remaining in the weld after repair welding performed as part of the nozzle-to-cap fabrication welding in 1977. Subsequent crack propagation continued through-wall by an interdendritic stress corrosion cracking mechanism due to high residual weld stresses in the Inconel weld metal. Corrective action taken included a nozzle weld repair consisting of a full structural weld overlay. The event posed no threat to public health and safety.
2962003001 | Browns Ferry 3 | 06/30/2003 | 08/26/2003 | ML03247100 | <strong>Mode Change Not Allowed by Technical Specifications During Vessel Reassembly</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2003, Unit 3 was in the latter stages of recovering from a scheduled mid-cycle outage during which the reactor vessel had been disassembled to allow fuel bundle testing. The Reactor Mode Switch had been previously placed in Refuel (Mode 5) to support testing of control rods. Vessel reassembly activities were in progress and the last reactor vessel head closure bolt was tensioned at 0220 hours. With the Reactor Mode Switch in Refuel and all vessel head bolts tensioned, Technical Specifications (TS) Table1.1-1, Modes, defines the reactor mode as Startup (Mode 2). So, the final tensioning of the head bolts resulted in an unintended reactor mode change from 5 (Refueling) to 2 (Startup). TS Limiting Condition For Operation (LCO) 3.0.4 prohibits ascending mode changes unless all TS equipment required for the mode is Operable. Due to the outage status of the plant, several TS systems required for Mode 2 were not in fully operable status, which resulted in not meeting the requirements of LCO 3.0.4. An oncoming dayshift operator noted that the Reactor Mode Switch was not in the proper position and placed the switch in Shutdown at 0726, which restored compliance with TS. The root cause of this event was the plant procedure for vessel assembly did not have a notification step to verify mode switch position when the vessel head was tensioned. The procedure has been revised. This event is being reported as a condition prohibited by TS in accordance with 10 CFR 50.73(a) (2) (i) (B). There was no safety significance associated with the event.
2982003001 | Cooper Station | 02/28/2003 | 04/28/2003 | ML03126062 | <strong>Inadequate Communication Results in Both Diesel Generators Inoperable Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2003, at 0857 Central Standard Time (CST), with Cooper Nuclear Station (CNS) in cold shutdown, diesel generator (DG) 1 and DG2 were inoperable at the same time. The DGs are the standby source of emergency Alternating Current (AC) power. DG1 was inoperable at the time due to failure of the fuel oil transfer system to deliver required flow during a routine inservice test. DG2 was declared inoperable as a result of discovering that a time delay relay in the diesel room ventilation system had been in service in excess of its qualified life as stated by the manufacturer. Declaring the relay inoperable resulted in the diesel room ventilation system being inoperable. The diesel room ventilation is a required support system for the diesel generator. Immediate corrective action was to replace the relay with one that was within its service life. DG2 was returned to operable status on February 28, 2003, at 1937 CST. The relay qualified life issue has been entered into the CNS Corrective Action Program. The root cause of this event is inadequate communication between the Operations and Engineering departments in that the possibility that analyses could be performed that would extend the qualified life of the relay was not communicated. Corrective actions to preclude recurrence are to establish, implement, and reinforce standards for formal communication between Operations and Engineering when preparing Operability Determinations.
2982003002 | Cooper Station | 05/19/2003 | 07/17/2003 | ML03204033 | <strong>Technical Specification Prohibited Operation Due To Safety Relief Valve Test Failures</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2003, a review of Target Rock safety relief valve (SRV) test data, provided by Wyle Laboratories, determined that four of eight SRV pilot valve assemblies failed to lift within their Technical Specification (TS) lift setpoint. Specifically, one SRV with a setpoint of 1080 +1- 32.4 psig lifted at 1168 psig, two SRVs with a setpoint of 1090+/-32.7 psig lifted at 1130 psig and 1166 psig respectively and one SRV with a setpoint of 1100+/-33.0 psig lifted at 1228 psig. The discovery was made as a result of routine TS surveillance testing of the pilot valve assemblies. Cooper Nuclear Station (CNS) was at 100 percent rated reactor power at the time of the determination. Examination determined that sufficient corrosion bonding existed between the SRV pilot valve assembly Stellite 21 disc and the pilot valve Stellite 6 in-body seat to cause the SRV pilot valves to lift outside TS setpoint tolerances. As documented in CNS Licensee Event Report 1999-004-01, this is a recurring problem at CNS and within the industry. The valves were replaced with tested and certified spare valves. This event is considered to have no safety significance from a Probabilistic Safety Assessment Risk evaluation standpoint. This event does not create a core damage scenario. There is no change to the CNS core damage frequency or the large early release frequency. This condition also has no impact on the Reactor Pressure Vessel pressure relief function capability. Even under postulated failure conditions, there is no associated risk increase to the plant.
2982003003 | Cooper Station | 04/10/2000 | 05/14/2003 | ML03140004 | <strong>Failure to Evaluate Heat-up Rate Leads to Technical Specification Prohibited Operation</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2000, during performance of the ASME Class 1 System Leakage Test surveillance procedure for refuel outage RE-19, the Technical Specification (TS) limit for Reactor Coolant System (RCS) heat-up rate was exceeded in Reactor Recirculation (RR) [EIIS:AD] loop B. The failure to meet TS Surveillance Requirement acceptance criteria was not recognized, and the required evaluation to determine if the RCS is acceptable for operation was not performed prior to start up from the RE-19 refuel outage. On March 20, 2003, with Cooper Nuclear Station (CNS) in Mode 5 (Refueling) for refuel outage RE-21, a review of the surveillance procedure and past performance of the procedure was performed in support of a modification to replace temperature recorders. During this review the above condition was discovered. This event was the result of inadequate procedural guidance for equalizing RCS temperatures in preparation for starting an idle RR pump, and evaluating available RCS temperature data. Appropriate procedure revisions were completed by April 4, 2003, and the required evaluation was completed on April 12, 2003. Additional corrective actions are being evaluated and tracked by the CNS Corrective Action Program.
2982003004 | Cooper Station | 05/26/2003 | 04/01/2004 | ML04097022 | <strong>Manual Reactor Scram Due To Main Turbine High Vibration</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2003, at 1321 hours, there was a step change in main turbine vibration indication from less than 4 mils to 10.2 mils. A manual reactor scram was initiated from 89% power. Subsequent to the scram, reactor vessel water level dropped to approximately 30 inches below instrument zero, resulting in Primary Containment Isolation System Group 2, 3, and 6 isolations, start of High Pressure Coolant Injection and Reactor Core Isolation Cooling systems, and trip of the Reactor Recirculation pumps. An evaluation of plant response determined all control rods fully inserted and systems controlling reactor pressure and level responded as designed. The most probable cause for the turbine blade failure in the low pressure turbine is material condition. The failure mechanism is consistent with age-related/end-of-life type failures. Long term corrective action will be to replace the low pressure turbine rotors with new rotors during the next refueling outage. Immediate actions taken were to manually scram the reactor, trip the main turbine, and place the unit in a cold shutdown condition. An initial visual exam of the turbine blade root specimen was obtained, which concluded the crack is consistent with high cycle fatigue. Magnetic particle and eddy current testing were performed on both faces of the last four rows on both LP1 and LP2 spare rotors. Blades with crack indications on the spare rotors were replaced. The in-service LP1 and LP2 rotors were replaced with the spare rotors.
2982003005 | Cooper Station | 09/28/2003 | 11/21/2003 | ML03329056 | <strong>Turbine Trip Failure During Testing Due to Ester Contamination of Turbine Lube Oil</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2003 at 23457 hours, during turbine trip testing, the turbine trip block failed to actuate as demanded while testing the solenoid and low vacuum trip. Troubleshooting identified resistance in the movement of the trip plate in the trip direction. Repeated cycling of the trip plate resulted in no abnormal resistance and the surveillance was repeated and completed satisfactorily. Per Technical Specifications, reactor power was reduced to less than 25% power. The most probable root cause was ester contamination of the turbine lubricating oil, combined with trace amounts of water, resulting in the formation of hydrolyzed esters that increased the forces required to open the trip valve. The source of the ester contamination is being investigated. In addition, particles collected in clearances around the trip valve. Immediate actions were to designate an extra operator to trip the turbine locally until trip capability was restored. An interim action is to perform the turbine trip functional test more frequently. The long-term corrective action is to remove particulate contamination from the turbine tube oil system.
2982003006 | Cooper Station | 10/28/2003 | 12/19/2003 | ML03363059 | <strong>Manual Reactor Scram Initiated Due To Transmission Line Structure Fire</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2003, at 0130 hours, a fire occurred on a wooden transmission structure located between the main generator output and the 345KV switchyard. Due to the imminent loss of the main generator output line to the switchyard, a manual scram was performed at 0200 hours. All control rods inserted and Primary Containment Isolation System Group Isolations for Primary Containment, Reactor Water Cleanup and Secondary Containment initiated as expected due to vessel level shrink. The Emergency Core Cooling Systems did not initiate. During water level recovery an overfeed condition caused the operating Reactor Feedwater pump to trip and a second manual scram was inserted in anticipation of a low level scram signal. Normal shutdown procedures were entered at 0300 hours and a vessel cool-down was initiated. The transmission structure fire was reported out at 0647 hours. The fire occurred when dust accumulation on the insulators and structure became wetted and created a path for stray electrical currents from phase to phase, or phase to ground across the wooden cross arm. The cause of this event is the failure to properly ground the insulator strings on the wooden structure. The damaged wooden structure and associated line disconnect switch were removed on October 30, 2003. Grounding cables were installed on a similar structure on November 24, 2003.
2982003007 | Cooper Station | 11/28/2003 | 01/25/2004 | ML04030051 | <strong>Automatic Reactor Scram Following Reactor Feed System Control Malfunction</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2003, "B" Reactor Feed Pump (RFP) transferred to manual and lowered to approximately 3100 revolutions per minute causing the reactor to automatically scram on low reactor vessel water level at 2202 hours. Subsequent to the scram, reactor vessel water level dropped to approximately 47 inches below instrument zero resulting in Primary Containment Isolation System Group 2, 3, and 6 isolations, start of High Pressure Coolant Injection and Reactor Core Isolation Cooling systems, and automatic trip of the Reactor Recirculation pumps. An evaluation of plant response determined all control rods fully inserted and systems controlling reactor pressure and level responded as designed. The approximate root cause of this event is a spurious signal entered the reactor feed pump turbine controller. Immediate action was taken to place the plant in a safe shutdown condition in Mode 3 (Hot Shutdown). Prior to plant startup, 1) operators were trained on the event, 2) radio frequency interference suppression, to attenuate frequencies greater than one mega hertz, was installed on the reactor feed control input signals, 3) a modification was completed that added annunciation for a RFP in manual and provided additional signal monitoring, and 4) installed ground wires from feedwater control station cases to cabinet ground bus. Subsequent to startup and still to be completed is a modification that will attenuate frequencies greater than one kilohertz. This will prevent spurious signals in the reactor feed pump turbine controller, dampen noise on the master controller, and filter noise.
2982003008 | Cooper Station | 12/03/2003 | 02/02/2004 | ML04037068 | <strong>Inadequate Evaluation Leads to Technical Specification Prohibited Operation</strong><br /><i>Abstract:&nbsp;</i>On December 3, 2003 after a reactor scram, operators exited a Limiting Condition for Operation (LCO) and entered Mode 2 for unit startup based on an inadequate engineering evaluation of the acceptability of the reactor coolant system for continued operations. This resulted in operations prohibited by Technical Specifications. Upon determination that the evaluation was inadequate unit was returned to a Mode 3 condition. The root cause of the problem that resulted in the use of an inaccurate and incomplete engineering evaluation to support the decision to commence a reactor startup was individual human performance error. Immediate actions were to return the plant to hot shutdown and correct the engineering evaluation to support a reactor startup. Long term corrective actions include counseling of involved individuals, revised processes to improve controls when exiting LCO's based on engineering evaluations, and improvements to the post-event review and start up approval process.
3012003001 | Point Beach 2 | 04/02/2003 | 07/28/2003 | ML03219065 | <strong>Containment Accident Fan Backdraft Damper Failure Results in Condition Prohibited by Technical Specification 3.6.6.C</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2003, the Nuclear Management Company (NMC) determined that the backdraft damper associated with the Point Beach Nuclear Plant (PBNP) Unit 2 W-1D2 containment cooling fan was substantially degraded. The function of that damper is to close when the 2W-1D2 fan is not operating to prevent diversion of air flow through the normal cooling fan when the 2W-1D1, Containment Accident Recirculation Fan, is operating. The damper was found in the open position with only the top louver being fully closed. The top louver was detached from the two louver linkage members. A gravity counterweight was found to be missing from the top louver shaft mounting location. Based on these findings, the 2W-1D1, Containment Accident Recirculation Fan, and the 2W-1D2, Containment Cooling Fan, were declared out of service at 14:05 on April 2, 2003. LCO 3.6.6, "Containment Spray and Cooling Systems," was declared not met and TSAC 3.6.6. Condition C was entered for one accident fan cooler unit not operable. Required action C.1 directs restoration of the cooler unit to operable status within a 72 hour completion time. A temporary modification was completed to secure the damper in the closed position and the containment fan cooler was returned to service. Further investigation determined that the degraded condition of the backdraft damper should have been identified during performance of a heat exchanger performance test on March 20, 2003, and a 72 hour TSAC entered at that time. Since the allowed completion time for the TSAC required action was exceeded, the unit was operated in a condition prohibited by the Technical Specification and is reportable per 10CFR 50.73. The failure of the backdraft damper is due to long term degradation of the assembly. The failure to identify the condition of the damper on March 20, 2003, was due to incomplete communication regarding the detached parts and the fact that other indications of damper degradation were not recognized.
3012003002 | Point Beach 2 | 04/05/2003 | 05/23/2003 | ML03155016 | <strong>Reactor Shutdown Required Due to Technical Specification TSAC 3.1.6.B.2 Not Met</strong><br /><i>Abstract:&nbsp;</i>At 2050 CST on April 5, 2003, indications were noted at the Point Beach Nuclear Plant Unit 2 that the sequence difference between the position of control bank "C" and control bank “D" was at 126 steps. Technical Specification LCO 3.1.6, ‘Control Bank Insertion Limits," states that the control banks shall be within the insertion, sequence, and overlap limits specified in the Core Operating Limits Report (COLR). Figure 3 of the Unit 2 COLR specifies the sequence limit is 125 steps. At that time Control Ban “C" was at 194 steps and Bank “D" was at 68 steps. In accordance with the Technical Specifications, TSAC 3.1.6.B.1.1 was entered to verify the shutdown margin (SDM) within one hour and TSAC 3.1.6.B.2 was entered to restore control bank sequence and overlap to within limits within two hours. The SDM was verified at 2124 CST and TSAC 3.1.6.B.1.1 was met. At 2250 CST the required action for TSAC 3.1.6.B.2 was determined to have not been met within the allowed completion time. As a result, TSAC 3.1.6.C was entered. This action statement requires the reactor to be in Mode 2 with keff < 1.0, with a completion time of six hours. At 0530 CDT on April 6, 2003, Unit 2 entered Mode 3 and the LCO 3.1.6.C.1 was considered met. Equipment performed as expected during this reactor shutdown. A reactor startup was subsequently initiated on April 8, 2003. The rod drive system performed as expected during this start up and returned to full power. The NRC was notified of this event in accordance with 10 CFR 50.72 (b)(2)(i) at 0942 CDT on April 6, 2003.
3012003003 | Point Beach 2 | 04/08/2003 | 05/28/2003 | ML03161004 | <strong>Failure to Place Instrument Channel in Trip as Specified by LCO 3.3.1 Required Action D.1</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2003, reactor startup was in progress. With Unit 2 in MODE 2, a steam generator (SG) feedwater (FW) flow alarm from flow indicator 2FI-466 was received. Although not known at the time, the water in the sensing line of this flow indicator had flashed, causing it to indicate erroneously. The FW system was secured at the time; therefore, there was no actual FW flow through the flow sensor. This FW flow indicator provides one of the required channels of input specified in Technical Specification (TS) 3.3.1, RPS Instrumentation. The FW flow alarm provided indication that this channel may have been inoperable. However, operators' attention and focus was on activities associated with reactor criticality and they did not recognize the significance of the alarm nor the associated flow indication. Operators did not discern the significance of this condition until about two and one-half hours after receipt of the initial alarm. Consequently, the one hour Completion Time for the TS Required Action to place an inoperable channel in trip had already elapsed. Plant technicians placed the channel in trip and refilled the instrument sensing line within one hour of the operators' recognition of this condition. Although the channel was not placed in trip within one hour of receipt of the initial alarm, it was restored to operable status within the seven hours allowed by the TS to exit the MODE of applicability. Therefore, the requirements of TS 3.3.1 were met. While no TS violation occurred, the initial operator response to this condition was not appropriate.
3012003004 | Point Beach 2 | 07/10/2003 | 08/15/2003 | ML03238055 | <strong>Reactor Trip Due to Failure of "B" Main Feed Pump Motor</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2003, at approximately 1340 CDT, while operating at 100% power, the Point Beach Nuclear Plant (PBNP) Unit 2 experienced the failure of the “B" Main Feedwater Pump (MFP) due to an electrical fault within the motor. The loss of the MFP resulted in an automatic Unit 2 reactor trip at approximately 1341 CDT. The trip was due to a feed flow/steam flow mismatch coincident with low steam generator level. The auxiliary feedwater system also actuated as expected due to the initial low steam generator water levels. The reactor protection and safety systems responded as required and the unit was stabilized in Mode 3. A four hour event notification was made to the NRC at 1455 CDT. The apparent cause for the failure of the "B" MFP motor failure has been preliminarily determined to be failure of the stator winding Insulation due to age related degradation. Additional inspection and testing will be performed by the vendor that is contracted to rewind the motor to determine the validity of this failure mode assessment. Unit 2 was taken critical at 2306 CDT on July 12 and operated with a single MFP and a nominal 50% power limit until the "B" MFP motor was replaced. Unit 2 returned to full power operation on July 16, 2003. Systems and equipment necessary to mitigate the consequences of this motor failure and subsequent reactor trip functioned as designed and the plant was maintained in a stable hot shutdown condition until the restart on July 12, 2003. The safety and welfare of the public and the plant staff was not impacted by this event and the safety significance was minimal.
3012003005 | Point Beach 2 | 07/11/2003 | 09/04/2003 | ML03259114 | <strong>Manual Reactor Trip and Safety Injection Due to Pressurizer Low Level</strong><br /><i>Abstract:&nbsp;</i>On July 11, 2003, Point Beach Nuclear Plant (PBNP) Unit 2 was in Mode 3 at normal operating temperature and pressure in preparation for critical approach. Upon closure of the Reactor Trip Breakers in preparation for the critical approach, the main feed water regulating valves (MFRV) opened in response to steam generator levers slightly below programmed level. The (MFRV) controllers had been left in automatic mode following a reactor trip on July 10, 2003. The increased feedwater flow to the steam generators caused a cooldown of the RCS, which resulted in a decrease in Pressurizer level. With Pressurizer level not within 10% of programmed level, Operators initiated a manual reactor trip, a manual safety injection, and a manual containment isolation per AOP 1A. There was no actual safety injection flow into the RCS and the charging pumps made up for the RCS shrinkage due to the cooldown. Steam Generator levels remained within their normal operating range. The plant was maintained in Mode 3 while an initial investigation of this event was conducted. A four hour event notification (EN# 39993) was made to the NRC at 2357 pursuant to 10CFR 5072(b)(2)(iv)(A). An investigation concluded that inadequate procedure guidance was the primary reason the controllers for the MFRVs were inappropriately left in automatic. Human performance and configuration control deficiencies were contributing factors. To prevent recurrence, procedure changes were made to ensure the MFRV controllers are in "manual" with valves "closed", prior to closing the Reactor Trip Breakers. All systems and equipment functioned as designed during this event. Accordingly, the impact on the health and safety of the public and the plant staff as a result of this event is negligible. Unit 2 was returned to power operation on July 13, 2003.
3022003001 | Crystal River 3 | 06/11/2003 | 08/07/2003 | ML03226068 | <strong>Incorrectly Set Motor Overload Relays Result in Loss of Both Control Complex Chillers</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2003, Progress Energy Florida, Inc.'s, Crystal River UnIt 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. At 13:35, Control Complex Chiller, CHHE-1B, tripped while swapping Control Complex ventilation trains. At 14:09, CHHE-1A tripped as it was being started and heat load was being added. Improved Technical Specification (ITS) 3.0.3 was entered at this time for having both Control Complex Cooling System trains inoperable. The cause of this event was the incorrect calibration of the chiller motor overload relays for CHHE-1B in December 2002 and for CHHE-1A in February 2003. CHHE-1A was manually started and successfully loaded incrementally. At 16:18, ITS 3.0.3 was exited. The motor overload relays for CHHE-1A/1B have been recalibrated. Maintenance procedures will be generated or revised, as appropriate, to provide detailed instructions for calibration of the subject motor overload relays. This condition does not represent a reduction in the public safety. One previous similar occurrence was reported to the NRC by CR-3 in Licensee Event Report 50-302/97-043-00.
3022003002 | Crystal River 3 | 09/29/2003 | 11/20/2003 | ML03332039 | <strong>Main Steam Safety Valve Setpoints Below Required Tolerance Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 19:58, on September 29, 2003, Progress Energy Florida, Inc., Crystal River Unit 3 was in MODE 1 (POWER OPERATION) at approximately 80 percent RATED THERMAL POWER. While performing surveillance procedure SP-650, "ASME Code Safety Valves Test," on the 'B' Once Through Steam Generator, the setpoint for main steam safety valve (MSSV) MSV-41 was found below its required tolerance. Subsequently, six of twelve tested MSSVs were found to have setpoints below their required tolerance. Improved Technical Specification (ITS) 3.7.1 states that the MSSVs shall be operable as specified in Table 3.7.1-1 in MODES 1, 2 and 3. In order to be considered operable, the MSSV setpoints must be within +/- 3 percent of the nominal tolerance. The existence of similar discrepancies in multiple relief valves is an indication that the discrepancies may have developed over a period of time. Therefore, PEF concludes that multiple MSSVs were inoperable during plant operation for a period longer than allowed by ITS and the condition is reportable under 10CFR50.73(a)(2)(i)(B). This condition does not represent a reduction in the public health and safety. The cause for this condition was previous test methodology. The six MSSVs were adjusted and retested satisfactorily. A similar occurrence was previously reported to the NRC in Licensee Event Report 50-302/01-002-00.
3022003003 | Crystal River 3 | 10/04/2003 | 11/19/2003 | ML03332005 | <strong>Reactor Coolant System Pressure Boundary Leakage Limit Exceeded Due to Pressurizer Instrument Tap Nozzle Cracks</strong><br /><i>Abstract:&nbsp;</i>At 1032, on October 4, 2003, Progress Energy Florida, Inc., (PEF's) Crystal River Unit 3 (CR-3) was in MODE 4 (HOT SHUTDOWN) at zero percent RATED THERMAL POWER. While performing a visual inspection of the pressurizer upper level instrument tap nozzles, evidence of a very small Reactor Coolant System (RCS) pressure boundary leak was found at three nozzles. Improved Technical Specification (ITS) 3.4.12 states that RCS operational leakage shall be limited to no pressure boundary leakage in MODES 1, 2, 3, or 4. If pressure boundary leakage exists, the plant shall be in MODE 3 within 6 hours and in MODE 5 within 36 hours. At 1741 on October 4, 2003, CR-3 entered MODE 5. The identified condition existed during plant operation and is being reported under 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(ii)(A). This condition does not represent a reduction in the public health and safety. The most probable cause for this condition was primary water stress corrosion cracking (PWSCC). The three pressurizer upper level instrument tap nozzles were repaired. This is the first occurrence of pressurizer level instrument tap nozzle pressure boundary leakage at CR-3.
3022003004 | Crystal River 3 | 10/17/2003 | 12/08/2003 | ML03350031 | <strong>Redundant Channels Of A Post-Accident Monitoring Function Not Operable Due To Reversed Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2003, Progress Energy Florida, Inc., (PEF) Crystal River Unit 3 (CR-3) was in NO MODE (Reactor Vessel Defueled) at zero percent RATED THERMAL POWER. While implementing Engineering Change 51164, "Upgrade the Keyboard Commander," CR-3 personnel noticed that the Safety Parameter Display System (SPDS) power supplies to the display servers and peripherals in the Main Control Room were reversed. Degrees of Subcooling is displayed on both SPDS displays. In the as-found configuration, loss of one Vital Bus Distribution Panel would cause the loss of both SPDS monitors. Two channels of the Degrees of Subcooling Function were not operable. Improved Technical Specification 3.3.17 requires that Post Accident Monitoring instrumentation for each Function in Table 3.3.17-1 shall be OPERABLE in MODES 1, 2 and 3. Table 3.3.17-1, Line Item 21, requires two channels of Degrees of Subcooling. With one or more Functions with two required channels inoperable, restore one channel to OPERABLE status within seven days. The identified condition existed since 1999 and is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical specifications. This condition does not represent a reduction in the public health and safety. The cause was incorrectly labeled SPDS power strips caused by inadequate work instructions in Modification Approval Record 96-11-03-01 implemented in October 1999. The power strips have been correctly labeled. Previous similar occurrences have not been reported to the NRC.
3022003005 | Crystal River 3 | 11/05/2003 | 03/22/2004 | ML04090043 | <strong>Reactor Trip Caused By Loss Of Feedwater While Troubleshooting Feedwater Pump Control Problems</strong><br /><i>Abstract:&nbsp;</i>At 17:34, on November 5, 2003, Progress Energy Florida, Inc., (PEF) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at approximately 37 percent RATED THERMAL POWER. While troubleshooting problems with the "B" Main Feedwater Pump (FWP-2B) control circuits, a feedwater transient occurred that resulted in an automatic reactor trip. When FWP-2B was placed in automatic, the control signal to the pump decreased significantly. This caused a loss of feedwater flow to both Once Through Steam Generators (OTSGs). Operators attempted to restore feedwater flow by placing FWP-2B back in manual and raising the set point of both feedwater pump controllers. As OTSG level continued to decrease, Reactor Coolant System (RCS) pressure and temperature increased. An automatic reactor trip occurred on high RCS pressure. An automatic Emergency Feedwater (EFW) System actuation occurred on low OTSG levels. The cause for this event was human error associated with not verifying the correct circuit cards were installed in the Integrated Control System (ICS) during the recent refueling outage. The correct circuit cards were installed in the ICS to correct the problem. Reactor Protection System and EFW System actuation are reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported to the NRC by CR-3.
3052003001 | Kewaunee | 01/14/2003 | 03/17/2003 | ML03084063 | <strong>Technical Specifications Action Requirements Not Followed - Personnel Failed To Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On 1/14/2003, with the plant operating at 100% power, Nuclear Management Company (NMC) personnel recognized that Technical Specifications (TS) 3.10.b, Power Distribution Limits, action requirements had not been implemented. The condition was discovered when questions were raised regarding operability of the computerized axial flux differential monitor alarm system. TS 3.10.b.13 requires, "If the alarms are temporarily out of service, the axial flux difference shall be logged, and conformance with the limits assessed, every hour for the first 24 hours, and half-hourly thereafter." On 1/12/03, in response to several spurious "Power Range Upper Radial Flux Tilt" alarms, Control Room Operators entered a fixed computer input value to correct a 'bad acting' input. Entering the fixed value was not immediately recognized as disabling the axial flux monitoring alarm system. The requirements for logging were initiated according to plant procedure approximately 14 hours later, it wasn't until 1/14/03 that the incident was recognized as failing to comply with TS requirements. The root cause evaluation for the event determined the operating crew failed to implement the requirements of plant procedures due to a false sense of security in their actions. Contributing causes included; flawed assumptions that the action taken was the same as routine actions performed in removing computer points from scan, and comparing the action to taking an instrument out of service for surveillance purposes which had not required logging in the past. A number of administrative actions have been initiated to preclude recurrence. There was no public health and safety risk as a result of this event. Reactor flux levels remained stable throughout the event. This report does not describe a safety system functional failure.
3052003002 | Kewaunee | 02/26/2003 | 04/28/2003 | ML03126051 | <strong>Shutdown Initiated - Diesel Generator Failed Start Test - Unusual Event - Caused by Start Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On 2/26/2003, with the plant operating at 100% power, Nuclear Management Company (NMC) personnel reported that a plant shutdown was initiated according to Technical Specifications (TS) and an Unusual Event (UE) had been declared. The shutdown was initiated and UE declared after the "B" Train Emergency Diesel Generator (EDG) failed to start while the opposite, "A" Train, EDG was out of service for maintenance. TS require that when an EDG is out of service the opposite train diesel must be tested daily. When the daily start of the "B" EDG was attempted, it failed to start. The TS action statement to shutdown the plant was initiated. The diesel failed to start due to an insulating oxide layer on a single set of contacts associated with one of the diesel start circuit time delay relays. The plant power reduction began at 0107. The faulty relay was replaced and the diesel was satisfactorily retested at 0624. The plant back-down was halted at ten percent power. The plant did not reach a shutdown condition. The UE was based on the Kewaunee emergency classification criterion of both EDGs being unable to be connected to and supply power to the emergency safeguards power buses. The UE was exited at 0656 following the "B" diesel generator being returned to service. The increased core damage probability associated with diesel generator B being out of service for 27.75 hours was calculated using the Kewaunee probabilistic risk assessment model to be 4.38E-7, which is considered a very low risk in the Significance Determination Process. This value was calculated assuming average test and maintenance unavailabilities for all other components. This report describes a safety system functional failure.
3052003004 | Kewaunee | 09/02/2003 | 11/03/2003 | ML03318044 | <strong>Failure to Log Nuclear Instrumentation Quadrant Power Tilt As Required by Tech Spec 3.10.j Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On September 2, 2003, with the plant operating at 100% power, Nuclear Management Company (NMC) Instrumentation & Control (I&C) personnel conducted a quarterly calibration of excore nuclear instrumentation (NI) channel N41. At the completion of the calibration, it was noticed that Control Room annunciator LOWER QUADRANT POWER TILT RATIO HIGH was lit. The alarm response procedure and procedure A-NI-48 "Abnormal Nuclear Instrumentation" were reviewed, and it was determined that logging of the power tilt was not necessary, since three of the four NI channels still had the same calibration and were operable. A-NI-48 did not provide clear guidance relative to the logging requirement, or on blocking the N41 channel to clear the alarm. On September 3, 2003, this alarm condition was further evaluated, and it was subsequently determined that the N41 channel should have been defeated. At this point, N41 was defeated, and a manual power tilt calculation was performed. No power tilts were found to be present. The root cause of this event was procedural deficiency relative to A-NI-48, in that it did not provide clear guidance as to how an NI channel should be addressed when it would alarm during a calibration. It was also not realized by the operating crews that the alarm would not re-flash if an actual power tilt had occurred. Corrective actions to be taken include a revision to procedure A-NI-48 to provide specific guidance on actions when an alarm is annuciated due to calibration. This report does not describe a safety system functional failure.
3052003005 | Kewaunee | 10/01/2003 | 12/01/2003 | ML03343037 | <strong>Failure to Perform Quarterly Surveillance Testing on Portable Radiation Survey Instruments as Required by Technical Specification Table 4.1-1 Item 25</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2003, with the plant operating at 100% power, Nuclear Management Company (NMC) Nuclear Oversight personnel discovered that the Technical Specification Table 4.1-1 Item 25 requirement for the Quarterly Test of Radiation Protection Portable Survey Instruments was not met for several instruments in July 2003. This test consists of exposing the survey instrument detector to a source of known strength, and verifying the proper response for each range I scale of the instrument. Initially, five instruments were found to have missed the quarterly test in the previous three months. The Radiation Protection (RP) Department promptly tested all portable survey instruments that were left in-use that had not been tested or calibrated within the previous quarter. Of the instruments initially tested, 3 did not meet performance acceptance requirements. They indicated higher readings than expected, and were subsequently removed from use. The root cause of this event was the failure of the existing process to properly control the performance of required Technical Specification surveillance requirements. A contributing cause of this event is procedural deficiency. The instruments that were not tested or calibrated in July, August, and September 2003 were removed from service until the quarterly tests were performed or verified current. Those instruments that were not in-use were quarantined. This report does not describe a safety system functional failure, since no plant safety systems were involved with this occurrence.
3052003006 | Kewaunee | 12/12/2003 | 02/10/2004 | ML04049066 | <strong>Component Cooling System R-17 Radiation Detector Pipe Assembly Leakage</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2003, with the plant operating at 100% power, Instrumentation & Control (I&C) Procedure (ICP) -45.47 (Channel R-17 Component Cooling Liquid Radiation Monitor Calibration) was being performed. As the bolts were loosened to remove the top shield piece, the I&C Technician observed water bubbling at the bolt hole. An inspection of the area indicated that an active water leak was not observed to be present. The detector lead shield was removed, and it was observed that the bottom of the lead shield was wet but the detector and its cavity were dry. Further examination resulted in discovery of possible evidence of leakage at an air test hole (residue noted) that is part of the pipe assembly (studding outlet) for R-17. On December 12, 2003 at 1224 hours, both trains of the Component Cooling Water (CCW) System were declared inoperable. This condition was based upon the discovery of less than one half of one millimeter of liquid in the cavity of the studding outlet of the R-17 detector housing. Chemistry analyses of the residue and liquid supported the conclusion of CCW leakage. This evidence of leakage was associated with Section XI Class 3 piping, and thus rendered both trains of component cooling inoperable, due to this being in a common header. A Technical Specifications guided power reduction was commenced at 1315 hours. The root cause of the pipe assembly flaw or confirmation that there is an actual flaw is not known at this time, because the inner weld to the studding outlet that is suspected to be flawed is not accessible during power operation. The corrective action taken was to move the pressure boundary, by means of installing a plug in the air test hole per Temporary Change Request 03-036. The CCW System was declared operable, the unit shutdown was terminated, and the reactor was returned to 100 percent power. This report does describe a safety system (CCW) functional failure.
3062003001 | Prairie Island 2 | 03/14/2003 | 05/13/2003 | ML03141002 | <strong>Exceeded Technical Specification Completion Time</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2003, Unit 2 was operating at 100 % power, the NRC Senior Resident Inspector was performing a routine review of operability determinations when he suspected that an operability determination for a "pinhole" leak identified on a ¾ inch cooling water line for the Component Cooling Heat Exchanger did not meet regulatory guidance. The Senior Resident Inspector contacted Engineering to discuss the issue. Following this discussion, engineering representatives concluded that the Cooling Water Header should be considered inoperable (per the guidance of Generic Letter 90-05) until a code repair could be completed. Prairie Island Technical Specification 3.7.8.B for "One CL supply header inoperable", has a Completion Time of 72 hours. When the leak was first discovered on January 25, 2003 the operability determination concluded that the system was "Operable but Degraded" and that immediate corrective action was not needed. Since the operability determination didn't meet GL 90-05 guidance, the system was considered "Inoperable" from that date until a code repair was completed on March 15, 2003. Based on that conclusion, the system exceeded the completion time and thus is considered a condition prohibited by Technical Specifications.
3062003002 | Prairie Island 2 | 07/26/2003 | 09/24/2003 | ML03273129 | <strong>Automatic Actuation of Unit 2 Emergency AC 4KV Bus 26 Load Sequencer</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2003 while operating at 100% power, a ground fault on an underground 13.8kV feeder from the substation resulted in a loss of power to a Unit 2 Safeguards 4kV Bus when substation breakers opened to clear the fault. As designed, the Bus Load Sequencer automatically initiated load rejection and load restoration following transfer to the Station Reserve Transformer. The Charging Pumps tripped as a result of the momentary loss of power to the bus, and charging/letdown automatically isolated. Operators manually started one Charging Pump and letdown was restored. The Reactor Vessel Gap Cooling Fan, Containment Dome Recirculation Fan and two Fan Coil Units (FCUs) also tripped on the momentary loss of power to the bus. The FCUs auto-started as designed, and the other fans were manually restarted after the bus was re-energized. Technical Specification 3.8.1 Condition A was entered due to loss of one path from the grid and the "Required Actions" were completed. An 8-hour Non-Emergency Notification was made to the NRC due to the unplanned Bus Auto Sequencer Actuation. The cause of the event was determined to be a "phase to ground" fault across the dielectric compound that had leaked out of and over the A Phase G&W Electric 13.8kV cable termination. Water from within the termination that entered via the cable jacket, is suspected to have provided the path to ground for the fault. The failed termination was replaced with a "3M Cold Shrink" termination and the 13.8 kV feeder was returned to service on August 8, 2003.
3112003001 | Salem 2 | 03/29/2003 | 05/22/2003 | ML03154056 | <strong>Manual Reactor Trip Due to Degradation of Condenser Heat Removal</strong><br /><i>Abstract:&nbsp;</i>A manual reactor trip was initiated at 0442 on March 29, 2003, with reactor power level at approximately 80%. The manual reactor trip was initiated in response to degradation of the normal plant heat sink when three of six Circulating Water (CW) pumps were emergency tripped due to loss of the CW traveling screens, with a fourth pump already out of service for condenser water box cleaning. All safety systems operated as designed following the reactor trip. The unit was stabilized in Mode 3 with the reactor at normal operating temperature and pressure with core cooling being provided by the auxiliary feedwater system and main steam dumps to the condenser. The cause of manual reactor trip is attributed to the inability of the Unit 2 Circulating Water (CW) system to handle the excessively high river debris (detritus, hydroids, trash, etc.) levels in the Delaware River due to the design capability of the CW traveling screens. The CW traveling screen shear pins were replaced, the condenser water boxes were cleaned and Operations procedures were reviewed and modified as appropriate to assist plant operators in actions to take during high detritus levels. An ongoing CW improvement project is developing CW traveling screen improvements to increase the reliability of the CW system. This report is being made in accordance with 1 OCFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the system listed in paragraph (a)(2)(iv)(B)."
3112003003 | Salem 2 | 11/23/2003 | 01/20/2004 | ML04029058 | <strong>Manual Reactor Trip Due To Dropped Control Rod</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2003, during low power physics testing with control bank D control rods at 209 steps, control rod 1D4 dropped in the reactor core. At 0507 hours, the Operating crew entered the abnormal procedure for a dropped control rod. Based upon the dropped rod causing the reactor to go subcritical, the abnormal procedure directs all rods to be inserted. The reactor was manually tripped as directed by the Control Room Supervisor. The unit was stabilized in Mode 3 with the reactor at normal operating temperature and pressure with core cooling provided by the auxiliary feedwater system and main steam dumps to the condenser. The cause of the dropped rod and subsequent manual reactor trip is attributed to a blown fuse (10amp) for control rod 1D4. The fuse blew as a result of infant mortality. In addition to the infant mortality, the present 10 amp fuses in the rod control system have minimal margin to prevent failure of the fuse during maximum peak current periods based on a study performed by the vendor of the rod control system. This minimal margin may have also contributed to the fuse blowing. A design change was implemented to replace the existing 10 amp fuses with higher amperage fuses in the Unit 2 rod control system. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph(a)(2)(iv)(B)."
3132003001 | Arkansas 1 | 08/29/2003 | 10/28/2003 | ML03303039 | <strong>Reactor Trip Due to Automatic Actuation of the Reactor Protection System on High Reactor Coolant System Pressure and Actuation of the Emergency Feedwater System Resulting from a Lightning-Induced Closure of the Main Turbine Governor Valves</strong><br /><i>Abstract:&nbsp;</i>At 1428 CDT on August 29, 2003, ANO-1 experienced an automatic actuation of the Reactor Protection System due to high Reactor Coolant System (RCS) pressure. The RCS high pressure condition was caused by the inadvertent closure of the main turbine governor valves due to a lightning-induced Electro Hydraulic Control (EHC) System malfunction. Following the trip, the main generator output breakers failed to open automatically due to the failure of both the primary and secondary reverse power relays to trip. The output breakers were manually opened approximately 1.5 minutes after the reactor trip. Main Feedwater Block Valve CV-2675 to the ''B" Once-Through Steam Generator failed to fully close resulting in erratic control of feedwater flow to the steam generator. The Emergency Feedwater Initiation and Control System actuated as expected and initiated emergency feedwater flow to the affected steam generator. Failure of CV-2675 to close was due to a failed rectifier that supplies DC voltage to the valve's clutches. The damaged and failed components were replaced and the main feedwater block valve and main generator output breakers were tested to verify operability. The EHC System and its power supplies were tested and found to be satisfactory. Improvements to the EHC System to provide isolation for the interlock circuit for the main generator output breakers are being developed.
3152003001 | Cook 1 | 01/15/2003 | 03/17/2003 | ML03085013 | <strong>Unit 1 Turbine and Reactor Trip Due to Main Transformer Fault and Fire</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2003, at approximately 2010 hours, a fault occurred in the Unit 1 main transformer. The fault caused the current differential relays to actuate resulting in an automatic trip of the main transformer. A sudden internal fault within the main transformer ruptured the transformer oil tank resulting in a loss of oil and a fire. The loss of the main transformer precipitated an automatic trip of the main generator and an immediate turbine and reactor trip. The main transformer fire was extinguished within 35 minutes of the event with one minor ref lash, which was promptly controlled and extinguished by onsite fire brigade members. One minor personnel injury occurred requiring off site medical attention. An Unusual Event was declared based on a fire of more than 15 minutes in duration within the protected area. All safety-related components functioned properly and no significant discrepancies in equipment time responses were noted. In accordance with 10CFR 50.72(b)(2)(iv)(B), 10CFR 50.72(b)(2)(xi), and 10CFR 50.72(b)(3)(iv)(A), all, applicable event (EN #39513) and emergency plan required notifications were completed in a timely manner. As such, this LER is being submitted in accordance with the requirements of 10CFR 50.73(a)(2)(iv)(A) for a condition resulting in an automatic actuation of the reactor protection system. A one-hour report was completed at 2105 hours and the remaining three reports were completed by a single notification at 2339 hours. The apparent cause of the event was a sudden internal fault within the main transformer. Corrective actions included replacement of the main transformer. Other non-safety related components damaged by the resultant fire were either repaired or replaced.
3152003002 | Cook 1 | 03/23/2003 | 03/28/2003 | ML03099054 | <strong>Technical Specification 3.3.3.1 Required Special Report for Inoperable Radiation Monitor 1-MRA-1701</strong><br /><i>Abstract:&nbsp;</i>This special report is provided in accordance with the special reporting requirements specified in Donald C. Cook Nuclear Plant (CNP), Technical Specifications (TS) 3.3.3.1, Action 22B. Radiation Monitor 1-MRA-1701, "Steam Generator #2 Power Operated Relief Valve (PORV) 1-MRV-223 outlet radiation detector," has been inoperaoable since March 16, 2003, therefore exceeding the allowed 7 days specified in TS 3.3.3.1, Action 22B. On Sunday, March 16, 2003, at 1119 hours, 1-MRA-1701, Unit I Steam Generator #2 PORV, 1-MRV-223 radiation monitor, went into a high alarm during source check operation. The high alarm cleared after 15 minutes with no action taken. Based on this condition of unreliable indication, the control room shift declared 1-MRA-1701 inoperable. Subsequently, on Saturday, March 22, 2003, at 0243, 1-MRA-1702, Unit 1 Steam Generator #3 PORV was declared inoperable, in accordance with TS 3.3.3.1, to allow de-energization of 1-MRA-1700, "Steam Generator safety relief PORV Loops 2 and 3 monitor," for Data Acquisition Module (DAM) card replacement in support of 1-MRA-1701 troubleshooting. Corrective actions have been performed, 1-MRA-1701 and 1-MRA-1702 were both returned to operable status at 1300, Friday, March 28, 2003.
3152003003 | Cook 1, Cook 2 | 04/24/2003 | 11/05/2003 | ML03318011 | <strong>Supplemental LER for Dual Unit Manual Trip Due to the Failure of the Intake Traveling Screens and Failure to Comply with Technical Specification 3.8.1.1</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2003, between 0255 and 0305 hours, a large school of alewives began impinging on the traveling water screens (TWS) located upstream of the common forebay of the circulating water (CW) and the essential service water (ESW) systems. As the volume of fish impinging on the TWS increased, the TWS system was overwhelmed. Differential pressure across the screens increased rapidly, resulting in most of the screens stopping due to either shear pin failure or tripping of breaker thermal overloads, and the eventual failure of multiple screen panels within the TWS system. As a result of the screen panel failures, the fish subsequently entered the suction of the CW and ESW pumps. Components serviced by the CW and ESW pumps began fouling. At approximately 0327 hours, Unit 1 was manually tripped due to fouling of the main feed pump condensers and at approximately 0330 hours Unit 2 was tripped due to degraded forebay conditions. Donald C. Cook Nuclear Plant (CNP) verified the availability of offsite power as specified by Action e of Technical Specification 3.8.1.1. However, the verification was not completed within one hour as required by the technical specifications. The root cause of the event included the lack of a fully-developed operational response to debris intrusion, the failure to maintain the TWS system, and the failure of CNP to address long-standing or repetitive equipment problems. Corrective actions include flushing and inspection of affected components, repair of the damaged TWS components, improvements in CNP's debris intrusion mitigation strategy, enhanced maintenance program for the TWS, and the development of action plans to address the top equipment reliability concerns. This condition is reportable in accordance with the reporting criteria established in 10 CFR 50.73(a)(2)(iii) and 10 CFR 50.73 (a) (2)(iv)(A) for the manual trip of both Unit 1 and Unit 2 reactors.
3162003001 | Cook 2 | 01/26/2003 | 02/02/2005 | ML05046020 | <strong>Unit 2 Shutdown In Accordance With Technical Specification 3.8.1.1, A.C. Sources, Action b</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2003, at 0426 hours, Donald C. Cook Nuclear Plant (CNP) Unit 2 was manually shut down in accordance with Technical Specification 3.8.1.1, A.C. Sources, Action b, and normal plant operating procedures, due to the CD Emergency Diesel Generator (EDG) approaching its allowed inoperability time. All remaining safety related equipment performed as required during the shutdown. No anomalies were noted. The CD EDG was removed from service on January 23, 2003, at 0400 hours for planned maintenance and testing. During the post-maintenance testing, unexpected KW load fluctuations were experienced with the EDG. The need for additional troubleshooting prevented completion of the planned maintenance and testing activities within the 72-hour allowed outage time. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) and NUREG-1022, Revision 2, Section 3.2.1, which requires each licensee to submit an LER for the completion of any nuclear plant shutdown required by the plant's technical specifications. This LER is a supplement which reports the root cause and corrective actions for the event. The root cause was unexpected binding of the governor linkage due to insufficient configuration control complicated by a lack of expertise in maintaining the obsolete governing system. Improvements to procedural controls and training of engineering and maintenance personnel were performed to address the condition.
3162003002 | Cook 2 | 02/05/2003 | 02/23/2005 | ML05063023 | <strong>Supplemental LER for Unit 2 Reactor Trip due to Instrument Rack 24 Volt Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2003, at 2058 hours, Donald C. Cook Nuclear Plant (CNP) Unit 2 tripped due to the failure of both redundant 24 volt direct current (VDC) control group cabinet #3 power supplies. This caused the feedwater regulating valve for steam generator #23 to fail closed and the reactor to trip on a feed-flow/steam-flow mismatch coincident with low level in the #23 steam generator. All control rods inserted, the turbine tripped, and the auxiliary feedwater pumps started as expected. Following the reactor trip, the operators closed the main steam isolation valves to limit cooldown. This LER supplement is being submitted in accordance with 10 CFR 50.73(a) (2) (iv) (A) and NUREG-1022, Section 5.1.5. This LER reports the root cause, corrective actions to prevent recurrence, and safety significance of the event. The root cause of the event was age degradation of the Control Group III power supplies. Corrective actions included replacement of the control group power supplies and implementation of an optimized preventive maintenance program to address timely replacement of critical power supplies.
3162003003 | Cook 2 | 03/08/2003 | 02/02/2005 | ML05046028 | <strong>Supplemental LER for Unit 2 Technical Specification 3.7.1.2 Limiting Condition for Operation Exceeded for Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>This supplemental LER is being issued to update the causal and corrective action statements. At 0400 hours on March 5, 2003,Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.1.2, Action 'a' was entered to perform routine maintenance on the Unit 2 West Motor Driven Auxiliary Feedwater (MDAFW) pump. During post-maintenance testing, a loud 'buzzing' noise was heard emanating from the vicinity of the pump motor. A supporting/refueling evaluation was performed, which eliminated the pump, breaker, or system alignment as the possible source of the noise. At this point, the decision was made to replace the suspect motor. Initially, Indiana Michigan Power (I&M) had expected to complete the replacement of the West MDAFW pump motor within the allowed outage times specified in TS 3.7.1.2. However, unanticipated delays prevented the completion of this activity within the allowed outage time. Therefore, I&M requested, and was granted, enforcement discretion on March 8, 2003. The apparent cause of the Unit 2 West MDAFW pump motor noise was loose air baffles due to mounting hole deformation as determined by the vendor's as found condition analysis. The cause for the failure to complete the motor replacement within the allowed outage time was inconsistent maintenance work practices and inadequate interface requirements that resulted in a lack of command and control process for short term LCO activities. Corrective actions to prevent recurrence included the establishment of administrative guidance to ensure the appropriate techniques and tools are used when performing work on critical components, and the development and satisfactory completion of coupling installation training. Also, going forward, I&M established a team to respond to equipment issues that challenge short duration allowed outage time. I&M determined that no net increase in risk was associated with extending the TS 72-hour allowed outage time by an additional 36 hours to restore the West MDAFW pump to an operable status. Although the proposed action deviated from a requirement in TS 3.7.1.2, it did not affect any safety limits, setpoints in the TS, or other operational parameters, nor did it affect any margins assumed in the accident analyses. In addition, the redundant Unit 2 East MDAFW pump and TDAFW pump continued to be operable to perform their required design function. The Unit 2 West MDAFW pump motor was replaced with a spare motor and the pump was declared operable at 0246 hours on March 9, 2003.
3162003004 | Cook 2, Cook 1 | 04/26/2003 | 06/25/2003 | ML03182063 | <strong>Weight of Ice Basket Below Minimum Allowed in Technical Specification 3.6.5.1</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2003, Donald C. Cook Nuclear Plant (CNP), during the performance of a routine inspection of the ice bed within the Unit 2 ice condenser, identified that ice basket 11-7-1 weighed 1125 pounds (lbs.). Technical Specification (TS) 3.6.5.ld requires that the ice bed shall be OPERABLE with each ice basket containing at least 1144 lbs. of ice (end-of-cycle). Therefore, the weight of ice basket 11-7-1 did not meet the minimum required weight specified in TS 3.6.5.1d. This condition is reportable pursuant 10 CFR 50.73(a)(2)(i)(B). During the extent of condition evaluation for this event, CNP discovered that during the Unit 1 2002 refueling outage ice basket 24-1-7 fell below the minimum TS weight limit. Ice basket 24-1-7 was emptied and refilled with 1445 lbs. of ice. This condition was not recognized as being reportable at that time. The failure to initiate an LER for ice basket 24-1-7 has been entered into the CNP corrective action program and will be reported in LER 50-315/2002-008-00. Ice basket 11-7-1 was emptied, inspected for damage, and refilled with 1484 lbs. of borated ice. Additionally, in accordance with TS 4.6.5.1.b.2, upon discovery of the low weight in ice basket 11-7-1, an additional 20 ice baskets within the same bay were weighed. The average weight of the 20 additional ice baskets and the discrepant basket (ice basket 11-7-1) was greater than 1144 lbs. Additional administrative requirements will be added to the ice basket inspection procedure to ensure discrepant conditions are evaluated prior to the basket being emptied.
3162003005 | Cook 2 | 12/30/2003 | 02/17/2004 | ML04055041 | <strong>Unit 2 Reactor Trip due to Steam Flow/Feed Flow Mismatch Occurs</strong><br /><i>Abstract:&nbsp;</i>On December 30, 2003, at approximately 1328 Eastern Standard Time, the Unit 2 reactor automatically tripped on low steam generator water level coincident with feed flow less than steam flow for Steam Generator #22. Just prior to the trip, the Control Room Instrument Distribution (CRID) IV inverter transferred to the alternate power supply. A Feedwater Isolation Relay (K666)(2), powered from CRID IV, opened. The opening of the relay initiated a seal-in closure signal to Steam Generator #22 and #23 Feedwater Isolation Valves (2-FMO-202 and 2-FMO-203), resulting in a loss of feedwater flow to Steam Generators #22 and #23 and produced a low steam generator water level trip coincident with feed flow less than steam flow. Following the reactor trip, the Unit Output Breakers failed to automatically open because a Main Turbine Stop Valve position indicator failed to provide a closed indication. The Unit Output Breakers were manually opened in accordance with the reactor trip response procedure. All safety components started and performed as expected. The initiator of the reactor trip was determined to be a momentary ground on the GRID IV bus, which occurred during the conduct of instrument calibration. The ground caused the automatic transfer of CRID IV to the alternate power source. The voltage drop on the CRID IV bus caused the Feedwater Isolation Relay to open. The root cause of the event has been determined to be inattention on the part of the Instrument and Control Technician who was performing the calibration. Corrective actions include the establishment of enhanced controls for the disconnecting and connecting of electrical leads.
3172003001 | Calvert Cliffs 1 | 01/06/2003 | 03/07/2003 | ML03071026 | <strong>Failure of 4 kV GE Breaker Due to Cracking in Auxiliary Switch Cam Follower</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2003, with Unit 1 and Unit 2 operating at 100 percent power, the 1B Diesel Generator (DG) Breaker, 1BKR152-1403, Circuit Breaker Assembly 199, failed to close on demand during a required surveillance test. Breaker 1BKR152-1403 is the output breaker for the 1B-DG, which provides power to 4 kV Alternating Current Vital Bus 14. The emergency diesel generators provide a dependable onsite power source capable of starting and supplying the essential loads necessary to safely shut down the plant and maintain it in a safe shutdown condition under all conditions. Subsequent investigation revealed Breaker 1BKRI52-1403 could not have been relied on to perform its safety function since the date of the last required surveillance test on December 9, 2002. The immediate physical cause for the breaker failing to close on demand was a physical failure in one of the auxiliary switch cam followers. The auxiliary switch contact provides a close signal to the associated circuit breaker. The auxiliary switch contact will not perform its intended function with a broken cam follower. The failure of Breaker 1BKR152-1403 caused the 1B DG to be unavailable to respond and meet its intended safety function during a design basis event. The emergency on-site power safety function was maintained by the 1A DG during this period.
3182003001 | Calvert Cliffs 2 | 02/23/2003 | 04/23/2003 | ML03115000 | <strong>Emergency Air Lock Containment Penetration Closure Requirements Violation</strong><br /><i>Abstract:&nbsp;</i>Calvert Cliffs Nuclear Power Plant's Technical Specifications requires one door in the emergency air lock (a containment penetration) to be closed during core alterations or during movement of irradiated fuel assemblies within the Containment Building. However, on February 24, 2003 at 1500 during a Containment Building tour, it was identified that the Unit 2 Emergency Air Lock was not in the Technical Specification required status. Specifically, "daylight" was seen around a hose penetrating the emergency air lock temporary closure device. The emergency air lock temporary closure device can be used in place of an emergency air lock door. Subsequent investigation determined that the violation occurred on February 23, 2003 at approximately 1300 when a contract employee cut through the foam sealant in the temporary closure device to install an oxygen hose needed to support steam generator replacement activities. The oxygen hose was removed and the hole was sealed on February 25, 2003, prior to commencing core off-load. However, since core alterations (specifically control element assembly uncoupling) were performed on February 23, 2003 from 0955 until 1805, a condition existed that is prohibited by the plant's Technical Specifications.
3182003002 | Calvert Cliffs 2 | 04/19/2003 | 06/18/2003 | ML03176017 | <strong>Unintentional Reactor Protective System Actuation During Plant Heatup</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2003, at approximately 1530 hours, the Calvert Cliffs Nuclear Power Plant Unit 2 Reactor Trip Circuit Breakers opened automatically on a trip signal from the Reactor Protective System. The trip signal was caused by a steam generator (SG) low pressure trip input. Unit 2 was shutdown with a plant heatup under way. Although Unit 2 Reactor Trip Circuit Breakers were closed to support surveillance testing, control element drive motors were de-energized, and control element assemblies were fully inserted into the core. The actuation of the reactor trip protective function occurred during plant heatup when the low SG pressure trip bypass signal cleared at approximately 749.8 psia and the low SG pressure trip, which had not reset from the original shutdown, completed the logic circuits to initiate a reactor trip. Investigation revealed that both the low SG pressure trip and bypass functions were within allowable setpoints. The low SG pressure trip circuitry has a non-adjustable reset function that clears the trip signal approximately 25-40 psig above the trip setpoint. This reset function is a characteristic of each low SG pressure trip circuit card and is not a calibrated value. The combined setpoint and reset function overlap represented no failure of any specific component but identified an off-normal situation that will be procedurally avoided in the future.
3182003003 | Calvert Cliffs 2 | 05/28/2003 | 07/23/2003 | ML03211003 | <strong>Reactor Trip Due to Main Turbine Governor Valves Closing</strong><br /><i>Abstract:&nbsp;</i>At 11:34 AM on May 28, 2003, Calvert Cliffs Unit 2 experienced an automatic reactor trip from 100 percent power. The automatic reactor trip was initiated by the Reactor Protective System due to the high pressurizer pressure condition that resulted from the rapid loss of load. The rapid loss of load occurred when the Main Turbine Governor Valves shut unexpectedly during planned troubleshooting on the Main Turbine controls in Turbine Auxiliaries Electro-Hydraulic Control Cabinet 2T11. A short circuit created during the troubleshooting induced a loss-of-voltage to the valve position limiter causing the governor valves to shut unexpectedly. The short circuit was caused by incorrect use of test equipment during planned troubleshooting; therefore, the root cause of the trip lies in Human Performance in the area of Work Practices. Also, contributing causes in the area of Verbal Communications and Procedural Clarity were identified. Corrective actions include awareness training on the event, its causes and recommendations, procedure changes, and also initial and continuing training on appropriate work practices when using test equipment. The unit was restarted and paralleled to the grid on May 29, 2003 at 7:03 PM.
3182003004 | Calvert Cliffs 2 | 10/11/2003 | 02/06/2004 | ML04062067 | <strong>Technical Specification Exceeded Due to Extended Repair of Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>During a routine inspection of No. 2A Diesel Generator (DG) standby tube oil circulating pump strainer on October 8, 2003, maintenance personnel discovered metal particles lodged in the strainer. The material was identified as aluminum, which is used as bearing material in Fairbanks-Morse DGs. All engine bearing clearances were measured. The No. 10 upper main bearing clearance was determined to be excessive and light scoring was subsequently found on the bearing surface. Limiting Condition for Operation (LCO) 3.8.1, requires two operable DGs and allows one DG to be out of service for 72 hours. Because repairs to the No. 2A DG could not be completed in the allowed time, repair and testing of the DG required enforcement discretion from the Nuclear Regulatory Commission for Unit 2 to remain in operation during completion of the repair. This regional enforcement discretion request was approved at 5:45 p.m., October 10, 2003 following a phone discussion with Nuclear Regulatory Commission staff at 2:00 p.m. that same day. At 2:00 a.m. on October 11, 2003 the No. 2A DG exceeded the 72 hour LCO Completion Time. Unit 2 remained in the LCO 3.8.1, Condition H until No. 2A DG was tested, and returned to service after completing repairs to No. 10 upper main bearing.
3212003001 | Hatch 1 | 06/09/2003 | 08/08/2003 | ML03143028 | <strong>Broken Reactor Protection System (RPS) Neutral Bolt Results in RPS Bus Trip</strong><br /><i>Abstract:&nbsp;</i>On 06/09/2003 at 0445 EDT, Unit 1 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, the "A" Reactor Protection System (RPS, EIIS Code JE) bus (1C71) tripped while the RPS MG Set (1C71SOO1A) continued to run with the output breakers closed in. The design of the RPS is "fail-safe" in that loss of power or control signal causes systems powered by the RPS power supply to change states to their emergency configurations. Thus, the trip of the bus caused Group 2, Group 5, and inboard small-bore Group 1 Primary Containment Isolation System (PCIS, EIIS Code JM) valves to receive an automatic isolation signal. The Main Control Room Environmental Control System (MCRECS, EIIS Code VI) entered the pressurization mode; both units' Standby Gas Treatment Systems (SGTS, EIIS Code BH) initiated; the Primary Containment Hydrogen and Oxygen Analyzers (EIIS Code IK) isolated. Also, the Reactor Water Cleanup (RWCU, EIIS Code CE) system, the Fission Product Monitoring (FPM, EIIS Code IJ) system, and the operating Steam Packing Exhauster tripped. Licensed personnel verified the proper plant response to the initiating signal per procedure 34AB-C71-002-1S, "Loss of RPS." By 0607 EDT, licensed personnel energized the RPS bus from its alternate supply and affected systems were subsequently returned to their normal lineups. The cause of the RPS bus trip was determined to be a broken neutral RPS cable bolt located in panel 1 C71-P001. The broken bolt was removed and replaced with a new bolt.
3212003002 | Hatch 1, Hatch 2 | 10/03/2003 | 12/02/2003 | ML03325053 | <strong>Potentially Non-Conservative Setpoints Result in Inoperable Oscillating PowerRange Monitor System</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2003, with Hatch Units 1 and 2 operating in the Run mode at 100% of rated thermal power, the Oscillating Power Range Monitor (OPRM) system for each Hatch unit was declared inoperable. The declaration was made based on the anticipated issuance of a 10 CFR Part 21 communication by General Electric (GE) concerning the adequacy of the OPRM period tolerance and cut-off frequency setpoints. The cause of the event was review of data from a recent industry instability event at Nine Mile Point - Unit 2. This review found that the OPRM period tolerance and cut-off frequency setpoints were set such that too many valid oscillation counts were reset during the event. Consequently, GE provided new recommendations for these setpoints. Since the Plant Hatch setpoints were not within the recommended ranges, the Unit 1 and 2 OPRMs were declared inoperable. The corrective actions consisted of: 1) implementing the alternate method of detection and suppression of thermal hydraulic instabilities and 2) resetting the setpoints to the values recommended by GE and subsequently declaring the Units 1 and 2 OPRM systems operable.
3212003003 | Hatch 1 | 11/17/2003 | 01/16/2004 | ML04021032 | <strong>Residual Heat Removal Service Water Pump 1C Inoperable For Its FailureTo Meet Seismic Requirements</strong><br /><i>Abstract:&nbsp;</i>On 11/17/2003 at 1400 EST, Unit 1 was in the Run mode at a power level of approximately 2516 CMWT (91.1 percent rated thermal power). At that time, personnel replacing corroded anchor bolt nuts securing the 1C Residual Heat Removal Service Water (RHRSW) pump identified corrosion on two of the nuts to the extent that the adequacy of the seismic supporting capability of the nuts for that pump was questionable for the design loads. This postulated seismic failure of the 1C RHRSW pump could have prevented this pump from being able to perform its design function during a seismic event. Because the corrosion of the nuts occurred over time, and based upon the extent of the corrosion found on the nuts securing the pump, it was concluded that this condition may have existed for a period of time longer than the 30 days allowed by the plant's Technical Specifications 3.7.1 Condition A. The Residual Heat Removal Service Water pumps are used in the long-term containment heat removal mode. This event was caused by untimely corrective action. Additional procedure guidance has been provided to address the Operability of components that are identified to exhibit progressive degradation. The corroded nuts on the 1B, 1C, and 1D RHRSW pumps were replaced. The bolts on 1A RHRSW pump were inspected and determined to not have any gross corrosion. The Unit 2 RHRSW pumps were inspected and found to have some degree of corrosion present. This was evaluated by a civil engineer and determined to not present an operability concern.
3232003001 | Diablo Canyon 2 | 02/13/2003 | 03/14/2003 | ML03078046 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>During the Unit 2 eleventh refueling outage with the unit defueled, analysis of Steam Generator (SG) eddy current test results indicated that greater than one percent of the active tubes were defective. On February 13, 2002, at 1645 PST, PG&E made a nonemergency report to the NRC as required by Technical Specification (TS) Table 5.5.9-2, "Steam Generator (SG) Tube Inspection," and 10 CFR 50.72(b)(3)(ii)(A), "Degraded Condition." On February 13, 2002, PG&E notified the NRC of the preliminary results of the eddy current inspection findings in accordance with TS 5.6.10.d.5. PG&E informed the NRC that outside diameter stress corrosion cracking (ODSCC) at the tube support plate (TSP) intersections exceeded the conditional burst probability reporting threshold of 0.01. PG&E also informed the NRC that circumferential indications were detected in a row 5 tube U-bend. The U-bend defects are due to primary water stress corrosion cracking (PWSCC). The TSP defects are due to ODSCC. PG&E inspected 100 percent of the SG tube U-bend region with a rotating coil (plus point) probe to ensure all circumferential PWSCC was detected. PG&E also plus point inspected 100 percent of greater than 1 volt distorted bobbin outside diameter indications at TSPs. On March 4, 2003, PG&E presented an assessment of the safety significance of exceeding a probability of burst of 0.01 to the NRC that concluded the safety significance of the inspection results is low.
3232003002 | Diablo Canyon 2 | 02/17/2003 | 04/17/2003 | ML03115041 | <strong>Unanalyzed Condition in the Unit 2 Component Cooling Water System Due to a Valve Liner Failure</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2003, at 0830 PDT, with Unit 2 defueled, Pacific Gas and Electric (PG&E) determined that the unit had been in an unanalyzed condition as a result of the damaged valve liner for Component Cooling Water (CCW) manual valve CCW-2-18. This valve, in its damaged condition, could have caused intersystem leakage between redundant headers in excess of licensing/design requirements. An 8-hour non-emergency report was made to the NRC at 1057 PDT on February 17, 2003, in accordance with 10CFR50.72(b)(3)(ii)(B). The root cause is unknown. PG&E believes the liner was torn as a result of valve manipulation during the Unit 2 eighth refueling outage during an attempt to use this valve as an isolation clearance boundary. Immediate corrective actions included: 1. Replacing the CCW-2-18 damaged valve liner, 2. Verifying the travel stop for valve CCW-2-18 to ensure the valve disc stops on the valve seat, and 3. Verifying the CCW System train separation function for similar butterfly valves in the CCW Systems of both units. Corrective actions to prevent recurrence include requiring periodic testing for similar valves to ensure the licensing bases for header separation and leakage are maintained within requirements.
3232003003 | Diablo Canyon 2 | 03/10/2003 | 04/25/2003 | ML03129001 | <strong>Technical Specification 3.4.12 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2003, at 0829 PST, with Unit 2 in Mode 5 (cold shutdown) during a refueling outage, the Limiting Condition for Operation for Technical Specification (TS) 3.4.12, "Reactor Coolant System (RCS), Low Temperature Over Pressure Protection (LTOP) System," was not met when the Power Operated Relief Valve's (PORV) control switches were placed in the CLOSED position while the Technical Specifications required them to be in the AUTO position. On March 10, 2003, at 0731 PST, with Unit 2 in Mode 5 (cold shutdown) the error was discovered and the PORV control switches were placed in the AUTO position, exiting TS 3.4.12. The root cause of the event was a combination of procedure deficiency and personnel error. The immediate corrective actions taken were to place the PORV control switches in AUTO position, thus restoring the TS condition for LTOP to the RCS. Corrective actions to prevent recurrence include revising the associated operating procedure and coaching the operations crews on the details of the event.
3232003004 | Diablo Canyon 2 | 03/17/2003 | 05/16/2003 | ML03148058 | <strong>Manual Reactor Trip Due to a Single Random Fuse Failure</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2003, at 0818 PST, with Unit 2 in Mode 3, "Hot Standby," licensed utility plant operators responding to a difference between digital rod position indication and demand position indication in the control room, initiated a manual reactor trip in accordance with plant procedures. The plant operators stabilized the plant and technicians identified a single random failure of a control rod moveable gripper fuse. At 1348 PST, plant operators made an 8-hour, nonemergency notification in accordance with 10 CFR 50.72(b)(2)(iv). Plant technicians replaced the fuse and licensed plant operators confirmed proper operation by performance of surveillance testing. The root cause of this event was the single random fuse failure. A review of maintenance and surveillance test results confirmed that the incidence of fuse failures is sufficiently low to presume the failure is a single random fuse failure. Corrective actions to prevent recurrence include revision of Surveillance Test Procedure R-1C, "Digital Rod Position Indicator Functional Test," to include guidance regarding verification of rod motion prior to exceeding 12 steps and operator training regarding the change.
3232003005 | Diablo Canyon 2 | 04/04/2003 | 08/05/2003 | ML03225069 | <strong>Technical Specification 3.7.5.C Required Shutdown Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2003, at 1800 PST, with Unit 2 in Mode 1 (power operation) at 54 percent power, the Limiting Condition for Operation for Technical Specification (TS) 3.7.5.C, "Auxiliary Feedwater System (AFWS)," was not met when Feedwater Check Valve FW-2-377 was determined to have internals installed incorrectly and operators conservatively assumed AFW flow to Steam Generator 2-1 was inoperable for two AFW trains. The two inoperable auxiliary feedwater trains resulted in execution of a TS action statement to be in Mode 4 (Hot Shutdown) within 18 hours. On April 4, 2003, at 2041 PST, Operators made an 8-hour non-emergency notification per 10CFR 50.72(b)(2)(i) and (b)(3)(ii)(A), reference Event #39735. On April 5, 2003, at 1043 PST, Mode 4 (Hot Shutdown) was achieved and the TS 3.7.5.C action statement completed. The cause of feedwater check valve FW-2-377 to be installed incorrectly was personnel error during the recent refueling outage maintenance. Inadequate procedural guidance and a lack of verification contributed to the error. The immediate corrective action was to replace the valve. Corrective actions to prevent recurrence include procedure and vendor manual revisions, and additional verification for this type of maintenance activity.
3232003006 | Diablo Canyon 2 | 04/08/2003 | 06/04/2003 | ML03162037 | <strong>Unit 2 Auxiliary Feedwater Actuation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2003, at 1453 PDT, with Unit 2 in Mode 5 (Cold Shutdown), the auxiliary feedwater (AFW) system automatically actuated on a valid signal when the solid state protection system (SSPS) was placed in service while Steam Generator (SG) 2-1 level was below the AFW system actuation setpoint. The actuation was unplanned. On April 8, 2003, at 1636 PDT, an 8-hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(3)(iv)(A). The root cause is a cognitive personnel error by a utility licensed plant operator. The Immediate corrective actions taken were to restore SG 2-1 level above the SG low-low level actuation setpoint and secure AFW Pump 2-3. Corrective actions to prevent recurrence: An Operations Incident Summary will be promulgated to provide operating experience on this event to all on-shift Operations personnel.
3232003007 | Diablo Canyon 2, Diablo Canyon 1 | 05/27/2003 | 10/10/2003 | ML03289050 | <strong>Technical Specification TS 3.8.4 Violation Due to Common Mode Battery Charger Failures</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2003, with Unit 2 in Mode 1 (power operation) at 100 percent power, battery charger (BTC) 2-1 failed a 1-hour load test. The cause of the BTC failure was electrolytic capacitor degradation on the gate filter module and/or firing module. On June 21, 2003, a review of equipment operating history identified 3 of 5 vital BTCs for Unit 1 and 3 of 5 vital BTCs for Unit 2 failed in service upon demand within the past 15 months. Based on the past history of BTC failures, it was concluded that BTC 2-1 failure did not occur at the time of discovery and was inoperable for a period greater than the completion time of Technical Specification (TS) 3.8.4, "DC Sources - Operating," prior to discovery. Thus, the failure of BTC 2-1 constituted a TS violation in accordance with 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii). The immediate corrective actions included replacement of failed modules with verified acceptable replacements and accelerated testing of all BTCs. The causes of this condition were aged capacitors, and premature capacitor failure, due to a control circuit design deficiency that exposed the capacitors to reverse voltage beyond their intended operating conditions that reduced the electrolytic capacitor service life. Corrective actions to prevent recurrence include revision of plant procedures regarding problem identification and review, initiation, of operability assessment(s), and inclusion of maintenance rule corrective actions in the readiness for restart review requirements. PG&E will revise the design of the BTC circuitry to install components that are correct for the subject electrical environment or replace the BTCs.
3242003001 | Brunswick 2 | 03/21/2003 | 05/15/2003 | ML03141049 | <strong>Main Steam Line Drain Isolation Valve Local Leak rate Test Failures</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2003, during the Unit 2 B216R1 refueling outage, the results of local leak rate testing of the main steam line drain inboard and outboard isolation valves, 2-B21-F016 and 2-B21-F019, determined that the valves would not pressurize and consequently, the Technical Specification primary containment leakage rate limit was exceeded. Following the performance of valve maintenance activities and prior to restart of the unit, post-maintenance leakage rate tests were performed which verified valve leakage rates were within allowable limits. The failure of the valves to minimize leakage rates within allowable limits is attributed to a less than optimum valve design. Corrective actions include future replacement of the valves with a valve design which is more suited for the valve application. Review of Licensee Event Reports within the past three years identified no similar events.
3242003002 | Brunswick 2 | 03/24/2003 | 05/23/2003 | ML03149026 | <strong>Reactor Protection System Instrumentation Out of Calibration Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>In March 2003, during a refueling outage, calibration surveillance activities resulted in the discovery of Main Steam Isolation Valve (MSIV) - Closure Reactor Protection system (RPS) instrumentation setpoints exceeding the Technical Specification (TS) Allowable Value (AV) on four out of eight limit switch assemblies. The cause of the condition is attributed to having the required as-left setpoint value for the switches set too close to the TS AV for the calibration method being used. A revised required as-left setpoint value and an improved calibration method were implemented in the calibration procedure and initially used during the March 2003, refueling outage. The safety significance of this occurrence is considered minimal. Although considered TS inoperable, the degree to which the affected channels were found to be outside the TS AV has been evaluated and it has been determined that the as-found condition resulted in no appreciable decrease in fuel thermal margin nor could it significantly impact peak transient system pressurization. The limit switch assembly setpoints were adjusted to required as-left values below the TS AV in accordance with plant procedures using the improved calibration method and required as-left value. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii)(A).
3242003003 | Brunswick 2 | 04/04/2003 | 06/02/2003 | ML03161099 | <strong>Unit 2 Scram During Startup Due to Electro Hydraulic Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2003, at 1354 hours, during reactor startup following the Unit 2 refueling outage, a primary containment group one isolation occurred, which resulted in a reactor scram from 22 percent rated thermal power. All group one isolation valves closed as expected. The containment isolation signal was caused by low main steam line pressure after the main turbine bypass valves inadvertently opened. The main turbine bypass valves opened due to a malfunction in an Electro- Hydraulic Control (EHC) System pressure regulator. Following the scram, an expected reactor vessel coolant level shrink occurred, causing coolant level to decrease from approximately 187 (normal) to 150 inches above instrument zero. As a result of the low water level, primary containment groups 2, 6, and 8 isolation signals were received. All required isolations occurred as a result of the reactor low water level isolation signal. All control rods fully inserted on the scram and all systems responded as designed. Reactor Core Isolation Cooling was manually started to restore reactor water level to the normal band. The cause of the event was determined to be an intermittent error signal from an EHC card that was improperly engaged in its hardware slot in the EHC pressure control circuitry. Following the event, all cards in the EHC control circuits were verified to be properly engaged. The process for checking card engagement will be enhanced to prevent recurrence of this event. The safety significance of the event is considered to be minimal.
3242003004 | Brunswick 2, Brunswick 1 | 11/04/2003 | 01/05/2004 | ML04007029 | <strong>Loss of Generator Excitation Results In Reactor Protection System and Other System Actuations</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2003, at approximately 1732 hours, Unit 2 received a generator/turbine trip due to loss of generator excitation, which resulted in a Reactor Protection System (RPS) actuation. All control rods fully inserted into the core. Plant response to the transient also resulted in High Pressure Coolant Injection and Reactor Core Isolation Cooling System actuations on low reactor pressure vessel (RPV) coolant level with injection into the RPV Additionally, Primary Containment Isolation System (PCIS) actuation signals for Valve Groups 1, 2, 3, 6, and 8 were received and the valves closed as required. All four Emergency Diesel Generators automatically started but did not load because electrical power was not lost to the emergency buses. The initiator of the plant transient event and system actuations was the failure of the generator exciter inner collector ring and brush holders, which resulted in loss of excitation to the generator. The root cause of the failure is a fabrication deficiency due to poor workmanship at the time of original installation of the collector ring onto the exciter shaft. Weaknesses in brush maintenance, preventive maintenance, monitoring, and trending were also identified as the root cause of the event. The damaged components were replaced. Enhanced exciter brush monitoring has been implemented on both Units 1 and 2. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A). The safety significance of this occurrence is considered minimal.
3252003001 | Brunswick 1 | 01/12/2003 | 03/13/2003 | ML03078076 | <strong>Reactor Feed Pump Trip Results in Specified System Actuations</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2003, at approximately 1552 hours, decreasing reactor coolant level, due to a reactor feedwater pump turbine (RFPT) trip, resulted in the actuation of the reactor protection system (RPS), as well as Group 2 and Group 6 primary containment isolation valve closures. After the plant trip, the four emergency diesel generators (EDGs) started due to an invalid signal generated by switchyard equipment. In addition, the Reactor Core Isolation Cooling system was manually operated to maintain coolant level in the reactor vessel. At the time of the event, Unit 1 was initially operating at 94 percent of rated thermal power. The cause of the RPS and subsequent equipment actuations was attributed to the decrease in reactor vessel level caused by a RFPT 1B trip which was the result of insufficient lube oil pressure margin on the RFPT 1B bearing header during a Main Oil Pump (MOP) trip. With proper margin, the standby MOP would have been able to maintain bearing header oil pressure, thereby avoiding RFPT trip and the event. The cause of the automatic start of the EDGs is the failure of a Power Circuit Breaker (PCB) to open on its initial trip signal, which resulted in the invalid automatic EDG start signal. The safety significance of this occurrence is considered minimal. RFPT 1B is being operated with both MOPS in operation until further investigation can be performed to resolve the rapid oil pressure decrease noted when an MOP is tripped in single MOP operation. The PCB was tested to ensure proper operation and returned to service.
3252003002 | Brunswick 1, Brunswick 2 | 10/05/2003 | 11/26/2003 | ML03336058 | <strong>Oscillation Power Range Monitor (OPRM) Inoperability Due to Inadequate Confirmation Count Performance</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2003, Progress Energy Carolinas, Inc. (PEC) received notification from GE Nuclear Energy (GENE) of a reportable condition in accordance with 10 CFR 21.21(d) (i.e., SC03-20, "Stability Option III Period Based Detection Algorithm Allowable Settings," dated October 4, 2003). SC03-20 identified the potential for numerous, unexpected confirmation count resets in the event of an instability condition. These confirmation count resets could result in the inoperability of Technical Specification (TS) Table 3.3.1.1-1, "Reactor Protection System Instrumentation," Function 2.f, "OPRM Upscale." Therefore, at 1100 Eastern Daylight Time (EDT) on October 5, 2003, the Unit 1 and Unit 2 Oscillation Power Range Monitor (OPRM) channels were declared inoperable in accordance with TS 3.3.1.1, "Reactor Protection System (RPS) Instrumentation," and an alternate method to detect and suppress thermal hydraulic instability oscillations was placed into effect as directed by Condition I of TS 3.3.1.1. PEC is preparing modifications to implement the recommendations of SC03-20 and return the OPRM Upscale function to operable status for both Units. The safety significance of this occurrence is considered minimal. The apparent cause of the event is an incomplete analysis, performed by GENE, when establishing the OPRM's period based detection algorithm (PBDA).
3272003001 | Sequoyah 1 | 08/28/2003 | 10/27/2003 | ML03301026 | <strong>Manual Reactor Trip as a Result of a Main Generator Trip and Loss of Load</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2003, at approximately 1603 Eastern daylight time, main control room (MCR) operators initiated a manual reactor trip as a result of a loss of load event. Preceding the manual reactor trip, plant personnel were performing quarterly simulated oil trip tests on the main turbine. During performance of the thrust-bearing trip test section of the procedure, a main generator trip occurred resulting in a 100-percent loss of load to the unit. MCR operators diagnosed the plant condition, determined that a loss of load event had occurred, tripped the reactor, and took actions to stabilize and maintain the unit in hot shutdown, Mode 3. The turbine tripped as a result of the manual reactor trip. Based on information that the reactor had not tripped and the successful manual trip, MCR operators made an Alert emergency declaration (failure of reactor protection). The immediate cause of the event was a closed instrument isolation valve to the Unit 1 turbine auto-stop oil pressure switch. The event analysis identified two likely causes: 1) failure to properly implement the valve verification process, or 2) failure to maintain a configuration control process. Immediate actions were taken to verify valve positions identified in the extent of condition evaluation. Individuals involved with auto-stop oil pressure switch maintenance were counseled and disciplined. Site personnel were provided event lessons learned that reinforced configuration control requirements. A design change was implemented to add visual indication of auto-stop oil pressure switch actuation.
3282003001 | Sequoyah 2 | 01/01/2003 | 02/26/2003 | ML03058059 | <strong>Reactor Trip Signal as a Result of a Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On January 1, 2003, at 0626 Eastern Standard Time, a steam generator Loop No. 2 low-low level initiated a reactor trip signal. The reactor trip signal did not initiate any pump or valve operation because the unit was already in Mode 5, cold shutdown, and related equipment had been secured or was already in the required position. Before the event, it was determined that the secondary side of the steam generators needed to be drained to support chemistry. In accordance with plant procedures, instrument maintenance technicians were dispatched to bypass the steam generator level reactor trip set points of the reactor protection system. However, the technicians inadvertently bypassed the steam generator low level alarms rather than the low-low level trips. As a result, a trip signal was generated upon draining the steam generator. The cause of the event was an inadequate procedure; the information contained in the procedure was too generic. Contributing to the event, supervisors incorrectly selected which portions of the procedure was to be performed and did not verify the information. Subsequent to the event, the correct steam generator level trip set points were bypassed and work was completed without incident. The involved individuals were counseled and the event was documented in the corrective action program where corrective actions were developed to provide more detailed procedural information.
3282003002 | Sequoyah 2 | 01/24/2003 | 03/25/2003 | ML03086022 | <strong>Limiting Conditions for Operation 3.0.3 Was Entered When Two Refueling Water Storage Tank Level Transmitters Failed During Cold Weather Conditions</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2003, at 0835 Eastern Standard Time, Operations personnel observed that one of the Unit 2 refueling water storage tank (RWST) level transmitters had failed high and another transmitter was observed to be reading higher than normal. Inspections revealed that the transmitters were malfunctioning because of freezing at the sense lines to the transmitters inside the junction boxes. The failures occurred during cold weather. The two RWST level transmitters malfunctioned because the heater circuits designed to prevent freezing in the boxes in which they are located did not operate properly. The malfunctions of the heater circuits were the result of damaged cables supplying power to the heater strips. After adding temporary heat, the two transmitters returned to scale. One transmitter was calibrated and returned to operable status. The other transmitter was replaced, calibrated, and returned to operable status. Evaluation of the cables determined that the root cause of the damage to both cables was excessive pull tension, during installation in December 1982. The evidence suggests that the excess tension resulted from an attempt to pull in kinked cables. The damaged cables were replaced.
3282003003 | Sequoyah 2 | 02/28/2003 | 04/23/2003 | ML03115051 | <strong>Excessive Leakage of a Containment Purge System Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2003, at 1851 Eastern standard time (EST), Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.9, Action b, was exceeded because of excessive leakage through a containment purge exhaust containment isolation valve and the inability to repair the valve within the TS allowed outage time (AOT) of 24 hours. On February 27, 2003, during performance of a surveillance instruction it was determined that containment penetration X-6 leakage was above TS acceptance criteria of .05La. Penetration X-6 contains two 24-inch air-operated butterfly valves. Before expiration of the TS AOT, NRC staff enforcement discretion was obtained for an additional 144 hours to identify the source of leakage, repair or replace the components, and perform verification testing. Troubleshooting found the inboard containment isolation valve had failed to fully close resulting in leakage through the valve seat. The valve failed to fully close because the actuator yoke key sheared as a result of inadequate key engagement. The valve is air operated with the operator mounted below the valve centerline. The key was replaced, the valve was tested and found acceptable, and the system was returned to service. Review of historical documents determined that inadequate actuator key engagement occurred either during plant construction or during valve assembly by the manufacturer. Similar valves will be inspected for adequate key engagement.
3282003004 | Sequoyah 2 | 03/10/2003 | 05/07/2003 | ML03132013 | <strong>Reactor Trip Resulting From a Neutral Over-Current Condition on the 2B Hotwell Pump and a Failure to Perform a Technical Specification Required Action</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2003, at 0918 Eastern standard time (EST), Operations personnel manually tripped the reactor because of a low condensate pressure and the loss of the 2A main feedwater pump (MFP). The event began with the loss of the 2B hotwell pump (HWP) causing the condensate pressure to drop. Subsequently the No. 7 heater drain tank (HDT) pumps tripped off because of a low HDT level resulting from the HDT outlet valve being secured at approximately 60 percent open for maintenance. The 2A MFP and the 2A and 2C HWPs tripped followed by Operations personnel initiating a manual reactor trip. Control room operators responded to the event in accordance with plant procedures. They promptly diagnosed the plant condition, took the actions necessary to stabilize the unit, and maintained the unit in hot standby, Mode 3. The cause of this event was an inappropriate prioritization of the work order to repair the No. 7 HDT outlet valve coincident with the electrical failure of the 2B HWP motor resulting in low and unstable condensate system pressure. The 2B HWP motor was replaced and returned to service. The No. 7 HDT outlet valve was repaired and returned to service. Following the reactor trip, dose equivalent Iodine (DEI) was determined to have exceeded the technical specification (TS) limits. TS require sampling of the reactor coolant system (RCS) for DEI every 4 hours until the activity is within limits. During a review of the TS required actions, it was determined that one of the samples was not taken within the required frequency. The RCS was subsequently sampled and the DEI was determined to be within limits.
3282003005 | Sequoyah 2 | 04/12/2003 | 06/04/2003 | ML03155077 | <strong>Reactor Trip Resulting From a Spurious Turbine Vibration Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2003, at 2221 Eastern daylight time, Unit 2 Operations personnel opened vibration power drawer No. 1, to reset a trip light alarm on the No. 7 turbine bearing. Operations personnel verified that the vibration trip cutout switch was in the cutout position. After resetting the trip light, Operations personnel proceeded to place the drawer back into its normal position. Upon sliding the drawer back into the panel, a spurious turbine vibration trip signal occurred, with a duration of less than one second, initiating an automatic turbine trip and subsequent reactor trip. The control room operators responded to the event in accordance with plant procedures. They promptly diagnosed the plant condition, took the actions necessary to stabilize the unit, and maintained the unit in hot standby, Mode 3. The root cause was determined to be a ground on the Unit 2 main turbine vibration drawer No. 1 causing the main turbine vibration trip relay to actuate. An investigation determined that the drawer wiring had been pinched and several wires had exposed conductors. When the drawer was inserted, it is suspected that one of the exposed conductors shorted against the cabinet casing or shorted with another exposed conductor that caused the relay coil actuation. The exposed conductors were repaired. A temporary modification was implemented on Unit 2 to prevent the main turbine vibration trip relay from actuating.
3282003006 | Sequoyah 2 | 04/24/2003 | 06/18/2003 | ML03170016 | <strong>Failure to Meet Technical Specification Limiting Condition for Operation Action Time for the Component Cooling System</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2003, at 1815 Eastern daylight time (EDT), it was determined that a failure to meet a technical specification (TS) limiting condition for operation (LCO) action time existed for the component cooling system (CCS). On April 21, 2003, at 0045 EDT, the common spare (C-S) CCS pump, that was supplying the B-train loads, was removed from service for maintenance and the 1B-B CCS pump was aligned to supply the B-train loads. At the time of discovery, Unit 2 had exceeded the TS LCO action time specified in LCO 3.7.3 of 72 hours. Upon identification of the condition, the TS LCO was entered, C-S pump maintenance activities were expedited, and a risk evaluation was performed of the condition. The risk evaluation indicated that the existing alignment was of least risk significance while the C-S pump was out of service. A review of the past three years of operator logs was performed, and no other occurrence of exceeding the action time of LCO 3.7.3 was identified. However, the review may be inconclusive because similar pump alignments existed without entry into the TS LCO being documented. The root cause of the event was that operators did not fully understand the TS applicability relative to the CCS equipment alignment. A required reading letter was issued to licensed operators to make them aware of this event and the requirements for entering the LCO. The appropriate operating procedure has been revised to indicate when entry into the LCO is applicable.
3312003001 | Duane Arnold | 02/01/2003 | 03/27/2003 | ML03092045 | <strong>Manual Reactor Scram and Reactor Coolant Chemistry Excursion Due to Punctured Main Condenser Tube Caused by Failed Condenser Deflector Plate</strong><br /><i>Abstract:&nbsp;</i>At 2242 on January 31, 2003, while operating the plant at 93% power, Control Room operators began receiving a series of conductivity alarms. Conductivity levels in the condenser hotwell, reactor feedwater and reactor coolant systems exceeded action levels established in plant procedures. After starting a normal reactor shutdown in response to those procedures, a manual reactor scram was inserted at 0233 on February 1, 2003, due to the rate and magnitude of the continued conductivity increases. The plant was cooled down and Mode 4 (Cold Shutdown) was reached at 1620 the same day. The cause of the chemistry transient was a punctured tube in the main condenser, which allowed water from the Main Circulating water system to leak into the Condensate system. A condenser steam deflector plate was found broken off inside the condenser, and was the cause of the punctured tube. The deflector plate experienced a fatigue failure due to sustained plant operation with a feedwater heater dump valve controlling heater water level; a condition created by the failure of the heater's drain valve. Corrective actions include repair of the heater drain valve, restoration of chemistry parameters, removal of the punctured tube, plugging of other damaged tubes, repairs to the condenser deflector plate, and follow-up inspections of deflector plates in other parts of the condenser. Extensive evaluations were performed for reactor vessel internal components, nuclear fuel, and other plant systems for adverse effects from the chemical excursion. The evaluations concluded there was minimal impact from this event. There was no impact on public health and safety as a result of this event.
3312003002 | Duane Arnold | 02/11/2003 | 04/08/2003 | ML03106034 | <strong>Inadequate Procedure Leads to Failure to Remove Key from Mode Switch When Locked in Refuel Position During Control Rod Movement as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2003 at 0945 hours, with the plant in Cold Shutdown (MODE 4), Control Rod Drive (CRD) exercises commenced utilizing Special Operations Technical Specification (TS) 3.10.4, "Single Control Rod Withdrawal - Cold Shutdown." TS 3.10.4 invokes TS 3.9.2, "Refuel Position One is Rod-Out Interlock" as a sub-tiered requirement. Surveillance Requirement (SR) 3.9.2.1 requires that the Reactor Mode Switch be locked in the Refuel position. The TS Bases for SR 3.9.2.1 defines "locking" as removing the key from the switch. When the key was discovered in the switch at 2041 hours, 23 CRDs had been exercised. While the Reactor Mode Switch remained locked in the Refuel position during the CRD exercises, the key was not removed as required by SR 3.9.2.1. This is considered to be a TS violation, as control rod withdrawal took place with TS 3.9.2 and 3.10.4 not met. The cause of the event was inadequate procedures that did not include a step to remove the key from the switch; coupled with unfamiliarity by the on-shift Operations crew of the Bases requirement to remove the key. Corrective Actions are to add steps to the appropriate plant procedures to remove the key as part of "locking" the Mode Switch. Also, an Operations Department "Hot Item" was prepared to make licensed Operations personnel aware of the incident. There was no safety significance to this event, as the Mode Switch remained in the Refuel position when Control Rods were exercised.
3312003003 | Duane Arnold | 04/20/2003 | 06/19/2003 | ML03176067 | <strong>Reactor Mode Change with an LCO in Effect in Violation of Technical Specification 3.0.4</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2003 at 1938, with the plant in Startup (MODE 2), Limiting Condition for Operation (LCO) 3.5.1 Condition B (One low pressure ECCS subsystem inoperable for reasons other than an inoperable RHR pump) was entered, declaring Low Pressure Coolant Injection (LPCI) inoperable due to Suppression Pool Cooling being in-service to support post maintenance testing. Following completion of post maintenance testing, Suppression Pool Cooling was left running to support other testing scheduled later during that shift. Prior to completion of that testing, the Mode Switch was taken to Run (MODE 1) at 0518 on April 20, 2003. This is considered to be a violation of Technical Specification 3.0.4, which prohibits entry into a Mode of Applicability when an LCO is not met. The causes of the event were confusion about the definition of the Mode of Applicability in Technical Specification 3.0.4 and inadequate communication of the definition once it was determined. Immediate Corrective Actions were taken to make all licensed Operations personnel aware of the definition of Mode of Applicability in Technical Specification 3.0.4 and to stress the importance of communications among crew members and between crews. Follow up Correction Actions will make procedural improvements and provide training to licensed Operations personnel. There was no safety significance associated with this event.
3312003004 | Duane Arnold | 04/20/2003 | 06/19/2003 | ML03176068 | <strong>Unplanned High Pressure Coolant Injection (HPCI) Limiting Condition for Operability (LCO) Caused by HCPI Seal Water Line Crack and Class 2 Leakage</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2003, the plant was in the process of starting-up after completion of Refueling Outage RFO) 18. During the performance of a surveillance test procedure, a small leak was detected on the seal water line on the main High Pressure Coolant Injection (HPCI) System pump. At approximately 1513 CDT, at about 18% power, the HPCI system was isolated and Technical Specification LCO 3.5.1, Condition F, HPCI System Inoperable, was entered. The piping was replaced. The HPCI system was restored to an operable status on April 21, 2003 at about 0436. Visual inspection confirmed that the leak was due to a narrow through-wall opening, approximately ¼” long, at the root of a thread. The pipe appeared to have failed due to excessive bending stresses. The stresses may have been a result of applying torque to the pipe unions to vent the system or by stepping on the piping system. There were no actual safety consequences associated with this event. There was no affect on public health and safety as a result of this event. This event is reportable under 10CFR50.73(a)(2)(v)(D).
3312003005 | Duane Arnold | 11/07/2003 | 01/06/2004 | ML04014034 | <strong>Unplanned Manual Reactor Scram Due To High Reactor Coolant Conductivity</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2003, during a plant startup, a manual reactor scram was inserted due to increasing reactor water conductivity (>5.0 µmho/cm). Plant Abnormal Operating Procedures require a scram to be inserted when conductivity exceeds 5.0 µmho/cm. Conductivity increase begun on November 6, 2003. All plant systems responded as expected to this event including Primary Containment Isolation System groups 2, 3, and 4, which isolated due to reactor water level dropping below 170". The reactor water level drop is normal following a scram from 45% power due to void collapse in the reactor vessel. Reactor water level was restored to normal and the group isolations were reset. Extensive evaluations were conducted and determined the cause of the increasing conductivity to be attributed to a resin intrusion. Trouble shooting activities determined that a single condensate demineralizer, 1T013E, had several septa installed that were not manufactured to the appropriate length. These septa allowed resin to be transported out of the system and subsequently into the reactor vessel. The affected demineralizer was repaired and successfully returned to service. There were no actual safety consequences associated with this event. There was no effect on public health and safety as a result of this event. This event is reportable under 10CFR50.73(a)(2)(iv)(A).
3312003006 | Duane Arnold | 11/25/2003 | 01/26/2004 | ML04034034 | <strong>Unplanned Manual Reactor Scram due to Degrading Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2003, while operating at approximately 20% power, a manual reactor scram was inserted due to degrading condenser vacuum. The plant was operating at reduced power to perform testing to determine a source of excessive air in-leakage. The manual reactor scram was inserted in anticipation of an automatic trip. All plant systems responded as expected to this event including Primary Containment Isolation System groups 2, 3, and 4, which isolated due to reactor water level dropping below 170". The reactor water level drop is expected following a scram from power due to void collapse in the reactor vessel. Reactor water level was restored to normal and the group isolations were reset. Extensive testing and evaluations were conducted and determined the cause of the degrading condenser vacuum was from excessive air in-leakage from a failed welded seam between the High Pressure Condenser and the crossover loop seal. The seam was repaired and a plant startup was commenced on December 4, 2003. There were no actual safety consequences associated with this event. There was no effect on public health and safety as a result of this event. This event is reportable under10CFR50.73(a)(2)(iv)(A).
3332003001 | FitzPatrick | 08/14/2003 | 10/14/2003 | ML03296012 | <strong>Automatic Reactor Shutdown Due to Grid Instability Associated With the August 14, 2003, Transmission Grid Blackout and Related Plant Mode Change with the "A" EDG Subsystem Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003 at 1611 hours, with the reactor operating at 100 percent power, a reactor scram occurred due to unstable conditions on the transmission grid causing rapid cycling of Turbine Control Valves (TCVs). This resulted in low turbine Electro-hydraulic Control System (EHC) oil pressure which caused a "Turbine Control Valve Fast Closure, EHC Oil Pressure - Low" Scram as instrumentation sensed conditions similar to a TCV fast closure - generator load rejection. A Main Turbine trip and generator trip followed approximately thirty-five seconds later, accompanied by a normal fast transfer of plant 4 kV busses to the offsite 115 kV supply. A subsequent loss of offsite power followed approximately two minutes later. Plant Emergency Diesel Generators (EDG) started and provided power to safety related plant loads. A cooldown was conducted using Safety Relief Valves, High Pressure Coolant Injection, and Reactor Core Isolation Cooling. MODE 4 was achieved on August 15, 2003 at 2220 hours. On August 29, 2003 at 1015 hours, during surveillance testing, the A EDG subsystem was determined to be inoperable due to out of tolerance no-load frequency, traceable to recovery from the August 14 event. A plant start-up had occurred subsequent to August 14, with an accompanying plant MODE change prohibited by Technical Specifications.
3332003002 | FitzPatrick | 08/19/2003 | 10/16/2003 | ML03296022 | <strong>Safety Relief Valve Setpoints Outside of Allowable Tolerances</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found setpoints for 11 Safety Relief Valve (SRV) [SB] pilot assemblies, removed at the end of Cycle 15, determined that 3 SRVs were outside the allowable as-found tolerance of 1145 psig +/- 34.3 psig (+/- 3%) required by Technical Specifications (TS) Surveillance Requirement (SR) 3.4.3.1. This report documents the failure to meet this SR for 3 of the 11 SRVs. The effect of 3 SRVs being out of tolerance during Cycle 15 is analyzed in this report. The results of this analysis show that Reactor Pressure Vessel (RPV) overpressure protection and nuclear plant safety were not adversely affected. The cause of the two high out of tolerance SRV setpoints was determined to be corrosion bonding between the SRV pilot disc and seat, a recognized industry generic problem. The cause of the low out of tolerance SRV pilot test failure was determined to be sticking of the air operator following the pilot diagnostic test. This SRV pilot tested satisfactorily on 3 subsequent test lifts.
3342003001 | Beaver Valley 1 | 02/24/2003 | 03/26/2003 | ML03091003 | <strong>Safety Injection and Reactor Trip Due to Inadvertent Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On 2/24/03 at 1548 hours, Beaver Valley Power Station (BVPS) Unit 1 was operating at 100% power, end of core life at steady state conditions, with preliminary Refueling No. 15 work evolutions (scaffold erection) in progress, when the Control Room received Annunciator A1-56 "Steamline Stop Valve Not Fully Open". This alarm was followed by a safety injection and reactor trip due to low main steam pressure. All required safety related systems functioned as required. After the automatic actuation occurred, control room operators noted that all three steam generator pressures were stable at normal post reactor trip values. No indications of a steam leak were observed. The plant was stabilized in Mode 3. The cause for the safety injection and reactor trip was the sudden inadvertent closure of the 'C' Main Steam Isolation Valve (MSIV), which caused a Low Steam Line Pressure safety injection and reactor trip. The west air cylinder rupture disk on the MSIV was damaged due to human error by craft workers installing scaffolding in the area below the MSIV. The rupture disk failed, thereby venting the instrument air pressure resulting in closure of the MSIV. Steam flows in the A and B loops subsequently increased and steam line pressures dropped such that the rate of the steam line pressure decrease in the B loop initiated a safety injection and reactor trip signal. An Unusual Event was declared for this event. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an applicable system.
3342003002 | Beaver Valley 1 | 02/05/2003 | 05/30/2003 | ML03155037 | <strong>Potential Overpressurization of Unit 1 Cable Vaults if a CO2 Discharge Were to Occur Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2003, during an extent of condition review of the potential to over-pressurize a fire area if the Carbon Dioxide (CO2) fire protection system discharges, it was discovered that the East and West Cable Vaults fire areas at Beaver Valley Unit 1 (BV-1) were susceptible to this concern. If the total flooding CO2 fire suppression systems in the East and West Cable Vaults were discharged, the resultant pressure transient could cause the fire barriers within the subject areas to be structurally challenged, causing the fire barriers to be breached. Losing the fire barrier integrity could result in a decrease in C02 concentration in the area, which would reduce the effectiveness of the CO2 system to extinguish the fire. If the fire were not extinguished it could result in the potential for a postulated fire in one fire area to spread to an adjacent fire area. This would invalidate the assumptions made in the BV-1 10 CFR 50 Appendix R fire protection safe shutdown analysis and thus represents an unanalyzed condition. As a compensatory measure, the automatic CO2 suppression systems in the East and West Cable Vaults were disabled on February 5, 2003 at 2150 hours in response to the initial identified issue and a fire watch was established in the affected areas. The fire protection system alarm function remained enabled in order to provide notification in the Control Room if a fire would occur. These measures eliminated the potential for a CO2 overpressure transient condition to occur in the affected areas. The root cause of this event was determined to be insufficient design and system interface applicable to engineering work practices with a secondary cause of inadequate or incomplete design aspects. These were chosen because the impact to the CO2 protected areas, due to the more tightly sealed areas resulting in a higher pressure peak, was never recognized by the fire barrier program owner when the new seals were installed. This condition is reportable pursuant to 10CFR50.72 (b)(3)(ii)(B) (EN# 39573) and 10CFR 50.73 (a)(2)(ii)(B) as an unanalyzed condition that significantly degrades plant safety.
3342003003 | Beaver Valley 1 | 02/27/2003 | 04/25/2003 | ML03121028 | <strong>Automatic Actuation of Emergency Diesel Generator Following Loss of Emergency Bus Offsite Source</strong><br /><i>Abstract:&nbsp;</i>At 1301 hours on 2/27/2003, Beaver Valley Power Station Unit 1 was operating at 58% power and returning to full power operation following a startup from a recent forced outage. During the startup of the 'B' main feedwater pump, an instantaneous ground overcurrent trip occurred on the offsite power to 4KV feeder breaker 1 D6. The opening of the feeder breaker de-energized the non-safety related 'D' bus which had been supplying power to the 'B' main feedwater pump. The 'B' train safety related emergency bus which is normally powered by the 'D' bus, then also became de-energized with the loss of power on the 'D' bus. The 'B' train emergency diesel generator automatically started on the loss of voltage and reenergized the emergency bus, with loads automatically sequenced back onto the bus as designed. The automatic actuation of the emergency diesel generator is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). The direct cause of this event was the unexpected opening of the 4KV feeder breaker 1 D6 from offsite power when the 'B' main feedwater pump was started. The root cause was that the ground sensor cable geometry induced a false ground fault current that actuated the ground fault detection relays. The improper geometry combined with a lowered ground relay setting caused the ground relay to operate on a false ground current and trip the feeder breaker. The safety significance of this event was low.
3342003004 | Beaver Valley 1 | 07/03/2003 | 08/27/2003 | ML03246070 | <strong>Safety-Related River Water Pump Not Declared Inoperable When Vibration Levels Exceeded Allowable Limit</strong><br /><i>Abstract:&nbsp;</i>During a follow-up evaluation to NRC inspector questions regarding previously identified abnormal vibrations on the Beaver Valley Power Station (BVPS) Unit 1 River Water System "A" pump, it was determined on 7/3/2003 that prior vibration data on the "A" pump had exceeded its ASME Section XI Alert Range limit for that pump on 5/13/03, which was not recognized when the vibration readings were first documented. Exceeding this ASME XI limit renders the pump inoperable. BVPS Technical Specification (TS) 3.7.4.1 Limiting Condition for Operation requires that at least two river water subsystems be operable. TS 3.7.4.1 Action requires with less than two river water subsystems operable, restore at least two subsystems to operable status within 72 hours or be in at least Hot Standby within the next 6 hours. The total elapsed time between when the first vibration reading on the "A" river water pump above its ASME XI limit was obtained on 5/13/03 and when the "C" river water pump was placed into service on 5/16/03 was 78 hours and 28 minutes. Since the time to restore compliance to TS 3.7.4.1 was greater than 78 hours, a violation of TSs occurred. This event is reportable pursuant to 10CFR 50.73(a)(2)(i)(B) as an event that previously resulted in a plant condition prohibited by plant TS. The causes of this event were procedure noncompliance in that the vibration monitoring program was not followed and inadequate error detection in that the vibration readings obtained on 5/13/03 were not compared against the ASME XI limits contained in the pump surveillance test procedure. The safety significance of this event was low.
3342003005 | Beaver Valley 1 | 07/18/2003 | 09/15/2003 | ML03266125 | <strong>Non-Conservative Reactor Coolant System Low Flow Reactor Trip Setpoint</strong><br /><i>Abstract:&nbsp;</i>On July 18, 2003, during a routine post-refueling outage review of the Reactor Coolant System (RCS) precision flow calorimetric data from a test procedure on RCS Total Flow Measurement, it was determined that one of the nine channels of RCS flow (3 channels per loop) was set non-conservatively with respect to Technical Specifications. Specifically, it was identified that channel F-1RC-424 on the B-RCS loop was set to 89.2 percent of full power RCS flow when the Technical Specification allowable value for loop flow is greater than or equal to 89.8 percent. The root cause of the non-conservative RCS flow setpoint is an inadequate process to verify RCS flow setpoints are within Technical Specification limits prior to reaching ten-percent power. Since, this condition existed longer than the allowed outage time of 6 hours permitted by Technical Specifications, it was a condition prohibited by plant Technical Specification 3.3.1.1; therefore this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). Additionally, there were two occasions where maintenance removed an operable instrument from service placing the plant in a condition outside of the action statement. Therefore, Technical Specification 3.0.3 was unknowingly in effect and actions to commence plant shutdown were not initiated within one hour. Thus, these events were also conditions that are prohibited by plant Technical Specification and are reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). Review of this event for effect on core damage frequency (CDF) for BVPS Unit 1 was performed and the cumulative safety significance of these events was determined to be small.
3342003006 | Beaver Valley 1, Beaver Valley 2 | 09/22/2003 | 11/12/2003 | ML03321036 | <strong>New Steam Generator Level Uncertainties Identified Which Exceed Available Setpoint Margins</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2003, Westinghouse issued Nuclear Safety Advisory Letter 03-9, which addressed an error in the Westinghouse steam generator water level setpoint analysis due to previously incorrectly addressing a differential pressure which occurs across a mid-deck plate within the steam generator during steam flow. This differential pressure adversely affected the steam generator low-low level setpoint uncertainty for Beaver Valley Power Station (BVPS) Unit 1 and Unit 2. During operation prior to when the steam generator water level low-low setpoints at both BVPS Units were recently raised, there was inadequate margin available to offset this newly identified effect which needed to be addressed as a non-conservative bias in the uncertainty calculations. Therefore, the design basis feedwater line break analysis of record may not be valid since it relied upon steam generator level to initiate a reactor trip. This event is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degrades plant safety since the impact of crediting another reactor trip function which may occur in place of steam generator low-low level during the specific postulated feedline break transient has not been calculated and is unknown. Similarly, this also represents a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition as described in each Unit's UFSAR and is reportable pursuant to 10 CFR 50.73(a)(2)(v)(A). The cause of this event was inadequate Westinghouse design analysis of steam generator mid-deck plate differential pressure. The safety significance of this event was low.
3342003007 | Beaver Valley 1 | 11/13/2003 | 01/07/2004 | ML04013073 | <strong>Inadvertent Reactor Trip During Solid State Protection System Testing</strong><br /><i>Abstract:&nbsp;</i>At 1135 hours on November 13, 2003, the Beaver Valley Power Station Unit 1 reactor received an unexpected automatic reactor trip signal while operating at 100 percent power. The reactor trip signal was inadvertently generated during the performance of a maintenance surveillance procedure on the Solid State Protection System. Instrument and Control Technicians connected a digital volt meter (DVM) across the incorrect terminals in the Reactor Trip Breaker Switchgear cabinet when verifying breaker position contact state. This incorrect action created a current path across an open contact and energized the turbine trip relay. The turbine trip initiated an automatic reactor trip. The operating crew entered Emergency Procedure E-0, and transitioned to ES-0.1 in response to the trip. During the event, all required plant safety systems responded as required. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B)(1). The cause was self-checking and peer checking that did not meet expectations. The `B' train of Solid State Protection System (SSPS) had just been returned to service, exiting the applicable Action of the technical specifications (a two hour allowed outage time). Because the crew had exited the time critical portion of the technical specification, they did not complete the remaining portion of the surveillance procedure with the same sense of rigor as was used in the prior steps. The safety significance of this event was low.
3352003001 | St. Lucie 1, St. Lucie 2 | 02/18/2003 | 03/17/2003 | ML03086020 | <strong>Unescorted Access Inappropriately Approved Due to Falsified Pre-Access Information</strong><br /><i>Abstract:&nbsp;</i>At 1200 hours on February 18, 2003 a review of a contract employee pre-access questionnaire revealed that the contractor had a positive test for THC in 1998 at a non-nuclear facility (hospital). This individual is not currently badged at the Site and access has been denied. However, this contractor had previously been granted access during fall of 2002. The pre-access questionnaire completed for the 2002 access did not contain this information, and no criminal record of the event was found during the background investigation. Had that information been provided, access for this individual would have been denied in 2002. This event is reportable as a one hour phone call per 10 CFR 73.71 in that pre-employment records were incomplete (falsified) and unescorted access would have been denied based on developed information.
3352003002 | St. Lucie 1 | 02/17/2003 | 04/16/2003 | ML03119022 | <strong>Invalid 4.16kV Bus Undervoltage Conditno During Maintenance Caused EDG Start</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2003, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. While St. Lucie maintenance personnel were performing the replacement of a failed 1B3 4.16kV bus undervoltage (UV) relay, a bus UV shed signal was generated. This resulted in momentary loss of the 1B3 4.16kV bus while loads were stripped and reloaded to the 1B emergency diesel generator. During the event all safety equipment operated as designed. FPL could not definitively determine whether the event was caused by personnel error or spurious operation of the UV protection relay. The defective relay was replaced and FPL plans to replace the existing lB3 4.16kV switchgear relays with a different model relay during the next refueling outage.
3352003003 | St. Lucie 1 | 09/25/2003 | 06/04/2004 | ML04161022 | <strong>Fire Seals Inoperable Due to Inadequate Qualification Testing</strong><br /><i>Abstract:&nbsp;</i>On September 25,2003, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. FPL determined that 16 cable tray fire penetration seals were inoperable due to inadequate qualification testing methods. The documented test results do not provide an adequate basis for qualification of the barriers as three-hour fire barriers. Condition reports were initiated for these conditions and fire impairments were logged against the affected fire seals in accordance with the St. Lucie Fire Protection Program. The apparent lack of detail during the initial St. Lucie Unit 1 10 CFR 50, Appendix R licensing activities led to this condition. Compensatory fire watches were verified to be in place at the time of discovery in the affected fire areas. FPL is evaluating corrective actions to resolve the identified condition. Revision 1 of this LER documents that an additional 34 discrepant cable tray fire penetration seals were discovered during a confirmatory walkdown of the Unit 1 Control Room floor penetrations. Revision 2 of this LER documents that of the additional 34 seals identified in Revision 1, 14 of those seals located in reactor turbine generator control boards were found with significant voids during the SL1-19 refueling outage.
3352003004 | St. Lucie 1 | 10/16/2003 | 12/15/2003 | ML03352029 | <strong>Improper Sampling Techniques Led to Operation of NaOH Tank Outside Tech Spec Limits</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2003, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. Chemistry personnel completed their investigation into an out-of-specification low sodium hydroxide (NaOH) sample result of September 19, 2003, and determined that the low concentration condition most probably existed for a time period in excess of the Technical Specification allowed outage time. The event was caused by inadequate mixing as a result of sampling procedures that failed to account for operational and hardware changes to the NaOH tank that had removed the continuous nitrogen sparging of the tank. Contributing to the event, there were several human performance errors including inadequate administrative controls of NaOH tank concentration in the TS surveillance test, and operations and chemistry personnel did not properly ensure that sparging was in operation prior to sampling. Procedural issues that were identified during this event were corrected as part of the corrective actions for this event. The NaOH tank was restored to TS concentration levels on September 20, 2003. This event had no impact on the health and safety of the public because the NaOH tank contained enough chemicals to meet the analysis requirements for pH control.
3352003005 | St. Lucie 1 | 12/03/2003 | 02/02/2004 | ML04035032 | <strong>Condition Prohibited by Tech Specs Due to Failed Containment Vacuum Breakers</strong><br /><i>Abstract:&nbsp;</i>On December 3, 2003, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. During repair activities associated with containment vacuum relief valve FCV-25-8, FPL determined that a common cause failure mechanism affected the past operability of both of the containment vacuum relief valves' actuator quick exhaust valves. The cause of the failures was degradation of the quick exhaust valves' urethane diaphragm that allowed air to bypass the actuator as air exhausted through the quick discharge port. This caused the containment vacuum relief valves to fail to open on demand. Both containment vacuum relief valve quick exhaust valves for FCV-25-7 and -8 were replaced and tested satisfactorily. A preventive maintenance change was also processed to perform a quick exhaust valve overhaul every 36 months. The containment vacuum relief function is provided to protect the containment structure from a vacuum condition caused by an inadvertent cool down from full containment spray and fan cooler actuation. The vacuum relief function is not a design bases accident mitigation function. Therefore, this event had no adverse impact on the health and safety of the public.
3362003001 | Millstone 2 | 02/17/2003 | 04/14/2003 | ML03114034 | <strong>Pressurizer Water Volume Periodically Exceeded the Technical Specifications Limit</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2003, at approximately 0945 with the plant in MODE 1 at approximately 100 percent power, it was identified that the surveillance procedure, SP 2402E, Pressurizer Level Calibration, did not contain the correct differential pressure values necessary to correctly measure the water level in the Millstone Unit No. 2 pressurizer. It was determined that the procedure error resulted in actual pressurizer level being approximately 4.7 percent higher than indicated level. Due to this error, the unit periodically exceeded the Technical Specification 3.4.4a requirement for pressurizer water volume to be maintained less than or equal to 1050 cubic feet (70 percent). The apparent cause of this event was that the surveillance procedure was prepared using an Engineering transmittal that provided incorrect differential pressure values for the calibration of the two pressurizer level transmitters. This error resulted in a loss of configuration control by the Engineering organization. The Engineering documents were revised to reflect the correct differential pressure calibration values for the pressurizer level transmitters. The results were subsequently incorporated into the surveillance procedure and on February 24, 2003 the two level transmitters were recalibrated to the correct values.
3362003002 | Millstone 2 | 03/07/2003 | 04/28/2003 | ML03126063 | <strong>Reactor Trip While Performing RPS Matrix Testing</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2003, at 1439, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred during normal monthly Reactor Protection System (RPS) matrix testing due to a fault in the test circuitry. Specifically, Control Rod Drive trip circuit breaker (TCB) pair TCB-1 and TCB-5 tripped open in addition to the expected opening of TCB pair TCB-3 and TCB-7 when AC Matrix Relay Trip Select switch was rotated to position "3." The opening of both pairs of trip breakers resulted in a reactor trip from full power followed by an automatic turbine trip. All control rods inserted into the core and all electrical busses transferred properly following the trip. Auxiliary Feedwater (AFW) initiated as expected, on low steam generator level. The post-trip plant response was complicated by several additional equipment failures, the most notable being a malfunction of the charging system leading to a loss of all charging. This latter condition is addressed in a separate report. The root cause of the event was historical in nature and determined to be poor workmanship of the original RPS matrix test module dating back to plant startup. Specifically, the keying pin hole was drilled too large in the adapter plate for the AC matrix relay trip select switch (Micro switch model X6210-25AS4-7448) allowing excessive movement of the switch. This movement, in addition to poor quality of soldering and lack of wiring strain relief in the test module, caused strain failure of the wiring at the switch terminal joint. Corrective actions to prevent recurrence included re-drilling the switch keying pin hole to remove excessive switch play, and to inspect for and repair damaged wiring and provide adequate strain relief for wiring as necessary, in the RPS matrix test module. These actions were completed prior to startup.
3362003003 | Millstone 2 | 03/07/2003 | 08/22/2003 | ML03247164 | <strong>The Charging System Did Not Perform Its Design Function in Response to Falling Pressurizer Level</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2003, at 1439 with the plant in MODE 1 at approximately 100 percent power, an automatic reactor trip occurred while performing Reactor Protective System matrix logic and trip path relay testing. The reactor trip resulted in Reactor Coolant System cooldown, and a drop in pressurizer level followed by the auto-starting of both standby charging pumps in addition to the one in operation. The combined flow of the three pumps fell and became erratic, varying from a high of 50 gpm to a low of 0 gpm. Because of this unexpected response, plant operators declared all three charging pumps inoperable and entered the Action Statement for Technical Specification 3.0.3. Pressurizer level was restored using a charging pump aligned to the alternate charging flow through the high-pressure safety injection line, and a plant cooldown was commenced. The Direct Cause of this event was that the Charging Pump Discharge Pulsation Dampeners were inadequately designed to prevent pressure spikes caused by simultaneous pump starts. The Root Cause of this event was a high tolerance for repeat Safety Device Precursor actuation. Specifically, the repeated lifting of the Charging Pump discharge relief valves was tolerated without sufficient consideration of the cause (pressure spike). The corrective action for the Direct Cause is to design and install improved discharge pulsation dampeners. The Corrective Actions for the Root Cause are to revise the Corrective Action Program Description to include guidance, which ensures trends of "Safety Device Precursors" are investigated with an apparent cause investigation, and to develop a list of “Safety Device Precursors,” which will include as a minimum; relief valve lifts, circuit breaker trips, and blown fuses. Application/implementation of the list will be documented in appropriate guidance documents (e.g. equipment reliability trend guidance of the system health reports procedure).
3362003004 | Millstone 2 | 10/11/2003 | 12/03/2003 | ML03346037 | <strong>Reactor Coolant System Pressure Boundary Leakage Event</strong><br /><i>Abstract:&nbsp;</i>This LER reports an event related to reactor coolant system pressure boundary leakage. On October 11, 2003, with the plant in Mode 5 (Cold Shutdown), a visual inspection of Millstone Unit No. 2 pressurizer heater penetrations and pressurizer instrument nozzle penetrations was being performed. Two heater sleeve penetrations were found to show indications of minor leakage as evidenced by boron precipitation build up on the outside of the penetrations. The cause of this event was a through-wall crack in two of the pressurizer heater sleeves as a result of primary water stress corrosion cracking. This allowed primary coolant into the annulus between the pressurizer lower head and the heater sleeve and therefore was a breach of the reactor coolant pressure boundary. Although most industry experience has identified axial cracking, recent inspections at Palo Verde identified the presence of some circumferentially oriented indications, predominantly in the area of the nozzle sleeve above the pressure boundary region. At Millstone Unit No. 2, the potential worst case situation of a circumferential crack that could result in the complete loss of the penetration would be well below the limiting hole size, less than 3 inch, for a Small Break Loss of Coolant Accident, and is therefore bounded by the current analysis basis. The heater elements were removed from the two identified locations, as well as two locations that were identified as leaking during the last refuel outage (2R14), and an ultrasonic test was performed to generally characterize the nature of the flaws. The defects were determined to be axial rather than circumferential and hence significantly less likely to suffer catastrophic failure. The leaking heater sleeves have been repaired by the use of Mechanical Nozzle Seal Assemblies.
3362003005 | Millstone 2 | 10/14/2003 | 11/21/2003 | ML03336070 | <strong>Loss of Shutdown Cooling as a Result of Switching Inverter Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2003, at 0407 with the plant in Mode 5, a loss of shutdown cooling (SDC) occurred when the SDC heat exchanger flow control valve (FCV) failed closed due to a loss of power at vital 120 vac panel VA10. When the FCV closed, the SDC heat exchangers were bypassed and resulted in a reactor coolant temperature rise of approximately 14 degrees F. The loss of SDC is reportable as a loss of safety function in accordance with 10CFR 50.73(a)(2)(v)(B). In addition, as expected upon a loss of VA10, one of the containment radiation monitors sent a signal to close the containment purge valves. Contrary to the normal response, the purge valves did not close and the operators manually closed them from the control room as directed by procedure. This unanticipated plant response did not complicate the event and is not reportable as the containment purge isolation function is not required in Mode 5. Operator action restored power to VA10 within 13 minutes causing the FCV to automatically open and reestablish cooling. The plant declared an Unusual Event (UE) at 0423 (Event Number 40245) when reactor coolant temperature rise exceeded 10 degrees F and subsequently terminated the UE at 0532 after stabilizing plant conditions. The root cause of the event was determined to be a procedure deficiency resulting from using an incorrect version of the vendor technical manual. The operations procedure allows switch manipulations that momentarily parallel two energized inverters without synchronous protection. The corrective actions to prevent recurrence are to modify the operations procedure, vendor manual, and associated training documents to reflect safe operation of the inverter and static switch.
3362003006 | Millstone 2 | 11/27/2003 | 01/23/2004 | ML04034022 | <strong>Two Manual Reactor Trips Due to Turbine Trips Caused by Turbine Vibrations</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2003, at approximately 0617 with the plant in MODE 1 at approximately 20 percent power, the reactor was manually tripped due to high vibration of the Main Turbine. Additionally, on November 28, 2003, at approximately 2205 with the plant in MODE 1 at approximately 11 percent power the reactor was also manually tripped due to high vibration of the Main Turbine. Following the manual reactor trips, all control rods inserted into the core. There were no safety system actuations. All electrical busses transferred properly following the trip, and all emergency diesel generators were operable, but not required. All other plant system responses were as expected. Therefore, these two events have low safety significance. The apparent cause of these two events is excessive turbine bearing vibration due to newly installed LP turbine monoblock rotors. Monoblock rotors are manufactured from a single forging with integral wheels formed by machining. The fact that the wheels are part of the rotor means that rubbing on the wheels can cause a rotor bow due to localized heating. This construction makes monoblock rotors more sensitive to rubbing than built-up rotors. In addition to the monoblock rotor sensitivity, the Millstone Unit No. 2 turbine rotor replacement includes all new packing. New packing also increases the possibility of a rub, as all the clearances are minimum.
3382003001 | North Anna 1 | 03/04/2003 | 04/24/2003 | ML03120069 | <strong>Reactor Vessel Head Penetration Nozzle Leakage</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2003, at 2100 hours Unit 1 was ramped offline for a scheduled refueling outage. On March 4, 2003, at 0854 hours, with Unit 1 defueled, an apparent reactor vessel head through-wall leak was noted during visual inspection of penetration 50. The reactor vessel head was being visually inspected at penetration 50 to follow up on inspection results from the previous outage in 2001. Penetration 50 was found to exhibit boric acid approximately one half inch in diameter at the lower side of the penetration-to- head transition. There was no sign of wastage on the reactor vessel head. This through wall leak has been assessed as a degradation of a principal safety barrier in accordance with 10 CFR 50.72(b)(3)(ii)(A). An 8-hour Non-Emergency Report was made to the NRC at 1033 hours on March 4, 2003. No significant safety consequences resulted from this event since RCS unidentified leakage was well below Technical Specification limits. The health and safety of the public were not affected at any time during this event.
3382003002 | North Anna 1 | 04/13/2003 | 06/05/2003 | ML03168128 | <strong>Entered Mode 4 with an Inoperable Containment Air Lock Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2003, at 1114 hours Unit 1 entered Mode 4 with an inoperable containment personnel air lock. Containment leakage testing was performed as part of the unit start-up activities following a refueling outage. The total containment personnel air lock leakage was identified at 22 standard cubic feet per hour (scfh) with a test procedure limit of = 12.9 scfh. Technical Specification (TS) limit is = 05 La, which equates to = 15.22 scfh. The personnel air lock leakage of 22 scfh was factored into the total containment leakage. The total maximum containment leakage rate was then calculated at 42.32 scfh well below the acceptance criteria of = 182.6 scfh. The requirements of Technical Specifications (TS) were not properly verified resulting in an incorrect assumption that the specified periodic test procedure acceptance leakage limits for the containment personnel air lock were administrative. As such, a condition prohibited by TS occurred and this event is reportable in accordance with 10CFR50.73(a)(2)(i)(B). The health and safety of the public were not affected at any time during this event.
3382003003 | North Anna 1 | 04/19/2003 | 05/30/2003 | ML03160096 | <strong>Manual Reactor Trip Due to Loss of Electro-Hydraulic Control System Pressure</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2003, at 2008 hours, with Unit 1 operating in Mode 1, at 74 percent power following a refueling and reactor vessel head replacement outage, a manual reactor trip was initiated. The manual reactor trip was initiated due to a loss of turbine electro-hydraulic control (EHC) system pressure which caused turbine control valves to drift shut. The cause of the EHC low pressure was a diaphragm failure on the auto stop oil side of the turbine auto stop oil EHC interface valve. At 2323 hours, a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection System and Engineered Safeguards Features System functioned as designed. Therefore, the health and safety of the public were not affected by this event.
3382003004 | North Anna 1 | 06/11/2003 | 07/29/2003 | ML03217062 | <strong>Automatic Reactor Trip Due to Main Transformer Fault</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2003, at 1453 hours with Unit 1 operating at 100 percent power an automatic reactor trip occurred as a result of a main transformer fault. The initiating signal was the Main Transformer Lockout Relay Turbine Trip resulting in a turbine trip/reactor trip. The cause of the main transformer fault was an unused electrical lead disengaging from the no-load tap changer and coming in contact with the transformer casing. At 1718 hours, a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection and Engineered Safety Feature systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
3382003005 | North Anna 1, North Anna 2 | 11/10/2003 | 01/07/2004 | ML04014051 | <strong>Inoperable Hydrogen Recombiner Due to Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2003, at 1030 hours, with Units 1 and 2 operating at 100 percent power, testing of the Unit 2 hydrogen recombiner was being conducted. During testing, the hydrogen recombiner tripped from a low flow condition while attempting to place it in service. An investigation determined that the high and low side isolation valves for the instrument lines to the hydrogen recombiner flow transmitter were closed when they should have been open. This condition existed for greater than the 30-day completion time permitted by Technical Specification 3.6.9. Therefore, this event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) for a condition prohibited by Technical Specifications. The cause of the isolation valves being closed was determined to be inadequate work practices. The isolation valves were subsequently opened and the hydrogen recombiner was successfully started. Testing was satisfactorily completed. This event posed no significant safety implications because no conditions requiring the use of the hydrogen recombiner were experienced during the time the hydrogen recombiner was inoperable. Therefore, the health and safety of the public were not affected by this event.
3392003001 | North Anna 2 | 03/31/2003 | 04/17/2003 | ML03114035 | <strong>Automatic Reactor Trip Due to Steam Flow - Feed Flow Mismatch</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2003, at 1259 hours with Unit 2 operating at 100 percent power an automatic reactor trip occurred. The initiating signal was the "C" steam generator (SG) low level coincident with a steam flow greater than feed flow mismatch caused by closure of the "C" main feed regulating valve. This resulted in a reactor and turbine trip. Closure of the "C" main feed regulating valve was due a blown fuse on the valve driver card. At 1540 hours a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection and ESF systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
3412003001 | Fermi 2 | 07/13/2003 | 08/29/2003 | ML03252058 | <strong>Loss of High Pressure Coolant Injection Safety Function Due to Closure of Steam Supply Valve</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2003, at 2200 hours, during surveillance testing of the High Pressure Coolant Injection (HFCI) system, valve E4150-F003, the Outboard Steam Supply Isolation Valve, failed to close when the close pushbutton was depressed. E4150-F003 is a normally closed valve and had just been successfully stroked open. In accordance with Technical Specification (TS) 3.6.1.3, Primary Containment Isolation Valves (PCIVs), the E4150-F003 valve was declared inoperable and the penetration flow path was isolated by closing and deactivating E4150-F002, the Inboard Steam Supply Isolation Valve. Isolating the HPCI steam supply rendered HPCI inoperable and TS 3.5.1, Emergency Core Cooling System (ECCS) and Reactor Core Isolation Cooling (RCIC) System, was entered. All other ECCS systems remained operable. The event was caused by an electrical contact failure. The normally open auxiliary electrical contact that provides the seal in feature for closing the E4150-F003 valve failed to close when the close pushbutton was depressed. Without the seal in feature the E4150-F003 valve stopped stroking closed when the operator released the close pushbutton. The auxiliary electrical contact that provides the seal in feature for closing the E4150-F003 valve was replaced during the scheduled system maintenance outage. Post maintenance testing was completed and the HPCI system was declared operable on July 18, 2003, at 2107 hours.
3412003002 | Fermi 2 | 08/14/2003 | 12/17/2003 | ML03357018 | <strong>Automatic Reactor Shutdown Due to Electric Grid Disturbance and Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, at approximately 1610 hours, the Reactor Protection System initiated an automatic reactor scram from 100% power as a result of a Turbine Control Valve (TCV) fast closure. The TCV closure was caused by a turbine trip signal initiated by the main turbine-generator protective control system upon sensing electrical grid voltage fluctuations. A Loss of Offsite Power occurred as a result of the regional electric grid disturbance that affected several eastern and central states and portions of Canada and that led to blackout conditions in a large portion of the United States. All safety related systems operated as expected in response to this event. All control rods fully inserted into the reactor core. Reactor Pressure Vessel (RPV) water level decreased and the Reactor Core Isolation Cooling system was manually started to restore RPV level; however, the High Pressure Coolant Injection system automatically started when RPV water level reached the setpoint for Level 2. Primary containment penetration isolations associated with RPV Level 3 and 2 setpoints occurred as expected. All Main Steam Isolation Valves closed and all four Emergency Diesel Generators started and energized their pertinent emergency loads. Nine Safety Relief Valves lifted and reseated. Combustion Turbine Generator (CTG) 11-1 did not initially start in response to this event. Offsite power was restored on August 15, 2003, and the plant was restarted on August 18, 2003.
3412003003 | Fermi 2 | 10/02/2003 | 11/26/2003 | ML03336060 | <strong>Non-Conservative Setpoints for Stability Option III (OPRM) Perod Based Detection Algorithm, Period Confirmation Adjustable Variables</strong><br /><i>Abstract:&nbsp;</i>General Electric Company submitted a 10 CFR 21 notification identifying that they had determined that the stability Option III period based detection algorithm (PBDA) period confirmation adjustable variables (period tolerance and conditioning filter cutoff frequency) may be non-conservative, and recommended that the Average Power Range Monitor (APRM) Operating Power Range Monitor (OPRM) Upscale trip (Technical Specification Limiting Condition for Operation (LCO) 3.3.1.1, function 2.f) be considered inoperable for plants with a PBDA period tolerance setpoint less than 100 msec, and with a cutoff frequency of greater than 1.0 Hz. All OPRM channels were declared inoperable (but were maintained in a functional and armed condition) on October 2, 2003, because the Fermi-2 OPRM period tolerance was set at 50 msec, and the conditioning filter cutoff frequency was set at 3.0 Hz. Alternate methods to detect and suppress thermal hydraulic instability oscillations were placed into effect in accordance with Technical Specification LCO 3.3.1.1, Action J. The apparent deficiency was identified by General Electric (the OPRM and reactor vendor) following a July 24, 2003 instability event at Nine Mile Point-2. The Fermi OPRM settings would have been sufficient to identify a wide range of stability transients. Additionally, the operators have been trained to recognize instabilities and to take appropriate actions should an instability occur. The period tolerance and conditioning filter cutoff frequency setpoints were changed and all OPRM channels were declared operable on November 18, 2003. This event has been documented in the Fermi 2 corrective action program.
3412003004 | Fermi 2 | 11/07/2003 | 01/06/2004 | ML04014033 | <strong>EDG 12 Lube Oil Pressure Low</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2003, it was determined Emergency Diesel Generator (EDG) 12 had been inoperable for a period which exceeded the limiting applicable Technical Specifications (TS) allowed outage time per TS 3.8.1, "AC Sources - Operating." Specifically, at 0200 hours on June 2, 2003, EDG 12 had been removed from its standby mode for maintenance. EDG 12 was restored to an operable status at 1448 hours on June 6, 2003; however, subsequent evaluation determined that EDG 12 had remained inoperable until 2134 hours on November 8, 2003. No TS Limiting Condition of Operation (LCO) had been invoked in the interim because it was believed that EDG 12 was restored to its standby operation mode at 1448 hours on June 6, 2003. This event is reportable under 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications. During maintenance activities for EDG 12 conducted on June 2, 2003, a lube oil pressure sensing line fitting was removed, cleaned, and reinstalled to correct an identified lube oil leak. On November 7, 2003, a loose fitting was discovered on the inside of the engine block. It was determined the fitting had been loosened during the June 2, 2003, maintenance to correct the oil leak on the outside of the engine block. This event was determined to be caused by latent organizational weaknesses: omission of information and insufficient work organization and planning. Corrective actions are being taken to reduce the probability of similar events occurring in the future.
3462003001 | Davis-Besse | 01/30/2003 | 05/27/2005 | ML05152046 | <strong>Potential Inability of Air-Operated Valves to Function During Design Basis Conditions</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2003, with the reactor defueled, it was determined that several air-operated valve (AOV) actuators had negative operating margins. After further review, it was determined that eight valves total were not capable of performing their intended safety functions for the most limiting conditions. A new actuator and air accumulator were installed for valve MU3 so it could fully close against maximum Reactor Coolant System pressure to isolate letdown flow. Larger capacity accumulators were added to seven Service Water (SW) and Component Cooling Water (CCW) system valves to ensure they could perform their intended safety functions upon a loss of non-safety instrument air. These valves are required to be able to be: closed to isolate CCW flow to non-essential equipment; opened to ensure adequate SW flow through the CCW heat exchangers; or manually closed from a remote location to provide containment isolation for SW return flow from non-operating Containment Air Coolers. These conditions, apparently caused by design assumptions that were not fully adequate, are being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operation or condition prohibited by the Technical Specifications, and 10CFR50.73(a)(2)(v)(D) as conditions that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
3462003002 | Davis-Besse | 10/22/2002 | 01/29/2004 | ML04033056 | <strong>Potential Degradation of High Pressure Injection Pumps Due to Debris in Emergency Sump Fluid Post Accident</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2002, with the reactor defueled, a potential deficiency was identified for the High Pressure Injection (HPI) pumps during the recirculation phase of postulated loss of coolant accidents (LOCA) and when HPI pump 2 is used for post-LOCA boron precipitation control. The HPI pumps may be damaged due to potential debris generated by certain postulated LOCAs and entrained in the pumped fluid. The HPI pumps may be subject to this debris after the pump suctions are switched over from the borated water storage tank to the discharge of the Low Pressure Injection Pumps, which are taking suction on the containment emergency sump. The HPI pumps use a process-fluid lubricated hydrostatic radial bearing on the outboard end of the pump shaft. The hydrostatic bearing, an inter-stage bearing, and wear rings may be damaged by debris or particles in the pumped fluid. The HPI pumps were declared inoperable since the ability to maintain long-term core cooling while taking suction through the sump screens was in question. A non-emergency eight hour notification per 10CFR 50.72 (b)(3)(ii)(B) was provided to the NRC as Event Number 39740 on April 7, 2003. Subsequently, this LER is being submitted in accordance with 10CFR 50.73 (a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety (in addition to other reporting criteria listed above). Following analyses, (HPI) pump modifications, qualification testing, and in-plant testing, HPI Trains 1 and 2 were declared operable on December 30, 2003.
3462003003 | Davis-Besse | 09/25/2002 | 09/12/2003 | ML03260054 | <strong>Potential Inadequate HPI Pump Minimum Recirculation Flow Following SBLOCA</strong><br /><i>Abstract:&nbsp;</i>The High Pressure Injection (HPI) Pumps are components of the Emergency Core Cooling System which is required to maintain core cooling following postulated accidents. In September 2002, a question was raised regarding the minimum flow protection of the pumps when the recirculation valves are closed upon pump realignment to the containment emergency sump. Application of improved analytical methodology predicted the occurrence of cyclic repressurization of the Reactor Coolant System for a subset of very small break loss of coolant accidents (SBLOCA). Repressurization may exceed the shut-off head of the pumps. Considering the highly conservative assumptions required by 10CFR50.46, a vulnerability with HPI Pumps' minimum recirculation flow protection was discovered. However, highly reliable but non-safety grade equipment is capable of mitigating the consequences of the very SBLOCA sequences. This condition was corrected by installation of a second HPI recirculation flow path to protect the pumps when they are aligned to the Low Pressure Injection Pumps during containment sump recirculation (piggy-back mode). This condition is being reported as operation prohibited by Technical Specifications, an unanalyzed condition, a loss of safety function, and a common mode failure.
3462003004 | Davis-Besse | 11/15/2002 | 06/15/2003 | ML03169017 | <strong>Inadequate Calibration of Reactor Coolant System Temperature Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2002, with the reactor defueled, a deficiency was identified with the calibration of Reactor Coolant System (RCS) Resistance Temperature Detectors (RTDs). Two of the four Post Accident Monitoring hot leg temperature sensors were not included in the channel calibration required to be performed per the Technical Specifications every refueling interval. The calibration of one sensor was subsequently checked satisfactorily, but the other sensor was damaged upon removal from its thermowell, and therefore could not be checked. Because the testing could not be completed as required by the Technical Specifications, the reporting exemption of 10CFR50.73(a)(2)(i)(B)(2) is not applicable. Therefore, this issue involving a late surveillance test is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical Specifications. The four temperature sensors were verified to have been functioning properly while the plant was in operation based upon historical computer point data and from monthly surveillance test data, therefore this issue had no safety significance. The inadequate channel calibration procedure has been altered to include all equipment required to be checked per the Technical Specifications.
3462003005 | Davis-Besse | 05/02/2003 | 01/23/2004 | ML04027021 | <strong>Containment Gas Analyzer Heat Exchanger Valves Found Closed Rendering the Containment Gas Analyzer Inoperable</strong><br /><i>Abstract:&nbsp;</i>Two redundant trains of Containment Gas Analyzers (CGAs) are designed to monitor the post-accident containment atmosphere and alarm when excessive hydrogen is detected. The CGA Heat Exchangers (HXs) provide cooling of the containment atmosphere sample which travels through the CGAs following a loss of coolant accident. Technical Specification 3.6.4.1 requires two redundant CGAs to be operable in Modes 1 and 2. On May 2, 2003, with the plant in Mode5, it was determined that no Component Cooling Water (CCW) flow existed through the CGA HXs. Further investigation revealed that the CCW valves were closed. Although the CCW valves allowed some hand wheel movement, apparent seating surface corrosion inhibited opening of the valves. Subsequently, when one valve was forced opened, its CGA HX was found to be leaking. It was also determined that operation of the CGAs is dependent on non-safety grade instrument air which may be unavailable post-accident. The affected components were replaced without reliance on instrument air for operation. Based on the identified conditions and the absence of identified maintenance activities, it appears these conditions have existed since as early as plant startup in 1977. This event is being reported in accordance with 10 CFR50.73 (a) (2)(i)(B) as any operation or condition prohibited by the Technical Specifications.
3462003006 | Davis-Besse | 05/21/2003 | 07/21/2003 | ML03204034 | <strong>Potential Errors in Analysis of Block Walls Regarding HELB Differential Pressure and Seismic Events</strong><br /><i>Abstract:&nbsp;</i>In the fall of 2002, a review of Auxiliary Building structural analysis was initiated. The focus of this review was on masonry walls. During this review, discrepancies were identified with the seismic analyses of these walls. The review of safety-related masonry walls determined that calculations performed in response to IE Bulletin 80-11, Masonry Wall Designs did not apply High Energy Line Break (HELB) loads in all applicable cases. However, only one wall, No. 2257, was determined to not remain operable when subjected to combined seismic and high energy line break loads. Failure of this wall could potentially damage Boric Acid System components and safety-related components. This condition will be corrected by a modification to the entrance to the affected room to reduce HELB pressure loads on the wall to an acceptable level. This condition was caused by less than adequate communications between engineering groups and inadequate control of calculations which have been addressed by the recently instituted Design Interface Evaluation process. The discrepant condition in the structural analysis of masonry wall 2257 is being reported as a condition resulting in an unanalyzed condition pursuant to 50.73(a)(2)(ii)(B) and a condition prohibited by Technical Specifications pursuant to 50.73(a)(2)(i)(B).
3462003007 | Davis-Besse | 06/06/2003 | 08/05/2003 | ML03220034 | <strong>AC System Analysis Shows Potential Loss of Offsite Power Following Design Basis Accident</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2003, while performing an upgrade of the analysis of the electrical distribution system, a deficiency was identified for the low probability limiting analysis design case involving a loss of coolant accident (LOCA) with the plant operating in Mode 1 with degraded voltage conditions. The in-rush current from starting all essential loads to mitigate a large break LOCA in conjunction with the degraded grid voltage may result in insufficient voltage for some essential 480 V equipment to operate satisfactorily during the degraded voltage condition. Furthermore, if a startup transformer and/or bus tie transformer is out of service in this condition, undervoltage relays may actuate causing a loss of preferred power to the 4160 V essential buses, resulting in loading of the Emergency Diesel Generators. This undervoltage condition is an original design deficiency that has a very low probability of occurrence because of the limited use of a single startup and/or single bus tie transformer and highly reliable grid voltages in the Midwest. This issue is being reported in accordance with 10CFR50.73(a)(2)(v) as a condition that could have prevented fulfillment of a safety function, and 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications.
3462003008 | Davis-Besse | 07/08/2003 | 09/08/2003 | ML03253038 | <strong>Relays Installed In Safety Features Actuation System with Insufficient Contact Voltage Ratings</strong><br /><i>Abstract:&nbsp;</i>On July 8, 2003, with the plant shutdown in Mode 5, it was discovered that output relays with insufficient contact voltage ratings were installed in the Safety Features Actuation System (SPAS). Approximately 250 output relays were replaced during the current extended outage due to the relay coils approaching end-of-life. The replacement relays were specifically manufactured and qualified for the Davis-Besse Nuclear Power Station SFAS. Due to errors in the procurement process, the new relays were manufactured to match the contact rating of the original SFAS relays (5 amps @ 30 VDC) instead of the upgraded ratings evaluated by the vendor during original installation (6 amps @ 125 VDC). It was discovered that five relays were installed during plant operation, but none were installed in redundant actuated equipment circuits. Testing during the current outage, which discovered the issue, did not reveal any operational problems with the five previously-installed relays. The new relays have been removed from the SFAS and the original design relays reinstalled. Additionally, the procurement process is being revised to strengthen equivalency reviews. This issue is being reported per 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(ix)(A) as a condition prohibited by the Technical Specifications and as a single cause that could have prevented the safety function of trains or channels in different systems.
3462003009 | Davis-Besse | 08/14/2003 | 10/13/2003 | ML03288053 | <strong>Loss of Offsite Power Due to Degraded Regional Grid Voltage</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, with the plant shutdown in Mode 5, degraded grid voltage conditions were experienced. At 1608 hours, grid voltage degraded to the point where the under voltage relays actuated to disconnect the essential buses from the normal power source, which resulted in a start of the Emergency Diesel Generators (EDGs). The EDGs re-energized the essential buses, and Decay Heat Cooling to the Reactor Core was manually restarted per procedure. An Unusual Event was declared at 1621 hours due to the loss of offsite power, and the Emergency Response Organization was activated to assist with plant recovery. The on-site electrical distribution system was re-energized in an orderly and controlled manner, and plant equipment was restarted as power was available, including restoration of Spent Fuel Pool cooling. A pressure transient was experienced in the Service Water System due to the stopping and automatic restarting of the Service Water Pumps, which caused a gasket leak on a Component Cooling Water Heat Exchanger and distortion of Containment Air Coolers expansion bellows. This event is being reported in accordance with 10CFR5O.73(a)(2)(iv) as a valid actuation of the EDGs, in accordance with 10CFR50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function, and in accordance with 10CFR50.73(a)(2)(iii) as an external condition that posed a threat to the safety of the plant.
3462003010 | Davis-Besse | 08/28/2003 | 10/27/2003 | ML03302034 | <strong>Potential Inoperability of Decay Heat/Low Pressure Injection System Due to Loss of Valve Disc Pins</strong><br /><i>Abstract:&nbsp;</i>During a High Pressure Injection comprehensive flow test conducted on April 29, 2003, DH14B, Train 1 Decay Heat Cooler outlet valve, was observed to operate erratically. On August 28, 2003, the valve was removed from the system, disassembled, and inspected. The two taper pins which provide an interference fit between the disc and the valve shaft were discovered to be missing. Based upon a detailed inspection, it was determined that the failure mechanism of the missing pins was a combination of incorrect (reverse) installation, flow conditions causing vibration, and the absence of pin staking. Valves DH13A and B and DH14A, which are of the same design, were inspected. These valves had the taper pins in place and correctly installed. Therefore, the condition of DH14B was determined to be an isolated case of incorrect pin installation. DH14B is open during normal plant operation and receives a confirmatory Safety Features Actuation System Level 3 signal to open. It was determined that DH14B may not have performed its safety function following a design basis accident. The taper pins have been replaced in DH14B, and the pins for this and butterfly valves DH13A/B and DH14A have been staked to back-up their interference fit. This condition is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3462003011 | Davis-Besse | 09/17/2003 | 11/17/2003 | ML04007030 | <strong>Inoperability of Containment Spray Pump 1 Due to Solid State Trip Device Ground Fault False Trip</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2003, with the plant in Mode 3, Containment Spray (CS) Pump 1 failed to start on demand and was declared inoperable. Investigation and industry experience determined the most likely cause was due to a false spurious trip of the ground fault function of the circuit breaker overcurrent device. Previous starts have proven to be successful. Prior to September 17, 2003, a previous trip of CS Pump 1 occurred on September 5, 2003 (when the plant was in Mode 5); corrective actions to address that trip, however, did not address the problem with the Solid State Trip (SST) ground fault trip function. CS Pump 1 operated successfully (at least five starts) before tripping again on September 17, 2003. Following the September 17, 2003, trip CS Pump 1 breaker was replaced with a breaker without the ground fault trip function. Technical Specification 3.6.2.1 requires two independent containment spray systems to be operable in Modes 1 through 4. Technical Specification 3.0.4 states that entry into an operational mode or other specified applicability condition shall not be made unless the conditions of the Limiting Conditions for Operation are met without reliance on provisions contained in the ACTION statements unless otherwise excepted. Transitioning from Mode 5 to Mode 3 with CS Pump 1 inoperable was a violation of Technical Specification 3.0.4 and is being reported in accordance with 10 CFR 50.73 (a) (2)(i)(B) as any operation or condition prohibited by the Technical Specifications.
3462003012 | Davis-Besse | 09/23/2003 | 11/24/2003 | ML03332021 | <strong>Auxiliary Feedwater Pump Turbine Inoperable Due to Degraded Steam Traps</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2003, with the plant in Mode 3, Auxiliary Feedwater Pump Turbine (AFPT) 1 failed response time testing and was declared inoperable. While the initial cause was believed to be improper setting of the turbine governor during an overhaul at the beginning of the outage, additional testing and troubleshooting led to the discovery of excessive moisture in the steam supply piping. Two steam traps in the AFPT steam supply piping were found to be degraded, one to the point that it was no longer functional. Because both AFPTs were not operable per Technical Specification 3.7.1.2 during the transition from Mode 4 to Mode 3, this condition represents a condition prohibited by Technical Specification 3.0.4 and is being reported in accordance with 10 CFR 50.73 (a) (2)(i)(B) as any operation or condition prohibited by the Technical Specifications. Corrective actions include repair of the subject steam traps, revision of the plant heatup operating procedure to maintain steam traps in the steam supply piping in startup mode until the plant achieves power operation, and creation of preventive maintenance activities to periodically inspect and repair the Auxiliary Feedwater System steam traps.
3462003013 | Davis-Besse | 09/30/2003 | 12/01/2003 | ML03337082 | <strong>Trip of Reactor Protection System During Plant Cooldown</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2003, with the plant in Mode 3 following completion of a normal operating pressure test using non-nuclear heat, operators were performing a plant cooldown. The Reactor Coolant System (RCS) was at approximately 1750 psig and 532 degrees F with the Reactor Protection System (RPS) Shutdown Bypass High Pressure Trip of approximately 1812 psig enabled. Control Rod Group 1 (trippable reactivity) was withdrawn. At approximately 2125 hours, plant cooldown commenced by opening of the Turbine Bypass Valves (TBVs). The degree of opening of the TBVs exceeded that required for a properly controlled cooldown rate. A decrease in RCS pressure and Pressurizer level was experienced. Recovery efforts then resulted in an increase in RCS pressure which caused an unplanned RPS actuation and reactor trip on a Shutdown Bypass High Pressure signal. The RPS and all components responded as intended. There were no post-trip response equipment issues identified. The causes of this event were determined to be operator performance, procedural guidance, and a pre-job brief which were all less than adequate. Corrective actions include event-specific training and procedure enhancements. Notification of this event was made on September 30, 2003, pursuant to 10 CFR 50.72(b)(3)(iv)(A). This report is being provided pursuant to 10 CFR 50.73 (a) (2)(iv)(A), an event that resulted in actuation of the RPS.
3462003014 | Davis-Besse | 10/17/2003 | 12/16/2003 | ML03352020 | <strong>Steam Feedwater Rupture Controls System Re-Energizes in a Blocked Condition</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2003, with the plant in Mode 5, the Steam and Feedwater Rupture Control System (SFRCS) Logic Channel 1 re-energized in a blocked condition. While performing the initial investigation, on October 17, 2003, it was discovered that any of the four logic channels could be re-energized in a blocked condition, depending on different operating configuration conditions. Therefore, this condition was conservatively reported to the Nuclear Regulatory Commission as required by 10 CFR 50.72(b)(3)(ii)(B), Notification Number 40256. Subsequent investigation determined that the effect on plant operation is limited to a rupture on Once Through Steam Generator (OTSG) 2 with Logic Channel 4 re-energizing in a blocked configuration. If this postulated event occurred, Auxiliary Feedwater Pump 2 would continue to feed the ruptured OTSG. This design condition has existed since 1988 following a modification to replace the SFRCS cabinets. Corrective Action has been completed which modified the SFRCS logic module to prevent the undesirable block from becoming enabled until the power supply voltage stabilizes and prevents the block initiation without operator action. Because SFRCS did not meet single failure criterion due to this condition, this event is conservatively reportable as an unanalyzed condition in accordance with 10 CFR 50.73(a)(2)(ii)(B). The condition also represented an operation or condition prohibited by the Technical Specifications and is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B).
3482003002 | Farley 1 | 04/22/2003 | 06/16/2003 | ML03170001 | <strong>Reactor Pressure Vessel Head Set in Place with Technical Specification 3.4.12 Not Met</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2003, at 1745, during routine shift monitoring activities, it was determined that Farley Nuclear Plant Unit 1 had been operated contrary to Technical Specification 3.4.12 since 1244 on April 22, 2003 in that the reactor vessel head had been set with three charging pumps capable of injecting into the RCS. Technical Specification 3.4.12 requires that a maximum of one charging pump be operable in Modes 5 and 6 when the reactor vessel head is in place and one or more RCS cold legs is = 180°F. By tagging order, two of the three charging pumps were made incapable of injection into the RCS as required by Technical Specifications by 1821on April 22, 2003. This event was caused by inadequate procedure in that the Unit Operating Procedure for setting the reactor vessel head did not address the limitation on the number of charging pumps available prior to setting the head. A contributing cause was cognitive personnel error in that equipment alignment was insufficiently reviewed prior to setting the head. The applicable Unit Operating Procedures on both units have been revised to add appropriate information from Technical Specification 3.4.12. Personnel involved have been coached. A Training Advisory Notice on this procedure change was sent to Operations personnel. This event has been discussed with Operations personnel in shift briefings.
3482003003 | Farley 1 | 05/02/2003 | 06/30/2003 | ML03183033 | <strong>Unplanned Auxiliary Feedwater Actuation upon Trip of Steam Generator Feed Pump</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2003 at 0605 with the reactor at 3.8 percent power during post refueling startup, an unplanned emergency safeguards actuation of the Auxiliary Feedwater (AFW) System occurred. An unexpected lB Steam Generator Feed Pump (SGFP) speed increase led to a manual trip of the 1B SGFP. The 1A SGFP was out of service at this time. Trip of the only operating SGFP caused both Motor Driven Auxiliary Feedwater (MDAFW) Pumps to start. Reactor power was lowered from 3.8 percent to 2 percent and the reactor was stabilized on Auxiliary Feedwater. Following extensive troubleshooting, the cause of the event on May 2 could not be determined. The sensing circuit was recalibrated and returned to service. Subsequently, on May 9, 2003, with the reactor at 100 percent power, an unexpected SGFP speed increase occurred again. The SGFP was removed from service and a replacement speed sensing circuit was installed in the SGFP speed control cabinet. No safeguards equipment actuation occurred in conjunction with this subsequent failure. The cause of both events is believed to be an intermittent failure of the speed sensing circuit. On the initial failure, the speed sensing circuit was recalibrated. On the subsequent failure on May 9, the speed circuit was replaced.
3522003001 | Limerick 1 | 01/31/2003 | 04/01/2003 | ML03098065 | <strong>Degraded Flood Barrier Due to Reactor Enclosure Dirty Radwaste Line Cleanout Plug Not Installed</strong><br /><i>Abstract:&nbsp;</i>One of the flood barriers for the lA subsystem and 1C subsystem of the Residual Heat Removal (RHR) system was discovered to be inoperable. The barrier was a 4 inch floor drain line cleanout plug that most likely was not reinstalled following hydrolazing activity in the area causing a breach of a flood barrier. The condition is assumed to have existed for a period that exceeded the TS AOT for RHR. The plug was reinstalled upon discovery. The plugs have been labeled as hazard barriers and will be added to the barrier breach procedure.
3522003002 | Limerick 1, Limerick 2 | 03/17/2003 | 05/16/2003 | ML03143033 | <strong>Core Alteration without Secondary Containment Established</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2003 the night operating shift was preparing to drain down the reactor cavity during refueling outage 2R07. Control rod exercising was in progress. Cavity drain down began which resulted in the breach of secondary containment at 01:06 hours on March 17, 2003. Contrary to Technical Specification3.6.5.1.2, control rod exercising continued until late on night-shift and ceased when all control rods had been satisfactorily exercised. The relieving operating shift realized that control rod exercising (a core alteration) had occurred while refueling enclosure secondary containment was inoperable. Two root causes were identified for the event. The primary cause of the event was less than adequate procedural guidance to verify secondary containment is established prior to control rod withdrawal. The second root cause was the failure of shift management to verify Technical Specification compliance upon breach of refuel enclosure secondary containment integrity. This action would have properly suspended core alterations. The corrective actions performed included revisions to two procedures, "Pre Control Rod Withdrawal Check" (ST-6-047-370-1 and 2) and "Draining Reactor Well and Dryer/Separator Storage Pool" (S53.4.A), and management's expectation for Technical Specification compliance.
3522003003 | Limerick 1 | 04/23/2003 | 06/11/2003 | ML03169038 | <strong>Automatic Scram on Low Reactor Level Due to Condensate Deep Bed Demineralizer Valve Closure</strong><br /><i>Abstract:&nbsp;</i>A valid reactor low level condition resulted in an automatic actuation of the reactor protection system. A closure of the deep bed condensate demineralizer inlet header block valve caused the reactor feed pumps to trip on low suction pressure resulting in the reactor low level condition. In addition, the low level condition resulted in actuation of the high pressure injection system, reactor core isolation cooling system and primary containment isolation valves. Operating procedures were revised to maintain the deep bed condensate demineralizer inlet header block valve open and de-energized during operation at power.
3532003001 | Limerick 2 | 03/03/2003 | 04/25/2003 | ML03121052 | <strong>Main Turbine High Vibration Manual Turbine Trip and Automatic Scram During Planned Shutdown</strong><br /><i>Abstract:&nbsp;</i>An unplanned automatic scram occurred as a result of a manual main turbine trip. The main turbine developed a high vibration condition during a planned power reduction to enter a refueling outage. The main turbine developed a light radial rub due to an inadequate specification for clearance between the oil deflectors and the main shaft as a result of main turbine retrofit. The oil deflector clearance specification has been restored to the pre-retrofit value. In addition, the affected gland seal clearances were restored to design values. Also, the operating procedures were revised to ensure main condenser backpressure remains greater than 1.5 inches Hg when less than 50% power.
3532003002 | Limerick 2 | 03/03/2003 | 06/29/2003 | ML03247150 | <strong>MSIV Closure Time Durring Hot Conditions</strong><br /><i>Abstract:&nbsp;</i>During a Main Steam Isolation Valve (MSIV) stroke time test on March 3, 2003, an unexpected result occurred when two Unit 2 MSIVs had closing times faster than the Technical Specification minimum 3 seconds. The MSIVs were declared inoperable and the plant proceeded to cold shutdown. No specific cause was identified for the unacceptable stroke time. However, during the investigation inadequacies in the test methodology were identified. The test method did not accurately account for all of the variables that contribute to the minimum closing time. As part of the corrective action Unit 2 MSIVs were adjusted during 2R07 to ensure that valve closing times were within the Technical Specification required range. This LER is being submitted as a voluntary LER to document an event pursuant to NUREG 1022 Section 2.7 which may be of a generic interest or concern.
3542003002 | Hope Creek | 01/12/2003 | 03/13/2003 | ML03079034 | <strong>Inoperability of Control Room Emergency Filtration Subsystems Due to Control Room Envelope Breach</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2003 Hope Creek operators discovered control room pressure to be negative relative to adjacent areas. A control room envelope (CRE) breach occurred upon the opening of a ventilation ductwork access hatch in the 'A' Control Room Supply Heating Ventilation and Air Conditioning (CRS) train during a scheduled system outage. At the time 'A' Control Room Emergency Filtration (CREF) subsystem was tagged out. The 'B' CRS was in service maintaining the control room at a positive pressure relative to adjacent areas. Technical Specification (TS) 3.0.3 was entered due the inoperability of the 'A' and 'B' CREF subsystems. Control room pressure was restored approximately ten minutes later by closing the access hatch. TS 3.0.3 was exited within one hour. Further action to initiate a plant shutdown was not required. The apparent cause of the event was the failure to identify that this particular access hatch was common to both ventilation trains during the planning, operations review, and engineering walk down while planning the work order for this job. Planned corrective actions include improvements in labeling access hatches on CREF ductwork, identification of configuration control lessons learned, review of the event with affected personnel and a review of existing training programs to address potential knowledge deficiencies. This event is reportable in accordance with 10CFR50.73(a)(2)(v)(D) as any event or condition that could have prevented the fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident.
3542003003 | Hope Creek | 04/26/2003 | 06/25/2003 | ML03188001 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2003 Hope Creek Engineering personnel received the initial results of the Target Rock Model 7567F Safety Relief Valve (SRV) setpoint testing required by Technical Specification 4.4.2.2. This testing revealed that following Hope Creek Cycle 11, eight of the fourteen SRVs experienced setpoint drift outside of the Technical Specification 3.4.2.1 limit of +/- 3%. The apparent cause for six SRV setpoint failures is corrosion bonding/sticking of the pilot disc. Pilot seat leakage was the apparent cause for the remaining two valves. Immediate corrective action was to replace all eight valves with tested and certified spare pilot assemblies; this was part of a scheduled activity to replace all fourteen SRV pilot assemblies during the refueling outage. Since the number of SRVs outside of the setpoint tolerance limit (eight) was greater than the number of SRVs (one) allowed to be inoperable by Technical Specification 3.4.2.1, this condition was determined to be reportable under 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant Technical Specifications. These eight valves will be disassembled and inspected to document the cause of the failure. In addition, since this failure mechanism could be present in all the valves, PSEG Nuclear LLC will continue to test all fourteen pilot assemblies at the next refueling outage.
3542003004 | Hope Creek | 04/22/2003 | 06/19/2003 | ML03182065 | <strong>Failure to Fully Implement LCO Action to Put Mode Switch in Shutdown During Mode 5</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage R11, Hope Creek operated in a condition prohibited by Technical Specifications (TS). On April 22 at 2036 when a Tagging Order was implemented, the Reactor Protection System and the manual scram switches were effectively rendered inoperable. At that time, Action 9 of TS Table 3.3.1-1 item 12 should have been implemented and was not fully implemented because the Mode Switch was not locked in SHUTDOWN as required. This condition existed until 1950 on April 26 when the Mode Switch was locked in SHUTDOWN. The apparent cause for this event was a lack of proper review of TS when the equipment was tagged out and removed from service. Subsequent shifts failed to identify the error. There were no safety consequences associated with this event since, at the time that the tagging operation was in effect, a full scram was implemented, all control rods were inserted, a control rod withdrawal block was in effect, and there were no activities scheduled or in progress that involved core alterations. This event will be provided to the Operations Training Review Group for inclusion in the Licensed Operator Requalification Program.
3542003005 | Hope Creek | 02/24/2003 | 07/02/2003 | ML03197046 | <strong>Hope Creek "B" Emergency Diesel Generator Inoperable Beyond Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2003, during fuel rack lubrication on “B" Hope Creek Emergency Diesel Generator Engine (EDG) the number two fuel injection pump rack was found stuck and the unit declared inoperable at 02:20. Immediate corrective action was to replace fuel pump on number two cylinder. The “B" EDG was returned to an operable status at 21:17 on February 25, 2003. Subsequent to this an investigation was conducted into the timeliness of identification of the failed fuel injector. The conclusion based upon the failure mechanism was that the diesel was inoperable from the time the diesel was taken out of service for the monthly surveillance test, which occurred at 16:37 on February 22, 2003. Technical Specification 3.8.1.1 Action b states that the "A" or "B" EDG must be returned to an operable condition within 72 hours. The apparent cause associated with being in a condition not allowed by TS 3.8.1.1 Action b was personnel error. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as any event, which was prohibited by the plant's Technical Specifications.
3542003007 | Hope Creek | 09/19/2003 | 11/17/2003 | ML03329056 | <strong>Reactor Scram Due To Electrical Transient, Low Reactor Water Level And Loss Of Reactor Feed Pumps A and C</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2003 at 2041 hours, Hope Creek reactor scrammed on low reactor water level following a reduction in feed water flow when two of the three reactor feed pumps tripped. The 'A' reactor feed pump turbine (RFPT) tripped when power was lost to the main and auxiliary lube oil pumps. The 'C' RFPT tripped when power was lost to the main lube oil pump and the auxiliary pump did not recover oil pressure prior to the protection logic sensing low oil pressure. The initiating event that led to loss of power was an electrical transient in the station switchyard. The electrical transient was due to an accumulation of salt on switchyard components following Hurricane Isabel. As a result of the electrical transient, the 'A' and 'C' emergency diesel generators successfully started and loaded to their 4160 volt Class 1E busses. The cause of the reactor scram was low reactor water level which resulted from an electrical transient and the loss of two reactor feed pumps due to the failure of the RFPT lube system to maintain proper oil pressure. There were no safety consequences associated with this event. Corrective actions included removing salt from switchyard components and modifying the procedural alignment of the RFPT lube oil pumps to improve reliability. This event is being reported in accordance with 10CFR50.73 (a) (2) (iv) (A).
3542003009 | Hope Creek | 09/14/2003 | 02/06/2004 | ML04049060 | <strong>Tech Spec Non-compliance - Inoperable High Ran a Noble Gas Effluent Monitor On North Plant Vent</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2003, while performing a scheduled Instrument and Controls (I&C) functional check of the North Plant Vent (NPV) wide range noble gas effluent monitor it was determined that the bypass pump was inoperable. Technical Specification (TS) 3.3.7.5, Accident Monitoring Instrumentation, requires the NPV high range radiation monitor to be operable during power operation or initiate the preplanned alternate method of monitoring. The purpose of the Accident Monitoring Instrumentation is to extend the range of the low range noble gas monitor. At the time of discovery Hope Creek was in Operating Condition 4 (Shutdown) so the TS Action Statement did not apply. However, based on troubleshooting it was determined that problems discovered would have prevented the required components from fulfilling the system's design function. Further investigation has determined that the monitor became inoperable on September 14, 2003 during previous maintenance activities. Monitor inoperability was not identified at that time due to inadequate post maintenance testing, thus no alternate means of monitoring was instituted, as required by TS 3.3.7.5. There were no safety consequences associated with this event because the system is not safety related or required for shutdown of the unit. Corrective actions included troubleshooting and repair of the radiation monitoring channel, and verification of correct operation of the radiation monitor, and coaching / counseling of those involved. This event is being reported in accordance with 10CFR50.73 (a) (2) (i) (B).
3612003001 | San Onofre 2, San Onofre 3 | 02/01/2003 | 03/24/2003 | ML03085012 | <strong>Incorrect Test Connection Results in Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 02/01/03, while Unit 3 was defueled for Cycle 12 refueling and Unit 2 was in Mode 1 at 100 percent power, a Technician (utility, non-licensed) was conducting planned outage work on the Unit 3 relay protection cabinet (RPC), 3L070. While establishing a reference test connection within the Unit 2 RPC, 2L070, the Technician misidentified the reference terminal and made an incorrect connection to the Field Suppression Relay for the Unit 2 Main Generator. Upon initiating the test, at 0310 PST, the error resulted in the following automatic and sequential events at Unit 2: (1) actuation of generator loss of field relay, (2) generated/turbine trip, (3) reactor trip, and (4) initiation of emergency feedwater. Systems responding to the event performed as designed. Additionally, Operator responses were correct and timely. This event was caused by a combination of personnel error and inadequate procedural guidance. SCE will take appropriate personnel actions and improve written work instructions. SCE concludes that this event was of low to no safety significance. There were no consequences to public health and safety.
3622003001 | San Onofre 3 | 12/17/2003 | 02/15/2004 | ML04055041 | <strong>Breaker Failure Coincident with Planned Maintenance Results in Both Trains of Emergency Core Cooling Systems and Containment Spray Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 15 and 16, 2003, Operators removed various Train "B" components from service for maintenance, including Train "B" Emergency Core Cooling System (ECCS) and Containment Spray (CS) components. On December 17, 2003, at 0315 PST, Train "A" Feeder breaker 3B0414 unexpectedly opened resulting in a loss of power to certain Train "A" ECCS and Containment Spray components. This caused Unit 3 to enter TS 3 .0.3 for two trains of ECCS being inoperable and for two trains of containment spray being inoperable. Operators initiated corrective actions to restore power to the Train "A" components and, at 0410 PST, began reducing power. At 0535 PST, Operators reported this event to the NRC (NRC Log No. 40396). At 0800 PST, power was restored to the Train "A" ECCS and CS components, and operators exited TS 3.0.3. This event was caused by an isolated spurious actuation of a breaker solid-state trip device (SSTD). Subsequent testing confirmed that the affected breaker consistently tripped earlier than the manufacturers specified response times for the long time overcurrent trip time. SCE determined this was an isolated occurrence.
3642003001 | Farley 2 | 11/10/2003 | 12/22/2003 | ML03358066 | <strong>Reactor Trip Due To Loss Of Power To Reactor Coolant Pump Breaker Position Indication</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2003 at 1036, with the reactor at 100% power, Unit 2 automatically tripped due to loss of power to the 2A Reactor Coolant Pump (RCP) breaker position input to the Reactor Protection System. By design, loss of this single breaker position input results in a direct reactor trip above 30% power. The power to the breaker position input circuit was lost due to a momentary loss of voltage on the 2A 120 VAC Vital Instrument Bus, which is normally powered by the 2A Inverter. The inverter automatically transferred to bypass during the electrical transient as it is designed to do on a fault. All safeguards equipment functioned as designed following the trip. The 2A Reactor Coolant Pump (RCP) breaker did not change position and the pump remained in operation throughout this event. Extensive troubleshooting on both the inverter and the instrument bus failed to determine any reason for the momentary loss of voltage or the transfer of the inverter output to bypass. Possible causes considered included an inverter failure, an electrical fault on the 2A 120 VAC Vital Instrument Bus or its connected loads, and maintenance activities possibly causing a short which would impact the 2A 120VAC Vital Instrument Bus. None of these could be confirmed. The RCP breaker position indication power supplies have been realigned from the inverters to independent dedicated regulated AC sources.
3662003001 | Hatch 2, Hatch 1 | 03/25/2003 | 05/24/2003 | ML03143028 | <strong>Plant Service Water Valve Found Closed Requiring Emergency Core Cooling Systems to be Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 3/27/03 at 1510 EST, Unit 2 was in mode 4 with the reactor shutdown for a refueling outage. Valve 2P41-F063, Unit 2 Plant Service Water Outlet from the Unit 2 Reactor Building, was found closed when its indicator showed it to be open. With valve 2P41-F063 closed PSW flow through the reactor building ECCS room coolers was isolated. The loss of the ECCS room coolers required the ECCS systems to be considered inoperable. On 3/25/03 at 0004 EST the plant entered Type B 1 secondary containment. At that time, Condition DI of TS 3.5.2 should have been entered, but because the plant operators believed that they had two OPERABLE low pressure ECCS injection/spray subsystems the Condition was not entered as required. Type B1 Secondary Containment does not include the Unit 2 Reactor Building and the required actions associated with Condition D were not met. On 3/26/03 at 1049 EST operators completed alignment of Secondary Containment to Type A. This Secondary Containment Type does include the Unit 2 Reactor Building and at this time TS 3.5.2 Required Actions D1, D2, and D3 were met. Plant Service Water butterfly valve 2P41-F063 was found with the spline clamp loose, allowing the actuator and indicator to turn without actually turning the butterfly valve shaft. Once the spline clamp was tightened, the actuator again was able to turn the valve shaft. The valve was placed in the correct position at 1545 on 3/27/03 restoring the required ECCS subsystems to OPERABLE status.
3662003002 | Hatch 2 | 03/29/2003 | 05/28/2003 | ML03143032 | <strong>High Pressure Coolant Injection System Inoperable After Performing Major Maintenance</strong><br /><i>Abstract:&nbsp;</i>On 3/29/03 at 245 EST, Unit 2 was in the Startup mode with the reactor critical at a power level of approximately 1% CMWT and reactor pressure of approximately 165 psig. Major maintenance was performed on the High Pressure Coolant Injection (HPCI) system during the refueling outage. Surveillance procedure 34SV-E41-005-2, "HPCI Pump Operability 165 PSIG Test" was being performed when it was determined that the turbine control valve would not open upon initiation. The procedure was backed out of and the HPCI system was returned to standby. The investigation of the problem determined that links TB1-39 and TB1-40 were open in panel 2H21-P050. These links that were found open provide power to the EGM/ramp generator. The links were closed and the HPCI surveillance was performed again. During this run, the control valve, 2E41-F3052, went to the fully open position and the flow controller, 2E41-R612, showed a system flow in excess of 5200 GPM. Investigation found that the magnetic speed pick-up for the speed feedback signal to the governor system was incorrectly set-up. The magnetic speed pick up was adjusted and the HPCI surveillance test was successfully completed and the HPCI system was declared operable at 1215 EST. The cause of this event was personnel errors during the performance of the six to ten year HPCI system preventive maintenance. A contributor to this event was that the procedure was poorly human factored (for link restoration) and did not have adequate checks regarding the setting of the magnetic speed pickup. The procedure will be revised to make it easier to use and follow.
3692003001 | McGuire 1 | 01/24/2003 | 03/24/2003 | ML03097058 | <strong>Failure of Refueling Water Storage Tank Level Instrumentation During Cold Weather Due to Sensing Line Heat Trace and Insulation Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On January 24, 2003, unit 1 experienced a failure of the Refueling Water Storage Tank (FWST) level instrumentation designed to initiate automatic swapover of the Emergency Core Cooling System (ECCS) suction from the FWST to the Containment Sump. While in this condition, automatic swapover of the ECCS suction from the FWST to the Containment Sump would not have occurred during an event requiring ECCS operation. This condition could have prevented fulfillment of this ECCS safety function. The level instrumentation failed due to frozen sensing lines. Annunciators immediately alerted operators who operated heat tracing in manual override such that continuous heat was applied to the sensing lines. These actions restored the Unit 1 FWST level instrumentation to operable status. This event was not significant with respect to the health and safety of the public. Event Cause: Design deficiencies with the sensing lines heat trace system and configuration control deficiency with the sensing lines insulation. Corrective Action: Redesign of the Unit 1 & 2 FWST level instrumentation heat trace systems. Revise heat trace system design documentation and ensure conformance. Insulate sensing lines in accordance with design documents. Revise FWST heat trace related configuration control documents.
3692003002 | McGuire 1 | 02/07/2003 | 04/04/2003 | ML03105044 | <strong>Operation Prohibited by Technical Specifications 3.6.3 and 3.7.5 Due to an Inoperable Auxiliary Feedwater System Valve for Greater than 72 Hours</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On February 4, 2003, Auxiliary Feedwater System Valve 1CA-42B was declared Inoperable to perform scheduled maintenance. While functionally testing this valve following maintenance, its valve stem failed. Repair of this valve stem could not be completed within the Technical Specification Required Action Completion Time of 72 hours which expired on February 7, 2003. Therefore, a Notice of Enforcement Discretion was requested and granted for an additional 72 hours. The restoration of valve 1CA-42B was completed within this additional 72 hours. Event Cause: The valve stem failure was caused by an overload condition resulting from the failure of the limit and torque control functions of the motor actuator switch mechanism. The control function failure was due to previous vendor assembly deficiencies combined with the recent maintenance. Corrective Action: Restore valve 1CA-42B to original design specification. Revise procedures to detect and prevent improper actuator assembly and prevent improper actuator annealing. Inspect other affected valves for improper actuator assembly.
3692003003 | McGuire 1 | 05/02/2003 | 06/26/2003 | ML03190025 | <strong>Both Trains of Hydrogen Mitigation System Inoperable Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of this event, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Train B of the Unit 1 Hydrogen Mitigation System (HMS) had been declared inoperable to implement a planned minor modification to replace cables associated with hydrogen ignitors in the ice condenser region of containment. Event Description: On May 2, 2003, while implementing the minor modification, a cable associated with Train A was inadvertently cut. Since Train B had been previously declared inoperable, this rendered both trains of the Unit 1 HMS inoperable. Technical Specification (TS) 3.0.3 was entered at approximately 0115 hours and action was initiated to place Unit 1 in Mode 3 within 7 hours. By approximately 0741 hours, the Train A cables had been repaired, TS 3.0.3 had been exited, and Unit 1 was at approximately 45 percent power. This event was not significant with respect to the health and safety of the public. Event Cause: The cause of this event has been attributed to human error. Personnel involved with inadvertently cutting the wrong (Train A) cable failed to appropriately apply human error prevention elements during task turnover and demonstrated a lack of rigor during task execution. Corrective Action: Prior to this event, training regarding verification techniques including correct components was initiated for Maintenance personnel. The individuals on the Maintenance crew involved in this event had not yet received the training when the event occurred. This training is now complete. Maintenance turnover guidance, including necessary protocol and roles and responsibilities, will be enhanced as appropriate.
3732003001 | LaSalle 1 | 04/09/2003 | 06/06/2003 | ML03164040 | <strong>Enforcement Discretion Required to Repair Division 2 125 VDC Battery Charger</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2003, oscillations were observed in the Unit 1 Division 2 125 VDC battery terminal voltage. The system remained operable because the Technical Specification (TS) Surveillance Requirements (SR) were still met. Repairs to the 125 VDC battery charger were estimated to take 12 hours, which was in excess of the two hours of system inoperability allowed by TS. In order to repair the battery charger while precluding a shutdown transient on the plant, a Notice of Enforcement Discretion was requested from the NRC, which was granted on April 9, 2003. Repairs began at 1742 hours on April 9, 2003. Planned work was completed and the system was returned to operable status at 0407 hours on April 10, 2003, after 10 hours and 25 minutes of inoperability. The voltage oscillations continued, although at a reduced level. On April 28, 2003, the 125 VDC feed to fire protection inverter lFP0lE was isolated and the oscillations stopped. Troubleshooting of lFP0lE continues. The safety significance of the additional 12 hours of Division 2 inoperability granted was minimal, since the Division 1 and 3 125 VDC subsystems remained operable.
3732003002 | LaSalle 1, LaSalle 2 | 04/23/2003 | 09/03/2003 | ML03254112 | <strong>1A and 0 Diesel Generators Inoperable Simultaneously Due to Inadvertent Partial CO2 Actuation</strong><br /><i>Abstract:&nbsp;</i>At 1848 hours on April 23, 2003, while the 1A Diesel Generator (DG) was inoperable for surveillance testing, a partial CO2 suppression system actuation occurred for the 0 DG room when a non-licensed operator attempted to. blow some dust off of a circuit board in the local CO2 fire suppression cabinet. The partial actuation closed several dampers in the 0 DG ventilation support system, which rendered the 0 DG inoperable. No C02 was discharged. Technical Specification 3.8.1 allows two DGs to be inoperable on the same unit for two hours. If operability cannot be restored, the unit must be placed in Mode 3 in 12 hours and in Mode 4 in 36 hours. The 1A DG was restored to operability at 1952 hours. The 0 and 1A DGs were simultaneously inoperable for 64 minutes. The safety significance of the event was minimal, because normal AC power was available to ESF loads throughout the event, and the 0 DG would have started and loaded on a loss of offsite power. The cause of the event was foreign material on the horizontal surface of the Zone 1 circuit board in the suppression cabinet. Corrective actions include revising the appropriate procedures to remove foreign material from the cabinet during periodic surveillances.
3732003003 | LaSalle 1, LaSalle 2 | 07/10/2003 | 09/04/2003 | ML03254113 | <strong>Reactor Core Isolation Cooling High Steam Flow Isolation Differential Pressure Switches Failed Due to Torn Diaphragm</strong><br /><i>Abstract:&nbsp;</i>On 7/7/03, during the performance of surveillance LIS-RI-101, "Unit 1 RCIC Steam Line High Flow Isolation Calibration," differential pressure switch 1E31-NO13AA failed its diaphragm integrity test. The surveillance was stopped, and the switch was replaced. The surveillance was continued, and on 7/10/03, differential pressure switch 1E31-N013BA also failed its diaphragm integrity test. The cause in each case was a rupture of the Kapton diaphragm in the Static O-Ring (SOR, Inc.) differential pressure switch. This condition is a known performance issue with these switches. The corrective action was to replace the failed switches. Efforts to identify, qualify, and install a replacement for the SOR switches are on-going. The safety significance was minimal. With both divisions of the RCIC Steam Line High Flow isolation inoperable at the same time, the RCIC equipment room Area and Differential Temperature instrumentation were operable and would have closed the steam supply line isolation valves in the event of a break or leak.
3732003004 | LaSalle 1 | 11/17/2003 | 01/06/2004 | ML04020069 | <strong>High Pressure Core Spray Inoperable Due to Improperly Seated Fuse</strong><br /><i>Abstract:&nbsp;</i>At 0110 on 11/17/03, during the performance of a maintenance surveillance, fuse 1B21A-F8, the power supply fuse for the High Pressure Core Spray System (HPCS) Low Level Initiation/High Level Trip, was found not fully seated in its fuse clip. Loss of fuse continuity would have prevented automatic actuation of HPCS on reactor vessel low level, and would have prevented automatic closure of the HPCS discharge valve on reactor water high level. The fuse was pushed back fully into the fuse- clip at 0143. Engineering determined that, with the fuse not fully seated, continuity might not have been retained during a seismic event. The cause of this event could not be determined. The most probable cause was a failure to fully seat the fuse during the last clearance order restoration in March 2002. Corrective actions included a walk down of other cabinets in the Main Control Room and Auxiliary Electric Equipment Room for similar conditions.
3732003005 | LaSalle 1 | 11/27/2003 | 01/23/2004 | ML04033078 | <strong>Manual Reactor Scram on Low Reactor Vessel Water Level Due to Stuck Open Feedwater Pump Discharge Check valve</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2003, at 0052 hours, while swapping from the 1A Turbine Driven Reactor Feed Pump (TDRFP) to the Motor Driven Reactor Feed Pump (MDRFP), Unit 1 was manually scrammed due to decreasing reactor water level. Reactor Water Level had decreased to approximately 20 inches, and was continuing to drop even with the indicated MDRFP discharge flow meeting the expected demand. Troubleshooting determined that the lA TDFRP discharge check valve 1FW001A had stuck open, causing the flow from the MDRFP to circulate back through the lA TDFRP preventing it from reaching the reactor vessel. The cause was determined to be internal binding. Corrective actions were to inspect and repair 1FW001A, and to schedule inspections on similar check valves on both Units. Additionally, vendor recommended enhancements identified during the investigation will be incorporated for these valves.
3742003001 | LaSalle 2 | 01/10/2003 | 03/11/2003 | ML03077065 | <strong>Manual Scram Due to Lowering Reactor Water Level as a Result of a Trip of the 2B Condensate/Condensate Booster Pump</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2003, at 1156, Unit 2 was manually scrammed in anticipation of an automatic scram due to decreasing reactor water level. The event was initiated by a trip of the 2B Condensate/Condensate Booster (CD/CB) pump on instantaneous overcurrent. The electrical perturbation, along with a latent failed level switch on the heater drain tank, caused the 2A and 2C Heater Drain pumps to trip. This resulted in a low suction pressure trip of both Turbine Driven Reactor Feed Pumps. When the Operators could not maintain reactor water level, a manual scram was inserted. Reactor water level was restored using the Motor Driven Reactor Feed Pump following the scram. The cause of the trip of the 2B CD/CB pump was a broken lug on the 6.9 kV cable connection to the B phase of the motor. Corrective actions include repairing the termination such that stresses on the connection are limited, and inspecting the terminations to other large motors. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The Emergency Core Cooling Systems were not challenged.
3742003002 | LaSalle 2 | 02/25/2003 | 04/16/2003 | ML03113053 | <strong>Average Power Range Monitor Flow-Biased Scram Inoperable Due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2003, upon return to full power after refueling outage L2R09, all reactor recirculation flow converters were discovered to be out-of-calibration in the non-conservative direction. As a result, the reactor protection system (RPS) Average Power Range Monitor (APRM) flow-biased scram was declared inoperable, and the unit entered a one-hour time clock in accordance with Technical Specification (TS) 3.3.1.1 to restore RPS trip operability of this function. The flow units were re-calibrated within the hour. The cause was determined to be an inadequate procedure, in that flow data from less accurate sources was allowed be used to calibrate the flow converters when the process computer was unavailable, but no additional guidance or limitations were provided. Corrective actions include revising the affected procedures. The safety significance of this event was minimal. The flow-biased thermal scram is not a credited scram per the Technical Specification Bases, as it is a backup to the neutron flux scram. Additionally, the flow-biased scram is clamped at 115.5 percent power, so at the point of discovery the scram would have occurred at the required value because the setpoint is not a function of flow at flow rates greater than approximately 74.5 percent.
3742003003 | LaSalle 2, LaSalle 1 | 03/18/2003 | 05/08/2003 | ML03134056 | <strong>Main Steam Safety Relief Valves As-Found Safety Mode Set Pressure Found Out-of-Tolerance</strong><br /><i>Abstract:&nbsp;</i>During a planned maintenance outage in April 2002, all 13 Main Steam Safety Relief Valves (MSSRV) on Unit 2 were removed and replaced with pre-tested valves. On March 18, 2003, the Station was notified by the vendor that bench testing of the 13 MSSRVs had revealed five that were outside Tech Spec and ASME OM Code allowed tolerances. All five valves lifted below their set pressures, with deviations ranging from -3.1 to -5.3 percent. The consequences of premature relief are not considered significant as long as the safety mode premature lift does not encroach upon the relief mode setpoint. The minimum difference between the safety mode relief set point and the relief mode set point for LaSalle is 6.4 percent, while the maximum discrepancy noted was 5.3 percent. Therefore an operating transient would not have been expected, and the significance of this event was minimal. The subject valves will be disassembled, inspected, rebuilt and retested prior to installation in the plant during refuel outages LlR10 and L2R10.
3742003004 | LaSalle 2, LaSalle 1 | 07/07/2003 | 09/02/2003 | ML03253040 | <strong>Unit 2 Scram Due To Main Power Transformer B Phase Disconnect Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On 7/7/03, while at 100 percent power, the LaSalle Station Unit 2 main power “B" phase disconnect in the switchyard catastrophically failed, resulting in a main generator trip and reactor scram. The electrical transient tripped the three circulating water pumps, which resulted in the loss of normal heat removal. While controlling reactor pressure and level using the safety relief valves (SRV), the resulting shrink and swell transients caused four additional scram signals on low reactor level. The cause of the disconnect failure could not be established. The cause of the additional scram signals was the lack of an operating strategy for these conditions. The safety significance of this event was minimal. A reactor scram with a loss of the main condenser is an analyzed event. Reactor level and pressure were maintained using Reactor Core Isolation Cooling and the safety relief valves, and the High Pressure Core Spray System was available throughout the event. Corrective actions include development of a condition monitoring program to inspect and monitor the condition of the insulators, and evaluating the adequacy of current switchyard inspection and maintenance procedures.
3822003001 | Waterford 3 | 08/26/2003 | 10/22/2003 | ML03301035 | <strong>Loose Breaker Fuse Rendered One Bank of Pressurizer Proportional Heaters Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2003, with the plant in Mode 1 at 100% reactor power, it was discovered that a loose control power fuse for a breaker rendered one bank of pressurizer proportional heaters technically inoperable for a period of four days, exceeding the Technical Specification allowed outage time. The loss of control power to the breaker would have prevented the proportional heaters from being manually energized from the emergency power source from the control room had a loss of offsite power occurred. On July 20, 2003, an operator noticed the indicating lights on the breaker were not illuminated, however miscommunication during turnover to another operator resulted in the condition not being corrected until four days later when another operator noticed and investigated the condition. The control power fuses were reinstalled and a corrective action was assigned to Operations to brief the operators on this event, including discussion of the problems encountered during the turnover. The apparent cause of the loose fuse was that the fuse carriage became partially disconnected while removing other fuses from the same fuse panel, and eventually the fuse lost its electrical continuity. This condition is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. This event is not considered a Safety System Functional Failure.
3822003002 | Waterford 3 | 09/29/2003 | 11/26/2003 | ML03335026 | <strong>Failure of Emergency Diesel Generator A Fuel Oil Line</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2003 at about 1020 hrs with the plant in Mode 1 and at about 90% power coasting down for Refuel 12, Emergency Diesel Generator (EDG) 'A' was started to perform the monthly surveillance run in accordance with station operating procedures. At approximately 1309 hrs with the machine running loaded, the left/right bank cross connect tubing failed. This event rendered EDG 'A' inoperable. Although, EDG 'A' testing surveillances were successfully completed prior to September 29, 2003, there is firm evidence that after the last successful surveillance on September 2, 2003 EDG 'A' may not have been able to complete a mission run time of 24 hours. The allowed outage time for EDG 'A' is 72 hours. Therefore, this condition is reported as a condition prohibited by Technical Specifications pursuant to 10CFR50.73(a)(2)(i)(B). This event did not affect the health and safety of the public. There was no fire that resulted from the event. The fuel oil spill was contained within the EDG 'A' room and sump for EDG 'A' in Reactor Auxiliary Building. The spill was cleaned in about 45 minutes. The EDG 'A' was promptly restored to operable status. The Root Cause Analysis determined there were no generic implications from the event. Waterford 3 conducted a probabilistic evaluation for the event. The probability risk was determined to be low and to meet the threshold for low safety significance. In conclusion, the plant operated safely and maintained the capability to achieve safe shutdown.
3822003003 | Waterford 3 | 10/24/2003 | 12/18/2003 | ML03356024 | <strong>RCS Pressure Boundary Leakage Due to Primary Water Stress Corrosion Cracking (PWSCC)</strong><br /><i>Abstract:&nbsp;</i>During Waterford 3's Refuel 12 outage, three indications of Reactor Coolant System pressure boundary leakage were identified. The first indication of leakage was identified on October 24, 2003 during an Alloy 600 Program Plan inspection of the small bore nozzles on Hot Leg #2.The leakage was identified on instrument nozzle RC-IPT-0106B. The other two leakage indications were identified on October 26, 2003, while inspecting the pressurizer bottom nozzles and heater sleeves in accordance with the same inspection program plan. One of the two pressurizer leakage indications was identified on heater sleeve C-1, while the other was on heater sleeve C-3. All three leakage indications are believed to be the results of primary water stress corrosion cracking. Nozzle RC-IPT-0106B was repaired using a permanent partial nozzle welded repair. The heater sleeves were repaired using the Mechanical Nozzle Seal Assembly (MNSA-2). The conditions were found during the planned, scheduled inspection program before they could develop into significant leakage. The aggressive inspection and repair program reduces the potential safety significance, via early detection. Plant operations were unaffected and this event did not compromise the health and safety of the public or plant personnel. The conditions are not considered Safety System Functional Failures (SSFF).
3872003001 | Susquehanna 1 | 01/29/2003 | 02/11/2003 | ML03055068 | <strong>Unusual event Declared After Alarm on Unit 1 Turbine Building Ventilation Monitoring System</strong><br /><i>Abstract:&nbsp;</i>At 19:36 on January 29, 2003 a Ventilation Stack Monitoring System alarm was received in the Unit 1 Control Room. The cause of the alarm was a high indicated iodine release rate from the Unit 1 Turbine Building Ventilation Exhaust Stack. Control Room personnel responded to the alarm per plant procedure. After evaluation, an Unusual Event was declared at 20:32 based on the criteria in EAL 15.1.a.A.2. Evidence gathered to date indicates that the most likely cause is a simultaneous failure of the two in-series drain valves on the delay line drain pot in the Unit 1 Offgas System. This would have created a flow path for non-condensable gases from the offgas stream to the turbine building environment and subsequently to the Unit 1 Turbine Building Ventilation Exhaust Stack. After further evaluation, it was determined that the release stream did not contain an iodine component and the release rates were well below limits established in the Technical Requirements Manual. The iodine detector was responding to Nitrogen-13. The Unusual Event was terminated within six hours at 01:25 on January 30, 2003. A Root Cause Analysis (RCA) Team has been formed to evaluate this event and to determine the causes and corrective actions. In conjunction with this RCA team, a systematic troubleshooting effort is in progress. Iodine detector sensitivity to Nitrogen-13 was previously recognized. A similar event occurred in February of 2002. The Emergency Plan was not entered for this event because an Emergency Action Level criterion was not reached. An RCA Team evaluated this event; however, the corrective actions identified by this team were not completed when this latest event occurred.
3872003002 | Susquehanna 1, Susquehanna 2 | 04/16/2003 | 06/10/2003 | ML03170053 | <strong>Both Trains of Standby Gas Treatment Inoperable Due to Inadequate Maintenance and Inadequate Operability Testing</strong><br /><i>Abstract:&nbsp;</i>At 22:35 on April 16, 2003 with Unit 1 in Mode 1 at 100% power and Unit 2 in Mode 4 at 0% power, a Secondary Containment Surveillance Test revealed that the 'B' train of the Standby Gas Treatment System (SGTS) inlet damper was inoperable. Electrical Maintenance personnel discovered that the control circuit wires external to the damper actuator had their polarities reversed. Although the polarity reversal had existed since 1998, the damper became inoperable during actuator replacement work performed in November of 2002. Additionally, it was determined that the 'A' train of SGTS was removed from service several times while the 'B' train of SGTS was inoperable. The wiring error was corrected and the 'B' train of SGTS was returned to operable status at 14:15 on April 17, 2003. A root cause analysis was performed for the event and three root causes were found. The procedure used to replace the damper actuator was not explicit enough with respect to control circuit wiring configuration. Work Management personnel did not specify the correct operability testing for the actuator replacement on the work order release in 2002 and Operations release and dose out of the work order did not detect the omission. A contributing factor to the work order release errors is that station procedures and computerized workflow steps for the operability testing process contain inconsistencies. The procedures for actuator maintenance and operability testing will be revised to correct these deficiencies. This event is reportable as a Condition Prohibited by the Technical Specifications per 10 CFR 50.73(a)(2)(i)(B) and as an Event or Condition That Alone Could Prevent Fulfillment of a Safety Function per 10 CFR 50.73(a)(2)(v)(C) for Unit 1 and Unit 2. There were no actual consequences to the health and safety of the public as a result of this event since neither of the SGTS trains were required to actuate during the time they were inoperable.
3872003003 | Susquehanna 1, Susquehanna 2 | 04/16/2003 | 08/21/2003 | ML03248093 | <strong>Both Trains of Standby Gas Treatment Inoperable Due to Inadequate Maintenance and Inadequate Operability Testing</strong><br /><i>Abstract:&nbsp;</i>At 22:35 on April 16, 2003 with Unit 1 in Mode 1 at 100% power and Unit 2 in Mode 4 at 0% power, a Secondary Containment Surveillance Test revealed that the 'B' train of the Standby Gas Treatment System (SGTS) Inlet damper was inoperable. Electrical Maintenance personnel discovered that the control circuit wires external to the damper actuator had their polarities reversed. Although the polarity reversal had existed since 1998, the damper became inoperable during actuator replacement work performed in November of 2002. Additionally, it was determined that the 'A' train of SGTS was removed from service several times while the 'B' train of SGTS was inoperable. The wiring error was corrected and the 'B' train of SGTS was returned to operable status at 14:15 on April 17, 2003. Three root causes were found. The procedure used to replace the damper actuator was not explicit enough with respect to control circuit wiring configuration. Work Management personnel did not specify the correct operability testing for the actuator replacement on the work order release in 2002 and Operations release and close out of the work order did not detect the omission. A contributing factor to the work order release errors is that station procedures and computerized workflow steps for operability testing process contain inconsistencies. The procedures for actuator maintenance and operability testing will be revised to correct these deficiencies. This event is reportable as a Condition Prohibited by the Technical Specifications per 10CFR 50.73(a)(2)(i)(B) and as an Event or Condition That Alone Could Prevent Fulfillment of a Safety Function per 10 CFR 50.73(a)(2)(v)(C) for Unit 1 and Unit 2. There were no actual consequences to the health and safety of the public as a result of this event since neither of the SGTS trains were required to actuate during the time they were inoperable.
3872003004 | Susquehanna 1, Susquehanna 2 | 06/11/2003 | 08/11/2003 | ML03231045 | <strong>Loss of Control Structure Chiller Safety Function Due to Spurious Chiller Trip</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2003 at 1217 hours, the 'A' Control Structure (CS) chiller tripped while the 'B' CS chiller was inoperable for planned maintenance. With the 'A' and 'B' CS chillers inoperable, both trains of the Control Room Emergency Outside Air Supply (CREOAS) system and the Control Room Floor Cooling system were inoperable. In addition, the emergency source of cooling water to the Unit 1 Emergency Switchgear Room Coolers was inoperable. With two trains of the CREOAS system and Control Room Floor Cooling inoperable, Unit 1 and Unit 2 entered Technical Specification (TS) 3.0.3 and a controlled shutdown of the units was commenced. A four-hour ENS notification was made to the NRC at 1407 hours on June 11, 2003 in accordance with 10 CFR 50.72(b)(2)(i) due to the initiation of a TS-required plant shutdown. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(D), for a condition that could have prevented the fulfillment of a safety function and 10CFR 50.73(a)(2)(i)(B). The most probable cause for the CS chiller trip was due to a loose connection identified at Point 40 within the "High Bearing or High Motor Temperature" circuit. Another potential cause was a momentary loss of the "High Bearing or High Motor Temperature" circuit due to an unknown electrical transient. Thermography will be performed to check the Reactor Building (RB) and Turbine Building (TB) chillers for loose electrical connections. To prevent the station chillers from tripping due to operational perturbations, a modification will be performed to install a short time delay within the trip relays for the 'High Bearing or High Motor Temperature" circuit for the CS chillers. Similar modifications to the RB and TB chillers are also being investigated. The safety significance of this event was minimal and did not impact the health and safety of the public.
3872003005 | Susquehanna 1, Susquehanna 2 | 07/05/2000 | 11/10/2003 | ML04023046 | <strong>"D" Diesel Generator Fuel Rack Linkage Became Disconnected</strong><br /><i>Abstract:&nbsp;</i>During the performance of a monthly surveillance on March 19, 2003, the D Diesel Generator (DG) load suddenly decreased from 3000 kW to 2000 kW. Investigation revealed that the fuel control linkage had separated from the governor terminal shaft lever causing the change in generator output. A ½ inch bolt that is designed to attach the fuel control linkage to the governor terminal shaft lever was found to have backed out. The bolt was reinstalled and tightened and the D DG successfully passed the monthly surveillance. A Root Cause Analysis Team is nearing the completion of its review of this event. A review of maintenance records indicated that the only time this bolted connection is disturbed is when the EGB50 electro/mechanical governor is replaced. This governor was last replaced on the D DG on July 5, 2000. It is believed that a human performance error occurred when the ½ inch bolt was installed in a hand tight condition only. Since the bolt was not adequately tightened, it was subject to further loosening each time the D DG was run. During diesel generator runs, the linkage is exposed to movement as the fuel racks reposition and to the movement associated with normal diesel generator running vibration. These combined effects gradually allowed the ½ inch bolt to back out until the linkage became disconnected during the monthly surveillance run conducted on March 19, 2003. Immediate corrective actions included restoration of the D DG fuel control linkage to the governor terminal shaft lever, and verifying that this linkage was tight on all five Susquehanna Emergency Diesel Generators. Actions to prevent recurrence include human performance reviews, enhancing the work instructions that control the relevant activities to provide specific direction to apply Loctite and torque the ½ inch bolt, adding a confirmation requirement to this work step, and determining the torque requirements for any critical component fasteners that do not already have an established torque requirement on all five diesel generators.
3872003006 | Susquehanna 1 | 09/24/2003 | 11/19/2003 | ML03336061 | <strong>Automatic Scram and ECCS Injection Following "C" Reactor Feedpump Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At 00:53 on September 24, 2003 with Unit 1 in Mode 1 at 100% power, an automatic reactor scram occurred in response to low reactor water level conditions. While performing required testing of the 'C' Reactor Feed Pump Turbine (RFPT), a control room operator incorrectly manipulated the 'C' RFPT lockout key switch instead of the Reset pushbutton thus causing the turbine to trip. Although the 'A' and 'B' Reactor Feed Pumps increased speed in an attempt to maintain reactor inventory levels, the reactor automatically scrammed when water level reached the Low-Level RPS initiation setpoint. HPCI and RCIC automatically initiated to assist the operating Feed Pumps with level restoration. Numerous Primary Containment Isolations occurred as designed during the transient. Susquehanna was designed to withstand a single RFPT trip without experiencing a Rx Low-Level Scram. This event suggests that previous changes made at Susquehanna have affected the plant's integrated response to the loss of a single RFPT and have cumulatively resulted in a reduction of the originally designed operating margin. The RFPT trip has been attributed to human performance error. Error prevention techniques will be reinforced to support desired human performance attributes. The scram that resulted following the human performance error has been attributed to the reduction in operating margin resulting from inadequate identification of operating margin requirements in plant change processes. Corrective actions have been initiated to strengthen station operating margin controls within plant change processes. This event is reportable for Unit 1 as an unplanned actuation of systems that mitigate the consequences of significant events per 10 CFR 50.73(a)(2)(iv)(A). There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3872003007 | Susquehanna 1, Susquehanna 2 | 10/23/2003 | 12/19/2003 | ML04002034 | <strong>Common Cause Inoperability of Multiple Core Spray Channels</strong><br /><i>Abstract:&nbsp;</i>During performance of Core Spray quarterly flow surveillances conducted In October, 2003 ; the Unit I and the Unit 2 'D' Core Spray pumps were declared inoperable due to an oil foaming condition observed in the upper bearing oil reservoirs for each pump motor. Liquid oil levels dropped below established minimum levels for pump operation as a result of the foaming. In response, oil was drained, the oil reservoirs were inspected, and new Gulfcrest 32 oil was placed in the reservoirs. Oil foaming was not observed during subsequent pump runs and oil levels remained in the normal range. Oil samples taken from the affected pump motors, when analyzed for foaming tendency and stability levels, were found to exceed Industry standard warning limits. The samples also yielded contaminants that mix with additives contained in the Gulfcrest 32 product to form a salt or soap compound capable altering the foaming properties of Gulfcrest 32. An oil previously used in the Core Spray application is the probable source of these contaminants. Compatibility between the two oils was not considered during the design change process. Additionally, susceptibility to foaming can occur when anti-foaming additives "settle" during long term storage and fail to transfer in proper proportion as the oil is siphoned for use. The plant intends to replace the Gulfcrest 32 used in selected equipment, revise change processes to ensure product compatibilities, and adjust inventory levels to reduce settling. This event is reportable as a common cause inoperability of multiple Core Spray channels per 10 CFR 50.73(a)(2)(vii). There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3892003001 | St. Lucie 2 | 04/01/2003 | 06/02/2003 | ML03155006 | <strong>Manual Reactor Trip Due to Decreasing Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2003, St. Lucie Unit 2 was in Mode 1 operation at 100 percent power. At approximately 1500 hours, control room operators noted that the backpressure in the St. Lucie Unit 2 main condenser was slowly increasing. The operators attempted to perform the off-normal operating procedure for loss of condenser vacuum and recover condenser vacuum by placing the hogging ejectors (hoggers) in service. However, the operators performed a manual reactor trip at approximately 1603 hours when condenser backpressure reached the procedurally defined limit. The plant was stabilized in Mode 3 with feedwater supplied by the main feedwater system. The cause for the manual reactor trip was a reduction of main condenser vacuum caused by a combination of increased air in-leakage to the condenser via a corrosion induced through-wall hole in the steam jet air ejector piping and the degraded function of the 2A condenser hogger. The 2A hogger degraded operation was caused by an out-of calibration steam supply pressure gage. The faulty piping was replaced during the Spring 2003 St. Lucie Unit 2 refueling outage. The steam supply pressure gage that lead to degraded 2A hogger operation was replaced, and the hoggers were inspected during the outage with no significant findings noted. FPL is evaluating the planned and preventative maintenance practices for the hoggers.
3892003002 | St. Lucie 2 | 04/30/2003 | 06/25/2003 | ML03190004 | <strong>Two Flaws Identified During Refueling Outage Reactor Pressure Vessel Head Inspections</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2003, St. Lucie was in a refueling outage and the reactor pressure vessel head surface and associated penetration nozzles were being inspected in accordance with NRC Order EA-03-009. Although the head surface visual examination revealed no evidence of reactor coolant system boundary leakage, ultrasonic testing revealed an axial flaw in each of the nozzles for reactor pressure vessel head penetrations 18 and 72. No other indications were found during the inspection activities. The most likely cause of the nozzle flaws was attributed to primary water stress corrosion cracking. The subject nozzles were replaced during the refueling outage. St. Lucie will continue to perform reactor pressure vessel head surface and associated penetration nozzle inspections in accordance with the requirements of the NRC Order.
3892003003 | St. Lucie 2 | 06/11/2003 | 08/11/2003 | ML03225037 | <strong>Feedwater Control Malfunction Led to Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2003, St. Lucie Unit 2 was in Mode 1 at approximately 22 percent reactor power with steam generator level controlled by the low power feedwater control system. The 15 percent feedwater bypass valve, LCV-9005, failed closed at approximately 0122 hours and the 2A steam generator high/low level alarm occurred as water level decreased. Control room operators attempted to control the 2A steam generator level using the 100 percent feedwater bypass valve along with the main feedwater isolation valve. At 0129 hours level in the 2A steam generator exceeded the high high level setpoint and the resultant automatic turbine trip caused an automatic reactor trip on loss-of-load. The unit was stabilized in Mode 3. All safe shutdown equipment operated as designed, resulting in this event having no adverse impact on the health and safety of the public. LCV-9005 failed closed due to valve stem separation that was caused by vibration induced fatigue. An anticipatory manual reactor trip was not performed because the control room supervisors failed to provide effective command and control. Major corrective actions include the repair of LCV-9005, extent of condition review, immediate training for all licensed operators, removing involved control room supervisors from licensed activities until remedial training completed, and training of the event in Licensed Operator Continuing Training
3892003004 | St. Lucie 2 | 12/04/2003 | 02/02/2004 | ML04035033 | <strong>Condensate Pump Motor Bearing Failure Resulted in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 4, 2003, St. Lucie Unit 2 was in Mode 1 at 100 percent power. At approximately 1600 hours, the control room operators were informed that the lower motor bearing area of condensate pump 2A was "hot and smoky." At 1605 hours, a rapid down power was initiated to reach 45 percent power in order to remove condensate pump 2A from service. At 1632 hours, the operators manually tripped the reactor from 60 percent power due to the rapidly degrading condition of the 2A condensate pump. The plant was stabilized in Mode 3. All safe shutdown equipment operated as designed. There were no human performance issues related to the downpower or manual trip. The most probable cause of the lower motor bearing failure was determined to be improper lubrication. Plant procedures incorrectly identified that the bearing was factory sealed and required no lubrication. Corrective actions include the planned inspection and repair of the 2A condensate pump and motor, correction of the procedural error, identification of other motors with incorrect bearing classifications, and increased predictive maintenance vibration and thermography analyses for those motors until the bearings are lubricated and/or replaced.
3892003005 | St. Lucie 2 | 12/20/2003 | 02/18/2004 | ML04051027 | <strong>Automatic Reactor Trip Due to Loss of Turbine Generator Excitation</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2003, St. Lucie Unit 2 was in Mode 1 at 100 percent power. At 0948 hours St. Lucie Unit 2 automatically tripped from full power on loss of generator field current. Except for the overspeed trip of the 2C turbine-driven auxiliary feedwater pump, the plant trip response was uncomplicated as all safe shutdown equipment operated as designed. There were no human performance issues associated with the trip. Vendor assisted trouble shooting efforts identified that the failure of the main generator voltage regulator current regulator instant limiter module was the most likely root cause the December 20, 2003 trip. St. Lucie Unit 2 was returned to full service on December 28, 2003. The faulty module was replaced, and a temporary multi-channel recorder was installed to monitor key areas of the main generator automatic voltage regulator circuitry. This monitoring equipment will remain installed until the fall 2004 refueling outage.
3892003006 | St. Lucie 2 | 12/20/2003 | 02/18/2004 | ML04054058 | <strong>Long-Standing 2C TDAFW Pump Design Issue Resulted in Condition Prohibited by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2003, at 0948 hours, St. Lucie Unit 2 was in Mode 3 following a reactor trip from full power. Both steam generator levels decreased to below their auxiliary feedwater actuation signal (AFAS) setpoints, generating separate AFAS signals 10 seconds apart. The 2C turbine-driven auxiliary feedwater (TDAFW) pump started successfully, but experienced a mechanical overspeed trip approximately 38 seconds after the first AFAS signal. The cause of the overspeed trip was that the original AFAS design did not fully consider the effect of a staggered start on the turbine-driven pump. Additionally, the steam admission piping allows condensate build-up to upset the turbine and governor as the second steam admission valve opens. Contributing factors include procedural inadequacies for setting and testing the turbine governor, procedural inadequacies for positioning steam supply line valves to minimize condensate in the steam supply lines, and surveillance procedure inadequacies that did not test system response to a staggered AFAS initiation. The 2C TDAFW pump is undergoing enhanced testing and procedural revisions are in progress to address the causes and contributing factors.
3902003001 | Watts Bar 1 | 03/10/2003 | 05/09/2003 | ML03133005 | <strong>Automatic Reactor Trip Due to Moisture Intrusion into an Electrical Connector</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2003, at 0012 Eastern Standard Time, with Watts Bar 1 at 100 percent power, a Generator Backup Relay unexpectedly actuated causing an automatic turbine/reactor trip. The relay actuated due to a ground fault caused by a broken o-ring in the C phase main transformer's high side bushing capacitance tap connector. Plant safety equipment performed as designed which included the auto-start of the auxiliary feedwater system. The root cause of this event was inadequate preventive maintenance procedure. Corrective actions include repairing the connector, revising preventative maintenance (PM) procedures, and a design change to the affected single point vulnerability relay scheme.
3902003002 | Watts Bar 1 | 05/21/2003 | 07/21/2003 | ML03205028 | <strong>Failure in Power Distribution Panel in Reactor Protection Panel 1-R-9</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2003, WBN Unit 1 was operating at 100 percent reactor power. At approximately 2153 EDT, the WBN operators were alerted to potential instrument channel III trouble when control room alarms were received. This equipment provides channel III process instrumentation of the engineered safety features actuation subsystem portion of the Reactor Protection System. The operators were able to clear the alarms and plant continued operation. However, throughout the early morning of May 22, 2003, alarms indicating the same trouble continued. Maintenance personnel performed troubleshooting and identified that a faulty power distribution panel located within Reactor Protection Set Channel Ill, Panel 1-R-9 was the source of the problem. The faulty power distribution panel was replaced and Panel 1-R-9 was returned to service. Throughout this event, the operators did not identify Panel 1-R-9 as inoperable since after clearing the alarms, plant parameters were within range (with an exception of entry into LCO 3.4.1 RCS Pressure, Temperature, and Flow DNB Limits due to reactor coolant pressure less than 2214 for a short period) and plant operation continued. However, it was concluded after the event that the panel should have been declared inoperable and Technical Specifications actions completed within the 6 hour time requirements. This event is being reported under 10CFR50.73 (a)(2)(i)(B) as operation prohibited plant technical specifications. The cause for this event was that there was no specific guidance to assist the operators in diagnosing a panel malfunction of the sort that would also affect operability of the Reactor Protection System panel. Corrective actions include the development of an Abnormal Operating Procedure to address panel malfunctions. Additionally, the initial maintenance troubleshooting activities identified the problem to be in the data link handler portion of the rack which would not affect operability.
3902003003 | Watts Bar 1 | 08/25/2003 | 10/24/2003 | ML03303040 | <strong>Automatic Reactor Trip Due to Bumping of Main Transformer Sudden Pressure Relay</strong><br /><i>Abstract:&nbsp;</i>On August 25, 2003, Watts Bar (WBN) Unit 1 was operating at 100 percent power when there was an operation of the 2 out of 3 logic for the Sudden Pressure Relays (SPRs) for Main Transformer Bank 1C. The actuation of the relays resulted in a turbine trip and a subsequent reactor trip at approximately 0945 EDT. All control rods inserted as required and the safety systems actuated as designed including the motor and turbine driven pumps for the Auxiliary Feedwater (AFW) System. AFW pump 1B-B was available but not operable at the time of the trip due to work on an associated penetration room cooler. The pump started as required. There was no loss of safety function. Unit 1 was stabilized in Mode 3. The immediate cause of the trip was the actuation of the SPRs which were initiated by a worker bumping into the junction box that houses the relays in the switchyard. Subsequent to this, it was identified that the design of the SPR configuration was sensitive to actuation when force was applied to the relay housing junction box. Corrective actions include a modification to improve the vibration isolation of the SPRs and the installation of a permanent protective barrier fence with access gate around each of the four SPRs, pipe, hydraulic hose, junction box, and support installations to prevent accidental impact during normal plant operations. Trip hazard signs have been placed on the fence barrier.
3902003004 | Watts Bar 1 | 08/28/2003 | 05/21/2004 | ML04162017 | <strong>Emergency Core Cooling System Surveillance Requirement 3 .5 .2 .3 - Verify Piping is Full of Water</strong><br /><i>Abstract:&nbsp;</i>During preparation for the Unit 1 Cycle 5 refueling outage, work orders were being prepared to perform ultrasonic testing (UT) on the emergency core cooling system (ECCS) safety injection (SI) system "piggy back" supply piping to the SI pump (SIP) 1 B-B. During the history review of that system for the work order preparation, it was discovered that on January 14-15, 2003, the SIP was drained to support maintenance activities. It appeared that the draining and subsequent refilling of the SIP 1 B-B may have been inadequate because the associated work orders did not contain instructions for draining and refilling, and because there was no evidence of special precautions to assure the supply piping to the SIP 1 B-B was filled with water when restoring the equipment to service. The method of filling in the procedure involved valve alignments outside the clearance boundary and therefore, did not adequately address the piggy back line. A work order was initiated to perform UT which subsequently verified the presence of approximately 5.5 cubic feet of gas in the piping line. The gas in the line is contrary to Technical Specification Surveillance Requirement 3.5.2.3 to verify piping is full of water. A work order was initiated to vent the piping. Following the venting of the piping, a UT verified that the pipe was full of water.
3902003005 | Watts Bar 1 | 10/03/2003 | 12/02/2003 | ML03339009 | <strong>Accident Mitigation System Degraded Due to Both Trains of ABGTS Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2003, Watts Bar Nuclear Plant Unit 1 was in Mode 6 during a refueling outage with core re-load in progress. At 1516 hrs (EDT), main control room personnel became aware that an activity involved with an upcoming test had inappropriately placed the B-Train Auxiliary Building Gas Treatment System (ABGTS) Exhaust Fan 480v breaker in the OPEN position. An operator was immediately dispatched and the breaker was closed at 1521 hrs, restoring the train to OPERABLE status. The opening of this breaker at about 1324 hrs caused the B ABGTS train to be INOPERABLE at a time when the A-train ABGTS was available to start but technically inoperable due to an unavailable emergency power supply (2A-A Emergency Diesel Generator). The ABGTS system is required for the mitigation of a postulated fuel handling accident. The immediate cause of the event was human error by a shift test director who did not realize the A-Train ABGTS was inoperable when he directed opening the subject breaker in support of equipment alignments for the upcoming test. Corrective actions include counseling of involved individuals on their awareness of plant conditions and need for adequate communications and adding a separate item to the Outage Schedule for preliminary alignments for 18 Month Blackout tests. The safety significance of this event was low. In an actual FHA, performance of site emergency procedures would have detected and quickly restored ABGTS Train B. Further, with offsite power available, ABGTS Train A would have immediately responded to an event. Dose consequences assuming loss of all ABGTS were determined to remain with regulatory limits.
3902003006 | Watts Bar 1 | 10/21/2003 | 12/22/2003 | ML03363076 | <strong>Containment Spray Pump Inoperable Due To Open Breaker</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2003, WBN Unit 1 was returning to service after completion of the Cycle 5 refueling outage. The unit was in Mode 1 at approximately 36% reactor power, when it was established that 6.9KV Shutdown Board breaker, 1-BKR-72-10, was not connected and was not capable of supplying power to the Containment Spray System (CSS) Pump 1B-B. In accordance with LCO 3.6.6, "CSS," Pump 1B-B is required to be operable in Mode 4. The restoration of the breaker should have been performed in accordance with Section 5.2.8 of General Operating (GO) Instruction 1, "Unit Startup from Cold Shutdown to Hot Standby," and verified in accordance with Step 6 of Appendix B, "Mode 5-to-Mode 4 Review and Approval," of GO-1. Due to the CSS pump not being operable as the unit transitioned from Mode 5 to Mode 1, the mode change restrictions of LCO 3.0.4 were not met. The total time CSS Pump 1B-B was inoperable was approximately 113.6 hours. Considering this, Action A of LCO 3.6.6, "CSS," requires that an inoperable CSS train be restored within 72 hours. When this action is not met, Action C.1 requires that the Unit be in Mode 3 in 6 hours. Neither of these actions were met. The failure to comply with the requirements of LCO 3.0.4 and LCO 3.6.6 is being reported as a violation of the Technical Specifications in accordance with 10 CFR 50.73 (a)(2)(i)(B).
3952003001 | Summer 1 | 04/22/2003 | 06/13/2003 | ML03174017 | <strong>Steam Propagation Barrier Door Found Secured in Open Position</strong><br /><i>Abstract:&nbsp;</i>On April 22-23, 2003, steam propagation barrier door DRIB/107 was first discovered chained and strapped open and later found blocked open. This event was caused by a lack of specific training for the Security Officers assigned to continuously monitor materials stored in the room behind the door. The door was being opened to provide cooling to the Security Officer on duty in the area. Upon first discovery, the chains and straps were removed and the door was secured. Approximately 10 hours later, the door was found blocked open by the Security Officer on duty by physically standing with his back against the door. At this time the door was secured again. Investigation revealed the event was reportable under 10 CFR 50.73(a)(2)(i)(B). Opening door DRIB/107 beyond normal ingress and egress impacted both trains of control room ventilation as a result of breaching the pressure boundary encompassing all three Heating, Ventilation, and Cooling Water (HVAC) rooms. Loss of both trains of Control Room Ventilation is prohibited by Technical Specifications (TS) 3.7.6.
3952003002 | Summer 1 | 05/12/2003 | 07/02/2003 | ML03190006 | <strong>Reactor Trip Due to Main Generator Breaker Unexpectedly Opening</strong><br /><i>Abstract:&nbsp;</i>A reactor tip on Over Temperature Delta Temperature (OTDT) occurred from 100 percent power on May 12, 2003, at 0102 hours, due to the main generator breaker opening. A root cause team was assembled to investigate the cause of the trip. Troubleshooting identified that the main generator field breaker position sensing circuit had degraded contacts that caused the digital voltage regulator to sense a loss of excitation and open the main generator breaker. Immediate corrective action involved replacing degraded contacts, removing suspect breaker position switch contacts, and adding a redundant circuit for this voltage regulator anticipatory trip function. This was a programmed anticipatory trip function. The main generator never actually lost excitation until the trip and was fully protected. Notification of this event was reported under Event Notification EN# 39838 at 0328 hours on May 12, 2003 in accordance with 10 CFR 50.72(b)(l). Following the plant trip, all major systems functioned as expected. The plant was stabilized in Mode 3.
3952003003 | Summer 1 | 09/08/2003 | 02/27/2004 | ML04069067 | <strong>Control Room Ventilation Boundary Breached During Maintenance</strong><br /><i>Abstract:&nbsp;</i>On September 8, 2003, at 1530 hours maintenance personnel opened the "A" train Control Room charcoal filter plenum to replace a charcoal filter that failed surveillance testing. On September 9, at 0730 hours, the shift supervisor asked if the system could perform its design function during an accident in the current configuration. At approximately the same time (0805 hours), maintenance was directed to close up the system (reinstall the plenum covers and gag the isolation dampers closed). Engineering stated that the tag-out of the "A" train ventilation system inadvertently repositioned the isolation dampers for the emergency charcoal filter plenum and fan XFN 0030A open. The configuration would not allow maintaining the required positive 0.125 inch water column as specified in TS (3.7.6) and as verified by the intermittent control room low pressure alarms. This maintenance activity effectively breached the control room boundary and rendered the two emergency trains inoperable. This activity unknowingly placed the plant into Technical Specification Limiting Condition for Operability (LCO) 3.0.3, which requires 1 hour to prepare for plant shutdown and 6 hours to Hot Standby. This is being reported under 50.73(a)(2)(i)(B), a condition prohibited by Technical Specifications as the condition was undetected for 16 hours. Additionally, the event is reportable under 50.73 (a)(2)(v)(D) and 50.73(a)(2)(vii). Replacement of the charcoal was suspended and the filter plenum was closed and isolated by manually gagging the isolation dampers while a plan was developed that would not degrade the ventilation system (charcoal replacement was completed on September 10, 2003). The NRC Emergency Operations Center was notified at approximately 1130 hours; event number EN# 40142. A root cause evaluation has been completed and is attached to the corrective action document (CER 03-2819).
3952003004 | Summer 1 | 10/20/2003 | 06/29/2004 | ML04183036 | <strong>Reactor Coolant Pump Seal Infection Nozzle Leakaqe</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2003, during performance of surveillance test procedure, STP 250.001B, Boric Acid Inspection Program, boron was observed around the seal injection nozzle and on the thermal barrier casing of reactor coolant pump (RCP) "C". Inspection personnel contacted the Control Room and Outage Management at 1350 hours. Evaluation of the condition was initiated and a dye penetrant examination (PT) was scheduled for the morning of October 20. Evaluation of the PT results at 0700 hours on October 20 determined that the seal injection nozzle to the RCP thermal barrier casing had a surface breaking indication. This along with the visual evidence of Boric Acid residues indicated through-wall leakage at this point. Notification of this event was reported under Event Notification EN# 40261 at 1321 hours on October 20, 2003 in accordance with 10 CFR 50.72(b)(3)(ii)(A). The plant was shutdown for refueling, Mode 6. An ultrasonic test (UT) examination was performed and a "boat" sample was removed from the nozzle for metallurgical evaluation of cause and determination of any additional corrective action. The nozzle was replaced and tested satisfactorily. Visual Inspections were performed on RCP "A" and "B" with no through-wall leakage identified. The event is determined to have no safety significance since the leak rate was small. There was no previous indication of leakage on either the radiation monitors or through leak rate calculation results.
3952003005 | Summer 1 | 10/03/2003 | 12/15/2003 | ML03352029 | <strong>Failure of Master Relay K507 During Solid State Protection System Testing</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2003, it was determined by the Senior Vice President, Nuclear Operations that the following event was reportable as a significant safety hazard. On October 3, 2003, the V. C. Summer Nuclear Station (VCSNS) was performing solid state testing. The testing is in accordance with Surveillance Test Procedure (STP) 345.037, Solid State Protection System Actuation Logic and Master Relay Testing. At 1300, Master Relay K507, which actuates the Feed Water Isolation circuits upon Hi/Hi Steam Generator Water Level, failed to actuate. This component was a master relay with a paper wrapped coil, manufactured by MidTex (part number [P/N] 156-14D200). A Non-Conformance Notice (NCN 03-3099) was written, and the master relay was replaced on October 3, 2003. The cause of the master relay failure was determined to be an open circuit in the coil resulting from corrosion caused by off-gassing of chlorine contamination from the paper used to wrap the coil, or the adhesive used to attach the paper to the coil. An investigation into other master relays at VCSNS revealed that three additional MidTex P/N 156-14D200 relays with paper wrapped coils were installed in the Solid State Protection System. Although none of these had actually failed, they were replaced during Refueling Outage 14. The majority of the MidTex P/N 156-14D200 relays installed at VCS have cloth wrapped coils, and showed no evidence of corrosion. This event is being reported under 10 CFR 50.73(a)(2)(vii) and 10 CFR 21.21.
3952003006 | Summer 1 | 11/21/2003 | 01/20/2004 | ML04022046 | <strong>Manual Reactor Scram Due to Digital Rod Position Indication Failure</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2003, the V. C. Summer Nuclear Station was performing control rod testing (Mode 3) in preparation for plant start-up, following refueling outage-14. The testing is in accordance with Surveillance Test Procedure (STP) 106.002, Rod Position Indication Operational Test. The Reactor Trip Breakers were closed and Control Rod bank "C" was being withdrawn. When Control Rod bank "C" reached 36 steps, the Digital Rod Position Indication (DRPI) for Rod M-4 went to 18 steps. At 0835, control rod motion was stopped and Abnormal Operating Procedure (AOP) 403.5, Stuck or Misaligned Control Rod, was entered after verification that the procedure was applicable in the current plant condition. At 0910, while taking action per the AOP, it was determined that both channels of DRPI were not functioning properly. Per the V. C. Summer Nuclear Station Technical Specifications 3.1.3.3 and 3.10.5, with both channels of DRPI inoperable, the Reactor Trip Breakers must immediately be opened. This action was satisfied at approximately 0910. The Emergency Operating Procedure (EOP) for a plant trip was entered. At 0915, the EOP was exited with the plant stable in Mode 3. This event is being reported under 10 CFR50.73(a)(2)(IV)(A). The cause of the DRPI failure was a failure in a data encoder card for rod M-4. After card replacement and additional testing the DRPI system was declared Operable and control rod testing re-commenced.
3972003001 | Columbia | 04/03/2003 | 06/02/2003 | ML03161100 | <strong>Residual Heat Removal (RHR) B Train Potentially Inoperable During a Design Basis Event Due to Apparent Inability of System to Adequately Maintain Pressure as Assumed in Appendix R Analysis</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2002, it was discovered that the Residual Heat Removal (RHR)-B train may not remain operable in the event of a control room fire. On April 3, 2003, it was discovered that system test data existed indicating that discharge back-leakage of the RHR-B train may have been in excess of the Appendix R design assumptions since as early as 1997. The RHR-B train may not have been capable of supporting 10 CFR 50 Appendix R assumptions and, therefore, was technically inoperable without the proper compensatory actions being in place. With multiple RHR trains vulnerable to the same postulated fire, the plant was in an unanalyzed condition that could degrade plant safety. Therefore, this event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B). On October 24, 2002, compensatory measures were put in place making the RHR-B system operable but degraded. The cause of this condition was a failure to periodically test/verify an Appendix R design assumption. Corrective actions to prevent recurrence of this event include developing a method to periodically verify RHR-B ability to maintain pressure, reviewing abnormal procedures for the need for additional periodic surveillances, placing the Appendix R analysis requirements/assumptions into site documents to ensure they are periodically validated, establishing a process for ensuring assumptions are reviewed for incorporation into plant documents, and reviewing similar design basis special event analyses to verify operating and surveillance procedures exist.
3972003002 | Columbia | 05/15/2003 | 06/13/2003 | ML03171054 | <strong>Vulnerability in a Safeguards System that Could have Allowed Unauthorized or Undetected Access to a Protected Area</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2003, with Columbia Generating Station (Columbia) shut down for a refueling outage, a vulnerability in a safeguards system was discovered that could have allowed unauthorized -or-undetected access-to-the-Columbia protected area (ref: Event Report 39852).The vulnerability existed due to a Safeguards Information (SGI) container that was determined to be unlocked and unattended for a period of approximately 24 hours. The unlocked SGI container allowed access to site-specific drawings, diagrams, and technical details regarding the physical security system that could facilitate access to the protected and vital areas. Subsequent to discovery of the vulnerability, the contents were inventoried and fully accounted for. The SGI container is located in a room for which access is controlled with a keycard reader and there was no evidence of forced entry. Neither is there indication the vulnerable condition resulted in an actual unauthorized or undetected entry into the protected area nor has this event presented a challenge to the safe operation of Columbia.
3972003003 | Columbia | 05/21/2003 | 07/17/2003 | ML04156031 | <strong>Shutdown Cooling Isolation Caused by Deenergization of Wrong Relay During Work Activity</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2003, Columbia Generating Station was in Mode 5 (refueling) with the reactor head removed, the reactor cavity flooded to greater than or equal to 22 feet above the top of the reactor pressure vessel flange, and the fuel pool gates removed. At approximately 1155 PDT, an isolation of the Residual Heat Removal (RHR) Shutdown Cooling (SDC) common suction header occurred when the inboard isolation valve RHR-V-9 closed. A maintenance team assigned to repair a lug connector on relay MS-RLY-K72A mistakenly worked on relay MS-RLY-K72. The neutral wires of MS-RLY-K72 and MS-RLY-K29 are daisy chained together. When the neutral wire to K72 was disconnected, relay MS-RLY-K29 deenergized and caused RHR-V-9 to close. The closure of RHR-V-9 caused the operating RHR SDC pump to trip. The causes of this event are the failure of the maintenance technicians to seek verification and validation that the proper relay was being worked and less than adequate relay labeling. Corrective actions include counseling appropriate personnel on expectations for equipment identification, self checking, and sharing the event with maintenance personnel. In addition, the standards for device labeling within electrical cabinets will be reviewed and a standard instruction format for locating relays will be developed.
3972003004 | Columbia | 06/08/2003 | 08/07/2003 | ML03226064 | <strong>Condition Prohibited by Technical Specifications Limiting Condition for Operation 3.10.4</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2003, with the reactor shutdown in mode 4 and the mode switch in the refuel position, a condition prohibited by the Columbia Generating Station Technical Specifications existed. Specifically, function 7.a of Table 3.3.1.1.1 was not operable as required by special operations Limiting Condition for operations Limiting Condition for Operation (LCO) 3.10.4.c.1. Function 7.a of Table 3.3.1.1-1 is the transmitter/trip unit instrumentation [LT] that initiates a Reactor Protection System (RPS) trip on high Scram Discharge Volume (SDV) water level. This requirement of LCO 3.10.4 was not met because the transmitter/trip unit instrumentation on both SDVs was isolated in support of an SDV flushing procedure that was not in progress at the time. Special operations LCO 3.10.4 permits withdrawal of a single control rod for testing or maintenance and may be applied when the reactor is in cold shutdown. This LCO allows placing the reactor mode switch in the refuel position to enable the single control rod withdrawal permissive in order to perform control rod scram timing pursuant to Technical Specifications Surveillance Requirement 3.1.4.1 prior to reactor startup. The cause of the condition prohibited by Technical Specifications is attributed to human performance errors. No safety consequences were associated with the condition and redundant SDV float switches [LS] (Function 7.b) were operable to provide the RPS trip on high SDV level as required by LCO 3.10.4. This condition existed for approximately 5.5 hours during which time testing was performed on four control rods.
3972003005 | Columbia | 06/16/2003 | 08/14/2003 | ML03237051 | <strong>Shutdown Cooling Isolation Caused by Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2003, Columbia Generating Station was in Mode 4 (cold shutdown) with reactor coolant temperature at approximately 112 degrees Fahrenheit. At approximately 1330 PDT, an isolation of the Residual Heat Removal (RHR) Shutdown Cooling (SDC) common suction header occurred when the outboard containment isolation valve RHR-V-8 closed. The RHR SDC isolation occurred while performing a containment isolation logic functional surveillance test. Surveillance Procedure TSP-CONT/ISOL-B501, section 7.6. requires depressing the manual Nuclear Steam Supply Shutoff System (NSSSS) initiation logic B pushbutton. Depressing this pushbutton causes an isolation signal to 16 NSSSS isolation valves, including RHR-V-8. The primary cause of this event was an inadequate surveillance procedure. A contributing cause was inadequate preparation by operators performing the test. The surveillance procedure has been modified to specify the isolations that will occur when performing section 7.6. The pre job briefing sheet for TSP-CONT/ISOL-B501, section 7.6 has been modified to list the NSSSS isolations that will occur when Section 7.6 is performed.
3972003006 | Columbia | 02/16/2003 | 04/17/2003 | ML03119023 | <strong>Failure to Restore Emergency Diesel Generator Within TS Completion Time and Subsequent Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>February 13, 2003 with Columbia Generating Station (Columbia) operating in Mode 1 at 100% power, the Division 1 Emergency Diesel Generator (EDG-1) was declared inoperable at 2100 hours due to a lack of reasonable assurance of operability based on a degrading trend in the generator north bearing vibration levels. The amount of time required to correct this condition exceeded the 72 hour completion time requirements of Technical Specification (TS) 3.8.1, Condition B.4. Energy Northwest requested and received NRC enforcement discretion (NOED) from compliance with the completion time requirements of TS 3.8.1, Condition B.4, for 11 additional days. It was subsequently determined that both EDG-1 generator bearings required replacement. After the bearing replacement, vibration testing and analysis indicated the newly installed bearings were degrading. A failure analysis and a second replacement of the bearings could not be completed prior to the expiration of the NOED. Therefore, a reactor shutdown was commenced at 1945 on February 27, 2003 and Mode 4 was reached at 1721 on February 28, 2003. A root cause analysis concluded the cause of the degraded bearings was electrical arcing due to bearing electrical insulation system failure. Corrective actions include replacement of the bearings, restoration of the generator bearing electrical insulation system and improved methods of detecting the occurrence of electrical arcing in the generator bearings.
3972003007 | Columbia | 06/30/2003 | 08/28/2003 | ML03255032 | <strong>Automatic Reactor Scram Due To A Main Transformer Differential Current Relay Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2003 while operating at 79% power, Columbia Generating Station automatically scrammed due to a main transformer differential current relay actuation. All equipment operated within design parameters. The cause of the relay actuation was traced to an insulation failure on a current transformer secondary wire that created an impedance unbalance in the sensing circuitry. The root cause of this event is the original construction use of non jacketed cable (single conductor wiring) which is more prone to failure due to fretting action. Corrective actions were to replace main transformer current transformer wiring with jacketed cable. Jacketed cable has heavier insulation which is less susceptible to fretting. The plant's normal transformers were inspected and similar wiring was found in ideal condition.
3972003008 | Columbia | 07/08/2003 | 09/05/2003 | ML03265101 | <strong>Reactor Core Isolation Cooling Isolation Due to Inadvertent Closure of Containment Isolation Valve During Testing</strong><br /><i>Abstract:&nbsp;</i>On July 8, 2003, Columbia Generating Station (Columbia) was in Mode 1 with the reactor operating at approximately 73 percent of rated thermal power. At 1008 PDT, Reactor Core Isolation Cooling (RCIC) was declared inoperable after one of its steam supply containment isolation valves (RCIC-V-63) was inadvertently closed during the performance of a surveillance test. The surveillance test was discontinued and plant operators verified that the High Pressure Core Spray System was operable as required by Technical Specifications. The RCIC system was restored to its normal standby lineup and declared operable within one hour. The cause of this event was a personnel error by an I&C technician who was involved in performing a channel functional test at a differential pressure indicating switch (RCIC-DPIS-13B) which senses steam flow to the RCIC turbine. The technician inadvertently applied pressure from a nitrogen bottle to the high pressure side of RCIC-DPIS-13B causing an upscale condition which closed RCIC-V-63 before it was deactivated in accordance with the test procedure. The technicians involved in this event have been coached concerning human performance and the proper use of self-checking and peer-checking techniques. This incident was referenced as a recent example of a human performance error in human performance timeouts with maintenance teams The I&C Training Advisory Group will review this issue to determine how it should be included in future training.
3972003009 | Columbia | 08/22/2003 | 10/21/2003 | ML03303045 | <strong>Reactor Core Isolation Cooling Rendered Inoperable Due to a 250 VDC Battery Cell Not Meeting TS Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2003 at 0234 PDT, the Reactor Core Isolation Cooling system (RCIC) was isolated as a result of a battery cell in the Division 1 250 VDC battery (E-B2-1) not meeting Technical Specification (TS) battery cell parameter requirements. With E-B2-1 inoperable, TSs require the supported features of E-B2-1 to be immediately declared inoperable. RCIC-V-19, the RCIC pump minimum flow bypass valve, is a containment isolation valve. RCIC-V-19 is also supported by battery E-B2-1. RCIC-V-19 was declared inoperable, and was closed and deactivated to comply with plant TSs. Because RCIC-V-19 was inoperable, operators isolated the steam inlet valve (RCIC-V-1) to the RCIC turbine to prevent operation of the RCIC system. The isolation of the RCIC system is reported as an event or condition that could prevent the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Upon replacement of the battery cell, E-B2-1 was restored to service, and the RCIC system was declared operable at 1700 PDT on August 22, 2003.
3972003010 | Columbia | 10/07/2003 | 12/08/2003 | ML03353042 | <strong>Unanticipated Inoperability of the Single Train High Pressure Core Spray System</strong><br /><i>Abstract:&nbsp;</i>At 1231 on October 7, 2003, with the plant in mode 1, a depressurization of the High Pressure Core Spray (HPCS) system [BG] occurred while the HPCS system waterleg piping was isolated during an unscheduled maintenance activity to replace the power frame on the waterleg pump motor. System pressure unexpectedly decreased to below the low pressure alarm point requiring plant operators to remove fuses for the main HPCS pump and perform a system fill and vent procedure. These actions rendered the single train HPCS system inoperable. With the HPCS system inoperable, the action required by Technical Specifications Limiting Condition for Operation (LCO) 3.5.1.B to verify operability of the Reactor Core Isolation Cooling system [BN] and restore HPCS within 14 days was taken. Approximately three hours later at 1538, after verifying the system was filled and vented, and the pump fuses reinstalled, the HPCS system was declared operable and all requirements of LCO 3.5.1 were met. The cause of this event is attributed to the judgment of control room operators who allowed the maintenance to proceed when contingency actions to be taken in the event of unexpected system conditions had not been pre-planned. Prior to the maintenance, the control room operators developed contingency actions that were not adequate to manage a rapid depressurization of the HPCS system. There were no safety consequences associated with the inoperable HPCS system and this event did not represent an actual loss of a safety function for greater than the time allowed by Technical Specifications.
3972003012 | Columbia | 11/04/2003 | 01/05/2004 | ML04014031 | <strong>Unanticipated Inoperability of Both Trains of Control Room Emergency Filtration System</strong><br /><i>Abstract:&nbsp;</i>At 1953 on November 4, 2003, with the plant in mode 1, it was determined that a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident had existed on November 1, 2003. This condition occurred when the normal and both remote outside air intakes for the Control Room Emergency Filtration (CREF) [VI] system were manually isolated for a period of approximately 4 hours during testing to measure control room in-leakage. In this configuration, the CREF system cannot perform its design safety function to pressurize the main control room with filtered air as described in Columbia's accident analysis. When this discovery was made, the CREF system was in a normal standby configuration and the test procedure was revised to remove the errant steps. The inoperable CREF condition is also reportable as an event where a single condition caused two independent trains to become inoperable in a single system designed to mitigate the consequences of an accident. The cause of this event is attributed to, inadequate preparation and review of the test procedure used to measure control room in-leakage. The review did not identify that the procedure directed test personnel to place the CREF system in a configuration that would prevent the system from performing its design safety function. There were no safety consequences associated with the inoperable CREF system and this event did not represent an actual loss of a safety function for greater than the time allowed by Technical Specifications.
4002003001 | Harris | 05/18/2003 | 07/17/2003 | ML03203035 | <strong>Turbine Trip - Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2003, with the reactor at approximately 27% power following a refueling outage (RFO-11), the reactor was automatically tripped from a turbine trip-reactor trip signal. Plant equipment functioned as required. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load reactor coolant system (RCS) temperature and pressure following the reactor trip. The most likely failure mode is an electrical failure of the turbine overspeed sensing probe that resulted in generation of a spurious turbine overspeed signal. This spurious signal subsequently resulted in the reactor trip. An installed spare turbine overspeed sensing probe has been placed in service. The sensing probe that was in service at the time of the trip remains installed in the system and is unavailable for forensic analysis until the next refueling outage (RFO-12). The root cause is a design vulnerability in which a single component failure can result in a spurious turbine overspeed signal and subsequently cause a reactor trip. Corrective action includes modifying the electrical turbine overspeed circuit to remove single-point vulnerability for turbine overspeed sensing probe failures.
4002003002 | Harris | 05/20/2003 | 07/21/2003 | ML03210061 | <strong>Manual Reactor Trip Due to Trip of "A" Condensate Booster Pump</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2003 at 0453 with the reactor at approximately 20 percent power, the reactor was manually tripped in response to an automatic trip of the operating main feedwater pump (MFP). The WA' MFP tripped in response to an unplanned trip of the A" condensate booster pump (CBP). Both motor-driven auxiliary feedwater (AFW) pumps started due to the trip of the MFP. Safety systems functioned as required. The operations crew responded to the event in accordance with applicable plant procedures. The plant was stabilized at normal operating no-load reactor coolant system temperature and pressure following the reactor trip. The cause of the unplanned trip of the "A" CBP was due to low oil pressure after a gear in is variable speed fluid coupling (VSFC) failed following vendor refurbishment. Immediate corrective action was to replace the VSFC. Additional corrective action will be to specify a "run-in" of the gear set following VSFC refurbishment to develop adequate load-carrying capability of the gear teeth.
4002003003 | Harris | 06/14/2003 | 08/11/2003 | ML03227044 | <strong>Manual Reactor Trip Due to Loss of "B" Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2003 at 1053 EST with the reactor at 100% power, the reactor was manually tripped In response to an automatic trip of one of two operating main feedwater pumps (MFPs). The “B” MFP-tripped following the failure of a Westinghouse (NAL2) bistable comparator card associated with MFP feedwater flow control system. This card failure generated a spurious low-flow alarm and low-flow trip signal to the "B" MFP. Both motor-driven auxiliary feedwater (AFW) pumps and the turbine-driven AFW pump auto-started due to lo-lo steam generator level. Safety systems functioned as required. The operations crew responded to the event in accordance with applicable plant procedures. The cause of the unplanned trip of the “B" MFP was due to a failed T30 transistor on a NAL2 comparator card. Immediate corrective action was to replace the failed card. In addition, HNP will modify the system by the end of the next refueling outage (Fall, 2004) such that failure of an NAL2 bistable comparator card in the MFP control system will not cause an unnecessary MFP trip.
4002003004 | Harris | 06/15/2003 | 08/12/2003 | ML03230048 | <strong>Auxiliary Feedwater Actuation Following Closure of the Reactor Trip Breakers</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2003 at 0928 with the reactor shutdown in Mode 3, an automatic actuation of the auxiliary feedwater (AFW) system occurred following closure of the reactor trip breakers (RTBs) in preparation for a reactor startup. Due to an inappropriate equipment configuration, closing the reactor trip breakers resulted in two of the Main Feedwater Regulating Valves (MFRVs) opening to their full-open position. Water levels in two steam generators increased and exceeded the high-high level setpoint (78%). This condition resulted in a trip of the A" main feedwater pump, which initiated an auto actuation of both motor-driven auxiliary feedwater (MDAFW) pumps. The root causes of the event are substandard performance of license duties by both individuals and the control room team. Corrective actions for these events cover a broad spectrum of plant programs and personnel management including training, procedures, and personnel assignment. Immediate corrective action verified that plant components were properly aligned to support plant start-up and adjustment of the control room crew assignments. Additional corrective actions include revising the procedure to verify proper alignment of the MFRVs prior to closure of the RTBs (complete) and enhancing operator training.
4002003005 | Harris | 08/17/2003 | 10/09/2003 | ML03288046 | <strong>Manual Reactor Trip Following a Trip of the "A" Condensate Pump Motor</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2003 at 1551 with the reactor at approximately 100% power, the Harris Nuclear Plant (HNP) manually tripped the reactor in response to an automatic trip of one of two operating condensate pumps (CPS). The "A" CP tripped following an electrical short in its motor due to a severe lightning storm. The trip of the "A" CP resulted in subsequent trips of the "A" condensate booster pump and the "A" main feedwater pump (MFP) as designed. As directed by plant procedures, the operations crew manually tripped the reactor upon the trip of a MFP with initial reactor power greater than 90%. The manual reactor trip coupled with the trip of the "A" condensate and feedwater train resulted in a reduction of steam generator (SG) water levels. The subsequent low-low SG levels resulted in an auto-start of the auxiliary feedwater pumps as designed. Safety systems functioned as required. The cause of the unplanned trip of the "A" CP motor was a lightning voltage surge that overcame the dielectric strength of the motor winding insulation (i.e., an electrical short). In addition, the grounding system was not effective at protecting the "A" CP motor from a lightning strike. Corrective actions included replacing the "A" CP motor and installing surge protection. In addition, HNP will enhance the "A" CP grounding system and install surge protection on the "B" CP motor.
4002003006 | Harris | 10/17/2003 | 12/16/2003 | ML03357048 | <strong>Main Control Room Emergency Filtration System Degradation</strong><br /><i>Abstract:&nbsp;</i>Harris Nuclear Plant (HNP) personnel conducted surveillance testing of the Control Room Emergency Filtration System (CREFS) on October 17, 2003. Test results were inconsistent with past surveillances; as a result, interim administrative controls were established to ensure CREFS remained operable. An investigation identified two boundary leakage paths that allowed interaction between CREFS and the non-safety ventilation system in an adjacent area. The condition could have prevented CREFS from meeting its required design function under various operating configurations of the non-safety ventilation system. The root causes were inadequate design analyses and configuration controls related to the two boundary leakage paths. Corrective actions isolated the two identified leakage paths. Additional corrective actions will ensure the non-safety ventilation system is secured following receipt of a control room isolation actuation.
4102003001 | Nine Mile Point 2 | 07/24/2003 | 09/22/2003 | ML03281013 | <strong>Oscillation Power Range Scram Due to Power and Flow Perturbations Resulting From a Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2003, at approximately 0550 hours, Nine Mile Point Unit 2 (NMP2) experienced a power supply failure resulting in power and flow perturbations that lead to an automatic reactor scram at approximately 0557 hours. NMP2 was at approximately 100 percent power when the power supply failed, and was at approximately 45 percent power at the time of the scram. The failed power supply affected main steam flow instrumentation, feedwater level control and reactor recirculation flow control. Oscillation Power Range Monitor (OPRM) channels 1 and 4 generated the scram signal when detected power oscillations met trip criteria. The cause of the power and flow perturbations was the failure of non-safety related power supply C33-K611 (Lambda Model LRS-54-24). The power supply failed because of the age related failure of internal components and no preventive maintenance activity to refurbish or replace the power supply. Corrective actions included replacing the failed power supply, and two similar non-safety related power supplies, with auctioneer style power supplies (Lambda Model LZS-250-3), and adding power supply C33-K611 to the preventive maintenance program. Additionally, activities were initiated to replace non-safety related power supplies whose failure could result in a reactor scram, impact mission critical equipment, or cause a significant plant transient. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a critical reactor scram.
4102003002 | Nine Mile Point 2 | 08/14/2003 | 10/14/2003 | ML03297010 | <strong>Reactor Scram Due to Electric Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003 at approximately 1611 hours, Nine Mile Point Unit 2 automatically scrammed from 100% rated thermal power. The scram resulted from a turbine control valve fast closure signal that was generated as the electrohydraulic system (EHC) attempted to control turbine speed and reactor pressure in response to a severe disturbance in the electric grid. All three (Divisions 1, 2, and 3) emergency diesel generators (EDG) started as a result of the grid disturbance and each EDG powered its associated emergency bus. At 1700 hours an Unusual Event (UE) was declared because of grid instability. The UE was terminated at 0734 hours on August 15, 2003 after grid stability had been established and off-site power had been restored to all three emergency buses. After the scram, the turbine tripped as a result of high reactor vessel water level. The high water level occurred because the electrical transient had caused the feedwater flow control valves to lock up at approximately 55% open. Because the feedwater flow control valves had locked up, operators used reactor core isolation cooling (RCIC) to maintain reactor water level. Reactor pressure was initially controlled using the turbine bypass valves. The cause of the event was the severe disturbance in the electric grid. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) because of the reactor scram while critical, and because the automatic starting of the EDGs.
4102003003 | Nine Mile Point 2 | 10/02/2003 | 12/05/2003 | ML03350040 | <strong>Oscillation Power Range Monitor Inoperable Due to Non-Conservative Settings for Adjustable Parameters</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2003, Nine Mile Point Unit 2 (NMP2) was operating at approximately 100% power when Part 21 information was received from General Electric (GE) informing Nine Mile Point Nuclear Station, LLC (NMPNS) that the Oscillation Power Range Monitor (OPRM) may not prevent exceeding the Safety Limit Minimum Critical Power Ratio (SLMCPR) for all anticipated instability events. The OPRM was declared inoperable and the action statement of Technical Specification 3.3.1.1, "Reactor Protection System Instrumentation," was entered. As required by the action statement, alternate methods to detect and suppress thermal-hydraulic instabilities were implemented, which allows continued operation for 120 days with the OPRM inoperable. The cause was a failure to ensure through proper qualifications that the OPRM system, as implemented at the plant, is capable of performing its expected trip function during an instability event. There were two contributing factors: a) failure to recognize the conditioning filter actual performance when applied to plant data, and b) the erroneous assumption that "tuning" the system at stable conditions will result in proper system performance for unstable conditions. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(vii)(A) in that the non-conservatism could result in OPRM Setpoints that may not provide Minimum Critical Power Ratio (MCPR) Safety Limit protection for all anticipated thermal hydraulic instability events.
4122003001 | Beaver Valley 2 | 12/31/2002 | 02/28/2003 | ML03063034 | <strong>Lag Time Constant for Steam Line Pressure Channel Used in the Reactor Protection System Found Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>During a routine 18-month calibration of the Loop B Steamline Pressure Protection Channel used in the Reactor Protection System at Beaver Valley Power Station (BVPS) Unit No. 2 on December 31, 2002, the as-found value of the lag time constant was found to be 8.95 seconds on a lead/lag card. BVPS Unit 2 Technical Specification 3.3.2.1, Table 3.3-3, Functional Item 1.e requires that Tau 2 (lag time constant) be less than or equal to 5 seconds. Subsequent investigation found that sometime between the last calibration of this instrument channel and when this calibration was performed on this channel, the coarse time constant switch was changed from setting 5 to 6, which caused the lag time constant to be out of tolerance. There were no known activities ongoing prior to the commencement of this calibration surveillance on December 31, 2002. Since firm evidence existed that the lag time constant was known to be at a value prohibited by BVPS Unit No. 2 Technical Specifications, then Action 14 of Table 3.3-3 in Technical Specification 3.3.2.1 was not met before December 31, 2002. This constituted a condition prohibited by plant Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The cause for the lag time constant discrepancy at BVPS Unit 2 was determined to be a human performance error by an Instrument and Control Technician. The exact time and place of the occurrence could not be definitively determined. The current licensing bases analyses remained conservative even with the incorrectly set low steam pressure lead/lag. Therefore, safety significance of this event was small.
4122003002 | Beaver Valley 2 | 06/11/2003 | 09/29/2003 | ML03280080 | <strong>Potential to Deadhead a Component Cooling Water System Pump Violates Safety Analyses Assumptions</strong><br /><i>Abstract:&nbsp;</i>During an evaluation of a previously identified design review issue with the Component Cooling Water System (CCP) at Beaver Valley Power Station (BVPS) Unit No. 2, it was determined that CCP minimum pump flow may not be met during a post-accident scenario involving specific conditions and timing. Specifically, the "B" CCP pump had been previously replaced with a stronger (head vs. flow) pump than the "A" or "C" train CCP pump. With the prior CCP operating criteria, a design bases accident (DBA) involving a complete loss of offsite power (LOOP) and a consequential start of both trains of CCP after onsite emergency power is restored by both emergency diesel generators starting, could result in the CCP pump with the weaker pump head versus flow characteristics becoming deadheaded and losing its minimum required flow. This could lead to failure of the weaker CCP pump. A single failure is then postulated (as required) to occur on the stronger "B" CCP pump which results in no CCP flow. This was determined to be a condition prohibited by plant Technical Specifications since the CCP system operation is needed for BVPS Unit 2 to reach Mode 5. Further review identified an additional post-accident scenario involving a LOOP and a containment isolation Phase A which needed to be addressed by the engineering analyses developed to resolve this issue. The new scenario involved a pump runout condition. The root cause of this condition is the original design of the BVPS Unit 2 CCP system in that the system had inherent flow instability characteristics which required constant automatic operation of the system's differential control valves for appropriate compensation. The safety significance of this event was determined to be small. Corrective actions were implemented to eliminate the possibility for losing CCP flow following a DBA.
4122003003 | Beaver Valley 2 | 10/14/2003 | 12/11/2003 | ML03351023 | <strong>Automatic Reactor Trip Due to Low Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2003, at 2355 hours, Beaver Valley Power Station Unit No. 2 reactor automatically tripped from 39 percent power and Auxiliary Feedwater was actuated due to low-low level in the "B" Steam Generator. Prior to the reactor trip, the control room operators were reducing power from 65 to 30 percent to support mechanical maintenance on the Heater Drain Pumps. The root cause was determined to be a failure of the Westinghouse 7300 multiplier/divider card, 2FWSFX486, in the channel IV "B" loop feedwater flow channel. After the reactor trip, Emergency Operating Procedure E-0 for Reactor Trip was performed, the plant was stabilized in Mode 3 and safety systems functioned as designed. This event was reported under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A) as a Reactor Protection System (RPS) actuation reactor trip. This event is also reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the RPS and Auxiliary Feedwater System that was not part of a pre-planned sequence. Based on the conditional core damage probability for the event when considering the actual component unavailability that was present at the time of the reactor trip, the safety significance of the automatic reactor trip was low.
4132003001 | Catawba 1 | 02/04/2003 | 03/24/2003 | ML03092001 | <strong>High Steam Generator Level Turbine Trip Causes Reactor Trip and Automatic Start of Motor Driven Auxiliary Feedwater System Pumps</strong><br /><i>Abstract:&nbsp;</i>February 4, 2003, at 1005 hours, Catawba Unit 1 tripped from 100% power. A Main Feedwater (MFW) System header pressure transmitter was being returned to service following replacement. As the transmitter was valved in, its hydraulic interaction with the other two nearby transmitters caused MFW header pressure indication to the MFW control system to fluctuate. In response to the transient, the MFW control system switched from automatic to manual control, as designed, at a pre determined pressure difference between the transmitters. As control room operators attempted to control steam generator levels manually, a high-high level on steam generator B resulted in a turbine trip, which resulted in a reactor trip. The high-high level also resulted in a trip of the MFW pumps, which caused an automatic start of the motor driven Auxiliary Feedwater (AFW) System pumps. This event was caused by an inadequate understanding of the MFW control system response to a common impulse line hydraulic interaction. Corrective actions planned in response to this event include training appropriate plant personnel concerning MFW control system design and response and revising procedures associated with the calibration and maintenance of selected transmitters.
4132003002 | Catawba 1, Catawba 2 | 02/12/2003 | 04/09/2003 | ML03106033 | <strong>Loss of Safety Function Due to Inoperability of the 2B Diesel Generator Upon Loss of Vital Inverter 2EID with the 2A Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0945 on February 12, 2003 Unit 2 experienced a loss of vital inverter 2EID resulting in a loss of power to channel IV 120 VAC panel board 2ERPD. 2ERPD provides power to support equipment for the 2B diesel generator (DG). This resulted in declaring the 2B DG inoperable. The 2A DG had been previously taken out of service for routine maintenance. This resulted in both DGs on Unit 2 being declared inoperable. This also resulted in both the 2A and 2B nuclear service water system (RN) pumps being inoperable. RN is a shared system between Unit 2 and Unit 1. TS 3.7.8 does not provide any actions for two RN pumps being inoperable so, both-Units entered TS 3.0.3. Power was restored to 2ERPD at 1028 when the alternate source, 2VRD, was manually aligned to provide power to 2ERPD, which allowed both units to exit TS 3.0.3. The cause of the 2EID failure on February 12, 2003 is a fabrication deficiency in choke CH804. The failed choke CH804 was replaced and the inverter aligned to supply power to 2ERPD. The vital inverters for both units at Catawba are being replaced with new models. The health and safety of the public was not affected.
4132003003 | Catawba 1 | 04/04/2003 | 09/25/2003 | ML03281044 | <strong>Failure of 4160 Volt Breaker Renders 1B1 Component Cooling Water Pump Inoperable for Longer than Technical Specifications Allow</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2003 during a start attempt on the 1B1 Component Cooling Water (CCW) pump, the pump would not start with the push button in the control room. The 1B1 CCW pump was declared inoperable and the actions of technical specifications (TS) were applied. Troubleshooting indicated that the failure was internal to the breaker 1ETB6. The breaker was replaced with a spare breaker and the 1B1 CCW pump was satisfactorily tested and declared operable. Additional testing narrowed the failure to the control device on the breaker. The control device was sent to the manufacturer for analysis. The vendor found an intermittent interference problem internal to the control device. Examination of the failure mode led to the conclusion that the breaker was most likely in this condition since the last time the breaker had been operated. Prior to this event, the 1B1 CCW pump had been started to support CCW system testing and had last been closed and tripped on 4/01/03. Therefore, 1B1 CCW pump had been inoperable since 4/1/03. This time frame exceeded the required action time of TS 3.7.7. The overall safety significance of this event was determined to be minimal and there was no actual impact on the health and safety of the public.
4132003004 | Catawba 1 | 05/11/2003 | 07/10/2003 | ML03197006 | <strong>1A Containment Spray System Inoperable for Longer than Technical Specifications Allow Due to Heat Exchanger Fouling</strong><br /><i>Abstract:&nbsp;</i>The 1A containment spray system (CSS) was declared inoperable on May 8, 2003 at 0918 hours for testing evolutions. During the testing of the 1A CSS heat exchanger the acceptance criterion of procedure PT/l/A/4400/009, "Cooling Water Flow Monitoring for Asiatic Clams and Mussels Quarterly Test" was not met. This procedure is used to monitor flow resistance in the CSS heat exchanger and essential nuclear service water system (NSWS) piping. Engineering, Operations, and Maintenance investigated the cause of the failed test for the 1A CSS heat exchanger. Necessary inspection, chemical cleaning and subsequent testing activities could not be completed by May 11, 2003 at 0918 hours. Duke Energy requested a Notice of Enforcement Discretion from the NRC so that the Completion Time for the Required Actions of the Technical Specifications for the CSS would be extended from the current 72 hours by an additional 168 hours, for a total of 240 hours, so that this work could be completed. The NRC granted the request on May 10, 2003. The CSS 1A heat exchanger was chemically cleaned, tested and declared operable on May 17, 2003 at 0454.
4132003005 | Catawba 1 | 08/29/2003 | 10/21/2003 | ML03309040 | <strong>Reactor Trip Due to Pressurizer Pressure Channel Failure</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2003 at 0203 hours with Catawba Unit 1 operating in Mode 1 at 95% power, an automatic reactor trip occurred due to an instrument failure. The reactor trip was caused by the pressurizer pressure channel 2 failing low resulting in the reduction of the loop 1B overtemperature delta T (OTdT) setpoint to approximately 50%. When the OTdT setpoint reached the operating value of the loop 1B conditions (approximately 95%), an automatic reactor trip was initiated on 2/4 OTdT trip bistables. The loop 1A OTdT trip bistable was previously tripped due to a reactor coolant system hot leg temperature detector failure. This event was caused by the equipment failure of the pressurizer pressure loop power supply card. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. Corrective actions for this event included repairs to the pressurizer pressure channel and reactor coolant system hot leg temperature detectors.
4132003006 | Catawba 1 | 10/09/2003 | 12/08/2003 | ML03350033 | <strong>1B Containment Spray System Inoperable For Longer Than Technical Specifications Allow Due To Heat Exchanger Baffle Plate Degradation</strong><br /><i>Abstract:&nbsp;</i>The 1B containment spray system (CSS) was declared inoperable on October 6, 2003 at 0400 hours to allow the installation of inspection ports to support upcoming Unit 1 refueling activities. Inspections of the 1B CSS heat exchanger revealed degradation of the baffle plates. Engineering review of the 1B CSS heat exchanger determined that the heat exchanger could not be returned to service within the time limits required by Technical Specifications (TS). A notice of enforcement discretion (NOED) was requested from the NRC to allow time to prepare and approve an exigent TS change to support continued operation. The NRC granted the NOED on October 9, 2003 at 2125. Subsequent evaluations by engineering with support from a vendor determined that the1B CSS heat exchanger could be determined to be operable with some limitations on shell side flows. This evaluation was reviewed and approved by station management and the 1B CSS heat exchanger was declared operable on October 21, 2003 at 2106. The exigent TS change was determined to not be required and was withdrawn. The 1B CSS heat exchanger is being replaced during the current Unit 1 refueling outage. The health and safety of the public was not affected.
4142003001 | Catawba 2 | 08/16/2003 | 10/09/2003 | ML03294056 | <strong>Two Channels of RWST Level Instrumentation Were Rendered Inoperable Following Lightning Strike, Resulting in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2003, at 0753, Channels 1 and 3 of Refueling Water Storage Tank (RWST) level instrumentation failed high in response to an apparent lightning strike in the area. Both of the failed channels were placed in bypass and Unit 2 entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3. Unit 2 began a TS required shutdown at 0850 and the NRC Operations Center was subsequently notified. Catawba pursued a Notice of Enforcement Discretion (NOED) with NRC Region II to allow an additional 48 hours to troubleshoot and repair the failed level channels prior to having to place Unit 2 in Mode 3. The NRC verbally granted the NOED at 1115. The first of the two inoperable channels was restored to operable status at 1357, which allowed Unit 2 to exit LCO 3.0.3; therefore, the NOED was never actually utilized. The root cause of this event was determined to be the fact that Channels 1 and 3 of RWST level instrumentation appear particularly sensitive to the effects of lightning. Planned corrective actions in response to this event include improving the RWST level transmitter grounding circuits and quality of ground connections.
4162003001 | Grand Gulf 1 | 01/30/2003 | 03/31/2003 | ML03091023 | <strong>Manual Reactor SCRAM Due to Loss of Condensate/ Feedwater</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2003, at approximately 10:54 a.m., Grand Gulf Nuclear Station was operating at 100 percent power when operators inserted a manual reactor scram. The manual scram was initiated due to decreasing reactor water level resulting from a loss of feedwater. The loss of feedwater was caused by isolation of the condensate demineralizers due to shorting of a conductor which tripped the common power supply for the position indication limit switches for the demineralizers valves. The loss of the inlet valve's position indication caused all operating demineralizer outlet valves to close. High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) auto initiated and injected into the reactor vessel to restore level. In response to the HPCS initiation the Division 3 Emergency Diesel Generator auto started but was not needed to supply the Division 3 Buss. As designed, Standby Service Water system loops "A" and "C" started, for required support of equipment.
4162003002 | Grand Gulf 1 | 04/24/2003 | 06/23/2003 | ML03279036 | <strong>Reactor Scram Due to a Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>GGNS automatically scrammed at approximately 0948 CDST on 4/24/2003 due to a partial loss of offsite power. At the time of the scram, there was a severe thunderstorm in the vicinity. High winds apparently resulted in closure of an open disconnect in the GGNS Switchyard which in turn led to the partial loss of offsite power. During the event the Reactor Protection System (RPS) auto-actuated; High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) auto-initiated on Reactor (Rx) Water Level 2 and injected into the Rx to restore Rx water level; Division 2 and 3 Diesel Generators (DGs) started and energized the 16AB and 17AC Electrical Buses, respectively; the 15AA Electrical Bus lost power and was re-energized by the Division 1 DG shortly after the initial event; all Standby Service Water (SSW) divisions started; all main steam line isolation valves (MSIVs) isolated on loss of power; and containment isolation occurred. Rx water level and pressure were restored and stabilized. Plant data was reviewed to confirm proper response of plant equipment. Switchyard inspections were conducted to assess damage and verify equipment condition prior to restoring tripped equipment. The NRC Resident Inspector was notified. NRC call-in per 10CFR50.72(b)(2)(iv) and 10CFR50.72(b)(3)(iv) was made at 1320 CDST.
4162003003 | Grand Gulf 1 | 08/17/2003 | 10/15/2003 | ML03290090 | <strong>Containment Airlock Seal Air Leakage in Excess of Technical Specification Allowable Rate</strong><br /><i>Abstract:&nbsp;</i>On August 16 and 17, 2003, during performance of "Personnel Airlock Door Seal Air System Leak Test," on the outer door of the Upper Containment Airlock, the air system leakage was found to be 2.3 pounds/square inch gauge (psig) in 48 hours, compared to the permissible leakage rate of 2 psig in 48 hours specified in Technical Specification SR 3.6.1.2.4. Preceding the above test On August 15, 2003, during initial testing on the inner door of the Upper Containment Airlock [BD] Seal System, the air system leakage was recorded to be approximately 81.6 psig in 48 hours. This leakage rate exceeds the permissible leakage rate of 2 psig in 48 hours specified in Technical Specification SR 3.6.1.2.4. In both cases immediate actions were taken to correct the leakage. The pressure switches for the doors and the "O" ring for the inner door clevis valve were replaced. The re-test for both doors was successful and the System was declared operable. The repetitive failure of two same types of pressure switches constituted "Common Cause Failure". The event is being reported per 10CFR50.73 (a)(2)(vii) due to a single cause or condition causing two independent trains to become inoperable in a single system designed to control the release of radioactive material.
4232003001 | Millstone 3 | 12/23/2002 | 02/20/2003 | ML03065092 | <strong>Reactor Trip Caused by Generator Backup Protection Fault</strong><br /><i>Abstract:&nbsp;</i>On December 23, 2002, at approximately 0200 with the plant at 100% power, a reactor trip occurred following a Generator fault. The appropriate alarms were received just prior to the trip. In addition, the trip signal opened a series of breakers and the Turbine and Reactor tripped sequentially. The Turbine Stop Valves closed within one second. The Steam Generator level shrinkage caused a low level in the Steam Generators starting the Auxiliary Feedwater System within 6 seconds, which was an expected occurrence. During and after the plant trip all main and auxiliary equipment functioned as designed and plant operators stabilized the plant in MODE 3. The generator stator fault on phase A was found to be due to an arc to ground associated with the T-4 high voltage bushing. Specifically, stator cooling water was leaking through a pin-hole at the joint area (braze material) of the tubular lead conductor and the cooling water inlet fitting. The leaking cooling water traveled along the bushing body underneath the insulation package where the leaking coolant picked up contaminants (making it more conductive). The leaking contaminated water ultimately traversed the entire bushing to the point of contacting the housing enclosure (ground). Per vendor evaluation, the leak was due to a void/porosity issue with the braze material itself. This was most likely a fabrication deficiency that deteriorated over time. The leak was repaired through re-brazing on the T-4 tubular lead connector and system integrity was confirmed through pressure testing. Other appropriate corrective actions are being addressed in accordance with the Millstone Corrective Action Program.
4232003002 | Millstone 3 | 01/16/2003 | 03/13/2003 | ML03085010 | <strong>Fire Safe Shutdown Strategy May Not Be Adequate For Fire Scenarios Which Assume Loss of All AC Power</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2003, while operating in Mode 1 at 100% power, an engineering evaluation concluded that the fire safe shutdown strategy may not be adequate for fire scenarios which assume the loss of all AC power. For these fire scenarios, both offsite and onsite AC power are assumed lost. The fire safe shutdown strategy assumes that power is manually restored 30 minutes later. As part of an engineering evaluation, it was concluded that this loss of offsite power with delayed emergency diesel generator availability could result in a pressure/temperature transient to the reactor coolant pump (RCP) seal return lines resulting in their failure. This failure would cause increased flow from the reactor coolant system beyond the make-up strategy established in the fire safe shutdown procedures and would also challenge the boration strategies. Since the fire safe shutdown strategy has been determined to be inadequate, this constitutes an unanalyzed condition that could significantly degrade plant safety and is being reported in accordance with 10CFR50.73(a)(2)(ii)(B). This condition is historical in nature dating to the original design of the RCP seal return lines and the development of the fire safe shutdown strategies. The apparent cause is a failure to recognize that a pressure/temperature transient at the RCP seal return lines could occur as part of the fire safe shutdown strategy. Upon discovery of this condition, compensatory actions to minimize risk of fire in the areas of concern were implemented. These compensatory measures will remain until needed Emergency Operating Procedure revisions, plant modifications, or further analysis are made to address this condition.
4242003001 | Vogtle 1 | 04/06/2002 | 09/11/2003 | ML03258041 | <strong>Debris in Containment Could Have Resulted in Safety System Loss of Function</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2003, an evaluation was completed that determined a safety system functional failure could have occurred on April 6 & 7, 2002, following the 1R10 refueling outage. Specifically, it was determined that the containment building held debris in an amount adequate to block the containment sump screens, which could result in inadequate net positive suction head and possible failure of the residual heat removal (RHR) pumps to perform at design limiting conditions. This may have occurred following a design basis accident had these pumps been called on to operate and draw suction from the containment sumps. The condition existed for a period of 37 hours and 12 minutes while the unit was subcritical, until a containment cleanliness walkdown removed enough of the debris to reduce the cross-sectional area of the sump screen blockage to an acceptable level. The July 28, 2003, evaluation included expanded insulation destruction due to missing insulation jacketing which increased the insulation debris contributing to sump blockage. The cause of this event was inadequate removal of debris from the Unit 1 containment building prior to Mode 4 (hot shutdown) heat-up. Debris was removed prior to the unit's return to power operations.
4242003002 | Vogtle 1 | 10/22/2003 | 12/15/2003 | ML03351026 | <strong>Ruptured Steam Hose Coupling Leads To Manual Main Steam Line Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2003, personnel were attempting to vent the bonnet cavities and equalize pressure on either side of the main steam isolation valves (MSIVs). In the South Main Steam Valve Room (SMSVR), a high pressure hose was connected to piping outside of double isolation valves for the Loop 4 Train B MSIV drain line. The inside drain line isolation valve was fully opened, the outside drain line isolation valve was partially opened, and a rubber seal at the first hose connection blew out. Steam exiting from this connection blocked the doorway to the room and also prevented the drain line isolation valves from being closed. Personnel phoned the control room and asked that the MSIV be closed. The Unit Shift Supervisor (USS) ordered a manual main steam line isolation (MSLI), which occurred at 0256 EDT, and personnel safely exited the SMSVR. The cause of this event was the use of inadequately rated hose couplings. The proper high pressure hose and couplings are being procured.
4252003001 | Vogtle 2 | 11/05/2003 | 06/29/2004 | ML04188015 | <strong>Tech. Spec. Required Shutdown Not Performed Following Issuance of NOED</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2003, personnel were performing Technical Specification (TS) surveillances on the Solid State Protection System (SSPS). A switch in the test circuit that is used to test memories logic functions would not operate properly in all positions. This prevented successful completion of the surveillance testing for some functions, which was due by November 5, 2003. After this time, following completion of a 24-hour TS Required Action Completion Time, a unit shutdown would have been required to be initiated per the action requirements of the TS. A telephone conversation with NRC personnel was conducted on November 4, 2003. During this conversation, the NRC granted a notice of enforcement discretion (NOED) allowing the TS surveillance requirements to be late without enforcement for a period of 28 days. The 28 days represented a reasonable period of time for a written request, to change the TS, to be processed by the NRC. The TS change allowed the required surveillance testing to be delayed until after the end of the fuel cycle in Spring 2004, or until the next unit shutdown to Mode 5 (Cold Shutdown), whichever comes first. On December 3, 2003, the requested TS change was approved. The cause of the event was found to be a failure of a reset pushbutton in the same circuit as the test switch. After the defective pushbutton switch was replaced, the deferred surveillance testing was completed satisfactorily. Similar pushbuttons will be replaced during the next refueling outage in each unit.
4402003001 | Perry | 05/10/2003 | 07/03/2003 | ML03195014 | <strong>Manual Actuation of the Reactor Protection System With All Control Rods Inserted During Testing</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2003, the reactor was in Mode 5, Refueling with the "Low Pressure Core Spray/Low Pressure Coolant Injection A Initiation and EH11 Response Time Test" in progress. This test verifies the plant response for a simulated Division 1 loss of offsite power/loss of coolant accident. One of the expected results of the test is the closure of instrument air containment isolation valve. After closure of instrument air containment isolation valve, the procedure requires the valve to be opened from the Control Room using the LOCA override control switch. When this was attempted, the valve did not open. The loss of instrument air to containment resulted in a decreasing scram air header pressure that if allowed to continue to decrease would result in opening of the scram pilot valves and then the scram valves. Due to the decreasing scram air header pressure, a manual scram was initiated at 1509 hours The NRC Incident Response Center was notified at 2054 hours in accordance with 10CFR50.72(b)(3)(iv)(A) and this report is being submitted per 10CFR50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of the Reactor Protection System. The failure of the valve to open was caused by a manufacturing defect of an Agastat relay. This event had minimal safety significance and a very small increase in risk. A new relay was installed and tested satisfactorily.
4402003002 | Perry | 08/14/2003 | 12/12/2003 | ML03353011 | <strong>Reactor Scram as a Result of a Loss of Off-site Power</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2003, at 1610 hours, with the Perry Nuclear Power Plant operating in Mode 1, at approximately 100 percent reactor power, a generator trip due to under-frequency occurred resulting in a turbine control valve fast closure scram. The under-frequency was the result of a loss of off-site power. The cause of the grid disturbance that resulted in the loss of off-site power is still under investigation by First Energy. The loss of off-site power required entry into the emergency plan for an Unusual Event. Entry into the emergency plan is reportable per 10CFR50.72(a)(1)(i). Additional reporting requirements are documented in the event report. Loss of off-site power to the safety-related emergency power supply busses for greater than 15 minutes resulted in the declaration of an Unusual Event, which was reported to the NRC via the Emergency Notification System (ENS) at 1635hours. Subsequently, it was recognized that power was not available at the Emergency Operations Facility and the Backup Emergency Operations Facility. This condition was reported to the NRC via the ENS at 2225 hours. The Unusual Event was terminated at 1952 hours on August 15, 2003, following restoration of off-site power. Following restoration of power to the emergency busses with the emergency diesel generators, low pressure alarms were received on low pressure core spray (LPCS) and on residual heat removal (RHR) A loop. Following initial investigation, both LPCS and RHR A were declared inoperable at 1847 hours. The associated water-leg pump was determined to be air bound and was vented. Both LPCS and RHR A were vented prior to returning to service. This report also satisfies Operational Requirements Manual section 7.6.2.1, which requires a special report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
4402003003 | Perry | 08/20/2003 | 08/03/2004 | ML04223025 | <strong>Unrecognized Diesel Generator Inoperability During Mode Changes</strong><br /><i>Abstract:&nbsp;</i>At 1206, August 21, 2003, with the reactor in MODE 1 at approximately 13 percent power, the monthly “Diesel Generator Start and Load” surveillance was performed and the starting output voltage was discovered to be set at approximately 4534volts. This value was greater than the Technical Specification acceptance criteria band of 3900 to 4400 volts AC and resulted in the Division 1 diesel generator [DG] being declared inoperable. The conditions initiating this event were traced to the reverse power trip of the Division 1 diesel generator and its output breaker at 1813, August 14, 2003, while restoring the Division 1, Class 1E, 4160 volt AC electrical bus to its offsite power supply. Subsequently, the plant changed MODES two times on 8/20/03with an inoperable diesel generator. The two MODE changes were made in violation of Technical Specifications, i.e. one at 0150 to MODE 2 at 0 percent power and the second at 2146 to MODE 1 at approximately 8 percent power. This condition is reportable per 10CFR50.73(a)(2)(i)(B). The root causes of this event are a deficient procedure that does not contain a Precaution or Limitation with the diesel generator high voltage limit; failure to reinforce expectations for the review of the operating parameters in the “System Operations” section of the system operating instructions; and failure of the post-event review process to detect the inoperability of the diesel generator prior to changing the plant Mode.
4402003004 | Perry | 09/05/2003 | 08/03/2004 | ML04223022 | <strong>Emergency Service Water Pump Upper Shaft Coupling Sleeve Failure</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2003, at 1717 hours with the plant operating in Mode 1 at 100 percent power, emergency service water (ESW) pump A was declared inoperable due to indications that the pump had failed. It was later determined that a pump shaft coupling had failed and that it would take longer than the Technical Specification (TS) Limiting Condition for Operation (LCO) completion time to complete repairs. A Notice of Enforcement Discretion (NOED) was requested of the NRC in order to obtain replacement parts, complete repairs and perform testing of the pump. The NOED for a 72 hour duration was verbally approved on September 4, 2003. At 0517 hours on September 5, 2003 the LCO for TS 3.7.1 and 3.8.1 expired and the plant entered the NOED. After completion of repairs, ESW A pump was declared operable at 1855 hours on September 5, 2003. The failure mechanism of the coupling sleeve is stress corrosion cracking (SCC) due to increased stresses from incorrect installation as a result of inadequate procedures and inadequate procedure use, a SCC susceptible material and a SCC susceptible operating environment. This event is considered to have a low safety significance. Since the Actions of the TSs were not satisfied when the NOED was entered, this is a reportable event in accordance with 10CFR50.73(a)(2)(i)(B), any operation or condition that was prohibited by the plant's TSs.
4402003005 | Perry | 10/31/2003 | 08/03/2004 | ML04223023 | <strong>Technical Specification Violation/Loss of Safety Function Due to Air Bound Water-leg Pump</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2003, it was determined that the division 1 feedwater leakage control system (DIV 1 FWLCS) piping and the low pressure core spray (LPCS) to residual heat removal (RHR) A crossover piping contained air. This condition resulted in air binding of the LPCS/RHR A water-leg pump on loss of power. This condition was previously reported in LER 2003-002. On October 31, 2003, it was determined that sufficient air had accumulated in the FWLCS line such that it would have prevented DIV 1 FWLCS and the RHR A suppression pool cooling mode from performing their function. This condition was determined to be the result of a procedural inadequacy to periodically vent the affected piping and an inadequate piping design that allowed air bubbles to migrate into the DIV 1 FWLCS. The condition is believed to have existed since initial plant operation. The air in the piping was estimated to take about 31 days following a refuel outage to reach the amount required to impact operability. Since the DIV 1 FWLCS and RHR A suppression pool cooling mode were inoperable longer than the required action completion time, this condition is reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications. Also since the redundant division 2 equipment had been inoperable for maintenance on several occasions during this time, this condition is also reportable per 10CFR50.73(a)(2)(v)(B) and (C). Procedures to periodically vent the affected piping have been established. Design modifications have been initiated to reduce the accumulation of air in the DIV 1 FWLCS.
4402003006 | Perry | 12/21/2003 | 02/19/2004 | ML04057051 | <strong>Loss of Safety Function and Limiting Condition for Operation 3.0.3 Entry due to Support System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2003, at 1945 hours with the plant operating at 100% power, an emergency closed cooling (ECC) system power loss annunciator was received. Two main line fuses were found to have operated (blown) for the division 1 ECC temperature control valve (TCV). The loss of electrical power caused the TCV to fail in the full cooling position resulting in the inoperability of the division 1 control complex chilled water (CCCW) system chiller. The division 2 CCCW system chiller was already in secured status and inoperable for maintenance. With both division 1 and 2 CCCW system chillers inoperable the heating ventilation and air conditioning (HVAC) systems supported by the chillers were determined to be inoperable. Since the HVAC systems were inoperable, the systems cooled by them, including ac and dc distribution and emergency core cooling systems were determined to be inoperable. The operation of the TCV fuses was due to shorted windings in the electro-hydraulic actuator motor (hydra-motor).The cause of the event was the failure to identify and implement effective corrective actions to improve reliability of hydra-motor operated equipment. Apparent and root cause evaluations of previous events did not identify organizational, process and management causes that, if resolved, could have prevented failure of additional hydra-motors. Corrective actions include replacement of the fuses and TCV motor. The corrective action program has been revised to improve tracking of corrective actions. Additionally, training of personnel will be conducted to resolve the skill deficit identified. This event was determined to be of low safety significance.
4432003001 | Seabrook | 06/10/2003 | 11/13/2003 | ML03329055 | <strong>Non-Compliance with Requirements of Technical Specification 3.8.1.1 Action b</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2003, due to a potential for a common mode failure found during preventive maintenance activities for the "A" Emergency Diesel Generator (EDG-1A), EDG-1B was started and run unloaded to satisfy the requirements of Technical Specification (TS) 3.8.1.1 action b. A subsequent review conducted on June 18, 2003, determined that unloaded testing of EDG-1B did not adequately address the requirements of TS 3.8.1.1. EDG-1B was subsequently retested satisfactorily under loaded conditions. Failure to complete the loaded run within the required action statement time constitutes noncompliance with the requirements of the action statement and is reportable as a condition prohibited by TS pursuant to 10 CFR 50.73(a)(2)(i)(B). LER 02-002-00 identified a condition where plant operators failed to start the operable EDG unit within 24 hours after discovery as required by TS 3.8.1.1 action b. The cause of this event was the failure of Licensee personnel to understand the entire affect of a change to the Technical Specifications due to an inadequate license amendment review process and an inadequate response to TS 3.8.1 .1 questions . Corrective actions include revising the TS change review process, and providing additional training for the Operations Department and personnel involved in the event. There were no adverse safety consequences as a result of this event.
4432003002 | Seabrook | 10/31/2003 | 12/23/2003 | ML03364063 | <strong>Reactor Trip Following the Loss of A Main Feed Pump</strong><br /><i>Abstract:&nbsp;</i>At approximately 1948 hours on October 31, 2003, with the plant operating in Mode 1 at 100% power, Seabrook Station experienced an automatic reactor trip following a transfer of the "A" Main Feed Pump (MFP) from the "Manual" to "Automatic" mode of operation. At the time of the reactor trip, plant personnel were troubleshooting the Emergency DC Lube Oil Pump (DC Pump) for the "A" MFP. In order to assist in the performance of troubleshooting activities, the "A" MFP slave controller was placed in the manual mode of operation. When the slave controller was returned to the automatic mode of operation, the "A" MFP control valves closed and the pump coasted down. Due to the reduced feedwater flow, steam generator levels decreased over an approximately forty-eight second period until an automatic reactor trip occurred when the lo-lo level setpoint (25%) was actuated. The cause of the reactor trip was a loss of the "A" MFP when its controller was placed in automatic mode of operation from the manual mode of operation. The loss of the "A" MFP was due to a degraded circuit board/component in the "A" MFP MDT-20 Governor Speed Controller. There were no adverse safety consequences as a result of this event. Plant systems responded normally as a result of the reactor trip. Corrective action was to replace the failed circuit board.
4452003001 | Comanche Peak 1 | 10/05/2002 | 03/07/2003 | ML03072043 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 1 was in Mode 1, Power Operation, operating at 100 percent power. At 1130 hours, it was determined that a reportable violation of Technical Specifications had occurred on October 5, 2002, when Train B of the Residual Heat Removal (RHR) system was unintentionally made inoperable during a condition when both RHR Trains were required to be operable during the Unit 1 ninth refueling outage. TXU Generation Company LP (TXU Energy) believes that the cause of the event was that the Outage Work Schedule Report did not contain the necessary predecessor logic tie to ensure that a Low Temperature Overpressurization (LTOP) channel calibration test was performed in a timeframe that would ensure the operability of both RHR Trains in compliance with the Technical Specification requirements. Corrective actions include changes to the Outage Work Schedule Report, procedure changes, and issuance of a lessons learned describing the event. All times in this report are approximate and Central Standard Time unless noted otherwise.
4452003002 | Comanche Peak 1 | 03/16/2003 | 05/09/2003 | ML03140020 | <strong>Actuation of Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 1 was in Mode 1, Power Operation, operating at 100 percent power. At 2149 hours, both Main Feedwater pumps tripped on low suction pressure due to an unexpected trip of Condensate pump 1-01. Operators manually tripped the Unit 1 reactor, and all control rods fully inserted. All Auxiliary Feedwater pumps automatically started as expected. TXU Generation Company LP (TXU Energy) believes that the event was caused by a manufacturing defect in the Condensate pump 1-01 motor. Corrective actions include repair of the Condensate pump 1-01 motor and evaluation of the Predictive Analysis Program for large electric motors. All times in this report are approximate and Central Daylight Standard Time unless noted otherwise.
4452003003 | Comanche Peak 1, Comanche Peak 2 | 05/15/2003 | 07/14/2003 | ML03204004 | <strong>Reactor Trip on Units 1 and 2 Due to Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2003 at 0252 with Units 1 and 2 in Mode 1 (Power Operation) with Unit 1 at 100 percent power and Unit 2 at 99.8 percent power, a disturbance on the Comanche Peak-Parker 345kV transmission line approximately four miles from the CPSES switchyard resulted in a loss of the 345kV switchyard and subsequent reactor trips on both units. Both units were stabilized in Mode 3 (Hot Standby) on natural circulation in accordance with plant emergency procedures as a result of the loss of non-safety related ac power. The protective relaying system associated with the CPSES Parker Line breaker failed to trip the breaker to isolate the switchyard from the fault and to initiate local breaker failure backup relaying. Because the switchyard breaker failed to isolate the faulted 345kV transmission line, the 345kV switchyard was deenergized and the Reactor Coolant Pumps in both units (4 per unit) tripped due to the loss of non-safety related ac power. CPSES Units 1 and 2 experienced turbine trips and subsequent reactor trips. Both units at CPSES experienced an automatic start of the Auxiliary Feedwater System. Unit 1 Class 1E electrical buses experienced a slow transfer to their alternate source that was fed from the 138kV switchyard. The emergency diesel generators remained available but did not start or load because offsite power was provided to the 1E electrical buses as designed. Systems functioned as designed and the units were stabilized and maintained in MODE 3 on natural circulation. All times in this report are approximate and Central Daylight Time unless noted otherwise.
4452003004 | Comanche Peak 1, Comanche Peak 2 | 08/20/2003 | 10/16/2003 | ML03300010 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2003, Comanche Peak Steam Electric Station (CPSES) Units 1 and 2 were both in Mode 1 operating at approximately 100 percent power. At 0434, combined maintenance activities on Unit 1 and Unit 2 Structures, Systems and Components resulted in a Technical Specification (TS) 3.0.3 condition on Units 1 and 2 when both trains of the Control Room Air Conditioning System (CRACS) became inoperable as outlined by the TS. The inoperable conditions and TS 3.0.3 entry criteria were not initially recognized. As a result, the shutdown actions of Limiting Condition for Operation (LCO) 3.0.3 were not met within the specified time limits. TXU Generation Company LP (TXU Energy) believes that the causes of this event were Operators failure to directly reference the Safety Function Determination Program (SFDP) Support System Reference Guide when completing the operability review for clearances being implemented during the shift, over-reliance by the Operators on the Probabilistic Risk Assessment (PRA) reviews to detect potential TS 3.0.3 conditions, and over-reliance by the Operators on the Operations Work Control Group to detect potential TS 3.0.3 conditions during the preparation of the work schedule. Corrective actions included the restoration of the inoperable equipment allowing exit from LCO 3.0.3, issuing a Shift Order regarding performance of SFDP evaluations, and issuing Lessons Learned on this event to all system/outage schedulers and all Reactor Operators and Senior Reactor Operators. All times in this report are approximate and Central Daylight Time unless noted otherwise.
4462003001 | Comanche Peak 2 | 07/09/2003 | 09/05/2003 | ML03258045 | <strong>Actuation of Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On July 9, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, operating at 100% power. At 0109 hours, the 2-04 Reactor Coolant Pump (RCP) motor breaker opened which resulted in loss of the 2-04 RCP and an automatic reactor trip. All control rods fully inserted and all Auxiliary Feedwater pumps automatically started as expected. TXU Generation Company LP's (TXU Energy) evaluation of this event has determined that the 2-04 RCP motor breaker opened due to a "B" phase stator to ground short in the 2-04 RCP motor. Corrective actions include repair of the 2-04 RCP motor stator and, as previously discussed in Licensee Event Report 03-002-00 for CPSES Unit 1, an evaluation of the Predictive Analysis Program specifically for large electric motors will be performed to assess the current program scope, monitoring practices, and overall effectiveness. All times in this report are approximate and Central Daylight Tune unless noted otherwise.
4462003002 | Comanche Peak 2 | 07/25/2003 | 09/23/2003 | ML03279016 | <strong>Actuation of Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operations, operating at 12 % power. At 1318 hours operators were valving in a string of low pressure feedwater heaters which had been bypassed since July 9, 2003. A low suction pressure trip of the operating Main Feedwater Pump occurred resulting in an auto start of both Motor Driven Auxiliary Feedwater Pumps. TXU Generating Company LP's (TXU Energy) evaluation has determined that this event was caused by the existence of a void in an isolated low pressure feedwater heater string, miscommunication, and not using applicable procedures. Corrective actions include revising applicable procedures, a post job critique, issuing a Lessons Learned, and re-enforcing Operations management expectations for procedure use. All times in this report are approximate and Central Daylight Time (CDT) unless noted otherwise.
4462003003 | Comanche Peak 2 | 11/02/2003 | 12/23/2003 | ML03364050 | <strong>Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2003, Comanche Peak Steam Electric Station Unit 2 was in Mode 1, Power Operation, operating at approximately 77 percent power. At 0934 hours, Operations personnel discovered that two valves in the Containment Spray system were mispositioned. With these valves mispositioned, the Spray Additive system was determined to have been inoperable for a period of time longer than allowed by the Technical Specifications. TXU Generation Company LP (TXU Energy) believes that the cause of this event was the lack of specific training and procedural guidance for verifying the status of valves with a remote "knocker" operating mechanism. This type of valve has a Roto-Hammer impactor and bridle fitted to the valve stem. Corrective actions include verification of the position of other similar valves, Operations procedure revisions, and training of Operations personnel on the specifics of this event. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462003004 | Comanche Peak 2 | 11/05/2003 | 12/22/2003 | ML03364049 | <strong>Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2003, Comanche Peak Steam Electric Station Unit 2 was in Mode 1, Power Operation, operating at approximately 99 percent power. At 0950 hours, Operations personnel discovered that one of the four Engineered Safety Feature Actuation System (ESFAS) intermediate range containment pressure channels had been inoperable for a period of time longer than allowed by the Technical Specifications. TXU Generation Company LP (TXU Energy) believes that this event was caused by a random electronic failure in a power supply circuit card for an ESFAS intermediate range containment pressure channel. Corrective actions include replacement of the failed power supply circuit card and installation of a deviation alarm. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462003005 | Comanche Peak 2 | 12/22/2003 | 02/20/2004 | ML04061076 | <strong>Actuation of Reactor Protection Systems</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2003, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at 99.5 percent power. At 0827 hours, during collection of voltage and current data readings from the operating 2-01 Main Generator rotor, a stroboscope lamp reflector assembly was inadvertently contacted, became dislodged, and migrated into the rectifier wheel. This caused a phase to phase fault in the Main Generator exciter which resulted in a Main Turbine trip followed by an automatic reactor trip. TXU Generation Company LP (TXU Energy) believes that the cause of the event was improper reassembly of the stroboscope. Corrective actions include enhancing the work instructions for disassembly and reassembly of stroboscopes and issuing a Lessons Learned on this event to personnel that are regularly involved in Main Generator work. All times in this report are approximate and Central Standard Time unless noted otherwise.
4542003001 | Byron 1, Byron 2 | 01/27/2003 | 05/23/2003 | ML03155011 | <strong>Control Room Ventilation System Alignment Results in Inoperable Radiation Monitors Without Taking Required Actions Per The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2003 it was determined that the Unit Common Control Room Ventilation System (VC) Filtration System Actuation Instrumentation (FSAI) radiation monitors were not operable when VC was aligned to the Turbine Building makeup air intake. The radiation monitors are located in the outside air makeup intake. On a high radiation signal, VC is realigned to the Emergency Makeup Mode. Some VC operating and surveillance procedures allow operation of the VC System with alignment to the Turbine Building makeup air intake resulting in an inoperable FSAI system since the system is incapable of performing its design function in this configuration (i.e., there would be no air flow past the radiation monitors.) The applicable Technical Specification Limiting Condition for Operation has historically not been entered for this condition. This issue has existed since initial licensing of the facility. In addition, during the investigation, a design flaw was discovered in that the automatic shutdown of a ventilation system that may contribute to unfiltered air in-leakage to the control room was improperly removed from the engineered safety feature safety injection action signal. The root causes for the event were inadequate evaluation of the original operating and surveillance procedures and subsequent revisions and inadequate evaluation of a design change. The condition is considered to have minimal safety consequences. An engineering evaluation has concluded there was no loss of safety function. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4542003002 | Byron 1 | 02/16/2003 | 08/22/2003 | ML03247152 | <strong>Two Main Steam Safety Valves Lift Setpoints Found Out of Tolerance During Testing Due to Unknown Causes</strong><br /><i>Abstract:&nbsp;</i>During mid-cycle testing of six Unit 1 Main Steam Safety Valves (MSSV's) on February 16, 2003, two valves failed to meet the Technical Specification 3.7.1 as found plus or minus 3% tolerance of nominal setpoint requirement. Operations entered the applicable Technical Specification Action Condition until each valve was readjusted and tested satisfactorily. The initial lift setpoint for the 1MS015B valve was measured at 1166.7 psig; which is approximately 3.2% below the 1205 psig nominal setpoint. The initial lift setpoint for the 1MS013A valve was measured at 1190 psig; which is approximately 3.6% below the 1235 psig nominal setpoint. The cause of the two valves failing their setpoint test is currently unknown. All valves were reset to within plus or minus 1% of the nominal setpoint as required by Technical Specifications. An engineering evaluation concluded that the as found condition of these two valves was still bounded by the design basis analysis. This event is reportable under l0CFR 50.73(a)(2)(i)(B).
4542003003 | Byron 1, Byron 2 | 08/28/2003 | 03/31/2004 | ML04097040 | <strong>Licensed Maximum Power Level Exceeded Due to Inaccuracies in Feedwater Ultrasonic Flow Measurements</strong><br /><i>Abstract:&nbsp;</i>Byron Station Unit 1 and Unit 2 exceeded their licensed maximum power level by 2.62% and 1.88%, respectively. In May of 2000 an Ultrasonic Flow Measurement System (UFMS) was installed on the main feedwater lines to the steam generators to more accurately measure feedwater flow. This corrected feedwater flow is then used in the reactor power calorimetric calculation. Feedwater flow pressure pulses occurred at frequencies that affected the UFMS signal and resulted in a bias in the determinations of the flow correction factors. This resulted in a non-conservative calorimetric calculation. When reactor power was adjusted to match the calorimetric power, an overpower condition was created. When this condition was discovered the UFMS was removed from service. Implementation of the UFMS has been suspended. Analyses performed indicated there was no adverse safety impact for the overpower condition on each unit. In accordance with Byron Station Unit 1 License Condition 2.Fand Byron Station Unit 2 License condition 2.G, a notification was made to the NRC at 1355 CST on August 28, 2003, due to the violation of license condition 2.C(1) of each license, "Maximum Power Level."
4542003004 | Byron 1 | 09/16/2003 | 11/14/2003 | ML03328046 | <strong>Two Main Steam Safety Valves Lift Setpoints Found Out of Tolerance During Testing Due to Unknown Causes</strong><br /><i>Abstract:&nbsp;</i>During setpoint testing of the Unit 1 Main Steam Safety Valves (MSSVs) on September 16, 2003, two of the 20 MSSVs (i.e.,1MS016A and 1MS015D) failed to meet Technical Specification (TS) required lift setpoint tolerances. The 1MS016A valve's as found lift setting was 3.9% low and the 1MS015D valve's as found lift setting was 3.5% low. Operations personnel entered the applicable TS Action Condition until each valve was reset and tested satisfactorily. Because the MSSVs were tested sequentially, only one valve was known to be inoperable at any one time. The cause of the 1MS016A and 1MS015D valves lifting low is unknown. An engineering analysis concluded that this condition was still bounded by the design basis analyses. This condition of multiple MSSVs being outside of their required lift setting tolerance band is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(b), "Any Operation or condition prohibited by the plants Technical Specifications.”
4562003001 | Braidwood 1, Braidwood 2 | 01/27/2003 | 05/23/2003 | ML03150047 | <strong>Control Room Ventilation System Alignment Results in Inoperable Radiation Monitors Without Taking Required Actions per the Technical Specifications due to Inadequate Evaluation of the original procedures and some subsequent revisions and inadequate evaluation of a design change.</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2003 it was determined that the Unit Common Control Room Ventilation System (VC) Filtration System Actuation Instrumentation (FSAI) radiation monitors were not operable when VC was aligned to the Turbine Building makeup air intake. The radiation monitors are located in the outside air makeup intake. On a high radiation signal, VC is realigned to the Emergency Makeup Mode. Some VC operating and surveillance procedures allow operation of the VC System with alignment to the Turbine Building makeup air intake resulting in an inoperable FSAI system since the system is incapable of performing its design function in this configuration due to there being no outside air flow past the radiation monitors. The applicable Technical Specification Limiting Condition for Operation has historically not been entered for this condition. This issue has existed since initial licensing of the facility. In addition, during the investigation a design flaw was discovered in that the automatic shutdown of ventilation systems that may contribute to unfiltered air in-leakage to the control room was improperly removed from the Engineered Safety Feature Safety Injection (ESFSI) actuation signal. The root causes for the event were inadequate evaluation of the original operating and surveillance procedures and subsequent revisions and inadequate evaluation of a design change. The condition is considered to have minimal safety consequences. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4562003002 | Braidwood 1 | 02/02/2003 | 04/03/2003 | ML03099045 | <strong>Residual Heat Removal Pump Technical Specification Completion Time Exceeded Requiring Notice of Enforcement Discretion Due to Poor Planning and Execution of Planned Maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2003 at 2200 hours, Braidwood Station Unit 1 entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.2 Condition A for planned maintenance on the Unit 1B Residual Heat Removal (RHR) pump. The planned work window for the 1B RHR pump included numerous routine surveillance and preventive maintenance activities. However, the primary activity in the work window was to inspect the 1B RHR pump internals and replace the stuffing box extension as follow-up actions from a station operability determination and lessons learned from a previous 2B RHR pump repair. It was determined, based on unexpected work delays, that the pump maintenance and testing would not support restoration to operability of the 1B RHR pump within the TS Completion Time and a Notice of Enforcement Discretion (NOED) was requested and subsequently granted by the NRC on February 2, 2003 at 1250 to extend the Completion Time by 20 hours. The pump was restored to an operable status and the LCO exited on February 3 at 0337. The root cause for exceeding the TS Completion Time was the lack of management oversight and the failure to recognize challenges related to planning, safety, dose and troubleshooting during work execution. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4562003003 | Braidwood 1, Braidwood 2 | 09/03/2003 | 10/03/2003 | ML03295054 | <strong>Licensed Maximum Power Level Exceeded Due to an Error in a Westinghouse Supplied Calorimetric Calculation Constant</strong><br /><i>Abstract:&nbsp;</i>Braidwood Station received Nuclear Safety Advisory Letter (NSAL) 03-06, "High Net Heat Input," from Westinghouse informing the Station that an error had been found in calculations that may result in the use of a non-conservatively high Net Heat input value in the calorimetric calculations. The Net Heat input is the difference between the reactor core power and the Nuclear Steam Supply System (NSSS) power. It consists of energy provided by the reactor coolant pump to the reactor coolant, heat supplied by the pressurizer heaters, and other minor heat removal and additions such as the cooling provided by the reactor coolant pump seal injection. The result of using a non-conservatively high Net Heat input value in the calorimetric calculations was that both Unit 1 and Unit 2 operated at higher than licensed core power levels on several occasions. The Westinghouse evaluation determined that the increase in Net Heat. input could be as much as 0.4 MWt. This condition applies to both Unit 1 and Unit 2. In accordance with Braidwood station Unit 2 License Condition 2.G a notification was made to the NRC at 1557 CST on September 3, 2003, due to violation of license condition 2.C(l), "Maximum Power Level."
4572003001 | Braidwood 2 | 07/21/2003 | 09/18/2003 | ML03273143 | <strong>Inadequate Enforcement of the Maintenance Fundamentals Results in the Inoperability of the 2A Train of the Chemical and Volume Control System for Twelve Days</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2003 the limit switch lead for Motor Operated Valve (MOV) 2CV8111, (i.e., Chemical and Volume Control System charging pump mini-flow isolation valve) was discovered lifted and taped. The lead had not been relanded following MOV diagnostic testing at the completion of the test on July 9, 2003. Also, the post maintenance testing (PMT) for this work did not detect the problem before the valve was returned to service. This resulted in the 2A train Centrifugal Charging pump (CV) being declared inoperable for 12 days since the mini-flow isolation valve was incapable of auto closure, however, valve 2CV8111 was still available for manual repositioning. The Root Cause for the event was the failure of Maintenance management to adequately enforce the required Maintenance Fundamentals (i.e., basic expected good work practices). They did not ensure that the personnel involved followed the standards, policies and administrative controls required to successfully perform the required work on the 2CV8111 valve. The corrective action is that Maintenance management will ensure that each worker knows the expectations for each job prior to starting the work, including performance of a pre-job brief, reviewing applicable operating experience (OPEX), reviewing critical steps and potential configuration control issues. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4572003003 | Braidwood 2 | 11/04/2003 | 01/05/2004 | ML04014037 | <strong>Inadvertent Auxiliary Feed Water Engineered Safety Feature Actuation Due to Placing a Clearance Order Ahead of the Outage Schedule</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2003 at 2132 the Unit 2 auxiliary feedwater (AF) system received an inadvertent engineered safety feature (ESF) actuation signal while in cold shutdown due to the concurrent de-energization of two 6.9 KV buses, i.e., undervoltage on 2/4 reactor coolant pump (RCP) buses. Following the shutdown of the last remaining RCP, the 6.9 KV buses were de-energized earlier than planned in the outage schedule. While the 6.9 KV buses were being de-energized, anticipated transient without scram (ATWS) mitigation system (AMS) testing was in progress. This test requires that the A and B train AF pump auxiliary lube oil pumps remain energized. Normally the 6.9 KV buses are not de-energized until after AMS testing is complete and the AF pump auxilary lube oil pumps de-energized. However, with the AF pump auxiliary lube oil pumps still energized, the de-energization of the 6.9 KV buses resulted in an AF actuation signal. This signal resulted in the unplanned, automatic start of both A and B train AF pump auxiliary lube oil pumps and the unplanned, automatic opening of both A and B train AF pump discharge valves. The root causes for the event were : 1) overconfidence by the outage electrical team coordinator which led to his decision to hang the 6.9 KV bus clearance orders (C/O) ahead of schedule (note that there was no process in place to control advancing the schedule activities) and 2) a procedure did not exist for deenergizing the 6.9 KV buses. The corrective actions to prevent recurrence are to develop a procedure to remove the 6.9 KV buses from service with appropriate precautions and limitations to prevent this event from occurring again, and to develop a process for changing outage schedule activities with proper oversight.
4572003004 | Braidwood 2 | 12/03/2003 | 02/02/2004 | ML04042059 | <strong>Unit 2 Reactor Trip and Auxiliary Feedwater Emergency Safeguards Actuation Due to Cascading Feedwater Pump Trips Caused by a Lack of Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>At 0336 on 12/03/03, the Unit 2 reactor tripped on 2D Steam Generator low-low water level due to the cascading trip of the 2C and 2B turbine driven feedwater pumps during 2C feedwater pump testing. While testing the 2C feedwater pump stop valves, the high pressure stop valve did not reopen as expected during the test due to a piece of age degraded tie wrap lodged in the relay contacts. The 2C feedwater pump subsequently tripped. The suspected reason for the trip of the 2C feedwater pump is believed to be a simultaneous closed signal from the low pressure and high pressure stop valves. During the start of the 2A motor driven feedwater pump, the 2B feedwater pump tripped on overspeed due to high flow demand when the 2C feedwater pump tripped and failure of the 2B feedwater pump speed feedback control circuit to limit the pump speed below the mechanical overspeed trip setpoint. The 2A motor driven feedwater pump could not provide sufficient flow to maintain the Unit 2 Steam Generator water levels above the automatic reactor trip setpoint. This event is the result of equipment failures and not due to human performance error. The significance of this event is an automatic Reactor Protection System actuation when the reactor tripped on low-low Steam Generator water level and subsequent Engineered Safety Feature actuation when the auxiliary feedwater pumps started. This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A).
4572003005 | Braidwood 2 | 12/10/2003 | 02/09/2004 | ML04049066 | <strong>Setpoint Drift Causes Three of Three Pressurizer Safety Valve Lift Tests to Exceed Technical Specification Tolerance</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2003, Braidwood Station discovered that three of three pressurizer safety valves (PSVs) removed during the fall 2003 refueling outage and subsequently tested at an offsite facility, did not meet the Technical Specification (TS) acceptance criteria. TS 3.4.10, "Pressurizer Safety Valves, "requires three PSVs to be operable with lift settings greater than or equal to 2460 psig and less than or equal to 2510 psig. The surveillance requirement requires each valve to be operable in accordance with the Inservice Testing (IST) Program and that following testing the lift setting shall be within+/- 1 percent of the TS setpoint. Two valves had lift setpoints that were low and one valve had a setpoint that was high. There are no material condition issues with the PSVs that contributed to the test failures. The PSVs are performing within their design capabilities. The test failures are mainly due to the close tolerance required by the current plant safety analyses reflected in TS requirements and the inability of the valves to perform within that tolerance. The corrective action to revise the safety analyses to support a relaxation of the one percent TS requirement for the PSV lift setpoint tolerance is being pursued. An evaluation on the effects of the PSVs lifting outside of the TS tolerance concluded that all acceptance criteria in the Updated Final Safety Analysis Report, Chapter 15, "Accident Analyses," were still met. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4582003001 | River Bend | 02/22/2003 | 06/26/2003 | ML03182053 | <strong>Unplanned Reactor Scram Due to Fluid Leak in Main Turbine Electrohydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>At approximately 1:23 a.m. CST on February 22, 2003, with the plant operating at 90 percent power in end-of-cycle coastdown, an unplanned manual reactor scram was initiated. During the scram recovery, the reactor core isolation cooling (RCIC) system was manually actuated to assist in reactor water level control. This event is being reported In accordance with 10CFR50.73(A)(2)(iv)(a) as a valid actuation of the reactor protection system and RCIC. The scram was necessitated by a fluid leak in the main turbine electrohydraulic control system that significantly depleted the system. Subsequent investigation determined that the leak occurred when a section of hydraulic tubing near the main turbine control valves developed a through-wall crack. An analysis of the failed tubing indicated that the likely cause was metal fatigue induced by system vibration. Additionally, pipe stress analysis verified that the tubing was overstressed due to deficiencies in design and configuration. Plant safety systems responded normally to the manual scram and the RCIC initiation. This event was of minimal significance to the health and safety of the public.
4582003002 | River Bend | 03/07/2003 | 06/05/2003 | ML03161099 | <strong>Secondary Containment Door Failure Due to Malfunction of Door Assist Device</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2003, at approximately 2:31 p.m. CST, the door assist device (DAD) on a secondary containment door in the auxiliary building failed, blocking the door open for a period of 78 minutes. At the time, the reactor was operating at approximately 87 percent power in end-of-cycle coastdown. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(c) as a condition that could have prevented the fulfillment of the safety function of secondary containment. The failure was caused when an inappropriately installed set screw on an internal spur gear caused the gear to bind on its shaft when it should have been free to rotate. There were no actual consequences to the health and safety of the public. Engineering evaluations have shown that, had a design basis accident occurred while the condition existed, the main control room, exclusion area boundary, and low population zone doses would have remained within the limits of 10CFR50.67.
4582003003 | River Bend | 03/10/2003 | 06/25/2003 | ML03182055 | <strong>Primary Containment Airlock Breach Due to Door Interlock Malfunction</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2003, at approximately 11:37 a.m. CST, the airlock door interlocks on the 171 foot elevation of the primary containment did not properly function, such that both the inner and outer doors were unsealed for a period of approximately 36 minutes. At the time, the reactor was operating at 87 percent power in end-of-cycle coastdown. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(c) as a condition that could have prevented the primary containment from performing its safety function. The most likely cause was a misadjustment of the mechanical interlock cables and/or excessive machining of the interlock cam ratchet. An engineering evaluation determined that the deflation of both airlock door seals had an insignificant impact on core damage frequency and large early release frequency. Thus, this event was of minimal significance with respect to the health and safety of the public.
4582003004 | River Bend | 03/28/2003 | 05/22/2003 | ML03148051 | <strong>Automatic Initiation of Standby Service Water System Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2003, at approximately 3:48 p.m., with the plant in cold shutdown for a refueling outage, the Division 2 standby service water (SSW) system automatically initiated. The cause of this event was a low pressure condition in the reactor plant closed cooling water system induced by an error during system realignment using the system operating procedure. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that caused the automatic initiation of an emergency service water system. The SSW system responded as designed to the low pressure signal. Cooling water flow was restored to the spent fuel pool cooling heat exchangers shortly after initiation of the event. Thus, this event was of minimal significance.
4582003005 | River Bend | 05/10/2003 | 07/30/2003 | ML03217054 | <strong>Operation Greater than Maximum Licensed Power Due to Erroneous Feedwater Flow Measurement</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2003, with the plant operating at 98 percent power, information was received from the manufacturer of the station's reactor feedwater flow measurement device indicating the station had been operated in excess of maximum licensed reactor thermal power in the past. This condition is being reported in accordance with the Facility Operating License (NPF-47) as a violation of License Condition 2.C(1), "Maximum Licensed Power." The investigation determined that changes to plant parameters outside the design assumptions of the instrument resulted in erroneous feed flow indication. This component is no longer installed in the plant. An evaluation has determined that adequate design margin existed to accommodate the overpower condition.
4582003006 | River Bend | 05/07/2003 | 07/07/2003 | ML03195008 | <strong>Automatic Initiation of Standby Service Water System Due to Inadequate Control of System Operations</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2003, at approximately 9:05 a.m., the plant was operating at 100 percent power when an unplanned initiation of the Division 2 standby service water (SSW) system occurred. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a condition that caused the automatic actuation of an emergency service water system. An unexpected low pressure condition that occurred during a scheduled shift of the normal service water (SWP) pumps caused the automatic start of the Division 2 SSW system. The system was returned to its standby configuration at approximately 11:41 a.m. This event was caused by inadequate margin in the operating parameters of the SWP system to the initiation setpoint of the SSW system. A review of the SWP system will be performed to minimize the vulnerability to recurrence of a similar event. The standby service water system responded as designed to the low pressure initiation signal. This event was of minimal significance to the health and safety of the public.
4582003007 | River Bend | 06/17/2003 | 08/15/2003 | ML03231037 | <strong>High Pressure Core Spray Pump Inadvertently Disabled Due to Personnel Error During Installation of Clearance Order</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2003, at approximately 4:20 p.m., with the plant operating at 100 percent power, the feeder breaker for the high pressure core spray (HPCS) pump was racked out inadvertently during placement of equipment clearance tags. This condition is being reported in accordance with 10CFR50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of the safety function of the HPCS system. Actions were immediately taken to restore the pump to its standby configuration. The HPCS pump was inoperable for approximately 16 minutes. All other emergency core cooling systems were operable during this event. Thus, this event was of minimal significance to the health and safety of the public.
4582003008 | River Bend | 09/22/2003 | 11/20/2003 | ML03330008 | <strong>Automatic Reactor Scram During Main Turbine Control Valve Testing Due to Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 10:43 p.m. CDT on September 22, 2003, with the plant operating at approximately 78 percent power, an automatic reactor scram occurred during scheduled testing of the main turbine control valves. The scram signal originated from reactor steam pressure instruments following a malfunction of the main turbine control system which caused the control valves to move toward the closed position. A containment isolation signal initiated due to the expected reactor low water level alarm, which caused the isolation of the suppression pool cooling system, as designed. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a valid actuation of the reactor protection system and the containment isolation logic circuitry. Modifications are being considered to prevent recurrence of this condition. Turbine control valve testing has been suspended pending further corrective actions. This event was of very low safety significance, as the response of the plant to the scram signal was bounded by the safety analysis.
4612003001 | Clinton 1 | 02/19/2003 | 04/16/2003 | ML03115041 | <strong>Human Performance Errors Result in Inoperable Containment Isolation Valve and Failure to Isolate Penetration Within 4 Hours</strong><br /><i>Abstract:&nbsp;</i>Residual Heat Removal (RHR) System [BO] Train B Suppression Pool Suction Valve, a Primary Containment Isolation Valve (PCIV), was made inoperable by de-energizing it in the open position in accordance with a clearance. After the valve was made inoperable, the affected Containment penetration was not isolated within 4 hours as required by Technical Specifications (TS). This valve does not have an automatic isolation function; it has remote operation capability from the Main Control Room in the event operator action is required to close the valve during design basis accident conditions. The first cause of this event was inadequate self-checking by the clearance writer during development of the clearance. The clearance writer omitted from the clearance a tag to address closure of the PCIV. The second cause was insufficient rigor and attention to detail by personnel involved in implementing the clearance. Corrective actions for this event include implementing a method of completing clearance development sheets, and implementing a dynamic learning activity to challenge licensed operator proficiency on the Operations Fundamentals including rigor and attention to detail. The open PCIV did not affect the reactor containment function.
4612003002 | Clinton 1 | 04/11/2003 | 06/09/2003 | ML03170036 | <strong>Manual Reactor Scram Due to Main Turbine Vibrations Caused by Deficient Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2003, with the plant in Mode 1 (Power Operation) while lowering reactor power in preparation for maintenance outage C1M13, the reactor was manually scrammed from 33 percent power in response to vibration levels on the Main Turbine approaching the automatic trip setpoint. The Low Pressure Turbine vibrations were caused by development of a minor rub between the rotating and stationary components as a result of the temperature change induced on the Low Pressure Turbine when the Moisture Separator Reheaters (MSRs) were removed from service. The root cause of the event-was that operating procedures were deficient in providing sufficient operating restrictions of the new monoblock turbine rotor due to inadequate vendor guidance. Corrective actions to prevent recurrence include revisions to plant procedures and the turbine vendor manual to incorporate more restrictive heat up and cool down ramp rates. Additional corrective actions identified include providing expectations in the design modification process to require independent operating experience reviews during the design phase.
4612003003 | Clinton 1 | 12/02/2003 | 06/16/2004 | ML04176024 | <strong>Reactor Scram Due to Loss of Power to 480 Volt Unit Substation 1I</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2003, at approximately 1700 hours, the reactor was manually scrammed from 88 percent power in response to low feedwater pump suction pressure and reactor pressure vessel (RPV) water level trending downward toward the RPV Low Water Level - Level 3 automatic scram setpoint. Initiating the event was a loss of power to the 480 Volt Unit Substation 1I (1AP19E) causing the 'B' turbine driven reactor feed pump (TDRFP) minimum flow valve to fail open. This resulted in a low pump suction pressure and a trip of both TDRFPs. The motor-driven reactor feed pump (MDRFP) automatically started to control water level and pressure. The cause of the 480 Volt Unit Substation 1I to trip was a lack of overload circuit protection (i.e., fuse protection) for a branch circuit due to a design error. A second event occurred on December 2, 2003 at approximately 1937 hours when a RPV Low Water Level - Level 3 Reactor Protection System (RPS) actuation occurred during the transfer of reactor coolant makeup from the MDRFP to the condensate/condensate booster pumps. The RPS actuation'(scram) was caused by the RPV water level dropping at a faster rate than anticipated by the operating crew. The MDRFP was restarted and water level was quickly recovered. This event was caused by less than adequate operating crew response in shutting down the MDRFP to reduce reactor pressure. The deficient circuit will remain removed from service until an engineering change to modify the circuit for over load protection is installed. For the second event, operations crews will be trained on the event in simulator training to emphasize the crew's response to challenges, including reactor water level responses to pressure reduction without high pressure feed injection available.
4822003001 | Wolf Creek | 01/03/2003 | 02/28/2003 | ML03070053 | <strong>Manipulation of Component Outside of Procedural Guidance Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2003, at 11:01 a.m. Central Daylight Time (CDT), Wolf Creek Generating Station (WCGS) experienced an automatic actuation of the Reactor Protection System (RPS), including an automatic reactor trip, due to power range neutron flux high negative rate. The reactor trip occurred while restoring the number one rod drive motor generator (RDMG) set to service after routine breaker maintenance. A Reactor Operator (RO) in the plant was simulating how to manually charge the non-operating RDMG set output breaker to two non-licensed operators. The RO manipulated the manual charging handle for the RDMG set number one output breaker outside of procedural guidance and without control room direction. Concurrent with the actuation of the manual charging handle, the number one output breaker closed, then reopened, and the number two RDMG set output breaker opened. When the number two RDMG set output breaker opened, the control rods lost holding power and started to insert. All control rods fully inserted, and the RPS and the Engineered Safety Features (ESF) systems performed as expected. The cause of this event was personnel error. The safety significance of this event is low. All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
4822003002 | Wolf Creek | 03/25/2003 | 05/23/2003 | ML03149036 | <strong>Reactor Vessel level Indicating System Inoperable for Period Longer Than Allowed by Tech. Spec.</strong><br /><i>Abstract:&nbsp;</i>At 1000 on March 25, 2003, the Wolf Creek Generating Station (WCGS) Shift Manager was notified that both "A" and "B" wide range trains of Reactor Vessel Water Level Indicating System (RVLIS) were not functioning as designed. Both "A" and "B" wide range trains of RVLIS in the Main Control Room were off-scale high (>120%), consistent with the plant computer point indication of 122.8%. Based upon discussion with vendor representatives and industry peers, WCGS concluded that this reading was approximately 12% higher than should be expected. The Shift Manager declared both "A" and "B" trains of RVLIS inoperable and entered Condition C of Technical Specification 3.3.3, Post Accident Monitoring (PAM) Instrumentation. Although WCGS entered the applicable Technical Specification Required Action immediately following recognition of this condition, further evaluation determined that this condition existed for a time longer than permitted by Technical Specifications. As such, this issue represents a condition prohibited by Technical Specifications, and is reportable per 10CFR50.73 (a)(2)(i)(B). Because various other means are available to plant operators to determine reactor vessel level, there is minimal safety significance associated with this issue.
4822003003 | Wolf Creek | 08/18/2003 | 10/16/2003 | ML03294059 | <strong>Reactor Protection System Actuation and Reactor Trip Due to Feedwater Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2003, at 3:54 PM, Wolf Creek experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to lo/lo water level in "B" steam generator (SG). This actuation occurred following the closure of the "B" SG main feedwater isolation valve (FWIV). When the FWIV closed, "B" SG level decreased below the reactor trip setpoint, initiating a reactor trip. The unit received an expected feedwater isolation and expected auxiliary feedwater actuation (both motor and turbine driven) because of the lo/lo SG level. All control rods fully inserted, and the RPS and Engineered Safety Features (ESF) performed as expected. The cause of the FWIV closure was a spurious signal from the Engineered Safety Features Actuation System for the "B" SG. The specific component failure could not be determined so all of the electrical components that could have caused the fast closure of the "B" FWIV were replaced. The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in Wolf Creek Generating Station Updated Safety Analysis Report (USAR) section 15.2.7 "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
4822003004 | Wolf Creek | 11/17/2003 | 01/15/2004 | ML04021079 | <strong>Failure of Safety Injection Accumulator Vent Line</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2003, during Wolf Creek Generating Station (WCGS) refueling outage number 13, a non-licensed Nuclear Station Operator observed water leaking approximately 25 to 30 drops per minute from the ASME Code Class 2, ¾-inch line upstream of Safety Injection (EP) system valve EPV0109.This is the 3/4 -inch vent line on the combined SIIRHR outlet piping to EP Accumulator Tank D. The Reactor Coolant System (RCS) leakage constitutes degradation of a principal safety barrier and is considered reportable to the requirements of 10CFR50.73(a)(2Xii)(A), "Degraded or Unanalyzed Condition.” Conditions that represent welding or material defects in the primary coolant system which cannot be found acceptable under ASME Section XI standards are reportable to this criterion. The cracked vent line and associated socket weld were removed and repaired on November18, 2003. The completed weld repair was inspected, tested and found acceptable. Initial evaluation concluded that this was a fatigue crack initiating from a filing groove that induced a stress concentration that, after several years of cycling, propagated through the vent line. The safety significance of this event is low. The RCS leakage that resulted from the cracked vent line is within the capability of reactor makeup systems and a complete failure is bounded by the plant Loss of Coolant Accident (LOCA) analysis.
4832003001 | Callaway | 01/07/2003 | 03/10/2003 | ML03077058 | <strong>Improper Administrative Controls Result in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On 01/07/03, with the Plant in Mode 1 at 100 percent Reactor Power, valve EGHV0061 (Component Cooling Water from Reactor Coolant Pump Thermal Barrier Outer Containment Isolation Valve) failed to stroke fully closed, during Containment Isolation Valve Inservice Testing. EGHV0061 was declared inoperable at 2012 and Technical Specification (T/S) 3.6.3.A.1 was entered. At 2020, EGHV0133 (the bypass valve for EGHV0061) was opened and then EGHV0061 valve was fully closed with power removed from the valve in order to satisfy T/S 3.6.3 A.1 for the EGHV0061 penetration flow path. The T/S required position for valve EGHV0133 is closed with power removed, except when opened under administrative controls. Later it was determined that EGHV0133 and EGHV0062 (the inner containment isolation valve) were both powered from Bus NG02B. This discovery revealed that the administrative controls were inadequate. This was a condition prohibited by the Plant's T/S. This condition existed until 01/10/03 when EGHV0061 was returned to service. The root cause of the event was a failure to recognize the common power source for both valves. Corrective actions included revising the test procedure to establish the requirement for local operation of these valves when administrative, controls are required.
4832003002 | Callaway | 03/05/2003 | 05/05/2003 | ML03134043 | <strong>EGHV0061 Inoperable for a Time Period Greater Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0148, 3/5/03, EGHV0061 was declared inoperable due to failing to stroke full closed during containment integrity surveillance, S704626. Technical Specification (T/S) 3.6.3 was entered and EOSL 10582 was written to track T/S time limits. EGHV0061 is a parallel sliding gate valve. Investigation revealed the valve failed to stroke to the full close position due to a hydraulic lock developing between the two valve discs. This was a repeat of a problem on 1/8/03. Actions taken in January involved valve disassembly and removal of a viscous film discovered on all areas where a no flow or low flow condition existed. Post maintenance testing indicated that cleaning resolved the problem. This was supported by testing performed under S539676 on 2/5/03. Upon the second failure of EGHV0061, further investigations were conducted. Manufacturer Velan Valve Corporation recommended drilling a 0.25-inch hole in the upstream disc to relieve any pressure trapped between the discs. This modification was performed and testing demonstrated proper operation and stroke times. At 1418, 3/7/03, EGHV0061 was declared operable. This failure was caused by changing valve stroke length in RF 12. The actual inoperable time span was from the last valve stroke in RF12 at 2116, 11/17/02, until proper restoration was completed at 1418, 3/7/03 for a total time span of 109 days, 17 hours, 2 minutes.
4832003003 | Callaway | 03/13/2003 | 05/09/2003 | ML03140057 | <strong>Incorrect Steam Generator Tube Rupture/Overfill Accident Analysis Contained in FSAR</strong><br /><i>Abstract:&nbsp;</i>On 3/13/03 while at 100 % power, during a review of future plant modification packages, Callaway Plant determined a problem existed in the current safety analysis for a steam generator tube rupture (SGTR) accident accompanied by an overfill condition. The current Final Safety Analysis Report (FSAR) does not explicitly address a SGTR overfill case. Investigations determined that for current plant conditions, an overfill condition could result if an auxiliary feedwater control valve supplying the ruptured steam generator (S/G) were to fail open. In this case water could be released through the S/G safety valves, resulting in a radioactive release to the environment greater than allowed by regulatory guidance. Since the SGTR overfill case was not explicitly addressed in the FSAR, credited operator action times were not maintained current. To assure regulatory compliance, plant procedures have been changed to administratively reduce the steady state Dose Equivalent Iodine (DEI) limit to 0.3 microcurie per gram (Technical Specifications currently limits DEI to 1.0 microcurie per gram). This lower DEI limit will ensure that if a SGTR overfill condition were to occur, post accident radiological consequences would not exceed limits contained in the FSAR and Standard Review Plan.
4832003004 | Callaway | 04/11/2003 | 06/09/2003 | ML03168132 | <strong>Boron Dilution Mitigation System Blocked in Mode 3 Which Is Not Consistent with FSAR Accident Analysis</strong><br /><i>Abstract:&nbsp;</i>On 4/11/03, while at 100 percent power, it was discovered that a note contained in Technical Specification (T/S) 3.3.9 for the Boron Dilution Mitigation System (BDMS), had been inappropriately applied during past reactor startups. This had been interpreted to allow blocking BDMS while withdrawing Shutdown (S/D) Bank rods in Mode 3. This action is not allowed in Mode 3 per Final Safety Analysis Report (FSAR) accident analysis Section 15.4.6.2 where BDMS is credited for automatically terminating a dilution event while in Mode 3. Wording of T/S 3.3.9 and T/S 3.3.9 Bases did not provide clear guidance as to what constitutes "reactor startup". The Bases indicate BDMS could be blocked prior to withdrawing "rods" for startup. These words do not delineate between control banks and shutdown banks. Based on this unclear guidance, procedure OTG-ZZ-001A was incorrectly revised allowing the blocking of BDMS prior to withdrawing shutdown banks. The discovery of the unclear T/S wording was the result of requested procedure enhancements to clarify when it was allowable to block BDMS. A review of reactor startups within the last 3 years indicated that BDMS was inappropriately blocked on three separate startups. The first occurred on 11/24/02, the second on 12/17/02, and the third on 4/2/03. Plant procedures governing reactor startup were revised to remove statements allowing blocking BDMS while withdrawing S/D Bank rods in Mode 3.
4832003005 | Callaway | 05/22/2003 | 07/21/2003 | ML03212054 | <strong>Failure of Both Containment Spray Pumps Due to Air Binding</strong><br /><i>Abstract:&nbsp;</i>On 5/22/03, with Callaway Plant in Mode 1 at 100 percent power, surveillance testing was being performed involving "B" Containment Spray pump, PEN01B. Upon starting, the pump failed to develop normal discharge pressure and flow for approximately 5 minutes. The pump then developed pressure and the test was completed satisfactorily. Subsequent review determined the pump had been gas bound. Ultrasonic exams and dynamic venting demonstrated that PEN01B was water solid and operable. An extent of condition review revealed that Containment Spray pump, PEN01A had experienced a 2 minute gas binding event on 4/29/03. Ultrasonic exams and venting were conducted and verified that PEN01A was operable. It was determined that both pumps were gas bound due to an inadequate system venting configuration after Mode 5 valve testing on 3/30/03 resulting in both trains of Containment Spray being inoperable upon entering Mode 4 on 3/31/03 until PEN01A was run on 4/29/03, and "A" train was declared operable. This resulted in noncompliance with Technical Specification 3.6.6 for a period of time greater than allowed. Potential corrective actions being evaluated include installing additional vent valves, and procedure improvements to address dynamic venting.
4832003006 | Callaway | 07/03/2003 | 03/18/2004 | ML04085054 | <strong>Multiple emergency procedure problems identified that could have impacted operator actionsand responses.</strong><br /><i>Abstract:&nbsp;</i>This revision of LER 2003-006-00 is being submitted to change the reporting criteria to specify that this is only a voluntary LER and no violation occurred. On 7/3/03, with Callaway Plant operating in Mode 1 at 100 percent power, and during development of Licensed Operator Continuing Training (LOCT), it was discovered that an error existed in emergency procedure E-3, STEAM GENERATOR TUBE RUPTURE. The postulated accident involved a reactor trip due to a loss of off-site power compounded by a steam generator tube rupture (SGTR) on "D" loop of the reactor coolant system, and a stuck open auxiliary feedwater flow control valve. Early in the procedure, the Pressurizer Power Operated Relief Valves (PORV) were being armed in order to provide cold overpressure protection during the cool down phase. By arming the PORVs early, this made it difficult to meet the conditions required to secure Safety Injection later in the SGTR recovery, which potentially could prolong recovery from the SGTR. Prolonged recovery would result in additional liquid being released to the atmosphere via the ruptured steam generator's atmospheric dump valve and additional dose to the public. Once the procedure error was identified, a procedure revision was issued which corrected the problem.
4832003007 | Callaway | 07/17/2003 | 04/23/2004 | ML04126016 | <strong>Engineering Evaluations incorrectly approved leaving Health Physics Access doors open.</strong><br /><i>Abstract:&nbsp;</i>This revision of LER 2003-007-00 is being submitted to delete the reporting criteria for an event or condition that could have prevented fulfillment of a safety function. Other previously identified reporting criteria remain applicable. On 7/17/03, with Callaway Plant at 100 percent power, an error was found in Engineering Evaluations that approved having the Health Physics (HP) Access doors 32201 and Hot Lab door 32282 open. These doors are pressure boundary doors between the Control Building and Communication Corridor and are required to be closed during accident conditions. With the doors open, HP Access Control fan coil unit SGKO3 would cause air from outside the Control Building to enter the HP Access area and mix with Control Building atmosphere. The Control Building atmosphere is credited in post-accident Control Room radiological consequence analysis and an outside air source has potential for impacting dose received by Control Room staff. An evaluation determined 25 minutes to close these doors in an emergency, which could result in an exposure of approximately 31.5 REM to Control Room staff. This dose was above regulatory limits and the event was classified as reportable as an unanalyzed event and a violation of Technical Specifications. When the door issue was identified, the doors were closed and a plant bulletin was issued indicating the doors were to remain closed except during normal use. Although the Regulatory Guide1.195 dose limit and ICRP30 Dose Conversion Factors are not currently part of Callaway's Licensing bases, they do demonstrate the limited safety implications of this event.
4832003008 | Callaway | 09/07/2003 | 11/06/2003 | ML03318010 | <strong>Technical Specification Violation Due to Valve Control Circuit Modification</strong><br /><i>Abstract:&nbsp;</i>On 9/4/03 with Callaway in Mode 1 at 100 percent power, a modification to replace the handswitch for "B" Pressurizer (Pzr) Power Operated Relief Valve Block valve (BBHV8000B) was implemented. During post modification testing, the valve operator and control breaker were damaged. The modification required removal of a wire which had not been specified by the modification work instructions. Repairs were performed and the valve control circuitry was restored to pre-modification conditions. The reportable condition occurred 9/7/03 when the Technical Specification Required Actions were not met within the associated Completion Time. Interim corrective actions restrict planning of motor operated valve control circuit work documents. Long term corrective actions include strengthening the training and qualification process for the planning of motor operated valve modification work documents.
4832003009 | Callaway | 10/21/2003 | 12/19/2003 | ML03363059 | <strong>Failure of NN11 Inverter Results in Technical Specification Required Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 0721, 10/20/03, with Callaway Plant at 100 percent power, inverter NN11 failed causing a momentary loss of electrical power to safety related AC bus NN01.The Control Room staff used approved plant procedures to recover from the event and stabilize plant conditions. Subsequent repair investigations extended past the 24 hour Technical Specification (T/S) Action time limit and a T/S required plant shutdown was performed. It was determined that the NN11 failure was due to a faulted static transfer switch circuit board. Repairs were completed and NN11 was declared Operable at 2202, 10/21/03. A plant startup was performed on 10/24/03 and normal plant operations resumed.
4982003001 | South Texas 1, South Texas 2 | 01/19/2003 | 03/20/2003 | ML03084066 | <strong>Partial Loss of Offsite Power To Unit 1 and Unit 2 Resulting in Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2003 at 1255, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 3 with the 2A and 2D Reactor Coolant Pumps running. While placing the North Bus Shunt Reactor in the switchyard in service, Unit 1 Standby Transformer received a lockout due to an over-current condition on the neutral of the Shunt Reactor. This caused the North Bus to clear and isolate the North Bus Shunt Reactor. Unit 1 experienced a partial Loss of Offsite Power (LOOP) to Standby Bus 1G and 1H which supply power to Engineered Safety Feature (ESF) Trains 1B and 1C. The Train 1B and Train 1C Emergency Diesel Generators (EDG) started as a result of the ESF Actuation - LOOP. The Train 1C components automatically loaded per design. The Train 1B Sequencer did not automatically load resulting in the manual loading of the Train 1B components by the Reactor Operators. Unit 2 experienced a partial LOOP due to the loss of the Unit 1 Standby Transformer which was supplying power to Auxiliary Busses 2F, 2J and Standby Bus 2F, which supplies ESF Train 2A. The Train 2A Emergency Diesel Generator automatically started and loaded as expected. The cause of the loss of Unit 1 Standby Transformer was de-energizing the switchyard North Bus, which provides power, to the Standby Transformer, due to a malfunctioning motor operated circuit switcher. There was no impact to radiological safety, safety of the public or safety of station personnel. Corrective actions include changing the protective relay scheme for the Shunt Reactor.
4982003002 | South Texas 1, South Texas 2 | 03/01/2003 | 09/30/2003 | ML03280151 | <strong>Manual Reactor Trip Due to Reduced Deaerator Level</strong><br /><i>Abstract:&nbsp;</i>At 0149 on March 1, 2003, a 24-volt DC (VDC) power supply in the Unit 1 Condensate Polishing System failed. This failure caused the Condensate Polishing service vessel outlet valves to close, as well as failure of the system bypass valve to open on high Condensate System differential pressure. The pressure transmitter signal that is required for opening the bypass valve was also not available due to the failed power supply. With all Condensate Polishing service vessel outlet valves closed and the system bypass valve closed, condensate flow to the deaerator was isolated. The Unit 1 reactor was manually tripped because of the ensuing decrease in deaerator level. The cause was a design characteristic in which loss of one power supply disabled the differential pressure signal required to open the system bypass valve and the signal required to maintain the output valves open for the normal system flow path. The power supply was determined to have failed due to age-related degradation. The affected power supply units have been replaced. A lock-up feature has been incorporated to ensure the Condensate Polishing Service Vessel outlet valves are locked in place in the event of a power supply failure. A fault tolerant power circuit will be developed and installed to prevent recurrence. This event resulted in no personnel injuries, offsite radiological releases, or damage to safety-related equipment. There were no challenges to plant safety.
4982003003 | South Texas 1 | 04/12/2003 | 10/15/2003 | ML03295048 | <strong>Bottom Mounted Instrumentation Penetrations Indications - Supplement to LER dated 6/11/2003</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2003, with South Texas Project Unit 1 in a refueling outage, personnel discovered deposits at two Bottom Mounted Instrument (BMI) nozzles of the reactor vessel. This condition was identified during the station's regular bare metal inspection of the reactor vessel bottom penetrations, which is done as part of the RCS Pressure Boundary Inspection for Boric Acid Leaks Program. A small amount of residue was noted around the circumference of BMI nozzle Penetrations #1 and #46 where they enter the reactor vessel. The residue consisted of approximately 150 milligrams of material from penetration number 1 and approximately 3 milligrams from penetration number 46. No wastage was observed on the outside of the bottom head, and samples of the residue were collected and analyzed. Both deposits contained boron and elevated levels of lithium consistent with reactor coolant system (RCS) leakage. Cesium isotopic analysis indicated an approximate age of 4 years for each sample. Ultrasonic testing was performed on all of the 58 BMI penetrations. Cracks were found in Penetrations #1 and #46, however, no cracks were found in any other penetration. The root cause is the use of Alloy 600 combined with nozzle manufacturing and installation methods that further increased the susceptibility of the metal to stress corrosion cracking when in contact with primary water. The nozzles at Penetrations #1 and #46 were repaired prior to restart of Unit 1. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment other than the affected BMI penetrations. There were no challenges to plant safety.
4982003005 | South Texas 1 | 09/04/2003 | 11/03/2003 | ML03311060 | <strong>Auxiliary Feedwater Pump 11 Breaker Failure to Close</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2003, Unit 1 was operating at 100% power when a routine surveillance test run of Auxiliary Feedwater Pump (AFWP) 11 was attempted. When operators attempted to start the pump, the supply breaker failed to close. The pump had been successfully run twice since the breaker was overhauled in June 2003. After the breaker was replaced with a spare, the surveillance was completed satisfactorily. The cause of the failure was determined to be increased mechanical resistance of the breaker mechanism caused by a random build up of tolerances from wear and case distortion which our existing overhaul program did not identify, coupled with a significant reduction in latch spring rotational torque capability (6 turn spring). It was determined that AFWP 11 was out of service while Standby Diesel Generator (SDG) 13 was out of service on August 18 and 19, 2003, in violation of Technical Specification 3.8.1.1, Action D. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
4982003006 | South Texas 1, South Texas 2 | 12/19/2003 | 02/09/2004 | ML04048051 | <strong>Unanalyzed condition that significantly degraded plant safety regarding the natural circulation cool down rate</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2003, Unit 1 and Unit 2 were operating at 100% power. During the performance of a fire hazards reactor coolant system (RCS) cool down analysis, it was discovered that the current procedural cooldown rate of 50°F/hr does not satisfy the design basis requirements when less than 4 steam generators are available during natural circulation cool down conditions. This condition placed both Unit 1 and Unit 2 in an unanalyzed condition that significantly degraded plant safety. The root causes of this event were the failure of the Westinghouse Owner's Group to fully address RCS loop stagnation conditions for natural circulation cool down and the failure to re-analyze the natural circulation cooldown cases when a change was made to increase the cool down rate to 50°F/hr. Corrective actions were taken to limit the natural circulation cool down rate and to complete long-term cooling analyses to validate the revised rate. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
4982003007 | South Texas 1 | 12/23/2003 | 02/17/2004 | ML04065009 | <strong>Failure of Main Steam Power Operated Relief Valve 1B</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2003, while performing the Main Steam System Valve Operability Test on Unit 1 Main Steam (MS) Power Operated Relief Valve (PORV) 1 B, the PORV hydraulic pump failed to start as required. MS PORV 1B was declared inoperable and initial investigation determined that the thermal overloads on the pump supply breaker (MCC E1B1/A3) had tripped. A detailed fault tree analysis was performed and the newly implemented PREP (Preventing Recurring Equipment Problems) process was utilized to troubleshoot the condition. During troubleshooting, the failure scenario could not be repeated. When the breaker (MCC E1B1/A3) was disassembled, a 3/8-inch piece of wiring insulation was found inside the contactor at "C" phase with evidence of arching on the insulation. This insulation caused intermittent contact of phase "C" which resulted in an over-current trip of the thermal overloads preventing the hydraulic pump from starting. The most likely source of the insulation is during the manufacturing and assembly of the breaker prior to arrival at South Texas Project (STP). It was concluded that failure of the breaker could have occurred during seismic events. Therefore, it was determined that MS PORV 1B had been inoperable originally from the breaker installation on 03/11/00 up until the replacement of its motor starter unit on 12/19/03. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
4992003001 | South Texas 2 | 01/25/2003 | 04/18/2003 | ML03115002 | <strong>Inoperable Residual Heat Removal Train</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2003 with Unit 2 in MODE 5, 2-RH-MOV-0060C, Loop C RHR pump suction valve, failed to open. 2-RH-MOV-0060C failed when the motor stalled and overheated causing the breaker to trip. This motor failure was caused by the motor pinion gear sliding down the motor shaft and contacting the declutching mechanism resulting in increased frictional loading. The motor pinion set-screw was not installed correctly in the drilled recess on the shaft. Consequently, when the motor was energized the pinion gear was thrust into the declutching mechanism. Coincident with this condition, the pinion key was also observed to be partially disengaged from the motor shaft keyway; however, this discrepancy was determined not to have contributed to the failure. Corrective actions include rework of MOV-0060C, inspection and repair as required of all potentially affected Unit 1 and Unit 2 motor operated valves (MOVs), and confirmation that the maintenance procedures for MOVs is adequate to assure proper installation of the setscrews. This event resulted in no personnel injuries, off site radiological releases or damage to safety related equipment other than MOV-0060C.
4992003002 | South Texas 2 | 03/09/2003 | 05/08/2003 | ML03133035 | <strong>Safety Injection Actuation</strong><br /><i>Abstract:&nbsp;</i>On March 09, 2003, Unit 2 was stable in Mode 3. Operators were transferring reactor coolant system temperature control from Main Steam (MS) Power Operated Relief Valve (PORV) 2C to MS PORV 2B when an unexpected MS Low Compensated Pressure Safety Injection actuation signal was initiated. The safety injection signal was generated when Low Compensated Steam Pressure signals were received on all three channels of Steam Generator 2B due to anticipatory gain as a result of dynamic pressure oscillations in the 2B Main Steam line. The pressure oscillations occurred due to condensed water in the MS line and PORV stack. The root cause was that STP elected to operate the plant in a non-routine configuration without properly assessing the plant conditions and consequences that it created. Corrective actions include procedure and program enhancements. This event resulted in no personnel injuries, offsite radiological releases, or damage to safety related equipment. There were no challenges to plant safety and the plant responded as expected.
4992003003 | South Texas 2 | 12/09/2003 | 05/03/2004 | ML04127047 | <strong>Standby Diesel Generator 22 Failure</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, December 9, 2003, a monthly surveillance test was being performed on Standby Diesel Generator 22. Unit 2 was operating in Mode 1 at 100% power. At approximately 1038, Standby Diesel Generator 22 experienced a mechanical failure in which the position 9 Master Connecting Rod fractured. This occurred approximately 18 minutes after the diesel generator was loaded to 100% during the surveillance. The failure caused significant peripheral damage to the cylinders, pistons, frame, control systems, lubrication system, crankshaft, and bearings on the engine, as well as the starting air system components located adjacent to the engine. The root cause of the failure is microcracks that developed on the position 9 Master Connecting Rod during the manufacturing process. The microcracks later propagated due to high cycle fatigue until the master connecting rod failed. Corrective actions include inspection of the master connecting rods of all Standby Diesel Generators to ensure that similar cracking had not occurred elsewhere. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment. Unit 2 continued to operate at 100% power after the event.
4992003004 | South Texas 2 | 12/09/2003 | 02/05/2004 | ML04042028 | <strong>Standby Diesel Generator 22 Failure</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, December 9, 2003, a monthly surveillance test was being performed on Standby Diesel Generator 22. Unit 2 was operating in Mode 1 at 100% power. At approximately 1038, Standby Diesel Generator 22 experienced a mechanical failure in which the position 9 Master Connecting Rod fractured. This occurred approximately 18 minutes after the diesel generator was loaded to 100% during the surveillance. The failure caused significant peripheral damage to the cylinders, pistons, frame, control systems, lubrication system, crankshaft, and bearings on the engine, as well as the starting air system components located adjacent to the engine. The root cause of the failure is microcracks that developed on the position 9 Master Connecting Rod during the manufacturing process. The microcracks later propagated due to high cycle fatigue until the master connecting rod failed. Corrective actions include inspection of the master connecting rods of all Standby Diesel Generators to ensure that similar cracking had not occurred elsewhere. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment. Unit 2 continued to operate at 100% power after the event.
5282003001 | Palo Verde 1 | 03/05/2003 | 09/21/2006 | ML06272011 | <strong>Pressurizer Safety Valve As-Found Lift Pressure outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2003, lift pressure verification testing was completed on four pressurizer safety valves(PSVs) that had been removed during the Unit 1 tenth refueling outage. The testing revealed that the as-found lift pressure for one of the four PSVs was found to be outside the Technical Specification limit of +3/-1 percent of design lift pressure. The valve design uses a spring to maintain the required lift pressure. The as-found PSV condition appears to be the result of a degraded spring. The equipment root cause failure analysis found that the valve spring did not meet the valve vendor's inspection criteria for squareness. The impact of the Unit 1PSV out-of-tolerance was evaluated and it was determined the results, based on the as-found conditions, were bounded by the peak Reactor Coolant System pressure results of the current Loss of Condenser Vacuum analysis of record. Loss of Condenser Vacuum is the most limiting event for peak primary pressure that is impacted by a PSV high out-of-tolerance condition. Previous similar events have been reported in the last three years.
5282003002 | Palo Verde 1 | 03/27/2003 | 04/21/2006 | ML06128056 | <strong>Manual Reactor Trip due to Degraded Main Condenser Tube Plug</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2003 with Unit 1 operating in Mode 1, Power Operation, at approximately 97 percent power, a HOTWELL A HIGH SODIUM alarm was received in the chemistry laboratory at approximately 09:27 MST. Chemistry personnel responded to the alarm and determined that hotwell 1A sodium was trending up. The condensate system was operating in the demineralizer by-pass mode at the time of the event. Control room personnel were notified and the abnormal operating (AO) procedure, Condenser Tube Rupture, 40AO-9ZZ10, was entered. Steam generator sodium levels continued to increase and at approximately 09:43 MST, in accordance with the procedure, the Control Room Supervisor (CRS) directed a manual reactor trip be initiated. All controls rods fully inserted and the plant was stabilized in Mode 3, Hot Standby. No other safety systems actuated and none were required. Problems were encountered with maintaining letdown flow but the control room operators were able to control pressurizer level within acceptable limits. The plant was cooled down to Mode 5, Cold Shutdown, to cleanup SG chemistry and to repair the cause of the intrusion to the hotewell. The cause of the event was determined to be the failure of a previously installed main condenser tube plug. The cause of the plug failure has been determined to be a manufacturing defect that may have been aggrevated during the installation of the plug. The failed tube was replalced. No other similar events have been reported by Palo Verde in the past three years.
5282003003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 09/19/2003 | 11/12/2003 | ML03324045 | <strong>Technical Specification Violation for Failure to meet Shutdown Cooling Trains OPERABLE Action Statements</strong><br /><i>Abstract:&nbsp;</i>Preparations for Unit 2 Steam Generator Outage (U2R11) revealed that the temporary Containment Pedestal Crane (CPC) was not seismically qualified. The CPC is installed on a Q-class structure during MODE 5 at the beginning of an outage, and is removed prior to MODE 4 at the end of an outage. The non-qualified CPC has been placed in service in all three units, the first application being Unit 1 in May 1995. With the CPC in operation with a load on the hook, and if a seismic event were to occur PVNGS may not have been able to meet the TS action statements for MODE 5 and MODE 6 Shutdown Cooling. Also, with one train of Shutdown Cooling inoperable due to maintenance activities, a seismic load failure may have prevented the fulfillment of a safety function to remove residual heat. The CPC will not be used during U2R11 while Shutdown Cooling or RCS integrity would be compromised or required to be operable. The temporary Containment Pedestal Crane had been used in all three Units during refueling outages since May, 1995. Palo Verde did not experience a recordable seismic event during any of the refueling outages during this time frame, May 1995 to September 2003.
5282003004 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 09/16/2003 | 05/25/2005 | ML05159029 | <strong>Cracks in Contact Block of Main Control Room Handswitches Result in Inoperable Equipment</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2003 a minor crack was discovered in a control switch contact block (Honeywell-Micro Switch model PTCC) in the Unit 3 main control room. Further evaluation was required to determine the transportability of the cracked contact block condition. The inspection of all applicable switches in all three units has been completed with a total of 57 switches, out of 2310 inspections, having unacceptable cracks. No actual switch failure, caused by the cracking condition, has been identified. The direct cause of this condition was determined to be over-torquing of the termination screws during initial switch installation. The root cause was attributed to the manufacturing process associated with the contact block. All defective Q-Class switches have been replaced in all three units and the remaining defective switches will be replaced. In addition, the applicable maintenance instructions have been revised to caution against over-tightening the termination screws and to verify crack free contact blocks when working on the associated hand switches. No other similar event has been reported by Palo Verde in the past three years.
5292003001 | Palo Verde 2 | 07/29/2003 | 04/25/2006 | ML06129053 | <strong>Reactor Trip with Loss of Forced Circulation due to Failed Pressurizer Main Spray Valve</strong><br /><i>Abstract:&nbsp;</i>On July 29, 2003, at 1500 Mountain Standard Time (MST), Unit 2 was at approximately 98% power when pressurizer main spray valve RCE-100F failed in the full open position. Attempts to close the valve per the alarm response procedure were unsuccessful. At 1515 MST, control room personnel manually tripped the reactor. In accordance with the applicable alarm response procedure, control room personnel secured the reactor coolant pumps (RCPs) to stop the reactor coolant system (RCS) depressurization. Control element assemblies fully inserted into the reactor core. Safety related buses remained energized during and following the reactor trip. Automatic safety injection and containment isolation actuation system (SIAS/CIAS) actuations occurred following the reactor trip, as RCS pressure continued to lower to the reactor protection system setpoint. The RCS was cooled on natural circulation with secondary heat removal via the main condenser. By 1616 MST, a containment entry was made and RCE-100F was manually isolated. At 1715 MST, RCP 1A was restarted restoring forced circulation to the reactor core. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. There were no previous events that involved the same underlying cause within the last three years.
5292003002 | Palo Verde 2 | 11/21/2003 | 01/16/2004 | ML04028043 | <strong>ESF Actuation-Unit 2 Emergency Diesel Generator Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2003, at approximately 22:53 Mountain Standard Time, Palo Verde Nuclear Generating Station Unit 2 experienced a valid Engineered Safety Feature (ESF) actuation of the "A" Emergency Diesel Generator (EDG). Unit 2 had been performing testing of the Gas Turbine Generator #1 (alternate AC Power source for station blackout) in isochronous mode. This testing required GTG #1 to be run in parallel with EDG "A." Upon completion of the paralleled operation, the Train "A" 4.16 kV bus had been successfully transferred to the EDG and loads carried by the EDG for approximately 5 minutes. When the EDG speed control was taken from "droop" mode (load sharing) to "isochronous" mode (fixed frequency,) the EDG output breaker tripped opened, resulting in a valid Loss of Power (LOP) signal based on under voltage on the Train "A" bus.EDG "A" shifted from the "test run" mode to the "emergency" mode and the output breaker re-closed, re-supplying the train "A" 4.16 KV bus. Offsite power was available to both safety buses throughout the event. The other (Train "B") safety bus was being supplied by offsite power and its EDG was operable. The offsite electrical grid was stable Palo Verde Unit 2 was defueled in its 11th refueling outage. No other ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. In the past three years, Palo Verde Nuclear Generating Station has not experienced a valid EDG actuation.
5292003003 | Palo Verde 2 | 11/23/2003 | 09/29/2006 | ML06285055 | <strong>Source Range Monitor Inoperable During Core Reload</strong><br /><i>Abstract:&nbsp;</i>All times are approximate and Mountain Standard Time. On November 23, 2003, Unit 2 was defueled preparing to enter Mode 6, when a Source Range Monitor(SRM) was found pegged low and reading "INVALID" on the Plant Monitoring System, and Emergency Response Facility Data Acquisition Display System. Technicians evaluated the channel and found all parameters within the nuclear instrument drawer to be normal. Based on the limited troubleshooting, the length of time since fuel had been off loaded and the absence of any neutron flux, the requirements of the Surveillance Test were considered satisfactory. With both SRM Channels declared as OPERABLE, the Irradiated Fuel Movement Checklist was completed. Unit 2 commenced core alterations to refuel the Unit 2 reactor and entered Mode 6 at 16:02. The first fuel assembly was lowered next to SRM Channel 1 with counts per second increasing as expected. However, as the second assembly was lowered next to SRM Channel 2, the counts per second did not change. At 16:25 SRM Channel 2 was declared inoperable and core alteration was suspended. No similar LER condition has been submitted to the NRC in the past three years.
5292003004 | Palo Verde 2 | 12/08/2003 | 05/27/2004 | ML04163015 | <strong>Mode 3 Entry With An Auxiliary Feed Water Pump Inoperable - Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On December 8, 2003 at approximately 0540 MST, Unit 2 was in Mode 4, Hot Shutdown, with heat-up activities in progress to return the unit to service following a refueling outage. A surveillance test was performed to verify that the A train auxiliary feedwater pump discharge check valve was closed. The acceptance criterion of the test was not met and the valve was declared inoperable. Subsequent review by engineering personnel concluded that the test was not valid since the check valve had not been opened with pump flow and the test was not required to be performed until the plant achieved normal operating temperature and pressure. The check valve was then declared operable. The unit entered Mode 3, Hot Standby, and the valve was subsequently successfully tested at NOT/NOP on December 11, 2004. On April 1, 2004, during an integrated inspection exit meeting, the resident NRC inspector stated that the NRC had concluded that a technical specification violation had occurred when the unit entered Mode 3 since there was insufficient evidence to conclude that the discharge check valve was operable at the time of Mode 3 entry. The cause of the condition was human error by Engineering and Operations personnel.
5302003001 | Palo Verde 3 | 03/20/2003 | 06/25/2004 | ML04189034 | <strong>Main Steam Safety Valve As-Found Lift Pressures Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2003, Unit 3 was in MODE 1, operating at approximately 98 percent power when augmented testing revealed that one main steam safety valve (MSSV) had an as-found lift pressure above the Technical Specification limit of +/- 3 percent of design lift pressure. The MSSV is believed to have experienced the phenomenon called "sticking" when the MSSV lifted during the surveillance testing. The out of tolerance as-found condition appears in some cases to be the results of the valve disc bonding with the nozzle seat. The valve was reset per plant procedures to +/-1% of the required setpoint upon completion of valve testing. Previous similar events were reported in LER 50-529/2000-002, LER 50-529/2000-009, LER 50-529/2001-001 and LER 50-529/2002-001.
5302003002 | Palo Verde 3 | 03/29/2003 | 05/27/2003 | ML03154055 | <strong>RCS Pressure Boundary Leakage Caused by Degraded Inconel Alloy 600 Components</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2003 with Unit 3 operating in Mode 4, Hot Shutdown, and cooling down to Mode 5, Cold Shutdown, for a refueling outage, engineering personnel discovered boric acid on a reactor coolant system hot leg instrument nozzle and a pressurizer heater sleeve. The cause of the boric acid leakage was attributed to primary water stress corrosion cracking of alloy 600 Inconel material in the instrument nozzle and the pressurizer heater sleeve. The amount of boric acid found was small. A second pressurizer heater sleeve was initially suspected to be leaking, but a subsequent VT-2 examination revealed no indication of leakage. The instrument nozzle was replaced with an Alloy 690 nozzle and the pressurizer heater sleeve was repaired using a mechanical nozzle seal assembly (MNSA). As a conservative measure, the second suspected heater sleeve was repaired with a MNSA clamp. Similar previous conditions were reported in LER 50-530/2001-003-00, LER 50-528/2001-001-00 and LER 50-528/1999-006-00.
5302003003 | Palo Verde 3 | 06/14/2003 | 08/08/2003 | ML03226053 | <strong>Technical Specification Violation for Failure to Calibrate Nuclear Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2003 with Unit 3 operating in Mode l, Power Operation, at approximately 40 percent rated thermal power a technical specification violation occurred when required reactor power instrumentation was not calibrated as required by surveillance requirements. The unit had reduced power from approximately 98 percent power on June 13 in response to a condenser in-leakage problem. The technical specification surveillance criteria, for when calibration of nuclear power instrumentation is required, changes when power is below 80 percent, from +/- 2 percent of the heat balance calorimetric to -0.5 to 10 percent of the heat balance calorimetric. During the first performance of the surveillance following the reduction in power several channels of nuclear power indication were more than -0.5 percent (but within -2 percent) below the heat balance calorimetric however a calibration of these channels was not performed. The cause of the event was human performance error by control room licensed operators who did not recognize the change in acceptance criteria when power was reduced below 80 percent. Corrective action was taken to require that personnel performing the surveillance select the applicable acceptance criteria. No other similar events have been reported by Palo Verde in the past three years.
5302003004 | Palo Verde 3 | 07/28/2003 | 09/19/2003 | ML03273135 | <strong>Reactor Trip with Loss of Forced Circulation Due To an Electrical Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2003, Unit 3 was in MODE 1. At approximately 18:54 Mountain Standard Time (MST), a sub-synchronous relay Lockout Trip was received during a grid perturbation resulting in a Main Turbine Trip. The reactor tripped from approximately 98% power on a Core Protection Calculator generated anticipatory Low DNBR Trip (Reactor Coolant Pump speed coast-down) when the automatic Fast Bus Transfer did not successfully transfer house loads back onto offsite power sources. Fast Bus Transfer logic prevented transfer due to momentary low voltage on the alternate supplies as a result of the fault. The subsequent loss of the 13.8kV non-class busses resulted in a loss of power to non-safety related AC buses. Another local utility, (Salt River Project) was performing switching operations in the Hassayampa Switchyard just prior to the grid disturbance. A human performance error left a grounding switch closed during the switching operation and a three-phase fault to ground occurred on the Hassayampa to Arlington Valley 500kV line, relaying off area power plants, including PVNGS Unit-3. The Control Room Supervisor diagnosed this event as a Loss of Forced Circulation, and the appropriate Emergency Operating Procedure (EOP: LOOP/LOFC) was entered. No Emergency Plan classification was required. On July 29, 2003 at approximately 00:44 MST, RCP 1A was restarted, restoring forced circulation. RCP lB was started a short time later. Unit 3 transitioned from the Loss of Forced Circulation EOP to the Mode 3 to Mode 5 Normal Operating Procedure. In the past three years, the station has not experienced a Reactor Trip with loss of Forced Circulation due to an Electrical Grid Disturbance.