## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192006001 | Oyster Creek | 05/06/2006 | 07/05/2006 | ML06188030 | <strong>Unplanned Manual Scram Inserted During Planned Reactor Shutdown to Expedite Plant Cooldown</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2006, Oyster Creek was shutting down to start a Forced Outage (1F10) to repair a leak from the Steam Packing Exhauster Cooling Condenser (EIIS: SE). This leak was adding excess volume to the radiological liquid waste processing systems (Radwaste). During the shutdown, it was decided to perform a manual reactor scram to improve plant cool down and thereby minimize the volume of component leakage being sent to Radwaste (EIIS: WD). This manual SCRAM was not a scheduled item during the pre-outage planning. The decision to insert the manual scram was made during the shutdown process. It was not performed to avoid reaching an automatic scram setpoint. The 1F10 reactor shutdown was planned to be accomplished using full manual control rod insertion and manual scram was not a planned activity. The manual scram was performed after reducing reactor power level to the Source Range and the reactor was subcritical at the time. All Control Rods fully inserted as a result of the manual scram, and all systems performed as designed.
2192006002 | Oyster Creek | 06/20/2006 | 09/22/2006 | ML06278024 | <strong>Failure of MSIV Surveillance Test due to Transcription Error</strong><br /><i>Abstract:&nbsp;</i>Oyster Creek performed a full closure test of main steam isolation valve NS04A (outboard MSIV on 'A' main steam line) during the 1F09 forced outage in February 2006. During this test the valve did not stroke closed in the allowable time specified in the surveillance procedure. When measured using the plant process computer (PPC), the valve stroked full closed in 2.0 seconds. The acceptance criteria for this timing test is 3.0 seconds. The failure of this surveillance test was not recognized at the time of performance and as a result the plant was started up from 1F09 with an inoperable MSIV. During the later 1F10 forced outage in May 2006 the valve was tested again under the surveillance procedure and failed to meet the acceptance criteria for the PPC timing. The valve therefore failed the surveillance test and was adjusted and retested acceptably prior to startup in May 2006. The discovery date of the failed surveillance tests was June 20, 2006.
2192006003 | Oyster Creek | 10/16/2006 | 12/13/2006 | ML06353047 | <strong>Local Leak Rate Test Results in Excess of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On Monday, October 16, 2006, with the plant in Cold Shutdown for refueling outage 1R21, the as-found Local Leak Rate Test (LLRT) of inboard Main Steam Isolation Valve (MSIV) NS03B failed to meet the acceptance criteria of Technical Specification 4.5.D.2. No as-found data could be obtained on this valve due to failure to maintain pressure. The valve was last refurbished during refueling outage 1R18 in October 2000, when a pilot poppet modification and new stem were installed. Following maintenance, in 1R18 the valve passed the as-left LLRT. The apparent cause of the as-found LLRT failure in 1R21 was attributed to an oxide layer build up on the valve poppet seat and in-body seat ring. The safety significance of this event is considered minimal. The leakage past NS03B would have been limited by the leak rate of the outboard MSIV (NS04B) in the same header which met the LLRT acceptance criteria of Technical Specification 4.5.D.2 when tested in 1R21. This leakage provides adequate margin between projected potential offsite dose and 10 CFR 100 guidelines.
2192006004 | Oyster Creek | 12/08/2006 | 02/02/2007 | ML07038031 | <strong>Operation Exceeding Maximum Power Level</strong><br /><i>Abstract:&nbsp;</i>An unplanned reactor power increase to 102.46% of rated thermal power occurred due to opening and re-closing of one of the five Electromatic Relief Valves (EMRVs). After being open for approximately 57 seconds, the EMRV re-closed without operator action. Subsequent to the EMRV closure, the reactor power increased to 102.46% and was immediately reduced to less than 100% as a result of operator action to decrease the recirculation flow rate. The most probable cause of this event was the malfunction of the pressure switch connected to the subject EMRV. The pressure switch was subsequently replaced.
2202006001 | Nine Mile Point 1 | 06/11/2006 | 08/10/2006 | ML06229026 | <strong>Technical Specification Required Shutdown due to Increased Drywell Leakage</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2006, Nine Mile Point Unit 1 (NMP1) commenced a planned downpower to perform a drywell entry to determine the cause of increased drywell leakage. Packing on a Reactor Coolant Recirculation System (RCS) pump drain valve was found leaking. The pump suction and discharge valves were then closed. The normally closed drain valve was backseated, which reduced the leak however, a leak in a weld downstream of the valve was discovered. The drain valve was subsequently closed to isolate the weld leak, and NMP1 began power ascension. On June 11, 2006, at 0126 hours NMP1 entered Technical Specification (TS) 3.2.5, "Reactor Coolant System Leakage," required shutdown due to an increase in leakage exceeding 2 gallons per minute in a 24 hour period. NMP1 was placed in cold shutdown mode at 1417 hours on June 11, 2006. The source of the increased leakage was determined to be the drain valve packing. The cause of the packing leak was installation of incorrect packing in March 1997. The packing that was installed did not have the same diameter as the inside diameter of the stuffing box. Adequate performance standards for valve packing installation did not exist in the early 1990s. The NMP1 valve packing program was initially issued in November of 1998. During the shutdown, NMP1 replaced the packing in the leaking RCS pump drain valve and repaired the weld leak. Extent of condition review identified the need for packing replacement of the redundant valve, which was entered in the corrective action process. The current NMP1 valve packing program provides adequate performance standards for packing installation.
2202006002 | Nine Mile Point 1 | 06/12/2006 | 08/11/2006 | ML06234005 | <strong>HPCI Logic Actuation due to Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2006, with Nine Mile Point Nuclear Station (NMPNS) Unit 1 reactor plant in the Startup mode at 0% power, 5 psig and 192 degrees Fahrenheit, reactor water level increased to the high level trip setpoint when plant operators placed the Feedwater system in the long path recirculation configuration to support chemistry sampling. This resulted in a valid Main Turbine Trip signal and actuation of the High Pressure Coolant Injection (HPCI) initiation logic. HPCI is a mode of operation that uses selected equipment of the condensate and feedwater system to perform its function. At the time of the event, HPCI was not required to be operable with reactor pressure less than 110 psig. In accordance with operating procedures, the feedwater booster pumps were not required to be in service and their control switches were in pull-to-lock. Without the booster pumps running, the feedwater pumps start permissive circuitry is not satisfied. Therefore, though the HPCI start logic was actuated, injection did not occur and was not required. The cause of this event is inadequate implementation of previous operating experience. Similar level control problems occurred in the past without the lessons learned incorporated into operating procedures to warn operators of possible consequences. To prevent recurrence, the applicable operating procedure will be revised to establish the proper sequence for placing the Feedwater system in long path recirculation configuration during plant startup and a precaution will be added to alert operators about potential reactor level control problems.
2372006001 | Dresden 2 | 02/01/2006 | 04/03/2006 | ML06101063 | <strong>Unit 2 Isolation Condenser Declared Inoperable due to Inadequate Backfilling of Instrument Sensing Lines</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2006, at approximately 1943 hours (CST), with Unit 2 at approximately 98 percent power, Dresden Nuclear Power Station technicians were performing a calibration of the Isolation Condenser Steam/Condensate Line High Flow instrumentation when a technician observed an unexpected response during the return to service of the Isolation Condenser Condensate Line High Flow Differential Pressure Switch DPIS 2-1349B. The switch monitors flow in the Isolation Condenser Condensate Return line. The calibration was stopped. The Isolation Condenser was declared inoperable and isolated. Subsequent investigations determined that the observed unexpected response was the result of voids in the instrument sensing lines of the Isolation Condenser Steam/Condensate Line High Flow Differential Pressure Switch and that the instrumentation was operable with the voids present. The apparent cause of the voids in the instrument sensing lines of the Isolation Condenser Steam/Condensate Line High Flow Differential Pressure Switch was the failure of Procedure DOP 1300-11, "Unit 2 Isolation Condenser Fill and Vent," to identify that the sensing lines required backfilling after filling of the Isolation Condenser piping. A corrective action was created to revise Procedure DOP 1300-11 to require the backfilling of sensing lines after filling of the Isolation Condenser piping.
2372006002 | Dresden 2 | 04/06/2006 | 06/05/2006 | ML06164035 | <strong>Unit 2 High Pressure Coolant Injection System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2006, at approximately 1039 hours (CDT), with Unit 2 at approximately 97 percent power, Dresden Nuclear Power Station Instrument Maintenance technicians were installing a new High Pressure Coolant Injection System temperature recorder 2-2340-9 when an energized recorder electrical lead was accidentally shorted to a recorder mounting bracket screw. A consequence of this electrical short was the transfer of the Essential Service System to its emergency power supply from Motor Control Center 28-2 and the trip of Essential Service System circuit 16. This resulted in the High Pressure Coolant Injection System being declared inoperable due to a loss of its automatic function from the loss of power to its flow controller and signal converter. However, the system was available due to control room personnel being able to manually control system operation. The apparent cause of this event was human performance associated with the technicians' lack of attention to detail in manipulating tools and failure to self-check. Corrective actions addressed the human performance issues through discussions of this event with the IM technicians during department training sessions and the evaluation the technicians during out-of-the-box training for proper use of human performance tools. These corrective actions reinforced the need for self-checking and the use of tape on adjacent metal components when working with energized electrical leads.
2372006003 | Dresden 2 | 05/31/2006 | 07/28/2006 | ML06216052 | <strong>Unit 2 Reactor Steam Dome Pressure-Low Permissive Switch Determined to Have Been Historically Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2006, at approximately 1400 hours (CDT), with Unit 2 at approximately 100 percent power, Dresden Nuclear Power Station Engineering and Operations personnel reviewed the equipment history of the Unit 2 Reactor Steam Dome Pressure-Low Permissive Switch and concluded that previous failures of the switch to pass the Technical Specification Allowable Value in 2004, 2005 and 2006 might have incorrectly assumed that the failures occurred at the time of discovery. A further evaluation was conducted which provided firm evidence that the historical failures should have been classified as a failure to meet the Technical Specifications Allowable Value for a period that exceeded Allowed Outage Times. These events are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." The apparent cause of the switch failures was a knowledge-based awareness by technicians performing the calibration of the switches that using smaller step changes during calibration can result in improved accuracy of the setpoint. Corrective actions include training of technicians on the technique to be used in calibrating this switch and changes to the calibration procedure.
2372006004 | Dresden 2 | 07/04/2006 | 09/05/2006 | ML06257023 | <strong>Unit 2 Reactor Scram due to Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On July 4, 2006, at approximately 0259 hours (CDT), with Unit 2 at approximately 98 percent power, Dresden Nuclear Power Station Unit 2 received a Group I Isolation on a Main Steam Line High Flow signal. The Main Steam Line High Flow signal was caused by the unexpected closure of the 1A Main Steam Isolation Valve and the resulting redistribution of steam to the remaining three main steam lines. All Group I isolation valves closed and the reactor automatically scrammed. Reactor water level was automatically controlled and the reactor vessel level shrink resulted in an expected Group II and Group III isolation signals. All systems responded as required and the Isolation Condenser was manually initiated to control reactor pressure. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)." The root cause of the event was attributed to two potential failure modes, inadequate tightening of the compression fitting nut causing inadequate compression of the ferrule to the tubing to the 1A Main Steam Isolation Valve, or the existing tubing to the 1A Main Steam Isolation Valve is undersized. Corrective actions include replacement of the compression fitting to the 1A Main Steam Isolation Valve, implementation of corrective actions as required to address any knowledge weaknesses relating to proper compression fitting assembly and verification practices as determined through the appropriate training systems analysis, and to inspect the compression fittings and tubing associated with Unit 2 and Unit 3 Main Steam Isolation Valves.
2372006005 | Dresden 2, Dresden 3 | 11/08/2006 | 01/08/2007 | ML07017035 | <strong>Units 2 and 3 Control Room Emergency Ventilation Air Conditioning System Inoperable due to Leaking Fittings</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2006, at 2254 hours (CST), with Unit 2 at approximately 85 percent power and Unit 3 in a refuel outage, Dresden Nuclear Power Station control room personnel identified that the Control Room Emergency Ventilation Air Conditioning System failed to maintain proper control room temperature. Technical Specification 3.7.5, "Control Room Emergency Ventilation Air Conditioning (AC) System," was entered. The system was restored to operable status on November 9, 2006 at 0555 hours (CST). This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident," as the Control Room Emergency Ventilation Air Conditioning System is a single train system. The cause of the event was attributed to a loss of process fluid from the Control Room Emergency Ventilation Air Conditioning System's Refrigeration Condensing Unit due to loose instrument tube fittings caused by vibration. The corrective action to address this event is to enhance existing Control Room Emergency Ventilation Air Conditioning System inspections by establishing a new maintenance activity to perform a yearly walk down to monitor for refrigerant leaks on the Control Room Emergency Ventilation Air Conditioning System.
2442006001 | Ginna | 05/17/2006 | 07/13/2006 | ML06201023 | <strong>Potential Failure of Charging Pumps due to Unevaluated Fire Scenario</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2006, during the performance of an electrical engineering circuit evaluation of certain Appendix R fire scenarios, it was discovered that a previously unevaluated failure mode potentially existed for the Charging Pumps. Certain fire scenarios occurring in the Control Complex, Cable Tunnel, or Auxiliary Building, could result in the failure of specific undervoltage protection circuitry. The failed circuitry could trip the "A" Charging Pump breaker and hold it in a tripped condition. A similar condition existed for the "B" Charging Pump breaker, during certain fire scenarios in the "A" Battery Room. The safety significance of this event was reviewed and determined to be of low risk significance.<br /><br /> This report is being made under 10CFR50.73(a)(2)(ii)(B).<br /><br /> Corrective action to address the failure mode is outlined in Section V.
2442006002 | Ginna | 08/01/2006 | 12/21/2006 | ML06361013 | <strong>Off-site Power Systems Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>This LER covers two separate events per NUREG 1022, Revision 2, Section 2.3. On August 1, 2006 and August 2, 2006 the Rochester Gas and Electric (RGE) Energy Control Center notified the R.E. Ginna Nuclear Power Plant (Ginna) control room that the post contingency low voltage alarm had been received for the off-site power system. Ginna Operations entered procedure O-6.9, Operating Limits for Ginna Station Transmission, and declared offsite power inoperable per Technical Specification (TS) 3.8.1 for each occurrence. Ginna declared the off-site power system operable for each occurrence when notified by RGE that the alarm had cleared. Corrective action to prevent recurrence is outlined in Section V.B.
2442006003 | Ginna | 07/25/2006 | 09/22/2006 | ML06272004 | <strong>Inoperability of Two Channels of Flow Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2006 during the review of planned maintenance work packages, it was discovered that the Residual Heat Removal (RHR) to Safety Injection (SI) flow transmitters required by the Technical Specification post accident monitoring (PAM) instrumentation have as one of their power sources the opposite diesel generator train as the RHR pump whose flow they monitor. Potential loss of electrical power scenario could have caused a loss of the "A" RHR Pump and flow indication for the "B" RHR Pump. The same condition existed for the "B" RHR Pump and flow indication for the "A" RHR Pump. This condition had been in place since original plant design and construction. This report is being made under 10CFR50.73(a)(2)(i)(B). Corrective action to address the potential failure mode is outlined in Section V.
2442006004 | Ginna | 04/09/2005 | 11/03/2006 | ML06318023 | <strong>Inoperability of Two Trains of Standby Auxiliary Feedwater</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2006, a reportable condition was identified during the review of a previous issue discovered on April 18, 2005. The current review was being performed in response to NRC inspection questions regarding the previous issue. On April 18, 2005, while at 100% power, both trains of standby auxiliary feed water (SAFW) flow transmitters were found isolated. The plant had entered Mode 3 on April 9, 2005 for a routine startup after a refueling outage. The transmitters were restored to their normal operational alignment promptly when the condition was identified. It has since been determined that this condition resulted in the inoperability of both trains of SAFW. Corrective action to address the condition is outlined in Section V.
2442006005 | Ginna | 10/09/2006 | 12/06/2006 | ML06347003 | <strong>B Containment Sump Covered While in Mode 4</strong><br /><i>Abstract:&nbsp;</i>At 0400 on October 9, 2006 with the plant in Mode 4, the B Containment (recirculation) Sump grating was discovered to be covered with lead shielding blankets. This would have restricted the ability for water to flow freely into the sump, rendering it inoperable. This was a violation of Ginna Technical Specification 3.5.3. Corrective action to prevent recurrence is outlined in Section V.B.
2442006006 | Ginna | 10/14/2006 | 12/15/2006 | ML06356006 | <strong>Core Alterations and Movement of Irradiated Fuel With CVI Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2006 it was discovered that the DC power to the Engineered Safety Features (ESF) relay racks was de-energized, which resulted in the Containment Ventilation Isolation (CVI) system being inoperable. This condition is prohibited by Technical Specifications section 3.3.5 during core alterations and movement of irradiated fuel assemblies within Containment. The ongoing fuel movement was immediately stopped. The investigation revealed that the DC power was isolated on the morning of October 13, 2006 and that core alterations and fuel movement had occurred on several occasions during the time that the system was inoperable. Corrective action to prevent recurrence is outlined in Section V.B. Subsequent analysis has concluded that a fuel handling accident with the CVI system inoperable would not have resulted in applicable regulatory limits being exceeded; therefore, this event had no impact on the health and safety of the public.
2442006007 | Ginna | 10/07/2006 | 03/01/2007 | ML07067015 | <strong>Main Steam Safety Valve Setpoint Exceedance</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2006, with the plant in Mode 1, in-place testing of main steam safety valve 3508 determined that the as-found lift pressure did not meet the acceptance band of +1% / -3% of setpoint (1085 psig), as specified by Technical Specification surveillance SR 3.7.1.1. This was the second unsatisfactory as-found lift pressure for a main steam safety valve, as in-place sequential testing had previously determined that safety valve 3515 had failed to meet the as-found acceptance band. Technical Specification LCO 3.7.1, "Main Steam Safety Valves (MSSVs)", requires eight main steam safety valves to be operable in Modes 1, 2 and 3. Since the two unsatisfactory as-found lift pressures may have arisen over a period of time (found during sequential testing), it is assumed that at least one required main steam safety valve was not operable during past plant operation for a time greater than allowed. Therefore, this occurrence is considered reportable in accordance with 10 CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The apparent cause of the set point drift in the MSSVs is additional friction in the spindle guide area. Corrective action to address the condition is outlined in Section V. Operation of the facility with the main steam safety valves as-found settings was within analytical bounds; therefore, this event had no impact on the health and safety of the public.
2442006008 | Ginna | 10/15/2006 | 12/21/2006 | ML06361008 | <strong>Charcoal Filter Efficiency Test Failure</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2006, with the plant shutdown for a refueling outage, and 29 days after a charcoal adsorber sample was taken from a Spent Fuel Pool Charcoal Adsorber System filter for penetration testing per Technical Specification (TS) surveillance SR 3.7.10.3 and specification 5.5.10, the methyl iodide penetration level of the charcoal sample was determined to be unacceptable. Movement of irradiated fuel that had decayed < 60 days since being irradiated occurred in the Auxiliary Building commencing on October 15, 2006. As a result of the unsatisfactory test result, TS 3.7.10 was not met. Therefore, this occurrence is considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the Ginna Technical Specifications. The cause of this event was due to incorrect test parameters being previously supplied to the vendor that performed the methyl iodide penetration testing and a delay in obtaining the test results. Corrective action to address the condition is outlined in Section V. Subsequent analysis has concluded that a fuel handling accident with degraded charcoal filtration would not have resulted in applicable regulatory limits being exceeded; therefore, this event had no impact on the health and safety of the public.
2472006001 | Indian Point 2 | 03/01/2006 | 04/18/2006 | ML06114025 | <strong>Manual Reactor Trip due to Multiple Dropped Control Rods Caused by Loss of Control Rod Power due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2006, at 1435 hours, operators initiated a manual reactor (RT) trip due to 12 of 53 control rods (CRs) dropping into the reactor core. All primary safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained in-service. The Auxiliary FW system automatically started as a result of the RT. The cause of the event was personnel error due to inadequate work practices and inadequate interface requirements. Supplemental personnel were erecting scaffolding in the cable spreading room where the power cabinets for the CRs are located. During this work activity, a scaffolder inadvertently bumped the disconnect switch associated with rod control power cabinet 1AC. Those CRs that lost power dropped into the core. Inadequate preparation practices resulted in not having a ladder required for the work and resulted in a worker stepping on the cabinet. The computer work flow process bypassed the work management process (procedure IP-SMM-WM-100) which requires operations/planning to assess risk and authorize work. Significant corrective actions included coaching personnel on management expectations on work control and interim measures requiring operations review and approval of scaffold work orders. The work flow process will be revised to match the work management procedure; the scaffold procedure will be revised to require operations notification for scaffold work and the pre-job briefing checklist will require identification and staging of tools. The event had no effect on public health and safety.
2472006002 | Indian Point 2 | 07/24/2006 | 09/22/2006 | ML06272014 | <strong>Technical Specification Prohibited Condition for Two Inoperable Channels of PAM Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2006, Post Accident Monitoring (PAM) instrument LT-3300 was determined to be inoperable. This determination was made when reviewing data taken during a July 22, 2006 containment pressure relief. The containment level transmitter LT-3300, which indicates sump water level, unexpectedly responded to changes in containment pressure. It was subsequently determined that LT-3300 had been inoperable since May 16, 2006, the date Unit 2 exceeded Mode 3 upon startup from the 2R17 refuel outage. The instrument, LT 3300, was one of three containment water level (containment sump) instruments required to be operable in accordance with Technical Specification (TS) 3.3.3. One other required PAM instrument, LT-940, had previously been declared inoperable since May 16, 2006. Therefore, two required channels had been inoperable since May, 16, 2006. This time period exceeded the TS 3.3.3, Condition C, 7 day completion time. In addition, entry into Mode 3 on May 16, 2006, and subsequent return to full power, was made with these two channels inoperable without meeting the requirements of LCO 3.0.4. The apparent cause of the failure of LT-3300 is indeterminate at this time due to instrument inaccessibility during plant operation. Corrective actions are to include troubleshooting and replacement or repair of LT-3300 during 2R18 refuel outage. The cause of LT-3300 inoperability will be further evaluated at that time. This event had no effect on public health and safety.
2472006003 | Indian Point 2 | 08/23/2006 | 10/23/2006 | ML06297024 | <strong>Manual Reactor Trip due to a Mismatch between Reactor Power and Turbine Load Caused by Cycling of Steam Dump Valves after a Power Reduction for Loss of Heater Drain Tank Pumps</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2006, at 1035 hours, control room (CR) operators initiated a manual reactor trip (RT) due to a mismatch between reactor power and turbine load. Power was initially reduced to 77% for loss of Heater Drain Tank (HDT) pumps then further reduced per Technical Specification 3.2.3 due to axial flux difference outside its required operating limit. CR operators initiated a RT during the further power reduction due to a mismatch between reactor power and turbine load from cyclic operation of the high pressure steam dump (HPSD) valves. All primary safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained in-service. The Auxiliary Feedwater system (AFWS) started due to steam generator (SG) low level from shrink effect. Feedwater (FW) isolation and actuation of the AFWS occurred due to a 22 SG high level as a result of overfeed from leakby through the 22 FW low flow bypass valve. The cause of the RT was improper gain settings on the HPSD temperature modules which caused the HPSDs to respond increasingly disproportional to the input signal. The improper settings were attributed to inadequate review during implementation of actions for the Power Uprate Project in 2004. The cause of the loss of the HDT pumps was a failed HDT level controller power supply. Contributing causes included incorrect information in the HPSD module calibration procedure and inadequate procedural guidance. Corrective actions include properly setting the HPSD modules, replacement of the HDT power supply, preparation of a calibration procedure for the HPSD modules, calibration training and procedure revisions. The event had no effect on public health and safety.
2472006004 | Indian Point 2 | 08/24/2006 | 10/23/2006 | ML06297023 | <strong>Automatic Actuation of Both Motor Driven Auxiliary Feedwater Pumps due to Trip of 21 Main Feedwater Pump Caused by High Vibration</strong><br /><i>Abstract:&nbsp;</i>On August 24, 2006, while performing a plant startup, the 21 Main Boiler Feedwater Pump (MBFP) tripped as a result of high vibration initiating the automatic actuation of both motor driven Auxiliary Feedwater Pumps (AFWP). At the time of the event both AFWPs were in operation, both MBFPs isolated and the 22 MBFP was shutdown. Operations was starting the 21 MBFP by rolling up the steam turbine. During the turbine rollup the MBFP turbine was near the low end of the turbine critical speed while operators were transferring MBFP turbine control. MBFP turbine vibration increased significantly during transition through the critical speed and the high vibration actuated one of the MBFP trip devices. As a result of the MBFP trip, both motor driven AFW pumps received start signals. The direct cause of the event was turbine vibration due to excitation of the turbine rotor and casing as a result of the rotor being near the turbine critical speed. The apparent cause was weak procedural guidance in the main feedwater (FW) system operating procedure (SOP) which provided a critical speed that was too narrow. Corrective actions include; a brief of operations on the event, a review for revision of the FW SOP to include a wider critical speed range and delay of turbine control transfer past the critical speed and to allow the MBFP turbine to be rolled on steam via Lovejoy controls past the critical speeds. Necessary procedure revisions will be implemented. The event had no effect on public health and safety.
2472006005 | Indian Point 2 | 11/15/2006 | 01/15/2007 | ML07030039 | <strong>Automatic Reactor Trip due to a Turbine Trip as a Result of a Main Generator Exciter Protective Trip Caused by a Generrex Power Supply Loss of Electrical Ground</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2006, at 1400 hours, with reactor power at 100%, an automatic reactor trip (RT) was initiated as a result of a turbine trip due to a main generator exciter protective trip during troubleshooting of the exciter Generrex power supply. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. A post transient evaluation was performed prior to restart. The apparent cause was believed to be a momentary loss of electrical ground to the alarm cards that monitor primary and redundant Generrex power supplies for the main generator exciter. After replacement of the #1 power supply circuit card, resistance measurements of a pin electrically connected to a common ground resulted in an output spike in the redundant power supply. The operating power supply spiked low dropping the voltage below the trip set point which initiated a main generator exciter protective trip. A screw terminal where the grounds are mounted was found to be loose. Corrective actions included providing proper connections for the common ground, repairs to the Generrex +15V/#1 Power Supply and checking all remaining +/-15 Volt pins and terminal points for proper operation. The Generrex power supply #1 will be replaced with a refurbished power supply. The event had no effect on public health and safety.
2472006006 | Indian Point 2 | 11/30/2006 | 01/29/2007 | ML07037019 | <strong>Automatic Actuation of Both Motor Driven Auxiliary Feedwater Pumps after Local Reset of the 21 Main Feedwater Pump During Corrective Maintenance and Troubleshooting of the Turbine Governor Valve</strong><br /><i>Abstract:&nbsp;</i>While in Hot Standby for an outage, a local reset of the 21 Main Boiler Feedwater Pump (MBFP) turbine resulted in an automatic actuation signal to start both motor driven Auxiliary Feedwater Pumps (AFWP) and isolation of steam generator blowdown. At the time of the event both AFWPs were in operation, and both MBFPs isolated and secured. Troubleshooting was being performed on the 21 MBFP turbine high pressure steam governor valve. After corrective maintenance was completed, control room (CR) operators attempted unsuccessfully to reset the 21 MBFP. Subsequently, Maintenance locally reset the 21 MBFP and an auto start signal was initiated for actuation of the AFWPs and isolation of blowdown. Continuing work activities resulted in another AFWP actuation and blowdown isolation. The direct cause of the AFWP actuation was a signal from the 21 MBFP trip circuit as sensed by a pressure switch from the MBFP turbine control oil system. The root cause was proceeding with the work and not stopping work activities after the CR reset failed and continuing the reset locally. Contributing causes were identified for the root cause and those contributing causes and corrective actions are included in the corrective action program (CAP). Corrective actions (CAs) for the direct cause of the AFWP actuation include dynamic testing of the MBFP auto stop oil pressure switch and testing of MBFP Lovejoy controls. Any necessary CAs as a result of the testing will be implemented in accordance with the CAP. The event had no effect on public health and safety.
2472006007 | Indian Point 2 | 12/05/2006 | 02/05/2007 | ML07045022 | <strong>Plant in a Condition Prohibited by Technical Specifications due to Operation of Containment Pressure Relief Valves While Surveillance Requirement Not Met</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2006 at approximately 0923 hours, Engineering determined that Containment isolation valves for the Containment pressure relief line had been inoperable but not closed and deactivated or operated under administrative controls contrary to Technical Specification (TS) requirements. This appears to have occurred several times since at least August 8, 2006, when stroke timing anomalies were identified during quarterly stroke testing. The direct cause of the TS prohibited condition was failure of the containment relief valves to be limited to the TS maximum stroke of 60 degrees open and failure of the containment relief valves to close within the specified Inservice Testing Program stroke time requirement. The apparent cause is the dislodging of the travel stop retaining clip due to a poor design that can lead to uneven loading of the travel stop plate. This can occur initially or through wear of the retaining clips and grooves during normal usage. Corrective action was taken to repair the valves, augment the maintenance procedure (by providing design details and inspection requirements), and implementation a modification of the travel stop design to provide a more reliable design. There was no significant safety hazard since the valves were capable of performing their safety function.
2492006001 | Dresden 3 | 11/12/2006 | 04/09/2007 | ML07107031 | <strong>Unit 3 Main Steam Safety Valves Exceed Surveillance Setpoint</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2006, with Unit 3 in a refuel outage, Dresden Nuclear Power Station Unit 3 was notified that vendor testing had identified three of the four Main Steam Safety Valves removed from the unit during this outage had exceeded their Technical Specification allowable as-found lift setpoint tolerance of plus orminus 1 percent. One of the valves lifted above the allowable lift setpoint tolerance by 0.1 percent and two of the valves lifted below their allowable lift setpoint tolerance by 1.4 percent and 1.5 percent. Additionally, a Target Rock Safety/Relief Valve also removed during the Unit 3 refuel outage, was tested on February 7, 2007 and lifted above the allowable lift setpoint tolerance by 1.9 percent. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plants Technical Specifications," and 10 CFR 50.73(a)(2)(vii)(D), "Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to mitigate the consequences of an accident. The cause of the event was attributed to setpoint drift. The corrective action to address this issue had been previously initiated. On June 2, 2006, Dresden Nuclear Power Station submitted a request for a change to the Technical Specifications for Units 2 and 3 to increase the allowable as-found Main Steam Safety Valve lift setpoint tolerance from plus or minus 1 percent to 3 percent. This change is currently under review by the Nuclear Regulatory Commission.
2502006001 | Turkey Point 3 | 03/12/2006 | 05/11/2006 | ML06143035 | <strong>Core Alterations without Direct Communications</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2006 at 21:37 with Turkey Point Unit 3 in mode 6, Core Alterations commenced in the form of unlatching the control rods. Shortly thereafter, there were communication problems (headsets cutting out). The decision was made to utilize radios set to a dedicated channel. On March 12, 2006, at approximately 400 hours, the plant commenced removal of the upper reactor vessel (RV) internals. This evolution is considered a Core Alteration as defined in the Technical Specifications (TS). TS 3.9.5 states "Direct communications shall be maintained between the control room and personnel at the refueling station." The Shift Manager had granted permission to lift the upper internals, based upon communications having been previously tested and assumed that communications would be re-established just prior to the actual lifting of the upper internals. The Shift Manager (SM) was monitoring the evolution via video monitors and recognized that communications had not been established and immediately paged the Senior Reactor Operator (SRO) inside containment at the refueling station to re-establish communications. However, since the evolution was in progress, the SRO inside containment completed the evolution and placed the RV internals on its stand, and then responded to the page from the Shift Manager. This event was a TS 3.9.5 violation for having performed Core Alterations without first establishing direct communications between the Control Room and the Refueling Station SRO. There was no adverse impact on the health and safety of the public due to this event.
2502006002 | Turkey Point 3 | 03/05/2006 | 10/09/2006 | ML06292010 | <strong>As-Found Cycle 21 Main Steam Safety Valve Setpoint Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2006, Turkey Point Unit 3 was in Mode 1 and holding at approximately 50 percent reactor power while performing Technical Specification surveillance testing of the Main Steam Safety Valves setpoints, just prior to the Unit 3 Cycle 22 Refueling Outage. The Unit 3 C Steam Generator (SG) MSSV, RV-3-1412, as-found lift pressure was 1154.6 psig, which was greater than the TS allowable setpoint pressure of +/- 3% of 1115 psig (1081.6 psig - 1148.4 psig). RV-3-1412 was declared inoperable and the plant entered TS action statement 3.7.1.1.b. Reactor power was at 50%, which was below the 53% reactor power required per TS 3.7.1.1.b. The valve was subsequently adjusted and retested twice to within +/- 1% of its required setpoint. In addition, the Unit 3 B SG MSSV, RV-3-1406, as-found lift pressure was 1154 psig, outside the TS allowable setpoint of +/- 3% of 1100 psig (1067 psig - 1133 psig). The cause of the failure to meet TS allowable setpoint for RV-3-1412 was a slow build-up of corrosion between the disc holder/guide interface and/or the spring/spring washers. The cause of the failure to meet TS allowable setpoint for RV-3-1406 was micro-bonding. During the planned Unit 3 refueling shutdown which commenced on March 5, 2006, the valves were either replaced with a spare or, the original valve was disassembled and repaired. Operation of the facility with the Main Steam Safety Valves as-found settings was within analytical bounds; therefore, this event had no impact on the health and safety of the public.
2502006003 | Turkey Point 3 | 03/06/2006 | 05/05/2006 | ML06136021 | <strong>Failure of RHR MOV 3-744B, Cold Leg Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2006, at approximately 0840, with Unit 3 in Mode 4 during a refueling outage, Motor Operated Valve MOV-3-744B failed to open in response to a manual demand signal. Subsequent investigation determined that its power supply breaker 30613 had tripped. With power restored, MOV-3-744 indicated mid-stroke via dual position indicating lights. Reports from Operations personnel indicated that the valve moved far enough on the initial demand for the position indicating light to change from closed to mid-position. On March 7, 2006, the valve was manually opened via the hand wheel and the motor was removed from the operator. Upon inspection, the rotor fins had damaged the windings in two places and caused an electrical fault that tripped the breaker. The motor was sent to an independent vendor who reported that the failure was due to corrosion of the magnesium rotor fins and shorting bar. The failed motor was replaced on March 10, 2006. It was determined that the valve would most likely have failed on demand, while operating at power. The valve was considered inoperable at some time during the operating cycle. This condition was in violation of Technical Specification 3.5.2.e, which requires two OPERABLE flow paths capable of taking suction from the containment sump. The event caused no adverse impact on public health or safety.
2502006004 | Turkey Point 3 | 03/08/2006 | 11/24/2006 | ML06342006 | <strong>Emergency Diesel Generator Automatic Actuation due to Loss of Power to a Vital Bus</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2006 at approximately 1553, loss a of the Unit 3 3A 4 kV electrical distribution bus occurred during restoration of the 3C load center (LC) following outage maintenance. The 3A load sequencer performed bus load stripping and a loss of offsite power to the 3A bus occurred due to a degraded voltage condition that was sensed on the 3C LC. This was caused by a misaligned auxiliary switch contact on the newly refurbished 3C 480V LC feeder breaker (30302). The 3A emergency diesel generator automatically started and restored power to the 3A bus; however, the 3C LC 4 kV supply breaker (3AA14) failed to close due inadequate contact wipe on normally closed relay contacts. Core cooling was reestablished at approximately 1600 utilizing the 3B residual heat removal (RHR) pump. The cause was vendor human error during breaker refurbishment of the 3C LC breakers (30302 and 3AA14) which went undetected by the vendor test and inspection programs and Turkey Point pre-installation checks. Corrective action includes: For breaker 30302, the breaker refurbishment standard revised the final test and inspection procedure to record as left auxiliary switch contact configuration and compare it to the as found configuration (checks to be independently verified). For breaker 3AA14, the procurement specification and applicable receipt inspection procedure for HMA relays have been revised to verify adequate contact wipe by vendor and receipt inspection personnel, respectively. The increase in risk due to loss of core cooling is judged to be very small given the availability of the redundant RHR pump and power source, and the short period for restoration of cooling.
2502006005 | Turkey Point 3 | 03/08/2006 | 07/28/2006 | ML06220050 | <strong>Ground Test Devices Installed in Startup Transformer Output Breakers Cause Unit 3 EDGs to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2006 at approximately 1553, a loss of power to the Unit 3 3A 4 kV electrical distribution bus occurred. The 3A emergency diesel generator (EDG) automatically started and restored power to the 3A bus. At approximately 0400 on March 9, 2006, while reenergizing the 3A 4 kV bus from the Unit 3 auxiliary transformer, Operations personnel suspected the 3A EDG to be in droop mode, since EDG speed decreased as loads were applied to the bus, which required frequency adjustments. Maintenance personnel confirmed both Unit 3 EDGs were configured to operate in droop mode, since required jumpers were not installed when ground test devices (GTD) were installed in the startup transformer output breakers. The 3A and 3B EDGs were declared inoperable at approximately 0550 and declared operable at approximately 0615 after installation of the jumpers. The cause was determined to be the use of an incorrect plant procedure for grounding the startup transformers. Subsequent to the event, a modification was completed that eliminates the need to install jumpers in the Unit 3 startup transformer breaker cubicles when GTDs are installed. Procedure requirements will be established to help ensure the appropriate component-specific procedure is used for grounding startup transformers. As a result of degraded EDG output in droop mode, supported equipment performance capability was also degraded; however, valid assumptions for event and accident analyses were maintained. Assessment results show that no acceptance criteria or limits would be exceeded if any design basis events were to occur while the Unit 3 EDGs are in the droop mode of operation.
2502006007 | Turkey Point 3 | 05/03/2006 | 10/13/2006 | ML06297024 | <strong>Age-Related Capacitor Failure Causes One Low Pressurizer Pressure Protection Channel to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2006, during the performance of a surveillance test one of three channels of the low pressurizer pressure protection instrumentation was found out of specification and inoperable. The instrument logic is two-out-of-three. It was subsequently determined through evaluation that channel 1 was most likely inoperable from March 6, 2006 until subsequently repaired after the May 3, 2006 surveillance test. An age-related failure of a power supply filter capacitor for comparator module PC-3-455E caused excessive noise in the channel and the output fuse for comparator PC-3-455B to blow during a reactor pressure change when the comparator setpoint was reached. Corrective action included the replacement of comparator module PC-3-455E and the blown fuse for comparator PC-3-455B. A subsequent surveillance test was satisfactorily passed. A Hagan module replacement program has recently been approved and will be implemented in phases. Since the other two low pressurizer pressure instrumentation channels remained operable to ensure the required functions of safety injection (SI) and SI block were met, the safety significance of this event is very low due to the reduced redundancy and susceptibility to a single failure.
2502006008 | Turkey Point 3, Turkey Point 4 | 11/01/2006 | 12/21/2006 | ML06363003 | <strong>Incorrect Emergency Diesel Fuel Oil Testing Program Surveillance Implementation</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2006, during a review of the Diesel Fuel Oil Testing procedures, it was discovered that procedure 0-NCAP-015.4, Fuel Oil Clear and Bright Determination, did not measure proper color. Technical Specification (TS) surveillance requirement 4.8.1.1.2.e. requires the new diesel fuel oil to be tested and verified in accordance with the Diesel Fuel Oil Testing Program. The Diesel Fuel Oil Testing program in TS 6.8.4.e requires that prior to adding new fuel to the storage tanks the sample has been tested in accordance with the American Society for Testing and Materials (ASTM) D4176-82 and verified to have a clear and bright appearance with proper color. This standard is valid for petroleum products with an ASTM color of 5 or less. Contrary to the TS and the ASTM standard, proper color was not verified during the performance of the clear and bright test. The cause of the event was failure to recognize and implement the specific test requirements for proper color. Other contributing factors are lack of technical rigor and lack of sufficient details in the procedures. The procedures have been revised to include the ASTM standard specific testing requirements for proper color and Chemistry Technicians have been trained to the ASTM standards. This condition is reported in accordance with 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by the TS. The health and safety of the public were not affected by this event.
2512006001 | Turkey Point 4 | 11/28/2006 | 01/29/2007 | ML07044014 | <strong>Containment Purge Penetration Fails Leak Rate Test due to Inadequate Preventive Maintenance on Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2006, while attempting to perform the local leak rate test (LLRT) of the Unit 4 containment purge exhaust penetration (36), the penetration was observed to be leaking excessively as it could not be pressurized. Subsequent investigation determined that power-operated containment isolation valve POV-4-2602 was not fully closed. The cause of the event is inadequate preventative maintenance. Penetration 36 failed its LLRT because the valve disc for POV-4-2602 was not fully closed. Corrosion in the actuator bearing surfaces created friction that exceeded actuator closing capability. It was conservatively determined that POV-4-2602 was inoperable from the last time it was stroked for a position indication surveillance on October 14, 2006. From October 27, 2006 to October 30, 2006, a containment purge was in progress in preparation for a refueling outage shutdown. As a result, a Technical Specification action requirement for an inoperable purge valve was not met. Immediate corrective actions included the lubrication of the actuator bearing surfaces, an increase in spring preload providing added closing force, and the installation of a valve disc travel stop. To prevent recurrence, a refueling outage preventive maintenance activity will be added to lubricate the bearing surfaces, and overhauls have been scheduled for POV-4-2602 and its counterpart on Unit 3 (POV-3-2602) during the next refueling outage for each unit. Since the redundant containment purge exhaust isolation valve (POV-4-2603) was operable, the safety function of containment penetration isolation was maintained.
2512006002 | Turkey Point 4 | 12/04/2006 | 03/29/2007 | ML07093042 | <strong>Intermediate Range High Flux Trip Setpoint Exceeded Technical Specification Allowable Value</strong><br /><i>Abstract:&nbsp;</i>On December 4, 2006, prior to Low Power Physics Testing on Unit 4 for Cycle 23, the Intermediate Range (IR) detector setpoints for amps equivalent to 25% power trip and 20% rod stop were questioned and found to be non-conservative for N-35. The setpoint for N-35 would have exceeded the Technical Specification (TS) Table 2.2-1 allowable value. The primary cause of the event was determined to be inadequate change management with respect to changing the detector housing from aluminum to titanium for the IR detector. This design change affected the operating characteristics in the as-installed condition that were not recognized by the vendor or the plant staff. The change was made in the refueling outage prior to Unit 4 cycle 22. The new detector was installed and new setpoints were calculated. Station engineering personnel failed to recognize that the installed setpoint value exceeded the TS 2.2 Allowable Value of 31%. The unit ascended in power in violation of TS 3.3.1 for having one less than the minimum channels operable. Review of the Unit 4 operating history revealed that N-35 was recalibrated once the unit reached 100% equilibrium conditions. To prevent recurrence, the procedure for validating IR trip setpoints will require comparison of installed values to TS limits.
2542006001 | Quad Cities 1 | 01/04/2006 | 05/02/2007 | ML07129005 | <strong>Failure of the Unit 1B Core Spray Pump Breaker to Operate due to Racking Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2006, during performance of the quarterly Core Spray (CS) system flowrate surveillance, the Unit 1B CS pump breaker did not close to start the CS pump. The 1B CS system was declared inoperable and a 7-day Completion Time was entered in accordance with Technical Specification 3.5.1, Condition B. The cause of the failure of the breaker to close was poor contact between the breakers secondary disconnect pins and the secondary disconnect slides of the cubicle. This was due to the breaker not being fully racked into the connect position, and misalignment of the secondary disconnect slides and pins. The breaker was racked out to permit an inspection of the cubicle and breaker, racked back in and verified to operate. Other similar breakers were visually inspected to ensure they were properly racked in. The safety significance of this event was minimal. Other than for normal maintenance and surveillance, the remaining Emergency Core Cooling Systems were operable. The breaker racking procedure has been revised to provide additional guidance.
2542006002 | Quad Cities 1 | 02/22/2006 | 04/14/2006 | ML06111037 | <strong>Automatic Reactor Scram from Turbine/Generator Load Reject due to Degraded Current Transformer Wiring on the Main Power Transformer</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2006, at 0122 hours, an automatic reactor scram occurred on Unit 1 in response to a turbine/generator load reject due to a trip of the main power transformer (MPT) B phase differential overcurrent relay. The relay trip was caused by degraded wiring insulation, resulting in a ground in the current transformer C phase wiring at a box mounted on the MPT. The degraded wiring insulation resulted in a direct short to ground and resultant trip of the protective differential overcurrent relay. All control rods inserted to the full-in position. The reactor was brought to the hot shutdown condition using normal methods and was maintained in hot shutdown during investigation and repair of the MPT issue until the reactor was returned to power operation on February 24, 2006. The degraded wiring insulation was caused by inadequate MPT wiring assembly design and installation. Corrective actions include repair of degraded wiring, inspection of accessible wiring and design changes.
2542006003 | Quad Cities 1 | 05/14/2006 | 11/20/2006 | ML06332051 | <strong>Unexpected Start of the Division II Emergency Diesel Generator due to Failure to Open Test Switch</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2006, at 0957 hours, an unexpected start of the Unit 1 Division II Emergency Diesel Generator (EDG) occurred when the EDG control switch was put in the "AUTO" position. At the time of the event, Unit 1 was in an abnormal electrical lineup such that the Division II emergency bus was de-energized to allow testing of the Reserve Auxiliary Transformer. The Operations crew believed that the previous crew had opened the three required test switches. The previous crew had opened two of the switches, but had not realized that the third switch was required to be opened. The cause of this event was that the crews did not take prudent measures to ensure all activities in progress were integrated into their awareness of plant status. The safety significance of this event was minimal. This event occurred while the unit was shut down for a refueling outage. The crew immediately recognized that the automatic start was inappropriate and shut down the EDG. The division EDG was operable throughout the event. Corrective actions include establishment of formal guidance for use of the Procedure in Progress (PIP) book, training concerning Technical Human Performance, a revision to the shift Turnover Checklist to require review of the PIP book, and clarified expectations concerning use of non-carded Clearance Order steps.
2542006004 | Quad Cities 1 | 10/12/2006 | 12/11/2006 | ML06353035 | <strong>Through-wall Leak in Standby Liquid Control Tank due to the Original Construction Use of Grout with Leachable Halogens</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2006, at 2236 hours, the Unit 1 Standby Liquid Control (SLC) system was declared inoperable due to a through-wall leak in the SLC tank. Although the SLC tank is exposed to atmospheric pressure, it is an ASME Code Section XI Class 2 boundary. The SLC tank leak was originally identified on May 27, 2004, but the ASME Code Class of the SLC tank was not identified, and the SLC tank was incorrectly determined to be operable at that time. On October 13, 2006, the NRC approved a Notice of Enforcement Discretion to extend the Allowed Outage Time for the inoperable SLC system. On October 15, 2006, following draining, repair, refilling and testing of the tank, the SLC system was declared operable. The SLC tank leak was due to the use of grout material containing leachable halogens during original installation of the SLC tank supports, resulting in an environment that supported stress corrosion cracking in the stainless steel tank where it was in contact with the grout. The safety significance of the event was minimal. The leak was extremely small and did not affect the capability of the SLC tank to perform its safety function. Corrective actions include development of issue review guidance, redesign of the SLC tank supports, and review of systems for the use of grout.
2552006001 | Palisades | 02/14/2006 | 04/14/2006 | ML06107009 | <strong>Potential Loss of Primary Coolant Makeup Function for Postulated Fire Scenario</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2006, during review of a 10 CFR 50, Appendix R analysis, a condition was identified that could challenge the ability to maintain the primary (reactor) coolant makeup function, as required by Appendix R, paragraph III.G, "Fire Protection of Safe Shutdown Capability." In the analysis, the specific fire scenario is assumed to render all charging pumps unavailable for maintaining the primary coolant makeup function. To compensate for the loss of all charging pumps, the analysis credited high pressure safety injection pump (HPSI) P-66B for supplying makeup. However, the review determined that the fire scenario could also result in damage to the control circuit for the HPSI pumps credited suction valve, CV-3031, resulting in a spurious closure of the valve. The spurious closure of the HPSI pumps suction valve with the HPSI pump in operation would likely render the HPSI pump inoperable, causing a loss of the ability to maintain the primary coolant makeup function. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition.
2552006002 | Palisades | 03/26/2006 | 05/23/2006 | ML06144009 | <strong>Main Steam Safety Valves Exceeded Lift Setpoint Acceptance Band</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2006, with the plant in Mode 1, in-place testing of main steam safety valve RV-07 determined that the as-found lift pressure did not meet the acceptance band of +/- 3% of setpoint, as specified by Technical Specification Table 3.7.1-1, "Main Steam Safety Valve Lift Settings." This was the second unsatisfactory as-found lift pressure for a main steam safety valve, as in-place testing on March 25, 2006, had previously determined that RV-0707 had failed to meet the as-found acceptance band. Technical Specification LCO 3.7.1 requires a minimum of 23 out of 24 main steam safety valves to be operable in Modes 1, 2 and 3. Since the cause of the two unsatisfactory as-found lift pressures may have arisen over a period of time, it is assumed that the required number of main steam safety valves was not operable during past plant operation. Therefore, this occurrence is considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plants Technical Specifications. The safety significance of this occurrence is considered minimal.
2552006003 | Palisades | 03/29/2006 | 05/26/2006 | ML06150007 | <strong>Completion of Plant Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2006, with the plant in Mode 1, left train high pressure safety injection system subcooling control valve CV-3070 failed to stroke open during a preventive maintenance activity, resulting in entry into Technical Specification (TS) LCO 3.5.2.B.1, for the inoperability of one Emergency Core Cooling System (ECCS) train. On March 31, 2006, a shutdown was commenced when it was determined that the 72-hour completion time for restoring CV-3070 to operable status could not be met. On April 1, 2006, the shutdown was completed in accordance with TS LCO 3.5.2.C.1 and 2 required actions. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A) as the completion of any nuclear plant shutdown required by the plant's Technical Specifications. The failure of CV-3070 occurred from excessive valve stem interference that resulted from inadequate support of CV-3070's air operator, which occurred as a result of removal of a support hanger. Valve components for CV-3070 were subsequently replaced. A support hanger has been reinstalled to support the valve's air operator.
2552006004 | Palisades | 05/04/2006 | 06/28/2006 | ML06179058 | <strong>Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2006, with the plant in Mode 5, an actuation of the reactor protection system (RPS) occurred during performance of startup testing activities. The RPS actuation signal was generated from activation of the 'A' steam generator low level trip circuitry. At the time of occurrence, a slight nitrogen overpressure of approximately 1.3 psi was being maintained on the secondary side of 'A' steam generator for chemistry control, as is typical for idle steam generators when in Mode 5. Subsequently, when the main steam isolation valves were opened to support a planned test activity, a sudden release of the nitrogen overpressure in `A' steam generator occurred. This resulted in a momentary level oscillation within 'A' steam generator between the tube bundle region and the downcomer region where steam generator level is measured. While there was no loss of water inventory from A steam generator, level in the downcomer region oscillated approximately 15% above and below the initial indicated level of approximately 40%. Since the RPS trip setpoint for low steam generator level is approximately 28%, the magnitude of the level oscillation was sufficient to exceed the RPS trip setpoint.
2552006005 | Palisades | 05/10/2006 | 07/07/2006 | ML06192008 | <strong>Uncoupled Control Rod</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2006, an unexpected quadrant power tilt was identified during reactor core startup physics testing. At the time of discovery, plant power was being maintained at approximately 22% following initial power ascension from a recently completed refueling outage. Subsequent analysis determined the most probable cause of the quadrant power tilt to be Control Rod 33 fully inserted into the core as opposed to being fully withdrawn as indicated. A shutdown was initiated to facilitate further troubleshooting. The reactor was manually tripped from approximately 11% power. On May 13, 2006, investigation determined that Control Rod 33 was uncoupled from its drive assembly, having not been successfully coupled during the refueling outage. Consequently, Control Rod 33 had remained fully inserted into the core throughout plant startup from the refueling outage. Prior to discovery, the upward mode changes into Mode 2 and Mode 1 that occurred on May 9 and May 10, 2006, respectively, were performed in violation of Technical Specification (TS) 3.0.4, since the intent of TS 3.1.4.D.1 is to prevent a reactor startup with an immovable control rod. Consequently, this event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation which was prohibited by Technical Specifications. In addition, the manual reactor protection system actuation is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A).
2552006006 | Palisades | 11/01/2006 | 12/15/2006 | ML06361018 | <strong>Inoperable Containment due to Containment Air Cooler Through-Wall Flaw</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2006, with the plant in Mode 1, a small service water leak (approximately 0.4 gallons per minute) was identified in VHX-4 containment air cooler (CAC). Although the specific location of the through-wall flaw could not be verified due to physical constraints, the leak is assumed to be from a pin-hole in a single cooling coil tube. The CAC cooling coil tubing is part of the containment boundary and is required to be structurally sound to ensure that post accident containment leakage will not exceed allowable leakage. Therefore, Technical Specification (TS) Limiting Condition For Operation (LCO) 3.6.1, "Containment," is applicable for any through-wall defects noted in CAC cooling coil tubing. Since it was not possible to characterize the flaw and verify the structural integrity of the tube for post-accident conditions over the CAC's mission time, the plant was taken to Mode 3 in accordance with TS LCO 3.6.1.B.1. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A) as the completion of a shutdown required by plant Technical Specifications and 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2552006007 | Palisades | 11/03/2006 | 12/15/2006 | ML07003050 | <strong>Auxiliary Feedwater Control Switches Not Positioned for Automatic System Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2006, with the plant in Mode 2, it was discovered that control switches associated with both trains of the auxiliary feedwater (AFW) system were not aligned as required for automatic system actuation. In the as-found control switch configuration, an auxiliary feedwater actuation signal (AFAS) would not have automatically actuated AFW system components. Investigation determined that the control switches had been positioned in the noted alignment two days prior, with the plant in Mode 3. At the time of discovery, and throughout the period during which the switches were not aligned for automatic actuation, one train of AFW was in operation providing the heat removal function. However, in the event of a postulated AFAS and loss of off-site power event, the motor-driven AFW Pump in the operating train would not have been automatically re-powered by the associated emergency diesel generator as it re-energized loads. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. In addition, the occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(vii)(B) as a condition that could have prevented the fulfillment of the safety function of a system that is needed to remove residual heat.
2552006008 | Palisades | 11/29/2006 | 01/26/2007 | ML07037035 | <strong>Inoperable Containment due to Containment Air Cooler Through-Wall Flaw</strong><br /><i>Abstract:&nbsp;</i>On November 29, 2006, with the plant in Mode 1, a small service water leak (approximately 0.1 gallons per minute) was identified in VHX-4 containment air cooler (CAC). The leak was subsequently determined to be from a pin-hole in a single cooling coil tube at the H-bend fitting. The CAC cooling coil is a part of the containment boundary, and is required to be structurally sound to ensure that post accident containment leakage will not exceed allowable leakage (La). Therefore, Technical Specification Limiting Condition For Operation 3.6.1, "Containment," is initially applicable for any through-wall defect noted in a CAC cooling coil. Although the size of the identified pin-hole would not have challenged La, it was not possible to characterize the flaw to verify the operability of the cooling coil for post-accident conditions over the CAC's mission time. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2612006001 | Robinson 2 | 10/25/2006 | 12/21/2006 | ML06363004 | <strong>Manual Reactor Trip due to Failure of a Turbine Governor Valve Electro-Hydraulic Control Card</strong><br /><i>Abstract:&nbsp;</i>At 0247 hours on October 25, 2006, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 100% power, control room operators responded to alarms received for steam flow greater than feed flow on all three steam generators. Turbine first stage pressure indicated 0 psig. Three of the four turbine governor valves indicated closed, the fourth indicated an intermediate position. The control rods began automatically inserting, as expected. The net megawatt recorder indicated that electrical generation had rapidly reduced from 742 to 0 megawatts. The control room operators diagnosed the event as a 100% load rejection and initiated a manual reactor trip at 0248 hours, 68.8 seconds following the start of the event. The root cause of this event was failure of a turbine governor valve electro-hydraulic control system card. A pressurizer power operated relief valve lifted and reseated during the event. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
2632006001 | Monticello | 02/01/2006 | 04/03/2006 | ML06094013 | <strong>Unplanned LCO due to Emergency Filter Flexible Connector Failure</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2006 at 2300 with the unit operating at 100% power, the unit "A" train (V-ERF-11) of the Emergency Filtration (EFT) system tripped. Investigation found that the rubber boot between the filter unit and the suction of the fan had ripped resulting in a low flow condition through the filter. The low flow condition initiated an automatic trip of the operating unit. Due to the back leakage through the tear in the "A" filter boot and in order to perform an extent of condition review, the "B" train (V-ERF-12) of the EFT system was declared inoperable. The station entered a 24-hour LCO for both trains being inoperable at 2300. A manual damper was closed to isolate the potential in-leakage from the "A" train to the "B" train. An extent of condition review of the "B" unit boot was completed and the "B" EFT system was declared operable at 0302 on February 2, 2006. The 24-hour LCO was exited at 0302. An eight hour ENS notification was made to the NRC at 0351 on February 2, 2006 in accordance with 10 CFR 50.72(b)(3)(v)(D). The replacement of the boots on EFT Train "A" and "B" were completed on February 2, 2006. The cause of the event was failure by the station to consider the effect of changing operating conditions on the Preventive Maintenance (PM) frequency for V-ERF-11 and -12. The station has replaced the rubber boots on both EFT trains and will revise the PM frequency for future replacements of the rubber boots.
2632006002 | Monticello | 05/27/2006 | 05/11/2007 | ML07141019 | <strong>Unplanned LCO due to Loss of Cooling in the Upper 4KV Room</strong><br /><i>Abstract:&nbsp;</i>Note: The LER is being revised to correct the cause of the event based on completion of the cause evaluation. On May 27, 2006, multiple trips of the 4KV switchgear room chiller (V-CH-27) resulted in the room temperature exceeding 104F in the Division II 4KV switchgear room. The Abnormal Operations Procedure, "Ventilation System Failure", required the affected division of 4KV switchgear to be declared inoperable at temperatures greater than 104F in the switchgear area. In addition, the procedure directs opening various turbine building High Energy Line Break (HELB) doors to promote room cooling. Consequently with HELB doors open to the Division II switchgear room, a single postulated HELB could render portions of both electrical divisions inoperable, resulting in no safe shutdown path available for the HELB of concern. The cause of this event was a failure of a chiller fan [FAN] motor [MO]. The chiller failure resulted in implementation of an abnormal operating procedure that directed operator actions which rendered the plant susceptible to a postulated HELB that could have caused the loss of portions of both safety related electrical divisions. Corrective actions include repairing the chiller unit and revising station procedures.
2652006001 | Quad Cities 2 | 04/10/2006 | 07/27/2007 | ML07219059 | <strong>Two Main Steam Safety Valves and Two Main Steam Safety/Relief Valves Outside of the Technical Specification Allowed Tolerance</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2006, at approximately 1400 hours, Quad Cities Nuclear Power Station determined that two of the four removed Main Steam Safety Valves (MSSVs) and the Main Steam Safety/Relief Valve (SRV), all removed from Unit 2 during the Spring 2006 refueling outage (QR 18), and the SRV removed during a planned outage in April of 2005 (Q2P03), had been found during as-found testing to have lift set pressures outside of the +/-1% Technical Specification (TS)-allowed tolerance. Both SRVs were also outside of the +/-3% ASME Code tolerance. The cause of these events is setpoint drift. No mechanical wear, degradation or foreign material was identified for the two MSSVs and the SRV removed during Q2R18, or for the SRV removed during Q2P03. All four of the removed MSSVs and the SRV were replaced during Q2R18 with newly refurbished valves that were certified to be within the +/-1% TS-allowed tolerance. Quad Cities Nuclear Power Station is pursuing a revision to the TS-allowable value for the MSSVs and SRVs to reflect the ASME code allowable.
2662006001 | Point Beach 1, Point Beach 2 | 05/30/2006 | 07/28/2006 | ML06220049 | <strong>Control Room Emergency Filtration System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2006, testing was conducted on the F-16, Control Room Charcoal/HEPA/Roughing Filter, per Technical Specification (TS) 5.5.10.c, "Ventilation Filter Testing Program." A sample of the charcoal was sent to NUCON for methyl iodide penetration testing. On May 30, 2006, at 0923 the Control Room Emergency Filtration System (CREFS) was declared inoperable based on failure of the charcoal to meet the methyl iodide penetration acceptance criterion of <1.0%. Units 1 and 2 entered TS LCO 3.7.9, "Control Room Emergency Filtration System (CREFS)," Condition A, "CREFS Inoperable," with a Required Action of "Restore CREFS to OPERABLE status." The F-16 charcoal filter trays were replaced and retested. A second failure occurred due to penetration and system bypass test exceeding allowable limits. The filters were replaced again and the degraded Sealant (RTV) repaired. Subsequent testing on June 3, 2006, demonstrated compliance with TS 5.5.10.b, TS 5.5.10.c, and TS 5.5.10.d. Operations exited the CREFS TSAC June 4, 2006, at 2030. CREFS is a single train system. Based on the guidance in NUREG-1022 for a single train system that performs a safety function, this condition was determined to be reportable per 10 CFR 50.73(a)(2)(v), "Event or Condition That Could Have Prevented Fulfillment of a Safety Function." Technical Specifications allow for this system to be inoperable for a period of seven days.
2692006002 | Oconee 1, Oconee 2, Oconee 3 | 03/29/2006 | 05/25/2006 | ML06153030 | <strong>High Energy Line Breaks Outside Licensing Basis May Result in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER to address certain postulated High Energy Line Break (HELB) event scenarios for Oconee Nuclear Site (ONS). These scenarios are outside the Current Licensing Basis (CLB) but potentially could result in loss of the High Pressure Injection System, which is credited for mitigation of HELB events, due to flooding caused by the event. This issue was discovered due to discussion with NRC inspectors about errors in crediting certain drain flow paths in existing analyses. The errors resulted from an inaccurate drawing, an inadequate field walkdown, and misinterpretation of drawings of inaccessible areas. Corrective actions include correction of the drawings and analyses. Additional actions are expected as a result of a long term project to enhance the plant and CLB to address risk significant HELB issues at ONS. This event is considered to have no significance with respect to the health and safety of the public.
2692006003 | Oconee 1, Oconee 2, Oconee 3 | 06/01/2006 | 05/29/2008 | ML08156065 | <strong>Foreign Objects Discovered in RBES Outlet Piping</strong><br /><i>Abstract:&nbsp;</i>Video inspection of the Reactor Building Emergency Sump (RBES) outlet pipes on all three Oconee units were performed with the units in cold shutdown. The inspections discovered the presence of foreign materials, including various hardware items such as two nuts, a washer, a nail, an O-Ring, and a piece of an adjustable wrench. These materials were evaluated as capable of damaging one or more Low Pressure Injection (LPI) Pumps in Unit 2 and 3 or one or more Reactor Building Spray (BS) Pump in each unit. Foreign material described above was removed prior to re-starting the units. The material was present for an unknown period of time. Past operability evaluations performed by Oconee Nuclear Station initially concluded that the debris found in Unit 2 was not capable of causing inoperability of any components. However, subsequent evaluation by the NRC reached a conclusion that reasonable assurance had not been provided to show that the 2B LPI Pump would have remained operable. A licensee-identified NCV (green finding) was issued, which ONS did not contest. Inspections on Units 3 and 1 were performed after the NRC finding was issued. NRC evaluation of the Unit 3 findings concluded that LPI function could have been lost. NRC safety significance evaluation determined the change in CDF was between 1E-5 and 1E-6, and a white finding was issued by the NRC. Again, Duke did not contest this finding.
2692006004 | Oconee 1, Oconee 2, Oconee 3 | 06/03/2005 | 05/13/2009 | ML09139064 | <strong>Design Oversight Results in Appendix R Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Licensee Event Reports 269/2002-02 (5-28-2002) and 269/2003-01 (8-4-2003) reported vulnerabilities to hot shorts and other Appendix R design deficiencies. As a result of the corrective actions from the first event, Oconee Nuclear Station initiated an Appendix R reconstitution program and subsequently elected to participate in the pilot NFPA 805 transition program. The original Appendix R evaluations considered spurious operation of many analyzed components to not be credible and assumed components would lose power, thus precluding spurious operation. However, the Current Licensing Basis requires that plant transients caused by one worst case hot short must be addressed. Between 6-3-2005 and 11-21-2006, the reconstitution program identified and documented in the Oconee corrective action program vulnerabilities to hot shorts which had not previously been considered. These issues involve potential spurious pump starts and spurious valve operations with associated procedure changes needed to address the possible hot shorts. The continuation of the Appendix R reconstitution program and the pilot NFPA 805 transition program will continue to identify and correct these items. This event is of low to moderate significance with respect to the health and safety of the public.
2692006005 | Oconee 1 | 12/09/2006 | 06/06/2007 | ML07164040 | <strong>TS LCO Conditions Not Entered and Required Action Completion Times Not Met Due to Undetected Inoperable LTOP RCS Pressure Indication and Alarms</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2006, with Unit 1 in Mode 3 and Reactor Coolant System (RCS) temperature below 325 F, Limiting Condition for Operation (LCO) 3.4.12 conditions of applicability were entered. This LCO requires two operable trains of Low Temperature Overpressure Protection (LTOP). Prior to entering the conditions of LCO applicability, the RCS narrow range pressure transmitter lead wire to the Operator Aid Computer (OAC) point had been disconnected, making one train of LTOP inoperable. However, the inoperable instrument channel was not detected by the control room operators due to the computer point quality continuing to read "GOOD". Consequently, entry into the applicable LCO conditions was not recognized and the required actions were not taken within the allowed completion times. Therefore, the unit was operated in a condition prohibited by technical specifications. There was no loss of function, as a redundant LTOP train (PORV) remained operable for the duration of the LCO applicability. This event was caused by a latent design error in the instrument loop containing the narrow range RCS pressure transmitter. Immediate corrective action was not required, as the condition was discovered after the period of LTOP applicability had passed. Additional corrective actions have been identified and captured in our corrective action program. This event has no significance with respect to public health and safety.
2702006001 | Oconee 2 | 04/12/2006 | 06/12/2006 | ML06171047 | <strong>Loss of Isolation During Pump Instrument Check Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2006, while operating at 100% in Mode 1, Oconee Nuclear Station Unit 2 experienced a reactor trip. The post trip response was normal, with all major operating parameters remaining within expected limits. Operators took appropriate action to stabilize the unit in Mode 3. The cause of the event was determined to be a trip of a reactor coolant pump during testing of a pump power transducer. The pump trip occurred due to a loss of isolation between the power transducer being tested and the operating circuit while connected to the test equipment. Corrective actions address changes to restrict use of this procedure on critical equipment while operating. This event is considered to have no significance with respect to the health and safety of the public.
2722006001 | Salem 1 | 03/08/2006 | 05/03/2006 | ML06136033 | <strong>Salem Unit 1 Turbine Trip - Reactor Trip with Reactor Power Above P-9</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2006 at 1109, with Salem Unit 1 at 100 % power, a turbine trip signal was received in the main control room with an immediate reactor trip. The reactor trip actions and plant recovery were performed without complications. Analysis of computer data indicated that the turbine over speed circuit initiated an overspeed signal at 103% and tripped the main turbine as designed. Turbine speed was a constant 1800-rpm as controlled by the electric grid with the generator synchronized to it. The most probable cause of the turbine trip reactor trip was Radio Frequency Interference (RFI) or Electro Magnetic Interference (EMI) by an unknown source. Some of the corrective actions taken were the following: (1) prohibiting the use of electric tools, radios, cellular phones, portable radios, arc flash welders and other equipment that could result in EMI or RFI in relay rooms and (2) posting warning signs in the effected areas. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B."
2722006002 | Salem 1 | 09/28/2006 | 11/27/2006 | ML06341022 | <strong>Inoperability of the Auxiliary Feedwater System due to a Partially Opened Damper</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2006, Auxiliary Building Ventilation system damper 1ABS20 was discovered to be partially open. This damper is normally closed and opens when the room cooler is in service. The damper is located in the ceiling of the turbine driven Auxiliary Feedwater pump enclosure and exhausts air from the enclosure to the surrounding pump area during room cooler operation. The safety function of the damper is to close in a steamline break inside the enclosure, separating a harsh environment area from a mild environment area. With the damper partially opened and unable to close as designed, the operability of the motor driven Auxiliary Feedwater Pumps could not be established. The failed damper actuator was replaced and the damper was retested satisfactorily. The cause of the failed damper actuator was attributed to a higher than design air pressure supply to the actuator. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications; 10CFR50.73(a)(2)(v)(B), any event or condition that alone could have prevented the fulfillment of a safety function of a system needed to remove residual heat; and 10CFR50.73(a)(2)(ii)(B) an event or condition that resulted in the nuclear power plant, including its principal safety barriers being seriously degraded or in an unanalyzed condition that significantly degrades plant safety.
2752006001 | Diablo Canyon 1, Diablo Canyon 2 | 08/15/2006 | 09/14/2006 | ML06264043 | <strong>Excessive Dead Birds Found at the Pacific Ocean Cooling Water Intake</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2006, during diving operations to clean the bar racks associated with Diablo Canyon Power Plant (DCPP) cooling water intake structure barracks, approximately 100 dead cormorants were discovered. Cormorants are diving sea birds common to the California central coast and often feed in the DCPP intake cove. They have recently started nesting in larger numbers on a large rock at the southern end of the intake cove. On August 15, 2006, at 15:21 PDT, Pacific Gas and Electric Company (PGE) made a nonemergency report in accordance with Facility Operating License Nos. DPR-80 and DPR-82, Appendix B, "Environmental Protection Plan (non-radiological)," Subsection 4.1 as an "Unusual or Important Environmental Event," requiring NRC notification. PGE believes that the birds died of natural causes and collected on the barracks due to the intake cooling water currents, and the event was not related to plant operation. Since the deaths are not believed to be related with DCPP operation, no corrective actions were identified. To help confirm the cause of death, some of the cormorants remains were sent to the California Animal Health and Food Safety Laboratory at the University of California at Davis, California, for testing and analysis. The results the of testing and analysis of the bird remains are expected by the end of October, 2006. The event did not impact plant operations.
2772006001 | Peach Bottom 2 | 09/22/2006 | 11/15/2006 | ML06326004 | <strong>Main Steam Isolation Valves Exceeded Their Allowable Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>On 9/22/06, Engineering Department personnel determined that there were multiple leak rate test failures involving the Main Steam Isolation Valves (MSIVs). This determination was based on local leak rate testing that had been performed over the time period of 9/18/06 to 9/21/06 during the P2R 16 Refueling Outage. Four of the eight MSIVs were found to be leaking in excess of their allowable leakage limits including both the inboard and the outboard MSIVs for the D Main Steam Line. This condition resulted in a degraded plant safety barrier, a condition prohibited by Technical Specifications and a condition that resulted in multiple trains being inoperable in a safety system. The cause of the leakage through the MSIVs was primarily due to the MSIV main poppet not concentrically seating on the in-body MSIV main seating surfaces. The underlying causes and corrective actions to resolve the underlying causes of this event are being finalized in accordance with the Corrective Action Program. The MSIVs were repaired and returned to an operable status. The as-left leakage rates were well below the Technical Specification allowable limits. This event was determined to be not significant from a risk perspective.
2772006002 | Peach Bottom 2 | 09/28/2006 | 11/15/2006 | ML06326004 | <strong>Automatic Depressurization System Safety Relief Valve Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Based on a review of testing performed on Safety Relief Valves (SRVs) during the P2R 16 Refueling Outage, Site Engineering personnel determined that the 71B and 71G SRVs did not meet their allowable leak rate for the pneumatic actuation controls for the Automatic Depressurization System (ADS) feature of the SRVs. Additionally, the 71C SRV, Serial Number (S/N) 83, did not properly re-close on the fourth actuation during laboratory testing. The cause of the 71B and 71G ADS SRV pneumatic leakage is attributed to leakage from each of the SRV's actuator diaphragm and solenoid valve. These leaks only occurred when the SRV solenoid valves were energized. The diaphragms and solenoid valves associated with the 71B and 71G ADS SRVs were replaced. As-left leak testing was performed and the valves were restored to an operable condition prior to plant startup from the P2R 16 Refueling Outage. A refurbished SRV was installed in the 71C SRV location to replace the S/N 83 SRV. There were no actual safety consequences associated with this event. This event was determined to not be risk significant.
2772006003 | Peach Bottom 2 | 10/07/2006 | 12/04/2006 | ML06342005 | <strong>Elbow Leak on Piping Attached to Suppression Pool Results in Loss of Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On 10/7/06 at 1802 hours, an Unusual Event was declared for Unit 2 as a result of the discovery of a leak at an elbow for piping that penetrates the Primary Containment Suppression Pool (i.e. Torus). The 4" piping is the High Pressure Coolant Injection (HPCI) / Reactor Core Isolation Cooling (RCIC) Torus Flush line. This line is normally isolated from the HPCI / RCIC systems by a closed motor-operated valve and is only used during testing activities. The leak was discovered by an equipment operator at approximately 1741 hours during a planned inspection associated with a RCIC system check valve. The leak occurred on the intrados of a 45 degree elbow of the 4" piping. The elbow was located approximately 1 foot above the Torus penetration (i.e. the leak was outside of Primary Containment). The cause of the crack in the elbow is due to cavitation and abrasive erosion and/or localized water-jet cutting resulting from excessively high flow velocities through this piping during test conditions in conjunction with an apparent lack of fusion between the weld backing ring and the weld root at the elbow weld. The leaking elbow was replaced and non-destructive testing was performed. The similar pipe on Unit 3 was examined and no significant concerns were noted. Extensive walk downs of similar piping that is attached to the Torus was conducted for both Units 2 and 3. There were no similar deficiencies discovered. Selected ultrasonic testing was performed on Unit 2 and 3 Torus attached piping that involved higher flow rates. These examinations also did not identify any similar concerns.
2772006004 | Peach Bottom 2, Peach Bottom 3 | 11/17/2006 | 01/12/2007 | ML07025014 | <strong>Plant Modification Created Diesel Generator Building Carbon Dioxide Suppression Room Flooding Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On 11/17/2006, Engineering personnel determined that a potential flood vulnerability had existed in the Emergency Diesel Generator (EDG) building Carbon Dioxide Suppression room. A plant modification performed in 1985 had installed a catch basin at the EDG building fuel oil filling station, which is located outside the EDG building. The catch basin discharge was tied in to the EDG building's oily waste separator tank, upstream of the flood protection isolation valve. In the event of a design basis flood, a potential pathway existed for floodwater to enter the building through the floor drains. It was determined that the maximum credible flow rate would have exceeded the capability of the floor sump, thereby potentially challenging the Emergency Service Water system booster pumps and return valves, as well as High Pressure Service Water system return valves. A temporary change to the applicable special event procedure for floods was previously implemented on 11/10/06 to mitigate this condition. The procedures will be permanently revised. There were no actual safety consequences associated with this event.
2782006001 | Peach Bottom 3 | 04/06/2006 | 05/23/2006 | ML06145030 | <strong>Technical Specification Non-Compliance due to Inoperable Primary Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 4/6/06 at approximately 1100 hours, Licensed Operations personnel declared an air-operated Primary Containment Isolation Valve associated with the HPCI Turbine Exhaust Drain Line inoperable in accordance with Technical Specification Limiting Condition for Operation (LCO) 3.6.1.3. This declaration was based on questions raised by an NRC Resident Inspector performing an in-plant observation of the position status of the HPCI Turbine Exhaust Line Inboard Isolation Valve (AO-137). The cause of the failure of the AO-137 to properly close was due to foreign material found in the seating areas of the valve. Similar foreign material was found in the associated drain / test connection valves associated with the AO-137 valve. Primary Containment Isolation Valve AO-137 was inoperable for a minimum time period of 15 days (i.e. the time period between the last HPCI operation on 3/23/06 and the return to operable status on 4/7/06). The last assurance of the valve being leak-tight was on 9/30/05 when the valve was leak tested with satisfactory results during the P3R15 Refueling Outage. The valves were repaired and appropriate leak-tightness was verified as part of an as-left local leak rate test. The redundant containment penetration barriers for the affected containment penetrations were operable throughout the period of exposure. Therefore, the Primary Containment isolation safety function was met during the period of non-compliance.
2802006001 | Surry 1, Surry 2 | 05/04/2006 | 07/03/2006 | ML06192058 | <strong>Voluntary Report - Motor Driven AFW Pump High Flow Condition with Low Steam Generator Pressure</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2006, with Unit 1 defueled and Unit 2 operating at 100% power, while evaluating the use of the auxiliary feedwater (AFW) system for heat removal during plant startup, an AFW system design issue, related to the original plant design, was discovered. The design concerns a motor driven AFW pump unanalyzed high flow condition that could occur during a limited time frame with low steam generator pressure and reactor coolant system (RCS) temperature between 350 F and 500 F. Specific postulated scenarios with certain initiating events, along with an assumed single failure, could result in no operating AFW pumps on a unit. However, the Surry plant design includes an AFW cross-connect. In the event of such circumstances, the AFW cross-connect could have been used to perform the required function of the AFW system. Temporary controls have been established to preclude the high flow condition. Review of the reporting criteria of 10CFR50.73 has concluded that a licensee event report is not required. However, given the safety significance of the equipment involved, this information is being submitted as a voluntary report.
2812006001 | Surry 2 | 07/27/2006 | 09/25/2006 | ML06276028 | <strong>Charging Pump Component Cooling Water System Inoperable due to Inadequate Venting</strong><br /><i>Abstract:&nbsp;</i>At 1947 hours on July 27, 2006, with Unit 2 operating at 100% power, a Unit 2 charging pump cooling water pump low discharge pressure main control room alarm was received while restoring the 'A' charging pump intermediate seal cooler to service. The standby charging pump cooling water pump started automatically, but no component cooling (CC) water flow was observed. Unit 2 charging pumps were declared inoperable and a 6-hour clock to hot shutdown (HSD) was entered in accordance with Technical Specifications (TSs) 3.0.1. The charging pump cooling water subsystem was vented and the standby charging pump cooling water pump restored to normal flow. The 6-hour HSD clock was exited at 2125 hours. A cause evaluation determined that the procedure did not provide proper guidance to sufficiently vent the cooler, which caused both charging pump cooling water pumps to become air bound. The procedure will be revised to ensure sufficient venting. The risk of this event was determined to be low and the charging crosstie from Unit 1 remained available, therefore, the health and safety of the public was not affected. This report is submitted pursuant to the requirements of 50.73(a)(2)(i)(B), a condition prohibited by TSs, and 50.73(a)(2)(vii), an event that caused two independent trains to become inoperable.
2812006002 | Surry 2, Surry 1 | 10/07/2006 | 12/05/2006 | ML06346017 | <strong>Spurious Actuation Results in Unit 2 Trip and Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2006, at 1711 hours, with Units 1 and 2 at 100% power, Unit 2 reactor was manually tripped when the Main Control Room received alarms associated with steam flow and feed flow mismatch and a report of a steam leak in the Turbine Building. The Unit 2 cross-under safety valves lifted unexpectedly causing Turbine Building siding to detach and contact Reserve Station Service Transformer (RSST) components. This resulted in faults and lockouts that de-energized two transfer busses, two Unit 2 reactor coolant pumps (RCPs), the Unit 2 containment air monitor, and caused the loss of offsite power to a Unit 2 and both Unit 1 emergency buses. Emergency systems functioned as designed, including the Reactor Protection System, Emergency Diesel Generators, and Auxiliary Feedwater System. Unit 1 was reduced to 73% power and Unit 2 was stabilized at hot shutdown. The cause of the event was a spurious signal from the Turbine Overspeed Protection Circuit (OPC). Modification of the OPC circuit will prevent recurrence during power operation. There were no significant safety consequences associated with this event. This report is provided pursuant to 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the Unit 2 RPS and AFW system, and 10 CFR 50.73(a)(2)(i)(B) for the loss of power to one emergency bus, two Unit 2 RCPs, and the Unit 2 containment air monitor.
2822006001 | Prairie Island 1 | 04/14/2006 | 07/31/2006 | ML06338029 | <strong>Unit 1 Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2006, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was operating at 100% power. At approximately 1425 CDT, an 11 FEEDWATER PUMP LOCKED OUT annunciator was received in the control room. Unit 1 operators responded per the alarm response procedure and manually tripped the reactor. The trip was uncomplicated and all systems operated as expected and operator response and recovery actions were as expected. Initial investigation of the cause of the 11 Feedwater Pump trip determined the feedwater pump tripped because the 11 Condensate Pump had tripped. The 11 Condensate Pump motor was shipped off site for repairs and the stator windings were found to have grounded. The root cause evaluation (RCE) of this event determined the condensate pump trip was caused by degraded motor insulation due to aging and environmental conditions. The RCE further determined that the organizational root cause of the condensate pump motor trip was a lack of an adequate long range planning and budgeting process to prioritize and budget large motor maintenance.
2822006002 | Prairie Island 1 | 06/06/2006 | 08/07/2006 | ML06220021 | <strong>Unit 1 Mode Change with the Turbine-Driven Auxiliary Feedwater Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>Prairie Island Nuclear Generating Plant (PINGP) Unit 1 conducted Mode changes during plant heatup following refueling outage 1R24 with 11 Turbine-Driven Auxiliary Feedwater (TDAFW) Pump inoperable. On June 1, 2006 at 0430 CDT PINGP Unit 1 transitioned to Mode 3. PINGP Unit 1 subsequently transitioned to Mode 2 on June 5, 2006 at 1414 CDT and Mode 1 on June 6, 2006 at 0913 CDT. At approximately 1811CDT on June 6, 2006, the 11 TDAFW Pump was shut down during performance of a flow test due to turbine outboard (governor end) bearing temperature exceeding the limit in a surveillance procedure. Upon disassembly, it was found that the inboard bearing was damaged and the outboard bearing was worn. The 11 TDAFW Pump was reassembled with new inboard and outboard bearings, tested, and declared operable on June 8, 2006 at approximately 1940 CDT. The ongoing engineering evaluation determined the 11 TDAFW Pump had been inoperable from the time the inboard bearing was installed without necessary machining (prior to Unit 1 performing Mode changes into Mode 3, Mode 2, and Mode 1). Technical Specification 3.7.5, AFW System, is applicable to 11 TDAFW Pump when the plant is in Mode 1, 2, or 3. Because the plant entered Mode 3 with 11 TDAFW Pump inoperable, this event is being reported in accordance with 10 CFR 50.73.(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2852006001 | Fort Calhoun | 04/07/2006 | 06/07/2006 | ML06164026 | <strong>Failure to Report Inoperable Containment Air Lock Valve Violates Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2006, at 0843 (Central Daylight Time), Condition Report 200601444 was created to document leakage from the Inner Personnel Air Lock (PAL) door equalizing valve. While the condition was reported on April 10, 2006, actual discovery followed a containment entry on April 07, 2006. Due to the delay in reporting, a technical specification (TS) for containment was violated, requiring application of a TS shutdown. At 1000 CDT on April 10, 2006, the Shift Manager was notified of CR 200601444, and TS 2.0.1(1) was entered. The valve was repaired prior to completing the shutdown and the plant was returned to 100 percent power. The root causes of the event were; the failure of the operator to recognize the TS significance of the equalizing valve leakage as a challenge to a fission product barrier; and, the lack of procedural controls to verify operation of the equalizing valve following use of the PAL. The equalizing valve was repaired and tested to ensure its operability. A step has been added to the procedure controlling access to containment at power for operations to inspect the equalizing valve on final egress.
2852006002 | Fort Calhoun | 07/07/2006 | 04/30/2008 | ML08130043 | <strong>Inadequate Design Control Results in Potentially Insufficient Auxiliary Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>During equipment train reviews by the Equipment Reliability Optimization Project in July, 2006, it was noted that the power supply to flow transmitter FT-1368 was from non-safety related Instrument Bus 1 (AI-42A). The flow transmitter performs a safety related function for recirculation valve FCV- 1368, associated with the electric auxiliary feedwater pump (FW-6). Upon discovery, on July 7, 2006, FW-6 was declared inoperable. A 1997 revision to a calculation originally prepared in 1989 concluded that the closure function of FCV-1368 was safety-related. However, engineering department procedures and processes did not provide clear direction as to the appropriate process to employ when a change to a credited design function and/or safety classification was discovered. Therefore, the lack of appropriate engineering processes is identified as the Root Cause of this condition. FW-6 was declared operable on July 8, 2006, based on the design quality level of the power supplies to the recirculation valve components and compensatory actions taken.
2852006003 | Fort Calhoun | 09/05/2006 | 11/06/2006 | ML06319033 | <strong>Technical Specification Violation of Containment Air Coolers due to Untimely Corrective Actions</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2006, torn pneumatic actuator piston rod dust boots (indicating possible actuator leaks) were identified on two component cooling water (CCW) valves to the containment air cooling and filtering units and the containment air cooling units. The valves were determined to be operable after having been cycled from the Control Room. The operability determinations for the two valves were subsequently found to be incorrect. Additionally, on July 18, 2006, an operability evaluation incorrectly concluded that the CCW valves to the cooling units, with as-found leakage of the backup nitrogen bottle regulators, were operable. On September 5, 2006 it was determined that these incorrect operability determinations had resulted in a Technical Specification violation. The root cause of both of the above described events is the failure to assign proper, timely corrective actions to address the need for updating appropriate station documents used for determining operability of these valves. The subject CCW valves have been inspected and repaired. Changes to appropriate station documents will be completed by March 2, 2007.
2852006004 | Fort Calhoun | 09/12/2006 | 11/10/2006 | ML06325033 | <strong>Loss of Shutdown Cooling Redundant Train due to Valve Mispositioning</strong><br /><i>Abstract:&nbsp;</i>Fort Calhoun Station was shutdown September 9, 2006 to commence a refueling outage. On September 10, 2006, a system lineup was performed to transfer removal of decay heat from the steam generators to the shutdown cooling system. Part of the lineup included opening two shutdown cooling heat exchanger outlet cross-connect valves, SI-173 and SI-174, which are located in a normally locked high radiation area room that is entered when performing shutdown cooling system valve lineups. An equipment operator and radiation protection technician entered the room to perform the valve lineup. Upon completion, the equipment operator reported to a licensed operator in the control room that the lineup was completed. On September 12, 2006, in preparation to drain the reactor coolant system (RCS) to dump steam generator tubes, a verification of shutdown cooling system lineup was performed. The equipment operator entered the room and found the shutdown cooling heat exchanger outlet cross-connect valve, SI-173, locked closed. The control room supervisor directed the equipment operator to unlock and open SI-173. SI-173 in a locked closed position rendered shutdown cooling heat exchanger, AC-4B, inoperable for the purpose of a decay heat removal loop. As a result of finding SI-173 locked closed, the entire operating procedure checklist was performed and no other discrepancies were found.
2852006005 | Fort Calhoun | 10/10/2006 | 12/11/2006 | ML06353047 | <strong>Faulty Maintenance Renders One Train of Containment Spray System Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1500 CDT, on October 10, 2006, while performing maintenance on one of two installed containment spray header valves (HCV-345), personnel determined that the HCV-345 valve disk had been installed incorrectly during the previous refueling outage. HCV-345 is a vee-ball valve. Actual valve position was found to be nearly the opposite of the remote indication. The resulting effect would be that an accident signal to open HCV-345 would have the valve 20 percent open instead of 100 percent open (or 80 percent open instead of closed during normal operations). A single failure of the other containment spray header valve would have resulted in substantially reduced containment spray flow. The maintenance procedure allowed for the flexibility of performing selected portions of the procedure without providing adequate annotations to identify risk-important steps that could impact final valve alignment. A test to verify flow and isolation capabilities after the valve was installed in the system is impractical to perform. The procedure used to conduct the maintenance was relied upon to ensure proper valve operation without detailed acceptance criteria or verifications. This resulted in the post maintenance test process failing to identify the problem. The valve was repaired and verified to be in its correct operating position. Maintenance procedures are being rewritten to preclude this from occurring again.
2852006006 | Fort Calhoun | 11/08/2006 | 01/08/2007 | ML07017037 | <strong>Inadvertent Start of Emergency Diesel Generator 2</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2006, Fort Calhoun Station was in a refueling outage with the core offloaded. At 1140 Central Standard Time (CST), Emergency Diesel Generator 2 (DG-2) inadvertently started while de-energizing vital 4160 VAC bus during a planned functional test. The DG-2 did not load onto the bus because the output breaker was in the pull-to-lock position for the test. No vital loads were lost as they had been transferred prior to commencing the functional test. An operator was dispatched to verify proper operation of DG-2. DG-2 responded as expected. The first time the operator attempted to shutdown DG-2 it was not taken out of auto. This resulted in DG-2 restarting. DG-2 was then properly secured. No other safeguards systems or equipment were actuated. The root cause of this event was determined to be inadequate procedural guidance. Appropriate procedures are being revised.
2852006007 | Fort Calhoun | 11/08/2006 | 01/08/2007 | ML07017038 | <strong>Inadequate Seismic Design of Reactor Vessel Head Refueling Stand</strong><br /><i>Abstract:&nbsp;</i>During the 2006 refueling outage, a question was raised regarding the seismic mounting requirements for the Reactor Vessel Head (RVH) while it is in the lay down area on the 1045'-0" elevation of containment. The RVH is not restrained when it is in the laydown area. Upon further review, it was discovered that the floor beams and piers that support the RVH are not seismically qualified for loads due to the RVH. If there was a failure of the head stand during an earthquake and the head fell to the northeast direction and penetrated the floors in that area, the shutdown cooling (SDC), safety injection piping and components in the basement below could be severely degraded. This would result in placing the plant in an unanalyzed condition. This is an unacceptable scenario that would potentially put the plant at risk due to the loss of decay heat removal capability. The root cause appears to be an original design oversight. During the 2006 refueling outage, a plant modification installed a seismic guard in the laydown area to preclude this scenario. This guard prevents the RVH from falling toward vulnerable equipment. The RVH falling other directions is bounded. Therefore, with the addition of the seismic guard, the consequences of the RVH falling from its support location in the laydown area are found to be acceptable.
2852006008 | Fort Calhoun | 11/27/2006 | 01/26/2007 | ML07037020 | <strong>Loss of Shutdown Cooling due to Repressurizing Reactor Coolant System</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2006, Fort Calhoun Station (FCS) was in Mode 4, cold shutdown, with shutdown cooling (SDC) in service. Reactor coolant system (RCS) temperature was approximately 119F and RCS pressure was approximately 233 pounds per square inch absolute (psia). Reactor Coolant Pumps RC-3A and RC-3B were in service. The pressurizer had maximum heaters and spray flow in service. RC-3B and RC-3A were secured at 1327 central standard time (CST) and 1330 CST, respectively, which reduced the spray flow to the pressurizer. As a result, RCS pressure rose to greater than 250 psia and initiated closure of shutdown cooling isolation valves, HCV-347 and HCV-348. The crew immediately recognized the loss of SDC condition and entered the appropriate abnormal operating procedure. The crew secured the running low pressure safety injection (LPSI) pumps, secured all pressurizer heaters and initiated auxiliary spray to lower RCS pressure. When RCS pressure was less than 250 psia, the crew restored the SDC system to operation. The root cause of this event was determined to be a mismatch between procedural guidance and crew experience. The SDC system was returned to operation. Operator training and appropriate procedures are being revised.
2862006001 | Indian Point 3 | 07/06/2006 | 08/28/2006 | ML06249043 | <strong>Reactor Trip as a Result of a Main Generator Trip due to Short in the Generator Differential Protection Circuit</strong><br /><i>Abstract:&nbsp;</i>On July 6, 2006, at 0352 hours an automatic reactor trip (RT) occurred as a result of a short circuit that occurred in the junction box of the Main Generator output phase "B" differential protection current transformer (CT). The plant responded to the trip as designed. The Auxiliary Feed Water System (AFW) actuated and the AFW Pumps started as designed due to the Steam Generator (SG) shrink caused by the trip from 100% power. All plant systems operated normally with the exception 31 Main Boiler Feed Pump Recirculation Valve did not open due to a failed solenoid and the 32 Main Steam Line Trap was isolated due to having a minor steam leak. The root cause of this condition was determined to be design inadequacy in material application. The abrasive property of the conductors insulation jacket was not evaluated for use in a continuous vibration environment. Corrective actions included repair of damaged cables, coaching of personnel on the lessons learned, process/procedure revisions to improve the considerations on material selection in the design process and training enhancements to address material considerations. This event had no effect on public health and safety.
2862006002 | Indian Point 3 | 07/21/2006 | 09/13/2006 | ML06271041 | <strong>Manual Reactor Trip as a Result of Arcing under the Main Generator between Scaffolding and Phase A&B of the Iso-phase Bus Housing</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2006, at 1031 hours, Operations initiated a manual reactor trip (RT) as a result of observing arcing under the main turbine generator (MTG) between scaffolding and Phase A&B of the Iso-phase bus housing. All control rods fully inserted and all primary systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater (AFW) system automatically started as expected due to a low steam generator (SIG) level. The direct cause of the RT was due to arcing between metal scaffolding contacting two phases (A&B) of the Iso-phase bus housing. The root cause was latent Organizational/Programmatic weakness. There was insufficient awareness across the organization regarding the potential impact of leaving or removing conductive materials in close proximity to the MTG Iso-phase bus housing while the unit is in operation. Scaffolding left in place from a previous shutdown inadvertently came in contact with the MTG Iso-phase bus enclosure during scaffold disassembly. The operational risk of this condition was not adequately assessed. The scaffold procedure has no specification for addressing clearances for electrical safety hazards related to electromagnetic flux concerns. Corrective actions include coaching personnel on the event and lessons learned, preparation of an improved method in the work control process for screening operational risks, and revision of the scaffold procedure to include clearance criteria and precautions. The event had no effect on public health and safety.
2872006001 | Oconee 3 | 05/15/2006 | 07/14/2006 | ML06206034 | <strong>Actuation of Emergency Generator due to Spurious Transformer Lockout</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2006, Unit 3 was in day 17 of a refueling outage. The unit was in Mode 6, with fuel reload activities complete. At 1059 hours, during performance of a maintenance activity, a technician moving/jarring an open electrical cabinet door inadvertently caused an invalid actuation of a lockout relay for CT-3, the start-up auxiliary power transformer in service supplying power to the unit. A loss of power occurred, resulting in a valid actuation of Keowee Hydro Station, the Oconee emergency on-site power source. Power was restored automatically after approximately 40 seconds and decay heat removal was restored after 14 minutes. The root causes were determined to be less than adequate establishment of work practices as well as a design deficiency for having an impact sensitive relay mounted on an electrical cabinet door. This event is considered to have no significance with respect to the health and safety of the public.
2892006001 | Three Mile Island 1 | 04/23/2006 | 06/22/2006 | ML06181027 | <strong>Design Change Error for the Decay Heat Valves Connecting the BWST and RB Sump Negatively Impacted the Fire Mitigation Strategy for an Auxiliary Building Fire Area</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2006, while performing reviews of fire abnormal operating procedures to assure compliance with the Fire Hazards Analysis Report (FHAR), a control logic error was identified in the circuit elementary drawing for the isolation valves (DH-V-6A and DH-V-6B) between the Borated Water Storage Tank (BWST) and the Reactor Building (RB) sump. The valve control circuit was verified to be wired as per the elementary drawing. The design was to prevent a hot short, due to a fire, from opening the valve, but the design change was made on the closing circuit. The identified control logic error could allow DH-V-6A or DH-V-6B to spuriously open due to a fire. The FHAR credits these valves as being protected from spuriously opening due to a fire in AB-FZ-5 (Auxiliary Building 281 general area). If this protection is not provided, then spurious opening could result in draining the BWST inventory to the RB sump. This hot short condition would result in the depletion of the BWST inventory and loss of the High Pressure Injection (HPI) makeup capability, resulting in an unanalyzed condition that significantly degrades plant safety. The Root Cause of the problem is identified as "accountability needs improvement" in that the reviewers did not validate the design requirements for DH-V-6A/B in the original 1985 Appendix R package. Upon discovery, an hourly fire-watch was established in the affected fire zone in the 281' elevation Auxiliary Building. The fire watch was continued until June 2, 2006, when the control circuitry was modified to prevent the RB sump isolation valves, DH-V-6A and DH-V-6B, from spuriously opening due to a hot short. No additional corrective action is needed, as the current Fundamentals Tool Kit procedure (HU-AA-1081) emphasizes personal accountability, which addresses the root cause of this issue. Also, current procedures for Design Input and Configuration Change Impact Screening (CC-AA-102), Configuration Change Control (CC-AA-103), and Technical Risk/Rigor Assessment (HU-AA-1212) provide guidance for both initial scope definition and changes in scope, including the required reviews. These process controls did not exist at the time this error was made, and would have prevented this event. This condition was determined to be an unanalyzed condition that significantly degraded plant safety (10 CFR 50.73 (a)(2)(ii)(B)).
2892006002 | Three Mile Island 1 | 11/02/2006 | 01/02/2007 | ML07010030 | <strong>Automatic Reactor Trip due to an Invalid Turbine Protective System Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2006, at 1334 hours, the Three Mile Island, Unit 1 (TMI-1) reactor tripped from 100% power during a calibration check of the main turbine Digital Turbine Control System (DTCS) condenser pressure instruments. The reactor trip was initiated from Reactor Protection System (RPS) ARTS (Anticipatory Reactor Trip System) due to a main turbine trip initiated from greater than 45% power. The turbine trip resulted from an invalid DTCS protective system actuation. The turbine trip initiated from the two in-service DTCS protective channels not being tested at the time of the event. Both channels received an invalid trip signal. The channel under test at the time of the event was properly bypassed from the trip logic and did not input a trip signal to the DTCS. Plant systems responded properly to the reactor trip transient and the plant was stabilized at hot shutdown conditions. The root cause of the turbine trip is a latent design weakness within the DTCS. Subsequent testing demonstrated that a short circuit of a single milli-amp input to the DTCS signal processing board will affect all of the processor inputs associated with that board and initiate a main turbine trip signal from the in-service trip channels. All online transmitter preventative maintenance activities that provide inputs to the DTCS trip logic circuit have been suspended until the cause for the turbine trip is eliminated. The actuation of the Reactor Protection System was reported to the NRC in accordance with 10CFR 50.72(b)(2)(iv)(B), reference EN# 42957. Submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv)(A).
2892006003 | Three Mile Island 1 | 12/13/2006 | 02/12/2007 | ML07053031 | <strong>Automatic Reactor Trip due to a Design Application Deficiency within the Reactor Coolant Pump Power Monitors Initiated by an Off-Site Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>At 1748 hours on December 13, 2006, the Three Mile Island, Unit 1 (TMI-1) reactor tripped from 100% power following a short duration power disturbance on a 230 kV transmission line located approximately 4 miles from TMI-1. This short duration power disturbance was caused by the failure of a 230 kV transmission line cable splice, which resulted in a single-phase ground fault. This short duration ground fault affected power supplied to the reactor coolant pump motors, which in turn caused actuation of the Reactor Coolant Pump Power Monitors (RCPPM). The RCPPM's actuation sends a signal to the Reactor Protection System (RPS) to trip the unit if a decrease in reactor coolant pump motor power consumption is detected. This reactor trip is designed to protect the fuel rods from overheating upon a sudden loss of Reactor Coolant flow. The RCPPM design includes a time delay to prevent inadvertent reactor trips due to short duration electrical disturbances, which would not affect the reactor coolant pump's ability to maintain adequate Reactor Coolant System flow. The RCPPM time delay has a maximum setting of less than 525 milliseconds. The root cause of the event is a design application deficiency within the RCPPM. The RCPPM circuit design focuses on fuel protection and specifies a maximum time delay, but does not consider the effects of a grid transient of short duration. The RCPPM calibration procedure will be revised to establish a minimum allowed time delay for the Reactor Coolant Pump Power Monitor circuit. A maintenance activity has been scheduled for the next available opportunity, but no later than the October 2007 refueling outage, to calibrate the RCPPM using the revised setpoint tolerance. The actuation of the Reactor Protection System was reported to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B), reference EN #43050. Submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv)(A).
2932006001 | Pilgrim | 03/13/2006 | 05/11/2006 | ML06137062 | <strong>Manual Scram due to High Offgas Recombiner Temperature Resulting from Inadequate Preventive Maintenance of Recombiner Preheater Pressure Control Valve Controller</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2006, at 1808 hours, an unplanned scram was manually initiated while at 43 percent reactor power. This procedurally required action was taken because of high temperature in the Augmented Offgas (AOG) system recombiner. There were no complications encountered during the response to the scram. The root cause of the event was the failure of the controller of a pressure control valve (PCV) that supplies steam dilution flow PCV and steam heating to the recombiners preheater. The failure was due to inadequate preventive maintenance of the controller. Corrective action taken included replacement of the pressure control valve controller and repair of a hand operated valve that enables steam to bypass the pressure control valve. Corrective action planned includes developing preventive maintenance for the AOG pressure controllers, training, and evaluating changes to procedures. The event occurred during power operation. The reactor vessel pressure was about 967 psig with the reactor vessel water temperature at the saturation temperature for that pressure. The event posed no threat to public health and safety.
2932006002 | Pilgrim | 06/23/2006 | 07/19/2006 | ML06208014 | <strong>Small Quantities of Unaccountable Licensed Material</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2006 the NRC Operations Center was notified that sealed detectors containing a small amount of special nuclear material greater than ten times the limit specified in 10 CFR 20.2201(a)(1)(ii)were not in the expected locations. The discovery was made as a result of removing previously used and severed dry tubes as part of a planned cleanup of the spent fuel pool (SFP). These detectors are in addition to the detectors that could not be accounted for that were reported in LER 97-001-00 and notifications made in June 2001. The apparent cause was inadequate verification of assumptions during the 1996 inventory of the spent fuel pool. A contributing cause was the failure to track special nuclear material (SNM) of quantities of less than one gram between 1975 and 1987 that prevented accurate inventory reconciliation and masked an incorrect conclusion that dry tubes stored in the SFP contained the detectors containing licensed material.All special nuclear material in inventory has been reviewed to determine if a similar condition may exist.Corrective actions planned include updating and validating the SNM records based on the results of the SFP inventory review and correcting shipping records. The devices were most probably shipped to a licensed disposal facility prior to 1996 and pose or posed no threat to national defense or public health and safety.
2962006001 | Browns Ferry 3 | 05/03/2006 | 06/23/2006 | ML06178035 | <strong>Main Steam Relief Valve Inoperability LCO Exceeded as a Result of Lift Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Following testing of main steam relief valves (MSRV) removed from Unit 3, it was discovered that 2 of the 13 tested valves mechanically actuated at pressures greater than 3% above their nominal setpoint. The Unit 3 Technical Specifications Limiting Condition for Operation (LCO) 3.4.3 requires that 12 MSRVs be operable in reactor modes 1, 2, and 3. If less than 12 MSRVs are operable, then the unit is to be placed into Mode 3 within 12 hours and Mode 4 within 36 hours. Since each BFN unit has 13 installed MSRVs, the inoperability of more than 1 MSRV would require the above actions to occur. While the setpoint-drift condition was not identified until after the valves' removal from the plant, MSRV pilot valve disc-seat corrosion bonding in boiling water reactor applications is a known phenomenon, and the condition is deemed to have developed while the valves were in service during Unit 3 Cycle 12 operation. The root cause of this condition was MSRV pilot valve disc-seat corrosion bonding which can develop during normal reactor operations. The affected valves will be refurbished and their lift-setpoints re-established prior to reinstallation in the plant. There were no actual safety consequences associated with this event.
2962006002 | Browns Ferry 3 | 08/19/2006 | 10/17/2006 | ML06290010 | <strong>Manual Reactor Scram due to Loss of the Reactor Recirculation Pumps</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2006, at 1105 hours central daylight time, Unit 3 was manually scrammed following a loss of both the 3A and 3B Reactor Recirculation pumps. Just prior to the event, the Unit 3 Unit Operator (UO) received alarms indicating low reactor water level, reactor feedwater level control system failure, and failure of the input/output modules for both the 3A and 3B Reactor Recirculation pumps. The UO also reported that main generator load was approximately 730 megawatts electrical (approximately 64 percent of full power output) and lowering. Based on these indications, the UO scrammed the reactor. The immediate cause of the manual scram was the loss of both the 3A and 3B Reactor Recirculation pumps. The manual scram was required by the conditions presented to the Unit 3 operator following the loss of recirculation flow. The initial investigation into the trip found the Variable Frequency Drive (VFD)microprocessors non-responsive. The root cause of the event was the VFD controls malfunctioned due to excessive traffic on the connected plant Integrated Control System (ICS) network. Corrective actions include developing a network firewall device that limits the connections and traffic to any potentially susceptible devices on the plant ICS network and installing a network firewall device on each Unit's VFD controller.
2962006003 | Browns Ferry 3 | 08/29/2006 | 10/16/2006 | ML06290004 | <strong>Manual Scram in Response to Main Turbine Electro-Hydraulic Control (EHC) System Fluid Leak</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2006, while in steady state operation at 100% power, control room annunciation was received at 2210 hours CDT of a low level in the main turbine electro-hydraulic control (EHC) fluid reservoir. Local inspection of the tank confirmed an actual low level and also that the tank level was continuing to drop. At 2223 hours, reactor power was reduced to approximately 78% via reactor recirculation pump speed reduction, and, at 2225 hours, a manual scram was initiated in accordance with plant procedures. All control rods fully inserted and expected system responses were received. Actuation of primary containment isolation system groups 2, 3, 6, and 8 occurred due to the expected temporary lowering of reactor water level below the actuation setpoint. Valve realignment as part of the main turbine trip which followed the scram isolated the location of the EHC fluid leak from the rest of the system. The normal heat rejection path (from the reactor to the main condenser via the main steam lines with reactor water make-up provided by the condensate/feedwater systems) remained in service. Reactor water level was recovered to the normal operating range by the normal reactor water level control system. Neither the high pressure coolant injection nor reactor core isolation cooling systems were used during this event. The root cause of the EHC fluid leak was determined to be inadequate O-ring compression on a solenoid valve mounting due to the use of device mounting bolts which were too long. The bolts and the valve were supplied as a kit by the vendor. Plant procedures will be revised to verify bolt length and mounting hole depth in future activities involving EHC components.
2982006001 | Cooper Station | 02/26/2006 | 04/25/2006 | ML06121001 | <strong>Reheat Valve Failure to Re-open due to Contaminated Control Fluid Results in Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2006, at 0250 Central Standard Time, Reheat Valve 1B did not re-open after the valve was closed during conduct of a surveillance test on the main turbine reheat/intercept valves. This occurred concurrent with a high level alarm in Moisture Separator D. Per procedure, the plant was manually scrammed. All control rods fully inserted and a Primary Containment Isolation System Group 2 isolation occurred. Reactor power, vessel pressure and level response were as expected. The cause of the event was contamination of the electro-hydraulic fluid in the turbine control system from inadvertent introduction of waste fluid to the control system fluid reservoir on August 14, 2005. Feed and bleed actions to reduce the contamination did not eliminate particulate contamination in normally stagnant lines associated with the reheat/intercept test solenoid valves resulting in a stuck reheat valve. Immediate actions were to cycle all intercept and reheat stop valves via the test solenoids several times to verify flushing of the electro-hydraulic fluid through the valves. Corrective actions to prevent recurrence include replacing the test solenoid valves for the turbine reheat/intercept and main stop valves and flushing and replacing the electro-hydraulic fluid in the turbine generator control system.
2982006002 | Cooper Station | 04/06/2003 | 05/22/2006 | ML06146016 | <strong>Scram Time Testing following Reactor Pressure Vessel Pressure Tests in Past Outages Violated Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2000, December 17, 2001, April 6, 2003 and on February 12, 2005, coming out of refuel outages RE19, RE20, RE21 and RE22, Cooper Nuclear Station (CNS) was in Mode 4 (Cold Shutdown)when CNS executed control rod scram time testing after the reactor pressure vessel class 1 leakage test was complete while coolant temperature was greater than 212 degrees Fahrenheit (F). Limiting Condition for Operation (LCO) 3.10.1 was applied in lieu of entering Mode 3 which violated LCOs 3.0.4 and 3.10.1. The impact of this on baseline core damage frequency is negligible due to the low level of decay heat, two trains of low pressure injection systems operable for makeup, higher than normal water inventory in the vessel, and Secondary Containment established. The cause was inadequate procedures. After adoption of Improved Technical Specifications, CNS failed to include in applicable procedures a caution to alert operators that continuing scram time testing above 212 F after hydrostatic test was completed could violate LCO 3.10.1. The procedural inadequacy was caused by a human error of not considering that performing other evolutions as part of hydrostatic testing under LCO 3.10.1 could conflict with the LCO. Those procedures were suspended until they are revised to clarify application of LCO 3.10.1, and include specific language that scram time testing can not be conducted under LCO 3.10.1 beyond completion of hydrostatic testing when reactor coolant temperature is greater than 212 F. CNS Corrective Action Program tracks these actions.
2982006003 | Cooper Station | 03/23/2004 | 06/15/2006 | ML06171010 | <strong>Both Diesel Generators Inoperable due to Voltage Regulator Design Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2006, during a drawing review, Engineering discovered that the diesel generator (DG) control circuitry caused a diesel generator connected (aligned) to the offsite power grid to be inoperable. A records review determined that on one occasion, March 23, 2004, DG #1 had been inoperable for maintenance. During this same time period, a surveillance test was performed that resulted in DG #2 being aligned to the grid and thus being inoperable. Both DGs inoperable constitutes a loss of safety function and is reportable under 10 CFR 50.73(a)(2)(v)(B) as an inability to remove residual heat. This was caused by a procedure change in late 1998 that, based on inaccurate information, allowed a DG to be considered operable while aligned to the grid. In subsequent years the procedure change process has been revised to require more detailed and extensive reviews of procedure changes. Immediate actions were to identify procedures that include aligning a DG to the offsite power grid during surveillance testing. These procedures have either been revised to require declaring the DG inoperable or already contained a requirement to declare the DG inoperable when aligned to the grid. Further corrective actions include additional changes to the procedure revision process, reviewing a sample of other procedure changes that used that same process for accuracy, and modifying the DG control circuitry to no longer require declaring a DG inoperable when aligned to the grid.
2982006004 | Cooper Station | 05/22/2006 | 07/20/2006 | ML06206029 | <strong>Manual Reactor Scram and Containment Group 2 Isolation due to Plant Air Failure</strong><br /><i>Abstract:&nbsp;</i>At 0651 on May 22, 2006, Service Air (SA) pressure began lowering for an unknown reason. Additional Service Air Compressors (SACs) could not be started in time to recover SA pressure. Following a rapid power reduction the reactor was manually scrammed at 0701 as a mitigating action. All automatic systems functioned as expected, and the plant entered and remained in Mode 3, Hot Shutdown. This event was not risk significant. Analysis revealed the most likely cause to be the SAC automatic control system failed to respond to system pressure changes. SACs were placed in local control mode to operate independently based on individual start-stop-unload setpoints. The plant subsequently started up on May 24, 2006. The cause was a single point failure mode introduced into the newly installed SAC compressor controller that was unrecognized in the design process. A standing order now prevents SACs from operation in other than local control until an evaluation of failure modes on the automatic control system has been performed. Action remaining includes revising applicable plant configuration change procedures to perform failure mode evaluation for Maintenance Rule (MR) Risk Significant control systems; revising the SAC operating procedure to normally operate in local mode, except when controlled methods retain at least two SACs to supply plant air; determining which of the past three years plant modifications require a failure mode evaluation; and performing evaluations for those modifications.
2982006005 | Cooper Station | 10/17/2006 | 12/15/2006 | ML06354016 | <strong>Residual Heat Removal Loop B Injection Valve Failure due to Incorrect Pinion Gear Installation in Motor Operator</strong><br /><i>Abstract:&nbsp;</i>At 04:05 CST on October 17, 2006, during surveillance testing, the Residual Heat Removal (RHR) Motor Operated Valve (MOV) Loop B injection valve (RHR-MOV-25B) failed to open when the associated switch was placed to open. Immediate action consisted of exiting the surveillance procedure and declaring the subject valve inoperable. The failure was a result of a dislocated motor pinion gear in the associated Limitorque motor operator. The MOV was incapable of opening for a period of approximately three months, which is a condition prohibited by Technical Specification 3.5.1 where one Emergency Core Cooling System train was inoperable for a period greater than seven days. The cause of the MOV failure was determined to be an improper pinion gear installation resulting from non-specific procedural guidance. This event was not risk significant.
3012006002 | Point Beach 2, Point Beach 1 | 06/26/2006 | 08/25/2006 | ML06242023 | <strong>Fuel Assemblies in Spent Fuel Pool Do Not Meet Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2006, while preparing a new procedure, the licensee identified 12 spent fuel assemblies stored in the Spent Fuel Pool (SFP) that had an initial enrichment of 4.70 weight percent and contained no Integral Fuel Burnable Absorber (IFBA) rods. These assemblies were first loaded in Unit 2 Cycle 21 in 1994. Technical Specification 3.7.12 requires fuel assemblies with an initial enrichment greater than 4.60 weight percent to have an acceptable number of IFBA rods based on Figure 3.7.12-1. The 12 assemblies in question had a nominal initial enrichment of 4.70 weight percent and no IFBA rods. Storage of the 12 assemblies had previously been evaluated as being acceptable using an approved methodology. A new criticality analysis confirms the earlier analysis by demonstrating that these assemblies may be used in any configuration in the SFP, even if the SFP were filled with unborated water and no Boraflex is present. Therefore, the safety significance of this condition is minimal. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." No corresponding 10 CFR 50.72 report applies.
3022006001 | Crystal River 3 | 10/20/2006 | 12/11/2006 | ML06353048 | <strong>Train B Raw Water System in a Condition Prohibited by Technical Specifications due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>At 11:15, on October 20, 2006, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when an evaluation concluded that flow through the Train B Nuclear Services and Decay Heat Seawater (RW) System cyclone separator (RWSP-1B) was severely reduced. A flow of approximately 9 gpm is required through RWSP-1B to ensure flush water with particles less than 250 microns to the bearings of RW System pumps RWP-2B and RWP-3B. A subsequent review concluded that Train B of the RW System was inoperable from July 6, 2006, through 11:15 on October 20, 2006. Additionally, Train A of the RW System was taken out of service for scheduled maintenance from 02:00 on July 18, 2006, to 15:00 on July 19, 2006, rendering both RW System trains inoperable during this time. The cause for this event was failure of a duplex strainer basket upstream of RWSP-1B. This failure allowed debris to migrate to and block the RWSP-1B drain port, stopping the filtration process. RWSP-1B was cleaned and flushed. This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(B). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported.
3022006002 | Crystal River 3 | 11/01/2006 | 12/14/2006 | ML07003051 | <strong>Emergency Diesel Generator in a Condition Prohibited by Technical Specifications due to Mispositioning</strong><br /><i>Abstract:&nbsp;</i>At 14:00, on November 1, 2006, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when attempts to close Emergency Diesel Generator EGDG-1A output Breaker 3209 during a surveillance test were not successful. The breaker charging motor direct current (DC) power control switch was found in the OFF position and the breaker closing spring was not charged, rendering EGDG-1A inoperable. A review concluded that EGDG-1A was inoperable from October 4, 2006 through 18:11 on November 1, 2006. Also, EGDG-1B was taken out of service for scheduled maintenance from 04:31 on October 18, 2006 through 15:30 on October 19, 2006, rendering both emergency diesel generators inoperable during this time. The cause for this event was that Operations did not ensure Breaker 3209 was returned to the correct operable condition following maintenance. The DC power control switch was restored to the ON position, the breaker closing spring charged and Breaker 3209 successfully closed. This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(D). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported.
3052006002 | Kewaunee | 04/18/2006 | 06/19/2006 | ML06178019 | <strong>Safety-Related Relay Racks with Improper Quality Classification of Foxboro Signal Conditioning Modules</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2006 at 1200 central standard time (CST), relay racks RR-119 and RR-120 were identified to contain Foxboro signal conditioning modules that did not have the required safety-related quality classification. Equipment powered through these relay racks was declared inoperable. The signal conditioning modules require a classification of safety-related for electrical boundary and non safety-related for function. Four modules were identified that did not have a safety-related classification in RR-119 and two modules were identified that that did not have a safety-related classification in RR-120. The following instrumentation and equipment were declared inoperable for relay racks RR-119 (Train A) and RR-120 (Train B): Reactor coolant system subcooling, reactor vessel level indication system, pressurizer safety valve outlet temperature, pressurizer power operated relief valve outlet temperature, and shield building ventilation damper control. The station entered a 12-hour Technical Specification (TS) action statement for both trains of the shield building ventilation system being declared inoperable. This TS was exited at 1611 CST on April 18, 2006 with the return to service of RR-120. A seven day action statement for one train of the shield building ventilation system being inoperable was exited with RR-119 returned to service at 2128 CST on April 18, 2006. This event was reported under 10 CFR 50.72(b)(3)(v)(C) for any event that could have prevented the fulfillment of the safety function of systems needed to control the release of radioactive material and is considered a safety system functional failure.
3052006003 | Kewaunee | 05/05/2006 | 07/05/2006 | ML06192057 | <strong>Residual Heat Removal Pumps Declared Inoperable due to Flooding Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2006 at 1600 CST in intermediate shutdown, the Kewaunee Power Station declared both trains of the residual heat removal (RHR) system inoperable due to internal flooding vulnerability caused by the possibility of non-seismically qualified pipe breaks during a seismic event. The RHR pumps are not protected from non-seismically qualified pipe breaks in the auxiliary building. The specific design criteria is stated in the Updated Safety Analysis Report Section B.5 Protection of Class I Items and states that "Class I items are protected against damage from Rupture of a pipe or tank resulting in serious flooding or excessive steam release to the extent that the Class I function is impaired." The two RHR trains are not separated in a manner that would prevent simultaneous damage to both trains from a failure of a non-seismically qualified pipe. This event was reported under Event Number 42557 in accordance with 10CFR50.72(b)(3)(v)(B), "Any event that at the time of discovery could have prevented the fulfillment of the safety function of systems that are needed to remove residual heat." This is being reported in accordance with 10 CFR 50.73(a)(2)(v)(B), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat" and 10 CFR 50.73(a)(2)(i)(B), "Any condition which was prohibited by the plant's Technical Specifications." Assessment of this issue is still under evaluation. Results of the assessment will be provided in a supplement to this LER. This is being reported as a safety system functional failure.
3052006004 | Kewaunee | 05/19/2006 | 12/28/2006 | ML07004004 | <strong>Incorrect Assumption Regarding De-Rating of EDGs During Loaded Operation</strong><br /><i>Abstract:&nbsp;</i>LER 2006-004-00 reported a preliminary determination that Kewaunee Power Station Train A Emergency Diesel Generator would periodically not have been able to meet its post-accident loading due to high ambient temperatures, sometimes coincident with inoperable Train B engineered safety features. Subsequent analysis determined that Train A Emergency Diesel Generator would always have been able to meet its design loading requirement throughout the reporting period. However, on 11/15/2006, in response to an NRC question, the station identified that both Emergency Diesel Generators would periodically not have been able to meet their 18 month load tests (Technical Specification Surveillance 4.6.a.5), due to elevated ambient temperatures. These surveillances are performed during refueling outages which generally occur in the Spring and Fall so ambient temperatures have never previously impeded the load test. EDG A passed this surveillance on 9/22/06, and EDG B passed it on 10/6/06. During the reporting period, ambient temperatures have periodically exceeded the limits that would prohibit performance of these tests. Since periods existed where the surveillance would not have been able to be performed, this condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." During the three year reporting period, EDG A & B would have been able to meet their post-accident loading requirements. Therefore, periodic conditions that would have established a failure to meet TS Surveillance 4.6.a.5 have no safety significance.
3052006005 | Kewaunee | 05/30/2006 | 06/06/2007 | ML07164037 | <strong>Seal Water Flow to the Service Water Pump Bearings Found Degraded</strong><br /><i>Abstract:&nbsp;</i>At 09:34 on 5/30/2006, with Kewaunee Power Station at 100 percent power, the backup safety-related bearing lube water supply to service water pump B1 was discovered to be inoperable, making both service water pump B1 and service water train B inoperable. Maintenance was performed, service water pump B1 was returned to service, and both the pump and train B were declared operable at 15:31 on 5/30/2006.The inoperability is assumed to have existed since the regulator was last demonstrated operable at 21:07 on 4/16/2006. During that 43.5 days of inoperability, the plant was at power twice (once for 10 days and once for 8 days). Also during that time, various Train A engineered safety features were concurrently inoperable.The direct cause of the safety-related bearing lube water flow disruption for service water pump B1 was the service water backup lube water supply pressure regulator stem sticking in the stem guide bushing as a result of contaminants from the plant equipment water lube supply adhering to the stem. Inspection of the plant equipment water system found the filter tanks and internal components severely corroded allowing water and contaminants to bypass the cartridge filters. This condition developed because the original plant equipment water cartridge filter retaining cup material was not suitable for the application and inadequate maintenance practices failed to identify and correct the issue. This is being reported in accordance with 10 CFR 50.73(a)(2)(v)(B) & (D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat & to mitigate the consequences of an accident", and 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plants Technical Specifications."
3052006006 | Kewaunee | 07/13/2006 | 09/07/2006 | ML06257017 | <strong>Safety Injection Accumulator Level to Volume Correlation and Alarm Setpoints Non-conservative</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2006, with the plant at 100 percent power, non-conservative values were identified for the safety injection accumulator levels due to incorrect volume to level correlations and incorrect level alarm setpoints. Questions had been raised on how to determine the proper indicated safety injection accumulator level to ensure compliance with the Technical Specification requirement of 1225 to 1275 cubic feet for each accumulator. Accumulator level is indicated from instrumentation in percent level. Two operator aids provide a correlation graph of cubic feet versus percent indicated level. Per the operator aids, the low level limit in accumulator A was 25% and the high level limit was 50%. The low level limit in accumulator B was 22% and the high level limit was 50%. Additionally, there are low and high accumulator level alarms at 26% and 50% respectively. If either alarm value was reached, level was established between 38% and 40%. Analysis currently shows that minimum required level to meet the Technical Specification is 39% for accumulator A and 42% for accumulator B and that the maximum required level is 60% for accumulator A and 62% for accumulator B. A new normal operating range has been established between 46% and 48% accumulator level. The causes of this event are; a 1978 set point methodology not taking into account instrument loop accuracy tolerances, and failure to update the operator aids and level alarm setpoints after an issue was identified in 1991 (calibration of the accumulator level instruments inaccurate due to not being properly pressure compensated for Nitrogen cover gas). This is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." There was no safety system functional failure.
3052006007 | Kewaunee | 06/13/2006 | 08/11/2006 | ML06234033 | <strong>RCS RTD Cross Calibration Procedure has the Potential to Exceed the TS LCO Allowed Time Limit</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2006, with the station at approximately 100% power, it was determined (by procedure review), that surveillance procedure SP-47-310, Reactor Coolant System RTD Cross Calibration, has the potential to exceed the 24 hr allowable Limiting Condition for Operation (LCO) of item 2.b of Tech Spec Table 3.5-4 (Instrument Operating Conditions For Isolation Functions). The surveillance procedure removes all four narrow range channels of RCS temperature from service during plant heatup, thus rendering all channels of Tavg inoperable. Item 2.b of Technical Specification Table 3.5-4 (Instrument Operating Conditions For Isolation Functions), requires at least 1 operable channel for the function (Hi Steam Flow and 2 of 4 Lo-Lo Tavg with Safety Injection). With less than the minimum channels operable, the LCO requires that the plant be placed in HOT SHUTDOWN. If the minimum conditions are not met within 24 hours, the LCO requires the plant be placed in a COLD SHUTDOWN condition. Therefore, if this surveillance procedure renders Tavg inoperable for greater than 24 hours, and plant heatup continues, the LCO is not met. Corrective actions included immediately placing the procedure on Administrative Hold and initiating paperwork to revise the procedure steps and develop additional resources to reduce the time required for performance to within the allowable 24 hours. This event is deemed to have no safety significance and does not constitute a safety system functional failure.
3052006008 | Kewaunee | 07/26/2006 | 09/11/2006 | ML06262025 | <strong>Diesel Generator Operability Testing Interval Exceeded</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2006, while operating at 100% power, it was discovered that an LCO-required daily test of an emergency diesel generator (EDG) was not performed within the prescribed time period. Technical Specification 3.7.b.2 states "One diesel generator may be inoperable for a period not exceeding 7 days provided the other diesel generator is tested daily to ensure OPERABILITY and the engineered safety features associated with this diesel generator are OPERABLE." EDG B was inoperable as of 1541 hours on July 25 due to train B of service water (SW) having been declared inoperable. The daily surveillance test for EDG A was required to be performed by 1541 hours on July 26. At approximately 1830 hours on July 26, the operating crew discovered the daily test of EDG A had not been performed. A satisfactory test of EDG A was completed at 1929 hours on July 26. The preliminary cause determination found inadequate communication and incomplete turnover among the operating crews. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." There is no safety system functional failure for this event.
3052006009 | Kewaunee | 08/17/2006 | 04/16/2007 | ML07114015 | <strong>Fuel oil leak on Swedgelock fitting renders Emergency Diesel Generator A inoperable</strong><br /><i>Abstract:&nbsp;</i>At 17:35 on 8/17/06, after approximately 10 minutes of operation during a planned surveillance test of the train A emergency diesel generator, a previously identified minor fuel oil leak (approximately 1 drop/minute)increased and required an unplanned engine shutdown. The emergency diesel generator had been declared inoperable at the start of the surveillance test and remained so following the leak. At its maximum, the leak rate was estimated at between 0.12 and 0.25 gpm. By 05:53 on 8/18/06, the leak had been repaired, the surveillance test completed, and the emergency diesel generator restored to OPERABLE status. The fuel oil leak was initially identified on 6/28/06 at 16:48. Between that initial discovery and the engine shutdown on 8/17/06, the emergency diesel generator had been operated four times with a cumulative run time of approximately 3.9 hours. On 10/26/06, the leak was determined to be from an approximately 350 degree circumferential crack in the copper tubing of the fuel supply line inside a 3/8" fitting to a pressure gauge. On 12/15/06, the cracked tubing was tested on a similar diesel generator. The tubing fully severed after approximately one hour of diesel generator operation at rated load. Thus it is concluded that the EDG was not capable of meeting its design basis between the originally identified leak on 6/28/06 and its return to operability on 8/18/06.
3052006010 | Kewaunee | 08/01/2006 | 10/02/2006 | ML06285026 | <strong>Inadequate Calibration of Radiation Monitor R-19</strong><br /><i>Abstract:&nbsp;</i>On 8/1/2006, it was determined that Kewaunee was not meeting the definition of Channel Calibration for radiation monitoring channel R-19, Steam Generator Blowdown System. The sources used to calibrate radiation monitoring channel R-19 were incapable of producing sufficient counts to test detector response above the High Level alarm (trip) setpoint. As part of the calibration, the setpoints were functionally tested by exposing the detector tube to a flashing LED, which simulates radiation. The limited frequency of the LEDs required the setpoints to be lowered for this functional test and then restored to their desired value after the test. KPS believed that the detectors had a linear response up to 1E+7 cps (which encompasses the Alert and High Alarm setpoints). Therefore, since digital setpoints do not drift, this method was considered acceptable for functional testing. Due to NRC concerns with the above calibration method, sources of sufficient strength to calibrate the detector above the Alert and High Level alarm setpoints were recently obtained. The calibration using these new sources discovered that R-19 responds linearly up to 5.68E+5 cpm but non-linearly at 1E+7. Therefore, this detector has not been properly calibrated and has been inoperable. However, channel counts never exceeded the highest known linear level (5.68E+5 cpm), and the detectors were reading accurately below this level. Thus, this event has a low safety significance. This event is being reported under 50.73(a)(2)(i)(B) as an operation which was prohibited by the plant's Technical Specifications (TS), and also as a Special Report required per TS Section 6.9.b.3 and Step 3.0.3 of the Off-Site Dose Calculation Manual (ODCM).
3052006012 | Kewaunee | 10/30/2006 | 12/29/2006 | ML07066004 | <strong>Reactor Trip from Loss of Instrument Bus</strong><br /><i>Abstract:&nbsp;</i>At 8:48 CST on 10/30/2006, Kewaunee Power Station tripped from approximately 92% full power due to steam generator B steam flow feedwater flow mismatch coincident with low water level on steam generator B. The cause of the plant transient that led to the reactor trip was a loss of the red instrument bus. The bus deenergized due to component failure during the performance of maintenance on its inverter. Following the reactor trip; - The auxiliary feedwater pumps automatically started, as designed, due to low-low level in the steam generators. No other safeguards systems actuated during the transient. - Non-safety related valve MS-201 B1, steam supply to reheater 1B reheater inlet valve, did not fully close. This resulted in pressurizing high pressure feedwater heater (15B) causing relief valve HD-130B, 15B headwater heater relief valve, to lift. - After the turbine trip, during bus transfer, non-safety related 4160V reserve auxiliary transformer breaker failed to close resulting in bus 4 losing power. This resulted in a loss of circulating water flow, which, in turn, caused a loss of condenser vacuum and condenser steam dump valves. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of the reactor protection system and the auxiliary feedwater system.
3052006013 | Kewaunee | 11/10/2006 | 01/09/2007 | ML07017036 | <strong>Reactor Trip from Nuclear Instrumentation Low Range-High Flux Trip Caused by Blind Relay Contact Failure</strong><br /><i>Abstract:&nbsp;</i>On 11/10/2006 at 14:20 CST, Kewaunee Power Station experienced a reactor trip while reducing power at 1/2 percent per minute during a planned shutdown to investigate abnormal temperature and vibration indications on the turbine number nine bearing at the turbine generator exciter. At approximately 10 percent reactor power as permissive P-10 cleared, a spurious reactor protection system actuation occurred due to failed open relay contacts on the B train associated with power range nuclear instrumentation N-41. The bistable for power range nuclear instrumentation N-42 was in a tripped condition due to an unrelated failure on 11/09/2006. When P-10 automatically unblocked, the power range nuclear instrumentation low range-high flux trip was generated. Following the trip, steam supply to reheater B1 inlet valve, MS-201B1, did not fully close and had to be isolated to limit the plant cool down. Main steam isolation valves remained open and the normal condenser heat sink remained available. Main feedwater regulating valve, FW-7A, did not automatically close on the reactor trip coincident with low Tave (554 deg F). The valve did not respond to manual closure actions. Level in A steam generator rose to 67 percent which initiated a feedwater isolation signal. The feedwater isolation signal tripped the running A main feedwater pump and main feedwater valves isolated. The A and B motor driven auxiliary feedwater pumps started as designed.
3062006001 | Prairie Island 2 | 02/05/2006 | 04/06/2006 | ML06097003 | <strong>Unit 2 Shutdown Required by Technical Specifications due to Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On January 29, 2006, Nuclear Management Company, LLC, (NMC) Staff removed the Train B, Unit 2 emergency diesel generator (D6) from service for planned maintenance. Technical Specification (TS) 3.8.1, "AC Source - Operating," Condition B, "One DG inoperable," was entered. TS Required Action 3.8.1.B.4 requires D6 be restored to operable status with a Completion Time of 7 days. The planned maintenance activities included replacing two sets of two pistons, rings and cylinder liners on Engine 2 of D6 (D6 is a tandem-engine diesel generator). Return-to-service testing was initiated on February 3, 2006, and at approximately 0000 CST on February 4, 2006, the test was halted due to high-indicated crankcase pressure on Engine 1 (not the engine that was worked on). The test procedure specified shutting down the diesel generator if crankcase pressure on either engine exceeds 30mm for more than a few minutes (the setpoint for the crankcase pressure trip is 52 mm). Initial investigation of the cause of the high-indicated crankcase pressure on Engine 1 attributed the crankcase pressure to abnormal blow-by. Evaluation of the scope of work to return D6 to operable status and the schedule for completing the work indicated that repairs could not be completed within the remainder of the 7-day Completion Time. NMC commenced shutdown of Unit 2 on February 5, 2006.
3062006002 | Prairie Island 2, Prairie Island 1 | 11/27/2006 | 01/23/2007 | ML07024017 | <strong>Unit 2 Event Monitoring Instrument Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the Unit 2 refueling outage, Nuclear Management Company, LLC (NMC) staff were inspecting the cables for Unit 2 neutron flux monitor channels 2N51 and 2N52 in response to an improper splice identified on the Unit 1 cables for neutron flux monitors earlier in 2006 (see Licensee Event Report (LER) 1-06-03). NMC staff found that neither 2N51 nor 2N52 had the required shim in the sleeves for the splice connection on their respective cables. The gap due to the missing shims could have exposed the associated connectors to accident environments and is an untested configuration for environmental qualification purposes. As a result of the improper Raychem splice installation, 2N51 was declared inoperable on November 27, 2006 and 2N52 was declared inoperable on November 28, 2006. Technical Specification 3.3.3, Condition D, requires that if one or more functions with two required channels are inoperable, one channel is to be restored to operable status within seven days. Condition H requires the unit to be in Mode 3 within six hours if Condition D is not met. The potential exists that the subject splices were inoperable from the time they were installed (several years before), and that Unit 2 had been operating in a condition prohibited by Technical Specification 3.3.3. The subject splices were corrected prior to returning Unit 2 to Mode 2.
3112006003 | Salem 2 | 09/26/2006 | 11/27/2006 | ML06341022 | <strong>Manual Reactor Trip due to Elevated Reactor Coolant Pump Seal Leak-off</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2006 at 1513, with Salem Unit 2 in an end of cycle (EOC) coast down at 94% power, a manual reactor trip was performed due to elevated seal leak-off flows on 21 Reactor Coolant Pump (RCP). The 21 RCP number one seal leak-off flow exceeded the pump trip criteria of greater than 6 gpm. The reactor trip actions and plant recovery were performed without complications. A root cause team determined that the most probable cause is the combination of dissolved oxygen being introduced into a low boron and low lithium Reactor Coolant System which caused corrosion products to become dislodged from the system and deposited onto the RCP seals. Corrective actions are to improve procedures to better cope with EOC chemistry conditions. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
3112006005 | Salem 2 | 10/29/2006 | 12/21/2006 | ML07004009 | <strong>Automatic Start of Auxiliary Feedwater Pumps in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2006, with Unit 2 in Mode 5 and starting up from its fifteenth refueling outage, Main Turbine surveillance testing (ST) was in progress with the turbine governor and stop valves open. The ST procedure allows testing with the plant to in Mode 5, Mode 6, or Mode 4 with the main steam isolated from the main turbine. Later in the day, the plant transitioned into Mode 4. This mode change procedurally required that the Main Steam Isolation Valves (MSIVs) and bypass valves be closed; however, not all members of the operating shift realized the requirement. During the performance of the turbine testing, post maintenance testing activities on the 22 loop MSIV were requested. Some of the shift Operations personnel were briefed on the opening of the MSIV for retest, but failed to recognize that the Main Turbine stop and governor valves were open. As the MSIV stroked opened, the 22 Steam Generator (S/G) narrow range indicated level decreased, generating an Engineered Safety Features automatic start signal for the 21 and 22 motor driven Auxiliary Feedwater pumps. Operators promptly restored indicated feedwater level to 22 S/G. The cause of this event is attributed to inadequate oversight of plant activities and is reportable in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section."
3152006001 | Cook 1 | 07/30/2006 | 09/27/2006 | ML06278019 | <strong>Plant Shutdown Required by Technical Specification Action 3.6.5.B.1</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2006, at 0730 hours, a unit shutdown was initiated in accordance with Technical Specification (TS) 3.6.5, Containment Air Temperature, Action 3.6.5.B.1. This action requires that the unit be placed in Mode 3 within six hours if containment air temperature is not restored to within limits during the previous eight hours. On July 29, 2006, at 2026 hours, TS Condition 3.6.5.A was entered due to containment lower compartment average air temperature exceeding the TS Limiting Condition for Operation 3.6.5.b limit of 120 degrees Fahrenheit. Efforts to reduce the containment temperature during the eight-hour completion time of TS Action 3.6.5.A.1 were unsuccessful. In accordance with normal plant operating procedures and TS Action 3.6.5, Condition B, Required Action B.1, Unit 1 entered Mode 3 on July 30, 2006, at 1014 hours. All safety systems and plant equipment used in the shutdown functioned as designed. The causes of the Unit 1 shutdown were: 1) the containment cooling water system design did not support continued plant operation with sustained high cooling water (Lake Michigan) temperatures and potential for cooler fouling; and 2) a failure by Engineering personnel to recognize and communicate that an evaluation supporting past operability would not permit unit operation under some possible operating conditions during the summer (a loss of operating margin), resulting in a delay in communicating the impact of the lost margin to station management so compensatory actions could be developed at an earlier time. Corrective actions include: 1) changes to engineering procedures for identifying and managing margin changes; 2) requirement to install a temporary modification for supplemental containment cooling prior to the summer season until a design change can be implemented; and 3) development of an analysis to support removal of containment ventilation cooling units for cleaning while at power.
3152006002 | Cook 1 | 10/03/2006 | 06/20/2007 | ML07179040 | <strong>Failure to Comply with Technical Specification Requirement 3.6.13</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2006, following an inspection of the Donald C. Cook Nuclear Plant Unit 1 containment divider barrier seal, Indiana Michigan Power Company (I&M) personnel discovered that contrary to Technical Specification (TS) 3.6.13, Divider Barrier Integrity, one divider barrier seal retaining bolt was missing and a second divider barrier seal retaining bolt was missing its associated nut. The investigation of this condition determined the missing components had previously been identified in November 1998. However, the 1998 evaluation of the condition failed to identify the TS noncompliance and subsequent corrective actions failed to correct the condition. This supplemental licensee event report is being submitted following revision of the causal investigation to incorporate revised causal statements. The historical nature of the event made it difficult to definitively identify the cause of I&M's failure to correct the condition in 1998.The probable causes of the inadequate initial evaluation and correction of the identified condition included inadequate communication, inadequate information verification and validation, and tunnel vision. The probable causes for not finding the missing bolts during the subsequent inspections are: inadequate oversight; inadequate training of personnel; and/or personnel error. The missing bolt and nut were replaced.The governing surveillance procedures have been placed on administrative holduntil the procedures are enhanced to require the performance of an engineering evaluation of all areas of the divider barrier seal not inspected during each refueling cycle. Additionally, training will be provided prior to conducting future similar testing activities. The failure to comply with TS 3.6.13 is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B).
3152006003 | Cook 1 | 10/24/2006 | 12/13/2006 | ML06356039 | <strong>Failure to Comply with Technical Specification 3.3.6, Containment Purge Supply and Exhaust System Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2006, Donald C. Cook Nuclear Plant Unit 1 was in MODE 6, Refueling, with core alterations in progress and the containment purge system (CPS) [VA] in service, with the CPS exhaust isolation valves open. While in this configuration, the Unit 1 Train B solid state protection system (SSPS) [JG] output mode selector switch was placed in the test position, causing the automatic isolation capability for the Train B CPS supply and exhaust valves to be inoperable. Technical Specification (TS) 3.3.6, Containment Purge Supply and Exhaust System Isolation Instrumentation, requires two operable trains of automatic and manual isolation capability for the CPS penetrations when moving irradiated fuel assemblies in the containment building. The inoperable condition of the Train B CPS supply and exhaust valves was not immediately recognized and no immediate actions were taken to either restore operability to the valves, close the valves, or terminate movement of irradiated fuel in the containment building. Failure to immediately stop moving irradiated fuel or close the isolation valves in the CPS containment penetrations constituted a failure to comply with TS 3.3.6. The causes of this event included inadequate procedural controls and personnel error. Corrective actions include enhancements to the applicable procedures. The failure to comply with TS 3.3.6 is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B).
3162006001 | Cook 2 | 03/13/2006 | 05/11/2006 | ML06143034 | <strong>Failure to Comply with Technical Specification 3.6.2, Containment Air Locks</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2006, at approximately 0941 hours, with Donald C. Cook Nuclear Plant (CNP) Unit 2 in MODE 1, Maintenance test technicians performed pressure testing of the inner and outer Unit 2 Containment Airlock (2-AIRLOCK-C612) door seals. The inner airlock door was the first door to be tested and this surveillance testing was successfully completed. Pressure testing of the outer airlock door seals was not successful and air could be heard escaping during the test. Investigation revealed that on March 13, 2006, contract Maintenance personnel exited the Unit 2 Containment via 2-AIRLOCK-C612 at approximately 1115 hours. These individuals failed to ensure the latch for the outer airlock door was fully engaged. This resulted in the equalizing air valve failing to seat. The cause of this error has been determined to be improper operation of the airlock doors associated with 2-AIRLOCK-C612 by the contract maintenance personnel. Corrective actions included the immediate closure of the outer airlock door, ensuring the responsible personnel were instructed on the proper operation of the airlock doors, issuance of a lessons learned to all maintenance personnel to alert them of the error and to refresh them on the proper operation of the airlock doors associated with 2-AIRLOCK-C612, and the verification that placards are in place at each airlock door for both the upper and lower airlocks in both Unit 1 and Unit 2 to provide guidance on the proper operation of the airlock doors. Operations, Radiation Protection, and Engineering will also complete the lessons learned to ensure these groups understand the proper operation of the airlock doors. During the time period of this event, the inner airlock door was closed and operable and 2-AIRLOCK-C612 was capable of performing its design function. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operational condition prohibited by Technical Specification 3.6.2, Containment Air Locks. Specifically, the contract Maintenance personnel did not verify the inner airlock door was closed within one hour of the failure to fully close the outer airlock door.
3162006002 | Cook 2 | 03/23/2006 | 05/19/2006 | ML06152046 | <strong>Multiple Main Steam Safety Valve Test Failures</strong><br /><i>Abstract:&nbsp;</i>Testing of Donald C. Cook Nuclear Plant Unit 2 main steam safety valves revealed a total of 5 out of 20 unsatisfactory as-found lift pressure tests (high). All of the unsatisfactory as-found lift pressures were above the acceptance band. Technical Specification (TS) Limiting Condition For Operation 3.7.1 requires a minimum of 20 (5 per steam generator) to be operable in Modes 1, 2, and 3. Since a similar cause was determined for the multiple unsatisfactory as-found lift pressures, this condition may have arisen over a period of time, and there is a likelihood that the affected main steam safety valves may not have been operable during plant operation.Therefore, this occurrence is considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plants TS and 10 CFR 50.73(a)(2)(vii) as a common cause of inoperability. The apparent cause of the occurrence is nozzle disc bonding. Immediate corrective action was that all affected safety valves were adjusted to within TS limits and satisfactorily retested. I&M will continue to work with its vendors and industry peers to ensure it fully understands and addresses this condition, with expanded testing and adjustments to be performed as appropriate.
3162006003 | Cook 2 | 04/27/2006 | 06/23/2006 | ML06187039 | <strong>Inadvertent Emergency Core Cooling System Actuation During Testing</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2006, at 0207 hours, while in MODE 5, Donald C. Cook Nuclear Plant (CNP) Unit 2 received a main steam line low pressure safety injection (SI) signal on both trains. All components actuated as expected. Injection to the reactor coolant system was precluded by the low temperature overpressure protection system alignments that were in effect. The root cause of the inadvertent SI actuation was the failure of instrument maintenance personnel to implement procedure use and adherence requirements when using the bypass function to clear the standing reactor trip signals. Immediate corrective actions included returning the bypass switches to their normal position, resetting the safety injection signal by reinstating the main steam line low pressure safety injection block, and restoring all actuated equipment to their pretest configuration. Additionally, Indiana Michigan Power Company will enhance procedural controls, provide additional training on the enhanced procedural controls, and establish specific programmatic guidelines and limitations to be implemented when using reactor protection system/solid state protection system channel bypass functions. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the CNP Unit 2 general containment isolation, emergency core cooling system, and emergency AC electrical power systems.
3162006004 | Cook 2 | 04/21/2006 | 06/29/2006 | ML06192058 | <strong>Failure to Comply with Technical Specification 3.8.2, AC Sources - Shutdown, LCO 3.8.2.b</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2006, while in MODE 5 following a planned refueling outage, it was determined that Donald C. Cook Nuclear Plant (CNP) Unit 2 failed to meet the requirements of Technical Specification (TS) 3.8.2, AC Sources -Shutdown, Limiting Condition for Operation 3.8.2.b, for 12 hours and 32 minutes between the dates of April 21, 2006, and April 22, 2006. Specifically, between 1204 hours on April 21, 2006, and 0020 hours on April 22, 2006, and again between 0319 hours on April 22, 2006, and 0335 hours on April 22, 2006, CNP Unit 2 did not have an operable emergency diesel generator (EDG). During these time periods, the Unit 2 AB EDG [EK] was out of service for planned maintenance/surveillance testing activities. Subsequently, plant personnel determined that the Unit 2 CD EDG was also inoperable due to an unidentified latent failure that resulted in mechanical binding of the fuel injector pumps. The mechanical binding of the Unit 2 CD fuel injector pumps was caused by inadequate barriers that permitted new fuel injection pumps, as supplied by the vendor, to contain foreign material of sufficient size and hardness to damage the pumps. To preclude recurrence of this event, I&M will impose cleanliness requirements on vendors who supply fuel injector pumps for application on the EDGs. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operational condition prohibited by TS 3.8.2, AC Sources - Shutdown and 10 CFR 50.73(a)(2)(v)(B) as an event that could have prevented the removal of residual heat. This report meets the reporting requirements of 10 CFR 21 for nonconforming materials installed in safety-related applications. Because the reportable condition discussed in this licensee event report was identified after the system was returned to operable status, notification of the event in accordance with 10 CFR 50.72, "Immediate notification requirements for operating nuclear power reactors," was not required.
3162006005 | Cook 2 | 04/10/2006 | 08/02/2006 | ML06228006 | <strong>Failure to Comply with Technical Specification Surveillance Requirement 3.6.1.1</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2006, 2-SI-189, ECCS Safety Valves Discharge Header To Pressurizer Relief Tank Containment Isolation Check Valve, had a required surveillance internal inspection performed on it that potentially affected the valve's leak tightness prior to performing the required as-found BC type leak rate test. This resulted in being unable to meet the Technical Specification Surveillance Requirement (SR) 3.6.1.1 to perform the as-found B&C type leak rate test. The cause of performing the required surveillance internal inspection prior to a required as-found leak rate test was a weakened barrier in that the work activity instructions did not require verification of completion of the as-found leak rate test prior to beginning the internal inspection. Corrective Actions taken were performance of an acceptable as-left leak rate test following the internal inspection, and revising the valves surveillance internal inspection work activity to verify completion of the as-found test prior to performing valve disassembly. Corrective Actions to be taken include revising all recurring work activities for Appendix J components that potentially affect a valve's leak tightness to require a verification of completion of the as-found B&C type leak rate test prior to performing an activity. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), due to being unable to meet SR 3.6.1.1.
3162006006 | Cook 2 | 04/19/2006 | 07/18/2007 | ML07213002 | <strong>Failure to Comply with Technical Specification 3.5.2</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2006, Donald C. Cook Nuclear Plant (CNP) tested the Unit 2 "B" Residual Heat Removal (RHR) system heat exchanger outlet safety valve and on April 19, 2006, CNP tested the Unit 2 "A" RHR system heat exchanger outlet safety valve. The safety valves for both trains of RHR had an unsatisfactory as-found lift pressure test (high). Technical Specification (TS) 3.5, Emergency Core Cooling Systems (ECCS); 3.5.2, ECCS - Operating, requires two trains of ECCS to be OPERABLE when in MODES 1, 2, and 3. When one or more trains are inoperable, Condition A requires that the inoperable train(s) be restored to OPERABLE status within 72 hours. Since a similar cause was determined for the unsatisfactory as-found lift pressures, this condition may have arisen over a period of time, and there is a likelihood that the affected safety valves on both trains of RHR may not have been OPERABLE during plant operation for a time longer that allowed by TS. Therefore, this occurrence is considered reportable in accordance with 10 CFR 50.73(a) (2) (i) (B) as a condition prohibited by CNP's TS and 10 CFR 50.73(a) (2) (vii) as a common cause of inoperability. The apparent cause of the occurrence is nozzle disc bonding. Corrective action included replacing both affected safety valves with new valves and the system was declared OPERABLE. Additionally, Indiana Michigan Power Company (IM) performed an extent of condition review for the corresponding valves in CNP Unit 1 and determined the event was isolated to RHR safety valves in Unit 2. This licensee event report is being submitted greater than 60 days after the event due to CNP's failure to recognize the multiple test failures constituted a reportable condition.
3172006001 | Calvert Cliffs 1, Calvert Cliffs 2 | 03/24/2006 | 12/26/2006 | ML07003050 | <strong>1A Emergency Diesel Generator Feeder Breaker Tripped due to Low Design Setpoint</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2006 with Unit 1 shutdown in Mode 6, Motor Control Center (1MCC123) Feeder Breaker (52-1703) tripped on short-time overcurrent during performance of a surveillance test procedure. Unit 2 was operating in Mode 1 at the time of the event. The feeder breaker powers safety-related auxiliaries required for operation of the 1A Emergency Diesel Generator (EDG). As a result of the feeder breaker tripping, operations personnel secured the 1A EDG and secured the surveillance test. Subsequent investigation determined that the short-time overcurrent amptector setpoint was set too low and had drifted down to a value lower than the associated inrush starting current, resulting in the feeder breaker trip. An engineering evaluation determined that the original amptector design setpoint, established by a vendor, was not adequate because the setpoint did not consider all potential loads that could be realized upon an EDG start and load during a design basis event. Corrective actions included installing a new amptector, increasing the amptector setting, and notifying the vendor. Additional actions planned include training engineering personnel and evaluating safety-related feeder breakers to ensure setpoints have adequate margin. The 1A EDG was subsequently tested satisfactorily and returned to service on March 25, 2006. This event is also reportable per 10 CFR Part 21.
3172006002 | Calvert Cliffs 1 | 04/08/2006 | 08/24/2006 | ML06241002 | <strong>Control Element Assembly Determined to be Untrippable</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2006 at 1835, Unit 1 was in Mode 2 undergoing low power physics testing following refueling. While inserting Regulating Group 2 Control Element Assemblies (CEAs), CEA 21 stopped inserting at approximately 134 inches. Comparison of CEA position indications revealed that CEA 21 did not move inwardly with the rest of Regulating Group 2 CEAs. Operators entered Abnormal Operating Procedure (AOP)-1B, CEA Malfunction, due to CEA 21 misalignment. Troubleshooting activities were initiated to determine the cause of CEA 21 failure to insert. As a result of troubleshooting, CEA 21 was declared untrippable. Technical Specification Limiting Condition for Operation 3.1.4.F was entered. Operators commenced a unit shutdown at 2342, placing the unit in Mode 3 at 2345. Operators manually tripped the reactor on April 9, 2006 at 0001. Control Element Assembly 21 remained withdrawn. At 0430, troubleshooting was commenced to determine the cause of binding. At 0459, CEA 21 was inserted to the Lower Computer Stop. The most likely cause of CEA 21 failure to insert was debris in or on top of a fuel assembly guide tube. The debris was released from the guide tube area during troubleshooting. Corrective actions include training enhancements, spent fuel pool clean-up, increased CEA testing and inspection of the affected CEA and fuel assembly during the next refueling outage.
3172006003 | Calvert Cliffs 1, Calvert Cliffs 2 | 08/30/2006 | 10/26/2006 | ML06303037 | <strong>Impact on Safety-Related Equipment Not Considered When High Energy Line Break Barrier Removed</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2006 during performance of a surveillance test, the Unit 2 auxiliary feedwater pump room double doors were open per plant procedure. However, the procedure did not consider the high energy line break design support function of the doors. As a result, the safety-related equipment in the pump room was not considered inoperable. Upon discovery of this condition, Operations declared the affected equipment inoperable while the doors were open. A subsequent review determined that all doors between the Turbine Building and the Auxiliary Building (Units 1 and 2) were credited as barriers for high energy line break events. As a result,Operations issued night orders to keep all affected doors closed, except during normal ingress and egress. A review of the control room logs over the last three years yielded several events where these barriers were defeated and the associated Technical Specification for the affected equipment was not entered. The cause of this event was determined to be inadequate barrier control procedures due to failure to incorporate corrective actions recommended from review of a regulatory issue summary. Corrective actions include changes to the barrier control procedures.
3172006004 | Calvert Cliffs 1 | 12/12/2006 | 02/12/2007 | ML07047064 | <strong>Reactor Trip due to Loose Wire During Maintenance on Turbine Control System</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2006 at 0907 a.m., Unit 1 was manually tripped due to a pressure transient on the primary system during performance of a turbine control system maintenance activity. Subsequent trouble-shooting identified a wire was broken at the wire-to-connector interface in the electrical cabinet to Turbine Control Valve 3. The broken wire resulted in inaccurate position feedback and initiated control valve closure, which caused the pressure transient. The wire was repaired and additional inspections were performed to verify there were no other broken wires. The turbine control system was tested to verify correct response and returned to service. Unit 1 was returned to service December 16, 2006.
3172006005 | Calvert Cliffs 1, Calvert Cliffs 2 | 12/17/2006 | 05/29/2007 | ML07151020 | <strong>Startup Rate Trip Bypass Removal Function Below Setpoint</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2006, at 04:25 a.m. plant personnel determined that the Reactor Protective System (RPS) Rate of Change of Power-High [or Startup Rate (SUR)] Trip would not be enabled at the Technical Specification required value of 12 percent Rated Thermal Power (RTP), decreasing, on Unit 1 RPS Channel A and Unit 2 RPS Channel C. This condition was identified by reviewing the results of Surveillance Test Procedures (STP). The most recent STPs for Unit 1 RPS Channel A and Unit 2 RPS Channel C recorded the Nuclear Instrument (NI) Level 1 Bistable resets as 11.9 percent and 11 percent RTP by local indication, respectively. The failure of the SUR Trip enabling function to reset prior to 12 percent RTP decreasing is prohibited by Technical Specifications. This condition rendered the automatic bypass removal feature inoperable for the affected channels. This event was caused by a failure to recognize that when Improved Technical Specifications were adopted at Calvert Cliffs Nuclear Power Plant in 1997, new acceptance criteria were added to the Technical Specifications for this function. The affected Unit 1 and Unit 2 SUR Channel Trip Units were placed in bypass mode upon discovery of the condition. Corrective actions to ensure the automatic bypass removal setpoints were within specifications for Unit 1 and 2 were completed at 11:30 p.m. on December 17, 2006. Technical Specification Bases and STP changes will be made to prevent future recurrence.
3182006001 | Calvert Cliffs 2 | 11/16/2006 | 02/23/2007 | ML07058010 | <strong>Reactor Trip During Performance of Maintenance Clearance Order</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2006, the Unit 2 Reactor automatically tripped due to a pressurizer pressure high signal from the Reactor Protective System, during the performance of a clearance order to support scheduled maintenance. The clearance order required opening an electrical disconnect for personnel safety. However, the personnel involved with developing and reviewing the clearance order were unaware that opening this disconnect would result in a reactor trip. As a result of the trip, Reactor Coolant System pressure increased causing the two power-operated relief valves (PORVs) to open as designed. One PORV remained open longer than expected resulting in a valid safety injection actuation signal. The PORV was replaced prior to returning Unit 2 to power. The root causes for this event were in the area of human performance. Corrective actions require clearance orders to be completed and second-reviewed at least three weeks prior to performance of scheduled maintenance and, loss of power/power restoration effects must be clearly understood when electrical isolation devices support clearance orders. Unit 2 was returned to 100 percent power on November 21, 2006. Unit 1 was not affected by this event.
3212006001 | Hatch 1, Hatch 2 | 02/17/2006 | 04/18/2006 | ML06109010 | <strong>Inadequate Surveillance Procedure Acceptance Criteria Resulted in Exceeding Secondary Containment Drawdown Time</strong><br /><i>Abstract:&nbsp;</i>On 02/17/2006 at approximately 1200 EST, Unit 1 was in the Refuel mode and aligned to Secondary Containment Type C. At that time, it was determined that within the past three years of operation the plant had operated in Secondary Containment Type A with Technical Specification Surveillance Requirement (TS SR) 3.6.4.1.3 not met. TS SR 3.6.4.1.3 requires that Standby Gas Treatment (SGT) be capable of drawing the secondary containment down to at least 0.2 inches of water vacuum, within 120 seconds. The procedure used to perform this surveillance test allowed 120 seconds to accomplish this drawdown using an energized bus and did not account for the 12 second delay in SGT initiation during an LOSP due to the diesel generator start time. On 12/12/2001 a Secondary Containment Type A test required 115.8 seconds to drawdown the Refuel Zone. The plant operated in Type A Secondary Containment for approximately 757 days before this same test was performed on 3/8/2004 when 56.4 seconds were required to drawdown the Refuel Zone. A review of the latest TS SR 3.6.4.1.3 tests was performed and determined that all of the Secondary Containment configurations for Types A, B 1, and C were within the 120 seconds. This event was caused by an inadequate acceptance criteria in the surveillance test procedure. The surveillance test procedure did not account for the 12 second diesel generator start time during a Loss of Offsite Power event (LOSP). The surveillance procedure was revised to account for the 12 second diesel generator start time.
3212006003 | Hatch 1, Hatch 2 | 10/12/2006 | 12/06/2006 | ML06341054 | <strong>Personnel Error Results in Failure to Report Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2006, it was identified that, in 1993, a determination had been made that Licensee Event Reports on Safety Relief Valve (SRV) setpoint drift due to corrosion-induced bonding were not required. This determination was based on the installation of a pressure switch actuation system as a non-credited defense-in-depth approach to addressing SRV setpoint drift, and guidance for Technical Specification use which denotes that component inoperability is assumed from the time of discovery. However, in revision 1 of NUREG-1022 issued in 1998, an example was added which discussed the reportability of multiple test failures regardless of the time of discovery. Review of the SRV data over the past three years indicates that multiple SRVs in each year failed as-found testing. Specifically, in the 2004 Unit 1 outage, 3 SRV as-found test results were greater than 34.5 psig above the Technical Specification required setting. For the 2005 Unit 2 outage, 4 SRV as-found test results were greater than 34.5 psig above the setpoint. For the 2006 Unit 1 outage, 3 SRV as-found test results were greater than 34.5 psig above the setpoint. This event was caused by personnel error in the organizations responsible for determining event reportability. Personnel failed to recognize that reporting of multiple occurrences of SRV setpoint drift should have ensued following the issuance of NUREG-1022, Revision 1 in 1998. Personnel involved in reportability determinations have been re-instructed on the need to use current regulatory guidance and review historical justifications.
3212006004 | Hatch 1, Hatch 2 | 12/19/2006 | 02/16/2007 | ML07047066 | <strong>Inadequate 10 CFR 50.59 Reviews Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2006, Unit 1 was in the Run mode at a power level of approximately 2804 CMWT (100 percent rated thermal power) when a condition prohibited by Technical Specifications (TS) was identified and corrected. Specifically, a door which is a part of the main control room (MCR) boundary had historically been left open for travel between the MCR and the MCR annex which was added in 1982. The practice of maintaining the door open during normal operation, with reliance on manual closure on initiation of the main control room environmental control (MCREC) pressurization mode, conflicted with the MCREC TS 3.7.4 requirement that the MCR boundary be maintained at all times, with allowance for MCR ingress/egress. On December 19, 2006, Southern Nuclear Company (SNC) determined that a condition prohibited by TS existed and the practice of maintaining the door open was discontinued. The radiological dose consequences of the proceduralized manual action to close the subject door upon initiation of pressurization mode were evaluated and compliance with 10 CFR 50 Appendix A General Design Criterion 19 was maintained. This event was caused by inadequate 10 CFR 50.59 reviews and lack of a complete understanding of the design function of the MCR boundary as it pertains to control room habitability and dose consequences during accident conditions. The subject door is now maintained closed, placards have been placed on all MCR boundary doors stating that the door must be maintained closed to ensure an intact MCR boundary, and lessons learned have been distributed to applicable SNC personnel emphasizing the design function of the MCR boundary. Finally, as a result of changes to 10 CFR 50.59 since the early 1980's and related issuance of more detailed guidance by the NRC and the industry, SNC has implemented more rigorous training and procedures regarding 10 CFR 50.59 implementation.
3232006001 | Diablo Canyon 2 | 03/31/2006 | 05/01/2006 | ML06129056 | <strong>10 CFR 21 Notification of a Defective Residual Heat Removal Check Valve</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2006, at approximately 1150 PST, Pacific Gas and Electric Company (PGE) Vice President - Diablo Canyon Operations and Station Director, concurred with a quality review determination that a significant defect potentially adverse to safety was identified in a component received from Flowserve, Flow Control Division, of Raleigh, North Carolina. The component is an 8-inch tilting disk check valve, Vendor Assembly Drawing W9023267, that was received for use in the Residual Heat Removal (RHR) System, but not yet installed. On March 31, 2006, at 1301 PST, PGE notified the NRC in accordance with 10 CFR 21.21(d)(1) via Event Notification Number 42459. PGE repaired the valve in accordance with vendor instructions, following which it was successfully bench tested. The valve is scheduled for installation during the Unit 2 Thirteenth Refueling Outage. PGE does not know of similar installations at other facilities that are potentially affected by the identified defect, and is providing this report in accordance with 10 CFR 21.21(d)(3)(ii).
3232006002 | Diablo Canyon 2 | 05/03/2006 | 05/19/2006 | ML06145013 | <strong>Steam Generator Tube Plugging due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2006, at 0214 PDT, with Unit 2 in Mode 6 (refueling, with the reactor defueled), analysis of eddy current testing on Steam Generator (SG) 2-4 indicated that greater than one percent of the tubes were defective. Pacific Gas and Electric Company (PGE) made a nonemergency report to the NRC as required by Technical Specification (TS) Table 5.5.9-2, "Steam Generator (SG) Tube Inspection," at 0928 PDT, via NRC Event No. 42547. On May 3, 2006, PGE discussed the preliminary results of the SG eddy current inspection during a phone conference with the Office of Nuclear Reactor Regulation. The primary cause of the SG tube cracking was axial outside diameter stress corrosion cracking at the hot tube leg support plates. In accordance with TS 5.5.9, "Steam Generator (SG) Tube Surveillance Program," PGE has plugged all defective Unit 2 tubes identified during the current refueling outage. All defective tubes met condition-monitoring requirements at the end of Cycle 13. PGE maintains a comprehensive program to minimize SG tube degradation, and plans to replace the Unit 2 SGs at the end of Cycle 14.
3232006003 | Diablo Canyon 2 | 12/10/2006 | 02/08/2007 | ML07047026 | <strong>Manual Reactor Trip due to Reactor Coolant Pump High Temperature Indication</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2006, at 16:08 PST, licensed plant operators manually tripped the Unit 2 reactor while it was subcritical. An 8-hour nonemergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) was made via the emergency notification system at 2231 PST. On December 10, 2006, with Unit 2 operating in Mode 1, at 100 percent power, licensed plant operators initiated an unplanned reactor shutdown due to indications of increasing reactor coolant pump (RCP) 2-2 stator temperature. In accordance with plant procedures, operators manually tripped the reactor and shutdown RCP 2-2 when the temperature indication reached 300 F. At the time of the reactor trip, Unit 2 was subcritical in Mode 3, Hot Standby, with Control Rod Bank A at 106 steps withdrawn, all other control rods were fully inserted. All rods fully inserted in response to the manual reactor trip, and all systems functioned as required. The auxiliary feedwater system was already in service as part of the shutdown. The electrical transmission grid was stable. With the exception of RCP 2-2, all major equipment including the three emergency diesel generators remained operable. The other three RCPs maintained forced circulation of the reactor coolant system. Investigations identified that a stator resistance temperature detector (RTD) had failed causing a false RCP 2-2 increasing temperature indication. The failed RTD input to the PPC monitoring was replaced with an installed spare RTD that was verified to be operating satisfactorily.
3232006004 | Diablo Canyon 2 | 12/12/2006 | 02/12/2007 | ML07053031 | <strong>Automatic Reactor Trip due to Circulating Water Pump Surge Capacitor Failure</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2006, at 1322 PST, with Unit 2 at approximately 25 percent power, an electrical failure occurred in the circulating water pump (CWP) motor enclosure for CWP 2-1. An Emergency Notification System (ENS) Notice of Unusual Event (NUE), Number 23, Confirmed Explosion Onsite, was reported in accordance with 10 CFR 50.72 (a)(1)(i) at 1359 PST. The NUE was terminated at 1430 PST following confirmation that the initial report was due to a CWP 2-1 electrical discharge and fire, that was extinguished. On December 12, 2006, at 1541 PST, ENS Event Number 43047 was updated to include a 4-hour report in accordance with 10 CFR 50.72 (b)(2)(iv)(B) due to a Reactor Protection System actuation while critical, and an 8-hour notification in accordance with 10 CFR 50.72 (b)(3)(iv)(A) due to the actuation of the accelerated system. All equipment responded as designed. The CWP 2-1 surge capacitor was replaced and the associated electrical system was repaired. The cause of the failure was a single random failure of the surge capacitor. Corrective actions will include replacing the 12kV three phase surge capacitors with more reliable single phase surge capacitors and enhancing the preventive maintenance program.
3242006001 | Brunswick 2 | 11/01/2006 | 12/29/2006 | ML07009043 | <strong>Loss of Startup Auxiliary Transformer Results in Unit 2 Manual Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2006, at approximately 18:23 (EST) Unit 2 experienced a loss of the unit's Startup Auxiliary Transformer resulting in a loss of reactor forced circulation and initiation of a manual Reactor Protection System actuation. All control rods properly inserted when the manual reactor scram was performed. Due to the loss of the Startup Auxiliary Transformer offsite power to the unit's power buses was lost when the Unit 2 main generator tripped. The four Emergency Diesel Generators (EDGs) properly started and EDGs 3 and 4 supplied the Unit 2 emergency buses. Appropriate Primary Containment Isolation System (PCIS) isolations occurred upon the loss of power to the unit's power buses. An expected Reactor Pressure Vessel coolant shrink resulted in the coolant level decreasing below the Reactor Vessel Water Level - Low Level 1, with appropriate PCIS isolations. Additionally, coolant level subsequently reached Low Level 2, at which point an additional PCIS isolation and system actuations appropriately occurred. Loss of the SAT was caused by an ineffective mechanical connection between the SAT's x-winding non-segregated bus and the associated bus bar. The root cause of the event is the ineffective connection combined with the fact that the condition monitoring performed for this bus was not adequate to detect the latent problem. Corrective actions include implementation of enhanced predictive maintenance requirements that will include thermography inspections and trending of all Unit 1 and Unit 2 non-segregated buses.
3242006002 | Brunswick 2 | 11/11/2006 | 01/10/2007 | ML07017046 | <strong>Manual Scram due to Conductivity Increase</strong><br /><i>Abstract:&nbsp;</i>At 1243 EST on November 11, 2006, with the reactor critical and in Mode 2 for startup activities, high conductivity in the condenser resulted in initiation of a manual Reactor Protection System actuation. All control rods properly inserted when the manual reactor scram was performed. No emergency core cooling systems (ECCS) actuated. At the time of the conductivity excursion, the condensate/feedwater system was not feeding the vessel, thus the reactor water chemistry was not adversely affected. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The high conductivity in the condenser was determined to be the result of missing plugs on 165 condenser tubes, of which 17 of the tubes were found leaking (i.e., existing tube leaks reopened). The root cause is the failure to have procedural guidance to inspect the condenser water boxes for missing tube plugs following a Loss Of Offsite Power (LOOP) event. Corrective actions included reinstalling the missing plugs and checking all plugs for tightness.
3242006003 | Brunswick 2 | 12/25/2006 | 02/23/2007 | ML07065045 | <strong>Automatic Reactor Scram due to Trip from Neutron Monitoring System</strong><br /><i>Abstract:&nbsp;</i>On December 25, 2006, at 0539 an automatic reactor scram occurred on Unit 2 due to a Reactor Protection System (RPS) actuation. The unit was operating at 64% reactor power in single recirculation loop operation when the RPS actuated on Neutron Monitoring System Oscillation Power Range Monitors (OPRMs), channels 2 and 4. All control rods properly inserted. Reactor water level reached Low Level 1 (LL1) and Low Level 2 (LL2) as a result of the scram. The LL1 signal caused a Group 2, Group 6, and Group 8 isolation signal. All LL1 actuations occurred as designed. The LL2 signal causes a Reactor Core Isolation Cooling (RCIC) actuation, a High Pressure Coolant Injection (HPCI) actuation, a Group 3 isolation, a secondary Containment isolation, a Standby Gas Treatment initiation (SBGT), a Control Room Emergency Ventilation (CREV) initiation, a Reactor Recirculation Pump trip, and an Alternate Rod Insertion (ARI) actuation signal. The LL2 condition was reached momentarily, and did not affect all instruments. Further evaluation concluded that the appropriate LL2 isolations and actuations occurred as designed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in manual or automatic actuation of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The root cause of this event was determined to be inadequate incorporation of Operating Experience into plant procedures and training.
3252006001 | Brunswick 1, Brunswick 2 | 01/12/2006 | 03/09/2006 | ML06076015 | <strong>Control Room Emergency Ventilation (CREV) and Air Conditioning (AC) Inoperable due to Loss of Control Air</strong><br /><i>Abstract:&nbsp;</i>At 0400 hours on January 12, 2006, the 2A Control Building (CB) Instrument Air Compressor was taken out of service for scheduled maintenance. On the same day, at 0920 hours, the Control Room received annunciator, CB INSTR AIR PRESS LOW, and determined that the in-service 2B CB Instrument Air Compressor was not maintaining pressure. Shortly after receiving the annunciator, the Control Room Emergency Ventilation (CREV) and Control Room Air Conditioning (AC) systems shutdown due to the resulting loss of control air. The two CREV subsystems and the three Control Room AC subsystems required by Technical Specifications (TS) 3.7.3 and 3.7.4, respectively, were declared inoperable. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Operability of the Control Room AC subsystems and one CREV subsystem was restored at 1014 hours when the 2A CB Instrument Air Compressor was returned to service. The safety significance of this event is considered minimal. The root cause of this event was determined to be ineffective condition monitoring of compressor oil pressure to detect hydraulic unloader degradation. Preventive Maintenance work orders for inspection and oil change have been initiated. The 2A and 2B CB Instrument Air Compressors have both been replaced with new compressors.
3252006002 | Brunswick 1 | 03/21/2006 | 05/18/2006 | ML06153028 | <strong>Cracking Found In B Loop Core Spray Header Piping</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2006, as a result of visual examinations of reactor vessel internals during the Unit 1 refuel outage (i.e., B116R1), cracking was identified on a Core Spray (CS) system header piping weld (i.e., weld P3c-270). Subsequently, on March 21, 2006, Ultrasonic Test (UT) examinations of the entire weld were performed to determine the extent of the indication on the portions of the weld inaccessible to visual examinations and to more accurately size the indications. The UT examination results demonstrated that the as-found condition of the weld was unacceptable for operation without repair. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B), as an unanalyzed condition that significantly degraded plant safety and 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications. The root cause of this event is intergranular stress corrosion cracking (IGSCC) in the heat affected zone (HAZ) of weld P3c-270. On April 1, 2006, weld P3c-270 was repaired by installation of a clamp designed to structurally replace the weld. The clamp was designed in accordance with Boiling Water Reactor Vessel and Internals Project (BWRVIP) Report BWRVIP-19-A, "BWR Vessel and Internals Project, Internal Core Spray Piping and Sparger Repair Design Criteria," which includes BWRVIP-84, "BWR Vessel and Internals Project, Guidelines for Selection and Use of Materials for Repairs to BWR Internal Components."
3252006003 | Brunswick 1, Brunswick 2 | 04/10/2006 | 06/07/2006 | ML06165029 | <strong>Control Room Emergency Ventilation (CREV) System Inoperable due to Chlorine Detection Modification Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1630 on April 10, 2006, plant personnel identified a potential failure mode of the recently modified chlorine detection system. The failure mode has the potential to render the Control Room Emergency Ventilation (CREV) system inoperable following power restoration after a Loss of Offsite Power/Loss of Coolant Accident(LOOP/LOCA) event. Due to this design deficiency, the CREV system was declared inoperable per Technical Specification (TS) 3.7.3, "Control Room Emergency Ventilation System," which placed Units 1 and 2 in Condition B of TS 3.7.3. This required the units to be in Mode 3 within 12 hours and in Mode 4 within 36 hours. At 2100 on April 10, 2006, the CREV system radiation and smoke detection mode was restored to operable after removal of the chlorine tank car from the exclusion area and disabling the chlorine detectors to prevent them from operating. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The safety significance of this event is considered minimal. The root cause of this event was determined to be ineffective review of the chlorine detector replacement modification prior to approval. Corrective actions include revising an engineering procedure to add a final approval checklist, revision of the modification to eliminate the unanticipated failure mode, and additional personnel training.
3252006004 | Brunswick 1 | 06/02/2006 | 11/17/2006 | ML06332044 | <strong>As-Found Values for Safety/Relief Valve Lift Setpoints Outside Technical Specification Allowed Tolerance</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2006, the Brunswick Steam Electric Plant received the results of as-found testing of 11 safety/relief valves (SRVs) which had been removed from Unit 1 during the spring 2006, refueling outage (i.e., B116R1). These results indicated that four of the 11 valves mechanically actuated at pressures outside of the 3 percent tolerance allowed by Technical Specification 3.4.3, "Safety/Relief Valves." Since Technical Specification 3.4.3 requires 10 of the 11 installed SRVs to be operable, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications. The root cause for the setpoint drift high for valves 1-B21-F013H and F013K was that proper lapping techniques were not fully understood when the BSEP SRV rebuild program began. This led to excessive lapping of the pilot disc. The root cause for the setpoint drift high for valve 1-B21-F013F was determined to be scoring of the pilot rod causing mechanical binding between the pilot rod and the pilot guide. The root cause for the setpoint drift low for valve 1-B21-F013B was leakage. The long term resolution for these items is to incorporate additional industry guidance into the SRV Rebuild Program and to replace the full complement of SRVs for the next Unit 1 and Unit 2 refuel outages.
3252006005 | Brunswick 1, Brunswick 2 | 08/06/2006 | 10/03/2006 | ML06285009 | <strong>Control Room Emergency Ventilation (CREV) System Inoperable due to Chlorine Detectors</strong><br /><i>Abstract:&nbsp;</i>At 1232 hours on August 6, 2006, the Control Room Emergency Ventilation (CREV) system unexpectedly realigned to the chlorine protection mode. Subsequent investigations determined that unexpected actuation of the chlorine detectors and realignment of the CREV system was due to sensitivity of the chlorine detectors to Nitrogen Dioxide (NO2), a constituent of diesel exhaust fumes. These detectors were installed by a modification, implemented on February 3, 2006, to replace obsolete detectors in the chlorine detection system. This failure mode has the potential to render the CREV system inoperable as a result of Emergency Diesel Generator operation in response to a Loss of Offsite Power/Loss of Coolant Accident event and is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Additionally, the event is also being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plants' Technical Specifications. No documentation existed indicating that the impact of EDG exhaust gases had been evaluated or considered in the original design of the CREV system. As a result of this undocumented and/or unconsidered design input, the modification to replace the obsolete chlorine detectors with detectors of a different design did not account for the potential impact of NO2. Operability of the radiation and smoke protection modes of the CREV system was restored and the system placed in its normal standby alignment at 1255 hours on August 6, 2006. The system has been operated in this configuration since that time.
3252006006 | Brunswick 1, Brunswick 2 | 10/27/2006 | 12/22/2006 | ML07004003 | <strong>Technical Specifications for Reactor Recirculation Pump Speed Match Criteria is Non-Conservative</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2006, plant personnel determined that Technical Specification (TS) Surveillance Requirement (SR) 3.4.1.1, which verifies that the recirculation pump speeds are within 20% of each other when operating at less than 75% of rated core flow or within 10% of each other when operating at greater than or equal to 75% of rated core flow, does not provide adequate assurance that the recirculation loops are operating within the initial conditions of the existing design bases loss of coolant accident (LOCA) analysis. SR 3.4.1.1 was a new surveillance, added during Brunswick Steam Electric Plants (BSEP) conversion to the Improved Technical Specifications in 1998. SR 3.4.1.1 required the recirculation loops to be operated with matched pump speeds, instead of matched pump flows, due to availability of control room indication. This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B), as an event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. The root cause of this event was determined to be ineffective implementation of the SR due to not fully understanding the relationship between recirculation pump speed mismatch and core flow mismatch. Corrective actions included issuing a new surveillance procedure to ensure plant operation within the design basis limits, and revising the Limited Condition of Operation (LCO) requirements of TS 3.4.1 and SR 3.4.1.1.
3252006007 | Brunswick 1, Brunswick 2 | 11/02/2006 | 01/26/2007 | ML07037017 | <strong>Operations Prohibited by Technical Specifications due to Inoperable Emergency Diesel Generator 1</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2006, at approximately 0400 EST, Emergency Diesel Generator (EDG) 1 tripped on low lube oil pressure. The EDG had automatically started at approximately 1823 EST on November 1, 2006, due to a loss of Unit 2 Startup Auxiliary Transformer and had been running unloaded. EDG 1 tripped due to a momentary drop in lube oil header pressure that occurred while refilling a cleaned lube oil duplex strainer basket with the process lube oil. The need to clean the strainer arose, in part, due to a cleaning towel that was left in the EDG 1 lube oil sump during maintenance activities performed October 23 through October 27, 2006. This towel was found at the EDG 1 engine driven lube oil pump suction strainer. As a result of the presence of the cleaning towel, EDG 1 is being considered inoperable from the time it was removed from service, for routine maintenance, on October 23, 2006, at 0208 EDT, until it was returned to service on November 7, 2006, at approximately 2125 EST. This constitutes approximately 15 days, 20 hours and 17 minutes of inoperability. The Technical Specifications (TS) allowed out of service time for an inoperable EDG is 7 days. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plants' TS. The extended inoperability of EDG 1 was a result of inadequate post-maintenance closeout inspections, which resulted in foreign material being left in the lube oil system. Corrective actions will include establishment of increased foreign material exclusion controls for the EDG lube oil systems.
3272006001 | Sequoyah 1, Sequoyah 2 | 02/09/2006 | 10/26/2007 | ML07304001 | <strong>Potential Loss of Component Cooling Water to the Seal Water Heat Exchanger During an Appendix R Fire</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2006, based on a review of an industry operating experience issue, engineering personnel identified a scenario involving a potential loss of component cooling system (CCS) water to the seal water heat exchanger during an Appendix R fire event. The scenario involves a loss of component cooling system flow to the seal water heat exchanger due to fire damage resulting in high suction temperature on the running centrifugal charging pump (CCP) causing a loss of adequate suction head (NPSH). During an Appendix R fire event, CCP suction is aligned from the refueling water storage tank (RWST), normal charging and letdown are isolated and the only reactor coolant system makeup flow is via the reactor coolant pump (RCP) seal injection flow path. If the seal water heat exchanger cooling is lost, the CCP recirculation flow and RCP seal return flow are not cooled and would mix with 30-40 gpm of cool water from the RWST resulting in concerns with pump cavitation and damage to the RCP seals. The initial evaluation of the condition focused on those fire areas where neither A-train CCS pumps were available. Subsequent investigation of the condition determined the abnormal operating procedures did not include a step to ensure an A-train CCS pump is operating for a fire in areas where only one of the A-train CCS pumps is available, since the operating pump could be affected. The cause of this event was that previous SQN fire safe shutdown analysis did not recognize the need to protect the seal water heat exchanger for hot safe shutdown, or to evaluate the ramifications of not protecting the heat exchanger. Interim compensatory measures were to post roving fire watches in the affected areas. These actions were replaced with a procedure revision to perform manual actions to ensure safe shutdown.
3282006001 | Sequoyah 2 | 03/22/2006 | 05/22/2006 | ML06146014 | <strong>Reactor Trip Resulting from Actuation of the Main Generator Neutral Overvoltage Relay</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2006, at 1624 Eastern standard time with Unit 2 operating at 100 percent power, the turbine tripped followed by a reactor trip as a result of operation of the main generator neutral overvoltage relay. The immediate cause of this event was attributed to an isolated phase bus duct gasket that came loose and caused a ground. The ground was on the electrical bus leading from the main generator to the 'C' phase main transformer. The gasket provided a path for electrical leakage to ground that was detected by the neutral overvoltage relays. The ground resulted in actuation of the main generator neutral overvoltage relay. The actuation of the relay stripped the main transformer resulting in subsequent turbine and reactor trips. The relays actuated, as designed, to prevent damage to other components. The cause of this event is ineffective corrective action of a previous similar event. The previous corrective actions from the 1995 event focused on methods to ensure retention of the gasket and did not focus on long-term equipment reliability. The Unit 2 bus duct gasket was reinstalled with additional tie-wraps to support the gasket and the bus was returned to service. The bus duct has been modified to no longer require the gasket on the Unit 1 bus ducts. The Unit 2 bus duct will be modified to remove the gasket during the upcoming refueling outage.
3312006001 | Duane Arnold | 03/05/2006 | 05/04/2006 | ML06143046 | <strong>Inoperability of Control Building/Standby Gas Treatment System (CB/SBGT) Instrument Air Compressor 1K-4</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2006, with the plant operating at 96% power in Mode 1, during testing of Control Building/Standby Gas Treatment System (CB/SBGT) Instrument Air Compressor 1K-4 per Surveillance Test Procedure (STP) 3.7.9-02, "CB/SBGTS Instrument Air Compressors System Leakage and Capacity Test," it was necessary to shutdown Compressor 1K-4 due to overheating. An unplanned Limiting Condition for Operation (LCO) was entered. It was subsequently determined that the valve stem and disc for V13-0141, 1K-4 Emergency Service Water (ESVV) Supply Header Isolation, had separated on February 8, 2006, causing flow blockage and loss of cooling flow to 1K-4. Therefore the Completion Times associated with LCO 3.7.9 were exceeded. The valve that failed was a Henry Vogt, model SW 12111, 1" gate valve. The valve disc failed due to corrosion bonding of the disc and seat upon closure and localized intergranular stress corrosion cracking (IGSCC). The disc was manufactured from 416 martensitic stainless steel with a Rockwell hardness of C50. This combination made it highly susceptible to IGSCC. There were no actual safety consequences and no effect on public health and safety as a result of this event. This event is reportable under 10CFR50.73(a)(2)(i)(B).
3312006002 | Duane Arnold | 03/18/2005 | 06/01/2006 | ML06164026 | <strong>Drywell Penetrations Calculations Do Not Account for Thermal Movement</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2005, while operating at 84% power, it was determined that a piping calculation for the Containment Vent Purge Exhaust line, did not account for thermal movement of the Drywell. Specifically, the stress model did not start at the Drywell shell and thermal anchor movements were not applied. The failure to account for thermal movement did not meet the design requirements for Drywell penetrations. As a result of the identified discrepancy, an immediate operability determination was completed that concluded that the Drywell penetration was operable based on meeting ASME Section III, Appendix F operablility criteria. As a result of an extent of condition review into this issue, all Drywell penetrations were reviewed. This review identified 14 other Drywell penetrations, for a total of 15, requiring modifications to restore them to original design requirements and 16 requiring further analysis. The 15 penetrations requiring modifications were modified during Refueling Outage (RFO) 19, which concluded on May 3, 2005. Of the 16 Drywell penetrations requiring further analysis, 8 were identified that required modifications to reestablish design margins. Operability calculations performed on these 8 Drywell penetrations identified no current or past operability concerns. As of the date of this LER, no past operability concerns have been identified concerning the 15 Drywell penetrations that were modified during RFO 19. Therefore, this LER is being submitted as a Voluntary Report.
3312006003 | Duane Arnold | 06/30/2006 | 08/30/2006 | ML06249048 | <strong>Residual Heat Removal Service Water Pump Inoperability due to Motor Cooler Failures</strong><br /><i>Abstract:&nbsp;</i>On June 30,2006, while operating at 100% power, operators identified water in the upper sight glass of the "A" Residual Heat Removal Service Water (RHRSW) Pump,1P-22A, Motor Oil Reservoir. An extent of condition review determined that the "B" and "C" RHRSW Pumps were also inoperable based on the same type and vintage motor cooler installed. As a result, 1P-22A, B, and C were declared inoperable. The inoperability of the three RHRSW pumps placed the plant in an 8 hour Technical Specification Limited Condition for Operation (LCO) to restore at least one pump in each train to operable status. The pump was restored prior to the expiration of the 8 hour LCO on July 1, 2006 with the restoration of the "C" RHRSW Pump. The cause of the motor cooling coil failures were determined to be erosion due to high Emergency Service Water (river water) flow through the copper coils of the motor coolers. This event resulted in the plant being in a condition that could have prevented the fulfillment of a safety function of a system that is needed to remove residual heat and therefore, is reportable under 10 CFR 50.73(a)(2)(v)(B). There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312006004 | Duane Arnold | 09/07/2006 | 11/06/2006 | ML06312017 | <strong>Containment Atmosphere Dilution System Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2006, while operating at 100% power, Containment Atmosphere Dilution (CAD) North Torus Inboard Isolation valve (SV-4334A) was declared inoperable as the result of not being able to fully open during testing. As a result, valve V-43-112, 'A' CAD Torus Spray Isolation, was closed and tagged in order to comply with TS 3.6.1.3, Required Action A.1 (isolate affected penetration in 4 hours). On August 31, 2006, V-43-112 was inadvertently opened after performance of a post maintenance Local Leak Rate Test. This condition existed until September 7, 2006. During this time,the unisolated inoperable containment penetration resulted in the plant being in a Condition Prohibited by Technical Specifications. This event was reportable to the NRC under 10CFR 50.73(a)(2)(i)(B). The cause of this event was inadequate execution of existing DAEC processes and expectations, as well as weaknesses in existing processes related to the tagging of primary containment isolation valves, which resulted in inappropriate actions being taken by Operations personnel associated with this event. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312006005 | Duane Arnold | 11/06/2006 | 01/05/2007 | ML07011019 | <strong>Reactor Scram During Main Turbine Testing</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2006, at 0110, while operating at 100% power, during the performance of Main Turbine Operational Tests, Surveillance Test Procedure (STP) NS93001, Section 7.3, "Overspeed Trip Device and Mechanical Trip Valve Test (Test A)," a reactor scram occurred. Investigation into this event has determined that the scram was initiated by Reactor Protection System (RPS) actuation due to at least three Turbine Stop Valves less than 90 percent open. The cause of this Turbine Stop Valve closure was a noise spike, of some level, in combination with normally open relays being closed (possibly stuck). Corrective actions included the replacement of a suspect cable, that was determined to be the most likely cause of the noise spike, the burnishing of relay contacts, and the replacement of a relay board. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3332006001 | FitzPatrick | 03/06/2006 | 05/04/2006 | ML06138014 | <strong>Inoperable Reactor Building-To-Suppression Chamber Vacuum Breaker in Excess of Technical Specifications Allowed out of Service Time</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2006, with the plant operating at 100 percent power, it was determined that the reactor building-to-suppression chamber vacuum breaker isolation valve (27A0V-101A) was not fully closed although remote position indication showed the valve was in the closed position. This condition was discovered during troubleshooting activities to determine the cause of rising oxygen concentration levels in the suppression chamber. The failure of 27A0V-101A to be fully closed resulted in not meeting LCO 3.6.1.6 for approximately 11 days and 20 hours. This period exceeded Technical Specifications (TS) 3.6.1.6 Required Action and associated Completion Time requirements of 72 hours and is therefore a condition prohibited by the plant's TS. There were no nuclear, radiological or safety consequences associated with this event. The failure of the valve to fully close was a result of mechanical binding between the valve shaft and the valve's manual actuator coupling block due to galling of the stainless steel material. Immediate short term actions included removal of the valve's manual actuator coupling block and returning the valve to an operable condition. Additional actions of performing Preventive Maintenance (lubrication) and installing new bronze bushings on valves with similar manual actuator couplings are planned and scheduled.
3332006002 | FitzPatrick | 11/04/2006 | 06/10/2009 | ML09166012 | <strong>High Pressure Coolant Injection (HPCI) System Declared Inoperable Due to Turbine Speed Oscillations</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2006, at 1810 hours, with the plant operating at approximately 20 percent power in Mode 1, Operations determined that the High Pressure Coolant Injection (HPCI) [BJ] System was inoperable due to HPCI flow and turbine speed oscillations during post work testing following refueling outage work activities. Therefore, HPCI was inoperable when MODE 1 was entered, which is prohibited by TS 3.0.4. During this post work testing, the HPCI turbine operated for approximately one minute, within required flow limits, but was manually tripped by the Operations crew when oscillations did not improve. The Operations crew declared the HPCI System inoperable until the unexpected oscillations could be evaluated and resolved. A 14 day TS LCO was entered as required. The NRC Operations Center was informed via the Emergency Notification System at 2101 hours on November 4, 2006. All other ECCS and RCIC remained operable. The turbine speed oscillations were caused by two turbine governor hydraulic actuator oil lines incorrectly connected during maintenance activities. The oil lines were reconnected to their correct ports. There were no adverse nuclear, radiological or safety consequences associated with this event.
3342006001 | Beaver Valley 1 | 02/12/2006 | 04/10/2006 | ML06102030 | <strong>Main Steam Safety Valve Relief Tests Exceeded Technical Specification Required Setpoint Tolerance</strong><br /><i>Abstract:&nbsp;</i>On February 12, 2006, Beaver Valley Power Station (BVPS) Unit No. 1 performed periodic Trevitesting on the Main Steam Safety Valves (MSSVs) just prior to entering its 1R17 refueling shutdown. All of the "C" Main Steam System header Main Steam Safety Valves [SV-1MS-101C, 102C, 103C, 104C and 105C], which were new valves that had been installed as replacements during the previous BVPS Unit No. 1 refueling (1R16), did not meet EVPS Unit No. 1 Technical Specification 3.7.1.1 acceptance criteria (+1 percent/-3 percent) for as-found lift pressures. The ten MSSVs associated with the "A" and "B" steam headers, which are original plant valves, all successfully passed the testing. The root cause of the high initial lift setpoint was oxide bonding between the discs and nozzles of the new MSSVs with 422 Stainless Steel discs installed during the previous refueling outage. This material is susceptible to the oxide bonding phenomenon. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) due to the assumption that the plant inadvertently operated with multiple MSSVs inoperable due to set points outside of their required lift setting tolerance band, without taking the actions specified in Technical Specification 3.7.1.1. The affected MSSVs will be removed and replaced with safety valves that have improved pre-oxidized Inconel X-750 discs and passivated nozzles. The risk due to the five MSSVs lifting slightly above their Technical Specification setpoint was determined to be of very low safety significance.
3342006002 | Beaver Valley 1 | 05/26/2006 | 07/21/2006 | ML06207015 | <strong>Unit Shutdown Completed as Required by Plant Technical Specification for Failed Solid State Protection System Memory Card</strong><br /><i>Abstract:&nbsp;</i>At 1046 hours on May 26, 2006, Beaver Valley Power Station (BVPS) Unit No. 1 removed Train B of Solid State Protection System (SSPS) from service to perform a routine bi-monthly channel functional surveillance test in accordance with Technical Specifications. The Unit is required to enter multiple BVPS Unit No. 1 Technical Specification Action statements for the SSPS being out of service. At 1145 hours, the Memory test portion resulted in failed indication from four memory test positions. At 1415 hours, BVPS Unit No. 1 commenced power reduction to comply with the most limiting Technical Specification Action since the memory tests were still failed and Train B remained inoperable. At 1831 hours, the reactor was shut down per the normal shutdown procedure and Mode 3 (Hot Standby) was entered. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(A) for completing a plant shutdown required by the plant's Technical Specifications. The root cause was indeterminate despite rigorous investigation. The most probable cause of the event was a poor or intermittent electrical connection in the testing circuit of Solid State Protection System. The suspect connection was narrowed down to one of three locations: Pin 4 of Universal Card A412 or the rack connector or termi-point clip for this pin. This failure would not have prevented the proper operation of the SSPS since Pin 4 is used only during testing and not during normal operation of the SSPS train. The failure of the SSPS Train B test circuit was very low risk significance.
3342006003 | Beaver Valley 1 | 07/22/2006 | 09/14/2006 | ML06262025 | <strong>Inadvertent Technical Specification Noncompliance due to Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 22, 2006, Beaver Valley Power Station (BVPS) Unit 1 initiated a work activity to replace a manual isolation valve in the Pressurizer liquid sample line outside of containment. The clearance intended to close and de-energize the outside containment isolation valve (TV-1SS-100A2) which is a normally open, fail-close, air-operated valve. The clearance activity isolated the air supply to this valve's solenoid actuator at approximately 1315 hours; however, the clearance did not provide adequate instructions to bleed off the trapped air in the valves actuator, keeping this valve open. At approximately 2310 hours, an oncoming Reactor Operator noted during his Control Board walk-down that the valve position indicating light for containment isolation valve TV-1 SS-100A2 was indicating open with a clearance tag posted on it. The valve was placed in the closed position at 2351 hours. BVPS Unit 1 did not comply with Technical Specification 3.6.3.1 Action a for an inoperable containment isolation valve, which is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant Technical Specifications. The root causes for this event were 1) human performance errors (inattention to detail) occurring during the development, review/approval and implementation process that resulted in inadequate/incomplete clearance instructions and 2) supervision/management failed to provide the necessary oversight and reinforce expectations to ensure that error prevention tools were used during work execution. The safety significance of this event was very low.
3342006004 | Beaver Valley 1 | 09/07/2006 | 11/06/2006 | ML06312017 | <strong>Reactor Trip due to a Failed Universal Logic Board in the Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2006, Beaver Valley Power Station (BVPS) Unit No. 1 experienced an unexpected reactor trip at 2157 due to an opening of the "B" Reactor Trip Breaker. All safety systems functioned as designed. All three Auxiliary Feedwater System pumps started as expected on low steam generator levels. The plant was stabilized in Mode 3 with primary and secondary parameters returned to normal hot standby values. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System. The cause of the reactor trip was due to the unexpected opening of the "B" Reactor Trip Breaker caused by a failure of universal logic card A312B output gate in the Solid State Protection System (SSPS) that produced an invalid SSPS signal to the trip breaker. The root cause was a manufacturing defect on the integrated circuit Z9 that was not identified by pre and post manufacturing testing. The plant risk associated with the BVPS Unit 1 reactor trip that occurred on September 7, 2006, is considered to be very low.
3342006005 | Beaver Valley 1 | 08/25/2006 | 11/06/2006 | ML06312016 | <strong>Failure to Comply with Technical Specification to De-energize Safety Injection Flow Path Valves</strong><br /><i>Abstract:&nbsp;</i>On September 8, 2006, during a procedure review being performed for other minor issues, a discrepancy was discovered between Beaver Valley Power Station (BVPS) Unit 1 station shutdown procedures and BVPS Unit 1 Technical Specifications (TSs). Specifically, TS Bases 3.5.4 requires isolation of the high head safety injection (HHSI) flow path in Modes 4, 5 and 6 by closing and de-energizing the isolation valves. The station procedures instruct the valves to be closed, but not de-energized. Thus, during a prior plant shutdown on August 25, 2006, HHSI flow path isolation valves had been closed but not de-energized. This was a condition prohibited by the plant's Technical Specifications, and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). There were two root causes for this event. Human performance errors occurred during the implementation of procedure changes associated with the Extended Power Uprate License Amendment Request (LAR) 1A-302 and the resulting BVPS Unit 1 License Amendment 275. Change Management was not totally effective regarding the BVPS Licensing philosophy over the last few years of expanding the content of the current Technical Specification Bases. The safety significance from this event is considered to be very low.
3352006001 | St. Lucie 1 | 01/05/2006 | 03/03/2006 | ML06076037 | <strong>Auxiliary Feedwater (AFW) Trip During Surveillance Run</strong><br /><i>Abstract:&nbsp;</i>While performing a surveillance run of the turbine driven 1C Auxiliary Feedwater (AFW) pump on January 5, 2006, with St. Lucie Unit 1 in Mode 1 at 100 percent power, the mechanical overspeed trip mechanism actuated and tripped the turbine. The turbine trip was caused by the AFW turbine trip lever not being properly re-latched following a previous surveillance on the AFW turbine. The identified failure mode would not have prevented the operator from re-latching the mechanical overspeed trip device and starting the pump. Given the availability of two other AFW pumps and the ability of the operators to correct the tripped condition within analytical bounds and time frames, the identified pump failure had minimal impact on the health and safety of the public.
3352006003 | St. Lucie 1 | 08/16/2006 | 10/16/2006 | ML06297044 | <strong>Unanalyzed Condition for Diesel Generators and Degraded Voltage Relaying</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2006, St. Lucie Units 1 and 2 were operating in Mode 1 at 100% power. An engineering evaluation was completed for an operational alignment of two component cooling water (CCW) or intake cooling water (ICW) pumps operating on the same electrical train. The evaluation concluded that these alignments would result in an unanalyzed condition. Administrative controls were established to address the identified condition. One of the apparent causes identified weaknesses in the design modification process that permitted the implementation of a plant modification resulting in a condition where two CCW pumps could load onto an emergency diesel generator (EDG) resulting in potential loss of the affected EDG. Existing EDG analyses did not include starting two CCW pumps. A second apparent cause identified latent procedural inadequacies that permitted operation of two CCW or two ICW pumps on an electrical train. This operational alignment was not evaluated as part of the degraded voltage protection scheme, and could result in the premature isolation of the offsite power circuit for a degraded voltage with loss-of-coolant accident (LOCA) condition. Corrective actions include procedure changes and planned modifications. This condition had no significant impact to the health and safety of the public.
3352006005 | St. Lucie 1, St. Lucie 2 | 12/12/2006 | 01/27/2011 | ML11035004 | <strong>Internal Conduit Penetration Seals outside Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2006, St. Lucie Units 1 and 2 were in Mode 1 at 100 percent reactor power. During the normal course of work FPL identified that the penetration seal configuration used for internal conduit penetration seals, although operable, were degraded due to inadequate qualification testing methods. The documented test results do not provide an adequate basis for qualification of the internal conduit penetration seals to perform as a 3-hour fire barrier. Approximately 1050 conduits at St. Lucie Unit 1 and approximately 2500 conduits at St. Lucie Unit 2 may be affected. The apparent cause was determined to be a legacy issue occurring during the time of the Unit 1 Appendix R modifications, and the original construction of Unit 2. The apparent cause was determined to be misinterpretation of fire test reports and guidelines from the NRC. At the time of discovery a condition report was initiated and general fire barrier impairments logged and issued in accordance with the Fire Protection Program. Corrective actions completed or planned include the development and implementation of a fire test that will bound the as-installed internal conduit seal design, a walkdown and documentation of the conduits requiring fire rated internal conduit seals, and incorporation of those seals into the inspection program.
3362006001 | Millstone 2 | 01/09/2006 | 05/26/2006 | ML06158059 | <strong>Loss of Charging Function</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2006, Millstone Power Station Unit 2 was operating in Mode 1 at 100% power. At approximately 0435, with one charging pump running, operators received a charging pump discharge pulsation dampener failure alarm. At 0455 charging header flow indication began to drop. The operators evaluated this as a loss of both facilities of the charging system. All charging pumps were declared inoperable at 0455. Additional investigation indicated potential gas binding of the charging pumps. At 0554 the operators vented and started one charging pump and declared it operable, restoring one train of the charging system. The failure of a discharge pulsation dampener bladder allowed the contained gas volume to expand into the system piping, including the suction header. The cause of the bladder failure resulted from operating the bladder at a high pre-charge pressure combined with changes made to the dampener shell during fabrication, which allowed improper seating of the bladder at the point of contact with the shell. The root cause of the event was attributed to an over reliance on industry operating experience and faulty design assumptions. Together these two factors resulted in a conclusion that passive failure of a bladder with the potential for a common mode loss of charging was not a credible event. The charging pumps have two credited safety functions associated with normal operation and shutdown of the reactor plant. These functions are Inventory Control, and Boration for Reactivity Control. For this reason the failure of the charging system is considered reportable under the provisions of 10 CFR 50.73(a)(2)(v)(A), as an event or condition that could have prevented fulfillment of a safety function of structures or systems needed to shutdown and maintain the reactor in a safe shutdown condition.
3362006002 | Millstone 2 | 02/23/2006 | 04/21/2006 | ML06122057 | <strong>Manual Reactor Trip due to Trip of Both Feed Pumps following a Loss of Instrument Air</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2006, with the plant in Mode 1 and 100% power, a Manual Reactor Trip was initiated due to a trip of both feed pumps following a loss of Instrument Air. Mechanics were attempting to replace a pipe clamp on a two-inch copper Instrument Air header on Millstone Power Station Unit 2 when an inadequately soldered joint failed on a 1/2 inch tee connection. The 1/2 inch line separated from the header and resulted in rapidly lowering Instrument Air pressure in a portion of the turbine building and shutting of an excess flow check valve, as designed. Numerous air operated valves shifted to their loss-of-air failure position. Feedwater heater high-level dump valves opened causing a reduction of heater drain flow and loss of suction pressure to the steam generator feed pumps (SGFP). Both SGFPs tripped and a manual reactor trip was initiated. The Auxiliary Feedwater System actuated as expected, however, the Number 1 Steam Generator AFW Regulating Valve went to its failed position (i.e. full open) allowing excessive flow to the Number 1 Steam Generator, which contributed to a greater than expected, cool down of the RCS. An operator was dispatched to take manual control of the regulating valve at which point RCS temperature was restored to the normal post-trip band of 530-535 F. All other safety systems functioned as designed. The plant was stabilized in Mode 3 at normal operating temperature and pressure. This event/condition is being reported pursuant to 50.73(a)(2)(iv)(A) as an event that resulted in the manual actuation of the Reactor Protection System as well as the automatic actuation of the Auxiliary Feedwater System.
3362006003 | Millstone 2 | 04/01/2006 | 05/31/2006 | ML06164026 | <strong>Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2006, Millstone Power Station Unit 2 completed a shutdown from 100% power required by the Technical Specifications due to the inoperability of the turbine driven auxiliary feedwater (TDAFW) pump. On March 29, 2006, Technical Specification (TS) 3.7.1.2 was entered when the TDAFW pump was taken out of service for maintenance and subsequent post-maintenance operability testing. During the operability test, white smoke was observed coming from the TDAFW pump outboard bearing housing vent. The test was terminated and subsequent inspection determined that the pump outboard thrust bearing had failed. The TDAFW pump could not be restored to an operable status within the specified TS allowed outage time so a shutdown was commenced on March 31, 2006, at 2220 hours. The unit reached hot shutdown at 1406 hours on April 1, 2006. The root cause of the bearing failure was overloading as a consequence of balance drum/sleeve wear caused by balance drum/sleeve misalignment. The damage progressed to the point that overloading of the thrust bearing occurred with resultant bearing failure. The time of failure was the time of discovery. Corrective actions included replacement of damaged components and review of all procedures that affect shaft alignment on HTMA model pumps (such as the TDAFW pump) to ensure correct pump assembly. This is being reported under 10 CFR 50.73(a)(2)(i)(A) as the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
3362006004 | Millstone 2 | 04/13/2006 | 06/09/2006 | ML06171051 | <strong>Failure to Enter the Technical Specification Action Statement for Inoperable Reactor Protection System Trips</strong><br /><i>Abstract:&nbsp;</i>During the course of an NRC inspection activity, a concern was raised regarding compliance with Technical Specification Limiting Condition for Operation (TS LCO) 3.3.1.1, which requires that, "as a minimum, the reactor protective (RPS) instrumentation channels and bypasses of table 3.3-1 shall be OPERABLE." Historically, Wide Range Nuclear Instrumentation (WRNI) channels were removed from service at power without declaring the associated channel of Thermal Margin/Low Power (TM/LP), Reactor Coolant System (RCS) Low-Flow, and Reactor Power Level-High inoperable. With the WRNI input inoperable, the associated automatic bypass reset function for the affected channel is also inoperable. It was identified that this condition occurred multiple times over the last three years, and for a duration that exceeded the allowed outage time and shutdown time of the associated TSAS. On this basis the condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as operation in a condition prohibited by the Technical Specifications. The cause was determined to be a weakness in licensed operator knowledge of the relationship between the WRNIs and the RPS Automatic Bypass Removal functions. There were no safety consequences associated with this event.
3362006005 | Millstone 2 | 05/02/2006 | 06/30/2006 | ML06192056 | <strong>Inadvertent Actuation of 'A' Motor Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2006 at approximately 1430, with Millstone Power Station Unit 2 at 100% power, the 'A' Motor Driven Auxiliary Feedwater (MDAFW) pump automatically started during restoration following surveillance testing. The operators immediately realized that this was an unexpected response and secured the pump. Since the input parameters for the initiation of automatic auxiliary feed (i.e., steam generator level and pressurizer pressure), were within the normal ranges, the start signal for the 'A' MDAFW pump was not valid. The actuation of the 'A' MDAFW pump is reportable under the provisions of 10CFR50.73(a)(2)(iv)(A) as an invalid actuation of a system listed in 10CFR50.73(a)(2)(iv)(B). The cause of this event was personnel error, l&C technicians did not ensure proper procedure place keeping protocol was followed and inadvertently skipped two steps in the procedure. There were no safety consequences associated with this event.
3362006006 | Millstone 2 | 10/07/2006 | 02/21/2007 | ML07065041 | <strong>Scaffolding Built for Work on Main Steam Isolation Valve (2-MS-64A) Prevented the Valve from Closing</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2006, with the plant in Mode 3, scaffolding built on August 25, 2006 to support work on the #1 steam generator main steam line isolation valve 2-MS-64A prevented the valve from fully closing during surveillance testing. The obstruction was removed within approximately one hour of discovery. An immediate report per 10 CFR50.72(b)(3)(v)(D) was made to the NRC. A review of valve closure under design basis conditions with the scaffolding interference in place concludes that the valve would not have closed for small steam line breaks downstream of the MSIV and steam generator tube rupture conditions due to insufficient pressure drop across the valve disc. An engineering evaluation determined the area around the MSIV would remain accessible to the operators and the scaffolding interference could be removed in time to complete the safety function. The root cause investigation for this event determined that supplementary instructions provided for the construction of scaffolding in the vicinity of the MSIV lacked sufficient specific information to ensure MSIV operability was not impacted. The stations scaffold evaluation process will be modified to ensure specific information is provided to maintain operability of safety related and other critical safety related systems, structures or components potentially impacted by the proposed scaffold. The scaffolding was in place for more than the TS allowed outage time, therefore this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as an operation or condition prohibited by Technical Specifications.
3362006007 | Millstone 2 | 11/21/2006 | 01/22/2007 | ML07039036 | <strong>Vendor Technical Manual Used in Common Maintenance Procedure on Support System Results in Inoperability of Redundant 480V Emergency Load Centers</strong><br /><i>Abstract:&nbsp;</i>At 14:24 on November 21, 2006 with the plant operating at 100% power in Mode 1, redundant 480V emergency load centers were declared inoperable when it was discovered that required ventilation systems were not able to perform their related support functions. Subsequent review determined that the condition had existed since November 15, 2006 when the plant entered Mode 4 starting up from a refueling outage. Upon discovery, at 14:24 on November 21, 2006, the plant entered Technical Specification 3.0.3. Operability of the 480V emergency load centers was restored at 16:05 on November 21, 2006. A vendor technical manual used in a common maintenance procedure for adding refrigerant to the associated air conditioning units did not ensure sufficient refrigerant charge to support adequate cooling of the associated emergency load centers. This condition is being reported pursuant to 50.73(a)(2)(i)(B), as an operation or condition prohibited by Technical Specifications and 50.73(a)(2)(vii) as a common cause inoperability of independent trains. Upon discovery, additional refrigerant was added to the air conditioning units restoring their functionality. The corrective action to prevent recurrence is to correct the vendor technical manual. Additional corrective actions are being taken in accordance with the station's corrective action program. The safety consequences associated with this event are under evaluation. The outcome of the evaluation, including the impact of the condition on required safety functions, will be reported in a supplement to this LER.
3362006008 | Millstone 2 | 12/21/2006 | 02/19/2007 | ML07071022 | <strong>Scaffold Impairment of Turbine Driven Auxiliary Feedwater Pump Room HELB Blowout Panel</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2006, with the plant in Mode 1 and operating at 100% power, it was identified that scaffolding was erected over the High Energy Line Break (HELB) blowout panel designed for the Turbine Driven Auxiliary Feedwater (TDAFW) pump room. Further investigation identified that the scaffolding was erected on December 11, 2006 and in this configuration, the scaffolding would have restricted the ability of the HELB blowout panel to lift should a HELB event occur. This could have resulted in a breach of the wall separating the TDAFW pump room from the adjacent Motor Driven Auxiliary Feedwater (MDAFW) pump room. The MDAFW pumps are not designed to operate in a steam environment. All three Auxiliary Feedwater (AFW) pumps were declared inoperable on December 21, 2006 at 02:05. The scaffolding was removed thereby restoring operability of the AFW pumps at 05:27. The root cause(s) of this event was determined to be a deficiency within the scaffold evaluation process. Specifically,the scaffold process does not provide clear guidance for evaluation, approval and assessment of scaffold installations. It was also identified that there is knowledge deficiency caused by inadequate training and qualification of individuals tasked with implementing the scaffold program. This is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications since the condition existed longer than allowed by Technical Specification 3.7.1.2, 10 CFR50.73(a)(2)(v)(D) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident and 10 CFR 50.73(a)(2)(vii) as a common cause inoperability of independent trains or channels.
3382006001 | North Anna 1 | 04/07/2006 | 05/24/2006 | ML06152036 | <strong>Manual Reactor Trip due to Shutdown Bank A Group 2 Step Counter Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2006, Unit 1 was in Mode 3, zero percent power, preparing for restart following a refueling outage. At 2217 hours, the "A" Shutdown Bank Group 2 step counter failed. As a result, at 2231 hours a manual reactor trip was initiated by opening the reactor trip breakers (RTB) in accordance with Technical Requirement (TR) 3.1.3. This is a valid actuation of the Reactor Protection System (RPS). On April 8, 2006, at 0111 hours a non-emergency 8-hour report was made in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Reactor Protection System. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in manual actuation of the Reactor Protection System. This event posed no significant safety implications because the reactor was subcritical when the RTBs were opened. Compliance with all Technical Requirements was achieved. Therefore, the health and safety of the public were not affected by this event.
3392006001 | North Anna 2 | 11/16/2006 | 01/09/2007 | ML07017039 | <strong>Reactor Trip due to Steam Generator Low Level Coincident with a Steam Flow Feed Flow Mismatch</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2006, at 0226 hours with Unit 2 operating at 100 percent power an automatic reactor trip occurred. The initiating signal was the "B" steam generator (SG) low level coincident with a steam flow greater than feed flow mismatch caused by closure of the "B" main feed regulating valve. This resulted in a reactor and turbine trip. Closure of the "B" main feed regulating valve was due to failure of the isolation card that provides steam flow input to the "B" SG water level control circuit. At 0357 hours a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A).This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection System and Engineered Safety Features Actuation Systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
3412006001 | Fermi 2 | 04/01/2006 | 05/24/2006 | ML06152040 | <strong>Excessive Feedwater Check Valve Leakage at Containment Penetration</strong><br /><i>Abstract:&nbsp;</i>At 0039 hours on 4/01/2006, Fermi 2 feedwater line check valves, B2100F010A and B2100F076A, failed their Local Leak Rate Test (LLRT) test. The air leakage rate of the inboard check valve B2100F010A was 324.21 standard cubic feet per hour (SCFH), and the leakage rate of the outboard check valve B2100F076A was above the measurement capability of the leak rate monitor. The penetration (X-9A) minimum-pathway air leakage value was determined to be 324.21 SCFH which is greater than the allowable containment leakage rate (La) value of 296.3 SCFH per Technical Specification 5.5.12 and higher than the allowable secondary containment bypass leakage rate of 0.1 La or 29.63 SCFH per Technical Specification Surveillance Requirement 3.6.1.3.11. The B2100F076A failure was attributed to soft seat degradation which was primarily caused by extending its service time to three operating cycles. The B2100F010A valve failure was attributed to soft seat degradation due to as light misalignment of the valve disc to the in-body seat exasperated by wear between the internal shaft and valve disc. The slight misalignment caused the soft seat along the top portion of the disc to contact the seat first resulting in a scraping action as the disc flexed to its full seat position. For both valves, the soft seats were replaced, and the soft seat service time has been limited to two operating cycles. The internal shaft for the B2100F010A valve was replaced, and the alignment between the disc and the valve seat was adjusted. Both valves were retested and met their associated LLRT acceptance criteria prior to restart of the unit.
3412006002 | Fermi 2 | 06/15/2006 | 07/26/2006 | ML06214009 | <strong>Automatic Reactor Shutdown due to Main Unit Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2006, at 1053 hours EDT, a reactor scram occurred from 100% power as a result of a main turbine /generator trip due to an internal fault on main unit transformer 2B. A reactor scram occurred as designed from the turbine control valve fast closure signal. The reactor protection system performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of approximately 134 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Reactor water was supplied by the condensate and reactor feedwater systems, and the resultant reactor steam was sent to the condenser via the main turbine bypass lines. Pressure control was maintained by the turbine bypass valves. Reactor dome pressure peaked at about 1077 psig, and none of the safety relief valves lifted. Reactor water Level 3 isolations occurred as expected. An internal fault to ground of the Z-phase of the high voltage transformer winding caused the transformer failure. The most probable cause of the internal fault is that two adjacent transformer oil coolers were taken out of service together and washed with cold water which caused the internal fault. Transformer 2B was isolated from the generator and the electrical system, and the plant was restarted at reduced power on June 18, 2006. The plant was subsequently shut down on July 8, 2006 for replacement of failed main unit transformer 2B and returned to 100% power on July 22, 2006.
3412006003 | Fermi 2 | 07/29/2006 | 09/21/2006 | ML06276030 | <strong>Automatic Reactor Shutdown due to Loss of Division 1 Power</strong><br /><i>Abstract:&nbsp;</i>On July 29, 2006 at 15:50 hours EDT, a reactor scram and main turbine / generator trip occurred due to a partial loss of feedwater accompanied by a reactor recirculation system scoop tube lock. The loss of the south reactor feedwater pump and scoop tube lock were caused by a loss of Division 1 electrical power which occurred when the transformer 2 differential relay tripped 120 kV bus 101 during an energization of transformer 2. This led to a reactor scram on reactor low water level 3. The lowest reactor vessel water level reached was 110 inches which is below the reactor low water level 2 setpoint. Plant safety system actuations and isolations occurred as expected, and the standby feedwater system was started and used to maintain reactor level in the normal range. Reactor pressure control was maintained using the turbine pressure regulator with the main condenser available as the heat sink. The event occurred during an energization of transformer 2 and was caused by a trip of the transformer 2 differential relay which is designed to preclude such a trip. Inaccurate risk perception by the Fermi organization was identified as the primary organizational cause of the event since work was allowed to be performed without adequate consideration of risk to generation that resulted in a loss of bus 101 and reactor scram. The transformer and associated relaying were removed from service, and a plant stand down (training session) was held with site personnel on the scheduling issues involved. Risk sensitive and safety related work was postponed until adequate risk reviews were performed. The plant was restarted, and the main generator was synchronized to the electrical grid on August 1, 2006.
3412006004 | Fermi 2 | 08/17/2006 | 10/12/2006 | ML06293021 | <strong>Emergency Diesel Generators Out of Service due to Undersized Control Power Transformers</strong><br /><i>Abstract:&nbsp;</i>At 1900 hrs EDT on August 17, 2006, all four emergency diesel generators (EDGs) were declared to be inoperable as a result of undersized control power transformers for each of the emergency diesel generator service water (DGSW) pumps. The concern was that the DGSW pump contactors would not receive adequate voltage to ensure they would pickup under degraded voltage conditions. The event was caused by a design error that occurred in 1998 when a design change was prepared for the replacement of motor control center (MCC) positions that did not account for the effect of higher inrush current of replacement contactors on the control power transformer sizing. At 0042 hrs on August 18, 2006, compensatory measures were put in place to restore operability to both Division 2 EDGs. On August 20, 2006, a modification was completed on the Division DGSW pump control circuits that replaced the control power transformers with properly sized control power transformers and used an interposing relay to remove remote cable resistance from the M-coil (contactor) circuits. On August 21, 2006, a similar modification was completed on the Division 2 DGSW pump circuits. During extent of condition reviews, the Division 1 EDG engine room supply fans were identified as potentially inoperable at degraded voltage conditions, and modifications were promptly performed to correct the situation. Other affected MCC positions did not involve technical specifications related equipment.
3462006001 | Davis-Besse | 01/20/2006 | 10/06/2006 | ML06285009 | <strong>Emergency Diesel Generator Engine Damaged due to Improper Torquing of Lock Nut</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2006, while preparing Emergency Diesel Generator (EDG) 2 for testing, an investigation was performed of a tapping noise heard following overhaul maintenance the prior week. When the top deck on the EDG engine was opened, damage was discovered to a cylinder valve bridge. The damage was determined to be due to an improperly torqued lash adjustment screw lock nut, which was caused by inadequate verification of the torquing. The observed damage would have prevented the EDG from operating for its duty time of one week as specified in the Safety Analysis Report. Because the EDG was inoperable from the start of the six year preventive maintenance overhaul on January 8, 2006, until repairs were completed on January 23, 2006, or more than the seven days permitted by the Technical Specifications, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. The diesel engine maintenance procedure will be revised to incorporate concurrent verification for the step that requires torquing of the lash adjustment screw lock nuts and add additional signoffs for steps that require a torquing operation to be performed. Because a structured problem solving technique was not used when the tapping sound was first heard, training in problem solving techniques has been given to applicable personnel.
3462006002 | Davis-Besse | 03/18/2006 | 05/22/2006 | ML06144028 | <strong>Ultrasonic Examination Identifies Axial Flaw Indication in Reactor Coolant Pump Drain Line Weld</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2006, with the plant shut down for refueling, ultrasonic examination of the Reactor Coolant Pump 1-1 cold leg drain line nozzle-to-elbow dissimilar metal weld detected an axial flaw indication. This ultrasonic inspection was performed in response to operating experience of leakage identified at other similar plants. Due to the configuration of the weld joint and lack of qualified depth sizing procedures for dissimilar metal welds, the length of the indication could not be accurately determined, but was estimated to be at least 0.25 inches in length. No evidence of through-wall leakage was observed during bare metal examination of the piping. This indication, caused by an inadequate welding process during initial plant construction, could not be found acceptable under American Society of Mechanical Engineers Boiler and Pressure Vessel (ASME) Code Section XI, so a repair consisting of a full structural weld overlay was performed. ASME Code relief was requested from the Nuclear Regulatory Commission for this repair method, which was verbally granted prior to plant restart. The overall safety significance of this axial flaw indication was minimal because no failures or leakage occurred, and the structural integrity of the Reactor Coolant System pressure boundary was not compromised. No unacceptable indications were found on other similar nozzles inspected as part of the extent of condition review.
3462006003 | Davis-Besse | 09/06/2006 | 11/05/2006 | ML06312017 | <strong>Degraded Condenser Pressure Due to Failed Drain Line Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2006, at 0137 hours with the plant at approximately 100 percent power, control room operators noticed rapidly rising condenser pressure. The operators commenced lowering reactor power in accordance with plant abnormal procedures, but could find no obvious cause for the increased pressure. When reactor power was reduced to approximately 45 percent power and condenser pressure remained above permitted values for continued operation, the reactor and main turbine were manually tripped at 0231 hours in accordance with procedures. Subsequent investigation determined the cause of the high condenser pressure to be air in-leakage from a broken low pressure turbine bearing waste water and oil drain pipe that is routed through the condenser. This pipe appeared to have failed as a result of cyclic fatigue that caused a complete shear of the drain pipe inside the condenser. The failed piping was plugged/capped at both ends, and the plant was returned to power operations. This report is being submitted in accordance with the 10CFR50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the Reactor Protection System.
3462006004 | Davis-Besse | 12/14/2006 | 08/29/2007 | ML07243073 | <strong>Potential Damage to Ventilation Dampers due to Design-Basis Tornado Differential Pressures</strong><br /><i>Abstract:&nbsp;</i>On December 14 and 15, 2006, with the plant at approximately 100 percent power, evaluations of ventilation systems required for safe shutdown in the event of a tornado revealed that dampers for the Low Voltage Switchgear Rooms (LVSGR) and the Component Cooling Water (CCW) Room could be overstressed during the depressurization experienced due to a design basis tornado. The overstressed dampers, which are normally closed, could be damaged to the point where they would not be able to open to allow proper functioning of the associated ventilation systems. Compensatory actions were taken to ensure the dampers were opened upon issuance of a Tornado Watch, which would allow the subject rooms to depressurize during a tornado and prevent damage to the dampers. While these actions were initially incorporated into site procedures, further evaluation determined these actions were not necessary based on resultant room temperatures with the dampers failed closed. This issue, which is due to inadequate design input for the ventilation dampers during initial plant construction, is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operation or condition prohibited by the Technical Specifications, and 10CFR50.73(a)(2)(vii) as a single cause that caused at least one independent train to become inoperable in multiple systems or two independent trains to become inoperable in a single system.
3482006002 | Farley 1 | 04/08/2006 | 06/05/2006 | ML06157003 | <strong>Main Steam Isolation Valve Failure to Close</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2006, at 0105, with Unit 1 in Mode 3 prior to cooldown for a refueling outage, during Main Steam Isolation Valve (MSIV) and Bypass Valves Cold Shutdown Valves Inservice Test, the Unit 1 downstream MSIV's failed to fully stroke closed. The A valve closed approximately 70%, and valves B and C did not move from the full-open position. On April 8, 2006, at 0700, after some cooldown, the A valve was found 90% closed, and would not move open or closed; the B valve was found 75% open, and was closed by repeated mechanical agitation; the C valve was found full open, and was closed by a single application of mechanical agitation. On April 9, 2006, at 1200, following completion of cooldown, all three valves would stroke both open and closed from the Main Control Room. This event was caused by inadequate preventive maintenance on shaft load-bearing components, improper valve assembly, omission of relevant information in the procedure and turbulence in the downstream valves resulting in a more severe duty condition than in the upstream valves. The shafts and all load-bearing components in contact with the shafts of the downstream valves have been replaced, and the quarterly partial stroke test has been re-established. Preventive maintenance (PM) for replacement of the shafts and load-bearing components in contact with the shafts will be established on Unit 1 and Unit 2 by August 1, 2006. Applicable Operations procedures have been revised. Applicable Maintenance procedures will be revised by August 1, 2006. Unit 2 valves have been partial stroke tested satisfactorily to verify that the stem will move. An engineering review to consider possible design changes to reduce the severity of the service conditions in the downstream valves will be completed by March 15, 2007.
3522006001 | Limerick 1, Limerick 2 | 12/09/2005 | 02/06/2006 | ML06037018 | <strong>Loss of One Offsite Circuit due to Invalid Actuation of Fire Suppression System</strong><br /><i>Abstract:&nbsp;</i>One of two offsite circuits tripped due to a valid actuation of the 10 station auxiliary transformer protective relays. The actuation of the A phase differential relay was caused by a spurious actuation of the fire suppression deluge system. The tripping of the transformer de-energized the 13 kV feed from the 220 kV substation to the safeguard transformer. Four of eight 4 kV safeguard busses were de-energized which resulted in four of eight emergency diesel generators (EDGs) automatically starting and running unloaded as designed. The 4 kV safeguard busses were automatically re-energized when four feeder breakers from the energized offsite circuit automatically closed as designed. Both loops of emergency service water (ESW) automatically started due to the start of the EDGs. The 10 station auxiliary transformer fire suppression deluge system manual isolation valve was closed to prevent automatic actuations. The 10 station auxiliary transformer was inspected, cleaned, tested and returned to service.
3522006002 | Limerick 1 | 03/19/2006 | 05/18/2006 | ML06145013 | <strong>SRV Position Indication on the Remote Shutdown Panel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2006 in refueling outage 1R11, a surveillance test of the Safety Relief Valves (SRV) from the Remote Shutdown Panel (RSP) was being performed. The red/open bulbs failed for the three Remote Shutdown Panel Safety Relief Valves (C, A, and N) when the SRV solenoid was returned to the closed position (de-energized) following the open function (energized). On subsequent operation, the lights failed to function. The loss of indication did not affect the ability of the SRV to be operated. The cause of the event was a faulty circuit design. When the energy of the solenoids magnetic field collapses upon de-energization, the resulting "kickback" is forced entirely into the red light bulb, which became very bright before it went out. The red bulbs were replaced and ECR 06-00138 changed the circuit design during 1R11 to incorporate a metal oxide varister (MOV), which will absorb the transient spike that occurs when the solenoid coil is de-energized.
3522006003 | Limerick 1 | 04/11/2006 | 06/21/2006 | ML06180014 | <strong>Accident Monitoring Instrument Channel Inoperable for Longer Than Technical Specification AOT</strong><br /><i>Abstract:&nbsp;</i>On Saturday April 22, 2006, the reactor operator identified that the suppression chamber air temperature recorder pen was failed downscale. Subsequent troubleshooting identified that the ribbon cable connector was unseated. The connector was re-seated which restored the failed indication. The periodic monitoring of the recorder was enhanced to ensure timely detection.
3522006004 | Limerick 1, Limerick 2 | 11/11/2005 | 11/06/2006 | ML06310036 | <strong>Offsite Circuits Inoperable due to Site Voltage Regulation Study Calculation Error</strong><br /><i>Abstract:&nbsp;</i>In response to INPO SOER 99-1 Loss of Grid-Addendum recommendation 4, an Engineering review of the site voltage regulation study calculation identified an error in the voltage drop limit. The site voltage regulation study calculation was determined to be non-conservative and could have resulted in actuation of the 4kV safeguard bus degraded voltage relays following a unit trip caused by a design bases loss of coolant accident (LOCA). This non-conservatism could have resulted in a loss of one or both in-service offsite circuits. Station procedures have been revised to declare the offsite sources inoperable when grid conditions do not support operability and direct initiation of appropriate compensatory measures. The site voltage regulation study calculation has been revised to correct the error.
3532006001 | Limerick 2 | 10/13/2006 | 12/13/2006 | ML06347047 | <strong>HPCI Ramp Generator Signal Converter Failure</strong><br /><i>Abstract:&nbsp;</i>On Sunday October 15, 2006, the Unit 2 high pressure coolant injection system turbine control valve failed to open during the weekly operability routine test. A failed ramp generator signal converter caused the event. The ramp generator signal converter was replaced and successfully tested.
3542006003 | Hope Creek | 04/21/2006 | 06/15/2006 | ML06172008 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2006, PSEG determined that three safety relief valve (SRV) setpoints exceeded Technical Specification (TS) allowable tolerance specified in TS 3.4.2.1. This specification requires SRV setpoint limits to be within +/- 3% of the specified value. The valves failing to meet limits were Target Rock Model 7567F SRVs. The testing followed Hope Creek fuel cycle thirteen. In all, a total of three of fourteen SRVs experienced setpoint drift outside of the Technical Specification 3.4.2.1 limit. The apparent cause for the three SRV setpoint failures is corrosion bonding/sticking of the pilot disc. Immediate corrective action was to replace all three valves with tested and certified spare pilot assemblies. These three valves will be disassembled and inspected to document the cause of the failure. Since the number of SRVs outside of the setpoint tolerance limit (three) was greater than the number of SRVs (one) allowed to be inoperable by Technical Specification 3.4.2.1, this condition was determined to be reportable under 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant Technical Specifications.
3542006004 | Hope Creek | 08/23/2006 | 10/23/2006 | ML06304056 | <strong>Main Steam Line Radiation Monitor Set Points</strong><br /><i>Abstract:&nbsp;</i>Latent errors in the Technical Specification Daily Surveillance Log rendered all Main Steam Line Radiation Monitors (MSLRMs) inoperable due to non-conservative monitor set points. Subsequent crew errors in implementing the required actions of the Technical Specifications led to Technical Specification (T/S) non-compliance. On August 23, 2006, PSEG determined that the set points for the MSLRMs were above the maximum allowable T/S Table 3.3.2-2 value of 3.6 times full power background. The required T/S Action to place an inoperable channel in both trip systems in the tripped condition within one hour was not completed. Causes include: - Guidance contained in the Technical Specification Daily Surveillance Log was incorrect. - Operability Screening did not initially recognize that all four MSLRMs were inoperable. - Crew independent review was not effective; the reviewer did not ensure that correct actions for inoperability were initiated.
3542006005 | Hope Creek | 05/02/2006 | 02/16/2007 | ML07058011 | <strong>Drywell Hoist Breaker Not Open prior to Operational Condition 2 Entry</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2006, the breaker 52-263042 for the drywell Safety Relief Valve (SRV) hoist 10H202 was discovered in the closed position. Technical Specification 3.8.4.1 requires that all primary containment penetration conductor over-current protective devices shown in Table 3.8.4.1-1 shall be operable in Operational Condition 1, 2, and 3, with the exception of three breakers identified with an asterisk. The breakers identified with an asterisk are to be administratively maintained open in Operational Condition 1, 2, 3, and are not required to be surveilled. Breaker 52-263042 is identified with an asterisk. Operation in Operational Condition 1, 2, and 3 with breaker 52-263042 closed is not in accordance with Technical Specifications. This condition was determined to be reportable under 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant Technical Specifications. A latent status control database (SAP) error and a procedure revision error to HC.OP-IO.ZZ-0002 (Q) "Preparation for Plant Startup" were identified as the root causes. The Database error was corrected, the procedure revised to ensure this step is not missed, and lessons learned training is being developed for Licensed Operator Training.
3612006001 | San Onofre 2 | 01/11/2006 | 03/06/2006 | ML06068008 | <strong>Both Trains of Shutdown Cooling Declared Inoperable due to the Discovery of a Through Wall Pipe Crack in Common Header</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2006, while San Onofre Unit 2 was in Mode 5 at the beginning of a scheduled refueling outage, SCE determined the source of a leak in the Shutdown Cooling System (SDCS) to be a small through-wall crack in the common discharge header of the Low Pressure Safety Injection (LPSI) pumps. SCE operators declared both trains of the SDCS inoperable. This event was reported to the NRC at 1743 PST on January 11, 2006, (NRC Event Number 42252), in accordance with 10CFR50.72(b)(3)(v)(B)as a condition that might prevent the removal of residual heat. Subsequently, SCE performed laboratory analysis of the affected pipe and confirmed the failure mechanism was high-cycle fatigue that initiated at a small weld discontinuity on the outside diameter surface of the LPSI discharge header pipe at the branch fitting that connects to a one-inch drain line. SCE is continuing to evaluate the cause of the high cycle fatigue. Based on later test results and engineering analyses, SCE concluded the pipe was capable of performing its safety functions under design basis conditions. On March 3, 2006, SCE retracted the January 11, 2006 phone report (Event Number 42252). SCE is conservatively submitting this voluntary Licensee Event Report to document this condition and inform the NRC of the corrective actions taken and planned.
3612006003 | San Onofre 2, San Onofre 3 | 07/20/2006 | 09/18/2006 | ML06271038 | <strong>Potential Emergency Diesel Generator Trip after a Seismic Event due to an Electrical Ground Fault in a Non-seismic Circuit</strong><br /><i>Abstract:&nbsp;</i>In January 2005, SCE recognized that a ground fault on a non-1E 4 kV circuit on the primary side of a non-1E transformer would not trip the 1E breaker to isolate the non-1E circuit from the emergency diesel generator (EDG). This could have resulted in the "A" train EDG tripping after an event that resulted in a ground fault on the non-1E circuit. At that time, SCE focused on the potential for fire to cause a ground on the non-1E circuitry and did not fully consider seismically-induced faults. In July 2006, the NRC questioned if a seismic event could also have caused a fault in the non-1E circuitry. SCE's reevaluation concluded that if a seismic event had occurred followed by a loss of offsite power and a ground fault on the primary side of the non-1E transformer, the "A" train EDG could have been tripped. If this occurred during an EDG "B" train outage, both EDG trains would have been unavailable. At times in the past and as allowed by the Technical Specifications, SCE has removed "B" train EDGs from service. Therefore, SCE is reporting this past condition under 10CFR50.73(a)(2)(v)(A) and (B). A modification installed in 2005 corrected this condition. The safety significance of this occurrence is minimal because the affected circuit is bypassed during SIAS-related events and SONGS is able to crosstie the EDGs between Units 2 and 3 to access the available "B" train EDG.
3612006004 | San Onofre 2, San Onofre 3 | 03/24/2006 | 03/28/2008 | ML08094047 | <strong>Late surveillances on Loss of Voltage Relays results in SR 3.0.4 violation</strong><br /><i>Abstract:&nbsp;</i>On 1/29/2008, Southern California Edison (SCE) discovered Loss of Voltage (LOVS) undervoltage relays and sequenced load relays on San Onofre Nuclear Generating Station (SONGS) Units 2 and 3 had not been tested per Surveillance Requirement (SR) 3.3.7.2, SR 3.3.7.3 and SR 3.8.1.18 within the required Frequency. This resulted from a change in the process used to schedule and track the completion of the LOVS relays surveillances. In 2000, SCE changed from refueling outage testing to on-line testing. The revised testing program for scheduling and tracking inadvertently allowed some individual components to exceed the SR Frequency. SCE reviewed the three year period preceding the discovery date, 1/29/2005 through 1/29/2008. On 3/24/2006, SONGS Unit 2 changed Mode without current SRs on the LOVS sequential loading relays. The on-line surveillance tracking program was common to both Units 2 and 3. Consequently, similar mode changes were made on both units over the same period ending on 1/29/2008. SR 3.0.4 prohibits entry into a Mode without the applicable SRs having been met within their specified Frequency. SCE is reporting this occurrence in compliance with 10 CFR 73(a)(2)(i)(B). The program has been modified and all missed relay surveillances have been completed with all response times within limits designated by TS.
3622006001 | San Onofre 3 | 02/15/2006 | 04/12/2006 | ML06104026 | <strong>Emergency Subgroup Relay Test Causes Inadvertent Fill of Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On 02/15/2006 at about 1034 PST, during a subgroup relay surveillance test of the Emergency Feedwater Actuation Signal 1 (EFAS-1) relay K-402B on Train B for Steam Generator (SG) E089, valves HV4706 and HV4715 did not close. The valves are in the Auxiliary Feedwater flowpath to SG E089. Operators terminated the surveillance. The main feedwater (MFW) control system responded as designed. SG E089 level rise stopped at about 77 percent and returned to the setpoint of about 67 percent by 1051 PST. SCE discovered that a Cutler-Hammer test switch contact block failed. The coils of a return spring for a test switch contact plunger stuck together in the compressed state due to hardened grease at the return spring. This allowed the circuit to open and reset the timing relay in the test circuit, which removed the actuation signal. SCE replaced the test switch contact block and re-performed the surveillance of the EFAS-1 subgroup relay K-402B with satisfactory results. The contact block is used only during surveillance tests and is automatically removed from the active circuit upon receipt of a valid EFAS signal. Therefore, the safety significance of the contact block failure is minimal.
3622006002 | San Onofre 3, San Onofre 2 | 03/29/2006 | 05/30/2006 | ML06157008 | <strong>Unit 3 Shutdown to Inspect Safety Injection Tank Spiral Wound Gaskets</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2006 at 0001 PST, Southern California Edison (SCE) declared both trains of the Unit 3 Emergency Core Cooling System (ECCS) inoperable, placing Unit 3 in a TS 3.0.3 shutdown action statement for not meeting TS 3.5.2. SCE took this action after discovering SIT manway gaskets degraded at Unit 2. On March 29, 2006, plant operators initiated a shutdown of Unit 3 at 0050 PST and entered Mode 4 at 1141 PST. Plant equipment performed as designed. SCE reported the initiation of the shutdown to the NRC Operations Center (Event Log No. 42451) in accordance with 10 CFR 50.72(b)(2)(i) at 0334 PST on March 29, 2005. After shutdown, Unit 3 SIT manway gaskets were found degraded but not interfering with ECCS operation. SEC replaced all SIT manway gaskets in both Unit 2 and Unit 3 with a different design. Subsequent evaluations determined that the gaskets would not have prevented the ECCS from performing its required safety function. Therefore, on May 30, 2006, SCE retracted the phone report to the NRC (Event Log No. 42451) and is submitting this voluntary LER to document this condition.
3622006003 | San Onofre 3 | 03/29/2006 | 05/26/2006 | ML06150042 | <strong>Reactor Coolant System Pressure Boundary Leak Caused by Incomplete Compression of a Mechanical Nozzle Seal Assembly Grafoil Seal</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2006, SCE initiated a controlled shutdown of Unit 3 in order to perform an inspection for a problem identified on Unit 2 (see LER 3-2006-002). At approximately 1450 PDT on March 29, 2006, with Unit 3 in Mode 4, SCE identified boric acid crystals on the Mechanical Nozzle Seal Assembly (MNSA) installed on the Unit 3 pressurizer Resistance Temperature Detector (RTD) mechanical nozzle. SCE inspected and confirmed RCS leakage past the MNSA seal and is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. SCE concluded that the RCS leak was caused by (1) primary water stress corrosion cracking of the pressurizer nozzle and (2) incomplete compression of the MNSA grafoil seal when the MNSA was installed (March 1998). SCE removed the leaking MNSA and repaired the nozzle with Inconel 690 material. In addition, the two remaining MNSAs at Unit 3 were removed and the nozzles replaced with Inconel 690 material. There are no MNSAs currently in use at San Onofre Unit 2 or Unit 3. The safety significance of this event is minimal.
3622006004 | San Onofre 3 | 09/27/2006 | 11/22/2006 | ML06332011 | <strong>Inoperable Breaker Causes Train A Charging Pump to be Inoperable for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2006 (discovery date) at approximately 0917 PDT, Unit 3 was operating at about 100 percent power when "A" train charging pump 3P190 failed to start. Upon investigation, SCE determined the pump failed to start because the supply breaker 3B0413 failed to close. Based on the cause analysis, SCE concluded the "A" train charging pump became inoperable when the breaker was last opened (September 23, 2006 at 1427 PDT). SCE is reporting this event in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TS. SCE determined that the supply breaker failed due to a failed shunt trip device (STD). The STD trip rod was sticking intermittently in the energized position, which prevented the breaker from closing. SCE replaced the STD in breaker 3B0413 and returned the pump to service on October 3, 2006. SCE is continuing to investigate the cause of the sticking STD. SCE plans to replace two other breaker operating mechanisms that were purchased in the same lot and that are installed in safety related applications. The safety significance of this condition is minimal because the "B" train charging pump was operating and the swing charging pump was operable and available to be aligned to "A" train during the time the "A" train charging pump was inoperable.
3622006005 | San Onofre 3 | 12/11/2006 | 03/07/2007 | ML07071007 | <strong>Dilution Error Results in Exceeding 20 Percent Power prior to Completion of Required Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 12/11/06, plant operators were in the process of starting up Unit 3 following a refueling outage. To support main turbine testing, about 1954 PST, operators began raising power from about 15% to 18% using boron dilution. The two operators involved erred when determining the amount of demineralized water necessary. Consequently, at about 2017 PST power briefly exceeded 20%. Operations had not yet completed all the required surveillance testing for exceeding 20% power which violated Technical Specification Requirement (SR) 3.0.4. Operators returned power below 20% about 2024 PST. As a result, there is little or no safety consequence of this occurrence. The event occurred because operators estimated boron dilution based upon an extension of the dilutions for xenon control already in progress. Operators did not follow procedures which require that the amount of reactivity insertion be obtained from a controlled source during planned load changes. Additionally, the Shift Manager and the Control Room Supervisor did not ensure that a reactivity pre-job brief was conducted prior to adding the dilution water for the power increase, which likely would have prevented the error. SCE has taken corrective actions including a stand-down with each crew, enhancements to reactivity management requirements and appropriate disciplinary action.
3622006006 | San Onofre 3, San Onofre 2 | 12/15/2006 | 04/09/2007 | ML07107032 | <strong>One train of Component Cooling Water considered inoperable for longer than allowed by Technical Specification 3.7.7 due to gas entrainment.</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2007, SCE concluded that Unit 3 Train B Component Cooling Water (CCW) system may have been inoperable between November 24, 2006 and December 15, 2006 due to entrained gas. During this period, Unit 3 was being returned to service following a refueling outage. Technical Specification (TS) 3.7.7 requires the CCW system to be operable in modes 1 through 4. Unit 3 entered Mode 4 on December 7, 2006. On December 15, 2006, with Unit 3 in Mode 1, plant operators vented CCW Train B returning Train B to operable status. Because this period exceeds the allowable out of service time limit of 72 hours as specified by TS 3.7.7, SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). The source of the entrained gas is not yet fully understood and remains under investigation. SCE is continuing to vent the CCW system in both Units to ensure the systems remain operable.
3662006001 | Hatch 2 | 01/16/2006 | 03/17/2006 | ML06076034 | <strong>Component Failure in an ATTS Card Leads to Inoperability of HPCI System</strong><br /><i>Abstract:&nbsp;</i>On 01/16/2006 at 18:31 EST, Unit 2 was in the Run mode at a power level of 2023 CMWT (72 percent rated thermal power). At that time, several annunciators alarmed and the 2E41-F003, High Pressure Coolant Injection (HPCI) system Steam Supply Outboard Isolation Valve began to close rendering HPCI inoperable. Operations personnel closed valves 2E41-F002 and 2E41-F003, primary containment isolation valves, per the requirements of the Annunciator Response Procedure (ARP) and entered the appropriate Technical Specifications Conditions and Required Actions. This event was caused by component failure. The 2E41-N658D ATTS card failed resulting in a low voltage signal to the 2E41-N660B ATTS card which initiates a HPCI isolation on High Differential Pressure. Subsequently, the 2E41-F003 began to close due to HPCI isolation signal from the 2E41-N660B ATTS card. The 2E41-003 and 2E41-F002 valves were closed at this time per the Annunciator Response Procedures which ensured complete isolation of the associated Primary Containment Penetration. The voltage transient from the 2E41-N658D card also resulted in damage to the 2E41-N658B ATTS card. Personnel inspected and checked calibration on related ATTS cards and replaced the two failed cards. After the failed ATTS cards were replaced, valves 2E41-F002 and 2E41-F003 were opened, and the appropriate functional testing was completed. The HPCI system was declared operable at 05:44 EST on 01/17/2006.
3662006002 | Hatch 2 | 04/05/2006 | 05/26/2006 | ML06159053 | <strong>Unit Scram on Turbine Control Valve Fast Closure</strong><br /><i>Abstract:&nbsp;</i>On 4/5/2006 at 00:16 EDT, Unit 2 was in the Run mode at a power level of 2804 CMWT (100 percent rated thermal power). At that time a power-load unbalance was sensed resulting in a turbine control valve fast closure. The sensed power-load unbalance was a false indication introduced by performance of a calibration procedure. Reactor pressure spiked to approximately 1125 psig, which resulted in an additional trip signal due to high reactor pressure. All control rods fully inserted. Eight of the eleven Safety Relief Valves opened as designed to mitigate the pressure transient. Pressure did not reach the nominal actuation set points for the remaining three Safety Relief Valves. Reactor water level initially decreased due to void collapse and then increased to a maximum value of approximately 60 inches due to swell after both Recirculation Pumps tripped automatically on End of Cycle-Recirculation Pump Trip per design and eight SRVs opened. Reactor water level subsequently decreased when the reactor feed pumps automatically tripped on high reactor water level per design. The minimum reactor water level decreased to approximately seven inches and was recovered with manual initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. This event was caused by a power-load unbalance created during the calibration of the KVR Generator and Main Transformer Protection Recorder. The calibration procedure was found to be inadequate in that it allowed this calibration to be performed with the main turbine on-line and at greater than 40 percent rated thermal power. The calibration procedure was revised.
3662006003 | Hatch 2 | 05/16/2006 | 07/17/2006 | ML06198060 | <strong>High Pressure Coolant Injection Inoperable due to Leaking Check Valve</strong><br /><i>Abstract:&nbsp;</i>On 5/16/2006 at approximately 9:38 EDT, Unit 2 was in the Run mode at a power level of approximately 2804 CMWT (100 percent rated thermal power). Quarterly testing of the High Pressure Coolant Injection (HPCI) system was in progress when leakage out of the bonnet on the pump discharge check valve was identified. Testing was halted and the leak was isolated. This event was caused by personnel error in that the spacer ring for the graphite pressure seal was incorrectly installed. This seal creates a leak tight boundary for the bonnet of the pressure seal valve. Incorrect installation of the spacer ring allowed a greater amount of extrusion of the pressure seal resulting in lower gasket stress. As a result, slow degradation of the pressure seal occurred ultimately resulting in a leak through the mechanical joint of the valve bonnet. After replacement of the spacer ring and pressure seal the HPCI system was functionally tested. The HPCI system was declared operable at 05:45 EDT on 5/18/2006.
3682006001 | Arkansas 2 | 10/30/2006 | 12/21/2006 | ML07003051 | <strong>Completion of a Plant Shutdown Required by Technical Specifications due to Loss of Motive Power to Certain Containment Isolation Valves as a Result of a Phase to Ground Short Circuit in a Motor Control Cubicle</strong><br /><i>Abstract:&nbsp;</i>At 1925 CST, on October 30, 2006, Arkansas Nuclear One, Unit 2 (ANO-2), initiated a plant shutdown as required by Technical Specifications because certain containment isolation valves were inoperable as a result of loss of their motive power. The reactor was manually tripped at 2134 CST, in accordance with the plant shutdown procedure. Power was lost to the valves at 1238 when the supply circuit breaker for 480 VAC motor control cubicle (MCC) 2B-53 tripped as a result of a bus to ground electrical fault. At 1244, operators dispatched to investigate the breaker trip discovered a small fire in the MCC, which they immediately extinguished. ANO-2 declared an Alert at 1304 due to a fire which affected one train of safety related equipment. Plant conditions remained stable at 67 percent power while the extent of damage was evaluated until 1925, when plant shutdown was initiated to facilitate repairs. The alert was terminated at 2000 on October 30, 2006. Repairs were completed and the unit returned to power operation at 0609 CST, on November 1, 2006. The root cause of this event was determined to be an inadequate MCC design that resulted in improper placement of a circuit breaker in the MCC. One of the three phase stabs did not make up to its associated bus bar correctly, resulting in a high resistance connection that caused melting of the stab's spring clip. An acceptable method for verifying proper stab engagement during breaker installation will be developed and incorporated into appropriate procedures.
3692006001 | McGuire 1, McGuire 2 | 06/19/2006 | 08/16/2006 | ML06263023 | <strong>Ice Condenser and Floor Cooling System Containment Isolation Valve Inoperable Longer than Allowed by Technical Specification 3.6.3.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time this historical condition was identified, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On June 19, 2006, Ice Condenser Floor Cooling (NF) air operated outside containment isolation valves, 1NF-234 and 2NF-234, were determined to be inoperable on McGuire Unit 1 and Unit 2 for a period longer than allowed by Technical Specifications. Engineering identified a historical condition affecting these valves which could potentially allow them to open after their closure on a containment isolation signal. This event was not significant with respect to the health and safety of the public. Event Cause: The cause for air operated containment isolation valves 1/2 NF-234 potentially not being able to remain closed after a containment isolation signal was attributed to inadequate actuator closing margin. This inadequacy stemmed from non-conservative system pressure considerations for ITT Grinnell diaphragm valves during original design. Corrective Actions: The valves were declared inoperable. Compensatory actions were implemented to limit system pressure increase and to restore the valves to operable but degraded or non-conforming condition. A safety grade relief valve was installed on each Unit to limit system pressure increase and to return the components to fully operable status.
3732006001 | LaSalle 1 | 02/20/2006 | 04/20/2006 | ML06116031 | <strong>Three Control Rods Fail to Indicate Fully Inserted following Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 2/20/06, Unit 1 was at approximately six percent power while shutting down for as scheduled refueling outage. At 0023 hours, approximately 20 minutes after the main turbine was taken offline, all of the main turbine bypass valves unexpectedly opened. The resulting drop in reactor and steam line pressure caused a Group 1 Primary Containment isolation and an automatic reactor scram. Following the scram, the operators observed that three control rods did not indicate fully inserted. Due to the inability to verify that shutdown criteria were met, a Site Area Emergency (SAE) was declared at 0028 hours in accordance with the current Emergency Action Level guidance. The SAE was exited and the site entered Recovery mode at 0427 hours, following determination that the reactor was in fact fully shutdown. The cause of the scram was a failed power supply in the main turbine EHC system. The three control rods failed to fully insert to position 00 due to friction from channel distortion. The EHC power supply was replaced, and actions were taken to address the channel distortion issue, including discharging fuel assemblies susceptible to channel bowing in the next operating cycle or placing them in non-control cell locations.
3822006001 | Waterford 3 | 06/12/2006 | 08/11/2006 | ML06227003 | <strong>Potential for Loss of Both Trains of Safe Shutdown Equipment from Damage due to Fire</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2006, at approximately 13:00, with the plant operating in Mode 1 at 100% Reactor Power, it was determined that a fire in Fire Area Reactor Auxiliary Building (RAB) 7 could potentially challenge the ability of the plant to achieve safe shutdown due to apparent non-feasible manual actions and potential equipment damage from a hot gas layer in the area. It has subsequently been determined that operators had other available feasible manual actions prescribed in an Emergency Operating Procedure that would have facilitated achievement of safe shutdown. However, preliminary engineering evaluations indicate that damage to redundant safe shutdown trains could have occurred from a hot gas layer in the fire area during a postulated fire. Fire Area RAB 7 has part height walls that separate the fire area into fire zones. The part height wall arrangement is part of the Waterford 3 license basis via an approved deviation. Adequate compensatory measures are in place to support current operability. The condition did not involve an actual fire event. This event did not compromise the health and safety of the general public. This event is not considered a Safety System Functional Failure since there was no actual loss of safety function.
3872006001 | Susquehanna 1 | 03/04/2006 | 04/25/2006 | ML06124038 | <strong>TS Required Shutdown due to Excessive Control Cell Friction</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2006, Susquehanna operators began the process of shutting down Unit 1 for its 14th Refueling and Inspection Outage. As had previously been experienced during Unit 1's last shutdown in October 2005, the station anticipated that some control rods would exhibit slow settling because of excessive rod-to-fuel channel friction. It was conservatively determined that those rods which failed to settle into their targeted latched position in a reasonable period of time would be declared inoperable. Technical Specification 3.1.3, "Control Rod Operability," would be entered when nine rods had been declared inoperable. Entry into TS 3.1.3.f requires that the Unit be taken to Mode 3, Hot Shutdown, within 12 hours. At the time the ninth control rod was declared inoperable at 0517 hours on March 4, Unit 1 had already been reduced to approximately 0% power. The controlled shutdown continued until 0743 hours when insertion of all rods was completed and Mode 3 had been entered by placing the mode switch to the Shutdown position. Although entry into the shutdown Tech Spec could have been avoided by inserting a manual scram before LCO control rod operability limits were threatened, station management instead implemented a decision strategy that emphasized a controlled shutdown of the Unit. Even though the plant shutdown was planned and in-progress, the shutdown became a Technical Specification mandate at 0517 hours on March 4 when the ninth control rod was declared inoperable. Accordingly, this event is being reported as a Tech Spec required shutdown per 10 CFR 50.73(a)(2)(i)(A). There were no safety consequences or compromises to public health and safety as a result of this event.
3872006002 | Susquehanna 1 | 03/23/2006 | 05/15/2006 | ML06144046 | <strong>Missed Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2006 with Unit 1 in Mode 5 for a refuel outage, Maintenance workers breached a containment electrical penetration to install a cable as part of a planned modification. On March 23, 2006 during review of a 10 CFR 50 appendix J post-modification local leak rate test (LLRT) for the penetration, it was discovered that a pre-modification LLRT had not been performed as required by the station's Containment Leakage Rate Testing Program. This constituted a missed surveillance in accordance with plant Technical Specification surveillance requirement SR 3.6.1.1.1 and is reportable under 10 CFR 50.73(a)(2)(i)(B). The apparent causes of the event were a lack of clear understanding of the procedural requirement by the programs engineer and the absence of a peer review. Because the penetration had an excellent history of leak rate results and was on an extended testing interval, it was reasonable to conclude that a pre-modification LLRT would have successfully passed its acceptance criteria. Corrective actions include the establishment of a pre-outage peer review of the outage plan and associated LLRT testing requirements for future outages. This event did not result in any actual adverse consequences to the health and safety of the public.
3872006003 | Susquehanna 1 | 04/06/2006 | 07/26/2006 | ML06219020 | <strong>Motor Operated Valve Stem Nut Failures</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary report of an event which does not specifically meet established reporting criteria. The situation discussed in this report is most closely related to the reporting criteria of 10CFR50.73(a)(2)(vii). During Susquehanna Unit 1's 14th Refueling Outage, two Motor Operated Valves (MOV) in the stations Generic Letter 89-10 program failed to stroke when called upon to do so. The first failure occurred on March 27, 2006 when the suppression pool suction valve for the D Residual Heat Removal (RHR) pump failed to close during system functional testing. Similarly, on April 6, the suction valve for the C RHR pump failed to stroke during system alignment. In both cases, the immediate cause of the valve failure was excessive wear on the internal stem nut threads of each valve. The failures did not cause RHR trains to become inoperable. Analysis has concluded that the visual inspection of valve stem grease for particulates is an ineffective means of monitoring long term stem nut thread wear. Additionally, routine preventive maintenance did not require periodic inspections of the stem nut itself. When inspections were performed, procedural guidance was not adequate. In response to these failures, Susquehanna has conducted inspections of those MOVs most susceptible to stem nut wear and has replaced stem nuts when appropriate. Additional inspections are planned. In the longer term, the station intends to incorporate changes to its MOV preventive maintenance program and to begin using MOV diagnostic data for monitoring stem nut thread wear. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3872006004 | Susquehanna 1 | 06/15/2006 | 09/27/2006 | ML06285028 | <strong>Reactor Scram During Transfer of RPS Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2006 with Unit 1 in Mode 1 at 100% power, the Control Room completed preparations to transfer Division B of the Reactor Protection System (RPS) from its normal power supply to its alternate source. The transfer momentarily de-energizes that division of RPS and results in a half-scram. During the 2006 Refuel Outage, a new Power Range Neutron Monitoring System (PRNMS) was installed. Because of differences in the original monitoring system logic and PRNMS logic, the transfer resulted in a full scram. The event was determined to be reportable under 10 CFR 50.72; reference ENS Notification EN #42642. Following the automatic scram, the Unit 1 reactor water level decreased to ˜-36". Reactor Core Isolation Cooling (RCIC) initiated and was within the instrumentation tolerance for the Level 2 setpoint of -38" to initiate High Pressure Coolant Injection (HPCI). Once reactor water level recovered, the normal feedwater system was utilized to maintain the normal operating level (+35"). Level 3 (+13") and Level 2 (-38") Primary Containment Isolation signals were received and all safety systems functioned as expected. The actuation of RPS, RCIC and HPCI systems and Primary Containment isolations are unplanned actuations of systems that are designed to mitigate the consequences of significant events and are reportable per 10 CFR 50.73(a)(2)(iv)(A). This event resulted in no actual adverse consequences to the health and safety of the public.
3872006005 | Susquehanna 1 | 08/31/2006 | 10/25/2006 | ML06312011 | <strong>HPCI Safety Function Compromised</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2006 with Susquehanna Unit 1 in Mode 1 at 100%, the High Pressure Coolant Injection System's Turbine Stop Valve did not, on an intermittent basis, attain complete closure during surveillance testing. This is significant because the HPCI ramp generator will not reset if the Stop Valve is not fully closed. Without a functioning ramp generator, HPCI would likely experience 1 or 2 overspeed trips before the governor could successfully control turbine speed. As such, Tech Spec mandated response times may not have been achieved for HPCI system starts initiated during actual emergency conditions. Friction between the valve's actuator shaft and the rod bushing, brought on by corrosion, is the most likely cause for the HPCI Stop Valves inability to fully close. Periodic replacement of the rod bushing is necessary to maintain proper operation. Investigation has revealed that an administrative error which occurred in the 1990's permitted this valve's rod bushing to remain in place beyond its ten-year intended replacement frequency. Had the rod bushing been replaced per its intended schedule, this failure would not have occurred. The rod bushing has since been replaced. Additionally, the preventive maintenance schedule has been recalculated to ensure the next rod bushing replacement conforms to the intended replacement frequency. This situation is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function required to mitigate the consequences of an accident. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3872006006 | Susquehanna 1 | 11/25/2006 | 01/24/2007 | ML07037010 | <strong>Automatic Scram due to Main Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2006 with Susquehanna Unit 1 in Mode 1 at 100%, the reactor automatically scrammed as a result of a turbine trip in response to a generator lockout. The main generator automatic voltage regulation circuitry did not positively respond to changes to the offsite grid which resulted in a loss of generator field and a subsequent unit shutdown. Investigation suggests that improper active/reactive current compensator (ARCC) settings in the automatic voltage regulation system were a probable contributor to this shutdown. In addition, a decision to forego modification of the automatic voltage regulators in a manner described in GE TIL 961-3, may also have contributed to the inability of Susquehanna's units to adequately respond to the grid disturbances. At the root of these suggested contributors to the shutdown, it has become apparent that there is a lack of sufficient, in-house understanding of the automatic voltage regulator response to a changing grid configuration. Until planned corrective actions are sufficiently completed, the Unit 1 Main Generator Voltage Regulator is being maintained in manual to ensure continued station operation during grid disturbances. In response to this event, the station intends to implement measures to ensure appropriate personnel fully understand generator control and protection schemes. Appropriate ARCC setting changes will also be established. Additionally, General Electric Technical Information Letter 961-3 will be re-evaluated and implemented if such action will enhance the unit's ability to respond correctly to grid disturbances. This situation is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an unplanned actuation of a system designed to mitigate the consequences of a significant event. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3882006001 | Susquehanna 2 | 01/25/2006 | 03/23/2006 | ML06095042 | <strong>Tech Specs Not Met for Inoperable ADS Pressure Switches</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2006 with Unit 2 in Mode 1 at 100% power, concerns were raised about the potential for interaction between an installed scaffold and Unit 2 "D" Residual Heat Removal pump instrument tubing. The tubing feeds two Automatic Depressurization System pressure switches that provide an ADS initiation permissive signal when the 2 DRHR pump is running. Analysis has conservatively concluded that scaffold movement during a dynamic event would have challenged the function of the ADS pressure switches. Accordingly, it was assumed that the ADS pressure switches were inoperable from the time of scaffold installation on February 1, 2005 to the time the scaffold was removed on January 27, 2006. This duration exceeds the Technical Specification 3.3.5.1 allowable completion times for inoperable Emergency Core Cooling System Instrumentation and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition Prohibited by Technical Specifications. Because the pump running permissive for ADS initiation can be fulfilled from numerous alternative sources, function of the ADS was not, in itself, lost. Analysis has concluded that the scaffold program design and supervisory reinforcement of administrative requirements were less than adequate. A site-wide inspection of accessible scaffold installations did not identify adverse impacts to other station equipment. Immediate compensatory measures such as procedural changes, stand-down meetings, and personnel training and qualification verifications were undertaken. In the longer term, the station intends to revise Susquehanna's scaffold control program, provide training on the program revisions, and to implement an in-plant Maintenance management observation process intended to reinforce administrative requirements among plant workers. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3882006002 | Susquehanna 2 | 04/19/2006 | 06/14/2006 | ML06187034 | <strong>Missed Technical Specification LCO 3.8.1 Entry for Unit 2 During Unit 1 ESS Bus Testing</strong><br /><i>Abstract:&nbsp;</i>As part of a cause investigation regarding a late entry into TS LCO 3.8.1 for Unit 2, on April 19, 2006, it was identified that a reportable event had occurred during the 2004 Unit 1 refueling outage. On March 6, 2004, the Unit 1 4.16kV ESS 1A Bus was being tested in accordance with plant procedures. The ESS 1A Bus was de-energized and LCO 3.8.7 was entered for Unit 2. Unit 1 busses supply electrical power to common systems which impact Unit 2 safety systems and require entry into LCO 3.8.1 and 3.8.7. A review of operator logs for March 6, 2004, identified that only LCO 3.8.7 was entered when the bus was de-energized. Entry into Unit 2 LCO 3.8.1, Conditions A, B and D was missed, resulting in Required Actions A.1 and B.1 not being performed within 1 hour and the mandated time for Unit 2 to be in Mode 3 being exceeded. The apparent cause for this event was attributed to confusing language in TS 3.8.1 which resulted in an inaccurate interpretation by plant personnel regarding which LCOs were required to be entered to support Unit 1 ESS Bus testing. Because no loss of safety function occurred, there was no impact to the power required to operate safety-related loads necessary to cool the reactor core, maintain containment integrity, and support other vital functions in the event of a postulated accident in one reactor unit, while safely shutting down the unaffected unit. Interim compensatory measures were established to clearly state which TS LCOs were required to be entered during the remaining Unit 1 ESS Bus testing that was being performed during the Unit 1 refueling outage. PPL will revise TS 3.8.1 and/or Bases to provide clarity and remove interpretation on LCO applicability during ESS Bus testing.
3892006001 | St. Lucie 2 | 01/20/2006 | 03/17/2006 | ML06087039 | <strong>Manual Reactor Trip due to Condenser Tube Leak</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2006, with St. Lucie Unit 2 in Mode 1 at 100 percent power, a Main Condenser high conductivity/sodium annunciator was received in the control room. Chemistry confirmed that the high sodium level was due to seawater intrusion fron the 2B2 Main Condenser waterbox. In accordance with the "Secondary Chemistry - Off Normal Procedure," 2-0610030, a rapid down power was initiated. The Shift Manager, based on Chemistry input and procedure direction, continued the down power and removed the unit from service rather than remain critical at a low power level. All systems worked as designed and the reactor was manually tripped at approximately 25 percent power in accordance with plant operating procedures without incident. All control rods fully inserted and the Steam Generator (SG) Safety Relief Valves did not actuate. Feedwater to the SG was supplied by the Main Feedwater (MFW) pumps during the shutdown and later transferred to the Auxiliary Feedwater (AFW) pumps. All safe shutdown equipment operated as designed with no equipment failures or impact to the health and safety of the public.
3892006002 | St. Lucie 2 | 02/15/2006 | 04/17/2006 | ML06115037 | <strong>Containment Purge Supply Isolation Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2006, with St. Lucie Unit 1 and Unit 2 in Mode 1 at 100 percent power, the St. Lucie Unit 2 inboard 8-inch containment purge supply isolation valve FCV-25-36 failed its local leak rate test (LLRT). The LLRT was being performed as required by Technical Specification (TS) surveillance requirement 4.6.1.7.4. Valve FCV-25-36 is the Containment side isolation valve for penetration P-56. Failure of the leak test caused entry in TS Action 3.6.1, requiring the penetration to be restored to operable status within 24 hours, or be in hot shutdown within 6 hours. As a result of the suspected failure mode of the isolation valve, and obstacles involved in repairing the valve within the TS required 24 hours, St. Lucie requested and received a Notice of Enforcement Discretion (NOED) from the NRC. As support for NOED-06-2-01, the valve was removed, a blank flange installed, and the LLRTsuccessfully performed. The valve has since been repaired and returned to service. Additionally, an exigent TS chance has been approved to adopt the Improved Standard Technical Specification which allows operation to continue with a blank flange installed or the upstream valve closed and de-energized.
3892006003 | St. Lucie 2 | 05/06/2006 | 06/28/2006 | ML06187046 | <strong>Missed Eddy Current Indication from SL2-15 Inspection</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2006, St. Lucie Unit 2 was in Mode 6, shutdown for the SL2-16 refueling outage. During steam generator eddy current testing (ECT), FPL determined that an error was made during the previous refueling SG ECT that allowed a defect in a steam generator tube (R100 L96 in SG 2B) to remain in service during Cycle 15 operation. This event was caused by an incomplete rotating probe inspection of bobbin probe identified indications during SL2-15. Corrective actions included plugging of the subject tube, and review of rotating probe data to ensure the entire target location was tested where the data was used to disposition a bobbin indication as "no degradation found" (NDF) during the SL2-15 outage inspection. This review determined that one other incomplete rotating probe test resulted in a second tube (R87 L97 in SG 2B) remaining in service during Cycle 15 that was not fully evaluated by Plus Point. Tube integrity assessment for both tubes and in-situ pressure testing for R100 L96 during the SL2-16 outage, demonstrated that the defective tubes met the structural integrity and accident induced leakage performance criteria of NEI 97-06, "Steam Generator Program Guidelines." Therefore, there was no impact to the health and safety of the public.
3892006004 | St. Lucie 2 | 06/15/2006 | 08/14/2006 | ML06234017 | <strong>Unplanned Manual Reactor/Turbine Trip due to DEH Leak</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2006, St. Lucie Unit 2, while returning to power from the SL2-16 outage, initiated an unplanned manual reactor/turbine trip due to a severe DEH leak on the number 1 throttle valve actuator [EIIS:FCV]. Operation procedures 2-E0P-01 "Standard Post Trip Actions," and 2-EOP-2, "Reactor Trip Recovery," were completed without contingencies and Unit 2 was stabilized in Mode 3. The DEH leak ceased upon turbine trip and all control rods fully inserted. No main steam safety valves [EIIS:SJ] lifted, Feedwater to the steam generator was supplied by the main feedwater pumps [EIIS:SJ] and all safe shutdown equipment operated as designed. The leak was a result of improper torquing by a contractor of the cap screws used to attach a blind flange to the actuator, which ultimately led to the failure of the interfacing o-ring under the high DEH pressure. The Root Cause determined the failed o-ring was the result of poor contractor workmanship and inadequate procedure guidance for torque verification following o-ring installation during rebuilding of the actuator at the vendor's facility.
3902006001 | Watts Bar 1 | 01/13/2006 | 03/14/2006 | ML06076038 | <strong>Entrained Air in Essential Raw Cooling Water (ERCW) Piping</strong><br /><i>Abstract:&nbsp;</i>The backup safety-related water supply for the Auxiliary Feedwater (AFW) system is provided by the Essential Raw Cooling Water (ERCW) system. On January 13, 2006, an attempt was made to take a chemistry sample of a portion of the ERCW piping. At this time, a sample could not be obtained due to air in the piping. The piping involved included: 1) a section of 12 inch ERCW supply piping to the Train B Motor Driven AFW (MDAFW) pump and to the Turbine Driven (TDAFW) pump, 2) a section of the 30 inch ERCW Train B Discharge header that ties to the 12 inch ERCW line. Troubleshooting activities were initiated to vent the affected ERCW supply piping to the AFW system. Ultrasonic testing of the affected piping was implemented to ensure the piping was properly filled. The Train A backup ERCW supply to the AFW system was also verified to be operable. The air in the 12 inch ERCW line was caused by an inadequate fill and vent of the line during work performed in the Cycle 6 refueling outage. For the 30 inch discharge header, the gas void was determined to have resulted from dissolved gases in the water coming out of solution and collecting in the piping. The corrective actions included the establishment of continuous vent paths for the 30 inch ERCW Train A and B discharge headers and the addition of ultrasonic equipment for the verification of the water level in the 30 inch headers.
3902006002 | Watts Bar 1 | 02/09/2006 | 04/10/2006 | ML06103040 | <strong>Potential Loss of Cooling to the Chemical and Volume Control Seal Water Heat Exchanger During an Appendix R Fire</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2006, engineering personnel identified a scenario involving a potential loss of cooling water to the Chemical and Volume Control System (CVCS) Seal Water Heat Exchanger during an Appendix R fire event. The scenario involves a loss of Component Cooling System (CCS) flow to the Seal Water Heat Exchanger due to fire damage. The loss of CCS flow results in a potential high suction temperature on the running CVCS Centrifugal Charging Pump (CCP) causing a loss of adequate suction head. During an Appendix R fire event, CCP suction is aligned to the Refueling Water Storage Tank (RWST), normal charging and letdown are isolated and the only makeup flow to Reactor Coolant System (RCS) is via the Reactor Coolant Pump (RCP) seal injection flow path. If the Seal Water Heat Exchanger cooling is lost, the CCP recirculation flow and RCP seal return flow are not being cooled. The outlet of the heat exchanger combines with cool water from the RWST. The net result is that the CCP suction temperature could reach saturation temperature leading to pump cavitation. The temperature increase could be high enough to potentially damage both the CCP and the RCP seals, which would result in increased seal leakage and a potential loss of RCS inventory. The cause of this event is a latent error in the WBN Fire Safe Shutdown Analysis. The original analysis did not evaluate the ramifications of not protecting cooling water flow to the CVCS Seal Water Heat Exchanger. Corrective actions include: 1) posting of roving fire watches in the areas affected, 2) procedure revisions to provide operator actions and 3) to issue a design change to reroute and or protect the identified vulnerable cables.
3902006004 | Watts Bar 1 | 05/30/2006 | 07/31/2006 | ML06213061 | <strong>Main Turbine High Vibration Trip</strong><br /><i>Abstract:&nbsp;</i>At 17:00:02 on May 30, 2006, main turbine vibration began increasing rapidly as indicated by a HI-HI alarm. At 17:00:16, the control room crew manually tripped the reactor and turbine when vibration reached the trip setpoint of 14 mils. Shortly after the plant trip, secondary chemistry parameters indicative of river water ingress began increasing. Following plant shutdown and cooldown, turbine and condenser inspections revealed a single blade from the last row (L-0) on the governor end of low pressure turbine (LPT) C (nearest LPT to generator) had fractured just below the rotor disk surface, causing damage to other blades on row L-0, L-0 fixed blades, surrounding turbine subcomponents, and several main condenser tubes below. Eddy current testing of all blade roots on the failed rotor identified seven more blade roots with cracks. The root cause of the reactor trip was failure of a blade on the governor end of the LPT C rotor. The corrective actions included replacement of the LPT C rotor and repairs of collateral damage to affected main condenser tubes. TVA has also limited operation at higher back pressures. TVA also chose to increase monitoring of turbine parameters (bearings, oil quality, shaft orbits, thrust movement, etc.) during startup to ensure reliability of turbine protection subsystems.
3902006005 | Watts Bar 1 | 07/31/2006 | 09/26/2006 | ML06310007 | <strong>Automatic Reactor Trip due to Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On July 31, 2006, at approximately 12:13 EDT, the control room unexpectedly received an exciter field overcurrent alarm, followed immediately thereafter (< 1 sec) by the generator field breaker opening, and a turbine/reactor trip. An event team was assembled subsequent to the plant trip. The most likely cause was determined to be in the main generator automatic excitation control circuitry. Corrective action taken was to return the plant to service while monitoring several input and output signals associated with the automatic controls so that any subsequent events could be captured and analyzed. The excitation system would also be operated in TEST mode instead of AUTOMATIC to preclude the possibility of an additional plant trip. Since restarting the plant, there have been several instances where the output of the Maximum Excitation Limiter (MXL) circuit board in the automatic excitation control circuitry has changed significantly (+14 volts dc to -15 volts dc) with no corresponding change on any of the inputs. Had the automatic circuit been in service, the MXL output change would have driven the excitation controls into a loss of the exciter field which was the case during the plant trip. Based on this data, during the current refueling outage, the MXL circuit board will be removed to determine if a discreet component on the device has failed and an inspection performed of the interface wiring to the MXL circuit board to determine if degraded wiring caused the failure. As a result of the plant trip, the actuation of the Reactor Protection and the Auxiliary Feedwater Systems were reported in accordance with 10 CFR 50.72(b)(2)(iv) and 10 CFR 50.72(b)(3)(iv), respectively. This event is also being reported as this Licensee Event Report in accordance with 10 CFR 50.73 (a)(2)(iv).
3902006007 | Watts Bar 1 | 07/21/2006 | 02/29/2008 | ML08057030 | <strong>High Range Radiation Monitors - Temperature Induced Current</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2006, at 09:00 EDT, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.3, Condition G was entered for both trains of High Range Radiation Monitors when it was determined that upper and lower containment radiation monitors 1-RM-90-271, 272, 273, and 274 may not meet reliability expectations due to temperature induced currents during some portions of postulated high energy line break scenarios in containment. Condition G required immediate action to provide a report within 14 days in accordance with TS 5.9.8, "PAM Report." That report was provided by TVA on August 4, 2006. Since the temperature induced current condition existed longer than 14 days required by TS to submit the report, this condition is reportable under 10 CFR 50.73 (a)(2)(i)(B) as Operation or Condition Prohibited by Technical Specifications. Revision 1 of the LER updates the corrective action based on testing documented in a report titled “High Range Radiation Monitor TIC Test Report.” Revision 2 corrects an error in the sequential number in Block 6 of the LER.
3902006008 | Watts Bar 1 | 10/27/2006 | 12/19/2006 | ML06356008 | <strong>Auxiliary Feedwater Auto-Start Function upon Loss of Main Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2006, with WBN Unit 1 in a core empty period, NRC issued Inspection Report 390, 391/2006004 which identified a non-cited violation of Technical Specification (TS) 3.0.4 for entering Modes 1 and 2 with the automatic auxiliary feedwater start signal for a loss of normal feedwater (TS 3.3.2.6.e) inoperable. Since initial startup in 1996, WBN has concluded this function was operable when a turbine-driven main feedwater pump trip bus was energized even though the pump was not running and supplying feedwater to the steam generators. This condition is being reported under 10 CFR 50.73(a)(2)(i)(B), "Operation or Condition Prohibited by Technical Specifications." The cause was determined to be a misunderstanding of the Technical Specification due to a disconnect between the design of Watts Bar and the assumed generic design in the standard Technical Specifications. The need for the AFW pumps to start on the loss of the Standby Main Feedwater Pump appears to have not been considered during the development of WBN's Technical Specifications. Procedure changes have been made to address the use of LCO 3.0.4.b for the startup of the unit utilizing the standby main feed pump or the use of the Auxiliary Feedwater System.
3902006009 | Watts Bar 1 | 10/26/2006 | 12/19/2006 | ML06356005 | <strong>Containment Spray Valve Interlock Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2006, with WBN Unit 1 in a core empty period, WBN personnel concluded that a condition that had been identified earlier in the U1C7 refueling outage performance of Surveillance Instruction 1-SI-63-915A, Appendix P, "Safety Injection System - Valve Position Indication Verification and Full-Stroke Exercising (Train A)," had existed since the U1C6 refueling outage (March 22, 2005). Specifically, on September 20, 2006, Valve 1-FCV-72-45-B, "Train B - Containment Sump Suction Valve," would not stroke electrically during the above surveillance performance. Subsequently, during the corrective action investigation, it was determined through review of maintenance records that Rotor 2 (Contact 6) on 1-MVOP-72-21-B (interlocked with valve 1-FCV-72-45-B) had been set incorrectly during the U1C6 refueling outage. The rotor was reset and a post maintenance test was successfully completed that demonstrated the misadjustment of the rotor was the cause for above 1-FCV-72-45-B condition. Further investigation found the opposite train check valves 1-CKV-72-562-A and -548-A were inoperable due to surveillance instruction inspection/disassembly during portions of the same period. Since this condition existed beyond the allotted TS outage time, it is being reported under 10 CFR 50.73(a)(2)(i)(B), "Operation or Condition Prohibited by Technical Specifications." In addition,since the opposite train valve has been also found to have been inoperable, it is also reportable under 10 CFR 50.73(a)(2)(v)(D). The issue was determined to stem from two causes. The first cause is a lack of procedural guidance and control during a motor-operated valve analysis and test system (MOVATS) test. The second cause was determined to be a lack of attention to detail during post maintenance testing (PMT) development and approval. Corrective actions include a revision to plant procedures to provide additional guidance on the performance of testing and limit switch development, and coaching of the individuals involved with the inadequate PMT development and approval.
3902006010 | Watts Bar 1 | 12/12/2006 | 02/12/2007 | ML07044032 | <strong>Both Trains of Auxiliary Building Gas Treatment System (ABGTS) Inoperable due to Boundary Breach</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2006, at 0927 Eastern Standard Time (EST) hours the Auxiliary Building Auxiliary Unit Operator (AUO) reported to the control room that both doors A111 and A112 were found open. The control room staff entered LCO 3.7.12, "Auxiliary Building Gas Treatment System (ABGTS)," Condition B due to both doors A111 and A112 being open at the same time causing a breach of the Auxiliary Building Secondary Containment Enclosure (ABSCE). With this breach of the ABSCE boundary, both trains of ABGTS were inoperable. Action B.1 of LCO 3.7.12 requires the plant to be in mode 3 in 6 hours and mode 5 in 36 hours. At 0929 hours, the AUO closed both doors A111 and A112. LCO 3.7.12 Condition B was then exited. Since this condition affected the operability of both trains of ABGTS, it is being reported in accordance with 10 CFR 50.73(a)(2)(vii), "any event where a single cause or condition caused ... two independent trains or channels to become inoperable in a single system designed to:...(D) mitigate the consequences of an accident." The cause of this event was a lack of positive controls to prevent operation of the A111 door interlock override button which allowed door A111 and A112 to be open simultaneously. Contributing to this event was improper supervisory oversight of the Radiation Protection personnel moving laundry in the auxiliary building. Additional administrative controls have been established to assist in preventing inappropriate simultaneous opening of doors A111 and A112 and Radiation Protection personnel directly involved with this event have been counseled.
3952006001 | Summer 1 | 05/18/2006 | 07/10/2006 | ML06194002 | <strong>Securing Emergency Recirculation of Control Room Ventilation While Associated Radiation Monitor Was Out of Service</strong><br /><i>Abstract:&nbsp;</i>On 5/18/06, at approximately 2117, 'B' train Control Room (CR) ventilation was in the emergency recirculation mode of operation as required by Technical Specification (TS) 3.3.3.1, Action 29. This Technical Specification action requires that the CR ventilation be in the emergency recirculation mode of operation when the radiation monitor RMA 1 is out of service. RMA 1 was out of service while being calibration tested using Surveillance Test Procedure (STP) 360.031. Confusion with a step in the STP resulted in the operator securing the CR ventilation from the emergency recirculation mode of operation thus violating TS 3.3.3.1, Action 29. When the operator attempted to restart 'B', train CR ventilation, a fan appeared to fail to start, thus prolonging the amount of time in violation of TS 3.3.3.1, Action 29. Troubleshooting revealed that indicator bulbs for the fan start switch were burned out. The 'B' train CR ventilation was subsequently restarted in the emergency recirculation mode. The station was in violation of TS 3.3.3.1, Action 29 for approximately 19 minutes.
3952006002 | Summer 1 | 10/06/2006 | 11/11/2006 | ML06319032 | <strong>Securing an Associated Radiation Monitor While the Reactor Building Alternate Purge System Was in Service</strong><br /><i>Abstract:&nbsp;</i>On 10/06/06, the Reactor Building Alternate Purge system was in service to provide cleanup for the reactor building atmosphere in preparation for the refueling outage (RF-16). Technical Specification (TS) 3.3.2, Table 3.3-3, Item 3.c.2 requires two radiation monitors to be available to automatically and independently isolate reactor building purging operations in the event of high containment activity. While purging was in progress, operators commenced steps in Surveillance Test Procedure (STP) 0144.001 to stroke-test the containment isolation valves for Radiation Monitor RMA 2. On 10/06/06 at 2030, the sample pump was secured per the STP, which made RMA 2 inoperable. At this point, the station had only one of the two required radiation monitors available during purging operations and thus was no longer in compliance with TS 3.3.2. Upon receiving the trouble alarm on RMA 2, personnel in the control room recognized that RMA 2 was inoperable coincident with the ongoing purging operations. Subsequently, the sample pump for RMA 2 was restarted which brought the station back into compliance with TS 3.3.2. The station was in violation of TS 3.3.2 for approximately one minute. During this time, Radiation Monitor RMA 4 was operable and available to isolate reactor building purging operations in the event of high containment activity.
3952006003 | Summer 1 | 11/09/2006 | 01/08/2007 | ML07010052 | <strong>Emergency Diesel Generator Start due to Undervoltage On 1DB Emergency Bus</strong><br /><i>Abstract:&nbsp;</i>At 1444 on 11/09/06, after initial installation of the Alternate AC Power Supply, post modification testing was being performed in accordance with STP-125.021, "Periodic Testing of The Alternate AC Power Supply." During the test the B Diesel Generator (DG) was in the standby mode and bus power was being supplied by the Alternate AC Power Supply. As individual loads were manually loaded on the 1DB bus, bus voltage momentarily decreased as each load was started. When the 'B' Emergency Feedwater Pump was started, an undervoltage condition occurred on the bus that was sufficient to pick up the undervoltage (UV) relays, (27-1 DB), starting the 'B' DG. Design Engineering has determined that the bus voltages were sufficient for operation of the bus. The Alternate AC Power Supply was functional and met all test requirements. The 'B' DG was operable, and it auto-started on low voltage, according to design. No load breakers or MCC based contactors opened due to low voltage during the performance of the test. The Supplemental Instrument Air Compressor tripped during the low voltage dip from the Charging Pump start, and the 'B' train Hydrogen Analyzer trouble alarm came in. Both of these components have local controllers and are not supplied by MCC based contactors. Although both were affected by the low voltage on the bus they were not a contributing factor in the UV start of the DG. STP-125.021 will be revised to align the DG to prevent an inadvertent start during testing. This action is scheduled for completion prior to the next scheduled test.
3952006004 | Summer 1 | 11/22/2006 | 01/19/2007 | ML07024012 | <strong>Turbine Trip due to High Steam Generator Level P-14</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2006 at approximately 0430 hours, during secondary plant startup, the "B" steam generator (SG) water level increased to the high level (P-14) setpoint. The P-14 signal isolated feedwater (FW), tripped the main FW pump turbines and the main turbine. The cause of this event is attributed to an operator over feeding the SGs while transferring feed flow from emergency feedwater (EF) to main FW. This action caused the reactor coolant system (RCS) temperature to decrease. When the crew recognized the excessive feed to the SGs, feed flow was reduced and the crew restored RCS temperature. The RCS temperature increase and narrow range (NR) SGWL lagging actual level caused SG level indication to continue to rise. The "B" SG reached the high level (P-14) setpoint. Following the turbine trip and FW isolation, the RCS temperature was stabilized and SG level control was reestablished on EF. As a result of this transient, the plant start up was delayed. The oncoming operations crew received simulator training on the startup evolution. The crew then assumed the watch, successfully raised power, and continued with the secondary plant startup. Corrective actions to preclude recurrence include improving pre-job briefings and just-in-time (JIT) training for the startup evolution. Additionally, licensed operators will be provided training on the event during the next scheduled Licensed Operator Requalification training cycle and simulator training on this evolution will be added to the Licensed Operator Requalification Program. These actions will be completed by April 1, 2007.
3972006001 | Columbia | 10/31/2006 | 01/02/2007 | ML07009047 | <strong>Reactor Trip due to Digital Electro-Hydraulic Control System Card Failure</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2006 at 0445 hours, the reactor tripped from 100% power. The trip resulted from a Reactor Protection System (RPS) actuation due to a failure in the Digital Electro-Hydraulic (DEH) system used to position Main Turbine valves. This failure caused four turbine throttle valves (TVs) and four turbine governor valves (GVs) to spuriously stroke to the full close position. When the TVs were closing and reached a position less than 95% open, RPS logic was met and a Reactor Scram occurred. The cause for the valve closure was a failure of an output peripheral driver chip on a DEH Digital Input Card. When the chip failed, the output went to high voltage which is equivalent to a turbine unlatched condition. This false turbine unlatched condition is the initiator for the subsequent turbine valve motion. The card was replaced and the circuit successfully tested. The DEH system has been previously determined to have multiple single point vulnerabilities. Long-term corrective actions have been pursued in which a new DEH system is scheduled to be installed in refueling outage R18 (May/June 2007). This event did not adversely affect the health and safety of the public. Two similar events were reported by Energy Northwest as LERs 2004-004-00 and 2005-003-00.
3972006002 | Columbia | 11/03/2006 | 01/02/2007 | ML07009048 | <strong>Shutdown Cooling Isolation due to Inadequate Procedure Step</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2006 at 0309 PST, Shutdown Cooling (SDC) was inadvertently removed from service while in Mode 4. The loss of SDC resulted from the isolation of the inboard primary containment isolation valve (RHR-V-9) on the Residual Heat Removal (RHR) SDC common suction header. The isolation occurred while transferring Reactor Protection System (RPS) B to its alternate power supply. During the transfer electrical disconnect RHR-DISC-V/9 was opened per Plant Procedures Manual (PPM) 2.7.6 to prevent a loss of SDC. Use of RHR-DISC-V/9 during the transfer resulted in an unintended containment isolation signal to RHR-V-9. The cause of this event was an inadequate procedure step derived from inaccurate technical information in procedure SOP-RHR-SDC-BYPASS. Corrective action has been initiated to revise subject procedures. More specific guidance for validation will be provided as part of the Procedure Review Program and expectations for technical accuracy will be reinforced. There have been two reported isolations of SDC at Columbia within the past 5 years (LER 2003-003 and LER 2003-005).
4002006001 | Harris | 12/19/2005 | 02/15/2006 | ML06053036 | <strong>Multiple Turbine EHC Low Fluid Pressure Switches Inoperable due to a Common Cause</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2005, with the reactor at approximately 100% power, the Turbine Generator Electro-Hydraulic Control (EHC) Low Fluid Pressure Switches [TG] were calibrated and four of six pressure switches were found outside their Technical Specification (TS) allowable limit of greater than or equal to 950 psig. All switches were recalibrated and left in an operable condition at the time of discovery. Upon review, it was determined that these four switches would have resulted in 2 of 3 channels on each protective train not being operable by TS. The switches were functional at all times and are not credited in the accident analysis. The Root Cause of this event was that the original instrument uncertainty calculation did not allow sufficient margin between the trip setpoint and allowable value due to a change in switch characteristics subsequent to the calculation development. The vendor changed the repeatability specification for the current model from 1.5% to 3.0% which was not reflected in the uncertainty calculation and/or margin allowed for these pressure switches. The corrective action to prevent recurrence was to develop and implement an Engineering Change to account for the vendor's increased repeatability specification from 1.5% to 3.0% and provide increased margin to the TS Limit of greater than or equal to 950 psig. This change was implemented on January 9, 2006.
4002006002 | Harris | 06/01/2006 | 07/28/2006 | ML06215034 | <strong>ESCW Inoperable for a Period Longer than Allowed by Technical Specifications due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage 13 (RFO-13), a rebuilt York Compressor was installed on the 'A' Chiller for the 'A' Essential Services Chilled Water (ESCW) system. To connect the rebuilt compressor, personnel reinstalled and reconnected the linkage between the compressor pre-rotation vane (PRV) shaft and the PRV motor. The 1/2" cap screw which connects the PRV internal shaft and the external lever was not torqued to 75 ft-lbs as referenced in plant drawings during this maintenance. On May 25, 2006, the A Chiller was started successfully for the ninth time following the maintenance, and the PRV motor rotated the linkage to fully open the PRVs. However, differential movement between the linkage and the PRV shaft occurred due to the inadequately torqued 1/2" cap screw. This movement created a misalignment of the connecting linkage, which prevented the VMS-1 switch from shutting when the unit was secured at 21:20 on May 25, 2006. The VMS-1 is a start permissive for the 'A' Chiller. Therefore 'A' Chiller was inoperable from this time until the condition was discovered, corrected and tested on June 3, 2006 at 05:00. The root cause of this event was a technically inadequate procedure. The corrective action to prevent recurrence is to revise the maintenance procedure for the ESCW Chillers to provide instructions for properly torquing the 1/2" cap screw.
4002006003 | Harris | 09/19/2006 | 11/17/2006 | ML06328020 | <strong>Automatic Reactor Trip due to Generator Lockout Signal</strong><br /><i>Abstract:&nbsp;</i>At 09:59 EDT on September 19, 2006, with the reactor at 100 percent power, the reactor automatically tripped from a turbine trip due to a generator lockout signal. There was no inoperable equipment at the start of this event that contributed to this event. Safety systems functioned as required and operators responded in accordance with approved procedures. Post trip discovery found that a ground fault protective relay module failure caused by self heating actuated the 86/G1A Main Generator Lockout Relay which initiated a turbine and reactor trip. Further investigation revealed that no module specific inspection requirements exist for the generator, main transformer and auxiliary transformer protective relay modules to detect self heating concerns. Completed corrective actions include replacing the failed relay module for the main generator stator ground detection circuit. Additional corrective actions are to establish specific inspection requirements for the generator, main transformer and auxiliary transformer protective relays and to brief appropriate maintenance personnel.
4102006001 | Nine Mile Point 2 | 03/09/2006 | 05/05/2006 | ML06136021 | <strong>Automatic Reactor Scram due to a Loss of Main Turbine Gland Sealing Steam</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2006, at 22:14 hours, Nine Mile Point Unit 2 reactor automatically scrammed from approximately 86 percent power. Nine Mile Point Unit 2 was coasting down in power for the upcoming refueling outage. The scram was caused by main Turbine Trip due to low condenser vacuum. The Turbine Generator Gland Seal and Exhaust System (TME) failed resulting in a loss of condenser vacuum. A Clean Steam Reboiler, which supplies steam to the TME, isolated on high water level and the TME Emergency Main Steam Backup System (EMS) failed to supply steam as designed. The EMS failed when the mechanical linkage for the pressure indicating controller became disconnected causing the associated pressure regulating valve to fail closed, isolating main steam from the TME. The mechanical linkage became disconnected due to either not being properly reassembled during previous maintenance, or due to the pressure transient within the EMS resulting from its automatic actuation. Corrective actions to prevent recurrence have been developed, including procedure revisions to emphasize performance, of maintenance on critical components, a design change of the EMS and enhanced training for operations and engineering.
4102006002 | Nine Mile Point 2 | 05/26/2006 | 07/25/2006 | ML06214004 | <strong>RCIC Exhaust Piping Vacuum Breakers Isolated Resulting in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2006, Nine Mile Point Nuclear Station (NMPNS) determined that an unanalyzed condition had existed on February 8, 2006, due to potential water hammer impacts in the Nine Mile Point Unit 2 (NMP2) Reactor Core Isolation Cooling (RCIC) system. During planned maintenance, the RCIC system was declared inoperable but available for automatic and manual start with the RCIC turbine steam exhaust piping vacuum breakers isolated. Under worst case conditions, if RCIC was manually or automatically started with the exhaust piping vacuum breakers isolated, the configuration may result in water hammer related stresses significantly above allowables. Under such conditions, there is an increased likelihood that primary containment boundary piping could be breached and other systems affected. The root cause of this condition has been attributed to the failure of original design change process to provide cautions in procedures and adequate training regarding the RCIC vacuum breaker function when the vacuum breakers were installed prior to NMP2 initial start-up. To prevent recurrence, key plant procedures have been revised to ensure the RCIC system will not be placed in the same or similar configurations as described in this report. Additional actions to prevent recurrence include implementing staff training with regard to potential water hammer events and improvements in evaluating and applying industry operating experience.
4122006001 | Beaver Valley 2 | 04/02/2006 | 05/24/2006 | ML06152019 | <strong>Turbine-Generator Trip due to Loss of Generator Excitation Power Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2006, the Beaver Valley Power Station (BVPS) Unit No. 2 reactor tripped at 1402 hours due to a Main Generator Loss of Field Protection Trip. All safety systems functioned as designed. Both Emergency Diesel Generators (EDGs) automatically started due to a momentary under voltage condition caused by the initial Main Generator trip. Both EDGs ran unloaded. All three Auxiliary Feedwater System pumps started as expected on low steam generator levels. The plant was stabilized in Mode 3 with primary and secondary parameters returned to normal hot standby values. The root cause of the generator trip has been determined to be less than adequate workmanship, manufacturing and/or disassembly inspections. Initial inspection by the vendor (post-trip) identified that the block which supports the field pole #1 and field pole #2 terminals was not present. With this block missing, the field pole connection is subject to increased flexing during normal operation and also during maintenance activities. This increased flexing led to fatigue failure of the Exciter Field. With the open circuit resulting from the failed pole connection, the Main Generator tripped on loss of field. It was indeterminate if the support block was removed during one of the Exciter inspections/ disassemblies or never installed during the manufacturing process. This reactor trip is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event which resulted in the valid automatic actuation of the Reactor Protection System, the Auxiliary Feedwater System, and the on site emergency AC electrical power systems - Emergency Diesel Generators per 10 CFR 50.73(a)(2)(iv)(B). The risk was determined to be very low safety significance.
4122006002 | Beaver Valley 2 | 04/11/2006 | 06/12/2006 | ML06165029 | <strong>Entry into Technical Specification 3.0.3 due to Inoperability of Both Trains of the Supplemental Leak Collection and Release System</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2006, Beaver Valley Power Station (BVPS) Unit No. 2 declared both trains of the Supplemental Leak Collection and Release System (SLCRS) inoperable due to a loss of filtering capacity of the charcoal main filter banks. The charcoal main filter banks were sprayed with water after an inadvertent actuation of fire protection deluge valves. With the charcoal main filter banks wet, their filtering capacity was diminished and both trains were declared inoperable. At 0924 hours, Unit 2 entered the actions of Technical Specification (TS) 3.0.3. In accordance with the requirements of TS 3.0.3, actions to prepare for a plant shutdown began at 1020 hours and a shutdown of the plant was commenced at 1055 hours. In parallel with the plant shutdown, a Notice of Enforcement Discretion (NOED) was prepared for presentation to the Nuclear Regulatory Commission (NRC). At 1520 hours, with reactor power at approximately 19 percent(%), the NOED was granted by the NRC for a period of 48 hours and the plant shutdown was terminated. The unit returned to 100% power on April 12, 2006, at 1455 hours. The most probable cause of the event was a ground that actuated certain fire protection actuation relays. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) due to an entry into TS 3.0.3 for greater than one hour, 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of the safety function of a system designed to control the release of radioactive material, and 10 CFR50.73(a)(2)(vii) as an event where a single cause resulted in the loss of two independent trains of SLCRS as required by TS 3.7.8.1. The plant risk associated with the inadvertent actuation of the fire protection deluge system is considered to be very low.
4122006003 | Beaver Valley 2 | 10/01/2006 | 02/26/2007 | ML07058043 | <strong>Scaffolding Adversely Impacts Main Steam Isolation Valves Closure Capability</strong><br /><i>Abstract:&nbsp;</i>At 0830 hours on 10/01/06, an Instrumentation and Control (IC) supervisor noticed that the scaffolding erected near the Beaver Valley Power Station (BVPS) Unit 2 'A' and 'B' Main Steam Isolation Valves (MSIVs) could potentially interfere with the closing operation of these MSIVs. Both MSIVs 'A' and 'B' were declared inoperable at 0835 hours. Technical Specification (TS) 3.7.1.5 requires each MSIV to be operable during Modes 1, 2 and 3, and allows one MSIV to be inoperable for up to 4 hours in Mode 1. Since TS 3.7.1.5 does not address two MSIVs being inoperable, TS 3.0.3 was entered which requires the Unit to be placed within Hot Standby (Mode 3) within the next 6 hours. By 0945 hours, the scaffolding that potentially inhibited the 'A' and 'B' MSIV movement had been removed, allowing these two MSIVs to be declared operable and BVPS Unit 2 to exit TS 3.0.3 and 3.7.1.5. This event is reportable pursuant to 10 CFR50.73(a)(2)(i)(B), 50.73(a)(2)(ii)(B), 50.73(a)(2)(v)(C) and 50.73(a)(2)(v)(D). The root cause of this event has been determined to be that supervisors did not reinforce procedure use and adherence for the scaffold implementation process in that implementing organizations failed to perform the pre-installation walkdown in accordance with plant procedures. The safety significance of this event was very low.
4132006001 | Catawba 1, Catawba 2 | 05/20/2006 | 07/19/2006 | ML06208003 | <strong>Loss of Offsite Power Event Resulted in Reactor Trip of Both Catawba Units from 100% Power</strong><br /><i>Abstract:&nbsp;</i>On 05/20/06, at 1401 hours, both Catawba units tripped automatically from 100% power following a loss of Offsite Power (LOOP) event. The event began when a fault occurred internal to a current transformer associated with one of the switchyard power circuit breakers. A second current transformer failure, along with the actuation of differential relaying associated with both switchyard busses, cleared both busses and separated the units from the grid. A Notification of Unusual Event (NOUE) was declared at 1414 hours. The Emergency Response Organization was electively activated. Both emergency diesel generators on each unit started automatically and supplied their required blackout and essential loads as designed. All three auxiliary feedwater pumps on each unit started automatically and fed the steam generators as designed. Decay heat was removed via natural circulation of the reactor coolant system, with steam relief through the steam generator power operated relief valves. Both units were stabilized in Mode 3 with cooldown activities in progress. Offsite power was restored to all 6900V busses on both units by 05/20/06 at 2041 hours. The NOUE was subsequently terminated on 05/21/06 at 0140 hours. The root cause analysis for this event determined that in 1981, certain switchyard relay tap setting changes were not implemented at Catawba. Power Delivery documentation was subsequently erroneously updated to indicate that the changes had been made. Corrective actions for this event will include developing an enhanced process to ensure correct configuration management for the Catawba protective relay settings. The health and safety of the public were not adversely affected by this event.
4132006002 | Catawba 1 | 05/22/2006 | 09/14/2006 | ML06271039 | <strong>Safe Shutdown Potentially Challenged by an External Flooding Event and Inadequate Design and Configuration Control</strong><br /><i>Abstract:&nbsp;</i>On 05/22/06, while Unit 1 was shutdown in Mode 3, the Unit 2 Cooling Towers (CT) experienced excessive overflow due to clogged upper level CT screens. This condition created a source of water that followed a flow path through unsealed electrical conduit penetrations to the 1A Diesel Generator (DG) Room. The water intrusion condition was discovered and stopped prior to any DG damage. DG 1A was the only DG affected by this condition. However, the presence of this flow path highlighted potential vulnerabilities in barriers to the Probable Maximum Precipitation (PMP) event that could challenge safe shutdown capabilities. The identified flood protection deficiencies were attributed to inadequate design and configuration control of features to protect against flooding.The flood protection deficiencies were corrected by the installation of new flood protection seal barriers. This report does involve a safety system functional failure as it relates to a postulated PMP. There was minimal safety significance to this event.
4132006003 | Catawba 1, Catawba 2 | 12/15/2006 | 02/12/2007 | ML07052026 | <strong>Technical Specification Violations Associated with Hydrogen Ignition System</strong><br /><i>Abstract:&nbsp;</i>On 12/15/06, at 1913 hours, with Unit 2 in Mode 1 at 100% power, Train A of the Unit 2 Hydrogen Ignition System (HIS) was declared inoperable as a result of ignitor temperature in the ice condenser region not meeting its Technical Specification Surveillance Requirement 3.6.9.3 acceptance criterion of 1700 F. Failure to meet the acceptance criterion was discovered as a result of ignitor testing that was being conducted on Unit 1, which was in No Mode during its end-of-cycle 16 refueling outage. It was determined that the requirements of Technical Specification 3.6.9 had not been met for HIS Trains 1A, 1B, and 2A. The root causes of this violation were determined to be: 1) a lack of monitoring and oversight of engineering worker practices associated with modifications to replace the ignitor glow plugs with glow coils, and 2) the measuring and test equipment process did not adequately integrate critical operating characteristics important to the accuracy of the test instrumentation into maintenance procedures or training. In addition, on 12/27/06, HIS Train 1B was determined to have also violated Technical Specification 3.6.9 requirements following two instances of a failed fuse which affected one ignitor group. Fuses were not properly sized due to a lack of fundamental knowledge that the fuse sizing requirements were contained in the electrical criteria. During the time that the affected ignitors did not meet Technical Specification requirements, both units' HIS would have been capable of performing its required function, as discussed in the LER text; therefore, there was no safety significance to this event.
4162006001 | Grand Gulf 1 | 05/12/2006 | 08/09/2006 | ML06237005 | <strong>Division 1 Diesel Generator Exhaust Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2006 following a post maintenance test of Division 1 Diesel Generator, both exhaust valves in cylinder head 8L were found to have developed cracks going through the outer lapping tool holes on the valves. One of the valve cracks had propagated to failure. The cracked valves were shipped to an off-site laboratory for analysis. Intergranular Corrosion Cracking was determined to be the cracking mechanism. The root cause of the valve cracking was the valve material -highly sensitized austenitic stainless steel. This sensitized valve material in the presence of moisture in the valve head creating sulfurous acid from the residual sulfur in combustion products led to cracking and subsequent failure. The source of the moisture was jacket cooling water leaking through a small crack in the cylinder head. The diesel was repaired and returned to service. An evaluation determined that the diesel could have performed its design function even with one of sixteen cylinders not firing. However, due the importance of communicating this issue to the nuclear industry, GGNS has elected to submit this voluntary LER.
4232006001 | Millstone 3 | 04/04/2006 | 10/04/2006 | ML06285053 | <strong>Loss Of Safety Function Of The Control Room Emergency Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2006, with the plant in Mode 1 at 100% power, both trains of the Control Room Emergency Ventilation System (CREVS) were made unavailable as a result of the valve air actuator and manual actuator being removed from one of the two in series air-operated control room air inlet isolation valves. The valves are required to open during manual alignment of the CREVS, which permits control room pressurization using filtered outside air in the emergency recirculation mode. The cause of this event was a failure to recognize and correct an operating practice associated with an allowed mode of operation (isolated filtered recirculation) after it was removed from Unit 3 Technical Specification 3.7.7 in 2002. The CREVS is relied upon in the plant safety analysis to mitigate the consequences of an accident by limiting the radiological exposure to the control room operators from a Loss of Coolant Accident. For this reason the loss of safety function of both trains of the CREVS is considered reportable under the provisions of 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented fulfillment of a safety function of structures or systems needed to mitigate the consequences of an accident.
4242006001 | Vogtle 1 | 04/17/2006 | 06/09/2006 | ML06160045 | <strong>Manual Reactor Trip due to Loop 3 Main Feed Regulating Valve Control Failure</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2006, while at 100% power, the Unit 1 Control Room crew was challenged by an erratic response of the Loop 3 Main Feed Regulating Valve (MFRV), 1FV0530, while operating in automatic. The crew was able to stabilize the valve in manual mode, however, over the next 24 hours the control of the valve continued to degrade. On April 16, 2006, it was decided that Unit 1 would be taken to Mode 3 for investigation of the control issue with 1FV0530. On April 17, 2006, at 0026 EDT, Unit 1 was manually tripped at 33% power when Steam Generator number 3 water level was observed to be slowly increasing with 1FV0530 unable to control level in either automatic or manual. A review found that 1FV0530 operated erratically due to a failed I/P transducer, which resulted in the inability to reduce feedwater flow requiring a manual reactor trip. Based on the results of the observations and failure analysis performed on the I/P transducer, two failures were identified. One failure was the supply air input connector and the resultant electrical to pneumatic conversion process for a valve internal to the controller, and the second failure was the electronic circuit board. The failed transducer and the remaining Unit 1 MFRV I/P transducers were replaced with different make and model I/P transducers prior to the unit restart.
4242006002 | Vogtle 1, Vogtle 2 | 07/26/2006 | 09/22/2006 | ML06268004 | <strong>Three Technical Specification (TS) Instruments were Determined to be in a Condition Which Was Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>The week of June 6, 2005, a Vogtle Equipment Qualification Program self-assessment was performed that identified a potential problem with the Rosemount model 1153 Series B and 1154 transmitters if the neck seal is broken. This seal protects the transmitter electronics from moisture intrusion to ensure the safe operation of the transmitter during accident conditions. This self-assessment resulted in the development of an inspection plan to determine if this condition existed at Vogtle. The inspection plan was initiated in June 2005 and completed in August 2006. The following three Technical Specification (TS) instruments were determined to have been inoperable as a result of a broken neck seal: 1FT-5152, Steam Generator (SG) 1 Auxiliary Feedwater Flow, 2PT-0455, Pressurizer Channel 1 Pressure, and 1PT-0456, Pressurizer Channel 2 Pressure. Per the vendor manual, the connection between the electronic housing and the sensor module is hermetically sealed with a baked-on environmentally qualified neck seal. The cause of the event was a result of inadequate installation and calibration procedure guidance in that a caution statement from the vendor manual not to break the neck seal between the sensor module and the electronics housing was not included. All three transmitters were replaced, and appropriate maintenance procedures have been updated to reflect the vendor manual caution to not rotate the head.
4242006003 | Vogtle 1, Vogtle 2 | 10/11/2006 | 12/06/2006 | ML06342035 | <strong>Contract Employee Failure to Self-Disclose Material Information for Unescorted Access</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2006 at approximately 1525 hours (EDST), Southern Nuclear Operating Company (SNC) determined that a contract employee failed to self-disclose material information in applying for unescorted access. The contract employee had been charged with aggravated assault on June 26, 2005, but failed to self-disclose this information prior to being granted unescorted access to Vogtle Electric Generating Plant (VEGP) in September 2005. The subject contract employee had been badged at another nuclear plant less than 365 days before arriving at VEGP and was not due for a background reinvestigation, which would have included a criminal history check. Based on the requisite Reinstatement review and issuance of a Certificate of Reliability, the contract employee was granted unescorted access at VEGP from September 16, 2005 to October 13, 2005. A detailed investigation by SNC Nuclear Fleet Security was performed on October 11, 2006, and determined that the contract employee failed to disclose the assault charge. Had this information been disclosed during the background screening process, unescorted access would not have been granted. The subject individual has been denied unescorted access at all SNC nuclear plants and has been identified in the shared, industry-sponsored Personnel Access Data System (PADS).
4242006004 | Vogtle 1 | 10/28/2006 | 12/18/2006 | ML06353009 | <strong>ECCS Accumulator #1 was Determined to be in a Condition Which was Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2006 at 0726 EDT, while in Mode 3 with Emergency Core Cooling System (ECCS) Accumulators required to be operable, Accumulator #1 was in a condition prohibited by Technical Specification (TS). The accumulator had been overfilled prior to entering Mode 3 due to the use of invalid level indication during the fill process. This overfill condition was not identified prior to being in Mode 3 with Accumulators required to be operable; therefore, Accumulator #1 was rendered inoperable per TS 3.5.1, which states that four ECCS Accumulators are required to be operable in Modes 1 and 2, and in Mode 3 with pressurizer pressure above 1000 psi. If one Accumulator is inoperable, action must be taken to restore the Accumulator to operable status within 24 hours. If the Accumulator can not be restored to operable status, the Unit has to be depressurized to less than or equal to 1000 psi within 12 hours. On October 28, 2006 at 0334 hours, Accumulator #1 was declared inoperable. Unit 1 was depressurized to below 1000 psi on October 28, 2006 at 1430 EDT. The primary cause of this event was inadequate identification of inoperable equipment on the main control board which led the operator to use inaccurate level indication to fill the accumulator. Accumulator #1 level instruments were replaced and properly calibrated, and controls have been established to require identification of unavailable/inoperable components on the main control board. Formal Shift Briefings, as prescribed by plant procedure, have been held for each operating crew summarizing this event, the actions taken, expectations, and the location of control documents to prevent reoccurrence.
4252006001 | Vogtle 2 | 02/03/2006 | 04/06/2006 | ML06096044 | <strong>Two Reactor Coolant Pressure Boundary Leaks Lead to Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2006, control room operators received indication of an increase in radioactivity in the containment atmosphere. On February 3, 2006, a robotic camera observed leakage inside the bioshield wall in the area of reactor coolant system (RCS) loop 1. Unit 2 was placed in Mode 3 (Hot Standby) at 1806 EST, on February 3, 2006, to allow further investigation of specific leakage locations. At 2124 EST, this investigation found RCS pressure boundary leakage at two welded connections on a 3/4" bypass line around the Residual Heat Removal (RHR) loop suction valve, 2HV 8701 B, and shutdown to Mode 5 (Cold Shutdown) was initiated. On February 5, 2006, at 0035 EST, Unit 2 entered Mode 5 to comply with Technical Specification 3.4.13.a. due to the RCS pressure boundary leakage. Although the cause of the weld failures is undetermined at this time, the root cause investigation is still underway. Issues being addressed include high vibration of the bypass line, support design, excessive weld stress, and weld quality. The theory presented by the root cause team is the cause of the cracks was from high cycle fatigue. Corrective actions included replacement of the Loop 1 bypass line, inspection of supports and snubbers for both Unit 2 bypass lines, inspection of welds on the Loop 4 bypass line, and installation of monitoring instrumentation. Following additional monitoring, the cause determination will be completed, follow-up corrective actions implemented and a revised LER will be submitted by July 11, 2006.
4252006002 | Vogtle 2 | 03/20/2006 | 05/18/2006 | ML06139003 | <strong>Reactor coolant pressure boundary leakage leads to shutdown required by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0356 EST and 0603 EST on March 20, 2006, Unit 2 control room operators received alarms indicative of increased radioactivity in containment atmosphere. Sampling revealed the presence of the isotopes Na-24 and Co-58, which indicated the possibility of an active Reactor Coolant System (RCS) leak. On March 20, 2006, at 1300 EST a robotic camera observed leakage inside the bioshield wall in the area of RCS loop 1. The leakage was determined to be RCS pressure boundary leakage located at the 3/4" bypass line around the Residual Heat Removal (RHR) loop suction valve, 2HV-8701B, and shutdown to Mode 5 (Cold Shutdown) was initiated and achieved on March 21, 2006 at 1800 EST. Unit 2 was previously in Mode 5 to repair pressure boundary leakage at the 2HV-8701B bypass line on December 10, 2005 and February 5, 2006. The source of the leakage was a crack in a 'A" socket weld between a flow-restrictor and half-coupling. Several factors caused vibration-induced fatigue, which led to the weld failure: RCS vortex shedding frequency, acoustic frequency of the RHR Loop 1 piping, structural frequency of the 2HV-8701B bypass line, no axial support for the bypass line and performance of an activity to reduce accumulator in-leakage by reseating a Safety Injection (SI) primary hot leg check valve. Prior to returning the unit to power operations, the 2HV-8701B bypass and leak-off lines were removed and the connections plugged. Manual isolation valves adjacent to and upstream of SI test header check valves on Unit 2 Loops 1 and 4 were installed to reduce leakage to the accumulators. Previously installed temporary instrumentation was optimized on Unit 2.
4252006003 | Vogtle 2 | 08/27/2006 | 10/26/2006 | ML06300022 | <strong>Unit 2 Reactor Coolant Pump #4 Tripped, Resulting in an Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2006, at 0631 EDT, Unit 2 experienced an automatic reactor trip from 100% power. The Loop 4 Reactor Coolant Pump (RCP) tripped and the Reactor Protection System (RPS) actuated on "Reactor Coolant System Low Flow." The post-trip investigation revealed that, inside the RCP motor junction box, a degraded current transformer (CT) wire was in contact with a degraded surge arrestor cable shield. The degraded CT wire was grounded in the CT wiring junction box, creating a ground path that resulted in a fault in the RCP #4 motor junction box that caused the pump to trip. Investigation determined that the cause of this event was an inadequate design change package. Contributing causes were inadequate procedures, work instructions, and installation practices. Prior to restart, the Loop 4 RCP junction box CT wiring and CTs were replaced as well as the surge arrestor wiring and the differential protective relay in the feeder breaker cubicle for RCP #4.
4252006004 | Vogtle 2 | 10/01/2006 | 11/30/2006 | ML06334043 | <strong>ESF Room Cooler was Determined to be in a Condition Which was Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2006, Engineered Safety Feature (ESF) Room Cooler 2-1555-A7-003 was found running with no discernable air flow to the ESF equipment room. The primary equipment cooled by this room cooler is electrical equipment. Investigation discovered that the motor leads were wired incorrectly which caused the room cooler motor and fan to rotate backwards. Per Technical Specifications (TS), two ESF room coolers and safety-related chiller system trains are required to be operable to provide redundancy to ensure that the system functions to remove heat from the ESF equipment rooms during and after an accident, assuming the worst case single failure occurs coincident with a loss of offsite power. If one ESF room cooler and one safety-related chiller system train are inoperable, action must be taken to restore the train to operable status within 72 hours. ESF Room Cooler 2-1555-A7-003 was determined to have been inoperable for longer than allowed by TS. The cause of the event was personnel error resulting from inadequate use of the "Plant Equipment Component Configuration Control" procedure which resulted in rolling the motor leads at the Motor Control Center (MCC). This resulted in the ESF Room Cooler fan motor running in the reverse direction. Based on review of work history, the probable time was determined to have taken place in 1999 during MCC switchgear cleaning.
4402006001 | Perry | 01/17/2006 | 03/19/2006 | ML06087039 | <strong>Incorrect Wiring in the Remote Shutdown Panel Results in a Fire Protection Program Violation</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2006, at about 1000 hours, with the plant operating at 84% power, an internal wiring jumper on a switch in the Remote Shutdown Panel (RSP) was found to be installed incorrectly. The jumper was identified as a result of surveillance testing. The switch contact has the function of isolating control room circuitry from the RSP circuitry for the Reactor Core Isolation Cooling (RCIC) turbine exhaust valve. Complete isolation of the control room circuitry for the RCIC valve would not have been established by transferring control switches to the emergency position. Although no actual fire occurred, this was a violation of the fire protection program, which is a violation of the Operating License condition 2.C.6. The cause of the event was determined to be a wiring drawing error during manufacture of the panel that resulted in the switch being incorrectly wired. The cause of the wiring error was determined to be a less than adequate vendor drawing review that failed to discover a drawing error on a wiring diagram and less than adequate testing. A contributing cause was determined to be less than adequate understanding of fire protection related design functions and testing requirements of the RSP. Completed corrective actions were to rewire the switch correctly and to inform the manufacturer of the drawing and wiring error in the supplied RSP. Additional corrective actions will be to revise the necessary surveillances and the Updated Safety Analysis Report to clarify fire protection program testing requirements and to present lessons learned from this investigation to the Design Engineering Section. This event is reportable as a violation of the Operating License, paragraph 2.C.6, Fire Protection. This event was determined to be of very low safety significance.
4402006002 | Perry | 01/25/2006 | 03/24/2006 | ML06094064 | <strong>Scaffold Built in the Containment Pool Swell Region</strong><br /><i>Abstract:&nbsp;</i>During the investigation of the program used to build scaffolding inside containment, it was determined that the current evaluation was not adequate for scaffolding to be erected in the pool swell region. A condition report was written to determine if any past operability concerns existed for scaffolding that had been built within the pool swell region. This analysis was concluded on January 25, 2006 and it determined that scaffolding built on December 8, 2005 and December 28, 2005 with the plant operating in Mode 1 at 100% power was erected in the pool swell region of containment in support of maintenance activities. The initial evaluation concluded that the use of an engineering seismic evaluation and a probability risk assessment without analyzing for pool swell hydrodynamic missile hazards to justify allowing scaffolding to be built in the pool swell region is not acceptable. As a result of the inadequate reviews, scaffold installed in the pool swell region placed the plant in an unanalyzed condition with respect to potential hydrodynamic missile hazards in the event of a design basis loss of coolant accident. This was determined to be reportable per 10CFR50.73(a)(2)(ii)(B): any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.
4402006003 | Perry | 05/04/2006 | 07/03/2006 | ML06199029 | <strong>Incorrect Wiring in the Division 1 Emergency Diesel Generator Results in a Fire Protection Program Violation</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2006, while performing research for a calculation revision, it was discovered that one circuit of the Division 1 Emergency Diesel Generator (EDG) Control Room Pull-To-Lock (PTL) Control Switch was not designed to isolate the Control Room from the local Division 1 EDG controls in the event of a Control Room fire. At 1430 hours on May 4, 2006, with the plant in Mode 1 at 100% power, it was determined that this condition violated the Perry Nuclear Power Plant Fire Protection Program and could adversely affect plant shutdown in the case of a Control Room fire. A potential fire induced hot short in the EDG logic circuit could have resulted in a failure to start or a spurious trip of the EDG, even if control was transferred to local control. This condition has existed since 1989. Interim actions in the form of procedure changes have been completed to address this issue. A final resolution to this issue will be a design change to incorporate Appendix R Control Room isolation features to the EDG PTL control switch circuit. A telephone notification was made on May 4, 2006 at 1719 hours for this event. A follow-up written report is required within 60 days by the Operating License, paragraph 2.F and by Technical Specification 5.6.6.a. This event was determined to be of very low safety significance.
4402006004 | Perry | 09/21/2006 | 11/13/2006 | ML06325031 | <strong>Oscillation Power Range Monitors (OPRMs) Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2006, the Perry plant staff was notified by General Electric (GE) via a draft Safety Communication SC06-010 of a potential non-conservative setting of the OPRM Enabled Region Drive Flow Setpoint when the plant is in Single Reactor Recirculation Loop Operations. On September 21, 2006, at 1815 hours, based on available information, it was conservatively determined that all four OPRM channels were inoperable due to their current flow setpoint settings and uncertainties associated with OPRM enabling. On September 21, 2006, at 1815 hours, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.1.3 Action B.1 was entered to initiate an alternate method to detect and suppress thermal hydraulic instability oscillations. At 2005 hours, operators completed implementation of backup stability protection for detecting and suppressing thermal hydraulic instability oscillations to meet the TS LCO Action requirement. The cause of the condition was that the Boiling Water Reactor Owners Group and GE approved methodology, as supplied in NEDO-32465-A, was flawed for not considering the maximum indicated drive flow while in Single Loop Operations. All four channels of OPRMs remain inoperable until the setpoints are corrected. The safety significance of this event is very low.
4402006005 | Perry | 12/13/2006 | 02/09/2007 | ML07047036 | <strong>Decreasing Instrument Air Pressure Results in Manual Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2006, at approximately 0435 hours, operators manually initiated a Reactor Protection System actuation in response to decreasing Reactor Pressure Vessel (RPV) coolant level. At the time of the event, the plant was in Mode 1 (i.e., Power Operation) with the reactor operating at 100 percent of rated thermal power. All control rods fully inserted into the core and RPV coolant level was maintained such that no emergency core cooling systems were needed to maintain level. The cause of the event is attributed to decreasing Instrument Air System pressure caused by the separation of a header tubing elbow joint, which resulted in a transient in the Reactor Feedwater System. Less than adequate workmanship during plant construction, in the assembly of the air header joint, was determined to be the cause of the air header joint separation. The header tubing joint was replaced. Inspections of a sample of the accessible portions of the Instrument Air System were performed, prior to plant startup. Additional inspections of 2" and 3" soldered joints will be completed by the end of re-fuel outage 12 in 2009. The safety significance of this event is considered to be minimal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
4402006006 | Perry | 12/31/2006 | 03/01/2007 | ML07066046 | <strong>Primary Containment Airlock Door Inoperability Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 1, 2007, at approximately 0400 hours, with the plant operating at 100 percent power, control room operators determined that a condition identified on December 8, 2006, resulted in the lower Primary Containment Airlock Inner Door being inoperable. Operators entered Technical Specification (TS) Limiting Condition for Operation 3.6.1.2, and implemented required actions to verify that the operable door was closed and locked. The event was caused by less than adequate utilization of the work management electronic tracking process for potential operability reviews of work management documentation. The air leak was repaired. The backlog of "outstanding" work management documentation reviews was eliminated. An operations night order was issued to reiterate expectations for senior reactor operator reviews of new work management documents. Future guidance will be provided to rework containment airlock tubing to facilitate maintenance on the door seal accumulator tubing and check valves for proper installation and fit up. The "compression fitting connection and inspection" instruction will be revised to include restrictions on short straight runs of tubing between two fixed position fittings. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), operation prohibited by plant TS.
4432006002 | Seabrook | 03/08/2006 | 04/07/2006 | ML06102054 | <strong>Noncompliance with the Requirements of Technical Specification 6.8.1.2.a</strong><br /><i>Abstract:&nbsp;</i>This report is submitted pursuant to the requirements of Facility Operating License Condition 2.G. At approximately 0800 on March 8, 2006 it was discovered that the annual report tabulating exposure by work and job function required by TS 6.8.1.2.a was not submitted by the March 1 due date. The requirement to submit the report was tracked by Seabrook Station's Condition Reporting System. In early February, a Regulatory Compliance Analyst contacted Radiation Protection (RP) Records for the report. RP Records personnel contacted the NRC's Radiation Exposure Information and Reporting System (REM) regarding report submittal and was told reports were due April 30. Based on the information relayed from REIRS, the licensing analyst inappropriately changed the due date in the condition report to April 30 without reviewing Technical Specification 6.8.1.2a. On March 8, while confirming due dates for April correspondence, it was discovered that the report known at Seabrook Station as the Annual Report on Radiation Exposure by Job Function was required to be submitted by March 1. A 24-hour report (EN# 42397) was made to the NRC for a violation of an administrative technical specification.
4432006003 | Seabrook | 02/05/2006 | 05/23/2006 | ML06152034 | <strong>Voluntary LER for Deficient Hydrostatic Barriers</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER. On February 5, 2006 at approximately 0400, personnel performing scheduled surveillance testing inadvertently actuated one of five fire protection water deluge subsystems in the Seabrook Station cable-spreading room. The actuation resulted in a discharge of approximately 1000 gallons of water to the cable spreading room. An operator responding to the event discovered several small puddles of water on the floor of the safety related "A" train switchgear room located directly below the cable spreading room. An inspection of the switchgear room determined the electrical distribution equipment was unaffected by the water. The presence of water in the switchgear room was unexpected because the design of the cable spreading room floor is to function as a watertight hydrostatic barrier. The safety-related electrical equipment in the essential switchgear rooms does not have a comprehensive design tolerance for water. The cause of the event was that design basis flood protection requirements contained in various design and licensing documents were not incorporated into the original penetration seal specifications or the cable spreading room floor slab design. As a result, the cable spreading room floor and associated seals were not originally specified, designed or installed as hydrostatic barriers. No adverse consequences resulted from this event.
4432006004 | Seabrook | 06/22/2006 | 07/19/2006 | ML06207013 | <strong>Technical Specification Violation due to Inoperable Battery Charger</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2006, at 0620, with the plant at 100% power, it was discovered that there was no battery charger in service on one of the two Train B vital batteries in violation of Technical Specification 3.8.2.1, DC Sources. Further review determined that the battery charger had been disconnected from its associated battery bank since approximately 1858 hours on June 21 when alarms caused by the opening of the battery charger breaker were received in the Control Room. While securing battery charger 1B after capacity testing, Maintenance electricians opened breaker DN4, which isolated both the battery charger and the portable battery charger from 125 VDC Bus 11B. The maintenance activity should not have repositioned breaker DN4. The opening of the breaker resulted in two Control Room alarms which operators believed to be expected alarms associated with the maintenance activity. The condition went unrecognized for approximately 12 hours. The cause of the event was personnel error by the electricians for opening the breaker when unsure of how to secure the charger and by the licensed Control Room Operator for incorrectly processing the alarms as expected. Additionally, subsequent Operations personnel failed to recoginize the meaning of the alarms or validate the status of the battery.
4432006005 | Seabrook | 07/03/2006 | 07/27/2006 | ML06215035 | <strong>Technical Specification Violation with Inoperable Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 3, 2006 at 0615, during operation at 100% power, Seabrook Station determined that the unit had been operated in a condition prohibited by the TS for approximately 20 hours. An alarm annunciated in the control room on June 30, 2006 indicating a malfunction of a power supply associated with one MSIV control cabinet. Subsequent troubleshooting identified a problem with a MSIV valve control module. The MSIV was declared inoperable for troubleshooting and replacement of the control module. A subsequent examination of the failed valve control module on July 3 identified both power supply fuses open. This condition would have prevented the control module from functioning and would have rendered the MSIV inoperable. As a result, the MSIV was inoperable from receipt of the control room alarm until the failed valve control module was replaced, a duration of approximately 20 hours. The plant operated at full power during this time while the TS allow only four hours to restore a MSIV to operable status before requiring a plant shutdown or closure of the MSIV. Consequently, this event resulted in a condition prohibited by the TS. The cause of the MSIV power supply malfunction was a random failure of the MSIV control module printed circuit board. The control module was replaced and the MSIV made operable. No adverse consequences resulted from this event.
4432006006 | Seabrook | 08/31/2006 | 02/05/2007 | ML07039012 | <strong>Plant Shutdown due to Inoperable Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2006 at 1409 while in Mode 1 at 100% power, Seabrook Station entered the action statement of Technical Specification (TS) 3.8.1.1, AC Sources - Operating, for two inoperable emergency diesel generators (EDG). During a planned maintenance test run, the train A EDG received a voltage regulator diode failure light. During subsequent testing to confirm operability, the train B EDG displayed a diode failure light, experienced an over-voltage condition, and was declared inoperable. With two EDGs inoperable, the station entered action f of TS 3.8.1.1, which requires restoration of one EDG within two hours or a shutdown to Hot Standby within the next 6 hours. A plant shutdown commenced at 1530. The NRC was notified in a four-hour report (event # 42820) in accordance with 10CFR50.72(b)(2)(i). The plant entered Mode 3 at 2052 on August 31, 2006. EDG-B was restored to operable status at 1359 on September 1, and the unit remained in mode 3 during repair of EDG-A. EDG-A was restored to operable status at 1928 on September 2, 2006. A Root Cause evaluation determined that the EDG-A diode failure light was caused by an imbalanced voltage input to the gate firing card. The EDG-B over voltage was caused by a high fly back diode circuit resistance in conjunction with a fast start voltage transient. No adverse consequences resulted from this event.
4462006001 | Comanche Peak 2 | 06/25/2006 | 08/24/2006 | ML06256004 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2006, Comanche Peak Steam Electric Station (CPSES) Units 1 and 2 were both in Mode 1 operating at approximately 100% power. While performing operator rounds on Unit 2, a Plant Equipment Operator (PEO) observed an oscillation in the air pressure supplied to the actuator of atmospheric relief valve (ARV) 2-PV-2328 on the #4 main steam line. Troubleshooting by the plant staff identified that the manual isolation valve in the instrument air supply from the accumulator to the air operator of the ARV was stuck closed. The valve was replaced and sent to an off site investigator for failure analysis. The results of this failure analysis indicated that a manufacturing defect and misalignment between the seat and disk led to the valve sticking closed. Due to the failure mode identified, this stuck closed condition had most likely existed since June 8, 2006, a period of time greater than that allowed by Technical Specifications. This report also includes voluntary reporting of data pursuant to the requirements of 10CFR21. All times in this report are approximate and Central Daylight Time unless noted otherwise.
4462006002 | Comanche Peak 2 | 10/27/2006 | 12/18/2006 | ML06361012 | <strong>Reactor Trip due to a Secondary Transient Initiated During Load Rejection Testing</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2006, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at approximately 28% power following the completion of the ninth refueling outage. During turbine load reject testing, a transient was initiated in the secondary system that resulted in a Steam Generator 2-02 Hi Hi level before manual control could be achieved. This resulted in the generation of a P14 signal causing a turbine trip and a Main Feedwater (MFW) pump trip. A manual reactor trip was initiated due to a loss of MFW. Auxiliary Feedwater automatically started and all systems responded normally during and following the trip. The cause of this event was the initiation of an oscillation in the Main Steam system while implementing a load rejection test which caused indicated steam flow to oscillate between 0 and 1.4Mlb/HR. The MFW, Heater Drain, and Steam Dump control systems were not able to dampen the oscillations. This caused steam flow and feed flow fluctuations that resulted in a turbine trip, MFW pump trip, and subsequently a manual reactor trip. Corrective actions include evaluating changes in the dampening for control inputs in the secondary system and training to ensure lessons learned from this event are shared. All times in this report are approximate and Central Time unless noted otherwise.
4462006003 | Comanche Peak 2 | 10/29/2006 | 12/18/2006 | ML06361012 | <strong>Reactor Trip due to Feedwater Regulating Valve Malfunction</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2006, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at approximately 80% power following the completion of the ninth refueling outage. While holding for xenon stabilization in preparation for incore/excore calibration, a "Steam Generator 3 Steam and Feedwater Flow Mismatch" was received. Manual control of the Steam Generator (SG) 3 Feedwater regulating valve was taken, but operators were unable to control feed flow. A manual reactor trip was initiated in anticipation of an automatic reactor trip on SG3 Lo Lo level. Auxiliary Feedwater automatically started on low-low level in SG 3. All systems responded normally during and following the trip. The cause of this event was believed to be a loose wire on a Unit 2 Feedwater regulating valve Weidmuller terminal block. Corrective actions included tightening the loose wire and inspecting the connections in other safety related Unit 2 Feedwater regulating valve and bypass valve terminal boxes. Future actions include inspecting the connections for safety related Unit 1 Feedwater regulating valve and bypass valve terminal boxes and checking the tightness of both the instrument and field terminals on all Weidmuller terminal blocks whenever either side of a circuit is being worked on a Weissmuller terminal block. All times in this report are approximate and Central Time unless noted otherwise.
4542006001 | Byron 1 | 01/24/2006 | 03/24/2006 | ML06089030 | <strong>Technical Specification Required Action Completion Time Exceeded for Inoperable Containment Isolation Valves due to Untimely Operability Determination</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2006, a Chemistry technician recognized an abnormal condition while attempting to obtain a Pressurizer liquid sample. He noted that he was able to obtain sample flow at the sample panel with both containment isolation valves and the sample panel isolation valve closed. The technician and his supervisor didn't have sufficient knowledge to recognize the potential impact on containment integrity with this condition and did not promptly notify Shift Operations. The supervisor did document the condition in a Corrective Actions Program Issue Report (IR) the next day on January 24, 2006 but failed to notify Shift Operations of the IR, which would have generated a prompt operability determination. On January 25, 2006 during subsequent IR screening activities, Shift Operations became aware of the condition and initiated a prompt operability evaluation. The containment isolation valves were declared inoperable at 1250 hours on January 25, 2006 and appropriate Technical Specifications entered and followed. This event is reportable in accordance with 10CFR 50.73 (a) (2) (i) (B), as an event or condition prohibited by Technical Specifications. Even though all Technical Specification actions were accomplished within the completion times there was firm evidence to indicate the inoperable condition existed on the day before. The operability evaluation and subsequent inoperability declaration should have occurred on January 24, 2006. The cause of this event was inadequate understanding within the Chemistry department concerning the threshold of when to report equipment issues to Shift Operations. Corrective actions include reinforcing the correct expectation to Chemistry personnel. During this delay in declaring the containment isolation valves inoperable the penetration flow path was always isolated.
4542006002 | Byron 1, Byron 2 | 04/11/2006 | 06/12/2006 | ML06163006 | <strong>All Refueling Water Storage Tank Level Instrumentation Channels Made Inoperable During a Single Channel Calibration Activity due to a Design Flaw</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2006, during the 18-month calibration of one of four Refueling Water Storage Tank (RWST) level channels, a licensed control room operator noticed a minor deviation in one of the other level channels. This anomaly was documented in the corrective action program. The ensuing investigation concluded on April 11, 2006, that the 1989 modification to the reference leg of the four channels was flawed in that it did not provide for a single channel calibration activity without impacting the other three channels. The condition renders the four safety related channels of RWST level indication inoperable when one of the four is being calibrated. The cause is a legacy issue with the design change process in the 1989 time frame and could not be exactly determined. Corrective actions involve modifying the channels to allow for single channel calibration without impacting the other channels and performing a extent of condition review of other plant modifications. This event had minimal safety consequences. This condition is reportable to the NRC under 10 CFR 50.73(a)(2)(v), as an event or condition that could have prevented fulfillment of a safety function.
4542006003 | Byron 1 | 09/01/2006 | 10/30/2006 | ML06304018 | <strong>Inadvertent Exceeding of Technical Specification Action Requirement Completion Time for Containment Spray Additive System due to Not Recognizing an Inoperable Condition</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2006, a Non-Licensed Operator (NLO) identified a leak on a weld on the upstream side of a Unit Containment Spray Additive Drain Isolation Valve (i.e., CS043A). Shift Management was notified and a Corrective Actions Program Issue Report (IR) was written. However, due to imprecise communications this was not recognized as an inoperable condition until September 1, 2006. The root cause was determined to be lack of reinforcement of operability considerations with Shift Management related to equipment related IRs. Corrective Actions include the development and implementation of a systematic methodology to improve the effectiveness of classroom and simulator training for operability determinations on IRs. In addition, a management standard that rewards behaviors associated with operability documentation/verification of that documentation related to equipment IRs. This condition had minimal safety consequences. The leak was characterized as a weeping type of leak (i.e., less than 1 drop per 5 minutes) and would have insignificant impact on the amount of caustic delivered to the CS system. This is reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(i)(b) as an event or condition that is prohibited by the TS.
4562006001 | Braidwood 1 | 04/25/2006 | 07/18/2006 | ML06200019 | <strong>Unit 1 Reactor Coolant System Pressure Boundary Leakage due to Inter-Granular Stress Corrosion Cracking of a Pressurizer Heater Sleeve</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2006, while removing insulation from the surge line of the Unit 1 pressurizer, an insulation contractor discovered boric acid on the insulation. On April 25, 2006, the leakage was identified as originating from the number 52 pressurizer heater near the upper weld between the pressurizer heater sleeve and heater coupling. Technical Requirements Manual Limiting Condition for Operation (TLCO) 3.4.f Condition A was entered for one or more ASME components not in conformance due to pressure boundary leakage. The heater coupling and a portion of the sleeve was cut out of the system and the remaining portion of the heater sleeve was plugged and welded using an engineered ASME section III repair detail. On April 28, 2006, following the repair of the pressurizer, TLCO 3.4.f Condition A was exited. Analysis of the boric acid found on the pressurizer and the pressurizer insulation determined a leak existed during the past operating cycle which is not in compliance with Technical Specification 3.4.13, "RCS Operational Leakage," that states there will be no pressure boundary leakage in Modes 1, 2, 3 and 4. This leak was identified through refueling outage inspection activities, not during plant operation. The root cause of the observed boric acid leakage was intergranular stress corrosion cracking of the number 52 pressurizer heater sleeve through a locally sensitized section of the Type 316 stainless steel base material. The corrective action to prevent recurrence will be the implementation of long-term recommendations provided by the Exelon Generation Company, LLC, Asset Management Group to prevent future leakage, and implementation of actions required to comply with industry guidance to accept visual examinations for evidence of leakage. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(ii)(A).
4562006002 | Braidwood 1, Braidwood 2 | 10/04/2006 | 12/04/2006 | ML06338044 | <strong>Units 1 and 2 Entry into Limiting Condition for Operation 3.0.3 due to Main Control Room Ventilation Envelope Low Pressure</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being submitted to report a condition that may be of generic interest for licensees. On October 4, 2006, at 0138, the Main Control Room (MCR) received an annunciator alarm for MCR low pressure. Operations entered the applicable alarm response and instructed a Non-licensed Operator (NLO) to adjust Auxiliary Building pressure. At 0220, an NLO adjusted pressure in the Auxiliary Building, raising it to above the minimum required value. Operations personnel continued to investigate the reason for the MCR annunciator alarm. At 0247, Operations personnel reported to the MCR that the door that connects Division 21 Miscellaneous Equipment Electric Room and the Train B Control Room Ventilation Room was found open. Operations personnel promptly shut the door and the MCR low pressure annunciator cleared. A late log entry was made to enter Technical Specification (TS) 3.7.10 conditions A & E and TS 3.0.3 for both units at the point of discovery of the door being found open, which was at 0247. The LCOs were subsequently exited immediately after the door was closed at 0247. This did not result in a dual unit shutdown. There were no safety consequences impacting plant or public safety as a result of this event. Braidwood Station is reporting this as a voluntary Licensee Event Report.
4582006001 | River Bend | 01/05/2006 | 03/06/2006 | ML06072003 | <strong>Unanalyzed Condition Regarding RCIC Availability in Post-Fire Safe Shutdown Scenario</strong><br /><i>Abstract:&nbsp;</i>On January 5, 2006, an engineering assessment of the River Bend Station fire protection program identified a deficiency in the post-fire safe shutdown analysis. Specifically, the safe shutdown analysis assumes that the reactor core isolation cooling (RCIC) system is available for operation at the remote shutdown panel following a postulated main control room (MCR) fire. The assessment determined that motor-operated valve E51-MOVF063, the RCIC inboard steam supply isolation, would be rendered nonfunctional. This valve is normally open, but must be assumed to close spuriously due to postulated damage to its control circuitry during the MCR fire. In this specific scenario, the valve would not be controllable from the remote shutdown panel, and the RCIC system would not be available. This is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as an unanalyzed condition that significantly degrades plant safety. This condition does not cause the RCIC system to be inoperable with respect to its functions required by plant Technical Specifications. At the time of this discovery, the plant was operating at 100 percent power. Interim compensatory actions have been implemented to preclude the postulated loss of the function of this valve.
4582006002 | River Bend | 01/24/2006 | 03/27/2006 | ML06093068 | <strong>Loss of Safety Function of High Pressure Core Spray due to Manual Deactivation</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2006, at 7:32 p.m. CST, the high pressure core spray (HPCS) system was inadvertently initiated during surveillance testing. The plant was operating at 100 percent power at the time. The HPCS injection valve was open for approximately 40 seconds before the operators manually closed the valve. The Division 3 diesel generator (DG) also automatically started in response to the actuation signal. The DG did not automatically connect to the Division 3 switchgear since there was not a low voltage condition on that bus. The manual closure of the injection isolation valve caused the system to be incapable of responding to an automatic actuation signal. The manual override of the injection isolation valve was reset approximately 97 minutes after the event, restoring the system to its standby condition. This event was caused by lack of procedural guidance concerning test leads needed for the surveillance. The affected procedures were subsequently revised and successfully completed. This event is being reported in accordance with 10CFR5073(a)(2)(iv) as an invalid actuation of the HPCS system, and with 10CFR50.73(b)(3)(v)(d) as a condition that caused the loss of function of the HPCS system. This event is also reportable pursuant to River Bend Station Technical Requirements Manual Section 5.6.9.2., "ECCS Systems Actuations."
4582006003 | River Bend | 04/04/2006 | 09/05/2006 | ML06255044 | <strong>Automatic Start of Division 2 Standby Service Water System During Normal Service Water Pump Shift</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2006, at approximately 2:46 p.m., the Division 2 standby service water system started automatically in response to a low pressure condition in the normal service water system. The plant was operating at 98 percent power at the time of the event. A planned shift of the running normal service water pumps was being performed, and system pressure momentarily dropped below the trip setpoint of the instrumentation that starts the standby service water pumps. This condition is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an automatic actuation of the standby service water system. Operators implemented the appropriate response procedures, and the Division 2 SSW system was restored to its normal alignment at 5:36 p.m. that day.The standby service water system responded as designed to the low pressure condition in the normal service water system. This event was of minimal safety significance.
4582006004 | River Bend | 04/15/2006 | 06/14/2006 | ML06171008 | <strong>Automatic Reactor Scram following Recirculation Pump Downshift due to Failed Optical Isolator Card</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2006, at 4:15 p.m., an automatic reactor scram occurred while the plant was operating at 100% power. Prior to the scram, both reactor recirculation pumps shifted from high to slow speed due to a failed optical isolator card in the reactor protection system. With the reactor control rod pattern set for full power operation, the decrease in reactor recirculation flow caused the average power range monitors (APRM) to trip on a simulated high thermal power signal. The APRM trip signal caused the reactor scram approximately twelve seconds after the recirculation pumps downshifted. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a valid actuation of the reactor protection system. There were no safety-related systems out of service at the time of the event. Plant systems responded to the scram as designed, and reactor pressure and water level were promptly stabilized. Both optical isolator cards in the EOC-RPT circuitry were replaced during the forced outage. A downshift of both reactor recirculation pumps while operating at full power is an event analyzed in the River Bend Updated Safety Analysis Report. As such, this event was of minimal safety significance.
4582006005 | River Bend | 05/01/2006 | 10/24/2006 | ML06303003 | <strong>Automatic Start of Standby Service Water During Realignment of Reactor Plant Cooling Water</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2006, at approximately 6:59 a.m., an unplanned automatic actuation of the Division 1 standby service water system occurred during a realignment of the reactor plant component cooling water (CCP) system. The plant was in cold shutdown for a refueling outage at the time. This event is being reported in accordance with10CFR50.73(a)(2)(iv) as an automatic actuation of an emergency cooling water system. The actuation occurred due to a low pressure signal in the CCP system, caused by a partial drainage of a section of the system during testing and maintenance. A contributing cause of this event was the masking effect of the pre-existing flush on the monitoring of CCP system operations. The manual valves that caused the drainage have been tentatively scheduled for repair in the next refueling outage. There was no loss of cooing water to any safety-related components, and the standby service water system responded to the actuation signal as designed. This event was of minimal safety significance.
4582006006 | River Bend | 05/27/2006 | 07/26/2006 | ML06213007 | <strong>Plant Mode Change with One Offsite Power Supply Inoperable Due to 4.16kv Breaker Alignment</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2006, while the unit was operating at 100 percent power, the determination was made that one of the required offsite power supplies to the Division 3 standby switchgear had been inoperable during the recent plant startup on May 13, 2006. A 4160 volt circuit breaker in one of the power supplies to Division 3 was not functional at the time of the plant startup. This condition does not meet the requirements of Technical Specifications Limiting Condition for Operation 3.0.4. In addition, during the investigation, it was determined that the surveillance test procedure that implements Surveillance Requirement 3.8.1.1 did not include the verification of the alignment of the offsite power supplies to Division 3. A similar condition was also found to exist for Surveillance Requirement 3.8.1.8. These conditions are being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications. The circuit breaker was subsequently repaired and demonstrated to be functional. The Division 3 emergency diesel generator is the safety-related power source for the Division 3 switchgear, and it was operable at the time this condition was discovered. Therefore, this condition was of minimal safety significance.
4582006007 | River Bend | 10/19/2006 | 12/18/2006 | ML06360017 | <strong>Automatic Reactor Scram due to Inadvertent Isolation of Main Feedwater Headers</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2006, at approximately 5:57 p.m. CDT, an automatic reactor scram occurred in response to a low water level signal (Level 3) in the reactor vessel. This condition was the result of the inadvertent closure of the motor-operated isolation valves in the main feedwater headers supplying the reactor. These valves closed when part of a chart recorder was accidentally dropped on their control switches. The high pressure core spray system automatically actuated as designed when its reactor water level (Level 2) initiation setpoint was reached. The reactor core isolation cooling system was out of service for planned maintenance. Reactor steam pressure began to decrease as expected, and when pressure reached 849 psig approximately three minutes after the scram, the main steam isolation valves (MSIVs) automatically closed. The MSIVs closed because the reactor mode switch was not promptly re-positioned as required by scram response procedures. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the reactor protection system and the high pressure core system (including the Division 3 diesel generator). Also, primary containment isolation signals actuated as a result of the Level 2 condition and the low reactor steam pressure signal to the MSIVs.
4612006001 | Clinton 1 | 03/20/2006 | 05/17/2006 | ML06145031 | <strong>Failure to Tighten Terminal Screw Causes Turbine/Generator Trip and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 3/20/06, at about 0450 hours with the plant at about 96 percent power, an open circuit in the C Phase neutral Current Transformer (CT) of the Main Generator output caused the Generator Differential Overcurrent 87-G1 relay to trip due to a sensed current imbalance. Actuation of the 87-G1 relay resulted in a Generator Trip / Lockout and an automatic Turbine Electro Hydraulic Control (EHC) trip. The Turbine EHC trip caused a Turbine Control Valve fast closure and a Reactor Protection System signal for the automatic scram. A loose terminal screw on the CT lead wire caused the open circuit, resulting in high resistance and overheating that melted the wire. The cause of this event was inadequate workmanship that occurred during Generator High-Potential testing, as a result of a process weakness. The inadequate workmanship most likely occurred during the eighth refueling outage. Terminal screws at the C phase CT were most likely loosened to install test leads and not adequately retightened following removal of the test leads, resulting in a failure of the wire termination. Corrective action includes adding process controls to ensure that lifted and landed leads will be adequately tightened in the future.
4612006002 | Clinton 1 | 08/17/2006 | 11/10/2006 | ML06325035 | <strong>Turbine Bypass Function Lost due to Circuit Card Maintenance Frequency</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2006, with the station operating in Mode 1 at 96 percent power, operators received a Main Condenser low vacuum alarm. Operators verified condenser vacuum was normal. Initial troubleshooting identified a false low condenser vacuum signal was present, inhibiting the Main Turbine bypass valves from being able to perform their safety function if called upon. Since no other system performs the Main Turbine Bypass System safety function, the safety function was not available. The actions of Technical Specifications (TS) 3.7.6, Main Turbine Bypass System, we reentered for the inoperable Main Turbine Bypass System, requiring the system to be restored to operable status within 2 hours. A lead was lifted to remove the low vacuum inhibit logic input which restored the Main Turbine Bypass valve function before the TS 2-hour action completion time expired. The cause of this event was failure of Main Condenser Pressure Trip Unit (electronic circuit card) components due to not having an appropriate replacement interval for the card. Corrective action includes replacing the circuit card that failed and revising the maintenance template for this type of circuit card to include an appropriate replacement frequency.
4612006003 | Clinton 1 | 08/27/2006 | 10/23/2006 | ML06304058 | <strong>High Reactor Water Level Scram Result of Bad Inverter Circuit Board Solder Joint</strong><br /><i>Abstract:&nbsp;</i>On 8/27/06, the station experienced a momentary loss of safety-related Division 4 Nuclear System Protection System (NSPS) inverter resulting in an automatic reactor scram on high reactor water level. The event cycled the safety-related 120 Volts Alternating Current (VAC) NSPS bus causing the Division 3 emergency diesel generator, the Division 3 shutdown service water system, and the High Pressure Core Spray System (HPCS) to automatically start, and HPCS to inject water into the reactor vessel. The loss of inverter also caused the "A" Reactor Recirculation (RR) pump to trip. The loss of the RR pump combined with the HPCS injection caused reactor vessel water level to increase to the high reactor water level trip. The cause of the momentary loss of the inverter was an intermittent failure of an inadequate solder joint in the Division 4 NSPS inverter. The solder joint is located on the backplane circuit board, and is a common node for both inverter and bypass transformer sources of power. Failure of the connection resulted in a loss of power to the safety-related 120 VAC bus. Corrective action includes replacement of the circuit board in the Division 4 inverter and the same board in the Division 3 inverter, and revising the purchasing description for the backplane circuit boards to disallow boards of this vintage. This event is reportable under 10CFR 21.
4612006004 | Clinton 1 | 11/09/2006 | 12/19/2006 | ML07009051 | <strong>Inadequate Configuration Control Risk Assessment Causes Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On 11/9/06, operators received an alarm indicating the Division 3 shutdown service water system (SX) was not available and a status light for a loss of position indication for motor-operated valve 1SX014C, plant service water system to Division 3 shutdown service water system header isolation, indicating the valve was not available. Operators declared the Division 3 SX, high pressure core spray (single train safety system), and Division 3 emergency diesel generator systems inoperable and unavailable. Investigation identified a security officer on rounds bumped the circuit breaker hand switch for valve 1SX014C, moving it to the off position. The officer was carrying a protective mask in a large bag attached to the officer's thigh. When the officer passed the circuit breaker panel, the bag contacted the breaker hand switch and actuated it. The officer was unaware the bag had contacted the breaker. The cause of this event was Security Management failed to adequately assess the inadvertent contact configuration control risk when the requirement to carry the mask in a bag attached to the thigh was implemented in 2005. Corrective actions include designating the area where the event occurred as an exclusion area and providing security officers a different route to pass this equipment, and walking down the plant to identify safety-related equipment subject to inadvertent contact.
4822006001 | Wolf Creek | 02/10/2006 | 04/11/2006 | ML06108059 | <strong>Potential for Fire-Induced Damage to Motor Operated Valves During an Appendix R Fire Event</strong><br /><i>Abstract:&nbsp;</i>As a result of Wolf Creek Nuclear Operating Corporations 2005 Triennial Fire Protection Inspection, a re-evaluation of concerns described in NRC Information Notice 92-18, "Potential For Loss Of Remote Shutdown Capability During A Control Room Fire" was performed. During that re-evaluation, on February 10, 2006, it was identified that in the event of a fire in the control room, 40 motor operated valves (MOVs) credited for post-fire safe shutdown could potentially fail in an unanalyzed condition. In the 40 MOV circuits, an intra-cable hot short between one conductor on the hot side of the indication circuit and another conductor on the load side of the control room hand switch could bypass the torque switch and energize either the open or close coil. The loss of protection from the torque switch could result in damage to the valve such that it could not be manually operated. Of those 40 MOVs, failure of 8 of the MOVs could potentially prevent achieving and maintaining safe shutdown conditions. An hourly fire watch was established in the Control Room due to a previous condition identified on November 16, 2005. This condition was included on the hourly fire watch.
4822006002 | Wolf Creek | 05/24/2006 | 07/21/2006 | ML06208052 | <strong>Potential for Fire-Induced Damage to Class 1E Electrical Equipment Air Conditioning Units During an Appendix R Fire Event</strong><br /><i>Abstract:&nbsp;</i>On May 24,2006, while performing the Post Fire Safe Shutdown (PFSSD) review for fire area C-35, an unanalyzed condition was discovered. A design basis fire in fire area C-35, located in the Control building, could prevent operation of both Class 1E electrical equipment air conditioning units. The postulated fire could damage cables associated with the automatic fire isolation circuit on the fan units. If the cables are damaged in a manner that causes an open circuit, the air conditioning units will shut down or fail to start. Loss of the Class 1E air conditioning units does not directly result in loss of capability to safely shut down. Rather, room heating beyond design limits could reduce the life of electrical components within the switchgear. A continuous fire watch was established for fire area C-35. The continuous fire watch was reduced to an hourly fire watch after a temporary procedure change was completed to allow the use of a jumper to restore the Train "A" Class 1E air conditioning unit to service.
4822006003 | Wolf Creek | 10/11/2006 | 12/07/2006 | ML06349004 | <strong>Indications Discovered on Pressurizer During Preplanned In-service Inspections</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2006, at approximately 12:40 Central Standard Time, Engineering personnel performing pre-planned in-service examination of the pressurizer nozzle to safe end dissimilar metal (DM) welds reported the identification of five circumferential flaw indications. Three indications were located in the surge nozzle DM weld, one indication was in the "C" safety nozzle DM weld, and one indication was in the relief nozzle DM weld. The locations are part of the Reactor Coolant System (RCS) pressure boundary. There was no evidence of RCS pressure boundary leakage. The most probable mechanism responsible for the indications is primary water stress corrosion cracking (PWSCC). Wolf Creek Generating Station was shutdown for its 15th refueling outage and was in Mode 5, cold shutdown. Weld overlay of the safe end DM welds on the pressurizer was an activity scheduled for the Refuel 15 outage. Weld overlay repairs of the flaw indications were performed prior to the unit's return to power operations. The safety significance of this event is low. These circumferential flaw indications were smaller than critical flaw sizes reported in Material Reliability Program, MRP-113. Although welds may be susceptible to PWSCC that can result in small leaks, industry experience with PWSCC shows that complete failure of the weld joints is considered to be very unlikely.
4822006004 | Wolf Creek | 10/24/2006 | 12/21/2006 | ML06362009 | <strong>Failure to Maintain Closure of Containment Penetrations During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2006 with the plant in Mode 6, Refueling, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel discovered a condition where containment closure, per Technical Specification 3.9.4 was not met. An air-to-air pathway existed from the containment recirculation sumps through the containment spray system to the auxiliary building. The containment recirculation sump suction for the containment spray pump B valve was stroked open while valves ENV0068 and ENV0095 were uncapped and open under a clearance order. Upon discovery, the penetration was immediately placed under administrative control.
4832006001 | Callaway | 11/14/2005 | 03/14/2006 | ML06083041 | <strong>Pressurizer PORV Stroke Time and Other Delays Exceed Times Assumed in COMS Analyses</strong><br /><i>Abstract:&nbsp;</i>During testing on 11/14/2005 the pressurizer Power Operated Relief Valves (PORV)s, BBPCV0455A and BBPCV0456A, initially closed slower than the maximum stroke time allowed (2 seconds) in the test procedure. The open stroke time for both valves were within procedure limits. Subsequent review of the basis for the stroke time values indicated that the limits in the procedure were not conservative with respect to the maximum allowed stroke times credited in the Callaway Analysis of Record (AOR) for a Cold Overpressure Mitigating System (COMS) function. The analysis for COMS assumes an opening time and delay time for the pressurizer PORVs. Evaluations have determined that PORV stroke times measured during surveillance testing did not account for all of the delay times credited in the Design Bases COMS AOR. Further reviews determined the allowed delay times could not be met by the control loop. This results in PORV stroke times which are non-conservative to the COMS AOR.
4832006002 | Callaway | 02/13/2006 | 04/13/2006 | ML06109052 | <strong>Unexpected Inoperability of 'A' Control Room AC due to a Failed Discharge Reed Valve in Its Associated Compressor</strong><br /><i>Abstract:&nbsp;</i>In January 2006, after approximately 22 years of service, the compressor to the 'A' Control Room A/C (Air Conditioner) unit was replaced as part of scheduled preventive maintenance. The A Control Room A/C was tested, placed in service, and declared Operable on 01/12/2006. On 02/13/2006, the System Engineer was performing a system walkdown and found the temperature of one of the three compressor cylinder heads to be higher than expected. Believing the unit remained functional, the System Engineer reported his findings to the appropriate Operations personnel. The unit was subsequently declared Inoperable on 02/15/2006, when Engineering determined there was insufficient data to support maintaining the A Control Room A/C unit as Operable. The System Engineer initiated a job to inspect the compressor and perform necessary repairs. During disassembly of the suspect cylinder head, foreign material was found in the compressor and later a hole was found in one of the discharge reed valves. The repair to the compressor was completed and the A Control Room A/C unit was tested and declared Operable on 02/16/2006. The compressor valve plate was submitted for laboratory analysis to help establish the cause of the failure. A root cause analysis team evaluated the facts and evidence of this event. The root cause analysis team determined the most iikely root cause of the compressor failure was due to foreign material within the compressor, introduced by the manufacturer.
4832006003 | Callaway | 03/10/2006 | 12/04/2006 | ML06346009 | <strong>Unexpected Inoperability of the Emergency Exhaust System due to Inoperable Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>During post maintenance testing following a preventive maintenance activity, the A train Control Building supply air damper was found unable to travel to a fully open or closed position rendering the damper and associated train of the Emergency Exhaust System inoperable on 3/9/2006. Subsequent stroke testing of the B train Control Building supply air damper was conducted on 3/10/2006 as part of an extent of condition investigation. The B train damper was also found unable to fully open or close, rendering it and the remaining train of the Emergency Exhaust System inoperable on 3/10/2006. Actions initiated to restore the dampers discovered broken tack welds on the damper actuator weld pads of both dampers. A root cause analysis team determined the most likely root cause of the damper failures was the performance of scheduled stroke tests on these dampers occurring shortly after a significant winter weather event in 1995 that had caused icing on the damper blades. Torsional stress against the ice buildup caused significant weakening, if not cracking, of the damper tack welds. Over the ensuing years, cyclic loading of the welds during damper actuations applied stresses to the weakened welds ultimately resulting in the weld failures observed on March 9 and 10, 2006. The root cause team also found that failure to evaluate the 1995 stroking event under the corrective action program and inadequate preventive maintenance practices prevented identification and correction of the degradation prior to failure.
4832006004 | Callaway | 05/12/2006 | 08/10/2006 | ML06229028 | <strong>Turbine Trip at 47% Power with Rods in Auto Leads to Manual Reactor Trip and Aux. Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On 5/12/2006 reactor power was being reduced to 45% for a planned maintenance activity. Reactor power had been lowered to approximately 48% when vibration on main turbine bearings started rising eventually reaching the turbine trip criteria. The turbine was manually tripped at 0047 on 5/12/2006. Control rods subsequently stepped in under automatic rod control, as designed. The control rods continually stepped in reducing power below 10% in approximately four minutes. Feedwater flow was controlled through the Main Feedwater Regulating Valves which are not normally in service below 20% power. At 0052, the Steam Generator High-High Level setpoint was exceeded on the A Steam Generator resulting in a Feedwater Isolation Signal and Motor Driven Auxiliary Feedwater Actuation Signal. All safety systems responded as designed. A manual reactor trip was initiated at 0053 in accordance with procedural guidance for the loss of both main feedwater pumps. The cause of this event is an inadequate mitigation strategy in procedure OTO-AC-00001, "Turbine Trip below P-9" (50% power permissive setpoint). The procedural deficiency was the result of an inadequate procedure change review process used in 1991. Corrective Actions to Prevent Recurrence include revision of the procedure change review process and revision of OTO-AC-00001 to incorporate an appropriate mitigation strategy.
4832006005 | Callaway | 06/06/2006 | 08/03/2006 | ML06228045 | <strong>Loss of a Train Off-site Vital Power During Relay Testing in Switchyard</strong><br /><i>Abstract:&nbsp;</i>LOSS OF A TRAIN OFF-SITE VITAL POWER DURING RELAY TESTING Callaway Plant was in MODE 1 at 100 percent power on June 6, 2006. Work was in progress calibrating B switchyard bus lockout devices. At approximately 1339 CDT during performance of this work, Callaway Plant experienced a loss of one of two switchyard buses. This resulted in loss of A train offsite power with subsequent actuations consistent with loss of one vital AC train. The A diesel generator started and loaded. B train offsite vital power and emergency diesel generator were available. Emergency systems responded as expected. Investigation of the switchyard bus trip revealed a set of contacts was stuck closed in a relay that was being returned to service. After the failure, the relay was tested several times without the contacts sticking. The contacts were burnished, and the relay was returned to service. The cause of the stuck contacts is indeterminate. Callaway will develop a comprehensive procedure to improve control of the switchyard maintenance scope and access.
4832006006 | Callaway | 08/05/2006 | 09/22/2006 | ML06278022 | <strong>Unexpected Inoperability of 'B' Emergency Exhaust System due to Main Control Board Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On 08/05/2006, the Train B Auxiliary Building Supply Damper, GLD0047, failed to close during a Technical Specification surveillance. The Train B Emergency Exhaust System was declared inoperable. A job was initiated to inspect the damper and damper motor and perform necessary repairs. Upon investigation, it was determined the damper motor was not receiving power and the handswitch on the Main Control Board had failed. When preparing to remove the handswitch, it was noticed the contact block plunger was protruding from the end of the handswitch assembly. This indicated the handswitch contacts were stuck in an abnormal alignment. The handswitch was replaced and the Train B Emergency Exhaust System was declared operable on 08/05/2006 after testing the proper operation of the damper. The handswitch was later disassembled by the System Engineer and foreign material was found inside the contact block of the handswitch. The foreign material was submitted for laboratory analysis to help establish the source of the material and possible causes of the failure. A root cause analysis team evaluated the facts and evidence of this event. The team determined the root cause of the handswitch failure was foreign material within the contact block of the handswitch, introduced during a modification to a main control board panel in the Main Control Room, during initial construction of the plant.
4832006007 | Callaway | 08/07/2006 | 11/17/2006 | ML06328020 | <strong>Inoperability of Train A Containment Coolers due to Inadequate Testing</strong><br /><i>Abstract:&nbsp;</i>The Train A Containment Coolers were determined to be inoperable for more than seven days during cycle 14 at Callaway Plant. Callaway Plant received NRC report "Callaway Plant - NRC Integrated Inspection Report 05000483/2006003," on August 7, 2006. The report stated the performance data for the Train A Containment Coolers did not demonstrate the Containment Coolers were capable of performing their required design bases function between August 16, 2005 and September 17, 2005 because of fouling. The Resident Inspectors independently performed calculations to verify operability of the Containment Coolers using a method different than that used by Callaway Engineering personnel. The Resident Inspectors' calculations resulted in identifying a data point at which the cooling capacity of the Train A Containment Coolers was not within limits. The inside of the cooling coils of the A Containment Cooler was cleaned during the Refuel 14 outage between September 21, 2005 and October 12, 2005. Because the as-found differential pressure for the A Containment Cooler was not required to be measured and recorded by procedure or work document instructions prior to cleaning the cooling coils, Callaway Plant could not perform the calculations required to prove the past operability of the Train A Containment Coolers for the time period in question.
4832006008 | Callaway | 08/30/2006 | 10/30/2006 | ML06311058 | <strong>COMS Inoperablility, RHR Suction Relief Valve Failure</strong><br /><i>Abstract:&nbsp;</i>Residual Heat Removal (RHR) suction relief valves EJ8708A and EJ8708B removed by Callaway Maintenance during Refueling Outage 14 (Fall 2005) were tested on August 30, 2006. Test results indicated EJ8708B relieved approximately 146 psig high; EJ8708A relieved correctly. The disc assembly pins of both valves were found broken when the valves were disassembled and inspected. An immediate action taken was to consider valve EJ8708B inoperable and EJ8708A operable but degraded from Refuel 12 to Refuel 14, and determine the overall effect as it relates to system operability. These mechanical failures were not known when the valves were in service from Refuel 12 to Refuel 14, and as a result, the Required Actions for Technical Specification 3.4.12 were not entered. The direct cause of pin failure is compression of the pre-load spring and shear of the disc assembly pin. The initiating event was a Safety Injection (SI), which was combined with a Power Operated Relief Valve (PORV) actuation on February 11, 2004. The inoperability of the RHR suction relief valves was coincident with the PORVs being inoperable for Cold Overpressure Mitigating System (COMS). The safety significance of this event is Technical Specification Required Actions were not entered as required, and COMS was out of service from the time of failure until the valves were replaced in Refuel 14.
4832006009 | Callaway | 11/30/2006 | 01/26/2007 | ML07031031 | <strong>Inadequate Application of Tech Specs Related to Main Steam Isolation Valves and Actuator Trains</strong><br /><i>Abstract:&nbsp;</i>Prior to June 2006 Callaway Plant Technical Specification 3.7.2 did not explicitly address Main Steam Isolation Valve actuator trains. Inoperability of actuator trains was addressed through a Technical Specification Interpretation, which specified that due to the redundant actuator design, inoperability of a single actuator train did not render the associated isolation valve inoperable. The interpretation was eventually incorporated into Chapter 16 of the Final Safety Analysis Report and applied to the failure of a single actuator train on December 29, 2004. The NRC questioned the use of this provision and took the position that Main Steam Isolation Valve Technical Specification 3.7.2 requirements should have been imposed. The issue was identified as an Unresolved Item for which NRC Office of Nuclear Reactor Regulation involvement was required. Prior to NRC resolution, Callaway Plant determined that Technical Specification 3.7.2 was inadequate. In May 2005, a license amendment request was submitted to explicitly include requirements for the actuator trains under Technical Specification 3.7.2. The NRC approved and issued the amendment request in June 2006. Following issuance of the license amendment, the ongoing NRC evaluation reached resolution in October 2006. The NRC concluded that the requirements of Technical Specification 3.7.2 were inadequately applied prior to the license amendment and should have been imposed for past instances of actuator train inoperability.
4982006001 | South Texas 1 | 03/25/2006 | 05/25/2006 | ML06153028 | <strong>Standby Diesel Generator Failed Surveillance Test Demonstrating Performance at 110% Load</strong><br /><i>Abstract:&nbsp;</i>On March 25, 2006, Standby Diesel Generator (SBDG) 13 was required by Technical Specifications to have a surveillance test demonstrating performance at 110% load. The 110% level could not be reached, and SBDG 13 was declared inoperable. On March 27, 2006, the condition was corrected by adjusting the fuel linkage to provide the required fuel to achieve 110% load. SBDG 13 was declared Operable at 0304 on March 28, 2006. The linkage had previously been adjusted during a five-year overhaul in May 2005. Post-maintenance testing performed following this adjustment did not include verification that the diesel generator was capable of achieving 110% of rated load. SBDG 13 is considered to have been inoperable from May 28, 2005, until the diesel generator was declared operable on March 28, 2006. Because SBDG 13 was inoperable during this time without entering the appropriate Technical Specification action statements, this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The root cause is insufficient barriers in place to ensure the SBDG is operable prior to returning it to service. The 5-year SBDG preventive maintenance test procedure did not require verification to ensure the linkage as-left position was correct. The work package did not specify that a 110% load test run be performed following linkage adjustment. For corrective action, requirements for verification have been added to maintenance procedures to ensure the fuel linkage is correctly positioned. Maintenance procedures involving diesel generator fuel linkage work will include requirements for load testing to 110% of capacity. Only SBDG 13 was affected. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
4982006002 | South Texas 1 | 03/31/2006 | 05/30/2006 | ML06157038 | <strong>Simultaneous Inoperability of Two Essential Chilled Water Trains</strong><br /><i>Abstract:&nbsp;</i>At 12:07 hours on March 31, 2006, Unit 1 entered Technical Specification 3.0.3 due to simultaneous Train A and Train C essential chiller inoperability and remained in the action longer than one hour. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Troubleshooting the Essential Chiller 12C circuit breaker revealed that auxiliary contact 5-7 on relay 69X had not closed. High resistance on contact 5-7 and contamination on both the stationary and movable contacts were found. The most likely cause of Essential Chiller 12A failing to start was an intermittent problem with one of the three electrical components that was replaced: the low chilled water temperature switch, the low chilled water flow switch, or the 14TR relay. Corrective actions included replacing the Chiller 12A low chilled water temperature switch, low chilled waterflow switch, and 14TR relay in the Chiller 12A control panel, and replacing relay 69X in switchgear E1C/9. STP will clean, inspect, or replace AR ultra-high-speed relays for the component cooling water pumps, containment spray pumps, centrifugal charging pumps, auxiliary feedwater pumps, essential cooling water pumps, and essential chillers in the Class 1E 4.16 kV switchgear in Units 1 and 2 during the next scheduled maintenance. This event did not have an adverse effect on the health and safety of the public.
4982006003 | South Texas 1 | 09/11/2006 | 11/09/2006 | ML06325032 | <strong>Control Room Envelope HVAC Makeup Fan 11B Failure to Start</strong><br /><i>Abstract:&nbsp;</i>On 9/11/2006, at 1210 hours, with Unit 1 in coast down operations, Control Room Envelope Makeup Fan 11B was manually actuated from the Control Room in support of maintenance activities and failed to start. The failure was due to the magnetic circuit breaker (short circuit trip protection) for Fan 11B tripping on instantaneous (starting) over current. As a result, Control Room Envelope HVAC Train B was declared inoperable. Investigation determined that during implementation of the Motor Control Center Upgrade Modification in 2000, the instantaneous trip setting of the magnetic breaker for the fan load was set based on code letter "G" motors rather than the required "J" setting. As a result, the magnetic breaker setting was set too low causing a vulnerability to spurious tripping during certain plant conditions. The locked rotor current setting was adjusted for the 11B Control Room Envelope Makeup Fan breaker, and the 11B Fan was declared operable on 09/12/2006 at 0240 hours. Walkdowns were performed on all Unit 1 and Unit 2 safety related 480 Volt motors affected by the Motor Control Center Upgrade Modification to verify the correct magnetic trip settings for the breakers. No other motors were found with incorrect magnetic breaker settings. Probabilistic risk assessment determined that there was no adverse impact to Core Damage Frequency or to the Large Early Release Frequency as a result of this event. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
4982006004 | South Texas 1 | 09/25/2006 | 11/27/2006 | ML06325034 | <strong>Multiple Main Steam Safety Valves Found Outside Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>While testing the Unit 1 Main Steam Safety Valves (MSSVs) on 9/25/06 just prior to 1RE13, three valves failed the as found acceptance test. If a valve fails the lift test, then additional valves in the same unit are required to be tested. On 9/25/06 two of the six valves being tested in Unit 1 were greater than 3% above the setpoint on the initial lift (MSSVs 7440A and 7440B). Four additional valves were tested in Unit 1 per scope expansion guidance. All additional expanded scope valves passed testing. Two additional valves were tested to determine generic cause and one of these additional cause determination tested valves was high outside of the 3% band (7430C) and another valve came within 1.5 psi of being 3% high (7430). All of the valves tested were adjusted so that they lifted within +/- 1% of their setpoints. It was determined that the primary cause of the MSSVs lifting high was due to the bonding of the oxide layers that grew on the nozzle seat and the disc after refurbishment. Corrective Actions include performing in service conditioning lifts on all refurbished valves. Three Unit 1 MSSVs that lift outside of the range specified in Technical Specification 3.7.1.1 is considered to be a multiple test failure and is reportable under 10CFR50.73(a)(2)(i)(B).
4982006005 | South Texas 1 | 11/06/2006 | 12/28/2006 | ML07016021 | <strong>TS 3.3.1 Action 2 Requirements Not Performed</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2006, at 1718 hours, Unit 1 was operating at 78% power when it was discovered that the Technical Specification Actions with one Power Range Nuclear Instrument out of service had not been performed as required. Technical Specification 3.3.1 Action 2 requires either (1) thermal power to be restricted to less than 75% and the Power Range Neutron Flux Trip setpoints be reduced to less than or equal to 85% power within 4 hours or (2) monitor Quadrant Power Tilt Ratio (QPTR) once per 12 hours per Specification 4.2.4.2. Neither of these actions was performed and the 12 hour requirement elapsed before the condition was discovered. The cause of the missed TS Action requirements was inconsistent adherence to procedural requirements regarding the logging and tracking of TS requirements. Subsequent to the discovery of the missed TS Action, Power Range Nuclear Instrument NI-43 was returned to operable status, and a QPTR surveillance was performed with satisfactory results. This condition did not have an adverse affect on the health and safety of the public.
4982006006 | South Texas 1 | 12/17/2006 | 11/08/2007 | ML07323012 | <strong>TS 3.3.3.6 Action 35 Allowed Outage Time Exceeded</strong><br /><i>Abstract:&nbsp;</i>At 0945 on December 15, 2006 several loads were lost on distribution panel (DP-1202) associated with the STP Unit 1 Train D inverter following an electrical transient. The loads included a qualified display processing system (QDPS) cabinet that provides auxiliary feedwater (AFW) flow indication and control functions for the Train D turbine driven AFW train. As a result of the loss of AFW flow instrumentation, STP Unit 1 entered Technical Specification (TS) 3.3.3.6 Action 35, and TS 3.7.1.2 Action b. The allowed outage time for the AFW flow indication is 48 hours and expired at 0945 CST on December 17, 2006. The allowed outage time for the turbine-driven (TD) AFW train is 72 hours and would have expired at 0945 CST on December 18, 2006. STPNOC determined the AFW flow instrumentation channel could not be restored prior to the expiration of the allowed outage times and requested enforcement discretion. NRC granted the enforcement discretion at 0839 on December 17, 2006, effective until 2145 hours on December 18, 2006. STPNOC found that two of three Electrically Erasable, Programmable, Read-Only Memory (EEPROM) chips located on a QDPS central processing unit (CPU) circuit board had been damaged due to the electrical transient. STPNOC replaced the damaged EEPROMs and affected downstream circuit boards. QDPS Cabinet D2 and the functions above were declared operable at 2155 hours on December 17, 2006. The electrical transient was caused by a capacitor failure in inverter 1202. The capacitor failure was due to a manufacturing defect. The affected capacitor bank was replaced on December 20, 2006.
4992006001 | South Texas 2 | 12/04/2006 | 01/31/2007 | ML07037032 | <strong>Safety Injection Train Inoperable Longer than Allowed under Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2006, Unit 2 High Head Safety Injection (HHSI) pump 2A of the Emergency Core Cooling System (ECCS) was declared inoperable at 0100 due to maintenance requirements; this also made the associated low head safety injection and containment spray pumps inoperable. During disassembly, internal damage to the pump occurred, requiring repairs before the HHSI pump could be returned to operability. The allowed outage time expired at 0100 on December 4, 2006. Because the repairs were expected to exceed that time, Enforcement Discretion was approved by the NRC on December 3, 2006, allowing operation for an additional eight days. Technical Specifications 3.5.2 and 3.6.2.1 require that if one train of ECCS and containment spray is inoperable, it is to be restored to operability within seven days or the unit is to be in at least hot standby within six hours. The HHS pump and the associated components were declared operable at 1119 on December 7, 2006. Because these components were inoperable longer than allowed under the Technical Specifications without entering the appropriate action statements, this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The root cause is that the unexpected condition was not sufficiently assessed and the potential hazards to the affected components were not identified prior to proceeding to use force in removing the pump half-coupling. For corrective action, affected personnel will be retrained on the Conduct of Maintenance and expectations on tool use. The Rotating Equipment Certifications of the craftsmen involved have been deactivated, pending remedial training and recertification. In addition, a contributing factor of a pre-existing condition involving assembly of the pump rotating element was identified. This aspect is currently under review. Only Train A of Unit 2 was affected. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
5282006001 | Palo Verde 1 | 03/20/2006 | 05/18/2006 | ML06145032 | <strong>Containment Spray Inoperable in Mode 4 with RCS Pressure Greater than 385 psia</strong><br /><i>Abstract:&nbsp;</i>All times in this report are approximate and Mountain Standard Time unless noted otherwise. On March 20, 2006 at 1530, while in the process of a reactor startup, Unit 1 was in Mode 4 (Hot Shutdown) with pressurizer pressure greater than 385 pounds per square inch absolute (psia) when Control Room personnel realized that "B" train Containment Spray (CS) had not been Operable on two occasions when it was required to be Operable. Technical Specification (TS) 3.6.6 requires both trains of CS to be Operable in Mode 4 when pressurizer pressure is greater than 385 psia. On March 20, 2006 at 0445 and at 0905 Unit 1 entered Mode 4 with pressurizer pressure greater than 385 psia with only the "A" train of CS Operable in violation of TS 3.0.4. At 1915 on March 20, Control Room personnel initiated cool down of the Reactor Coolant System (RCS)to return to Mode 4 operation with pressurizer pressure less than 385 psia. At 2030, while still in the process of cooling down, "B" train CS was returned to Operable status and Control Room personnel exited Limiting Condition for Operation 3.6.6. The cause of the event was human error. In the past three years, Palo Verde reported four violations of TS 3.0.4 on separate Licensee Event Reports.
5282006002 | Palo Verde 1 | 03/21/2006 | 05/18/2006 | ML06145032 | <strong>Mode 3 Entry without the Required Number of Pressurizer Heater Groups Operable</strong><br /><i>Abstract:&nbsp;</i>All times in this report are approximate and Mountain Standard Time unless noted otherwise. On March 22, 2006 at 0645, while in the process of a reactor startup, Unit 1 was in Mode 3 (Hot Standby) when Control Room personnel discovered that circuit breaker PGBL32E3, which supplies power to the"B" class pressurizer (Pzr) heaters, was in a tripped open condition. This condition would have prevented operation of the "B" class Pzr heaters. Unit 1 had entered Mode 3 the previous day. Technical Specification (TS) 3.4.9 requires two groups of Pzr heaters be Operable in Mode 3. On March 21, at 0117, Unit 1 entered Mode 3 with only one group of Pzr heaters Operable in violation of TS 3.0.4. On March 22, at 0645 Control Room personnel entered TS Limiting Condition for Operation 3.4.9. Troubleshooting revealed a ground on Pzr backup heater A05. A temporary modification was installed to isolate backup heater A05 and connect in its place backup heater B04. Following a successful retest, the"B" class heaters were returned to Operable status. The cause of the event was human error. In the past three years, Palo Verde reported four violations of TS 3.0.4 on separate Licensee Event Reports.
5282006003 | Palo Verde 1 | 05/30/2006 | 07/25/2006 | ML06214044 | <strong>Emergency Diesel Generator Actuation on Loss of Power to A Train 4.16KV Bus</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2006, at approximately 08:13 Mountain Standard Time (MST) Unit 1 was defueled, when a loss of power (LOP) to the A train class 4.16 kilo-volt (KV) bus (PBAS03) occurred. At the time of the LOP, Emergency Diesel Generator (EDG) 'A' had been manually removed from the PBAS03 bus following a maintenance surveillance test. The PBAS03 bus was powered from its normal offsite power source when an invalid load shed signal was received from the 'A' train load sequencer which caused the normal offsite power supply breaker to open and strip all loads off the bus. A valid LOP signal was received and EDG 'A' received a valid emergency run signal. EDG 'A' returned to rated frequency and voltage; however, its output breaker did not close due to the 'A' train load sequencer which had stalled, thus, preventing the needed closure signal to the EDG 'A' output breaker. PBAS03 was eventually energized from its normal offsite power supply. The investigation identified electrical noise sensed in the load sequencer as the most likely cause of the event. Corrective actions included the installation of a modification and refurbishing the load sequencer cabinet which reduced the electrical interference. In the past three years, there were no similar events reported for a LOP to a safety bus caused from a load sequencer problem.
5282006004 | Palo Verde 1 | 09/18/2006 | 06/30/2008 | ML08198012 | <strong>TS Required Reactor Shutdown on Failure of the Class Pressurizer Heaters to be Able to Meet their Mission Time</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2006 at 10:35 PM, station personnel entered TS Action statements 3.0.3 and 3.4.9, Condition B. Operations personnel declared the Pressurizer (Pzr) Class heaters INOPERABLE when Engineering personnel, with input from the manufacturer (Watlow), informed the control room staff that reasonable assurance of OPERABILITY no longer existed. On September 19, 2006 at 1:05 AM Palo Verde Unit 1 was in Mode 1 (Power Operations), operating at approximately 100 percent power, when Control Room personnel commenced a reactor shutdown required by Technical Specification 3.0.3. At 3:07 AM, Operations personnel manually tripped the reactor. Mode 4 was entered at 5:07PM. The cause of the Watlow heater failures was high sheath tensile stress introduced during the fabrication process. Palo Verde has replaced or removed from service the affected Watlow heaters, and has installed heaters from a different manufacturer (Doosan). Watlow heaters installed in the other two units at Palo Verde have not experienced the same failure rate, indicating the failure mechanism was unique to those heaters installed in Unit 1. In the past three years, Palo Verde experienced one similar event where the failure of a Watlow heater resulted in Unit 1 entering a mode of operation without the required number of operable heaters. That event was the first identified failure of this type of heater, which ultimately resulted in this event.
5282006005 | Palo Verde 1 | 10/05/2006 | 08/08/2008 | ML08231057 | <strong>Technical Specification Prohibited Condition due to Check Valve Not Seated</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2006, with Unit 1 in Mode 3, Hot Standby, a safety injection check valve failed to seat properly as indicated by surveillance testing. Safety injection check valve 1PSIEV134 (SI-134) was not in its fully seated position at the time of entry into a condition that required the valve to be OPERABLE. The cause of the valve failure was frictional forces in excess of the gravitational forces acting on the disc assembly which prevented the valve disc from fully seating and sealing on its own. Contributing to this cause was the fact that SI-134 was not assembled by the supplying vendor in accordance with their assembly drawings. SI-134 was disassembled and inspected, a new bonnet/disc assembly was installed in the valve and the valve passed required testing. Preventive maintenance programs have been revised to prevent recurrence. APS reported one similar check valve event within the past three years. Corrective actions for that event were scheduled, but had not been implemented for the valve identified in this event prior to occurrence of this failure.
5282006006 | Palo Verde 1 | 10/21/2006 | 12/18/2006 | ML06361034 | <strong>Reactor Trip due to Core Protection Calculator Generated Low Departure from Nuclear Boiling Ratio (DNBR) Trip Signal</strong><br /><i>Abstract:&nbsp;</i>All times listed in this event report are approximate and Mountain Standard Time (MST) unless otherwise indicated. At 15:49 hours on October 21, 2006, the PVNGS Unit 1 Reactor automatically tripped from 100% power due to Core Protection Calculator (CPC) generated Low DNBR trips. Prior to the reactor trip, Control Element Assembly (CEA) #29 position indication on Reed Switch Position Transmitter (RSPT) 'A' was observed fluctuating approximately between 142 - 150 inches withdrawn, resulting in numerous Control Element Assembly Calculator (CEAC) #1 deviation alarms from 14:40 hours until the time of trip. Following Operations Computer Systems (OCS) confirmation of the fluctuating field input signal for CEA #29, the Control Room staff was preparing to remove CEAC #1 from service. The automatic reactor trip occurred before the CEAC #1 inoperable (INOP) codes were placed into the CPCs. The Direct Cause of this event was fluctuations in the CEA #29 position indication signal sent from RSPT "A" to CEAC #1 due to excessive circuit resistance at a cable connector. In the past three years, Palo Verde experienced one similar trip event due to a fluctuating CEA position input signal.
5282006007 | Palo Verde 1, Palo Verde 3 | 10/26/2006 | 12/18/2006 | ML06361034 | <strong>Emergency Diesel Generator Actuation on Loss of Power to B Train 4.16KV Buses in Units 1 and 3</strong><br /><i>Abstract:&nbsp;</i>All times listed in this event report are approximate and Mountain Standard Time (MST) unless otherwise indicated. On October 26, 2006, at approximately 23:53 MST, a valid actuation of the Palo Verde Nuclear Generating Station Unit 1 Train B Emergency Diesel Generator (EDG) and Unit 3 Train B EDG occurred as a result of under-voltage on their respective safety buses. Both EDGs started and loaded as designed. No Emergency Plan declaration was made and none was required. The loss of power to the two safety buses was the result of an apparent protective relay actuation of Startup Transformer X01 output breakers to Unit 1 NAN-S06 and Unit 3 NAN-S06 electrical distribution busses. Unit 1 NAN-S06 bus was being supplied by its Alternate breaker (1 ENANS06F) and Unit 3 NAN-S06 was being supplied by its Normal breaker (3ENANS06C). Prior to the event, maintenance personnel were restoring potential transformer (PT) fuses at Unit 1 breaker 1ENANS06, Cubicle G. Current belief is that the two simultaneous LOP conditions occurred when the cubicle door was closed on 1ENANS06, Cubicle G. This condition apparently caused the output breakers of Startup Transformer X01 to open. There was no electrical fault or damage to any electrical components. In the past three years, Palo Verde reported Emergency Diesel Generator Actuation on Loss of Power but none associated with the same root cause.
5292006001 | Palo Verde 2 | 04/10/2006 | 04/06/2007 | ML07107029 | <strong>TS Required Reactor Shutdown on failure to complete repairs on an AFW valve within the 7 day completion time.</strong><br /><i>Abstract:&nbsp;</i>All times listed in this event report are approximate and Mountain Standard Time (MST) unless otherwise indicated. On April 3, 2006, at 10:41 MST, during the performance of the A train Auxiliary Feed Water (AFW) turbine driven pump "In-service" surveillance test, Unit 2 obtained inconsistent position indications for a steam admission valve (SG-138A). All plant indications/parameters indicated the valve was closed with the exception of its power supply breaker. The breakers red light indicated open, however, the turbine driven pump was not rolling and all other indications showed the valve did close as it was expected to. Maintenance activities included: coil and fuse replacement, reed switch replacement, valve internals replacement, and then replacement of the entire valve. During the retest, valve position indication was again lost. Since the additional repairs could not be made within the TS 7 day allowed completion time permitted for restoration, a Reactor Shutdown was commenced as required. On April 10, 2006 at 12:33 MST Palo Verde Unit 2 was in Mode 1 (Power Operations), operating at approximately 91 percent power, when Control Room personnel commenced a reactor shutdown required by Technical Specification 3.7.5 Condition C. At 14:38 MST Operations personnel manually tripped the reactor from approximately 23 per cent power and entered Mode 4 at 20:56 MST. In the past three years, Palo Verde reported reactor shutdowns required by Technical Specifications but none associated with the same root cause.
5292006002 | Palo Verde 2 | 07/16/2006 | 09/14/2006 | ML06271040 | <strong>Two Independent Trains of Auxiliary Feedwater Inoperable due to Single Cause</strong><br /><i>Abstract:&nbsp;</i>On July 16, 2006 at approximately 14:52 Mountain Standard Time (MST) Unit 2 was operating at 100 percent power, Mode 1 (power operations), when an Area Operator (AO) notified the control room that door C-A-06 was found open with no compensatory measures established. Door C-A-06 is a watertight fire door that functions as the train separation barrier between Auxiliary Feedwater (AF) pump rooms A and B. When door C-A-06 is open with the unit operating in Mode 1, compensatory action must be taken in order to maintain both trains of AF operable. The AO who discovered door C-A-06 open and unattended, closed the door immediately. Based on a review of security computer transaction logs, control room personnel determined that door C-A-06 was open with no compensatory actions in place for approximately 4 hours and 20 minutes. As such, AF trains A and B were considered inoperable between 10:32 and 14:52 (MST). Based on further review and personnel interviews, an investigation concluded that a Fire Department Emergency Services Officer (ESO) had failed to close C-A-06 after leaving the AF pump room. In the past three years, there were two similar events reported (LER 50-529/2005-003-00, and 50-530-2006-001-00).
5292006003 | Palo Verde 2 | 07/26/2006 | 10/31/2007 | ML07318046 | <strong>Unit 2 Variable Overpower Reactor Trip During Main Turbine Control Valve Restoration</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2006, at 07:33 Mountain Standard Time (MST), Unit 2 was in Operating Mode 1, Power Operation, at approximately 90 percent rated thermal power with main turbine control valve #2 (CV#2) closed to complete maintenance on its position transducer and linkage arm. A jumper installed in the test button circuit kept CV#2 closed during the maintenance. After removal of the jumper and CV#2 from "test", the valve was allowed to re-open resulting in a series of control system responses causing reactor power to increase rapidly. The reactor tripped on core protection calculator high variable overpower at approximately 90 percent power, approximately 18 seconds after removing CV#2 from "test". No other safety system actuations occurred and none were required. The root cause of the event was an inadequate assessment of the risk associated with performing the valve maintenance on-line, resulting in implementation of an inadequate action plan for corrective maintenance which did not accommodate for the build up of condensate in the isolated main turbine piping associated with CV#2. This occurred due to a belief that the maintenance evolution was equivalent to control valve testing. All monthly CV testing in Unit 2 was suspended until the root cause of the plant transient was determined. A standing order was issued to prohibit performance of CV maintenance on-line, and remained in effect until adequate procedural guidance was provided for removal of a CV from service for on-line maintenance. A similar trip event caused by a main turbine upset occurred on June 7, 2004, in Unit 3, when a main turbine electro-hydraulic system malfunction caused main turbine control and intercept valves to close, resulting in a reactor trip.
5292006004 | Palo Verde 2 | 07/17/2006 | 09/28/2006 | ML06278019 | <strong>Unit 2 Feedwater Isolation Valve Inoperability Results in Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2006, station personnel discovered that the hydraulic accumulator for Feedwater Isolation Valve #174 (FWIV #174) would not recharge because a failed four-way valve became lodged in the center blocked position. Further evaluation concluded that the condition would have prevented fast closure of the FWIV upon receipt of a main steam isolation signal and had existed since approximately 21:09 Mountain Standard Time (MST) on July 13, 2006. This exceeded the technical specification required action time. The four way valve was replaced and the FWIV was declared operable on July 28, 2006. The preliminary cause of exceeding the technical specification action time was that the failed condition of the four-way valve was not known to operators until the accumulator failed to recharge on July 27, 2006. Corrective action included revision of the depressurizing procedure to verify the respective four-way valve returns to its required position and is not lodged in the blocked position. A non-reportable failure of FWIV #174 occurred in Unit 2 on May 13, 2003 when the four-way valve became lodged in the standby position which did not adversely impact the FWIV operability.
5292006005 | Palo Verde 2 | 10/07/2006 | 11/21/2006 | ML06345013 | <strong>Reactor Head Vent Axial Indications Caused by Degraded Alloy 600 Component</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2006 engineering personnel performing preplanned in-service examinations of the reactor vessel head vent penetration discovered two axial indications in the reactor vessel head vent penetration. The indications were located on the inner diameter surface of the pipe adjacent to the J-weld to the head. The indications were conservatively identified as abnormal degradation of the reactor coolant system pressure boundary and necessitated taking corrective action to restore the barrier's capability. The indications were removed prior to the unit's return to power operation. These indications are similar to indications found during the previous refueling outage in April 2005. Similar previous conditions were reported in LER 50/529-2005-001-00, LER 50/528-2004-001-00, LER 50/530-2004-001-00 and LER 50/530-2003-002-00.
5292006006 | Palo Verde 2 | 12/22/2006 | 03/22/2007 | ML07095034 | <strong>Technical Specification 3.7.7 Violation - Inoperable Essential Cooling Water Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2006, the Palo Verde Nuclear Generating Station (PVNGS) received a Final Significance Determination letter from the Nuclear Regulatory Commission (NRC) for Apparent Violations received during an NRC Heat Exchanger Performance inspection. The NRC concluded in the letter that the Unit 2 Essential Cooling Water, Train B heat exchanger was Inoperable and a Technical Specification (TS) 3.7.7 violation for a period of 78 days occurred, ending on September 27, 2003 when Unit 2 was shutdown for a refueling outage (U2R11). The subject heat exchanger was restored to Operable during the refueling outage. Essential Cooling Water, Train A heat exchanger was functional for the 78 day period that EW 2B was considered inoperable. As a result of other heat exchanger problems, in May 2006, Arizona Public Service (APS) initiated an investigation of the Essential Cooling Water heat exchangers and the chemistry controls for the Spray Pond System. The APS investigation identified system problems with chemistry control, equipment maintenance and organizational weakness which allowed the problems to develop and remain uncorrected for an extended period. A number of corrective actions were implement or are being implement which include restoring effective chemistry controls of the system, procedure changes, personnel training, and equipment modification. In the past three years, there were no similar events reported.
5302006001 | Palo Verde 3 | 02/17/2006 | 04/18/2006 | ML06115035 | <strong>Two Independent Trains of Auxiliary Feedwater Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2006 at approximately 13:15 Mountain Standard Time (MST) Unit 3 was operating at 100 percent power, model (power operations), when a Security Officer notified the control room that door C-A06 was found open with no compensatory measures established. Door C-A06 is a watertight fire door that functions as the train separation barrier between Auxiliary Feedwater (AFW) pump room A and B. When door C-A06 is open with the unit operating in mode 1, compensatory action must be taken in order to maintain both trains of AFW operable. The Security Officer who discovered door C-A06 open and unattended, closed the door immediately. Based on a review of security computer transaction logs, control room personnel determined that door C-A06 was open with no compensatory actions in place for approximately 4 minutes. As such, AFW trains A and B were considered inoperable between 13:03 and 13:07. Based on further review and personnel interviews, an investigation concluded that a Maintenance worker had failed to close C-A06 after leaving the AFW pump room area. In the past three years, there was one similar event reported (LER 50-529/2005-003-00).
5302006002 | Palo Verde 3 | 03/05/2006 | 04/28/2006 | ML06130008 | <strong>Automatic Reactor Protection System Actuation due to an Invalid Control Element Assembly Calculator Penalty Factor</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2006 at 07:10 Mountain Standard Time (MST) Palo Verde Unit 3 was in Mode 1 (Power Operations), operating at approximately 100 percent power, when an automatic reactor trip occurred on a low Departure from Nucleate Boiling Ratio (DNBR) input. The four Core Protection Calculators (CPC) generated a reactor trip on low DNBR due to an invalid Control Element Assembly Calculator (CEAC) input. CEAC number 1 sensed positional data for Control Element Assembly (CEA) 60 that exceeded the allowed deviation and as a result generated a high penalty factor which was transmitted to all four CPC channels. This high penalty factor resulted in a CPC DNBR trip output, as per design. The reactor was stabilized in Mode 3 (HOT STANDBY), and the Shift Manager classified the event as an uncomplicated reactor trip. No engineered safety feature actuations occurred during the event and none were required. The cause of the reactor trip was an electronic component failure on a circuit board that caused an invalid (CEA) position deviation to CEAC number 1. The circuit board was replaced and the Unit was restarted. In the past three years, Palo Verde reported Reactor Protection System (RPS) actuations, but none associated with the same root cause.
5302006003 | Palo Verde 3 | 04/02/2006 | 05/26/2006 | ML06153027 | <strong>Loss of Power to One Class Bus During Testing due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2006, Unit 3 was in Mode 5, Cold Shutdown, when a loss of electrical power to the B train class 4.16 KV bus occurred. At the time of the event engineering and maintenance personnel were performing integrated safeguards testing when the B train emergency diesel generator (EDG) tripped causing a loss of power to the class bus. Equipment operated as expected, the EDG was reset and automatically actuated to reenergize the bus. Testing was then successfully completed. The event is under investigation. Initial investigation results have identified that human error was the cause of the event. Corrective actions taken included verification of no damage to the EDG or the class bus. Action to preclude recurrence included implementation of a formal prejob briefing for engineering personnel and peer checking by engineering during the testing. There has been no similar event reported to the NRC by Arizona Public Service in the last three years.
5302006004 | Palo Verde 3 | 05/06/2006 | 10/06/2006 | ML06292046 | <strong>Emergency Diesel Generator Actuation on Loss of Power to A Train 4.16KV Bus</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2006, at approximately 16:35 Mountain Standard Time (MST) Unit 3 was in Mode 5, Cold Shutdown, when a loss of power (LOP) to the A train class 4.16 kilo-volt (KV) bus (PBAS03) occurred as a result of an undervoltage condition. Emergency Diesel Generator (EDG) A started and loaded as expected to re-energize PBAS03. The loss of power to PBAS03 occurred during Gas Turbine Generator (GTG) testing. GTG number 1 was supplying PBAS03 at a lower than normal voltage when the normal supply breaker PBASO3L opened due to the undervoltage condition which de-energized PBAS03. The EDG started and all required related safety equipment started as expected. The investigation identified the cause of the event was not having the GTG load adjusted properly to accept the full load from offsite power prior to opening the normal supply breaker for PBAS03. As a corrective action, steps in the test procedure were resequenced and the test was re-performed. After resequencing the test steps the GTG test was successful. In the past three years, there were no similar events reported for a LOP to a safety bus caused from an insufficient procedure during GTG testing.
5302006005 | Palo Verde 3 | 07/01/2006 | 03/20/2007 | ML07089030 | <strong>Manual Reactor Trip due to Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2006 at approximately 19:28 Mountain Standard Time (MST) Unit 3 was in Mode 1, Power Operation, at approximately 100 percent rated thermal power when a sight glass on a condensate demineralizer ruptured. This resulted in a low pressure condition at the suctions for both main feedwater pumps. One of the pumps tripped causing a reactor power cutback and subsequent decrease in reactor power to approximately 55 percent rated thermal power. Suction pressure to the other main feedwater pump remained low and a control room operator manually tripped the reactor. No engineered safety feature system actuations occurred and none were required. The sight glass rupture occurred because of undetected defects to the glass. The root cause was alternatives to single pane borosilicate glass were not recognized as being needed. The sight glass was replaced. The station will install condensate demineralizer sight glasses that are more resistant to catastrophic failiure. No similar event has been reported in the last three years.
5302006006 | Palo Verde 3, Palo Verde 1, Palo Verde 2 | 09/05/2006 | 03/09/2007 | ML07082008 | <strong>Failure of Emergency Diesel Generator to Attain Required Voltage due to a Failed K1 Relay Contactor</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2006 at 01:18 Mountain Standard Time (MST) Unit 3 was in Mode 1, Power Operation, at approximately 100 percent rated thermal power when the A train emergency diesel generator (EDG) failed to attain its required voltage during post maintenance surveillance testing. This occurred because the field shorting contactor K1 did not drop out as required following an engine start, preventing field excitation. Root cause testing determined that the condition existed since 14:19 MST on September 4, 2006 when the EGD was stopped following satisfactory completion of surveillance testing. Unit 3 was in a condition prohibited by Technical Specifications for an inoperable EDG since September 5, 20:19 MST. The direct cause of the EDG failure was insufficient auxiliary contact compression which caused inconsistent electrical operation of the K1 Contractor. The failure was also caused by inadequate troubleshooting and problem solving after the K1 Contractor exhibited inconsistent electrical operation when it was installed on July 25, 2006. The insufficient auxiliary contact compression was corrected by straightening a metal actuator arm for the affected contact. Formal troubleshooting and problem solving processes were developed to address the process inadequacies. No similar events were reported to the NRC by Arizona Public Service in the last three years.
5302006007 | Palo Verde 3 | 10/19/2006 | 12/13/2006 | ML06356039 | <strong>Manual Reactor Trip due to Degrading Condenser Vacuum and Condensate Flow</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2006 at about 1147 Mountain Standard Time, Unit 3 was operating in Mode 1, Power Operation, at approximately 100% power when control room personnel initiated a manual reactor trip in response to lowering condenser hotwell level which had caused two of the three operating condensate pumps to trip coincident with degrading condenser vacuum. The cause of the hotwell level and condenser vacuum reduction was determined to be a failed open air operated valve on the condensate demineralizer drain header which created an opening from condenser shell "C" to atmosphere. The root cause of the event was determined to be that the challenge to the unit posed by degraded condenser vacuum created by an open SCN-UV-232 valve concurrent with condensate demineralizer service vessel draining evolutions was not addressed through single point vulnerability reviews. Procedures have been changed to require an in-line manual valve to be closed except during specific demineralizer rinsing operation.