## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0032008001 | Indian Point 1, Indian Point 2, Indian Point 3 | 05/27/2008 | 07/21/2008 | ML08210044 | <strong>Attempted Introduction of Contraband into the Plant Protected Area due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2008, a contractor with unescorted access attempted to enter the Indian Point Energy Center site protected area (PA) at the PA access control point with a hand gun in a backpack which was discovered during the normal search process. The individual was denied PA access and held for questioning. Interviews with the individual by plant security officers determined there was no malevolent intent or attempt to enter the PA with a weapon. The individual was on a scheduled work assignment for Unit 1 and was previously approved for access. The New York State Police were notified and the individual was taken into custody and removed from the site. There was no impact on any plant equipment or facilities.
2192008001 | Oyster Creek | 11/28/2008 | 01/21/2009 | ML09026008 | <strong>Automatic Reactor Shutdown Caused by Main Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2008 at 2101 while operating at 98% power, a generator trip occurred due to a transformer differential relay actuation. The cause of the differential relay actuation is attributed to an electrical fault internal to the M1A Main Power Transformer. This transient led to a reactor automatic shutdown due to a load reject SCRAM. All safety systems operated as expected following the SCRAM. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to the automatic reactor protection system actuation.
2202008001 | Nine Mile Point 1 | 05/13/2008 | 07/07/2008 | ML08190026 | <strong>Loss of Offsite Power due to an Equipment Malfunction</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2008, at 0806 hours, with Nine Mile Point Unit 1 (NMP1) operating at 100% steady state reactor power and one of two 115 kV offsite power lines (Line 1) out of service for planned maintenance, a loss of the second 115 kV offsite power line (Line 4) occurred. Line 4 is a shared line with the James A. Fitzpatrick Nuclear Power Plant. As a result of the loss of Line 4, both emergency diesel generators auto-started and commenced carrying emergency loads. The Loss of Offsite Power (LOOP) also resulted in tripping of one of five Reactor Recirculation pumps and tripping of the operating Spent Fuel Pool (SFP) cooling pump, as designed. Operators entered applicable Special Operating Procedures (SOPs) and took appropriate corrective actions. At 0825 hours, an Unusual Event (UE) was declared and the required notifications were made. The cause for the loss of Line 4 was external to Nine Mile Point (NMP) and was determined to be a switchyard equipment malfunction at the James A. Fitzpatrick Nuclear Power Plant switchyard. On May 13, 2008, at 0843 hours, Line 1 was restored to service. The UE was terminated at 1022 hours and the required notifications were made. On May 16, 2008, at 0515 hours, Line 4 was restored to service.
2202008002 | Nine Mile Point 1 | 10/23/2008 | 12/18/2008 | ML09006087 | <strong>Manual Reactor Scram due to Loss of Reactor Pressure Control</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2008, at 2126 hours, with Nine Mile Point Unit 1 (NMP1) operating at 100% steady state reactor power, operators initiated a manual scram when it was determined that the reactor pressure regulator was not functioning properly. The loss of reactor pressure control was due to an unresponsive Electrical Pressure Regulator (EPR) that prevented transfer of control to the backup Mechanical Pressure Regulator (MPR). During the shutdown, operators entered an Emergency Operating Procedure due to low reactor water level and took appropriate corrective actions. The High Pressure Coolant Injection (HPCI) system initiated as designed to restore reactor water level to normal. After the turbine trip, all Turbine Bypass Valves failed open due to EPR binding that prevented the bypass valves from closing. The Main Steam Isolation Valves (MSIVs) were manually shut to control reactor pressure and limit reactor cooldown rate. The MSIVs were reopened subsequent to regaining pressure control on the MPR. The cause of the EPR malfunction has been determined to be debris plugging of the internal filter of the EPR servo-valve. The most likely cause of the debris in the servo-valve was due to inadequate design of the EPR filters located immediately upstream of the servo-valve. On October 26, 2008, after replacement of the EPR servo-valve and the filters, the unit was restarted and on October 27, 2008, at 0131 hours, the unit was synchronized to the grid.
2202008003 | Nine Mile Point 1 | 11/06/2008 | 01/06/2009 | ML09022003 | <strong>Power Supplies for Drywell Pressure Indication not Qualified for Required Post-Accident Operating Duration</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2008, at Nine Mile Point Unit 1 (NMP1), both channels for the dryvvell pressure monitors required by Technical Specification (TS) 3.6.11, Accident Monitoring Instrumentation, were declared inoperable. While performing design and qualification basis validation activities for Environmental Qualification, it was discovered that the power supplies for the drywell pressure monitors credited for TS compliance are not qualified for the required 100-day post-Loss of Coolant Accident (LOCA) integrated dose. As such, this item is reportable because the drywell pressure monitors were inoperable and the action required by the TS was not implemented. Per TS 3.6.11, Table 3.6.11-2, Accident Monitoring Instrumentation Action Statements, Action 4.b, a preplanned alternate method of monitoring drywell pressure was initiated upon discovery. The alternate instruments being utilized cover the drywell pressure ranges expected during design bases accidents and are the instruments currently utilized in the NMP1 Emergency Operating and Severe Accident Procedures. Design modifications to restore the drywell pressure monitoring instruments referenced in TS 3.6.11 to operable status are being evaluated.
2372008001 | Dresden 2 | 11/19/2007 | 03/17/2008 | ML08085090 | <strong>Procedure Adherence Issue Results in Violation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2008, a Dresden Nuclear Power Station Qualified Nuclear Engineer was performing mentoring with a reactor engineering trainee on control rod sequencing and discussing the reference documents used to prepare a sequence. As part of the discussion, the Dresden Nuclear Power Station Unit 2 Cycle 21 cycle-specific control rod drop accident analyses were reviewed. During this review it was identified that the control rod sequence used for the startup of Unit 2 following the refueling outage in November 2007 did not comply with the control rod drop accident analysis. A review of the Unit 2 startup conditions on November 19, 2007, identified that the unit did not comply with the requirements of Technical Specification 3.1.6, "Rod Pattern Control," for approximately 5 1/2 hours. The Root Cause of this event was human performance and was attributed to failure of Dresden Nuclear Power Station personnel to follow procedures due to a lack of understanding of the requirements for using a Level 2 procedure and the qualified individual incorrectly assumed that the "Level 2 - Reference Use" procedures did not need to be reviewed in detail during preparation of the sequence. The corrective action to prevent recurrence was to counsel and coach the individuals associated with this event.
2372008002 | Dresden 2 | 04/15/2008 | 06/16/2008 | ML08176026 | <strong>Unit 2 High Pressure Coolant Injection System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2008 at 0700 hours (CDT), with Unit 2 at approximately 99 percent power Dresden Nuclear Power Station (DNPS) personnel declared the Unit 2 High Pressure Coolant Injection (HPCI) inoperable due to the Flow Indicating Controller failing to 60 percent output demand from the expected 100 °A, while in Standby Mode of operation. Technical Specification 3.5.1.F was entered with the Isolation Condenser (IC) being verified operable. The controller failure was discovered by Control Room Operators performing hourly panel checks of panel indications. The controller output demand was observed lower than expected and the HPCI Motor Gear Unit was observed below the High Speed Stop. On April 16, 2008 a spare re-configured, calibrated controller was installed and at HPCI was declared operable 1213 hours following the successful HPCI fast start test. The Apparent Cause of this event is age degradation of the controller's internal power supply. The examination of the controller identified the failed power supply had failed due to aged electrolytic capacitors. An extent of condition review identified that there are twelve similar type controllers in use at DNPS. Actions have been taken to schedule replacement of these controllers prior to the currently scheduled 2010 replacement.
2372008003 | Dresden 2, Dresden 3 | 04/23/2008 | 06/23/2008 | ML09217014 | <strong>Control Room Emergency Ventilation Air Conditioning System Inoperable due to Excessive Vibration</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2008, at approximately 2300 hours (CDT), with both Units 2 and 3 operating at approximately 100 percent power, the Control Room Emergency Ventilation Air Conditioning System was in operation to perform a post maintenance test. During the activity, the Control Room Emergency Ventilation Air Conditioning System experienced excessive vibration. Technical Specification 3.7.5, "Control Room Emergency Ventilation Air Conditioning (AC) System," was entered. The system was restored to operable status on May 1, 2008. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident," as the Control Room Emergency Ventilation Air Conditioning System is a single train system. The apparent cause is attributed to the lack of lubrication due to the oil in the compressor being displaced by refrigerant. Liquid refrigerant accumulates in the compressor due to liquid floodback during operation and flooded starts. Following the completion of the actions associated with the equipment apparent cause analysis, Plant Engineering will evaluate system operation to determine the effectiveness of the actions taken. Based on this evaluation, if it is determined that system reliability has not been improved, further actions will be developed and implement, as appropriate.
2372008004 | Dresden 2 | 04/25/2008 | 06/24/2008 | ML08184006 | <strong>Non-Conservative Core Spray Flow Utilized in LOCA Analysis</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2008, the fuel vendor (Westinghouse) notified Exelon of a non-conservatism in the Large Break - Loss of Coolant Analysis affecting Dresden Nuclear Power Station, Unit 2. The non-conservatism involved the amount of Low Pressure Core Spray (LPCS) flow that actually reaches the reactor core during a postulated Large Break - Loss of Coolant Analysis event. For Dresden Unit 2, the error resulted in an increase of 80°F in the calculated Peak Cladding Temperature, resulting in exceeding the Peak Cladding Temperature acceptance criterion of 2200°F by 30°F. Dresden Operations took immediate actions to apply a Maximum Average Planar Linear Heat Generation Rate (MAPLHGR) administrative limit on Dresden Unit 2 to bring the plant configuration into compliance with 10 CFR 50.46 requirements. Based on the results of the cause evaluation performed by Westinghouse, the apparent cause of this error was that the author and verifier of the Westinghouse analysis had an incomplete understanding of the evaluation model, coupled with a false sense of security due both to the bounding system response being essentially the same as the original response and by the fact that the MAPLHGR margin recovery items had been developed by a panel of technical experts. Additionally, the Exelon subject matter experts do not have detailed knowledge of each fuel vendor's methodology and codes, and did not adequately challenge why the LPCS flow values used were bounding for Unit 2.
2442008001 | Ginna | 05/08/2008 | 07/03/2008 | ML08193067 | <strong>Plant Heatup with Required Residual Heat Removal Loops Inoperable due to Personnel Error (Voluntary Report)</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2008, while in Mode 4 and performing a plant heatup, Technical Specification (TS) Limiting Condition of Operation (LCO) Action 3.4.6.A was inadvertently entered. Both loops of Residual Heat Removal (RHR) were isolated from the Reactor Coolant System (RCS) by Motor Operated Valve (MOV) closure and subsequent removal of power, rendering both RHR loops inoperable by TS Bases definition. The operability of Reactor Coolant Pump "A" was under evaluation at the time of RHR isolation, conservatively leaving RCS Loop B the only operable and operating loop available for cooling. Upon recognition of the LCO entry, power was immediately restored to the RHR valves, consistent with the requirements of LCO Required Action 3.4.6.A. This report is being submitted voluntarily under the provisions of NUREG-1022. The apparent cause, planned corrective actions and similar LERs are described in the appropriate sections of the attached report.
2472008001 | Indian Point 2 | 03/23/2008 | 05/22/2008 | ML08149031 | <strong>Manual Reactor Trip Due to Decreasing Steam Generator Levels Caused by Loss of Feedwater Flow as a Result of Feedwater Pump Speed Control Malfunction</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2008, at 2216, with reactor power at 94.5%, as part of a planned coast down for a scheduled refueling outage, a manual reactor trip (RT) was initiated as a result of 22 Main Boiler Feed Pump (MBFP) rapid speed reduction causing lowering steam generator levels. All control rods inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as off-site power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink. The direct cause was radio frequency interference (RFI) from camera use near a MBFP speed control signal processer. The root cause of the event was lack of knowledge that a digital camera is an RFI source that can produce adverse effects on digital control components. Contributing causes were a poor choice of the controlling procedure for camera activity, poor change management in implementing the review requirements without providing adequate review tools, failure to follow procedure. Corrective actions include preparation of specific procedural guidance on electronic interference sources, creating a change management plan to track implementation of the new procedure and process, perform a needs analysis for training, and a site communication of this event and lessons learned from the event. The event had no effect on the public health and safety.
2472008002 | Indian Point 2 | 03/28/2008 | 05/27/2008 | ML08156020 | <strong>Technical Specification Prohibited Condition Due to Exceeding the Allowed Completion Time for an Inoperable Engineered Safety Feature Actuation System Automatic Actuation Logic and Actuation Relay Caused by Improper Relay Wiring</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2008, during Safety Injection (SI) and Black Out testing, with the unit shutdown for a refueling outage, a 480 V breaker {BKR} on Safeguards Bus 2A (ED) did not close during a surveillance test. Troubleshooting discovered that SI Logic Train A, relay 3-2, contact 17-21, when closed had high contact resistance. Relay 3-2 is part of the Engineered Safety Feature Actuation System (ESFAS), whose design function is to actuate safeguards equipment required to mitigate an accident. On March 28, 2008, troubleshooting discovered relay 3-2 did not have wires associated with 23 Fan Cooler Unit (FCU) Breaker connected to it in accordance with plant design. The wires were found landed on an adjacent SI Logic Train A relay 3-3. Subsequently equivalent wires on the SI Logic Train B relays, 3-12 and 3-13, were discovered to be similarly mis-wired. The incorrect wiring associated the 23 FCU with Bus 5A rather than its assigned Bus 2A. If power was lost on Bus 5A during an SI, the mis-wiring would prevent the automatic start of the 23 FCU even though its assigned Bus 2A was energized. The apparent cause of the circuit anomaly was an improperly implemented design change by the original plant installer in 1973. The design schematic was properly revised by the design change but the wiring lists and plant were not. The specific cause can not be determined due to the passage of time. Corrective actions included re-wiring of relay contacts in accordance with re-verified design documents. An extent of condition was performed and no additional wiring anomalies were identified. The event had no effect on public health and safety.
2472008003 | Indian Point 2 | 04/21/2008 | 06/23/2008 | ML08184010 | <strong>Manual Reactor Trip due to Decreasing Steam Generator Levels Caused by a Main Turbine Runback due to a Failed Runback Circuit Bistable with a Control Switch Mis-positioned to Armed</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2008, during power ascension following a scheduled refueling outage, Operations initiated a manual reactor trip as a result of observing decreasing steam generator levels and a turbine runback. Troubleshooting discovered a failed bistable permissive (PC-412B-1) in the loss of main boiler feedwater pump (MBFP) main turbine runback system. The system circuitry uses MBFP speed signals, main turbine steam inlet pressure representing percent power, and an Arm/Defeat switch to actuate a runback. The failed bistable gave the runback system a signal that the turbine was greater than 76.5 percent. With one of two MBFPs below the runback speed limit and the Arm/Defeat switch Armed, the circuit coincidence for runback was completed. The direct cause of the event was a failed bistable for main turbine steam inlet pressure. The causes identified were weak procedural guidance for placement of the Arm/Defeat switch in the Defeat position at power levels below 76.5%, failure to follow the startup procedure due to human performance error, and failure to document status control per the intent of the procedure for conduct of operations. Corrective actions include replacement of two turbine inlet pressure bistables, revision of plant operating procedures for Arm/Defeat switch positioning and coaching involved operators on procedure use and adherence. Management expectations will be re-enforced on expected actions when components are not in needed positions, operations will be briefed on the event and expectations, and training will revise the simulator for event and include lessons learned in operator training. The event had no effect on public health and safety.
2492008001 | Dresden 3 | 08/17/2008 | 10/16/2008 | ML08303004 | <strong>Unit 3 Drywell Floor Drain Sump Monitoring System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2008, at approximately 2000 hours (CDT), with Unit 3 at approximately 100 percent power, Dresden Nuclear Power Station Operations personnel attempted to pump the Unit 3 drywell floor drain sump, which is used to partially satisfy Surveillance Requirement 3.4.4.1. The pumps started as expected, however, the drywell floor drain sump monitoring system flow integrator indicated no flow. Since the water volume in the drywell floor drain sump could not be measured, the plant was not able to meet Technical Specification 3.4.4, "RCS Operational Leakage." Unit 3 initiated a plant shutdown on August 17, 2008 at approximately 0902 hours (CDT), as the repairs to the system could not be made with Unit 3 online. Dresden Nuclear Power Station requested a Notice of Enforcement Discretion on August 17, 2008 at approximately 1030 hours (CDT) to allow Unit 3 to remain at power for 7 days to allow time for the processing of an emergency Technical Specification amendment. The NRC granted the Notice of Enforcement Discretion on August 17, 2008 at approximately 1200 hours (CDT). Dresden Nuclear Power Station requested and received an emergency Technical Specification amendment to allow continued power operation with an inoperable Unit 3 drywell floor drain sump monitoring system within the time allowed by the Notice of Enforcement Discretion. The cause of the event is indeterminate until the drywell floor drain sump monitoring system can be examined during an outage of sufficient duration, but no later than the startup from D3R20.
2492008002 | Dresden 3 | 10/29/2008 | 12/23/2008 | ML09006087 | <strong>Unit 3 Primary Containment Isolation Valve Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2008, at approximately 2300 hours (CDT), with Unit 3 at approximately 85 percent power, Dresden Nuclear Power Station operations personnel identified that the OPEN indication light for the normally open primary containment isolation valve 3-3702 was flickering. Actions were taken in accordance with the requirements of Technical Specification 3.3.3.1, "Post Accident Monitoring (PAM) Instrumentation." An investigation into the flickering of the indication light on November 1, 2008, discovered an intermittent high resistance electrical connection at the motor control center for control power to valve 3-3702. The intermittent high resistance electrical connection caused the flickering indicator light and also would have prevented valve closure from the control room. On November 1, 2008, at approximately 1050 hours, valve 3-3702 was declared inoperable and actions were taken in accordance with the requirements of Technical Specification 3.6.1.3, "Primary Containment Isolation Valves (PCIV)." The valve was restored to operable status on November 1, 2008, at approximately 1309 hours. The cause of the event was an intermittent high resistance electrical connection at the motor control center for control power to valve 3-3702. Additionally, the cause of not entering Technical Specification 3.6.1.3 on October 29, 2008 was a lack of proper procedure guidance that led operations personnel to assume the problem was a faulty light socket.
2492008003 | Dresden 3 | 11/03/2008 | 12/31/2008 | ML09009037 | <strong>Unit 3 Unplanned Control Rod Withdrawals</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2008, at approximately 1036 hours (CST), with Unit 3 in a refuel outage, Dresden Nuclear Power Station operations personnel observed an unplanned withdrawal of control rod D-7. The control rod withdrawal stopped at position 06 with no actions taken by main control room personnel. An unplanned withdrawal of control rod E-6 to position 18 and control rod E-7 to position 16 also occurred and stopped with no actions by main control room personnel. All control rods were re-inserted to the full-in position per procedure on November 3, 2008, at approximately 1156 hours (CST). The root cause of the unplanned control rod withdrawals is attributed to latent procedure deficiencies in DOP 0500-05, "Discharging CRD Accumulators with Mode Switch in Shutdown or Refuel," Revision 4 that were not identified during an Operating Experience Review of the Significant Event Notification (SEN) 264, "Unplanned BWR Control Rod Withdrawals While Shutdown," per procedure LS-AA-115, "Operating Experience Procedure." Corrective actions to address this event include procedure revisions to DOP 0500-05 and LS-AA-115.
2502008001 | Turkey Point 3, Turkey Point 4 | 02/26/2008 | 04/25/2008 | ML08130074 | <strong>Human Error Causes Grid Disturbance Resulting in a Dual Unit Trip</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2008 at approximately 1309 hours, a momentary grid voltage disturbance occurred that caused a reactor trip of both Turkey Point Units 3 and 4 when both channels of safety-related 4 KV bus undervoltage relays for each unit actuated after a one second time delay. In addition, at approximately 1620, while shutting down the Unit 4 4A steam generator feed pump after transferring to standby feedwater, auxiliary feedwater (AFW) automatically actuated due to a red flag semaphore still present on the 4B SGFP control switch since the switch had not been taken to the stop position. This AFW actuation was inadvertent. The grid voltage disturbance occurred due to human error when a Protection and Control field engineer disabled both levels of local protection at an electrical substation which then failed to actuate when a fault occurred during equipment troubleshooting. The inadvertent AFW actuation occurred due to inadequate procedural guidance. Since plant response to the grid disturbance was as designed and AFW was not required to mitigate any plant condition at that time, the safety significance of the plant trips and inadvertent AFW actuation are minimal. Corrective actions relating to the grid disturbance include a new procedure setting requirements related to disabling protection. Corrective action for the inadvertent AFW actuation entails future procedure changes to ensure the control switches for various components powered by the 4C 4 KV bus are placed in the appropriate position after a loss of power and to verify the control board switches are green flagged.
2502008002 | Turkey Point 3 | 03/01/2008 | 04/30/2008 | ML08130042 | <strong>Containment Purge Valve and Associated Penetration Fail Leak Rate Test due to Inadequate Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2008, a local leak rate test (LLRT) was performed on Penetration 35 (POV-3-2600 and POV-3-2601) and a purge valve, POV-3-2600, and penetration 35 failed the test with a leakage of about 45,000 sccm. The acceptance criteria was less than or equal to 16,500 sccm. The valve POV-3-2600 failed its LLRT because the valve disc was not fully closed. Corrosion in the actuator bearing surfaces created friction that was suspected to have prevented the actuator from delivering the seating torque needed to provide an adequate seal. The penetration and associated valves were put under administrative controls to prevent further operation. The penetration is considered to have been inoperable from 2/28/08 at 00:25 hours when the penetration was opened in Mode 3, until the successful LLRT on 3/1/08 at about 14:10 hours. Since the penetration was inoperable for approximately 61 hours, the 24-hour allowed outage time of Technical Specification (TS) 3.6.1.7.b was exceeded. Immediate corrective actions included performing a "snoop" check on the outer isolation valve disc/seat. The snooping (which would act as a seat lubricant), additional pressurization of the penetration (up to approximately 60 psig), and waiting time most likely allowed the actuator spring force to position the disc a small amount further into the seat resulting in a successful LLRT. Preventive maintenance (PM) was revised to grease the bearing surfaces on an 18-month frequency.
2502008003 | Turkey Point 3 | 06/01/2008 | 08/11/2009 | ML09233011 | <strong>Inoperable Steam Generator Blowdown Containment Isolation Valve in Excess of Technical Specification Required Isolation Time-Supplement</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2008, Turkey Point Unit 3 was in Mode 1, at 100% Reactor Power. At 1844, the 3C Steam Generator (SG) blowdown containment isolation valve, CV-3-6275C failed to close in the absence of instrument air during the surveillance testing of its accumulator check valve. On June 9, 2008, it was recognized that CV-3-6275C was inoperable and it would no longer be able to perform its containment isolation function. Unit 3 was operating in a condition prohibited by Technical Specifications (TS) from June 1, 2008, until June 9, 2008, when action was taken to comply with TS 3.6.4 action requirements. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B). It was also identified that the effects of the inoperable SG blowdown isolation valve, on June 9, 2008, created a condition for 6 hours and 37 minutes, which could have prevented the fulfillment of the valve's safety function to support steam generator pressure integrity during plant transients that require Auxiliary Feedwater system operation. As such, this event is also reportable under 10 CFR 50.73(a)(2)(v)(B) and (D) as an event or condition that could have prevented fulfillment of a safety function for removing residual heat and/or mitigate the consequences of an accident. The root cause of the event is a latent design omission. Corrective actions include repair of the instrument air leak, communications to increase Operations awareness, revision of surveillance testing requirements, and design modification of the valve is being processed to improve the isolation capability on loss of instrument air.
2502008004 | Turkey Point 3 | 08/27/2008 | 10/23/2008 | ML08305051 | <strong>Emergency Containment Filter Inoperable Due to Control Circuit Length</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2008, during the design of a control switch modification, Engineering personnel identified a voltage drop concern with the Unit 3 3B Emergency Containment Filter (ECF) control circuit. The ECF fans are required to automatically start upon a loss of coolant accident (LOCA) signal. Two of three ECF fans are required to accomplish the safety function. Calculations show that the voltage is not adequate to pickup the 3B ECF starter coil for a LOCA start signal at the minimum allowable post trip switchyard voltage. The 3B ECF was declared inoperable on August 27, 2008. The apparent cause for the 3B ECF being declared inoperable is a latent design error. An interposing relay was installed within the control circuit and the 3B ECF was declared operable on August 30, 2008. The control circuit length for starting the 3B ECF from the control switch is within the allowable length, therefore, the 3B ECF would have been able to be started manually in a low voltage situation. The ECF system does not play a role in the prevention of a core damage accident and the conditional containment failure probability given a LOCA or steam line break is very low, reducing significantly the risk importance of the ECF system function of removing radioactive gases and particulates from the containment.
2512008001 | Turkey Point 4 | 02/29/2008 | 04/25/2008 | ML08127023 | <strong>Manual Reactor Trip due to High Level in the 4A Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On February 29, 2008, Turkey Point Unit 4 was in Mode 1. Power escalation was in progress following an automatic reactor trip that occurred on February 26, 2008 due to an under voltage condition on the electrical grid. At 0447, following the turbine and main generator synchronization the operating crew loaded the main generator abnormally fast. The operator at the feedwater controls was using the Main Feedwater Regulating Bypass Valves to control steam generator (SG) levels in manual. The increasing steam demand resulted in SG level fluctuations causing the SG levels to "swell." The operator did not stabilize SG levels and he did not communicate his concerns to the operating crew. The 4A SG level exceeded 75% Narrow Range (i.e., the procedural upper limit for performing a manual reactor trip due to high steam generator level). At 0451, with Turkey Point Unit 4 reactor power at 10%, the operating crew initiated a manual reactor trip due to high level in the 4A steam generator. There were no equipment issues, and no adverse effects on plant parameters. The root cause of the event is insufficient guidance for the initial loading of the main generator and for stabilizing power while preparing to transfer to automatic feed regulating valve control. Corrective actions include procedural changes to provide guidance for ramp rates during initial turbine loading and appropriate hold points to ensure proper control of plant parameters. Additional corrective actions have been generated to address control room oversight and effective communications.
2512008002 | Turkey Point 4 | 05/05/2008 | 07/02/2008 | ML08196008 | <strong>Safety Injection Isolated in Mode 3 due to Inadequate Configuration Control</strong><br /><i>Abstract:&nbsp;</i>Safety Injection (SI) cold leg injection isolation valve 4-867 to Unit 4 was discovered out of position (locked closed) on May 5, 2008 at approximately 1237 hours and placed in its correct position, locked open and backseated at approximately 1307. Valve 4-867 is required to be locked open and backseated when reactor coolant system (RCS) temperature is greater than 380 degrees F. The valve was out if its required position for approximately five hours 26 minutes, from 0741 on May 5, 2008 when RCS temperature was above 380 degrees F until the valve was repositioned at 1307. The SI System was inoperable during this time. The cause of the event is that current component alignment processes used to restore systems during outages do not contain the rigor and control necessary to maintain the proper physical configuration of the plant. Corrective actions include 1) procedure revisions to ensure mitigating system flow path verification surveillances are included, can not be waived during refueling outages and are completed prior to Shift Manager hold points, and 2) determination of safety significant systems that cannot be waived and are required to have a valve alignment performed prior to Mode changes when returning from a refueling outage. Safety significance is low due to the short period of time the valve was closed when required to be open and low decay heat levels coming out of an outage.
2512008003 | Turkey Point 4 | 08/07/2008 | 10/06/2008 | ML08289019 | <strong>Class 1 Weld Leak due to Fatigue and Completion of Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2008, at approximately 1230 with Unit 4 at 100% reactor power a small weld crack was discovered on a 3/4 inch test connection line for the 4B reactor coolant pump (RCP) seal water injection (SWI) header inside containment. On August 15, 2008, FPL was informed by the NRC that Technical Specification (TS) 3.4.10, Structural Integrity, was applicable to the Class 1 leak. As TS Limiting Condition for Operation 3.4.10 and its related Action for Class 1 components could not be met, entry into TS 3.0.3 was required. A Unit 4 shutdown commenced at approximately 1629 on August 15, 2008, and was completed on August 17, 2008 at approximately 0402 when Unit 4 reached Mode 5. Entry into TS 3.4.10 was not made on August 7, 2008 as FPL had previously determined that TS 3.4.10 did not apply to operational leakage. The socket weld fracture initiated at the weld root and propagated outward by fatigue, initiated by inherent minor positive displacement charging pump induced system vibration over an extended period of time. The cause of the failure to enter TS 3.4.10 and TS 3.0.3 on August 7, 2008 is attributed to a lack of clarity in TS 3.4.10. FPL and the NRC came to different conclusions regarding the applicability of TS 3.4.10 to operational leakage. Corrective actions include the following: 1) The 4B RCP SWI test connection line has been repaired. 2) Initial extent of condition inspections are complete on Unit 4. 3) A license amendment request will be submitted to the NRC to delete or relocate TS 3.4.10.
2512008004 | Turkey Point 4 | 09/08/2008 | 01/29/2009 | ML09056052 | <strong>Undervoltage Trip Time Delay Relays Cause Loss of Function</strong><br /><i>Abstract:&nbsp;</i>On September 8, 2008, one of the Unit 4 undervoltage time delay (UVTD) relays (Agastat model E7024PB004) for Channel B of the Reactor Protection System failed during a surveillance test. Subsequent investigation revealed the cause to be the same for a failed test of the same channel on August 22, 2008 that was not repeatable from the initial failure at that time. In addition, the time delay requirements (less than 2 seconds for reactor trip) were determined to have not been met since July 14, 2008 for Channel B and August 22, 2008 for Channel A. Previously, timing was only checked during 18 month Channel Calibration. The root cause of the UVTD-2B failure was a manufacturing defect. A wrong size spring was installed. The root cause of the timing failures is that the relays were not calibrated according to the manufacturer's Technical Bulletin. Corrective actions include: 1) Unit 3 UVTD relays were tested to ensure proper operation and timing. 2) One of each pair of Unit 4 Agastat model E7024PB004 UVTD relays was replaced with an Agastat model E7022 relay in the trip channel. The function of the other (E7024PB004) UVTD relay in each pair was revised to provide only annunciation. 3) The calibration test procedure will be revised to be more closely aligned with the original equipment manufacturer's procedure. As a backup to the undervoltage trip, credit can be taken for reactor trip on 4.16 kV bus underfrequency for an event causing complete loss of reactor coolant system flow due to a loss of power.
2542008001 | Quad Cities 1, Quad Cities 2 | 07/10/2008 | 09/04/2008 | ML08260047 | <strong>Past Operation of Safe Shutdown Makeup Pump Outside Technical Specifications Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2008, the Station Engineering Department identified an error in the calculation that determines required discharge pressure for the Safe Shutdown Makeup Pump (SSMP) to meet its applicable Technical Specifications (Tech Spec) Surveillance Requirement. As a result of an increased pressure drop across the discharge valves (due to reduced port design), the required SSMP discharge pressure necessary to meet the Surveillance Requirement for a flow rate of 400 gpm into the reactor at 1120 psig was calculated to increase from 1196.3 psig to 1215.0 psig when the identified error is corrected. The SSMP was tested most recently on August 4, 2008, and was observed to have a corrected discharge pressure of 1269.4 psig. Therefore, the identified error does not impact the current condition as the pump maintains more than 50 psig of operating margin. The SSMP is common system to both Units 1 and 2. This calculation error resulted in historical Tech Spec Surveillance testing failures of the corrected required SSMP discharge pressure during two periods of time: Surveillances from November 1995 to November 1999, and Surveillances from September 2007 to January 2008. It was later determined that the discharge flow rate under safe shutdown conditions would have been adequate to ensure the SSMP provided its minimum Appendix R function (approximately 350 gpm). The SSMP was repaired on December 21, 2007 (wear ring degradation found, impeller replaced) and February 4, 2008 (new modified impeller installed due to limited margin in the prior pump impeller). When the pump was replaced in February 2008, this resulted in the current acceptable operating margin of more than 50 psig described above. This issue was determined to have resulted in a past operation or condition prohibited by the plant Technical Specifications, and is reportable per 10CFR50.73(a)(2)(i)(B).
2552008001 | Palisades | 01/13/2008 | 03/10/2008 | ML08072037 | <strong>Reactor Protection System and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 13, 2008, with the plant in Mode 1 at 100% power, main feedwater pump P-1B tripped unexpectedly. Operators entered the loss of main feedwater procedure and appropriately carried out the procedurally directed action to manually trip the reactor. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The immediate cause of the main feedwater pump trip was low lube oil pressure. The low lube oil pressure resulted from the loss of the main feedwater pump's shaft-driven lube oil pump, which occurred when its drive coupling became disengaged. An incorrect shaft key allowed the lower hub to slide down the shaft, making only partial engagement with the sleeve. The partial tooth engagement between the lower hub and sleeve was not sufficient to withstand the shaft torque, which ultimately resulted in stripping the splines on the coupling sleeve and decoupling the lube oil pump's shaft drive. The lube oil pump was rebuilt, incorporating a design change that added a spacer beneath the lower hub to prevent the hub from sliding down the shaft and losing engagement with the coupling sleeve. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
2552008002 | Palisades | 03/26/2008 | 05/27/2008 | ML08148050 | <strong>Breaker Cubicle Switch Failure Results in High Pressure Safety Injection Pump Inoperabilty</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2008, with the plant in Mode 1 at 100% power, during planned maintenance on high pressure safety injection (HPSI) pump P-66A, operators experienced difficulty in removing the P-66A 2400VAC breaker 152-207 from its cubicle. A mechanism-operated cell (MOC) switch operator (bayonet) located inside the breaker cubicle was found with two broken connections. The condition of the MOC switch bayonet would have prevented operating a contact that provides a permissive to open HPSI subcooling control valve CV-3071, thereby rendering P-66A inoperable. It was concluded that the MOC switch bayonet failed when breaker 152-207 operated on January 3, 2008. The MOC switch bayonet was replaced on March 26, 2008. The cause was determined to be that the MOC switch bayonet design is marginal for the force applied by the stored energy vacuum breaker 152-207. The contributing cause is a failure to validate that the MOC switch used during manufacturer testing matched the switches installed at the plant. The opposite train MOC switch bayonet was inspected and no damage was found. Subsequently the MOC switch bayonets for the safety bus switchgear were inspected. Replacement of the MOC switch bayonet and others of the same type in stored energy breaker cubicles is planned.
2552008003 | Palisades | 05/23/2008 | 07/21/2008 | ML08203079 | <strong>Reactor Protection System and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2008, at 1249 hours, with the plant in Mode 1 at 100% power, an actuation of the 346 generator negative sequence relay caused an actuation of the 386C coastdown lockout relay. The 386C relay actuation caused the main generator output breakers in the switchyard to open, causing a turbine trip, which actuated the reactor protective system to trip the reactor. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The cause of the generator negative sequence relay could not immediately be determined. The relay spuriously failed. The relay was replaced and sent to Asea Brown Boyeri (ABB) for analysis. The problem could not be reproduced at ABB. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
2552008004 | Palisades | 07/15/2008 | 09/15/2008 | ML08266058 | <strong>Noncompliance with Technical Specification 4.3.1.1.b</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2008, with the plant in Mode 1 at 100% power, Entergy Nuclear Operations, Inc. personnel discovered that the Palisades Nuclear Plant region 1 spent fuel pool (SFP) storage racks contain less neutron absorber material than assumed in the SEP criticality analysis of record. This neutron absorber material is relied on to maintain the region 1 SFP storage racks within the Technical Specification (TS) 4.3.1.1.b criticality requirements. The TS reflects credit for the neutron absorber material in maintaining SFP criticality within limits. At the time of discovery, SFP boron concentration was 2732 ppm. TS 4.3.1.1.b requires that Keff for region 1 fuel racks be less than or equal to 0.95 if fully flooded with unborated water. With soluble boron required to maintain Keff less than or equal to 0.95 in the region 1 fuel racks, assuming nominal enrichment, PNP no longer complies with TS 4.3.1.1.b. The degraded neutron absorber material did not involve an immediate safety concern at the time of discovery because the SFP boron concentration was 2732 ppm, and a SEP criticality operability assessment concluded that a soluble boron concentration of 150 ppm is required to maintain a Keff less than or equal to 0.95 in the region 1 racks. In addition, plant procedures required that SEP boron concentration be maintained at a minimum of 2550 ppm in Modes 1 through 4. In Modes 5 and 6, 1800 ppm was required. A past operability evaluation confirmed that SFP boron concentration had been maintained greater than 2550 ppm in recent years. Compensatory measures are in place. This condition does not represent a safety system functional failure. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(13) as a condition prohibited by TS.
2552008005 | Palisades | 08/05/2008 | 10/02/2008 | ML08280045 | <strong>Completion of a Plant Shutdown Required by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>During a planned shutdown, on August 5, 2008, at 1629 hours, with the plant in Mode 1, at approximately 97% power, Entergy Nuclear Operations, Inc. control room personnel noted that unidentified primary coolant system (PCS) leakage had exceeded the Technical Specification (TS) limit of one gallon per minute. Limiting Condition of Operation (LCO) 3.4.13, Condition A, was entered while the planned shutdown continued. All required actions for the condition were completed. The event was reported as a four-hour non-emergency report, in accordance with 10 CFR 50.72(b)(2)(i), as the initiation of a plant shutdown required by TS, because if the event had occurred with the plant at normal operation, a shutdown would have been required. The plant entered Mode 5 on August 6, 2008, at 1025 hours. The cause of the leakage was determined to be letdown relief valve RV-2006, which lifted when a second charging pump was started. RV-2006 was replaced during the planned shutdown. In addition, an engineering study is being completed for a modification to slow the associated orifice stop valve response to an open/close signal, and allow the associated pressure indicating controller to adequately control letdown pressure. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A) as the completion of a plant shutdown required by TS.
2552008006 | Palisades | 10/09/2008 | 12/03/2008 | ML08340014 | <strong>Emergency Diesel Generator Inoperable in Excess of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2008, Entergy Nuclear Operations, Inc. (ENO) engineering personnel completed a past operability evaluation that concluded during the 30 days between January 21, 2008, and February 19, 2008, emergency diesel generator (EDG) 1-2 would have been unable to operate satisfactorily for the EDG's required 30-day mission time. Therefore, it was inoperable. This period of inoperability corresponds to the time from when the Technical Specification (TS) surveillance test for EDG 1-2 was completed satisfactorily and ENO maintenance personnel discovered fragments of metal (broken pieces of a valve seat spring lock) in various locations throughout the valve assembly area of EDG 1-2 cylinder head, 2L. Consequently, the required actions and associated completion times of TS 3.8.1, condition B, were not met. Additionally, during the period EDG 1-2 was inoperable, EDG 1-1 was inoperable for approximately three hours for the performance of monthly surveillance testing. Therefore, both EDGs were simultaneously inoperable for a period of time longer than the two hours allowed by TS 18.1, condition E. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications and 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2552008007 | Palisades | 10/14/2008 | 01/21/2009 | ML09022018 | <strong>Potential Loss of a Safety Function due to Non-Conservative Auxiliary Feedwater Trip Setpoint</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2008, after completing reviews of evaluations performed by Entergy Nuclear Operations, Inc. (ENO) engineering, the Nuclear Regulatory Commission (NRC) closed an unresolved issue related to potentially non-conservative setpoints for the low suction pressure trip (LSPT) of the auxiliary feedwater (AFW) pumps. The potentially non-conservative setpoints, which were first identified on February 13, 2006, could have existed at certain Condensate Storage Tank (CST) levels and AFW pump flow rates. The CST is the normal suction source of the AFW pumps. In the extreme unlikelihood of a tornado, a tornado-generated missile could have caused a rupture near the bottom of the CST. The rupture may have allowed rapid draining of the CST, without completely emptying the tank. Subsequent automatic operation of the AFW pumps after a plant trip could have caused the onset of vortexing within the CST, leading to air entrainment in the auxiliary feedwater suction piping and pumps. This entrained air could have rendered the AFW pumps inoperable. Consequently, the AFW system may not have been capable of supplying the steam generators with Lake Michigan water, as outlined in the Palisades Nuclear Plant design basis. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
2592008001 | Browns Ferry 1 | 09/03/2008 | 11/03/2008 | ML08312008 | <strong>Loss Of Secondary Containment When The Reactor Vent Zone Dampers Failed To Close On A Group 6 Signal Containment Isolation Signal.</strong><br /><i>Abstract:&nbsp;</i>On September 3, 2008, at 2344 hours Central Daylight Time (CDT) during a scheduled performance of the Unit 1 Surveillance, RPS Circuit Protector Calibration/Functional Test for 1A1 and 1A2, the Unit 1 Reactor Operator noted that secondary containment dampers Reactor Zone Exhaust Inboard Isolation Damper (1-DMP-64-42) and Reactor Zone Exhaust Outboard Isolation Damper (1-DMP-64-43) failed to close on a Group 6 Primary Containment Isolation Signal generated during the surveillance. The root cause of this event is the use of Dow Corning 550 lubricant in a normally energized solenoid. In a March 2002 event, an ASCO solenoid valve failed to close. Silicone based lubricant used by the manufacture during assembly caused the valve to malfunction. The corrective actions included replacement of the Units 2 and 3 solenoid valves. However, the solenoids associated with the Unit 1 secondary containment isolation dampers were not replaced. In response to this event, TVA replaced the solenoid valves for these two dampers.
2592008002 | Browns Ferry 1 | 11/23/2008 | 03/16/2009 | ML09086077 | <strong>ASME Code Class 1 Pressure Boundary Leak On An Instrument Line Connected to the Reactor Vessel</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2008, at approximately 1200 hours Central Standard Time (CST), during the performance of the Unit 1 vessel hydrostatic test, ASME Section XI System Leakage Test of the Reactor Pressure Vessel and Associated Piping, 1-SI-3.3.1.A, a reactor pressure boundary leak was discovered on an unisolatable instrument line connected to the reactor vessel. This instrument line is an ASME Code Class 1 equivalent component, 2-inch pipe, near pressure vessel nozzle N11B. BFN entered Technical Requirements Manual (TRM) Section 3.4.3 - Structural Integrity, which requires the integrity of ASME Code Class 1, 2, and 3 equivalent components shall be maintained through the life of the plant. Unit 1 was in Mode 4 at the time of discovery; it remained in Mode 4 until the repairs were completed. The root cause of the event was residual stress introduced to the safe end inside diameter during initial fabrication. The N11B safe end was examined ultrasonically (UT). The through wall leak was repaired by weld overlay. TVA added inservice examination requirements for N11B weld overlay to the Unit 1 inservice inspection program.
2592008003 | Browns Ferry 1 | 12/12/2008 | 02/11/2009 | ML09048008 | <strong>Main Steam Relief Valve As Found Setpoint Exceeded Technical Specification Lift Pressure</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2008, TVA determined that 10 of the 13 Main Steam Relief Valves (MSRVs) removed from Unit 1 following Cycle 7 operation mechanically actuated at pressures greater than 3 percent above their Technical Specifications (TS) setpoint, thus inoperable. Unit 1 TS limiting condition for operation (LCO) 3.4.3 requires that twelve (12) MSRVs are operable in reactor modes 1, 2, and 3. If less than twelve MSRVS are operable, the unit is to be placed in Mode 3 hot shutdown within 36 hours. As such, it is probable that Unit 1 operated outside the TSs longer than allowed by the TSs. Therefore, TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2602008001 | Browns Ferry 2 | 10/04/2002 | 11/24/2008 | ML08338019 | <strong>Automatic Turbine Trip and Reactor Scram Resulting from a Failure of the Design Change Process</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2008 at 2208 hours, Central Day Light Time (CDT) the Unit 2 reactor automatically scrammed following a turbine generator load reject signal. At approximately 2107 hours CDT, just prior to the reactor scram, operations noted the 500 kV Unit Station Service Transformer 2B tap changer operating excessively and the generator was experiencing field voltage, transfer voltage, and phase amperage swings. Operations decided to place the voltage regulator in the manual control mode in accordance with Operating Instruction, 2-OI-47, Turbine-Generator System. However, when Operations transferred the voltage regulator from the auto mode to the manual mode, Unit 2 received a turbine trip and subsequent automatic reactor scram. While placing the voltage regulator in the manual mode, contacts 7 and 8 on the Voltage Regulator Auto/Manual Transfer Relay (43A relay) failed to make-up; thus, causing the turbine to trip. The root cause of this event was a failure of the design change process. The process did not provide a prompt to consider relay contact wetting and signal threshold when selecting a relay for switching low energy control signals. The event was result of the installation of a relay in an application for which it was poorly suited. TVA replaced the 43A relay in main-generator voltage regulator circuit with a relay that is better suited for a low power application. TVA will revise the Technical Evaluation Considerations Checklist to address contact selection for relays installed in low energy circuits.
2612008001 | Robinson 2 | 05/21/2008 | 07/21/2008 | ML08206019 | <strong>Appendix R Pathway Impassable due to Lock Configuration</strong><br /><i>Abstract:&nbsp;</i>During a security exercise on May 21, 2008, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 100% power, Security personnel were unable to open the gate between the Radwaste Building and the "C" Auxiliary Boiler due to an improperly locked gate. This gate is part of an Appendix R safe shutdown pathway. It was subsequently identified that the key that would have been obtained by Operations personnel as part of their dedicated shutdown equipment would not have opened the security lock on the gate between the Radwaste Building and the "C" Auxiliary Boiler, had it been required. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR 50.73(a)(2)(v)(A), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition: (B) Remove residual heat: (C) Control the release of radioactive material: or (D) Mitigate the consequences of an accident." The health and safety of the public and plant personnel were not impacted by this event. No actual fire events or loss of safe shutdown capability have occurred. Completed corrective actions included establishing the proper lock configuration, the individual involved was counseled, a sign was added showing the proper configuration, and the required keys were placed in the appropriate location. Planned corrective actions include a procedure change to strengthen the verification and validation process for locked doors and gates, and installation of a breakable seal to replace the locks.
2612008002 | Robinson 2 | 11/17/2008 | 01/16/2009 | ML09023017 | <strong>Manual Reactor Trip due to High Turbine Vibrations</strong><br /><i>Abstract:&nbsp;</i>At 0551 hours EST on November 17, 2008, the H. B. Robinson Steam Electric Plant, Unit No. 2, reactor was manually tripped from approximately 78% power due to high vibrations detected on the main turbine. At 0516 hours EST, the No. 9 bearing vibration was about 13.5 mils and increasing. A power reduction from 100% power was commenced in accordance with Abnormal Operating Procedure, AOP-006. At approximately 0551 hours, with power level at approximately 78%, the No. 9 bearing vibrations reached the AOP-006 trip criterion of 14 mils and the reactor was manually tripped. The auxiliary feedwater system started automatically, as expected, in response to steam generator level changes after the reactor trip. The primary system and steam generator power operated relief valves and safety valves did not actuate during this event. The main feedwater system, main steam system, and condenser remained available during the event and were used for decay heat removal. The root cause investigation for the turbine vibrations determined that the most probable causes were: 1) The size and placement techniques for the shims installed under the exciter base were incorrect, 2) procedure, CM-024, "Exciter Maintenance and Inspection," utilized standard shim placement, which for the new exciter was not adequate, 3) incorrect clearances of the refurbished generator hydrogen seal resulted in a rub condition, and 4) a vendor fabrication error in the exciter gusset plate configuration could have resulted in a soft foot condition. This report is being made in accordance with 10 CFR 50.73(a)(2) (iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
2632008001 | Monticello | 01/31/2008 | 03/31/2008 | ML08091015 | <strong>Non-Conservative High Energy Line Break Analysis Discovered During Uprate Extended Review</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2008 during a review of the High Energy Line Break (HELB) calculations for the plant's Extended Power Uprate (EPU) project, it was determined that the existing HELB calculations failed to consider the actuation of the fire sprinklers in the condenser bay and the resultant flooding impact on the lower Division 1 4kV equipment. The station had previously installed a flood barrier near the 4kV Switchgear room door therefore present operability was not impacted. The station determined that prior to the installation of the barrier, there was a potential for the loss of the lower Division 1 4kV equipment. This LER addresses the past operability impact. The cause of the event was a failure to consider the impact of the fire sprinklers. Corrective actions taken or planned are: the flood barrier will remain in place and a revision of the affected HELB calculations will be performed.
2632008002 | Monticello | 02/19/2008 | 11/30/2009 | ML09335075 | <strong>Inoperability of Channel "B" Spent Fuel Pool Radiation Monitor due to Incorrect Calibration</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2008 Monticello was performing an investigation into a potential calibration methodology error on the Channel "B" Spent Fuel Pool Radiation Monitor. As part of the past operability evaluation, it was determined that the error had the potential to cause the "B" radiation monitor to be inoperable from the time period of November 20, 2007 to February 19, 2008. The cause for the potential inoperable condition of the radiation monitor was a combination of three adverse conditions; a faulty meter, a procedure deficiency, infrequent verification of the source strength of the calibrator. Corrective actions taken or planned are: the monitor trip setpoint was verified, the meter was replaced, and the source strength of the calibrator was verified. The station will revise affected procedures. The station will perform verifications of the source strength of the calibrator on an annual basis.
2632008003 | Monticello | 02/13/2008 | 11/30/2009 | ML09335075 | <strong>Control Room Emergency Filtration Trains Inoperability in Recirculation Mode</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2008, a surveillance procedure was identified that placed the Control Room Emergency Filtration system in a configuration where both trains were unable to automatically initiate in the High Radiation mode. This procedure placed both Control Room Emergency Filtration Master System switches in the Recirculation mode. Placing both Master switches in the Recirculation mode prevents automatic initiation of the High Radiation mode. The cause of the event was the failure by station personnel to understand the result of operation with both Master System Switches in the Recirculation mode. The procedure was quarantined until it was revised eliminating this problem.
2632008004 | Monticello | 04/29/2008 | 06/30/2008 | ML08183010 | <strong>Required Manual Isolation Time For High Energy LIne Break Calculation Not In Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2008 during a review of the High Energy Line Break (HELB) calculations, it was discovered that the station did not incorporate the required times for isolating the fire sprinklers and service water into the affected Operations procedure. This could result in the loss of the lower 4kV room due to flooding. Currently the station has installed a flood barrier near the lower 4kV Switchgear room door therefore present operability is not impacted. The station determined that prior to the installation of the barrier, there was a potential for the loss of the lower Division 1 4kV equipment. This LER addresses the past operability impact. The cause of the event was a failure to incorporate the required isolation time for the fire sprinklers and service water into the flooding response procedure. Corrective actions taken or planned are: the flood barrier will remain in place and a revision of the affected procedure will be performed.
2632008005 | Monticello | 09/11/2008 | 11/07/2008 | ML08315002 | <strong>Reactor Scram due to Loss of Normal Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2008 at 2248 hours, the site experienced a lockout of the primary auxiliary transformer with the reserve transformer isolated for planned maintenance. This resulted in a Loss of Normal Off-site Power (LONOP) and an associated SCRAM. The cause of the event was the A and B phase conductors supplying power to the primary auxiliary transformer faulted to ground. Corrective actions taken or planned are: the faulted cable was repaired, repaired other degraded cable splices identified by the extent of condition, and improvements in the cable condition monitoring program.
2632008006 | Monticello | 09/17/2008 | 11/14/2008 | ML08322102 | <strong>Loss of Normal Offsite Power due to Equipment Contact with 115KV Lines</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2008 at 0934 with the unit in a forced outage, the site experienced a Loss of Normal Off-site Power (LONOP) when man-lift equipment being serviced by a vendor came into contact with a 115 kV line. The loss of power resulted in a valid actuation of the Reactor Protection System (with reactor shutdown), Containment isolation resulting in a loss of normal shutdown cooling, and starting of the plant emergency diesel generators. The cause of the event was a portable man-lift contacting a 115 kV line causing the 1R transformer to trip with the 2R transformer out of service for repair, which resulted in a loss of normal off site power (LONOP). Corrective actions taken were to implement additional controls for the staging of equipment by supplemental personnel on site.
2632008007 | Monticello | 09/20/2008 | 11/18/2008 | ML08324076 | <strong>Loss of Shutdown Cooling due to ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2008 at 21:35 hours with the unit in a forced outage, the site experienced a Loss of Shutdown Cooling (SDC) caused by a Low-Low Reactor Water Level Engineered Safety Feature (ESF) actuation during restoration of the Control Rod Drive (CRD) system. The actuation of the ESF resulted in a Reactor Protection System signal (with the reactor shutdown), Containment isolation resulting in a loss of normal shutdown cooling, and starting of the plant emergency diesel generators. The cause of the event was an instrument back-fill valve which had been left open. When the CRD system was started, a pressure spike was transmitted to the Reactor Water Level Low-Low transmitter and an ESF signal was generated. Corrective actions taken were to revise station procedures and to hold communication meetings with each operating crew.
2632008008 | Monticello | 11/13/2008 | 01/08/2009 | ML09008038 | <strong>Technical Specification Required Shutdown Margin Not Met During All Conditions for Refueling Outage 23</strong><br /><i>Abstract:&nbsp;</i>Following review of an industry refueling Shutdown Margin (SDM) best practice, the Nuclear Analysis Department evaluated the best practice and tested the practice on the core alterations made during the last Refuel Outage (RFO 23) in 2007 with SIMULATE-3, taking into account both a core exposure dependent bias and the use of a three-dimensional method. On November 13, 2008, it was determined that the Technical Specification (TS) SDM was not met for all conditions during the refuel outage. The root cause for not meeting the SDM during RFO 23 was insufficient verification and validation using higher order (known and industry accepted) method for determination of TS SDM compliance. The corrective action taken to prevent recurrence was to require utilizing only a three-dimensional model when determining SDM during core alterations and the operating cycle.
2662008001 | Point Beach 1 | 01/16/2008 | 03/16/2008 | ML08077018 | <strong>Manual Reactor Shutdown Required by Technical Specification LCO 3.8.1 AC Sources-Operating Not Met</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2008, at 1404 Central Standard Time, Point Beach Nuclear Plant (PBNP) experienced a loss of transformer 1X04, low voltage station auxiliary transformer for Unit 1. The loss of 1X04 resulted in the declaration of an Unusual Event, SU1, "Loss of All Offsite Power to Essential Busses for GREATER THAN 15 Minutes." The Unusual Event was reported on EN# 43907 in accordance with 10 CFR 50.72(a)(1)(i), "The declaration of any of the Emergency Classes specified in the licensee's approved Emergency Plan," 10 CFR 50.72(b)(2)(xi), "News Release or Notification of Other Government Agency," 10 CFR 50.72(b)(2)(i), "Plant Shutdown Required by Technical Specifications." Technical Specification (TS) 3.8.1 Action Condition B, "Associated unit's 13.8/4.16 kV transformer inoperable," was entered at 1404 on January 15, 2008. This Condition has a Completion Time of 24 hours to return the transformer to operable status. At 1404, January 16, 2008 the Completion Time was not met and Unit 1 entered TS 3.8.1 Action Condition H with a Required Action to be in MODE 3 in 6 hours and MODE 5 in 36 hours. Unit 1 shutdown commenced at 1549 and Unit 1 was in MODE 3 at 1948, January 16, 2008.
2662008002 | Point Beach 1, Point Beach 2 | 02/02/2008 | 05/23/2008 | ML08205023 | <strong>One Service Water Pump lnoperable in Excess of Technical Specification Allowed Completion Time</strong><br /><i>Abstract:&nbsp;</i>At 0241 hours on February 2, 2008, vibration at point M1Y, which measures upper motor vibration parallel to pump discharge flow, on service water pump P-32E was determined to be 1.2 inches per second (ips) which is in excess of the American Society of Mechanical Engineers (ASME) Code "required action" level. The pump was secured and declared inoperable. The pump was disassembled, with significant wear identified on the shaft at the Cutless bearing locations. Shaft runout was measured, with the third intermediate shaft exhibiting the largest amount, which confirmed the cause of the damage and high vibrations to be a bent shaft. Shaft straightness is verified prior to installation so rigging practices used during installation are believed to have caused the bending. The historical vibration data from P-32E was evaluated in concert with the observed bearing and shaft damage. It was determined that the ASME "required action" vibration limit of 0.421 ips would have been reached on about January 9, 2008. Had vibration data at that magnitude been obtained on January 9, 2008, the pump would have been declared inoperable. The pump was declared inoperable on February 2, 2008. The Technical Specification Action Condition (TSAC) Completion Time limit of 7 days was exceeded because 24 days had elapsed between January 9 and February 2, 2008.
2662008003 | Point Beach 1, Point Beach 2 | 07/16/2008 | 05/11/2009 | ML09132044 | <strong>Appendix R Fire Scenario Resulting In Safe Shutdown Required Capability Not Maintained</strong><br /><i>Abstract:&nbsp;</i>This supplement provides the results of the detailed extent of condition evaluation completed in March 2009 and the risk significance evaluation completed on April 17, 2009. On July 16, 2008, plant staff concluded that an inadequate cable separation condition in the Auxiliary Feedwater (AFW) room could potentially compromise the plant's ability to meet Appendix R safe shutdown requirements. An 8-hour report was made via the emergency notification system (EN 44351), pursuant to 10 CFR 50.72(b)(3)(ii) (B). Immediate corrective actions included fire area rounds already being performed by plant personnel, implementation of transient combustible controls in the AFW area and performance of thermography for insipient fire detection in the AFVV pump rooms. An extent of condition evaluation completed in March 2009 confirmed the results of the August 2008 evaluation identifying six (6) areas where an inadequate cable separation condition could potentially result in a loss of significant equipment in areas beyond that postulated in the initiating fire area. The results of a risk significance evaluation completed on April 17, 2009, concluded that the risk significance of each of the inadequate cable separation conditions was less than the red finding threshold and may be resolved in accordance with the alternate methods established in NFPA-805.
2692008001 | Oconee 1 | 09/13/2008 | 11/12/2008 | ML08323005 | <strong>Gas Void Found in High Pressure Injection System Suction Piping</strong><br /><i>Abstract:&nbsp;</i>On 09/13/2008, while Oconee Unit 1 was operating in Mode 1 at 100% rated power, an examination being performed in response to Generic Letter (GL) 2008-01 detected a gas bubble (void) in the suction piping to the High Pressure Injection (HPI) suction header. At 13:46 hours, Engineering completed a calculation of the void volume and initiated a Problem Investigation Process report. At 15:12 hours, Engineering and Operations concluded that the void could render the 1A HPI pump and 1A HPI train inoperable. Operations declared 1A HPI pump and 1A HPI train out of service and entered Technical Specification (TS) 3.5.2, Conditions A and C. The line was vented, and, at 16:43 Operations declared the pump and train Operable and exited the TS conditions. Additional examinations confirmed that the equivalent locations on the Unit 1B HPI train and on Units 2 and 3 did not contain voids. No specific source or cause could be found for the void. Duke Energy responded to GL 2008-01 by letter dated 10/13/2008 and committed to actions which are expected to permanently resolve this issue. This event is considered to have minimal significance with respect to the health and safety of the public.
2702008001 | Oconee 2 | 03/31/2008 | 05/29/2008 | ML08155014 | <strong>Unit 2 Reactor Trip due to Indication of Loss of Vacuum During Calibration of a Condenser Pressure Transmitter</strong><br /><i>Abstract:&nbsp;</i>At 1352 hours, on March 31, 2008, while operating at 100%, Oconee Nuclear Station, Unit 2 experienced an indicated loss of condenser [SG] vacuum. The most probable cause for the loss of condenser vacuum indication was a combination of obstruction (corrosion or foreign material) in the impulse line to the vacuum instrumentation and leakage of the 23 condenser pressure isolation valve(s). The obstruction and leakage produced an indication of loss of vacuum that resulted in the trip of Unit 2 main turbine. The trip of the main turbine caused the Unit 2 reactor to trip. The post trip response was normal, with all major operating parameters remaining within expected limits. Operators took appropriate action to stabilize the unit in Mode 3. Corrective actions address changes to procedures to restrict maintenance activities on vacuum and absolute pressure instruments while operating and also prevent the usage of B-6P4T Swagelok plug valve(s) for isolation in this particular application. This event is considered to have no significance with respect to the health and safety of the public.
2702008002 | Oconee 2, Oconee 1, Oconee 3 | 10/24/2008 | 10/01/2009 | ML09280035 | <strong>Main Steam Relief Valves Exceeded Lift Setpoint Acceptance Band</strong><br /><i>Abstract:&nbsp;</i>When tested on 10/24/2008, while in Mode 1 prior to shutdown for refueling, as-found lift pressure tests of Oconee Unit 2 main steam relief valves (MSRVs) revealed 3 unsatisfactory MSRVs out of a total of 16. Technical Specification (TS) 3.7.1 requires 16 MSRVs (8 on each header) to be operable in modes 1, 2 and 3 so Condition A was entered. The affected MSRVs were adjusted, satisfactorily retested, and the condition exited. Since multiple failures indicate the condition may have arisen over time, there is a likelihood that all of the required MSRVs were not operable during past plant operation. Therefore, this occurrence is considered reportable in accordance with 10 CFR 50.73 (a) (2) (i) (B) as a condition prohibited by TS. A review of prior similar events found three additional occurrences which were not previously recognized as reportable and are addressed in this report (Unit 1, 2 MSRVs, 2006; Unit 2, 2 MSRVs, 2007; and Unit 3, 2 MSRVs, 2007) . The cause of these occurrences has been identified as setpoint drift. All of the unsatisfactory as-found lift pressures were above the acceptance band but within analysis limits so there was no loss of function. This event is considered to have no significance with respect to the health and safety of the public.
2712008001 | Vermont Yankee | 06/10/2008 | 07/31/2008 | ML08220027 | <strong>Crane Travel Limit Stops not Installed as Required by Technical Specifications due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 06/10/08, with the reactor at 100 percent power, Vermont Yankee (VY) identified that the reactor building crane travel limit mechanical stops were not installed in accordance with Technical Specification (TS) 4.12.G.2 "Crane Travel". TS 4.12.G.2 requires crane travel limit mechanical stops to be installed during cask handling operations to prohibit movement of the cask over irradiated fuel. VY was performing dry fuel storage activities and had just removed a loaded spent fuel cask from the spent fuel pool. The cask was suspended above the refuel floor adjacent to the spent fuel pool. Once the cask is removed from the fuel pool, the crane limit mechanical stops need to be rearranged to prohibit movement over fuel assemblies in the fuel pool. The reactor building crane was de-energized and the crane travel limit mechanical stops were rearranged. Subsequently, VY determined that the sequence that the stops were removed and reinstalled did not comply with the requirements of the TS. There were no personnel or public safety implications because the crane was de-energized during the period of time the travel stops were rearranged and VY personnel were providing oversight of the evolution. The event was determined to be the result of an inadequate procedure. The procedure has been revised to address the identified weaknesses. No release of radioactivity or personnel injury occurred as a result of this event. No similar events have occurred in the last 5 years. This event is reportable as a Licensee Event Report per 10CFR50.73(a)(2)(i)(B) as a condition that is prohibited by TS.
2722008001 | Salem 1 | 11/05/2008 | 12/31/2008 | ML09013047 | <strong>Inadvertent Start of an Emergency Diesel Generator During Testing</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2008, Salem unit 1 was shutdown in Mode 5 completing its nineteenth refueling outage (1R19) activities. During the performance of an overlap test to complete the Technical Specification 4.8.1.1.2 required Mode Operation surveillance test for the 11 containment fan coil unit, the 1A vital bus unexpectedly de-energized and the 1A safeguards equipment controller actuated in the blackout Mode starting the 1A emergency diesel generator. The apparent cause of the event was a technical rigor / human performance error made in the test plan development that was not identified and corrected in the subsequent reviews. Corrective actions taken included: an extent of condition review to identify similar test plan errors, no additional errors were identified; shared lessons learned with the plant engineering department and station personnel. Additionally the Mode Operations surveillance test procedures will be revised to include specific requirements for the use of alternate test methodologies in the event a component(s) is not available for Mode Operations testing or fails to properly actuate during the test. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(A)...."
2722008002 | Salem 1 | 12/09/2008 | 02/07/2009 | ML09042049 | <strong>Missed Containment Spray Valve Surveillance per Technical Specification 4.0.5</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2008, with Salem Unit 1 in Mode 1, it was identified that Containment Spray pressure relief (vacuum breaker) valve 1CS12 could not be located to perform a required post removal as-found surveillance test in accordance with the requirements of the Technical Specifications (TS) and the ASME OMa-1988, Part 1, Requirements for lnservice Performance Testing of Nuclear Power Plant Pressure Relief Devices. The inability to perform the test because of the loss of the 1CS12 resulted in a conservative determination that the valve would not have passed the TS surveillance pressure test. The valve misplacement is attributed to failure to follow work order instructions to properly retain the valve for testing. The valve testing scope was expanded to the second redundant valve on the tank. The test of the redundant valve concluded that the valve would have performed its function. All pressure relief valves on the containment spray additive tank were replaced with new valves. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2752008001 | Diablo Canyon 1, Diablo Canyon 2 | 06/11/2008 | 08/11/2008 | ML08226030 | <strong>Potential Accumulator Drain Line Actuation Following a LOCA due to Solenoid Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2008, at 14:05 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at approximately 100 percent power, licensed plant operators entered Technical Specification (TS) 3.0.3 due to a potential solenoid valve failure mechanism that could initiate draining of the safety injection system (SIS) accumulators following a small break loss-of-coolant-accident (SBLOCA). Licensed plant operators made an eight-hour nonemergency event notification (EN 44287) in accordance with 10 CFR 50.72(b)(3)(v)(D) at 20:48 PDT. Plant engineers identified four nonsafety-related solenoid valves that could malfunction due to a low minimum operating pressure differential (MOPD) following a SBLOCA. These valves could misposition in an intermediate position such that upon reestablishing supply air pressure they could open their associated safety-related valve resulting in a loss of SIS accumulator inventory. Emergency Operating Procedures (EOP) direct operators to reinstate the air supply to containment if isolated during a postulated SBLOCA scenario.
2802008001 | Surry 1 | 04/20/2008 | 06/16/2008 | ML08182043 | <strong>Turbine Vibration Results in Manual Trip</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2008, Unit 1 was placed online following repairs to the "B" 6th point Feedwater Heater. At 54% reactor power, a rapid load reduction was initiated in response to high turbine bearing vibrations. At 2216 hours, due to sustained high turbine vibrations, a Unit 1 manual reactor trip was initiated with the reactor at 37% power. All safety systems functioned as designed and the operating staff stabilized the unit at Hot Shutdown. Auxiliary feedwater (AFW) automatically initiated, as expected, due to low steam generator levels. The cause of the event was high turbine vibrations resulting from improperly installed balance weights. The installation was made using the turbine vendor's recommendations that were in error. Updated vendor information was received and the balance move was independently verified by station personnel. The turbine was rebalanced and the unit placed on line April 21, 2008 and ramped to 100% reactor power with acceptable turbine vibrations. Dominion will participate in the vendor's evaluation of this event and procedures will be revised to ensure independent review of vendor data. There were no significant safety consequences associated with this event. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv)(A) for a manual actuation of the reactor protection system and automatic AFW initiation.
2802008002 | Surry 1, Surry 2 | 05/17/2008 | 07/08/2008 | ML08205039 | <strong>Relay Failure Results in Emergency Diesels Auto-Starting</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2008, at 0904 hours Emergency Diesel Generators 2 and 3 automatically started to re-power the 2H and 1J Emergency Busses due to a failed relay on an offsite power supply breaker in the switchyard. Unit 1 remained at 100% power and Unit 2, which was in cold shutdown for a scheduled refueling, maintained its shutdown cooling. The cause of the event was a failure of a 34.5 KV breaker failure lockout relay resulting in a loss of off-site power to the "A" and "B" Reserve Station Service Transformers which de-energized the "D" and "E" transfer busses that supplies the 2H and 1J Emergency busses. The defective lockout relay was replaced with a new relay and offsite power was restored to the 2H and 1J Emergency busses. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv)(A) for automatic actuation of the Emergency Diesel Generators.
2812008001 | Surry 2 | 05/02/2008 | 06/30/2008 | ML08198005 | <strong>Pressurizer Safety Valves Fail As Found Setpoint</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2008 with Unit 2 shut down for a refueling outage, a pressurizer safety valve (PSV) 2-RCSV-2551C as found lift setting was 2368 psig, which is 4.7% below the nominal value of 2485 psig. Technical Specification (TS) 3.1.A.3.b specifies the as found tolerance shall not exceed +\- 3% (2410-2510 psig). On May 9, 2008, PSV 2-RC-SV-2551B failed to lift within the as found set pressure requirement. The as found lift setting also did not meet the +/- 3% tolerance allowed by TS 3.1.A.3.b. This PSV exhibited an as found lift setpoint of 2399 psig which was 3.51% below the nominal value of 2485 psig. The as found PSV lift settings were evaluated and it was determined that the PSVs were capable of performing their safety function and operation with the low as found lift setpoints was within the limits assumed in the accident analysis. Therefore, the health and safety of the public were not affected. There were no significant safety consequences associated with this event. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) "Any operation or Condition prohibited by the plant's Technical Specifications".
2822008001 | Prairie Island 1 | 03/15/2008 | 05/14/2008 | ML08135032 | <strong>One Train of Auxiliary Feedwater Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2008, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 went to Mode 3 at 1059. On March 23, 2008, with Unit 1 in Mode 1, Technical Specification (TS) 3.7.5 Condition B was entered to conduct surveillance testing on the 11 turbine-driven auxiliary feedwater pump (TDAFWP). The test was stopped before it could be completed due to high temperature on the outboard turbine bearing. An evaluation concluded the 11 TDAFWP had been inoperable since before the plant entered Mode 3. The 11 TDAFWP is required per TS 3.7.5 to be operable when the unit reaches Mode 3. TS 3.7.5 Condition B requires the inoperable auxiliary feedwater (AFVV) train be restored to operable within 72 hours. If Condition B is not met, Condition C allows six hours to get to Mode 3 and 12 hours to get to Mode 4. Since Unit 1 was determined to be inoperable as a result of surveillance testing, and was in Mode 3 and was not brought to Mode 4 after 84 hours in Condition B as required by TS 3.7.5 Condition C, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. In addition, Unit 1 went from Mode 4 to Mode 1 with the 11 TDAFWP inoperable, which is also prohibited by TS. After troubleshooting, the pump was restored to operable status by adjusting the insulation on the turbine and nearby hot components and then successfully passed the surveillance test.
2822008002 | Prairie Island 1 | 07/31/2008 | 09/29/2008 | ML08273089 | <strong>Inadvertent Reactor Trip Caused by Failed Controller During Reactor Protection System Testing</strong><br /><i>Abstract:&nbsp;</i>On July 31, 2008, Prairie Island Nuclear Generating Plant (PINGP), Unit 1 was operating at 100 percent power. At 0817 CDT during performance of the quarterly analog protection functional test, Unit 1 reactor tripped. At the time of the trip the yellow channel over-temperature delta T (OT delta T) bistables were in the tripped condition as directed by the testing procedure when a red channel OT delta T reactor trip signal was generated due to a failed controller. The red channel OT delta T setpoint was not expected to be challenged nor was a reactor trip expected at any point during yellow channel OT delta T analog testing. All automatic actions for a reactor trip occurred as required with two exceptions: The Unit 1 turbine-driven auxiliary feedwater pump (11 TDAFWP) auto started as designed, but tripped 42 seconds later on low discharge pressure (see LER 1-08-03); and a Unit 1 Turbine 2 Reheat Stop Valve indicated intermediate vice closed due to a fault with the position indication. Operator response and recovery actions were as expected. The reactor trip was caused by a failed F delta Q proportional controller, which was subsequently replaced. Planned corrective actions include replacement of all similar controllers.
2822008003 | Prairie Island 1 | 07/31/2008 | 09/29/2008 | ML08273090 | <strong>Loss of AFW Safety Function and Condition Prohibited by Technical Specifications due to Mispositioned Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 31, 2008, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was operating at 100 percent power. At 0817 CDT Unit 1 reactor tripped (see LER 1-08-02 for details). Subsequent to the trip, the Unit 1 turbine-driven auxiliary feedwater pump (11 TDAFWP) auto started as designed, but tripped 42 seconds later on low discharge pressure. Local and remote indications did not indicate any abnormal operating conditions. A prompt investigation into 11 TDAFWP trip revealed the discharge pressure switch (PS-17700) was isolated. A time delay in the pump protective circuitry is designed to trip the pump on a continuing low discharge pressure condition. Monthly surveillances to test the operability of the 11 TDAFWP do not test the low discharge pressure trip function of the pump as the pump is in manual, which bypasses the low discharge pressure trip. The 12 motor-driven auxiliary feedwater pump (12 MDAFWP) started as designed and ran as needed throughout the event. Valve lineups were verified, the 11 TDAFWP was tested and restored to operable status. The subject valve was lock wired into the open position. Action will be taken to identify any similar components that can affect operability of safety systems and to revise procedures for locking and blocking.
2852008001 | Fort Calhoun | 03/15/2008 | 01/23/2009 | ML09028058 | <strong>Reactor Trip due to Turbine Control System Failure</strong><br /><i>Abstract:&nbsp;</i>The plant was operating at a reduced power level (nominal 85 percent) due to turbine control system problems. The station was preparing a troubleshooting plan when on March 15, 2008, at 0833 CDT, a reactor trip occurred. The operators entered Emergency Operating Procedure (EOP) 00 “Standard Post Trip Actions.” The main steam and feedwater system operated normally. All control rods inserted fully. The apparent cause of the reactor trip was the failure of a circuit board in the EHC control system resulting in the closure of turbine control valves CV-1 and CV-3. Closure of these valves results in a preemptive trip of the reactor due to the loss of load. The root cause of the circuit board failure was an improperly adjusted potentiometer, which resulted in a long term overcurrent condition to one of the transformers on the affected circuit board. The overcurrent condition resulted in the failure of the affected transformer. The failed circuit board was replaced. The output of the affected potentiometer was verified to be correctly adjusted. Post maintenance testing was performed on the EHC system to ensure its reliability.
2852008002 | Fort Calhoun | 03/15/2008 | 09/03/2008 | ML08248045 | <strong>Loss of Containment Integrity due to a Leaking Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2008 at 0833 CDT, following a plant trip from 85% power, relief valve CH-223 lifted and failed to reclose, thus causing a two to three gallon per minute reactor coolant system leak through the letdown system into the pressurizer quench tank. CH-223 is a two inch relief valve located on a branch line between two automatic containment isolation valves; therefore, this valve is classified as part of the containment boundary. The operators did not immediately recognize CH-223 as a containment boundary valve governed by technical specifications. On March 16, 2008 at 1355, operators determined CH-223 to be a containment boundary valve. At that time operators entered abnormal operating procedure AOP-12, "Loss of Containment Integrity" and Technical Specification 2.6(1)a. At 1401 the appropriate containment isolation valve was locked closed thus restoring containment integrity. The root cause of this event was determined to be the failure to translate containment integrity design requirements from the Final and Updated Safety Analysis Reports into appropriate plant operating procedures and guidance. Corrective actions include reviewing and revising the Updated Safety Analysis Report (USAR) and plant operating procedure.
2852008003 | Fort Calhoun | 03/21/2008 | 04/17/2009 | ML09135005 | <strong>Operation With Inoperable EDG and Opposite Train Feature Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2008, Fort Calhoun Station personnel confirmed that on March 21, 2008, the plant was in a configuration where an appropriate Technical Specification (TS) was not entered. At that time, entry into TS 2.5(1)D Limiting Conditions for Operation (LCO) was not made for the inoperability of two Auxiliary Feedwater (AFW) pumps or two inoperable AFW trains. Early on March 21, 2008, turbine driven AFW pump (FW-10) was declared inoperable. Entry was made into TS 2.5(1)B, a 24-hour LCO. At 1427, Diesel Generator (DG) 1 was taken out of service and declared inoperable for the performance of a surveillance test. Entry was made into TS 2.7(2)j for a single DG inoperable, a 7-day LCO. At 1445, DG-1 was subsequently declared operable. With FW-10 inoperable and the emergency power source for the motor driven AFW pump (FW-6) inoperable, FW-6 was also inoperable for the 18 minutes that DG-1 was inoperable. The root cause of this event is that concise guidance has not been developed to assist Operations on the required redundant equipment to FW-6 that is needed when DG-1 is considered inoperable. Following discovery of this event, interim guidance was provided to operations on application of TS. Additional actions will be administered by the corrective action system.
2862008001 | Indian Point 3 | 01/27/2008 | 03/27/2008 | ML08092052 | <strong>Technical Specification Prohibited Condition due to Exceeding the Allowed Completion Time for an Inoperable Safety Injection Pump Caused by a Failed Motor Supply Breaker</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2008, during an attempt to start the 31 Safety Injection Pump (SIP), the 31 SIP failed to start. Investigation into the cause of the failure determined that the 31 SIP 480 volt AC supply breaker had failed to close. Technical Specification (TS) 3.5.2, Emergency Core Cooling Systems (ECCS), Condition A was entered for one or more trains inoperable. A review of past operation of the 31 SIP determined it was last operated successfully on January 11, 2008. TS 3.5.2, Emergency Core Cooling Systems (ECCS), requires three trains of ECCS to be operable. The required action A.1 for TS 3.5.2 Condition A, one or more trains inoperable, is to restore the train(s) to operable within a completion time of 72 hours. The inoperable condition during past operation exceeded the 72 hour allowed completion time for TS 3.5.2 and the required actions were not performed resulting in a reportable condition. The cause of the breaker not closing was a failure of the breaker closing springs to charge. The failure of the breaker closing springs to charge was caused by a failure of the breaker charging motor brush assembly to remain intact due to a retaining screw becoming dislodged. Corrective actions included replacement of the breaker spring charging motor, breaker testing and return to service on January 27, 2008. A contributing cause was lack of an inspection requirement to check the breaker motor brush retaining screws. The breaker maintenance procedure was revised to require inspection of the breaker motor.
2862008002 | Indian Point 3 | 02/19/2008 | 04/18/2008 | ML08119008 | <strong>Loss of Single Train 31 Pressurizer Backup Heater Bank Required to Function to Shutdown and Maintain the Reactor in a Safe Condition Remote From Control Room</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2008, the Control Room received an alarm due to a trip of the 31 Pressurizer backup heater group. Investigation determined that the 31 backup heater group was inoperable due to failure of a transformer. Technical Specification (TS) 3.3.4, Condition A was entered for loss of a single remote shutdown heater. Reportability per 10 CFR 50.72(b)(3)(v)(A) was not identified at the time. The event is reported under 10 CFR 50.73 (a)(2)(v)(A) because the redundant backup heater banks cannot be credited as they are not part of the current licensing basis for remote shutdown under TS 3.3.4 and because other guidance indicating single trains not credited in the accident analysis need not be reported are not applicable to this situation. The apparent cause of the event was an insulation breakdown between the primary and secondary windings of the transformer. Corrective action was taken, by sending the transformer to a vendor for failure investigation. The failure investigation report will be used to determine the exact cause of the failure and this will be incorporated into the corrective action process. The safety significance is negligible since the redundant backup heaters could have been operated locally and safe shutdown (analyzed for a fire) does not require the use of pressurizer heaters.
2862008003 | Indian Point 3 | 03/25/2008 | 05/21/2008 | ML08149031 | <strong>Automatic Actuation of Emergency Diesel Generator 33 During Surveillance Testing Caused by Inadvertent Actuation of the Undervoltage Sensing Circuit on 480 Volt AC Safeguards Bus 5A</strong><br /><i>Abstract:&nbsp;</i>On March 25, 2008, during surveillance testing, Instrumentation & Control (I&C)Technicians inadvertently actuated the undervoltage sensing circuit on 480 volt AC, safeguards bus 5A causing the normal supply breaker to open and an automatic actuation of emergency diesel generator (EDG) 33 which started and re-energized the bus. In accordance with design, loads on bus 5A were stripped and then sequentially re-loaded back onto the bus. All systems performed as designed. The cause of the inadvertent actuation was procedure usage and adherence. During testing, an Agastat timer was discovered out of specification and an adjustment was performed but the incorrect Agastat was adjusted. Instead of stopping and notifying supervision, the test was continued and the correct Agastat was adjusted to spec. Then a re-adjustment began on the incorrectly adjusted Agastat but this action was out of sequence of the procedure. After the re-adjustment was completed, an attempted restoration to normal resulted in a degraded voltage condition sensed due to the bypass of procedure steps which required the closure of knife switch contacts which resulted in action of the undervoltage relays. Corrective actions include the conduct of procedure adherence reinforcement training, conduct of oral boards for I&C Supervisors, and incorporation of this event into the I&C re-qualification training program. The event had no effect on public health and safety.
2862008004 | Indian Point 3 | 08/04/2008 | 09/29/2008 | ML08284057 | <strong>Automatic Actuation of the Motor Driven Auxiliary Feedwater Pumps During Surveillance Testing Caused by Incorrect Test Jumper Connection Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2008, during performance of the monthly Reactor Protection Logic Channel Functional Test 3-PT-M13B1, Instrumentation & Control (I&C) technicians were testing Low-Low Steam Generator Water Level (SGWL) which required installation of jumper wires on terminal board logic contacts when a jumper became dislodged. When the I&C technicians completed installation of the second jumper they reinstalled the jumper that became dislodged and continued installation of the remaining jumpers. At this time Control Room Operators notified the technicians of an automatic start of the motor driven 31 and 33 Auxiliary Feedwater Pumps (AFWPs). The I&C technicians stopped the test, removed the jumpers, performed troubleshooting and testing and satisfactorily completed the test. The cause of the event was the AFWP Auto start actuation logic was satisfied when a relay was energized as a result of installation of a jumper on an incorrect terminal of the Low-Low SGWL logic circuit. The incorrect jumper connection was due to personnel error as a result of ineffective use of Human Performance (HP) tools because standards and expectations have not been adequately reinforced in I&C technicians. Corrective actions included coaching I&C personnel on use of HP tools, discussion with I&C Supervision of the event, lessons learned, and management expectations for procedure use and adherence and use of proper clips. A Maintenance Stand-down was developed and conducted on details of the root cause events in 2008 to include their causes, HP traps, and HP tools used ineffectively. HP Simulator High Intensity training will be performed. A needs analysis will be performed for the frequency of Human Performance refresher training. The event had no effect on public health and safety.
2862008005 | Indian Point 3 | 09/01/2008 | 10/28/2008 | ML08312037 | <strong>Technical Specification Prohibited Condition Due to Exceeding the Allowed Completion Time for an Inoperable Isolation Valve Seal Water System Due to an Out of Position Valve Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2008, during the performance of Check Off List 3-COL-CB-004, Operations discovered valve IV-1692 of the Isolation Valve Seal Water (IVSW) system out of position with a Temporary Modification (TM) tag applied and the valve closed. The required position of valve IV-1692 is open but was discovered closed rendering the associated IVSW header inoperable. Technical Specification 3.6.9, "Isolation Valve Seal Water System (IVSWS)," Condition A, One IVSWS header inoperable, required action A.1, is to restore IVSW to operable within 7 days. Investigations determined that a temporary modification installed in March 2007, required the position of the valve to be closed and during system restoration the valve was required to be opened and TM tags removed. The condition is reportable because the inoperable header exceeded the TS 3.6.9 allowed completion time. The apparent cause was procedure use and adherence and inadequate error detection practices. Corrective actions include; restoration of IV- 1692 to locked open and tag removal. Maintenance personnel will also be briefed on the event and lessons learned, counseled on the expectations and standards for procedure adherence and effective use of Human Performance tools such as self checking, good verbal communications and a good questioning attitude, and coached on the TM process. Human Performance simulator high intensity training will be performed for Maintenance personnel. The event had no effect on public health and safety.
2862008006 | Indian Point 3 | 10/09/2008 | 10/29/2009 | ML09314025 | <strong>Automatic Actuation of an Emergency Diesel Generator and Two Auxiliary Feedwater Pumps During Surveillance Testing due to Inadvertent De-Energization of the Normal Supply Breaker to 480 Volt Safeguards Bus 6A</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2008, Instrumentation & Control (I&C) Technicians were performing surveillance testing, when the normal power supply breaker for 480 Volt AC safeguards bus 6A inadvertently opened, causing the bus to de-energize. In accordance with design, loads on bus 6A were stripped and then sequentially re-loaded back onto the bus. The bus undervoltage control circuitry caused an automatic actuation of emergency diesel generator (EDG) 32 which started and re-energized the bus, actuation of motor driven auxiliary feedwater pump (AFWP) 33 and steam driven AFWP 32. All systems performed as designed. AFW was injected into the steam generators (SG) that resulted in a 1-2% change in SG level, an approximate 0.1% increase in reactor power and no control rod movement. The initial root cause analysis (RCA) did not identify a cause but determined the breaker trip was caused by energizing its shut trip coil. The most probable cause was an intermittent fault in the digital volt meter (DVM) used for the test. Subsequent analysis by an independent vendor determined the DVM operated properly in all functions and ranges and calibration results were within specifications and no anormalies were noted. Troubleshooting and testing for a similar event on January 9, 2009, did not identify a cause. A revised RCA failed to identify a specific cause but identified a probable cause as a meter lead short between terminals of degraded grid time delay relay (62-1/6A). Corrective actions included revision of the surveillance test to require the use of different test meter leads and brief of personnel on potential of test leads causing a short circuit. The event had no effect on public health and safety.
2872008001 | Oconee 3 | 11/07/2008 | 01/07/2009 | ML09012043 | <strong>Unit 3 Trio due to Control Rod Drive System Processor Failure</strong><br /><i>Abstract:&nbsp;</i>At 0834 on November 7, 2008 Oconee Unit 3 experienced a reactor trip. The trip was the result of the Control Rod Drive (CRD) processor modules P1 and P2 experiencing a kernel fault caused by an inability to decode a clock signal inputted to the processors with a day value of zero. This resulted in both CRD system processors failing simultaneously, causing a loss of power output from the single rod power supplies and control rods to drop into the core. The processor failure also caused relays to actuate and produce a Reactor Trip Confirm (RTC) signal which in turn initiated a turbine trip and generator lockout signal. The Reactor Protection System (RPS) received a Loss of Main Turbine Anticipatory Trip Signal and tripped the CRD breakers. The unit responded as expected. The Emergency Operating Procedure was entered, subsequent actions completed, and a transfer to the unit shutdown procedure was made without complication. Appropriate post-trip reviews were performed and recovery actions completed per station procedures. The clock signal was disconnected from the CRD system P1 and P2 processors on all units to prevent recurrence of this event. Unit 3 was returned to service on November 9, 2008. This event is considered to have no significance with respect to the health and safety of the public.
2892008001 | Three Mile Island 1 | 02/12/2008 | 06/09/2008 | ML08170023 | <strong>Decay Heat River Water System Pump (DR-P-1B) Failed to Start</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2008, it was discovered that the "B" Decay Heat River Water System Pump (DR-P-1 B) was inoperable from January 25, 2008 till February 13, 2008. This conclusion was reached following evaluation of test data on a failed X relay coil for the circuit breaker of DR-P-1B. At approximately 2250 on February 12, 2008, the "B" Decay Heat River Water System Pump (DR-P-1 B) was being started in accordance with procedure OP-TM-533-402, "Operating DR-P-1B for Other Than Decay Heat Removal Operations," and the pump failed to start. DR-P-1B was declared inoperable, placing TMI-1 in an unplanned 72 hour shutdown Limiting Condition of Operation (LCO). Troubleshooting determined that the coil for the DR-P-1B breaker control X relay was open circuited. The function for the control X relay is to control the operation of the breaker closing solenoid and to provide the breaker anti-pumping control feature. The anti-pumping feature allows only one closing attempt for the breaker as long as a close signal is present. The control relay for the breaker was replaced and DR-P-1B was successfully returned to service at approximately 1032 on February 13, 2008. The apparent cause of the X relay open circuit was a coil manufacturing defect. This relay failure is considered to be an isolated occurrence. The submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73 (a)(2)(i)(B), "a condition prohibited by Technical Specifications.
2932008001 | Pilgrim | 01/10/2008 | 03/07/2008 | ML08078050 | <strong>Failure to Meet Technical Specification Requirements for Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2008 between 0700 and 1600 hours, on-line testing of the Reactor Building Isolation Control System (RBICS) ventilation dampers was performed. This testing identified that in the closed position, damper AO-N-78 did not fully close. The damper was reported to have a one-half inch gap opening across two of the four damper blades and did not meet Technical Specification requirements for full damper closure. Subsequently, Technical Specification compensatory actions to restore operability or to secure the damper were not taken for approximately 96 hours. Reactor power was at 100% prior to and during the event. The cause of not performing the Technical Specification compensatory actions for 96 hours is failure of non-licensed, utility workers to report the damper closure failure to the Control Room. Corrective action was taken to repair the damper. Corrective actions planned include development of enhanced damper maintenance procedure instructions, establishment of a damper preventative maintenance repetitive task, and overhaul of the RBICS isolation damper actuators. Additional corrective actions planned include event discussions with operations, maintenance and engineering personnel. The focus of these discussions will be to address pre-job brief adequacy; test failure reporting responsibilities; and to ensure that sufficient detail is included in maintenance work plans. The event posed no threat to public health and safety.
2932008002 | Pilgrim | 01/11/2008 | 03/11/2008 | ML08091002 | <strong>Failure to Meet Technical Specification Requirements for Undervoltage Relay Trip Setting</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2008, the as-found, post-service, calibration test of the GE Type RAV11.B AC undervoltage (UV) 127-A5/1 and 127-A5/2 relays determined that the undervoltage relays that had been installed on the A5 safety-related 4KV bus from May 2, 2005 to June 11, 2007 exceeded the Technical Specification (TS) required set point range of 20-25% specified in TS Table 3.2.B. The post-service calibration test determined actual set points were 27.17% and 30.29% of rated bus voltage, respectively. Therefore, it was concluded from May 2, 2005 to June 11, 2007, Entergy Pilgrim did not meet the TS requirement for the undervoltage protection function for the safety-related 4KV safety-related bus A5. The cause of the as-found relay settings was determined to be an improper calibration method utilized prior to the relay installation in May 2005. The immediate corrective actions taken included verification that the installed undervoltage relays in the safety-related A5 bus met the TS requirements and verification that undervoltage relays on safety-related bus A6 were properly calibrated. The corrective actions planned include the use of a new testing apparatus, a revision to the calibration procedure to incorporate use of a new calibration methodology and specialized training. The extent of condition review confirmed that the problem was limited only to the 127-A5/1 and 127-A5/2 relays. The event posed no threat to public health and safety.
2932008003 | Pilgrim | 10/06/2008 | 11/20/2008 | ML08337050 | <strong>RCIC System Declared Inoperable During Surveillance Testing due to Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2008, at 2224 hours, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable. This action was taken because the RCIC system received an inadvertent Group 5 isolation signal during the performance of an Instrumentation and Control (I&C) surveillance. All isolations went to completion. RCIC was not operating at the time of the surveillance. The Group 5 isolation was reset and RCIC was placed in stand-by line up. The cause of the event was due to an error introduced into the recently revised surveillance procedure. The restoration section of the procedure was sequenced incorrectly in that the procedure required the removal of control relay contact blocking devices (boots) prior to the resetting of the RCIC automatic isolation signal. Immediate corrective action taken included the revision of the subject l&C surveillance procedure and an extent review of similar surveillance procedures. Corrective actions planned include the review of the procedure revision process and enhancements to the associated training programs. The event posed no threat to public health and safety.
2932008004 | Pilgrim | 10/21/2008 | 12/10/2008 | ML08359034 | <strong>High Pressure Coolant Injection System Inoperable due to Undervoltage Relay Failure in Valve Power Supply Circuit</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2008, at 1944 hours, with the plant operating at 100% power, the Control Room received a Motor Control Center (MCC) D9 trouble alarm. Operators noted that the indicator light for the High Pressure Coolant Injection (HPCI) Injection Valve MO-2301-8 was extinguished. Investigation at the MCC revealed that the 125V DC valve control power circuit for the normally closed HPCI Injection Valve MO-2301-8 was deenergized due to failure of the undervoltage relay in the 250V DC power feed to the valve motor operator. HPCI was declared inoperable and applicable Technical Specification (TS) Limiting Conditions for Operation (LCO) were applied. The undervoltage relay was replaced, and HPCI was returned to operable standby status at 0404 hours on October 22, 2008. The most probable root cause of the event was identified to be an isolated premature failure of the undervoltage relay due to a manufacturing defect. Immediate corrective actions taken included the replacement of the undervoltage relay. Corrective actions planned include destructive failure analysis of the undervoltage relay; and engineering evaluation of installed DC powered motor operated valve undervoltage relays and associated preventative maintenance requirements. The event posed no threat to public health and safety.
2932008005 | Pilgrim | 11/20/2008 | 01/08/2009 | ML09014033 | <strong>HPCI System Declared Inoperable During Surveillance Testing due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2008, at 1657 hours, the High Pressure Coolant Injection (HPCI) System was declared inoperable with the plant at 100% power. No other plant equipment was out of service at the time. This action was taken because the HPCI System isolated on a Group IV signal when Instrumentation and Control (I&C) Technicians were performing a scheduled surveillance test of temperature switches in the HPCI steam leak detection circuitry. This isolation was not part of the planned evolution. HPCI was not operating at the time of the surveillance and all isolations went to completion. The Group IV isolation was reset and HPCI was placed in stand-by line up at 1805 hours on November 20, 2008. The root cause of the event was identified to be less than adequate application of fundamental human performance tools on the part of an l&C Technician, specifically use of situational awareness relative to task analysis, job site review, questioning attitude, and stopping when unsure. Immediate corrective actions taken included verifying that all temperature switches that were tested were left in the proper configuration. In addition, appropriate management attention was directed to the individual(s) involved including disciplinary action. Corrective actions planned include the revision of temperature switch procedures to include formality to the concurrent verification process. The event posed no threat to public health and safety.
2932008006 | Pilgrim | 12/19/2008 | 02/12/2009 | ML09057004 | <strong>Automatic Scram Resulting from Switchyard Breaker Fault During Winter Storm</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2008 at 1831 hours during a severe winter storm an automatic reactor scram occurred with the plant operating at 100% power. The automatic scram initiated from a valid Reactor Protection (RPS) Signal resulting from fast closure of the turbine control valves due to actuation of the main transformer bus differential relay (87B/MT). Automatic response from the main transformer protective relay scheme included opening 345 kV circuit breakers ACB-104 and ACB-105; main turbine trip; and fast transfer of 4.16 kV power from the Unit Auxiliary Transformer (UAT) to the Startup transformer (SUT). The 120 V ac safeguards panels (Y3/31 and Y4/41) de-energized after the UAT to SUT power transfer. The direct cause of the event was an electrical fault resulting from conductive snow and ice build-up on the nonconductive porcelain surfaces of the ACB-105 "A" phase generator side bushing. The direct cause of power loss to the safeguards panels was high in-rush current and transformer (X55) input breaker trip to Y3/31; and transformer (X56) tap control board malfunction to Y4/41. Corrective actions were taken to evaluate and assess switchyard circuit breaker and main transformer equipment damage. The bushing on the "A" phase generator side feed on ACB-105 was replaced. The input breaker to X55 and the tap control board to X56 were replaced. Corrective actions planned include analysis of equipment design modifications to reduce flashover and ground fault events in the switchyard. In addition, the input breakers to X55 and X56 will be modified and replaced, and a vendor evaluation of the X56 tap control board will be completed. The event posed no threat to public health and safety.
2932008007 | Pilgrim | 12/20/2008 | 02/12/2009 | ML09057051 | <strong>Momentary Loss of all 345kv Off-Site Power to the Startup Transformer from Switchyard Breaker Fault</strong><br /><i>Abstract:&nbsp;</i>On Saturday, December 20, 2008 at approximately 1045 hours and while in a Hot Shutdown condition from the previous day's reactor scram (Reference LER 2008-006-00), Pilgrim Station experienced a momentary loss of all 345kv off-site power to the Startup Transformer (SUT) X4. As a result, the following safety system automatic actuations occurred: Reactor Protection System (RPS) actuation (all control rods were previously inserted), start of both Emergency Diesel Generators (EDG) and loading of their respective emergency buses, actuation of Primary Containment Isolation Systems (PCIS) Groups I, II, VI and Reactor Building Ventilation. The High Pressure Coolant Injection (HPCI) System was placed in service for reactor pressure control, and Reactor Core Isolation Cooling (RCIC) System was placed in service for reactor level control. All plant systems functioned as designed and expected. The direct cause of the momentary loss of all 345kv off-site power was a Phase B to ground fault on the switchyard Line 355 bus section (Bridgewater Station) which caused ACB-102 and ACB-103 breakers to trip. The ACB-103 breaker tripped because it received a remote transfer trip signal from Auburn Street Station owned by the transmission system operator, National Grid (NGRID). The ground fault was cleared by the ACB-102 breaker, and the Bridgewater Station breakers (the ACB-105 breaker was already open from the previous day's reactor scram), however, the ACB-103 breaker should not have tripped. Tripping of ACB-102 and ACB-103 resulted in a loss of the SUT and transferring of the safety busses to the EDGs. Immediate corrective actions taken included a visual inspection for damage which was completed with satisfactory results and a successful carrier test was performed on the Line 342 to and from Pilgrim Station. Additionally, a ground overcurrent relay was reset at the Auburn Street Station. Corrective actions planned include working with local Transmission and Distribution Companies to review and reset line protection relays based on investigation results. The event posed no threat to public health and safety.
2962008001 | Browns Ferry 3 | 05/05/2008 | 07/07/2008 | ML08189056 | <strong>Unanticipated Auto-Start of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2008, at approximately 0332 hours Central Daylight Time (CDT) Emergency Diesel Generators (EDGs) 3EC and 3ED auto-started and tied to their respective shutdown boards due to an under voltage condition. Operations was in the process of returning the Unit 3 4KV Unit Board 3B to the normal supply in accordance with Operating Instruction 0-OI-57A, Switchyard and 4160V AC Electrical System, when the board failed to transfer. The loss of power to Unit Board 3B resulted in a loss of power to 4KV Shutdown Boards 3EC and 3ED, 480V Reactor Motor-Operated Valve (RMOV) Board 3B, and Reactor Protection System 3B (RPS) [JC] power supply. Due to the loss of power on the shutdown boards, EDGs 3EC and 3ED started and tied to their respective shutdown boards. Unit 3 also received Primary Containment Isolation System (PCIS) Groups 3 and 6 isolations and actuations. A coincidental upscale trip of the 3A intermediate range monitor (IRM), which resulted in RPS Channel 3A half scram, in combination with the de-energizing of the RPS Channel 3B resulted in an unexpected full reactor scram. The Standby Gas Treatment (SGT) and Control Room Emergency Ventilation (CREV) systems initiated as expected. By 0352 hours CDT the reactor scram and PCIS logic was reset, the SGT and CREV Systems were returned to standby readiness. By 0944 hours CDT power was restored to 4KV Shutdown Boards 3EC and 3ED; likewise, EDGs 3EC and 3ED were secured. TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(iv)(A) as any event of condition that resulted in manual or automatic actuation of any system listed in paragraph 10 CFR 50.73 (a)(2)(iv)(B).
2962008002 | Browns Ferry 3 | 06/02/2008 | 07/31/2008 | ML08214019 | <strong>Main Steam Relief Valve As Found Setpoint Exceeded Technical Specification Lift Pressure</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2008, TVA determined that 7 of the 13 Main Steam Relief Valves (MSRVs) [SB], removed from Unit 3 following Cycle 13 operation mechanically actuated at pressures greater than 3 percent above their Technical Specifications (TS) setpoint, thus inoperable. One valve exhibited leakage past the seat, and the lift pressure could not be verified. Unit 3 TS limiting condition for operation (LCO) 3.4.3 requires that twelve (12) MSRVs be operable in reactor modes 1, 2, and 3. If less than twelve MSRVs are operable, the unit is to be placed in Mode 3 hot shutdown within 36 hours. As such, it is probable that Unit 3 operated outside the TSs longer than allowed by the TSs. Therefore, TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant’s Technical Specifications.
2982008001 | Cooper Station | 08/09/2008 | 10/03/2008 | ML08281040 | <strong>Turbine Reheat Stop Valve Failure Results in Manual Scram</strong><br /><i>Abstract:&nbsp;</i>At 0025 Central Daylight Time (CDT) on August 9, 2008, reactor power was lowered from 85% to 69% to perform main turbine stop valve closure and steam valve functional testing. At 0156 CDT, during the first reheat/stop valve (1A) test, while reheat/stop valve had failed to reopen, a Moisture Separator (MSR) 'C' high level alarm occurred. In accordance with the alarm procedure for MSR high level, the plant was manually scrammed. Control rods fully inserted, and a Primary Containment Isolation System Group 2 isolation occurred. Plant and mitigating system responses were as expected. Risk significance was negligible. The event was caused from a manufacturing defect that caused the reheat/stop valve test solenoid to jam. The root cause was attributed to a practice of performing reheat/stop valve testing at a power level which could result in a MSR high level condition should a reheat/stop valve test solenoid malfunction. Action was taken to prevent recurrence by deleting sections in the functional test procedure for energizing the reheat/stop valve test solenoids.
2982008002 | Cooper Station | 07/07/2008 | 11/24/2008 | ML08337030 | <strong>Technical Specification Prohibited Condition due to Safety Relief Valve Test Failure</strong><br /><i>Abstract:&nbsp;</i>During safety relief valve (SRV) as-found testing, performed July 7 through July 9, 2008, by Wyle Laboratories, one of eight Target Rock SRV pilot valve assemblies failed to lift within its Technical Specification (TS) lift set point of 1100 +/- 33.0 psig. The SRV lifted at 1165 psig. Two subsequent lifts were performed and were within the TS pressure set point tolerance. This testing was performed to satisfy the TS surveillance for SRV pilot valve assemblies removed during Refueling Outage 24. Cooper Nuclear Station (CNS) was in Mode 1 at 100% power at the time of the discovery. The remaining SRV pilot valve assemblies tested within their TS lift set point tolerances. A subsequent inspection of the failed SRV pilot valve assembly revealed corrosion bonding, a recurring problem at CNS and in the industry, was the failure mechanism for the high lift pressure. The performance of the two-stage Target Rock pilot-actuated valves in the current design application has not been successful in meeting the as-found lift test requirements contained within the current CNS TS. This event is considered to have negligible safety significance.
2982008003 | Cooper Station | 11/30/2008 | 01/22/2009 | ML09028021 | <strong>Control Room Envelope Door Found Open Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2008, at 01:58 Central Standard Time (CST), Cooper Nuclear Station (CNS) Operations declared the Control Room Emergency Filter (CREF) system inoperable due to failure of a control room envelope boundary door to fully close as required. Operations investigated the condition and found a piece of steel protruding from the bottom of the door which prevented it from fully closing. CNS returned the door to a fully closed position and declared the CREF system operable at 02:14 CST. The door was subsequently repaired on November 30, 2008, at 16:48 CST. The mechanistic failure was caused by material inadvertently left in the door during fabrication. This material had fallen through a gap in the bottom of the door and obstructed it from closing. The root cause was that the expectation to self-check door closure was not communicated and reinforced. A corrective action is established to develop and implement a change management plan to address expectations for site personnel to self-check door closure. Additional corrective actions are to revise applicable door inspection procedures. This event was not risk significant.
3022008001 | Crystal River 3 | 01/23/2008 | 03/20/2008 | ML08087042 | <strong>Software Change Causes Inoperability of Redundant Core Subcooling Monitors for Longer than TS Allowable</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2008, while operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER, at Progress Energy Florida, Inc. Crystal River Unit 3 (CR-3), during the performance of Surveillance Procedure SP-144C, "Core Exit Thermocouple Calibration," the Core Subcooling Monitors would indicate out of range above a simulated Core Exit Thermocouple (CET) input temperature of 1250 degrees Fahrenheit (F). As part of the extent of condition investigation, SP-144C was performed for the Channel B recorder and the same failure mechanism was identified. At 1717 on January 25, 2008, both Core Subcooling Monitors were determined to be inoperable. These instruments are OPERABLE when accurately indicating between 0 to 2500 degrees F. Improved Technical Specification (ITS) 3.3.17, "Post Accident Monitoring (PAM) Instrumentation," Condition C, allows 7 days for restoration if one or more functions with two required channels inoperable. The condition was determined to have existed since the new Safety Parameter Display System (SPDS) multiplexer server Modbus driver was installed on August 13, 2007. This exceeded the ITS completion time and as such, this report is being submitted under 10 CFR 50.73(a)(2)(i)(B). The cause for this condition was that the responsible engineer did not identify the impact of the software change to the system and require full range, post modification testing for this function following implementation of the Engineering Change. The condition was corrected on January 26, 2008 through a software change. This condition does not represent a reduction in the public health and safety. A previous similar occurrence has not been reported to the NRC.
3022008002 | Crystal River 3 | 03/01/2008 | 04/29/2008 | ML08122024 | <strong>Emergency Feedwater Actuation On Low Steam Generator Level Due To Feedwater Pump Speed Tuning</strong><br /><i>Abstract:&nbsp;</i>At 04:27 on March 1, 2008, while operating in MODE 1 (POWER OPERATION) at approximately 20 percent RATED THERMAL POWER, Progress Energy Florida, Inc., Crystal River Unit 3 (CR-3) was being shut down to replace a reactor coolant pump seal when an Emergency Feedwater Initiation and Control (EFIC) System actuation occurred. Feedwater (FW) flow to both Once Through Steam Generators (OTSGs) began oscillating and an EFIC actuation was received on low level in both OTSGs as the Steam Generator/Reactor Demand was being lowered to zero in accordance with OP-209A, "Plant Shutdown and Cooldown." EFIC actuated as expected by automatically starting Emergency Feedwater pumps EFP-2 and EFP-3 and aligning Emergency Feedwater to both OTSGs. Required equipment operated as designed. The root cause for this event was a programmatic weakness in that the impact on other systems was not understood when the Feedwater pump FWP-2A Integrated Control System (ICS) Bailey module IC-5714-FW calibration data sheet was revised prior to Refueling Outage 15. ICS Bailey module IC-5714-FW was re-calibrated on March 21, 2008. This condition does not represent a reduction in the public health and safety. Loss of FW is an event analyzed and bounded by the CR-3 Final Safety Analysis Report accident analysis. A previous similar occurrence has not been reported to the NRC.
3022008003 | Crystal River 3 | 08/24/2008 | 12/10/2008 | ML08359028 | <strong>Manual Reactor Trip due to Main Feedwater System Oscillations Caused by an Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>At 15:53 on August 24, 2008, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at approximately 60 percent RATED THERMAL POWER, when the reactor was manually tripped. At 15:37, the Condensate Pump CDP-1A magnetic coupling became uncoupled. Delays in rapid power reduction led to a low Deaerator (FWHE-1) level and eventual cavitation of the Main Feedwater (FW) System booster pumps and Main FW pumps. The cavitation caused a loss of FW flow control to the Once-Through Steam Generators. This loss of flow control led to the decision to manually trip the reactor. The root cause for this event was original plant design failing to provide adequate alarms to the operating crews to promptly identify Condensate Pump failures. Required equipment operated as designed during the manual reactor trip. Loss of FW is an analyzed event bounded by the CR-3 Final Safety Analysis Report accident analysis. This condition does not represent a reduction in the public health and safety. Operating crews were trained on this event. Compensatory measures to alert the operating crew of a loss of a Condensate Pump were established. Design options are being evaluated to alert the operating crew of Condensate Pump failures. A previous similar occurrence has not occurred or been reported to the NRC.
3022008004 | Crystal River 3 | 12/05/2008 | 01/28/2009 | ML09036051 | <strong>Motor-Operated Main Feedwater Isolation Valve Inoperable due to Motor Rotor Oxidation/Corrosion</strong><br /><i>Abstract:&nbsp;</i>At 02:41, on December 5, 2008, Progress Energy Florida, Inc., Crystal River Unit 3 was in MODE 1 (POWER OPERATION) at approximately 50 percent RATED THERMAL POWER when the breaker for an A Train motor-operated Main Feedwater Isolation Valve (FWV-30) motor tripped soon after receiving a close signal. This occurred during a scheduled power reduction to replace the Main Feedwater Pump FWP-2B controller. Improved Technical Specification (ITS) 3.7.3 requires two Main Feedwater Isolation Valves in each Feedwater System flow path to be operable with at least one Main Feedwater Isolation Valve capable of isolating Feedwater within the required isolation time while in MODES 1, 2 and 3. FWV-30 was determined to be inoperable for a period longer than allowed by ITS 3.7.3. The remaining Main Feedwater Isolation Valves were operable. This condition does not represent a reduction in the public health and safety. The cause for the motor-operated valve failure was oxidation/corrosion of the magnesium rotor. A contributing cause was an inspection program, put into place to monitor the degradation mechanisms associated with magnesium rotor motors, that did not predict the FWV- 30 failure. The motor-operated valve motor has been replaced. This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B). A previous similar occurrence was reported in LER 50-302/2005-004-00.
3052008001 | Kewaunee | 09/11/2008 | 11/07/2008 | ML08324008 | <strong>Pressurizer PORV and Reactor Coolant System Vent Valves Appendix R Spurious Operation Concern</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2008, while responding to a question during a NRC Triennial Fire Protection Inspection, the control cabling for pressurizer PORV PR-2B was found to be vulnerable to spurious operation due to hot shorts in the event of a fire in the relay room as defined in NRC guidance and NRC endorsed NEI guidance for circuit analysis for reactor coolant system high-low pressure interfaces. Additionally, on October 15, 2008, a similar condition was identified for pressurizer and reactor head vent valves. A fire in the relay room would require use of an Appendix R fire shutdown procedure that would deenergize the PR-2B and vent valves' 125-volt direct current (DC) circuits. The procedural action to deenergize the valves was previously accepted by the NRC as a post-fire mitigating action for these high-low pressure interface valves. Subsequently, modifications were made to the valves' cabling to enhance protection from a hot short by routing cabling in dedicated conduit. However, some of the cabling was left in cable trays in the relay room. Spurious opening of the valves could be postulated as follows: Control cable for the valves has fire damage resulting in an internal short between conductors; and, an external cable-to-cable hot short occurs with the power supply cable and another energized DC cable in the same cable tray (two concurrent DC hot shorts of the proper polarity from the same battery). This event is possible because current procedural guidance does not deenergize all of the DC cables in the cable tray containing the PORV and vent valve control and power cables.
3052008002 | Kewaunee | 10/30/2008 | 12/18/2008 | ML08366015 | <strong>Blocked Open Steam Exclusion Door Results in Postulated Inoperability of Safety Systems</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2008, a Dominion Energy Kewaunee (DEK) technician was routinely transiting through a steam exclusion door (Door 140), when the door's weather stripping partially dislodged and became wedged in the staircase grating. This prevented the door from immediately shutting until the technician physically lifted the stripping out of the way to shut the door. The door was in this condition for less than one minute. Upon shutting Door 140, even with the weather stripping degraded, the steam exclusion function for the zone being supported was fully met. Kewaunee Power Station (KPS) Technical Requirements Manual (TRM) 3.0.9, "Steam Exclusion System", directs that all equipment supported by a nonfunctional steam exclusion barrier be declared inoperable immediately. Door 140 supports multiple trains of emergency core cooling systems (ECCS) and other equipment required by Technical Specifications (TS). With Door 140 blocked open (albeit briefly), TRM 3.0.9 required all equipment supported by that door to be declared inoperable. Since multiple out of service trains is technically an unanalyzed condition, this condition is being conservatively reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), as a condition that resulted in the nuclear power plant being in an unanalyzed condition. Additionally, since both trains of emergency core cooling were postulated to be inoperable, this condition would also meet the reporting criteria of 10 CFR 50.73 (a)(2)(v)(B), any event or condition that could have prevented the fulfillment of a safety function.
3052008003 | Kewaunee | 12/30/2008 | 02/27/2009 | ML09070012 | <strong>Door Bottom Seal Failure Results in Inoperability of Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On December 30, 2008 with the plant at full power, a Dominion Energy Kewaunee, Inc. plant operator was transiting through a door that was both a steam exclusion barrier and control room exclusion zone barrier (Door 141) when the seal at the bottom of the door separated from the door. The door was in this condition for forty-four minutes while the bottom seal was replaced. The opening caused by the missing seal exceeded the allowable opening size for the door's steam exclusion and control room exclusion zone barrier functions. Technical Specification operability requirements for the control room post-accident recirculation system were impacted based on the control room post-accident habitability analysis assumption for air inleakage to the control room envelope and the control room itself from the nonfunctional steam exclusion and control room exclusion zone barrier. The control room post-accident recirculation system and control room exclusion zone were declared inoperable. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear power plant being in an unanalyzed condition. Additionally, since both trains of the control room postaccident recirculation system were inoperable, this condition also meets the reporting criteria of 10 CFR 50.73 (a)(2)(v)(B), any event or condition that could have prevented the fulfillment of a safety function.
3062008001 | Prairie Island 2 | 07/31/2008 | 01/19/2009 | ML09021024 | <strong>Unanalyzed Condition Due to Both Trains of Component Cooling Susceptible to a Postulated High Energy Line Break</strong><br /><i>Abstract:&nbsp;</i>On July 31, 2008, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was operating at 100 percent power. At 1345 CDT Prairie Island staff declared both trains of the Unit 2 component cooling water (CC) system inoperable due to the discovery that a postulated Unit 2 high energy line break (HELB) in the Turbine Building could fail a CC line that would affect both trains of the Unit 2 CC system. With both trains of CC declared inoperable, PINGP staff entered Technical Specification (TS) Limiting Condition for Operability (LCO) 3.0.3. PINGP staff isolated the CC line in the Turbine Building at 1612 on July 31, 2008, which returned Unit 2 CC to operable status. The as-found condition was an original design issue uncovered during walkdowns in support of turbine building CC system seismic qualification. The planned corrective action is to modify the cooling source to the cold lab and turbine building sample coolers to reroute or eliminate CC lines from the Turbine Building.
3062008002 | Prairie Island 2 | 10/30/2008 | 12/19/2008 | ML08357057 | <strong>Unit 2 Manual Reactor Trip During Low Power Physics Testing</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2008, at 1414 CDT during reactor physics testing following a Unit 2 outage, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was just above the point of adding heat (POAH) when an urgent failure alarm was received while moving Bank A control rods inward. It was noted that Group 1 control rods in Power Cabinet 21AC unexpectedly stopped moving while Group 2 control rods in Power Cabinet 22AC continued inward rod motion. Operators stopped Group 2 control rods and initiated a manual reactor trip. All systems operated as expected following the trip and operator response and recovery actions were as expected. Subsequent troubleshooting identified that a Phase C fuse in the 21AC Moveable Gripper bus duct disconnect switch had blown. Troubleshooting also identified that the blown fuse was not fault related and likely due to a random failure. All 21AC moveable gripper bus duct disconnect switch fuses were replaced on October 31st, 2008 at approximately 0031 CDT thereby restoring full functionality of bank A control rods. In addition, all of the moveable gripper bus duct disconnect-switch fuses for the other two power cabinets (22AC and 21BD) in Unit 2 were replaced to ensure that the extent of condition was corrected. Reactor startup and physics testing were resumed on October 31, 2008 at 1115 and Unit 2 reactor was returned to criticality on October 31, 2008 at 1311 CDT.
3112008001 | Salem 2 | 03/20/2008 | 05/19/2008 | ML08149032 | <strong>As-Found Pressurizer Safety Valve Lift Setpoint Exceeds Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2008, during Salem Unit 2 Refueling Outage 2R16, in Mode 6, a Pressurizer Safety Valve (PSV) failed its as-found surveillance test. The valve was being tested in accordance with the requirements of the Technical Specifications (TS) and the ASME OM-1987, Part 1, Requirements for lnservice Performance Testing of Nuclear Power Plant Pressure Relief Devices. After the failure of the first PSV, the remaining two PSVs were tested and found within TS lift tolerance. The apparent cause of the safety valve lifting low was valve spring relaxation during its first operational service cycle. All PSVs were replaced with refurbished spare valves that have been tested to a ±1% setpoint pressure tolerance. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
3112008002 | Salem 2 | 05/09/2008 | 07/08/2008 | ML08199024 | <strong>Salem Unit 2 Manual Reactor Trip due to High Level on 23 Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2008, Salem Unit 2 was at approximately 47% power and ramping up to 100% following its sixteenth (2R16) refueling outage. At 09:44 the Salem Unit 2 control room observed that there was no power to the circulating water traveling screens. A power reduction was initiated in accordance with operating procedures. Shortly following the removal of the main turbine from service, at approximately 25% power, control room personnel noticed the main feedwater regulating valve (23BF19) had swapped to manual and 23 Steam Generator level was increasing. With the regulating valve in manual control and level in the Steam Generator rising, the Unit 2 reactor was ordered tripped at 10:59. The cause for the 23BF19 swapping to manual shortly after the turbine trip was determined to be the result of the 23 Steam Generator steam flow input signals decreasing (spiking) to below the low sensor limit. The steam flow signal spike was caused by a pressure wave initiated from the main turbine stop valves closing as a result of the manually initiated turbine trip. Corrective actions included restoring power to the circulating water screens, and PSEG will revise the Unit 1 and 2 ADCFS low sensor limits (for DP transmitters) to consider the lowest possible output that can be experienced. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...."
3112008003 | Salem 2 | 05/12/2008 | 07/11/2008 | ML08204058 | <strong>Technical Specification 3.0.3 Shutdown due to All Steam Flow Channels Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2008, Salem Unit 2 was at approximately 84% power when power ascension was placed on hold. During refueling outage 2R16 the steam generators were replaced. Based on review of plant indications, a determination was made that all eight main steam flow reactor protection channels were reading lower than expected. The steam flow channels were reading up to 14% lower than the feedwater flow channels. As a result of these lower than expected indications, the steam flow channel input into the safety injection actuation and main steam line isolation logic was determined to be non-conservative and Technical Specification (TS) 3.0.3 was entered at 1500 hours. A load reduction was commenced and Salem Unit 2 entered Mode 3 (Hot Standby) at 2140 hours. At 2248 the high steam line flow safety injection signal was blocked in accordance with procedures when reactor coolant system temperature was lowered below 543°F and TS 3.0.3 was exited. The causes of this event were incomplete administrative controls for the use of the Computerized Scaling Manual (CSM) for steam flow instrumentation calibration and a post modification test plan that did not identify and correct the incorrect steam flow calibration. The steam flow channels were recalibrated and additional corrective actions include procedure changes for the CSM and post modification testing. This report is being made in accordance with 10CFR50.73 (a)(2)(i)(A), "the completion of any nuclear plant shutdown required by the plant's Technical Specification," and 10CFR50.73 (a)(2)(i)(B), "any operation ...prohibited by the plant's Technical Specification."
3132008001 | Arkansas 1 | 12/12/2008 | 02/10/2009 | ML09041066 | <strong>Two Manual Reactor Trips from Power in Response to Abnormal Control Rod Movement Caused by Control Rod Drive Control System Component Degradation</strong><br /><i>Abstract:&nbsp;</i>At 0855 CST, on December 12, 2008, and again at 1212 CST, on December 20, 2008, Arkansas Nuclear One, Unit-1, initiated a manual plant trip from power in accordance with plant procedures in response to receipt of asymmetric rod alarms and recognition of abnormal control rod group 7 movements. The Control Rod Drive Control System (CRDCS) was in automatic at the time of each occurrence. Post trip responses were normal with all plant systems functioning as expected and with no safety system actuations. Testing and analysis determined that the probable root cause was degradation of two of the Automatic Bus Transfer (ABT) relays as the result of inadequate preventive maintenance. The two subject ABT relays were replaced as well as the programmer for the Group 7 Control Rods which was identified as single point failure vulnerable. In addition to the immediate actions to replace the above components, actions have been initiated to evaluate and upgrade the preventive maintenance associated with the CRDCS. Additional online monitoring requirements were implemented to obtain diagnostic information and enhanced inspection requirements were implemented for the CRD programmers. Both occurrences were reported to the NRC Operations center pursuant to 10CFR50.72 reporting requirements.
3152008001 | Cook 1 | 02/02/2008 | 04/01/2008 | ML08095012 | <strong>Unit 1 Manual Reactor Trip due to Main Turbine Vibrations</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2008, at 0530 hours, Donald C. Cook Nuclear Plant Unit 1 operators initiated a manual reactor trip from 93% power when main turbine bearing vibration reached the manual trip setpoint. All control rods fully inserted and the Auxiliary Feedwater System (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed. The reactor trip and AFW actuations were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) respectively, and are reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A). An unintentional cooldown of Main Turbine Lube Oil (MTLO) induced an oil whip condition that exacerbated main turbine bearing vibrations. After raising MTLO temperature, operators were performing a power reduction in an attempt to lower main turbine vibration. During the power reduction, vibration levels reached the manual trip setpoint and operators manually tripped the reactor in accordance with plant procedures. Corrective actions included installation of main turbine balance weights to return vibration to normal levels as well as actions to address the MTLO cooldown.
3152008002 | Cook 1, Cook 2 | 02/06/2008 | 04/01/2008 | ML08095012 | <strong>250 Volt DC Cable Separation Criteria For 10 CFR 50 Appendix R Not Met</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2008, during verification performed as part of preparation for fire protection analysis compliance transition to NFPA 805, Donald C. Cook Nuclear Plant personnel identified an error in the original, and subsequent, Appendix R analyses for the Train B 4 kV switchgear room fire analysis area in both units. The error involved a failure to identify a short section of Train A 250 VDC conduit enclosed cable passing through the Train B 4 kV switchgear room. This cable run connects the Train A battery charger transfer switch cabinet to the shunt cabinet. The routing of this unprotected Train A 250 VDC cabling in the Train B 4 kV switchgear room presented the possibility of a fire in the Train B 4 kV switchgear room disabling the Train B switchgear as well as remote control to the Train A 4 kV switchgear as a result of fire damage to the conduit enclosed cable. This failure to identify and correct the error in the analyses has been determined to be human error. Compensatory fire watch tours of the affected fire zones were established and remained until permanent corrective action was implemented. Permanent corrective action included wrapping the conduit with a fire retardant material, and converting the CO2 Suppression System from manual to automatic in accordance with the requirements of Appendix R, Section III.G.2.(c). Also, the applicable design documents have been updated to reflect the installed fire protective material.
3152008003 | Cook 1, Cook 2 | 03/13/2008 | 05/12/2008 | ML08142001 | <strong>Failure to Comply with Technical Specification Limiting Condition for Operation 3.0.6</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2008, it was identified that Donald C. Cook Nuclear Plant (CNP) personnel had failed to comply with Technical Specification (TS) Limiting Condition For Operation (LCO) 3.0.6. This was identified from a review of the activities related to the removal of the Unit 1 East Essential Service Water Pump (ESW) from service for scheduled maintenance on March 5, 2008. Due to the nature of the work being performed on the Unit 1 East ESW pump, the supported systems should have been considered inoperable and a Safety Function Determination evaluation performed as specified by TS LCO 3.0.6. Otherwise, the supported systems should have been declared inoperable and the required LCO actions should been completed in accordance with TS LCO 3.0.2. Further review of this condition identified multiple instances in which the Safety Function Determination evaluation required by TS 3.0.6 was not performed. The cause for this event was a lack of appropriate Procedural cross references to ensure the requirements of TS LCO 3.0.6, TS 5.5.13, and the Safety Function Determination Program implementing procedure were met. Corrective actions included providing immediate guidance to licensed operators of the LCO 3.0.6 requirements. This licensee event report (LER) has been initiated in accordance with 10 CFR 50.73(a)(2)(i)(B), to document the multiple failures to comply with TS LCO 3.0.6.
3152008004 | Cook 1 | 04/25/2008 | 06/23/2008 | ML08184011 | <strong>Non-Isolable Reactor Coolant System Pressure Boundary Leak</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2008, personnel at Donald C. Cook Nuclear Plant (CNP) Unit 1 identified a non-isolable RCS pressure boundary leak on a 3/4-inch instrument line connected to the Reactor Coolant System (RCS). Technical Specification Limiting Condition for Operation (LCO) 3.4.13 limits the RCS to no pressure boundary leakage and is applicable in Modes 1, 2, 3, and 4. While Unit 1 RCS temperature and pressure were being increased during a refueling outage, personnel identified a leak on a 3/4-inch instrument line upstream of a reactor coolant loop differential flow instrument low pressure side root valve. Steam was noted coming from a weld between the RCS piping and the instrument isolation valve. In that location, the leak is non-isolable. The plant was taken to Mode 5 (out of the Mode of Applicability) approximately 7 hours later, satisfying LCO 3.4.13 Action D for Pressure Boundary Leakage. The apparent cause of the leak was high cycle vibratory fatigue causing flaw propagation and the subsequent weld failure. Corrective action included weld repair with an overlay in accordance with ASME Boiler and Pressure Vessel Code, Section XI, Code Case N-666. Use of Code Case N-666 for the repair as an alternative to a code repair was verbally approved by the Nuclear Regulatory Commission on April 26, 2008. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
3152008005 | Cook 1 | 07/15/2008 | 09/10/2008 | ML08262021 | <strong>Containment Isolation Valve out of Position</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2008, personnel at Donald C. Cook Nuclear Plant, Unit 1, identified that a containment isolation drain valve on the Non-Essential Service Water System was sealed open and capped rather than sealed closed and capped as required. When the valve was verified not in its required position, the Unit Supervisor entered Technical Specification Limiting Condition for Operation (LCO) 3.6.3, Condition A, One or more containment isolation flow paths with one containment isolation valve inoperable. Required action is to verify the affected flowpath isolated within 4 hours. Twenty-two minutes later, corrective action was taken to close the valve and verify closed in accordance with the containment isolation surveillance procedure and LCO 3.6.3 Condition A was exited. The apparent cause of the mispositioning is a failure of the individual positioning the valve to perform adequate review during the self-check process. The apparent cause of the individual verifying the valve position not identifying the misposition is a failure to maintain an adequate questioning attitude regarding the position of the valve stem, which was extended one half inch higher than other similar valves. The valve was closed on July 15, 2008, at 0242 hours. Additional corrective actions are planned which will address the human performance aspects of the apparent cause. This event is reportable in accordance with 10 CFR 50.73 (a) (2) (i) (B) , Any operation or condition which was prohibited by the plant's Technical Specifications.
3152008006 | Cook 1 | 09/20/2008 | 05/06/2009 | ML09139060 | <strong>Manual Reactor Trip Due To Main Turbine High Vibration</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2008, at 2005 hours, Donald C. Cook Nuclear Plant Unit 1 control room operators initiated a manual reactor trip from 100% power following high-high vibration alarms on all main turbine supervisory instrumentation vibration points. In addition, numerous alarms on components in the condensate and feedwater flowpaths along with severe vibration and rumbling were noted by control room operators. Upon the reactor trip, all control rods fully inserted, the Auxiliary Feedwater System (AFW) and other major plant components functioned as designed. The main generator was reported to be on fire, and the Shift Manager declared an Unusual Event (UE) when the fire was not extinguished within 15 minutes. The f ire was declared extinguished at 2028 hours. At 2044 hours, the operators tripped closed the Main Steam Isolation Valves (MSIV) in accordance with procedure. Closure - was based on an observed cooldown of the Reactor Coolant System (RCS) . RCS temperature recovered following closure of the MSIVs . The reactor trip, UE, AFW actuation, and MSIV closure were reported in accordance with 10 CFR 50.72(b) (2) (iv) (B) , 10 CFR 50.72(a) (1) (i) , and 10 CFR 50 . 72 (b) (3) (iv) (A) . The reactor trip, AFW actuation and MSIV closure are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73 (a) (2) (iv) . (A) . The cause of the reactor trip was high-high vibration of the main turbine. Corrective actions have commenced and include repair of the main turbine and generator.
3172008001 | Calvert Cliffs 1 | 02/25/2008 | 04/25/2008 | ML08120059 | <strong>Pressure Boundary Leakage Caused by Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2008, during performance of a bare metal visual examination, dry boric acid was noted on pressurizer heater sleeve C-2 indicating reactor coolant leakage. Subsequent ultrasonic examination confirmed the absence of a circumferential flaw. All other pressurizer heater sleeves were inspected with no additional findings. The most likely cause of the leak is Primary Water Stress Corrosion Cracking. The heater sleeve was repaired by installing an approved mechanical clamp. As a preventive action, the Unit 1 Pressurizer Heater Sleeves will be repaired/replaced in a future refueling outage which eliminates their susceptibility to Primary Water Stress Corrosion Cracking. This preventive action was established due to similar events discussed in Licensee Event Reports 318/89-007 and 317/94-003.
3172008002 | Calvert Cliffs 1 | 07/21/2008 | 09/11/2008 | ML08255053 | <strong>Pressurizer Safety Valve Setpoint High due to Low Torque and Misalignment</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2008, during scheduled testing at the offsite testing facility, the As-Found Lift Setting for Pressurizer Safety Valve Serial Number BM07952 was measured higher than the Technical Specification allowable value. The valve had been installed in Unit 1 at the 1 RV201 location (Unit 1 pressurizer safety valve) and was removed during the 2008 Unit 1 refueling outage for scheduled testing and maintenance. To determine the cause of the high setpoint condition, the valve was disassembled and inspected by a vendor technician on July 25, 2008. A low inlet nozzle torque value and indications of internal valve misalignment were identified during the inspection. Although the apparent cause evaluation is not complete, it is reasonable to assume that the low nozzle torque and internal valve misalignment most likely led to the high setpoint during valve testing on July 21, 2008. A review of the testing and maintenance records for the currently installed valves indicated that they are not susceptible to the condition that led to the high setpoint of BM07952. Additional evaluations are required to determine the apparent cause and establish final corrective actions. A supplemental licensee event report will be submitted after the evaluations are completed.
3182008001 | Calvert Cliffs 2, Calvert Cliffs 1 | 01/04/2008 | 03/04/2008 | ML08066064 | <strong>Pressurizer Safety Valve Setpoint Low due to Different Temoerature Profiles</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2008, Calvert Cliffs Nuclear Power Plant received vendor confirmation that the temperature profile used to establish the As-Found Lift Setting for pressurizer safety valve 2RV200 (BV02950) in 2006 was not consistent with the temperature profile used to establish the valve's As-Left Lift Setting in 2003. As a result, the As-Found Lift Setting was outside the Technical Specification limits. Because 2RV200 had partially lifted during the November 16, 2006 Unit 2 reactor trip (Licensee Event Report 318/2006-001, Revision 1 dated February 23, 2007), the valve was removed and shipped to the vendor for As-Found testing and a complete refurbishment. Initially, the apparent cause evaluation determined that due to a loose compression screw/valve bonnet thread interface, thermal effects from the Unit 2 trip may have caused the lift setting to decrease during the event. However, a subsequent revision to the apparent cause evaluation determined that the low lift setting was caused by a difference in the temperature profiles. BV02950 was replaced with a valve set at the correct temperature profile. All valves currently installed in Units 1 and 2 were verified to be set at the correct temperature profile. Procedures will be changed to reflect the effect of temperature changes on the setpoint and a checklist will be developed to track relief valve testing prior to installation.
3212008001 | Hatch 1 | 03/06/2007 | 05/02/2008 | ML08126037 | <strong>Leak in Reactor Pressure Boundary Piping due to a Crack Caused by Intergranular Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2008, at 0400 EST, Unit 1 was in the Cold Shutdown mode. At that time, a leak was identified in a one-inch pipe adjacent to a socket weld elbow, located between the “A” Main Steam Line (MSL) and the MSL flow instrument condensing chamber. The Technical Specification (TS) definition of pressure boundary leakage is “leakage through a non-isolable fault in the reactor coolant system.” Due to its location, the leak met this definition. Based upon inspection of the weld and adjacent area, it was determined that the leak existed when the Unit was in mode 1. The TS allows no pressure boundary leakage in mode 1. The cause of the leak is failure of the pipe due to Intergranular Stress Corrosion Cracking (IGSCC). Corrective actions for this event included replacing the failed weld and inspection of similar piping to confirm no other leaks.
3212008002 | Hatch 1 | 03/29/2008 | 05/27/2008 | ML08148050 | <strong>Corrosion Induced Bonding Results in Safety Relief Valve Lift Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 29, at approximately 1104 EDT, Unit 1 was at 1697 CMWTh, which is 60.5 percent of rated thermal power (RTP). On that day, it was identified during bench testing that two Safety Relief Valves (SRVs) experienced setpoint drift that exceeded the allowable plant Technical Specifications (TS) limit. At the conclusion of bench testing, a total of three of the eleven SRVs were identified as having setpoint drift in excess of the TS limit. The root cause of the SRV setpoint drift is corrosion-induced bonding between the pilot disc and seating surface. Immediate corrective actions for this event included replacement of all eleven SRVs with refurbished pilot valves which have pilot discs made from Stellite 21 material, which is more resistant to corrosion bonding in this application. In addition, the pilot discs on the eleven valves that were removed for testing will be replaced with pilot discs made from Stellite 21. Evaluation of additional actions to further improve SRV performance will be tracked under the plant’s corrective action program.
3212008003 | Hatch 1 | 07/04/2008 | 08/25/2008 | ML08238087 | <strong>Sensed Low EHC Pressure Causes Turbine Trip Resulting in a Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On July 4, 2008 at 08:39 EDT, Unit 1 was in the Run mode at a power level of approximately 2797 CMWT, 99.7 percent rated thermal power. At that time testing of the 'Electro-hydraulic Control (EHC) pump auto start was in progress. During the testing, a Low EHC Pressure was sensed which resulted in a turbine trip. The reactor tripped on turbine control valve fast closure. Following the reactor scram, reactor pressure peaked at approximately 1120 psig, resulting in four of the eleven safety relief valves (SRV’s) opening as designed to reduce pressure. Water level decreased due to void collapse resulting in the closure of the Group 2 primary containment isolation valves, and a Reactor Feed Pump Turbine speed increase, both per design. The feedwater level control system controlled reactor water level with a minimum water level of approximately 2.5 inches above instrument zero (about 160 inches above the top of active fuel). All control rods fully inserted. Pressure did not reach the nominal actuation set points for the remaining seven SRV’s. This event was caused by a sensed low pressure in the EHC system tripping the main turbine which results in an automatic reactor scram. Performance of the weekly EHC pump auto start procedure has been suspended pending additional corrective actions. Installation of a time delay circuit, relocation of the pressure sensor tap to its previous location, along with additional corrective actions will be considered and tracked in the corrective action program.
3212008004 | Hatch 1 | 11/22/2008 | 01/13/2009 | ML09014015 | <strong>Power Supply Card Failure Causes Loss of Feedwater Flow Resulting in Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2008 at approximately 1019 EST, Unit 1 was in the Run mode at a power level of approximately 2800 CMWT, 99.8 percent rated thermal power. A manual scram was inserted due to Reactor Water Level (RWL) decreasing to 10 inches above instrument zero and continuing to decrease. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) automatically started on low RWL, Level 2. RWL decreased to approximately negative 68 inches (about 90 inches above the top of active fuel) prior to it being recovered by HPCI and RCIC operation. Due to the RWL reaching the Anticipated Transient Without Scram - Recirculation Pump Trip (ATWS-RPT) low level, the recirculation pumps tripped as designed. As RWL was recovering, HPCI was manually secured and RCIC flow was decreased. The 1A Reactor Feed Pump (RFP) was subsequently restarted and RWL control was then transitioned to the 1A RFP. Investigation determined that the direct cause of the event was failure of DC power supply 1N21-K088 which provides power to the differential pressure (DP) controller for the (Steam Jet Air Ejector) SJAE Intercondenser Cooling water control valve 1N21-F211. The DC power supply 1N21-K088 was replaced and a repetitive task has been created to replace the component at a prescribed interval.
3232008001 | Diablo Canyon 2 | 08/16/2008 | 10/15/2008 | ML08297022 | <strong>Reactor Trip Due to Main Electrical Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2008, at 23:57 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 100 percent power, a main generator Unit Trip signal initiated a Reactor Trip due to the failure of the main electrical transformer "C" phase. On August 17, 2008, at 00:12 PDT, plant operators declared an Unusual Event (UE) due to an observed fire at the "C" phase transformer. Plant operators made an Emergency Event Notification (EN 44419) in accordance with 10 CFR 50.72(a)(1)(i) at 00:37 PDT. Plant operators stabilized Unit 2 in Mode 3 (Hot Standby) and updated the UE that the fire was out at 02:02 PDT. At 07:38 PDT, EN 44419 was updated to specify 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(3)(iv)(B). This event was due to a catastrophic failure of the main electrical transformer "C" phase high voltage bushing. The event investigation will continue, however, this event is considered a random component failure based upon onsite inspections and vendor reviews performed. Corrective actions include the "C" phase transformer replacement, electrical tests of transformers and bushings, oil analysis of transformers and bushings, installation of a bushing monitoring system, evaluation and replacement of equipment damaged as a result of the electrical failure, and review of industry and station operating experience regarding main transformer issues.
3232008002 | Diablo Canyon 2 | 10/21/2008 | 12/19/2008 | ML09007003 | <strong>Manual Reactor Trip Due to Pacific Ocean Circulating Water System Debris</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2008, at 20:49 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 55 percent power, a manual Reactor Trip was initiated due to the failure of the Pacific Ocean Circulating Water System (CWS) debris removal system to maintain adequate flow for power operation. Plant operators stabilized Unit 2 in Mode 3 (Hot Standby) and made an emergency event notification (EN#44588) in accordance with 10 CFR 50.72(a)(1)(i) at 22:44 PDT. This event was due to a sudden large influx of Moon Jellyfish in the Pacific Ocean CWS that exceeded the ability of the debris removal system to effectively remove. PG&E has developed extensive models to help predict the impact of Pacific Ocean storms associated with CWS debris removal, and to give adequate time to prepare for such events. PG&E could not have anticipated this event and the potential adverse affects from the sudden large influx of jellyfish.
3242008001 | Brunswick 2 | 08/30/2008 | 10/23/2008 | ML08309038 | <strong>Automatic Reactor Scram Due to Turbine Power/Load Unbalance Actuation</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2008, at 1503 hours Eastern Daylight Time (EDT), a Power/Load Unbalance (PLU) actuation caused the Turbine Control Valves (TCVs) and the Main Turbine Bypass Valves (BPVs) to cycle. The initial cycle resulted in BPV No. 1 partially opening while a second cycle resulted in four BPVs going full open. At that time, the order was given to insert a manual scram. An automatic scram signal occurred just as the operator was beginning to insert the manual scram. Reactor water level momentarily dropped below Low Level 1 (LL1) during the response, resulting in Primary Containment Isolation System (PCIS) Group 2 and Group 6 isolations. LL1 actuations occurred as designed. All control rods fully inserted and all systems responded as designed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The select cause of this event was the lack of adequate work controls for transmission maintenance activities due to an inaccurate perception of risk. The corrective actions to prevent recurrence include the revision of site procedures to provide additional work controls and improve risk assessment.
3242008002 | Brunswick 2 | 11/09/2008 | 01/07/2009 | ML09015004 | <strong>Manual Reactor Scram due to Spurious Safety Relief Valve Opening</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2008, at 1108 hours Eastern Standard Time (EST), Safety Relief Valve (SRV) 2-B21-F013H (i.e., SRV H) spuriously opened with no Operator action or testing in progress. The SRV's control switch was cycled as required by Abnormal Operating Procedure with no success. At 1113 hours, the fuses were pulled for SRV H in an attempt to close the valve. At 1117 hours, a manual reactor scram was inserted based on the Suppression Pool temperature reaching 109.8 degrees Fahrenheit (F). Technical Specifications requires a manual reactor scram to be inserted when Suppression Pool average temperature exceeds 110 degrees F. All control rods fully inserted from the manual reactor scram signal. Reactor water level lowered to Low Level 2 resulting in Primary Containment Isolation System (PCIS) isolations of Groups 2, 3, 6, and 8. In addition, the Reactor Core Isolation Cooling (RCIC) system actuated and injected into the reactor. The High Pressure Coolant Injection (HPCI) system actuated but did not inject since reactor water level had recovered. An Alternate Rod Insertion signal was received, the Standby Gas Treatment (SBGT) system initiated, and the Reactor Recirculation pumps tripped as designed. All systems responded as designed. The root cause of this event was the failure to verify proper seating of the set pressure spring in the upper spring follower plate. The corrective action to prevent recurrence is to revise the corrective maintenance procedure to perform verification of proper set pressure spring seating prior to the reassembly of the pilot valve.
3252008001 | Brunswick 1 | 04/29/2008 | 06/30/2008 | ML08191014 | <strong>High Pressure Coolant Injection (HPCI) System Inoperable due to Main Pump Seal Leak</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2008, at approximately 2313 Eastern Daylight Time (EDT), during performance of the High Pressure Coolant Injection (HPCI) system operability test, the HPCI system was declared inoperable due to a leak on the main pump seal. When the pump seal leak developed, operators secured HPCI and isolated the leak by closing the pump suction isolation valves and the keep fill supply valves. The safety consequences of this event were minimal. The Emergency Core Cooling Systems (ECCS) and the Reactor Core Isolation Cooling (RCIC) system were operable and would provide appropriate Loss-of-Coolant Accident (LOCA) response. Investigation of this event found that inadequate post-maintenance venting of piping between the discharge of the HPCI booster pump and the suction of the HPCI main pump led to the seal faces overheating and subsequent failure. An engineering analysis is in progress to substantiate the ability of the HPCI system to fulfill its safety functions in the degraded condition. This LER will be supplemented, and based on the results of the engineering evaluation, may result in retraction of Event Notification 44179 and withdrawal of this LER.
3252008001 | Brunswick 1 | 04/29/2008 | 07/31/2008 | ML08225045 | <strong>High Pressure Coolant Injection (HPCI) System Inoperable due to Main Pump Seal Leak</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2008, at approximately 2313 Eastern Daylight Time (EDT), during performance of the High Pressure Coolant Injection (HPCI) system operability test, the HPCI system was declared inoperable due to a leak on the main pump seal. When the pump seal leak developed, operators secured HPCI and isolated the leak by closing the pump suction isolation valves and the keep fill supply valves. The safety consequences of this event were minimal. The Emergency Core Cooling Systems (ECCS) and the Reactor Core Isolation Cooling (RCIC) system were operable and would provide appropriate Loss-of-Coolant Accident (LOCA) response. Investigation of this event found that inadequate post-maintenance venting of piping between the discharge of the HPCI booster pump and the suction of the HPCI main pump led to the seal faces overheating and subsequent failure. An engineering analysis has been completed and has concluded that the HPCI system maintained its ability to fulfill its safety functions in the degraded condition. Based on the results of the engineering evaluation, this LER is formally withdrawn. Event Notification 44179 was also retracted.
3252008002 | Brunswick 1, Brunswick 2 | 06/03/2008 | 08/04/2008 | ML08225044 | <strong>Loss of Two Control Room Air Conditioning (AC) Subsystems</strong><br /><i>Abstract:&nbsp;</i>At 1313 hours EDT on June 3, 2008, two operating Control Room Air Conditioning subsystems, required by Technical Specification (TS) 3.7.4, "Control Room Air Conditioning (AC) System," tripped during the replacement of a solenoid valve for the Unit 1 Cable Spread Room supply/exhaust fan dampers. The trip occurred when the control air supply line was momentarily uncapped to enable the installation of the control air supply to the newly installed solenoid valve, causing the dampers on the two operating AC subsystems to close. With the third Control Room AC subsystem in standby with the damper closed, all Control Room AC subsystems were shut down. Because BSEP has a shared Control Room, both Unit 1 and Unit 2 immediately entered TS Limiting Condition of Operation (LCO) 3.0.3. At 1325 hours, following completion of the solenoid valve replacement, the Control Room AC subsystems were restored to operable status and LCO 3.0.3 was exited. No reactor power reduction took place on either unit as a result of the LCO 3.0.3 entry. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The root cause of this event was determined to be a reliance on an Engineering Change calculation which did not adequately consider the impact of system material condition and resulted in an inadequate assessment of risk. The corrective action to prevent recurrence is to revise the Preventive Maintenance tasks to use a Temporary Modification whenever the Control Room AC system solenoid valves are being replaced, which will allow the Control Room AC system to run on total loss of Control Room instrument air.
3252008003 | Brunswick 1, Brunswick 2 | 06/11/2008 | 08/11/2008 | ML08232081 | <strong>Reactor Building Crane Design Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2008, as a result of a review of the Reactor Building crane structure by the original equipment manufacturer (OEM), it was determined that the structural design of the Unit 1 and Unit 2 Reactor Building cranes did not ensure the crane structural integrity during a design basis seismic event. Specifically, the allowable design stresses for the design basis seismic event are exceeded in the end connector plates and bolted connections connecting the crane girders. This condition has existed since operation of the plants began. The direct cause of this event is that the crane girder end connection design was not adequately evaluated during the initial design of the crane by Whiting Corporation (i.e., the OEM). The crane design was performed by Whiting Corporation in the 1970's. Due to the historical nature of this condition, determining a plausible cause is not practical or feasible. Modifications have been implemented for the Unit 1 and Unit 2 Reactor Building cranes to allow continued restricted use of the cranes for loads of up to 40 tons. Engineering Changes will be developed and implemented to restore the cranes to their original seismic design requirements.
3252008004 | Brunswick 1, Brunswick 2 | 06/19/2008 | 08/18/2008 | ML08240008 | <strong>Control Room Emergency Ventilation (CREV) Subsystems Inoperable due to Failure to Isolate</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2008, at 1641 hours Eastern Daylight Time (EDT), the Control Room authorized post-maintenance testing following replacement of solenoid valves affecting the Control Room Emergency Ventilation (CREV) subsystem. This test inputs a simulated high radiation signal into the logic for the Control Building ventilation system to ensure that the CREV subsystem automatically aligns to the radiation/smoke protection mode. At 1735 hours, during performance of this test, the 2D Control Building exhaust fan damper failed to close and associated Control Building exhaust fan failed to trip as expected. The affected functions of the CREV system are to provide isolation, positive presurrization, and emergency filtration of the Control Room in the event of high radiation or smoke intrusion into the Control Building. Because BSEP has a shared Control Room, both Unit 1 and Unit 2 immediately entered TS Limiting Condition of Operation (LCO) 3.7.3, "Control Room Emergency Ventilation (CREV) System," Required Action B.1 for two CREV subsystems inoperable (i.e., be in Mode 3 within 12 hours). At 1910 hours, the 2A CREV subsystem was manually placed in the radiation/smoke protection mode restoring the subsystem to operable status, and LCO 3.7.3, Required Action B.1, was exited. No reactor power reduction took place on either unit as a result of the LCO entry. An exact root cause for this event has not been determined. The select cause of this event was determined to be failure to identify appropriate Preventive Maintenance (PM) routes for the CREV system components. The corrective action to prevent recurrence is to develop PM tasks for the Control Building ventilation system dampers, actuators, limit switches, and relays.
3252008005 | Brunswick 1 | 07/16/2008 | 09/10/2008 | ML08261022 | <strong>As-Found Values for Safety/Relief Valve Lift Setpoints outside Technical Specification Allowed Tolerance</strong><br /><i>Abstract:&nbsp;</i>On July 16, 2008, the Brunswick Steam Electric Plant as-found testing of 11 safety/relief valves (SRVs), which had been removed from Unit 1 during the spring 2008, refueling outage (i.e., B117R1) was completed. The testing indicated that two of the 11 valves were found to lift at greater than 3 percent tolerance allowed by Technical Specification 3.4.3, "Safety/Relief Valves." A third SRV pilot valve was unable to be pressurized to obtain as-found data because of excessive disc-to-seat leakage. Since Technical Specification 3.4.3 requires 10 of the 11 installed SRVs to be operable, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications. The cause for the setpoint drift for SRV pilot valves 1-B21-F013F and 1-B21-F013J was an incomplete understanding of proper lapping techniques when the BSEP SRV rebuild program began and corrosion bonding. In addition, misalignment caused mechanical binding between the pilot rod and guide assembly for valve 1-B21-F013F. The failure of SRV pilot valve 1-B21-F013G to open was an incomplete understanding of proper lapping techniques when the BSEP SRV rebuild program began. Corrective actions for these items include: (1) incorporation of additional industry guidance into the SRV Rebuild Program, and (2) refurbish and recertify each pilot valve.
3252008006 | Brunswick 1, Brunswick 2 | 08/18/2008 | 07/30/2009 | ML09217017 | <strong>Emergency Diesel Generator Failure to Start From Local Control Panel</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2008, at 2152 hours Eastern Daylight Time (EDT), during the performance of surveillance OPT-12.14.L, "Diesel Generator 4 Local Control Operability Test," Emergency Diesel Generator (EDG) 4 failed to start from the local control panel. The biennial (i.e., every 24 months) surveillance is a non-Technical Specification (TS) related test to demonstrate that control and indication for EDG 4, and the EDG 4 to Bus E4 output breaker, can be isolated from the Control Room and be controlled from the respective local control station, as required by the Alternate Safe Shutdown (ASSD) analysis. Troubleshooting determined that the Lockout Control Relay (LOCR), installed in a 2007 plant modification, was wired such that power was lost when the associated ASSD switch was in the LOCAL position, preventing EDG 4 to be reset so that it could be started locally. The plant modification was installed on all four EDGs, and it has been concluded that this condition impacted the ability of EDG Nos. 2, 3, and 4 to perform their intended ASSD function (i.e., local control of EDG 1 is not credited in the ASSD analysis). This condition did not affect the TS operability of the EDGs and they remained fully capable of performing their intended safety system functions. Two root causes were determined for this event; a latent organizational weakness existed where the EDG control wire circuitry maintained the same wire segment number on either side of the ASSD key-switches, and a lack of sufficient rigor by Engineering in performance of their responsibilities during activities associated with modification of control logic circuitry. The corrective actions to prevent recurrence include generating an Engineering Change package to clearly denote on applicable plant drawings that duplicate wire numbers exist on either side of the EDG ASSD keyswitches, revising the applicable plant drawings, revising respective Engineering procedures, and addressing other factors affecting rigor and risk management during design and review activities.
3252008007 | Brunswick 1 | 11/26/2008 | 01/26/2009 | ML09042027 | <strong>Automatic Reactor Scram due to Electro-Hydraulic Control System Failure</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2008, at approximately 1200 hours Eastern Standard Time (EST), Unit 1 experienced a primary containment Group 1 isolation which resulted in an automatic actuation of the Reactor Protection system. The Pressure-Load Gate Amplifier (PLGA) circuit board (A58), in the Electro-Hydraulic Control system, operated erroneously which caused a sensed Main Steam Line low pressure on Main Steam Line Low Pressure instruments B21-PT-N015A through D. The sensed low pressure while in Mode 1 resulted in the Group 1 isolation. Following the scram, an expected reactor vessel coolant level shrink occurred. As a result of the low water level, primary containment Groups 2 and 6 isolation signals were received. All required isolations occurred as a result of the reactor low water level isolation signals. All control rods fully inserted on the scram and safety-related systems responded as designed. The Reactor Core Isolation Cooling System was manually started to restore reactor water level to the normal band. The erroneous operation of the PLGA circuit board was due to loose connection(s) within the blade / blade receptacle connection. The root cause of the loose connection was that the key slot in circuit board A58 was not squared at the bottom mating surface. Resin at the bottom mating surface, present since original manufacturing of the circuit board, prevented full seating with the terminal receptacle. Corrective actions to prevent reoccurrence include: (1) visual verification of Unit 1 and Unit 2 EHC circuit board engagement at the next opportunity and (2) procedural enhancements to ensure circuit board engagement after maintenance work is performed.
3272008001 | Sequoyah 1 | 01/16/2008 | 03/04/2008 | ML08065077 | <strong>Manual Reactor Trip Resulting from a Failure to Follow Procedures</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2008, at 1925 Eastern standard time, the Unit 1 reactor was manually tripped as a result of a low steam generator level on Loop 3. Maintenance personnel were performing a transmitter calibration on a Loop 3 steam generator pressure transmitter. During performance of the calibration, Maintenance personnel made an incorrect assumption that a place-keeping aid placed in the procedure was intended to be the procedure start point when in fact they should have started two pages previous to the place-keeping aid location. The two missed pages resulted in Operations not being notified to remove the channel being tested as a controlling channel. This resulted in performing testing on the pressure transmitter on a controlling channel, causing closure of the Loop 3 main feedwater regulating valve. Operations placed the feedwater regulating valve in manual to open the valve. However, before steam generator water level began to increase, the pre-established low steam generator level trigger-point was reached and the operating crew initiated a manual reactor trip. The cause was determined to be a failure to follow procedure because of personnel not performing proper place keeping during performance of a calibration procedure. Corrective actions include establishing and proceduralizing standard placekeeping requirements, strengthening and proceduralizing standard pre-job brief requirements, and training on these standard requirements.
3272008002 | Sequoyah 1, Sequoyah 2 | 09/26/2008 | 06/16/2009 | ML09169057 | <strong>Loss of a Main Control Room Air Handling Unit In Conjunction With an Emergency Power Source Out of Service</strong><br /><i>Abstract:&nbsp;</i>The enclosed LER is being revised to indicate that the reported condition has subsequently been determined to be a condition that could have prevented the fulfillment of the safety function. On September 24, 2008, at 1705 Eastern daylight time (EDT), Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1.1, was entered for scheduled maintenance of the IA-A emergency diesel generator (EDG) 125-volt battery bank. At the time of entering the LCO, both Units 1 and 2 were operating in Mode 1. The scheduled battery bank maintenance was expected to take approximately 64 hours. On September 25, 2008, at 2255, LCO 3.7.15, was entered because of a motor failure on the associated "B" train main control room air handling unit. Also TS LCO 3.0.5 was entered, which required action to be initiated within 2 hours to place both units in Hot Standby in the following 6 hours. Enforcement discretion was requested and granted on September 26, 2008, to extend the expiration time of LCO 3.0.5 an additional 36 hours. Compensatory measures were initiated to administratively control and protect vital plant equipment during this period of time for completing maintenance to replace the batteries for the IA-A EDG and the unplanned maintenance to replace the motor in the "B" train main control room air handling unit. Subsequently, SQN returned the EDG battery bank to service and exited LCO 3.8.1.1 and LCO 3.0.5 on September 26, 2008 at 1400 EDT. The risk associated with swapping the main control room air handling units while the 1A-A EDG was inoperable was not adequately assessed. Actions were expedited to repair the "B" train main control room air handling unit motor and return the 1A-A EDG operable.
3282008001 | Sequoyah 2 | 11/03/2008 | 12/19/2008 | ML08354071 | <strong>Manual Reactor Trip Following Partial Loss of Main Feedwater Flow to Loop 4 Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2008, at 2322 Eastern standard time with Unit 2 operating at 100 percent power, a manual reactor trip was initiated because of a partial loss of main feedwater flow to the steam generator Loop 4. The immediate cause was failure of the Loop 4 feedwater regulating valve controller. During normal power operations, operators received a steam generator level high-low deviation annunciation. An operator identified a decreasing level on the steam generator Loop 4. The controller was placed to manual, but the controller failed to respond to the operator’s attempt to increase level. Operators took action to manually trip the reactor. Following the reactor trip, an RCS leak occurred. The leak was from an instrumentation sensing line to the pressurizer. The plant systems responded as designed. The K1 Relay to the Unit 2 Loop 4 main feedwater regulating valve flow indicating controller has been determined as the most probable root cause of this event. The relay failure is attributed to a failing contact connection, which resulted in a slow closing drift of the main feedwater regulating valve.
3282008002 | Sequoyah 2 | 11/09/2008 | 12/19/2008 | ML08354072 | <strong>Indications of a Dropped Control Rod During Startup</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2008, at 1821 Eastern standard time with Unit 2 in Mode 3, the Unit 2 reactor trip breakers were opened from the main control room (MCR) because of indications of Shutdown Bank “A” Rod E-11 dropping into the reactor core. At the time the reactor trip breakers were opened, the MCR operators were in the process of withdrawing shutdown banks in preparations for entry into Mode 2. Rod E-11 rod position indication (RPI) dropped to zero and the rod bottom light was lit. The MCR operators entered the appropriate abnormal operating procedure and opened the reactor trip breakers based on indications that were available. All other shutdown banks and control banks were inserted at the time the reactor trip breakers were opened. All safety-related equipment operated as designed. Subsequent to the manual reactor trip, investigation revealed that the plant computer trace for Rod E-11 showed that the failure was in the RPI system and was not a dropped rod. Further investigation showed that the problem was a broken wire on the E-11 RPI coil stack on top of the reactor head. The unit was cooled down to Mode 5 to repair the broken RPI coil stack wire for Rod E-11. The corrective action to prevent recurrence will be a modification to the reactor head to provide a new RPI coil stack top plate, connector, and cable to the vertical panel.
3332008001 | FitzPatrick | 09/16/2008 | 11/17/2008 | ML08330036 | <strong>Loss of Shutdown Cooling Resulting from Invalid Primary Containment Isolation System Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2008 at 0734, with the plant shutdown and in the refueling mode (Mode 5), a fuse was removed during an equipment tag-out evolution resulting in the closure of two Primary Containment Isolation System (PCIS) valves that resulted in a loss of Residual Heat Removal (RHR) Shutdown Cooling (SDC). At the time of the event cavity flood-up was in progress. In response to this event, the Reactor Protection System (RPS) response and logic circuits functioned as designed. The appropriate Technical Specification LCO Actions were entered and shutdown cooling was restored at 0827. The event was reported to the NRC Operations Center as EN# 44492 via the Emergency Notification System pursuant to 10 CFR 50.72(b)(3)(v) for loss of SDC (8-hour report). The cause of the event was ineffective implementation of the outage risk assessment procedure. There were no safety system functional failures. There were no nuclear, radiological or industrial safety consequences associated with this event. All systems performed as designed and there were no component or system failures. Loss of the common SDC suction line impacts both systems/trains, however, the system remained available through manual realignment of the suction isolation valve. Therefore, barriers providing safety to the public were not compromised and the safety significance of this event is considered low.
3332008002 | FitzPatrick | 09/23/2008 | 11/24/2008 | ML08330036 | <strong>Reactor Pressure Vessel Recirculation Inlet Nozzle Axial Flaw Indication Discovered During Refueling Outage Consistent with Inter-Granular Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On 09/23/2008 at 1654, with the plant shutdown and in refueling mode (Mode 5) (Refueling Outage 18), an ultrasonic (UT) examination was performed, in accordance with the In-Service Inspection (ISI) Program, on Reactor Pressure Vessel (RPV) Reactor Recirculation Inlet nozzle, N2-C, that showed an inner diameter axial flaw indication approximately 0.8" long with a 0.5" wall depth. The flaw indication, in the dissimilar metal weld (DMW) area of RPV N2-C nozzle to safe-end weld, is consistent with inter-granular stress corrosion cracking (IGSCC). JAF performed a full structural weld overlay repair based on ASME Codes cases N-740 and N-638-1. This code alternative repair procedure was submitted to and approved by the NRC by as ISI Program Relief Request RR-7. The other N2 nozzles had been inspected during Refueling Outage 17 or were inspected during Refueling Outage 18 using enhanced PDI techniques with satisfactory results. No adverse safety consequences were associated with this event. This condition was reported to the NRC Operations Center via the Emergency Notification System (EN# 44516) pursuant to 10CFR50.72(b)(3)(ii)(A) as a seriously degraded principle barrier (8-hour report).
3332008003 | FitzPatrick | 10/07/2008 | 12/06/2008 | ML08346033 | <strong>Loss of Emergency Bus and Auto-Start of "B" EDG(s) due to Re-Scheduled Relay Functional Test w/o Risk Assessment Review</strong><br /><i>Abstract:&nbsp;</i>On 10/07/2008, with the plant in Cold Shutdown (Mode 4), the trip and lockout relay associated with circuit breaker 71-10402 was manually actuated during a functional test resulting in a loss of power to 4160 VAC Emergency Bus 10600, auto-start of the "B" and "D" Emergency Diesel Generators (EDG) and a Primary Containment Isolation System (PCIS) Group 2 actuation. The PCIS Group 2 actuation resulted in the closure of containment isolation valves in multiple systems including Residual Heat Removal (RHR) shutdown cooling (SDC), Reactor Water Clean-Up (RWCU), Reactor Building Ventilation and Containment Atmosphere Monitoring (CAM) systems. Plant components and systems responded as expected with no anomalies noted. Operations restarted plant systems and restored shutdown cooling to service in accordance with plant procedures. The cause of the event was the re-scheduling of a trip and lockout relay functional test outside of the bus outage work window without performing a risk assessment review. The functional test required actuating the trip and lockout relay associated with circuit breaker 71-10402, and as a result, power was lost to the 10600 Emergency Bus. During the event, the redundant 4160 VAC emergency bus and associated loads remained operable. Barriers providing safety to the public were not compromised during this event and the safety significance was minimal.
3332008004 | FitzPatrick | 09/23/2008 | 12/05/2008 | ML08346033 | <strong>Loss of Power Instrumentation Inoperable and Technical Specification Required Action Time Exceeded due to Relay Set Point Drift</strong><br /><i>Abstract:&nbsp;</i>On 9/23/08 , with the plant shutdown and in the refueling mode (Mode 5), 4.16 KV Emergency Bus Degraded Voltage Time Delay Relay, 71-27T3-1HOEB03, failed to meet the "as-found" Technical Specification (TS) surveillance acceptance criteria. Since this same relay failed the same acceptance criteria in 2006 the guidance in NUREG 1022 Rev 2 does not allow taking "time of discovery" as "time of failure". Therefore, the timer may have been outside the TS acceptance criteria for a period of time longer than allowed by the Technical Specifications and is reportable under 10 CFR 50.73(a)(2)(i)(B). The apparent cause of the relay failure is installation of the wrong component for the application. While this type of relay has been widely used in this type of application, the cause evaluation determined that these relays are only marginally acceptable in this application due to instrument drift. Therefore, the cause is an original design deficiency. The "as-found" delay times measured less than the calculated delay times credited in plant design basis accident analyses, therefore, the safety significance of this event is considered low.
3342008001 | Beaver Valley 1, Beaver Valley 2 | 11/10/2008 | 01/09/2009 | ML09013009 | <strong>Control Room Envelope Air Intake During Normal Operation Higher than Assumed in Design Basis Accident Dose Calculations</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2008, the results of the Control Room Envelope (CRE) tracer gas in-leakage testing for the Beaver Valley Power Station Unit 1 and Unit 2 combined control room were reported. The measured CRE in-leakage value for the Unit 1/Unit 2 Control Room Emergency Ventilation System (CREVS) Pressurization Mode used following an accident was 0 cubic foot per minute (cfm), which is below the design basis dose calculation limit. However, the routine intake of outside unfiltered fresh air into the combined Unit 1/Unit 2 CRE during normal plant operation was measured to be above the design basis dose calculation assumption of 500 cfm maximum. This was caused, in part, due to a corrosion hole in a normally closed Unit 1 control room ventilation purge damper. This higher-than-assumed normal intake air flow rate resulted in a calculated postaccident dose higher than the current bounding design basis control room dose. This represents an inadequate, and inoperable CRE boundary. This is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications. The cause of this event was less than adequate CRE boundary definition stated in site procedures which resulted in the failure to ensure adequate maintenance and surveillance activities on appropriate CRE components. This event is considered to have very low safety significance.
3352008001 | St. Lucie 1 | 10/18/2008 | 12/16/2008 | ML08366038 | <strong>Unattended Ammunition Discovered Inside Protected Area</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2008, St. Lucie Units 1 and 2 were operating normally in Mode 1 at 100% power when a box containing six ammunition cans was discovered inside a warehouse within the protected area. The box containing the ammunition was received and searched on October 6, 2008, but contents of the box were not identified as ammunition before being processed into the protected area. The event was reported to the NRC in accordance 10 CFR 73.71 Appendix G. The Root Cause Evaluation identified that a latent organization weakness resulted in an ineffective search by Security and a failure to implement process controls during identification and authorization of materials before entry into the protected area (PA). Corrective actions included procedure revisions, training, establishment of a segregated area outside of the protected area for materials not authorized for entry into the protected area, alignment of plant procedures to Physical Security Plan, and effectiveness measures to evaluate security search performance.
3362008001 | Millstone 2 | 04/03/2008 | 05/30/2008 | ML08157034 | <strong>Failure of Eight Main Steam Safety Valves to Lift within the Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>With the plant in MODE 1 at 100% power on April 3 and 4, 2008, set pressure "simmer" testing of Millstone Power Station Unit 2 (MPS2) main steam safety valves (MSSVs) was conducted per plant procedures. During the testing, eight MSSVs failed to lift within the (+/- 3%) acceptance criteria of Technical Specification (TS) 3.7.1.1. The failure of two MSSVs to lift within the required set pressure range is attributed to a corrosive oxide locking action between surface layer materials of the disc-seat interface, sometimes referred to as "oxide locking" or "micro bonding". The failure of the other six MSSVs to lift within the required set pressure is the result of differences between two Appendix B approved test methods. A Crosby Set Pressure Verification Device (SPVD) was being used for the first time at MPS2 for MSSV testing. Prior testing and "as-left" settings utilized a Dresser Hydroset system. Although both methods are Appendix B approved, there are key differences between the tests, primarily involving repeatability of results using the Hydroset System at MPS2 in determining when a valve lifts. The Crosby SPVD was used for the current as-left settings and will be used in future tests to provide consistent valve lift data. Following testing, as-left settings were within +/- 1% of set pressure to account for future drift.
3362008002 | Millstone 2 | 04/13/2008 | 06/11/2008 | ML08170028 | <strong>Unplanned LCO Entry - Three Charging Pumps Aligned for Injection With the Reactor Coolant System Temperature Less than 300 Degrees F.</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2008 at 0805 with the plant shut down in MODE 6, while performing control room operator rounds, a Licensed Operator identified three charging pumps were aligned so they were capable of injection with the Reactor Coolant System temperature less than 300 degrees F. The plant was in this configuration for approximately six hours. Upon discovery of this condition, Technical Specification Action Statement 3.1.1.3.b was immediately entered and then exited when the swing charging pump was made incapable of injection into the Reactor Coolant System. The cause of this event was determined to be inadequate configuration control because the tag for the charging pump removed from service to comply with the Boron Dilution TS 3.1.1.3.b. did not provide adequate guidance. Subsequent reconfiguration of the charging system to support electrical work activities aligned three charging pumps so they were capable of injection with the Reactor Coolant System temperature less than 300 degrees F. Since the plant was in a configuration prohibited by the Technical Specifications, this event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's Technical Specifications.
3362008003 | Millstone 2 | 05/22/2008 | 07/14/2008 | ML08206005 | <strong>Failed Pilot Wire Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2008 at 1359 with the Millstone Power Station Unit 2 (MPS2) at 100% power in Mode 1, the reactor automatically shutdown following a loss of load and subsequent turbine trip. Investigation determined that a lightning strike on a transmission line created an over current condition to which the unit responded. The 345 kV main generator output breakers in the transmission switchyard opened causing a turbine trip on loss of load. A pre-existing mechanical failure of a connecting wire lug created an open circuit in the pilot wire circuitry. The power surge from the lightning strike coupled with this open circuit caused the pilot wire relay to act as an over current protection device which opened the breakers. The transmission switchyard breakers and associated interlocks operated as designed protecting station equipment. During the event, the in-house electrical buses were automatically transferred from the Normal Station Service Transformer (NSST) to the Reserve Station Service Transformer (RSST) causing a momentary loss of the nonsafety grade 120 volt power supplies (VR-11 and VR-21). This affected multiple components which required additional operator actions. The systems functioned as expected based upon the signals received. The operators took actions as trained and in accordance with procedures. No equipment was damaged as a result of this event. The unit was brought to a stable condition in hot-standby (Mode 3) and the lug was repaired. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B).
3362008004 | Millstone 2 | 05/24/2008 | 07/14/2008 | ML08206005 | <strong>Reactor Trip due to a Loss of Normal Power Event</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2008 at 09:38 while at less than 0.01% power in Mode 2, the Millstone Power Station Unit 2 (MPS2) reactor automatically tripped due to a loss of normal power (LNP) event. At the time of the LNP, reactor startup was in progress, the reactor was critical and power was below the point of adding heat. Plant electrical power was supplied from the reserve station service transformer (RSST). The LNP was caused when the low-side supply breakers from the RSST to the 4160 volt and 6900 volt buses unexpectedly opened. Opening the low-side supply breakers to the buses removed power from the reactor coolant pumps (RCP) and control element drive mechanism motor-generator (CEDM MG) sets. As a result, automatic reactor trip signals were initiated on low reactor coolant flow and low RCP speed. Loss of power to the CEDM MG sets resulted in control rods inserting into the reactor core. The emergency diesel generators started and loaded as expected. The Engineered Safety Feature Actuation System responded as expected for a LNP event. The most probable cause for the reserve station service low-side supply breakers opening is a spurious signal that was not sufficiently filtered by the primary audio tone circuitry due to degradation of the tone generation/filtering circuitry. As corrective action, the primary audio tone circuit has been disabled. A modification is being developed to improve the reliability of the audio tone circuit. Longer term corrective actions are being addressed in accordance with the Millstone Corrective Action Program. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 50.73(a)(2)(iv)(B).
3362008005 | Millstone 2 | 06/28/2008 | 08/22/2008 | ML08248004 | <strong>Feedwater Heater Level Oscillation and Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2008, at 1146 with the Millstone Power Station Unit 2 in Mode 1 at 100% power, operators manually tripped the reactor when both main feedwater pumps tripped. Main turbine combined intercept valve (CIV) testing was in progress. The testing of the #3 CIV had just been completed when the 2A feedwater heater level began oscillating. The perturbations in the feedwater heater levels caused a feedwater pump suction pressure to decrease to the pump trip setpoint tripping both pumps. The operators manually tripped the reactor prior to reaching the steam generator low level automatic trip setpoint. During the event, the in-house electrical buses were automatically transferred from the Normal Station Service Transformer to the Reserve Station Service Transformer causing a momentary loss of the non-safety grade 120 volt power supplies (VR-11 and VR-21). This affected multiple components which required additional operator actions. The systems functioned as expected based upon the signals received. The operators took actions as trained and in accordance with procedures. No equipment was damaged as a result of this event. The unit was brought to a stable condition in hot-standby (Mode 3) and the feedwater heater level control valve was repaired. Ineffective configuration control of parts allowed parts to be installed in a feedwater level control valve causing it to operate incorrectly which caused divergent feedwater heater level oscillations and the main feedwater pumps to trip. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
3382008001 | North Anna 1, North Anna 2 | 04/17/2008 | 06/13/2008 | ML08175052 | <strong>Two Service Water Pumps Inoperable Greater Than Technical Specification Allowed Completion Time</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2008, with Units 1 and 2 in Mode 1 at 100% power, planned preventive maintenance commenced on the Unit 2 "H" (2H) Emergency Diesel Generator (EDG). On March 29, 2008, the 2H EDG was returned to operable. On April 1, 2008, the Unit 1 "B" SW pump was removed from service for maintenance. On April 5, 2008, excessive oil leakage was identified on the 2H EDG. The 2H EDG was declared inoperable. The oil leakage was due to 2-EG-P-4H, standby lube oil circulating pump, pushing oil to the engine upper crank line overfilling the engine upper pistons. With the 2H EDG inoperable, the Unit 2 "A" Service Water (SW) Pump was considered inoperable. Consequently, two SW pumps were inoperable for longer than the Technical Specification (TS) allowed completion time. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications. The cause for having two SW pumps inoperable greater than the allowed TS completion time was not knowing that the 2H EDG was inoperable because of the installation of the incorrect gear set on standby lube oil circulating pump 2-EG-P-4H during the maintenance outage. Maintenance activities were completed on the Unit 1 "B" SW pump and 2H EDG and the equipment was returned to operable. A PRA analysis was performed and determined that the core damage probability associated with the event was low.
3392008001 | North Anna 2 | 02/08/2008 | 04/01/2008 | ML08099062 | <strong>Manual Reactor Trip Due to Shutdown Bank "A" Group Step Counter Deviation Greater Than Allowed</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2008, Unit 2 was in Mode 3, zero percent power, preparing for restart following a planned maintenance outage. At 1759 hours, a rod control urgent failure alarm was received while withdrawing the "A" Shutdown Bank control rods. Rod withdrawal was stopped and it was noted that the Group Step Counters deviated by three steps. As a result, at 1812 hours a manual reactor trip was initiated by opening the reactor trip breakers in accordance with Technical Requirement 3.1.3. This is a valid actuation of the Reactor Protection System. Four suspect cards were replaced in Power Cabinet 2AC. Following card replacement the reactor trip breakers were closed. Shutdown Banks "A" and "B" were fully withdrawn with no concerns. On February 8, 2008, at 1959 hours, a nonemergency 8-hour report was made in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Reactor Protection System. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in manual actuation of the Reactor Protection System. This event posed no significant safety implications because the reactor was subcritical when the reactor trip breakers were opened. Compliance with all Technical Requirements was maintained. Therefore, the health and safety of the public were not affected by this event.
3392008002 | North Anna 2 | 10/18/2008 | 12/12/2008 | ML08353061 | <strong>Both Trains of High Head Safety Injection Inoperable due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2008 Unit 2 was in Mode 3 at 1400 psig and 360 degrees Fahrenheit. At 1125 hours, it was recognized that both trains of High Head Safety Injection (HHSI) had been inoperable for approximately eight (8) hours as a result of having both boron injection tank inlet isolation valves inoperable. At this time TS 3.0.3 was applicable, with thirteen (13) hours to reach Mode 4 and thirty seven (37) hours to reach Mode 5. At 1205 hours, boron injection tank inlet isolation valve 2-SI-MOV-2867A was opened (accident position) and TS 3.0.3 action was cleared. On October 18, 2008, at 1643 hours a non-emergency 8-hour report was made in accordance with 10 CFR 50.72(b)(3)(v)(D) due to both trains of Safety Injection being inoperable. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(v)(D) for a condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. This event posed no significant safety implications since the reactor coolant system was borated to cold shutdown conditions and 2-SI-MOV-2876A was opened and TS 3.0.3 was exited before exceeding the time limits of TS 3.0.3. Additionally, emergency procedures identify alternate means (e.g., 2-SI-MOV-2836, BIT bypass MOV) to provide HHSI flow to the core. Therefore, the health and safety of the public were not affected by this event.
3412008001 | Fermi 2 | 01/31/2008 | 03/27/2008 | ML08098003 | <strong>Manual Reactor Scram in Response to a Trip of Both Reactor Recirculation Pumps</strong><br /><i>Abstract:&nbsp;</i>At 15:44 hours EST January 31, 2008, the reactor mode switch was taken to shutdown in response to the trip of both reactor recirculation pumps. This inserted a manual reactor scram within 9 seconds of the trip of the recirculation pumps. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of approximately 157 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Pressure control was maintained by the main turbine bypass valves. Reactor dome pressure peaked at about 1077 psig. Reactor water Level 3 isolations occurred as expected. There was no maintenance or testing in progress that would explain the pump trips. No operator performance issues were identified in response to this event. Safety related plant equipment responded as expected to the manual reactor scram. This event posed no significant safety implications because the reactor protection and safety related systems functioned as designed following the manual reactor trip. The cause of both recirculation pump trips was determined to be an intermittent failure of the 65G bus undervoltage trip logic. The undervoltage relay and its cutoff knife switches were replaced. The undervoltage circuit fuses were replaced, fuse clips tightened, connections cleaned, continuity checked, and the circuit was meggered to identify any potential faults prior to restart of the unit.
3412008002 | Fermi 2 | 03/12/2008 | 04/22/2008 | ML08120059 | <strong>Secondary Containment to Suppression Chamber Vacuum Breaker Functionality</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2008 at 1445 hours, with Fermi 2 operating at 100 percent power, it was identified that the differential pressure switches that operate to open the reactor building to suppression chamber vacuum breaker isolation valves would not perform their safety function. The condition impacted the function of both reactor building to suppression chamber vacuum breaker isolation valves. These isolation valves are in series with the reactor building to suppression chamber vacuum breakers and automatically open to establish a flowpath to the vacuum breakers for equalizing the pressure between the suppression chamber and the reactor building during postulated accident events involving failure to secure drywell spray following a steam leak in the drywell and following a design basis accident (DBA). The failure was caused by operation of the pressure switches outside their qualified range. This event was evaluated and determined to have no significant safety implications based on the change in Large Early Release Frequency of 8.4E-8/yr, which is less than the limit of 1.0E-7/yr. The differential pressure switches were replaced with a model having a range that encompasses the normal suppression chamber pressure. This event is being reported under 10 CFR 50.73(a)(2)(v)(D), as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
3412008003 | Fermi 2 | 03/26/2008 | 05/19/2008 | ML08149032 | <strong>Control Center Pressure Boundary Door Blocked Open</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2008, at 1045 hours, it was recognized that Auxiliary Building Door R5-6 is part of the Control Center (CC) pressure boundary. The door had been blocked open since March 24, 2008, at approximately 1400 hours, to allow for passing a drain hose that was being used to drain the Division 1 chiller of the Control Center Air Conditioning (AC) System. Upon realizing that the door is part of the CC pressure boundary, Technical Specification (TS) 3.7.3, Condition B.1 was entered for two inoperable Control Room Emergency Filtration (CREF) Subsystems due to inoperable control room boundary. Actions were taken to promptly remove the drain hose and close the door. The TS Condition was exited on March 26, 2008, at 1120 hours. The primary cause of this event was attributed to missing information in one of the maintenance procedures used in the preparation work for performing maintenance activity on the Division 1 chiller of the Control Center AC System. The procedure identified other doors as control center pressure boundary barriers; however, door R5-6 was not identified as such. Review of the maintenance procedure was performed to ensure that all other control center pressure boundary doors are properly identified. All control center pressure boundary doors were verified closed. During the period of time the door was blocked open, plant conditions did not require isolation of the control room and shifting CREF into the recirculation mode; therefore, this event did not result in an appreciable reduction of plant safety and reliability.
3412008004 | Fermi 2 | 04/09/2008 | 05/30/2008 | ML08157034 | <strong>Relay Locking Straps Not Fully Engaged</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2008, in preparation for planned maintenance to replace a relay, the relay locking straps for two installed relays were discovered not fully engaged. This condition was subsequently determined to exist on five relays. All relays were Agastat relays. Operations and Engineering reviewed the relay functions and determined that with the exception of one control relay for Reactor Core Isolation Cooling (RCIC) system Level 8 trip, all other relay design functions were met by redundant relays. In the case of the control relay for RCIC Level 8 trip, an automatic level 8 trip function would not occur if the relay failed to operate as a result of the relay locking strap not being fully engaged. This event is being reported under 50.73(a)(2)(i)(B), as a condition which was prohibited by Technical Specifications for the RCIC Level 8 control relay and a high drywell pressure control relay. This event is also reportable under 50.73(a)(2)(vii), as a common cause inoperability of independent trains or channels since a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems. Calculated values for the change in Core Damage Frequency (CDF) and Large Early Release Frequency (LERF) demonstrate the safety significance of this issue was very low. Corrective actions for this licensee-identified condition include training for instrument technicians and operators and revision to preventative maintenance documents for similar relays.
3412008005 | Fermi 2 | 12/04/2008 | 01/26/2009 | ML09042006 | <strong>Loss of High Pressure Coolant Injection System Safety Function due to Closure of Steam Supply Valve</strong><br /><i>Abstract:&nbsp;</i>On December 04, 2008 at 17:35 EST during High Pressure Coolant Injection (HPCI) system steam line warming performed as part of a planned system pump and valve surveillance test, the HPCI Steam Supply Outboard Isolation Valve Bypass Valve (E4150F600) position indication lights did not function as expected. Upon discovery of the problem, Operations determined that the ability of the E4150F600 valve to close on a containment isolation signal was unreliable, and declared the valve inoperable. Containment Isolation Limiting Condition for Operation (LCO) 3.6.1.3 Condition A was entered for the E4150F600 valve, and the required action to isolate the penetration within four hours was completed on December 04, 2008 at 21:18 EST which rendered the HPCI System inoperable and unable to perform its intended safety function. A 14-day LCO was entered at that time for an inoperable HPCI System per LCO 3.5.1. System troubleshooting, diagnostic testing, and analysis were performed. The cause of the event was attributed to degraded contacts in a control relay (CR1), and it was replaced. Post maintenance testing was successfully completed. The HPCI Steam Supply Isolation Valve was opened, the system returned to service, and the LCOs cleared by December 6, 2008 at 00:12 EST. The HPCI system was out of service for less than 27-hours of the 14-days allowed by the Technical Specifications. The safety consequences of this event were evaluated using the Probabilistic Safety Analysis (PSA) Model and determined to be very low.
3462008001 | Davis-Besse | 01/04/2008 | 02/28/2008 | ML08064020 | <strong>Pressure Boundary Leak Found During Decay Heat Removal Drop Line Weld Overlay</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2008, during the Fifteenth Refueling Outage with the plant in Mode 6, while installing a pre-emptive full structural weld overlay of alloy 52M weld material for mitigation of an alloy 600/182/82 weld on the 12-inch decay heat drop line branch connection from the Reactor Coolant System hot leg, the weld machine operator identified reactor coolant water seeping from a small hole. The weld overlay was stopped, and both loops of the decay heat removal system were declared inoperable. Ultrasonic examination and excavation of a repair cavity confirmed a single axial flaw approimately 1.75 inches long in the nozzle-to-elbow dissimilar metal butt weld. The probable cause was attributed to Primary Water Stress Corrosion Cracking (PWSCC). The corrective action consisted of completing the structural weld overlay after a repair to seal the axial flaw. The overall safety significance of this event is low. Although the welds may be susceptible to PWSCC that can result in small leaks, industry experience with PWSCC shows that complete failure of the weld joints is considered to be very likely.
3482008001 | Farley 1 | 03/13/2008 | 05/09/2008 | ML08130083 | <strong>Emergency Diesel Generator 1B Exhaust Pipe Failure</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2008 at 16:24 hours, during testing of Emergency Diesel Generator (EDG) 1B [EK], the EDG exhaust line failed. The exhaust from the EDG heated the room and resulted in actuation of the CO2 fire protection system in the 1B EDG room. The actuation of the CO2 system resulted in alarms in the control room. The EDG building System Operator notified the Control Room of unusual noise coming from the EDG 1B room and that a fog of CO2 was actuating. Main Control Room personnel unloaded and shut down EDG 1B at 16:26 hours. The presence of CO2 in the EDG building resulted in operations evacuating the building at 16:30 hours. An ALERT was declared at 16:44 hours. Later investigation revealed that a section of the exhaust piping had failed due to the section of pipe not being fully welded to the connecting flange. The exhaust system on EDG 1B was a new stainless steel system that was installed on February 9, 2008. Corrective action was taken to fully weld each of four flanges on the exhaust piping on EDG 1B. EDG 1B was returned to service March 16, 2008 at 02:54 hours. For the exhaust header replacement project, work order planning sequences for the two remaining EDGs scheduled for replacement have been enhanced to require field welding of these flanges and post maintenance testing of the connections.
3482008002 | Farley 1 | 04/15/2008 | 06/11/2008 | ML08164061 | <strong>TS 3.0.3 Entry due to Inoperability of Residual Heat Removal System</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2008 control room operators identified several Emergency Power Board (EPB) alarms for the Service Water structure shared Load Control Center (LCC) 1-2L [EC]. Along with the alarms the operator noted that the lights on the EPB for the 1-2L LCC were dimming. Troubleshooting efforts were initiated and voltage on the 1-2L LCC was found to be fluctuating below the Technical Specifications (TS) minimum. LCC 1-2L was declared inoperable at 0849 hours. This resulted in the B-Train Service Water (SW) Battery Chargers being inoperable and thus, B-Train SW for Unit 1 and Unit 2 was inoperable. At this same time, A-Train of Residual Heat Removal (RHR) for Unit 1 was inoperable due to a planned equipment outage. TS 3.0.3 was entered due to both trains of RHR being inoperable on Unit 1. This also represented a loss of the safety function to remove residual heat. At 1029 hours Unit 1 exited TS 3.0.3 when A-Train RHR was returned to service. No A-Train safety related equipment was out of service on Unit 2. Troubleshooting efforts identified a loose connection for the phase 2 bus bar on the Unit 1 side of this split 1-2L LCC. LCC 1-2L has been repaired. Based on the extent of condition review, a corrective action plan has been developed to perform periodic testing or inspection of the 4160 volt switchgear, 600 volt LCCs, and 600 volt Motor Control Centers to ensure the integrity of bolted connections on the bus bars.
3482008003 | Farley 1 | 07/21/2008 | 09/15/2008 | ML08261022 | <strong>Emergency Diesel Generator 1-2A Lube Oil Heat Exchanger Leak</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2008 water was discovered in the Lube Oil [LA] sump and the Lube Oil Heat Exchanger [LB] of Emergency Diesel Generator (EDG) 1-2A [EK] during investigation of a high level alarm in the Rocker Arm Lube Oil Reservoir. The Lube Oil sump level was found to be three inches above the normal level which represents approximately 300 gallons. An additional 65 gallons of water was drained from the Lube Oil Heat Exchanger shell side drains. EDG 1-2A (an A-Train EDG) was declared inoperable on July 21, 2008 at 2058 hours. Unit 1 B-Train EDG had been previously removed from service on July 20, 2008 for a planned exhaust header replacement. The combination of both diesels being out of service required entry into Technical Specification (TS) 3.8.1 Conditions E and F. A technical specification required shutdown from Mode 1 to Mode 3 was commenced at 0541 CST on July 22, 2008 in accordance with TS 3.8.1 Condition F, which required Unit 1 to be placed in Mode 3 prior to 1058 hours. Unit 1 reached Mode 3 at 1046 hours. Eddy current and pressure testing was performed on the Lube Oil Heat Exchanger with two tubes showing indication of leakage. Four additional tubes were preventatively plugged. The Lube Oil Heat Exchanger was hydrostatically tested with no indication of leakage. The entire diesel lube oil sump contents were drained and the engine cleaned to remove any residual water. EDG 1-2A was returned to service on July 29, 2008 at 2000 hours. EDG 1B was returned to service on July 28, 2008 at 0921 hours. Until the failed tubes can be removed and the leakage mechanism determined, monitoring of all EDG Lube Oil Sumps and Lube Oil Heat Exchangers has been increased.
3482008004 | Farley 1 | 11/19/2008 | 01/07/2009 | ML09008012 | <strong>Reactor Trip due to Loss of RCP Breaker Position</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2008 at approximately 04:25, Farley Unit 1 was operating at 100 % power. Due to a gradual drop in 4160 v safety related bus voltage over the last several hours from grid conditions, Farley contacted Alabama Power - Alabama Control Center (ACC) to discuss removing the shunt reactor from service in the Farley High Voltage Switch Yard (HVSY) to raise the 230 kv grid voltage. After receiving the request, the ACC operator used an air-break disconnect switch to isolate the shunt reactor, instead of using the breakers normally used for this purpose. Opening the disconnect switch which is not designed to break load, caused a significant electrical arc and phase to phase fault. The transmission protection system tripped the appropriate devices and cleared the fault in approximately 3 cycles. However, the instantaneous HVSY voltage drop resulted in loss of breaker position indication for the 1B Reactor Coolant Pump (RCP) [AB] which initiated an automatic Solid State Protection System (SSPS) [JC] reactor trip. Flow to the reactor core was never lost. The reactor tripped without complications and all safety systems performed normally. The switching control screens for ACC have been updated to alert the ACC operator of the requirement to isolate the shunt reactor prior to operating the air-break disconnect and the requirement to use switching orders for operations at the Farley HVSY. Farley Operations shift personnel and ACC personnel have been briefed of the event.
3522008001 | Limerick 1 | 03/16/2008 | 05/12/2008 | ML08133025 | <strong>Core Alteration with Source Range Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage a control rod was withdrawn with the source range monitor in the affected core quadrant inoperable. The source range monitor was restored to operable and the control rod was inserted. The root causes of this event were that the control room supervisor and reactor operator failed to ensure the 1C Source Range Monitor was not bypassed and the control room supervisor failed to obtain a peer check by a second senior reactor operator prior to declaring it operable. The source range monitor channel check surveillance test was revised to ensure the source range monitors and intermediate range monitors are inserted and not bypassed. The site procedure for returning equipment to service will be revised to require a peer check for operability decisions when returning equipment to service.
3522008002 | Limerick 1 | 03/22/2008 | 05/19/2008 | ML08140080 | <strong>Automatic Actuation of Reactor Protection System due to Invalid Power/Load Unbalance Condition</strong><br /><i>Abstract:&nbsp;</i>A valid automatic actuation of the reactor protection system occurred as a result of an invalid power/load unbalance actuation. This invalid power/load unbalance actuation caused an actuation of the main generator protection lockout relays, which resulted in a Main Turbine trip. The root cause of this event was the main generator protection relay logic that failed due to a defective relay. The main generator relay testing procedures will be revised to include a circuit loop signal verification test to ensure reliability of newly installed equipment.
3522008003 | Limerick 1 | 11/02/2008 | 12/30/2008 | ML09005032 | <strong>High Pressure Coolant Injection System Instrument Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>The High Pressure Coolant Injection system was rendered inoperable due to observed oscillations in the system flow indication. The condition was corrected by recalibration of a flow transmitter, replacement of a square root converter, and replacement of a degraded inverter in the turbine control system. Failure analysis will be performed on the degraded inverter.
3522008004 | Limerick 1, Limerick 2 | 11/11/2008 | 12/31/2008 | ML09005034 | <strong>Remote Shutdown Procedure Error</strong><br /><i>Abstract:&nbsp;</i>The procedure for performing a remote shutdown during a MCR or cable spreading room fire did not include a step to align the reactor core isolation cooling system suction to the suppression pool. This alignment is assumed in the plant fire safe shutdown analysis. The procedure was revised to add the required step.
3532008001 | Limerick 2 | 01/12/2008 | 02/02/2009 | ML09033039 | <strong>Valid Actuation of the D23 Emergency Diesel Generator Bus Undervoltage Logic</strong><br /><i>Abstract:&nbsp;</i>A valid actuation of the D23 Emergency Diesel Generator bus undervoltage minimum actuation logic occurred following manual operator action to mitigate a bus overvoltage condition during emergency diesel generator post maintenance testing. The event was caused by a failure of the emergency diesel generator voltage regulator due to an intermittent failure of the #1 rectifier bank. The emergency diesel generator voltage regulator was swapped to the #2 rectifier bank and the emergency diesel generator governor tuning was successfully completed. The #1 rectifier bank was replaced and a failure analysis was performed. The failure was primarily caused by looseness at a bolted connection and corrosion at the rectifier flyback diode.
3532008002 | Limerick 2 | 02/01/2008 | 03/31/2008 | ML08091006 | <strong>Automatic Actuation of the Reactor Protection System at Power</strong><br /><i>Abstract:&nbsp;</i>A valid automatic actuation of the reactor protection system occurred as a result of a phase-to-ground fault at the 2A Main Transformer low voltage (22 kV) bushing connection to the Iso-Phase bus. The Main Generator neutral overvoltage relay actuated and tripped the generator protection lockout relays, which resulted in a Main Turbine trip. The cause of the ground fault was overheating of the bolted connection between the Main Transformer bushing and the flexible links that connect the bushing to the Iso-Phase Bus. The degraded bushings and flexible links were replaced. The transformer maintenance procedure was revised to provide enhanced direction for assembly of the bolted connection.
3532008003 | Limerick 2 | 04/15/2008 | 06/12/2008 | ML08170023 | <strong>Condition Prohibited By Technical Specifications Due To Inoperable Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>The Hi-Hi radiation alarm setpoint for the process radiation monitor on the reactor enclosure cooling water system was discovered to be exceeding the Technical Specification allowable value by the surveillance test coordinator during a review of completed surveillance test documentation. The required grab samples were not collected during the affected period. The condition was caused by a less than adequate self-check by the technician recording the as found data during the functional test surveillance. In addition the peer check and supervisory review of the test data were less than adequate. A work group stand-down was performed to reinforce the consequences of not applying the barriers that are designed for error prevention. All Instrument and Control (I&C) work group surveillance test performers perform an independent verification and initial each surveillance test data table. I&C supervisors review and initial each surveillance test data table. I&C surveillance test reviewer training will be performed to reinforce the critical risk elements of reviewing surveillance tests.
3542008001 | Hope Creek | 01/19/2008 | 03/18/2008 | ML08085056 | <strong>Reactor Recirculation Pump Motor Generator Set Scoop Tube Mechanical and Electrical Stop Over Speed Set Points Found Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2008, during the performance of 18 month Technical Specification (TS) Surveillance Requirement 4.4.1.1.3 to demonstrate operability of the reactor recirculation pump Motor Generator (MG) set scoop tube mechanical and electrical stops, the "A" and "B" MG set mechanical and electrical stops were found non-conservatively high. In accordance with the surveillance procedure, the stop set points were adjusted to their proper settings. An eight-hour notification was made for this event under the provisions of 10CFR50.72(b)(3)(v)(D). An apparent cause evaluation was conducted. Corrective actions include adjusting the Stop set points to their proper settings, review of the Recirculation System trending program to identify any near term changes needed to ensure compliance with TS 4.4.1.3, benchmarking of the Recirculation System trending program, and consideration of revision of the TS BASES. A similar LER, Hope Creek, LER 2000-010-000, described the "B" recirculation pump motor-generator set stops as being set non-conservatively high. The LER was retracted after further investigation showed an error was made in the calibration of the stops and the Technical Specification required set point values for the stops were never exceeded.
3542008002 | Hope Creek | 04/22/2008 | 10/17/2008 | ML08303013 | <strong>BLOWN 1E INVERTER MAIN FUSE WITH ONE EMERGENCY DIESEL GENERATOR INOPERABLE CAUSES LOSS OF CONTROL ROOM EMERGENCY FILTRATION LOSS OF SAFETY FUNCTION</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2008, the CD481 1E Safety Related Inverter Main Power input fuse failed. This failure combined with the `D' Emergency Diesel Generator being in a maintenance outage caused both trains of the Control Room Emergency Filtration (CREF) system to be INOPERABLE. This constituted an entry into Technical Specification (TS) 3.0.3. and a loss of the control room emergency filtration function in the event of a Loss of Offsite Power (LOOP). An eight-hour notification was made for this event under the provisions of 10CFR50.72(b)(3)(v)(D). A prompt investigation and an equipment apparent cause evaluation were conducted. The apparent cause of this event was a spurious misfire of Silicon Controlled Rectifiers (SCR's) in the inverter or static switch section. This caused a 1/2 cycle (or less) short circuit failure of the main input 600-amp DC fuse. Corrective actions included replacing the blown fuse in CD-481 and checking the voltage output for stability before restoring to normal power.
3542008003 | Hope Creek | 10/05/2008 | 12/04/2008 | ML08350036 | <strong>HPCI Inoperability due to Instrument Failure Initiated Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2008 at 0431, during a channel calibration associated with the High Pressure Coolant Injection (HPCI) Div 3 Steam Leak Detection Temperature Monitor, the Nuclear Measurement Analysis and Control (NUMAC) drawer failed. During troubleshooting activities the drawer was down powered and re-powered resulting in a HPCI isolation signal and HPCI turbine trip signal. The HPCI isolation valve was de-energized to prevent an inadvertent isolation however no actions had been taken to prevent the turbine trip. This resulted in unavailability and inoperability of the HPCI System. The NUMAC drawer failed during the final steps of the surveillance test and the NORMAL/BYPASS switch had been returned to NORMAL. When the NUMAC was re-powered, the initialization caused isolation and turbine trip signals. Having the appropriate breaker open prevented the isolation, however the turbine trip was not prevented. The troubleshooting log, which was prepared and approved, did not require a precaution to prevent a HPCI turbine trip. Corrective actions include: roll-out communications to all supervisors regarding adequate rigor and questioning attitude in preparing simple troubleshooting; addition of turbine trip to the reference document used to prepare the troubleshooting log; an extent of condition review for the need to revise additional reference documents; and, presentation of the issue to the Licensed Operator Requalification Curriculum Review Committee for knowledge of protective functions of the equipment.
3612008001 | San Onofre 2 | 01/23/2008 | 02/22/2008 | ML08057009 | <strong>Valid Actuation of Emergency Feedwater System following Main Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On 1/23/08, at about 1415 PST, with SONGS Unit 2 in Mode 1 at about 95 percent one of two main feedwater (MFW) [SJ] pumps tripped on low oil pressure. Control room operators manually actuated the emergency feedwater system (AFW) [BA] in accordance with plant procedures. The AFW system responded successfully. Control room operators reduced reactor power level to about 65 percent which can be sustained with one normal feedwater pump in operation. The AFW manual actuation by plant operators was in response to the MFW pump trip. The MFW pump trip was due to overadjustment of the pump lubricating oil pressure regulator. Maintenance workers used the pump overhaul procedure that did not provide sufficient detail to adjust the oil pressure regulator while the pump is on-line. The oil pressure regulator was correctly adjusted and the Unit was returned to power. SCE is completing a cause evaluation which may identify additional corrective actions. All systems responded as designed and Control Room personnel acted timely and correctly. Neither the health nor the safety of plant personnel or the public were affected by this occurrence. No valid actuation of the AFW due to inappropriate procedures has occurred over the last 3 years.
3612008002 | San Onofre 2, San Onofre 3 | 05/20/2008 | 06/06/2008 | ML08164009 | <strong>Disturbance on the Pacific DC Intertie Cause Offsite Power Frequency to Dip Below Operability Limits</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2008, at about 1310 PDT, the offsite power grid connected to San Onofre Nuclear Generating Station (SONGS) experienced a momentary disturbance. Control Room indicators dipped below 59.7 Hz, to about 59.69 Hz. Southern California Edison (SCE) reported this event in accordance with 10CFR50.72(b)(3)(v)(D) (NRC Log No. 44227). The frequency dip at SONGS lasted approximately 10 seconds and was caused by a disturbance on the Pacific DC Intertie line in Oregon. SCE is submitting this follow-up written report in accordance with 10CFR50.73(a)(2)(v)(D). During this occurrence, Unit 2 was operating at about 99 percent power; Unit 3 was operating at about 80 percent power. During the event, both trains of onsite AC sources [EK] on Unit 3 and one train on Unit 2 were available. The size and duration of the frequency dip were small. Consequently, there was little to no safety significance to the event. There are no corrective actions required at SONGS due to this event. LER 2-2004-003, dated July 16, 2004 and LER 2-2008-003 dated June 6, 2008 also reported grid underfrequency events.
3612008003 | San Onofre 2, San Onofre 3 | 05/29/2008 | 06/06/2008 | ML08164009 | <strong>Disturbance on the Pacific DC Intertie Cause Offsite Power Frequency to Dip Below Operability Limits</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2008, at about 1136 PDT, the offsite power grid connected to San Onofre Nuclear Generating Station (SONGS) experienced a momentary disturbance. Control Room indicators alerted Operators that grid frequency dipped below 59.7 Hz, to about 59.6 Hz. Southern California Edison (SCE) reported this event in accordance with 10CFR50.72(b)(3)(v)(D) (NRC Log No. 44247). The frequency dip at SONGS lasted approximately 10 seconds and was caused by a disturbance on the Pacific DC Intertie line in California. SCE is submitting this follow-up written report in accordance with 10CFR(a)(2)(v)(D). During the occurrence, Unit 2 was operating at about 99 percent power; Unit 3 was operating at about 80 percent power. During this occurrence, all trains of Emergency Diesel Generation (EDG) [EK] on both Units 2 and 3 were available. The size and duration of the frequency dip was small. Consequently, there was little to no safety significance to the event. There are no corrective actions required at SONGS due to this event. LER 2-2004-003, dated July 16, 2004 and LER 2-2008-002, dated June 6, 2008 also reported grid underfrequency events.
3612008004 | San Onofre 2 | 06/05/2008 | 08/01/2008 | ML08218022 | <strong>Malfunctioning Stator Water Cooling System Check Valve Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2008 (Event Date), with Unit 2 at approximately 97 percent power, plant personnel began a monthly test of the stator water cooling system. In accordance with the test procedure, Operators swapped the stator water pumps by starting the pump that was in standby and then stopping the operating pump. Three alarms were received in quick succession indicating a reduction in stator water flow. Approximately two minutes later, the Main Generator [TA] tripped from a "Rectifier Low Flow." At approximately 2256 PDT, Unit 2 reactor automatically tripped on a "Loss of Load" signal. SCE's cause evaluation concluded that a pump discharge check valve momentarily remained open following the stator water pump swap and then slammed shut. The resulting pressure spike was sufficient to lift one or both of the relief valves on the stator water heat exchangers. The discharge from the relief valve(s) reduced stator cooling water flow and resulted in a main generator trip and a reactor trip. SCE repaired the malfunctioning check valve and has suspended monthly stator water cooling flow testing at both Units pending further evaluation. This event remained bounded by the Updated Final Safety Analysis evaluation of a loss of load event. Therefore, the significance of this event was minimal.
3612008005 | San Onofre 2, San Onofre 3 | 06/09/2008 | 07/30/2008 | ML08217029 | <strong>Missed Surveillance and Plant Mode Change Causes TS Violation</strong><br /><i>Abstract:&nbsp;</i>On 6/9/08 at about 1314 PDT, San Onofre Nuclear Generating Station, Unit 2 entered Mode 2 from Mode 3 in accordance with startup procedures. At about 1443 PDT, the Control Room Supervisor (CRS) recognized that the Control Element Assembly (CEA) [AA] Alignment Surveillance Requirements (SR) 3.1.5.1 and SR 3.1.5.2 had not been completed prior to Mode change. (Technical Specification (TS) 3.1.5 is applicable in Modes 2 and 1, but not in Mode 3 or lower). Because SR 3.0.4 prevents entry into Modes without completion of all applicable SRs, SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). Operators completed the surveillances with satisfactory results. Consequently, there was no safety significance to this occurrence. This event was caused by (1) a lack of detail in the applicable procedure and (2) lack of oversight by the Control Room Supervisor (Utility, Licensed). SCE has coached the Operator's (Utility, Licensed) involved and will revise the affected procedure. LER 3-2006-005, dated 1/26/07, reported an instance of exceeding 20 percent power without all required SRs completed. That event resulted from a boron dilution error during startup. LER 2-2007-002, dated 8/17/07, reported a missed TS SR required with the plant entered Mode 3 following a failure of the instrument air system and consequential plant trip.
3612008006 | San Onofre 2 | 03/25/2008 | 09/17/2008 | ML08266003 | <strong>Loose Connection Bolting Results in Inoperable Battery and TS Violation</strong><br /><i>Abstract:&nbsp;</i>On 3/25/08, with Unit 2 at about 100 percent power, plant personnel were performing surveillance (SR 3.8.4.1) of a 1E battery and discovered its voltage below the required value. Subsequently, signs of a loose connection were observed on the breaker connecting the battery to its DC bus, which provides charging current in its normal configuration. Reactor Operators (RO)s declared the battery inoperable, entering TS 3.8.4 Action A, while actions to find and fix the cause of the low reading continued. At about 0840 PDT, ROs initiated actions to shutdown upon entering TS 3.8.4 Action B. SCE determined the low voltage was caused by loose bolts on the DC breaker. By 0850 PDT on 3/25/08, SCE had torqued the loose connection bolts and completed the required TS SRs with satisfactory results. ROs declared the battery operable, terminated the plant shutdown, and returned the unit to full power. SCE determined that the degraded electrical connection on the DC breaker was due to an incomplete work plan and lack of checks during installation. SCE believes that the degradation most likely caused the battery to be inoperable for about 4 days prior to discovery (see Safety Significance section). This exceeds the TS allowed outage time of 2 hours, SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). SCE has initiated action to improve SONGS electrical work plans.
3612008007 | San Onofre 2, San Onofre 3 | 08/22/2008 | 11/14/2008 | ML08323004 | <strong>Failure to Comply with TS Surveillance Requirement Completion Time</strong><br /><i>Abstract:&nbsp;</i>On 09/18/2008, SCE identified a practice that did not satisfy a Technical Specification (TS) Condition requirement. TS 3.8.1, Condition B, requires surveillance requirement (SR) 3.8.1.1, AC Sources Verification, within 1 hour after declaring an Emergency Diesel Generator (EDG) inoperable, and once per 8 hours thereafter. In contrast, for planned periods of EDG inoperability, Operators (Licensed) performed SR 3.8.1.1 within 1 hour prior to declaring an EDG inoperable, and once per 8 hours thereafter. This practice has existed since initial plant startup, and was consistent with San Onofre Nuclear Generating Station (SONGS) original TS but not with SONGS Improved TS (implemented August 5, 1996). This event was caused by an inadequate procedure that was inconsistent with the improved TS. For planned periods of EDG inoperability, the procedure directed Operators (Licensed) to perform SR 3.8.1.1 prior to declaring the EDG inoperable. This practice, although prudent, is inconsistent with TS 1.3, Completion Time, which specifies that completion time begins at the time the condition is entered (i.e., the EDG is declared inoperable). The applicable SR 3.8.1.1 implementation procedure has been revised to clearly specify the SR must be performed within 1 hour after declaring the equipment inoperable. SCE reviewed other TS SRs and found no similar examples.
3612008008 | San Onofre 2 | 07/15/2008 | 04/03/2009 | ML09098029 | <strong>Missed Technical Specification Surveillance Requirement on Spare Station Battery BOOX</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2008, SCE identified that spare 125 VDC Station Battery BOOX did not have all current completed Technical Specification (TS) Surveillance Requirements (SR) when it was put in-service from July 15 - July 17, 2008. This resulted in a violation of TS Limiting Condition of Operation (LCO) 3.8.6 and 3.8.4. The applicable SR was successfully completed on BOOX on July 26, 2008. This event was caused by a combination of incorrect procedure use and failure to properly implement a transition plan for scheduling TS surveillance testing. SONGS personnel improperly made pen-and-ink changes to a surveillance Maintenance Order. On July 1, 2008, SONGS transitioned from the MOSAIC System to the new Enterprise Resource Planning (ERP) System which significantly changed the process for scheduling TS surveillances. Prior to the transition to ERP, a transition plan was developed to ensure surveillances were completed in accordance with the applicable schedule. This transition plan was not properly implemented, resulting in the missed SR for BOOX. SCE conducted an extent of condition review and identified other examples where the transition plan was not properly implemented resulting in other missed IS SRs. The other missed TS SRs were successfully completed after the 25% extension allowed by IS SR 3.0.2 (i.e., 1.25 times the required surveillance interval), but did not result in additional reportable TS violations.
3622008001 | San Onofre 3 | 09/01/2008 | 10/27/2008 | ML08302036 | <strong>TS Required Shutdown due to EDG Repair beyond Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On 9/1/08, at about 1035 PDT, with Unit 3 near full power, plant operators manually initiated a plant shutdown to complete repairs on Emergency Diesel Generator (EDG) 3G003. A condition identified while performing testing following the replacement of the generator, required the EDG to be inoperable longer than allowed by Technical Specification 3.8.1 (14 days). At 1403 PDT, SCE reported initiation of the shutdown on 9/1/08 (NRC Log No. 44456) under 10 CFR 50.72(b)(2)(i). Operators tripped the reactor on 9/1/08 at 14:47 PDT. SCE is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(A). The Allowed Outage Time (AOT) began on 8/19/08 as planned maintenance that included replacement of bearings on Diesel fuel racks and an inspection of the generator. The inspection revealed cracks in the shorting ring, requiring replacement of the generator. Post-maintenance testing revealed anomalous readings that could not be resolved during the AOT. Subsequently, SCE determined that the readings were due to an improper fit of a newly replaced bearing, causing momentary binding of a fuel rack. The bearing was replaced, the Surveillance Requirements met and the EDG was returned to Operable status. The reactor returned to Mode 1 on 9/11/08 at about 22:22 PDT. The shutdown was a normal, uncomplicated plant shutdown. Therefore, the significance of this event was minimal.
3622008002 | San Onofre 3 | 12/19/2008 | 02/17/2009 | ML09049014 | <strong>Loose Fuse Results in Inoperable Auxiliary Feedwater Pump and TS Violation</strong><br /><i>Abstract:&nbsp;</i>On 12/19/08, at about 1651 PST, with Unit 3 in Mode 1 at about 55 percent power, Control Room personnel received a Turbine Auxiliary Feedwater (AFW) pump governor/overspeed out-of-service alarm. Voltage measurements of the AFW control circuit indicated an open circuit across a fuse. SCE determined the clip retaining the fuse was sprung. SCE concluded the clip was damaged when the fuse was pulled during maintenance performed on 12/9/08. Although the circuit was tested successfully during a surveillance on 12/12/08, SCE concluded that, due to the loose clip, the circuit may not have functioned in a seismic event. Technical Specification 3.7.5 requires restoration of an inoperable AFW train within 72 hours. Because the AFW pump was in service for about 10 days and 5 hours while it may not have been seismically qualified, SCE is reporting this event in accordance with 10CFR50.73(a)(2)(i)(B). The clip was repaired and the AFW pump declared operable at 0330PST on 12/20/09. SCE removed the fuse block from Units 2 and 3 to verify conditions and is inspecting similar fuses. The calculated incremental core damage probability (ICDP) and incremental large early release probability (ILERP) are estimated to be 5E-7 and 4E-8, respectively. SCE concluded the risk significance of this event was very small.
3622008003 | San Onofre 3 | 11/30/2008 | 01/30/2009 | ML09048039 | <strong>Missed TS Completion Time Results in TS Violation</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2008, during Unit 3 startup following a refueling outage, SCE discovered that a Technical Specification required action for one of the 125V DC station batteries was not performed within its TS required action times. This caused a violation of TS 3.8.6 and TS 3.8.4. SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). SCE's cause evaluation concluded that this event occurred due to the lack of a formal process to track and ensure that battery related 7-day and 31-day actions are completed on time. Instead, SCE was relying on the maintenance personnel to track these required actions. This is not a robust tracking process and was vulnerable to a single point error. SCE successfully completed the 31 day surveillance inspection on December 1, 2008. SCE will review this event with the appropriate Maintenance Division Personnel. SCE will revise the template for battery service test and the battery performance test to require the 7 day and 31 day actions to be included in the associated work plans as separate operations within each surveillance work order and to ensure appropriate scheduling within the applicable work orders. When SCE completed the 31 day action on December 1, 2008, all battery parameters were in specification and the battery was confirmed to be operable. Consequently, SCE concludes that there was no safety significance to this event.
3642008001 | Farley 2 | 06/06/2008 | 07/29/2008 | ML08214027 | <strong>Condition Prohibited by TS 3.8.6 Battery Cell Parameters</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2008 the quarterly surveillance testing procedure (STP) was performed on the Unit 2 Auxiliary Building B-Train Battery [EJ]. The STP was signed off as satisfactory. This quarterly STP was repeated on May 7, 2008 and Cell number 33 of B-Train Battery was determined to have a voltage of 2.06 V which is below the minimum allowed cell voltage of 2.08 V. Technical Specifications (TS) Action statements were entered which resulted in Cell number 33 being replaced on June 3, 2008. On June 6, 2008 during the review of the paper work associated with this Cell replacement, SNC determined that the February 11, 2008 STP was approved in error since the recorded voltage for Cell number 33 was 2.06 V which is below the minimum allowed voltage of 2.08 V. The recorded voltage was transcribed illegibly by the journeymen and subsequently misread by the journeymen and supervisor as 2.16 V. This error resulted in the B-Train battery being inoperable between February 11 and May 7, 2008 due to not completing the required TS Action Statement. Cell number 33 of the 2B Auxiliary Building Battery was replaced on June 3, 2008. Personnel involved in the event have been coached on the importance of attention to detail when using procedures and legibility of recorded data.
3662008001 | Hatch 2 | 02/18/2008 | 05/16/2008 | ML08137059 | <strong>Leak in Vent Pipe to Process Pipe Half Coupling in RHRSW System</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2008 at 1800 EST, a crack was identified at a weld on a 3/4 inch vent line of the Residual Heat Removal Service Water (RHRSW) system. An immediate operability determination was conducted based on available information with the conclusion reached at that time that there was reasonable assurance the RHRSW system could continue to perform its safety function. Subsequent engineering review resulted in a determination on February 20, 2008 at 1505 EST that had this condition developed into a complete shearing of the vent line, with no operator action it could have prevented the RHRSW system from meeting its 30-day mission time. On February 20, 2008 at 1505 EST, the RHRSW system was declared inoperable, and both loops of RHRSW were removed from service in order to make the necessary repairs. It was postulated that a complete shear of the vent line at the crack location could have prevented continued operation of the system for 30 days, as required by the Unit 2 Final Safety Analysis Report for design basis accident (DBA) conditions. The resulting leakage from the postulated shearing of the line, over a prolonged period of operation, could have resulted in excessive water levels in the Reactor Building Torus Room area. The cause of this event is attributed to high cycle fatigue due to vibration resulting from cavitation downstream of the 2E11F068B flow control valve for the “B” loop of the RHRSW system. The vent line was repaired and the system returned to service on February 20, 2008.
3662008003 | Hatch 2 | 05/19/2008 | 07/08/2008 | ML08192018 | <strong>Crack in Reactor Pressure Boundary Piping due to High Cycle Fatigue Results in Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2008, it was determined that a condition discovered on March 8, 2005, consisting of a leak on a non-isolable portion of the reactor coolant boundary identified during the reactor vessel leakage test was reportable under 10 CFR 50.73. The leak was located in a section of one inch stainless steel instrumentation piping associated with the four inch steam supply to the reactor core isolation cooling (RCIC) system. The Technical Specification (TS) definition of pressure boundary leakage is "leakage through a non-isolable fault in the reactor coolant system." Due to its location, the leak met this definition. Pressure boundary leakage in Modes 1, 2, or 3 is not allowed by the plant's TS. Although the leak was discovered when the unit was in Mode 4, review of the failure analysis report provided indication that the leak most likely started at some point during the run cycle (i.e. during Modes 1, 2 and/or 3) leading up to the time of discovery. The piping was sent to an independent testing facility which determined the cause of the leak was failure of the pipe due to High Cycle Fatigue. Corrective actions for this event included replacing the failed weld, evaluating similar small bore Class 1 piping for additional action, and revising The Corrective Action Program to elevate the severity level even if the unit is in an operating mode at the time of condition discovery that does not require operability, and regardless of how the condition was discovered.
3662008004 | Hatch 2 | 07/01/2008 | 08/12/2008 | ML08226000 | <strong>Safety Relief Valves Allowable Test Range Exceeded due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2008 at approximately 1:00 pm EDT, Unit 2 was at 2799 CMWTh, which is 99.8 percent of rated thermal power (RTP). On that day, it was determined that during bench testing at an independent testing facility two Safety Relief Valves (SRVs) experienced setpoint drift that exceeded the allowable plant Technical Specifications (TS) limit above the setpoint value. One other SRV exceeded the allowable plant Technical Specifications (TS) limit by being below the setpoint value. The root cause of the SRV setpoint drift above the setpoint value is corrosion-induced bonding between the pilot disc and seating surface. The cause of the SRV setpoint drift below the setpoint value is initially identified to be a reduction in spring force. Immediate corrective actions for this event included replacement of the SRVs with refurbished pilot valves which have been certified to actuate within 11.5 psig of the setpoint. Each of the four pilot discs from the valves removed for testing will be replaced with a pilot disc made from Stellite 21 material. Evaluation of additional actions to further improve SRV performance will be tracked under the plant’s corrective action program.
3662008005 | Hatch 2 | 02/21/2008 | 01/29/2009 | ML09029106 | <strong>Main Control Room Environmental Control System Inoperable due to System Tagout</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2008 at approximately 1119 EST, it was determined that a written report should have been made to report an instance where the Main Control Room Environmental Control System (MCREC) was inoperable on February 21, 2008. At the time the system was inoperable Unit 2 was in the Run mode at a power level of approximately 2796 CMWTh, 99.7 percent rated thermal power. On February 21, during refueling outage 1R23, work on Essential Cabinet 1B supply breaker was to begin and a tagout was authorized to provide a clearance boundary. Prior to de-energizing Essential Bus 1B, the tagout instructions required placing Instrument Bus 1B on alternate power supply. The ‘A’ Air Handling Unit (AHU) had previously been tagged out and was still out of service. When Instrument Bus 1B was de-energized, the ‘C’ AHU tripped, and the ‘B’ AHU did not auto-start. The control room crew realized that no AHUs were operable and directed that Instrument Bus 1B be placed back on normal supply. This action took approximately 10 minutes. After power was restored to Instrument Bus 1B, the ‘C’ AHU was restarted, and the ‘B’ AHU could auto-start if required. The direct cause of the inoperable MCREC system was determined to be an inadequate clearance and tagging review to identify plant response to removing Instrument Bus 1B from service. The load list was revised to include more detail regarding response of the ‘C’ AHU on de-energizing the instrument bus or breaker, and procedures were revised to include additional details regarding expected response of ‘C’ AHU when the instrument bus is de-energized.
3682008001 | Arkansas 2 | 03/13/2008 | 05/08/2008 | ML08130037 | <strong>Containment Isolation Valve Inoperable Longer Than Allowed by Technical Specifications as a Result of Personnel Error During Planning and Construction of Scaffolding</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2008, with the plant shutdown in Mode 5, the outside containment isolation valve for the chill water system did not fully close during “as-found” stroke time testing. Investigation by Operations personnel revealed that a scaffold pole was interfering with the close stroke of the valve, resulting in it remaining approximately 30 to 40 percent open. The scaffold was constructed on March 13, 2008, while the plant was in Mode 1 at 100 percent power. Since the plant was shutdown for Refueling Outage 2R19 on March 16, 2008, the valve was inoperable for a period of time longer than allowed by the Technical Specifications. The obstruction was removed, and the valve was successfully stroke tested. The cause of this event was human error in that the walkdown conducted before the scaffold was installed did not identify the subject valve as a work site interference issue. Due to the unique design of the valve associated with this event, it was determined to be an isolated occurrence. However, a “lessons learned” discussion will be conducted with the Operations staff of both ANO units regarding this event to stress the importance of walkdowns with scaffolding personnel in identifying all potential interference issues.
3682008002 | Arkansas 2 | 04/07/2008 | 06/06/2008 | ML08155066 | <strong>Manual Reactor Trip from Hot Standby Conditions due to Perceived Inoperability of Individual Control Element Assembly Position Indication</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2008, at approximately 1345 CST, with the plant shutdown in Mode 3, and with all Control Element Assemblies (CEAs) withdrawn two steps in preparation for CEA drop time testing, the Control Room was informed that the software verification for the Control Element Assembly Calculators (CEACs) had not been verified and that the CEACS should be considered inoperable. The Shift Manager (SM) was told by Reactor Engineering (RE) personnel that the raw CEA inputs to the CEACs could not be used to verify CEA position. Although the CEACs were not required to be operable in Mode 3, at least one position indicator is required to be operable for each CEA not fully inserted. At 1350, the Shift Manager directed that the reactor trip breakers be opened to comply with the associated technical specifications action statement. The cause of this event was inadequate communication between the SM and RE personnel which led to the incorrect conclusion that the CEA position indicators were inoperable. A “Lessons Learned” document regarding this event was prepared by the involved SM and was distributed to the SMs of both ANO units.
3692008001 | McGuire 1, McGuire 2 | 03/20/2008 | 05/19/2008 | ML08149032 | <strong>Potential Failure of Containment Isolation Valves (CIV) to Remain Fully Closed and Inoperable longer than allowed by Technical Specification 3.6.3.</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2008; Air Operated diaphragm Containment Isolation Valves (CIVs) were declared inoperable when it was discovered inadequate bleed paths during thermal pressurization could cause actuator closing margins to be exceeded. Exceeding actuator closing margins could cause a CIV to open during an event requiring containment isolation. This condition existed during a mode of applicability specified in the plant's Technical Specifications (TS) and is reportable as an operation or condition which was prohibited by the plant's TS in accordance with 10CFR 50.73 (a) (2) (i) (B). In addition, since the CIV could have opened when required to be closed, this condition could have prevented fulfillment of the safety function and is reported in accordance with 10CFR 50.73(a) (2), (v) (C). The Safety Analysis for this event has concluded that this condition was not significant with respect to the health and safety of the public. Upon discovery, the applicable CIVs were declared inoperable and immediate corrective action was taken to restore CIV operability on the operating unit. Corrective actions to restore operability included modifications and procedural alignment changes necessary to restore adequate closing margins. The root cause for this event was a lack of formal expectations or guidelines relative to timely completion of corrective actions having significant regulatory impact. A previous corrective action to review calculations for air operated diaphragm valves susceptible to the thermal pressurization was not completed in a timely manner and resulted in station operation with inoperable CIVs. Corrective actions have been initiated to ensure timely completion of corrective actions having significant regulatory impact.
3692008002 | McGuire 1 | 06/26/2008 | 08/21/2008 | ML08247053 | <strong>Unit 1 Reactor Trip due to the 1B Reactor Coolant Pump Motor Trip Which Was Caused by a Failed Surge Capacitor</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event Unit 1 and 2 were in Mode 1 at 100% power. Event Description: On June 26, 2008, the 1B Reactor Coolant (NC) pump motor tripped when the 6900 Volt feeder and safety breaker over-current protective relays sensed a ground fault which in turn caused a Unit 1 Reactor trip due to low NC system flow sensed by the Reactor Protection system. Unit 1 returned to Mode on June 29, 2008. This event is considered to be of no significance with respect to the health and safety of the public. Event Cause: Electrical testing determined an NC pump motor surge capacitor had shorted to ground. The cause of the failed surge capacitor was determined to be improper design. Corrective Actions: The failed surge capacitor was replaced. Replace all the Unit 1 NC pump motor surge capacitors during the Fall 2008 refueling outage. Replace all existing surge capacitors with a more robust design. Perform a detailed electrical system analysis to determine if NC pump motor surge capacitors can be eliminated.
3692008003 | McGuire 1 | 10/31/2008 | 12/30/2008 | ML09013044 | <strong>Unit 1 Manual Reactor Trip Taken to Mitigate Control Rod Drop Caused by Shorted Control Rod Drive Mechanism (CRDM) Cable Connector</strong><br /><i>Abstract:&nbsp;</i>Event Description: On October 31, 2008, Unit 1 was in Mode 2 and performing Zero Power Physics Testing when operators received a "Rod Control Urgent Failure" annunciator. Abnormal procedure 14 was entered and subsequently re-entered when control rod K-2 dropped to the fully inserted position. The condition was terminated when the operators manually opened the Unit 1 Reactor Trip Breakers per operating procedure and completed subsequent emergency response procedure actions. This event is considered to be of no significance with respect to the health and safety of the public. Event Cause: A root cause was completed following the event and it was determined a CRDM power cable head connector failed causing the K-2 control rod to drop to the fully inserted position. It was concluded the CRDM power cable head connector design was inadequate for the application. Corrective Actions: The Unit 1 CRDM connectors were removed and the cables were spliced and tested prior to returning Unit 1 to service.
3742008001 | LaSalle 2 | 06/11/2008 | 08/08/2008 | ML08221026 | <strong>High Pressure Core Spray System Declared Inoperable due to Failed Room Ventilation Supply Fan</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2008, at 0545 CDT, the supply fan for the Division 3 Switchgear Room ventilation system (VD) [VJ] tripped unexpectedly. Division 3 AC power supports the High Pressure Core Spray System (HPCS) [BG]. HPCS remained functional and capable of vessel injection following the loss of ventilation to the Division 3 Switchgear Room; however, HPCS was declared inoperable based on long-term temperature considerations associated with potential heat up concerns of the areas served by the failed ventilation system. Because HPCS is a single train system, this occurrence is reportable under 10 CFR 50.73(a)(2)(v)(D) as an event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The direct cause of the supply fan trip was a failure of the fan motor stator winding. The apparent root cause was a failure to implement a time-based refurbishment program, which allowed the motor to be in-service beyond the expected lifetime of 20 years. Corrective actions included replacing the fan motor, and updating the preventative maintenance database to require replacement and/or refurbishment of these motors on a 20-year periodicity.
3822008001 | Waterford 3 | 03/02/2008 | 05/01/2008 | ML08135005 | <strong>Mispositioned Essential Chiller AB Return Header B Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2008, at approximately 1700, with the plant operating at approximately 100% power (Mode 1), Essential Chiller 'AB' Return Header 'B' Isolation Valve (CHW-786B) was discovered in the locked open position while its required position is locked closed. Trains 'A' and 'B' of Chilled Water were declared inoperable, and Technical Specification 3.7.12 and 3.0.3 were entered. The valve was immediately closed and locked. The valve had been inadvertently left open as a result of failure to follow a quarterly inservice inspection test procedure. With CHW-786B open, Trains 'A' and 'B' of the Essential Chilled Water System were cross-connected. With CHW-786B in the open position, train independence was not met. Both trains 'A' and 'B' of Essential Chilled Water were operable and capable of performing their safety functions during the time that the valve was left open. However, the loss of train independence violated Technical Specification 3.7.12. The valve was closed approximately 17 minutes -after entering Technical Specification 3.0.3, and Technical Specification 3.0.3 was exited. The condition did not involve an actual loss of Chilled Water since both trains of Chilled Water were operable during the affected period. The condition is not a Safety System Functional Failure. The condition did not compromise the health and safety of the general public.
3822008002 | Waterford 3 | 05/23/2008 | 07/17/2008 | ML08204027 | <strong>Inoperable Steam Generator Narrow Range Level Channels</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2008, at approximately 1400 hours, with the plant in Mode 6, Refueling (RF15), one transmitter for Steam Generator (SG) 1 and one transmitter for SG 2 used for SG narrow range level Plant Protection System (PPS) trip input were determined to be out of calibration. On May 23, 2008, the two transmitters were determined to be inoperable. Evaluation established the transmitters were inoperable since RF14. The Apparent Cause Evaluation established the condition occurred due to procedural inadequacy as the procedures did not provide sufficient detail to assure proper manipulations of valves and venting of sensing lines after installation of the SG narrow range transmitters. Technical Specification Table 3.3-1, Action 2, requires that with the number of channels operable one less than the total number of channels, which are four per Steam Generator, startup or power operation may continue provided the inoperable channel is placed in the bypassed or tripped condition within 1 hour. Since the channels were inoperable and were not placed in bypass or tripped position, as the condition was unknown to plant personnel, this condition resulted in a violation of TS Table 3.3-1. Upon discovery of this condition, both SG transmitters were calibrated during Mode 6 of RF 15, restoring the SG narrow range channels to operable status. Although one narrow range channel from each Steam Generator was determined to be inoperable, three narrow range channels were operable on each SG as required by Technical Specifications. The condition is not a Safety System Functional Failure. The condition did not compromise the health and safety of the general public.
3822008003 | Waterford 3 | 05/18/2008 | 07/17/2008 | ML08204027 | <strong>Movement of Fuel Assembly in Reactor Vessel with Fuel Handling Machine Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2008, at about 1659 hours, with the plant shut down in Mode 6 for Refuel 15, fuel assembly LAY405 was raised within the reactor vessel without automatic overload cut off protection enabled, a condition prohibited by Technical Specification 3.9.6. The refueling machine computer became nonfunctional on May 18, 2098, at approx 1621 hours. At approximately 1659 hours, the hoist was being raised with fuel assembly LAY405 to the up-limit, which is a prerequisite for rebooting the computer. Fuel assembly LAY405 was raised in a mode referred to as "Key Override" wherein automatic overload cut off protection is not enabled. Personnel raising fuel assembly LAY405 incorrectly believed that the overload cut off was enabled in key override mode. Thus, Technical Specification 3.9.6, which requires an overload cut off limit of less than or equal to 3350 pounds for the fuel mast during movement of fuel assemblies within the reactor pressure vessel, was not entered. This condition is reportable as a violation of Technical Specification 3.9.6 pursuant to 10CFR50.73(a)(2)(i)(B). Fuel assembly LAY405 was located away from other fuel assemblies and reactor internals when fuel assembly LAY405 was raised in key override mode. The fuel assembly did not contact reactor internals during the raising of fuel assembly LAY405. The condition did not involve a Safety System Functional Failure. The condition did not compromise the health and safety of the general public.
3822008004 | Waterford 3 | 09/02/2008 | 06/02/2010 | ML10180033 | <strong>Loose Intercell Connecting Bolts on 125 vdc Station Battery (Revised)</strong><br /><i>Abstract:&nbsp;</i>On 9/3/2008, at 0105 hours, with the plant in MODE 4 (associated with Hurricane Gustav), Operations declared 125 vdc Station Battery 3B-S INOPERABLE due to low voltage and entered Technical Specification (TS) 3.8.2.1. Loose bolts were discovered on an intercell connector connecting two of the 60 battery cells (57-58). The bolts were immediately tightened, and satisfactory intercell resistance readings were verified. The battery was declared OPERABLE on 9/3/2008 at 0430 hours. The point in time that an unacceptable intercell resistance formed at the loose connection was not determined when originally reported on 11/3/2008 by the voluntary LER 2008-004-00, as it was not observable by previously weekly battery surveillances. The Root Cause Analysis (RCA) was revised after this condition was reported. The RCA concluded the most likely cause of the loose connection was that the bolts were left loose during the replacement of the battery cell #56 on 5/24/2008, without tracking the configuration of this loosened connection. The clamping force from adjacent bolts was sufficient to pass the battery load test on 5/26/2008 and to declare the battery OPERABLE even though the loose connection was later reported on 1/6/2009 to have had a resistance of approximately 200 micro-ohms, as estimated by a vendor analysis of the 5/26/2008 test data. The TS 3.8.2.1 intercell resistance limit of 150 micro-ohms was exceeded for longer than allowed. The revised RCA determined that the most likely time that the connection was further degraded to the extent that the Station Battery 3B-S was no longer reasonably capable of performing its safety function occurred on 8/25/2008, when disturbed by the weekly voltage check measurement.
3872008001 | Susquehanna 1, Susquehanna 2 | 02/05/2008 | 08/29/2008 | ML08259001 | <strong>Irradiated Fuel Movement without All Required Radiation Monitoring Operable</strong><br /><i>Abstract:&nbsp;</i>Susquehanna Unit 1 and Unit 2 Reactor Buildings share a common Refuel Floor. To mitigate the consequences of a fuel handling accident, radiation monitors exists on both units to realign the Reactor Building ventilation system and initiate the Standby Gas Treatment & Control Room Emergency Outside Air Supply Systems if elevated radiation levels are detected. On 1/31/2008, a work order was implemented to defeat the Unit 1 & Unit 2 High Exhaust Radiation Monitors in support of activities on the Refuel Floor. The Exhaust Radiation Monitors are required to be operable during irradiated fuel moves and are defeated during activities which could cause a spurious trip as a result of 'shine'. A procedural checklist was Completed without confirmation that the Radiation Monitors were operable. At 1700 on 2/05/2008 permission to move fuel was documented in the control room log and then subsequently logged at 1804 that fuel moves were complete for the day. During the oncoming shift turnover that same day it was recognized that the High Exhaust Radiation Monitors were inoperable. The inability of these systems to respond to radiological conditions on the refuel floor constitutes a condition that could have prevented the fulfillment of safety functions needed to control the release of radioactive material and is reportable per 10 CFR 50.73(a)(2)(v)(C). The Control Room alarms and indications for all of these monitors remained operable and actual radiological conditions observed on the refuel floor during the fuel shuffles did not approach levels necessary for system actuation. There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3892008001 | St. Lucie 2 | 01/29/2008 | 03/27/2008 | ML08108010 | <strong>RCP 2B1 Upper Seal Cavity Line Leak</strong><br /><i>Abstract:&nbsp;</i>On January 29, 2008 at 0325, St. Lucie Unit 2 was in Mode 1 at 100% power when the reactor was down powered and manually tripped in accordance with plant procedures as a result of an increasing unidentified reactor coolant system (RCS) leak rate. Subsequent investigation of the leak identified the 2B1 reactor coolant pump (RCP) [EIIS:AB:P] to be leaking at the socket weld in the 3/4 inch upper seal cavity pressure transmitter line. Repairs were made and the unit was returned to power. A root cause was completed and determined that a synergistic effect of four separate causes: localized abnormal chemistry conditions, line resonance vibration levels, inherent stress concentration effects of socket welds, and elevated RCP vibration levels all contributed to causing the through wall crack. Corrective actions identified beyond the immediate weld repair includes a forensic evaluation of additional socket welds, flushing of Unit 2 RCP instrument sensing lines during future outages, evaluation of replacing pipe spools with flex hoses and performance of pipe vibration analysis of Unit 2 RCP lines. There was no adverse impact on the health and safety of the public.
3892008002 | St. Lucie 2 | 06/04/2008 | 08/04/2008 | ML08225025 | <strong>Unit 2 Manually Tripped as a Result of Maintenance</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2008, St. Lucie Unit 2 was in Mode 1 at 100% power while Plant instrument and control (I&C) personnel were performing maintenance on the 5B Feedwater (FW) Heater High Level Limit Switch LS-11-26B, when two taped energized leads were being routed through a conduit elbow came in contact with the conduit and grounded. The ground resulted in the 28 Heater Drain Pump being tripped on low level and the 2A Main Feedwater Pump tripping on low suction pressure 50 seconds after the heater drain pump tripped. The reactor was manually tripped in anticipation of a low steam generator level auto-trip. All safe shutdown equipment operated as designed with no impact on the health and safety of the public. The root cause of the event was determined to be a failure to implement adequate process controls to minimize risk during level switch replacement, and the drifting of the pressure switch (PS-12-14A) set point resulting in a premature actuation of the switch during a feed water transient. This ultimately resulted in a manual reactor trip. Corrective actions included, development of specific procedural direction for controlling energized leads during work evolutions using the risk management process, design modifications to address vulnerability when performing maintenance on level switches, and evaluation of industry best practices for training and handling of energized leads.
3892008003 | St. Lucie 2 | 06/07/2008 | 07/31/2008 | ML08232111 | <strong>Unit 2 Condensate Pump Failure Resulting in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2008, St. Lucie Unit 2 was operating normally in Mode 1 at 100% power when operators observed that the 2B condensate pump and 2B steam generator feedwater pump had tripped and steam generator water levels were rapidly decreasing. Operators took action to manually trip the Unit in accordance with plant procedures. An investigation determined the 2B condensate pump "B" phase motor leads had overheated and failed due to high resistance at the lug crimp connections. All safe shutdown equipment operated as designed and there was no adverse impact on the health and safety of the public. The root cause of the event was determined to be undetected epoxy resin in the motor lead cables resulting from not having specific hold points to detect epoxy resin in the motor rewind specification during the a vendor vacuum pressure impregnation process. Contributing causes included not understanding the adverse effects epoxy contamination could have on connections and the lack of controls for contamination in the controlling specifications. Corrective actions included revising motor rewind specification (SPEC-E-008) to ensure epoxy is not applied to the motor leads during the Vendor's vacuum pressure impregnation process.
3902008001 | Watts Bar 1 | 03/20/2008 | 05/19/2008 | ML08140079 | <strong>Automatic Safety Injection Actuation Blocked in Modes 4 and 3</strong><br /><i>Abstract:&nbsp;</i>Jumpers installed near the beginning of the Cycle 8 refueling outage to block automatic actuation of Safety Injection (Auto SI) had not been removed when Mode 4 was achieved at 0020 EDT on March 20, 2008, or when Mode 3 was entered at 0100 EDT on March 21, 2008. At 0913 EDT on March 21, 2008, plant personnel identified that the jumpers installed during the outage had not been removed. The Auto SI function is required in Modes 1, 2, 3, and 4 per Function 1.b of Table 3.3.2-1 of LCO 3.3.2. Since both trains of Auto SI actuation instrumentation were inoperable, LCO 3.0.3 was entered until jumpers were removed at 0958 EDT. At 2133 EDT on March 21, 2008, it was identified that the Auto SI function was still inoperable because the Auto SI function had not been reset. The reactor trip breakers were cycled to reset Auto SI and LCO 3.0.3 exited at 2206 EDT. Safety consequences of this event were not significant for the existing plant conditions. The cause assessment for the event identified an inadequate General Operating (GO) Instruction and an inadequate Instrument Maintenance Instruction (IMI). The corrective actions include revisions to selected GOs, the IMI, and establishment of a jumper tracking program.
3902008002 | Watts Bar 1 | 08/07/2008 | 10/06/2008 | ML08280024 | <strong>Manual Reactor Trip in Response to Start of Feedwater Heater Isolation</strong><br /><i>Abstract:&nbsp;</i>During a planned shutdown on August 7, 2008, unexpected annunciator alarms were received in the control room that indicated hi level in the A and B feedwater heater strings. The reactor was manually tripped when indication was received that the third string, C, was beginning to isolation. An event team was assembled subsequent to the plant trip. The cause was determined to be a failed air line on the Heater Drain Tank bypass to condenser valve. This air line failure was most likely due to vibration fatigue caused by improper installation. Corrective action was taken to replace this line in accordance with vendor requirements. As a result of the plant trip, the actuation of the Reactor Protection and the Auxiliary Feedwater Systems were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), respectively. This event is also being reported as this Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv).
3902008003 | Watts Bar 1 | 08/07/2008 | 10/06/2008 | ML08281005 | <strong>Automatic Start of Auxiliary Feedwater Unavailable During Startup Entry into Modes 2 and 1</strong><br /><i>Abstract:&nbsp;</i>NRC Inspection Report 05000390 identified in a noncited violation (NCV) that TVA started Watts Bar Nuclear Plant (WBN) Unit 1 since initial plant startup without an operable channel of auxiliary feedwater (AFW) automatic start on a trip of all main feedwater pumps as required by Technical Specification (TS) 3.3.2 Function 6.e. The NCV finding was determined to be of very low safety significance because the finding did not represent an actual loss of safety function of a single train for greater than its TS allowed outage time since other initiation signals were available to automatically start the auxiliary feedwater pumps if needed. With this inspection report, NRC clarified that the instrumentation channels must not only be capable of transmitting a trip signal, but must also reflect the actual operating condition of the main feedwater pump. TVA has submitted a TS change to permit operation without the AFW autostart on trip of all main feedwater pumps until a main feedwater pump is actually providing feedwater flow to the steam generators. Until operation in accordance with the revised TS is approved, TVA will startup using all three AFW pumps, which will eliminate the need for the autostart, since the signal would be to start the pumps that are already running.
3902008004 | Watts Bar 1 | 09/20/2008 | 11/19/2008 | ML08325029 | <strong>Automatic Reactor Trip in Response to Opening of Exciter Field Breaker</strong><br /><i>Abstract:&nbsp;</i>During normal plant operation on September 20, 2008, unexpected annunciator alarms were received in the control room indicating an automatic reactor trip based on a loss of electrical load. Subsequently, the control room was informed by a Nuclear Assistant Unit Operator that he had tripped open the Exciter Field Breaker, leading to the turbine trip and successive reactor trip. The cause of this event has been determined to be human performance error in that the NAUO failed to recognize the need to utilize error reduction techniques when opening the exciter field breaker cabinet door. Corrective action has been taken to add the applicable information to operator requalification programs. As a result of the plant trip, the actuation of the Reactor Protection and the Auxiliary Feedwater Systems were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), respectively, as ENS notification 44506. This event is also being reported as this Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3902008005 | Watts Bar 1 | 10/29/2008 | 12/29/2008 | ML08365006 | <strong>Inoperability of Radiation Monitor due to Non-Conservative Setpoint</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2008, a discrepancy in the setpoint of the particulate channel of the radiation monitor being credited for meeting Technical Specification (TS) 3.4.15 was identified and the appropriate Limiting Condition for Operation (LCO) was entered. On October 14, the radiation monitor had been calibrated to a setpoint that was no longer within the specified tolerance as a result of a design change. From October 14 to October 29, the Reactor Coolant System Leakage Detection System had been inoperable due to this incorrect setpoint. Consequently, WBN had been operating in a condition prohibited by Technical Specifications. The cause of this event was determined to be a human performance error during the preparation of design change impact forms. An insufficient level of Question, Validate, and Verify (QV&V) was used, and self-checking was flawed by a wrong assumption regarding design change scope. The setpoint was corrected October 30.
3952008001 | Summer 1 | 01/24/2008 | 07/30/2008 | ML08217030 | <strong>Manual Reactor Trip due to Low Steam Generator Level Caused by Feedwater Flow Control Valve Malfunction</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2008, the C feedwater flow control valve (IFV00498) exhibited oscillations as indicated by the plant computer and on the Main Control Board (MCB). As the feedwater flow oscillations increased in size, the Shift Supervisor directed the operator to take manual control of the valve. Feedwater flow was greater than steam flow when manual control was implemented. When the operator decreased flow demand on the manual/auto station, IFV00498 indicated closed and feedwater flow decreased to zero. Due to a rapidly decreasing level in C Steam Generator, the Shift Supervisor directed a manual reactor trip at 1604 hours. The operations crew entered the reactor trip procedure. All systems responded as required. The plant was stabilized in Mode 3. The root cause was determined to be the failure of the feedwater flow control valve positioner pilot valve. The failure was due to either fretting as a result of normal operation or foreign material inclusion into the component's air system due to insufficient filtration and vibration induced component wear. On each feedwater flow control valve, the positioners, check valves, and pressure regulators were replaced, and additional filtration was installed. Copper tubing and the brass check valves were replaced with stainless steel to minimize particulate intrusion. In addition, components susceptible to vibration were relocated. To address future problems, an "air-gag" device was installed on each feedwater flow control valve to facilitate on-line maintenance without loss of safety function.
3952008002 | Summer 1 | 03/11/2008 | 09/02/2008 | ML08252000 | <strong>Control Room Normal and Emergency Air Handling Systems Inoperable due to Pressure Boundary Breach</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2008 following maintenance on an outside air intake valve, Surveillance Test Procedure STP-454.002 was performed to restore the "A" train of the Control Room Normal and Emergency Air Handling (CR Ventilation) System to service. The test results were unsatisfactory. Investigation into the test failure determined that a control room pressure boundary (CRPB) breach occurred during normal preventive maintenance performed February 26, 2008 on Instrument and Control (I&C) Area Air Handling Unit XAH0048. The identified breach was sufficient to allow a quantity of air out-leakage that reduced CRPB pressure below Technical Specifications (TS) minimum and resulted in increased outside air flow that exceeded the maximum allowed by TS. Repairs were made to the air handling unit and the surveillance test was successfully completed on March 14, 2008. The effect of the leakage at XAH0048 on the "B" Train of CR Ventilation could not be readily determined. Therefore, both trains of CR Ventilation were assumed to be inoperable from February 26 to March 14, 2008. Since this condition affected both trains of CR Ventilation and existed for greater than 24 hours, TS Limiting Condition for Operation (LCO) 3.7.6.a.2 was violated. A root cause analysis determined that the root causes of this event were: 1) adequate maintenance retests were not procedurally addressed, and 2) Air Handling Unit XAH0048 was located within the CRPB, but not purchased to meet the CRPB design requirements. The corrective actions to prevent recurrence include: 1) revise procedures to verify CRPB restoration requirements and to provide additional guidance for CRPB envelope testing, and 2) perform a design change to either relocate or upgrade Air Handling Unit XAH0048.
3952008003 | Summer 1 | 05/21/2008 | 07/14/2008 | ML08199021 | <strong>Inadvertent Actuation of the Emergency Diesel Generator in the Emergency Start Mode due to Bus Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2008 during post-maintenance testing of the "A" Emergency Diesel Generator, the voltage regulator did not respond as expected and control was switched from automatic to manual operation. When this occurred, the output voltage decreased resulting in actuation of the undervoltage relays on electrical bus 1DA. Actuation of these relays resulted in the "A" Emergency Diesel Generator being shifted from the test start mode to the emergency start mode. Bus voltage was immediately restored to normal and the emergency diesel generator response was verified to be appropriate. The plant was shutdown for refueling at the time of this event. A root cause analysis of this event has been completed. The results of this analysis indicate that the root causes of this event are due to inadequate procedural guidance and training on operation of the voltage regulator in manual control. Corrective actions have been identified to develop procedure enhancements and provide operator training on operation of the voltage regulator with the manual control.
3952008004 | Summer 1 | 02/15/2007 | 03/17/2009 | ML09078025 | <strong>Technical Specification Violation due to Alternate AC Unavailability</strong><br /><i>Abstract:&nbsp;</i>On three occasions during Cycle 17, Virgil C. Summer Nuclear Station (VCSNS) extended Emergency Diesel Generator outages beyond 72 hours for maintenance by taking credit for the Alternate AC (AAC) power source as allowed by LCO 3.8.1.1 Action b.4. AAC testing during Refueling Outage 17 called into question the availability of AAC. On August 11, 2008 after a review of the past operability determination, it was determined that the AAC may not have been available during these periods. Therefore, VCSNS is reporting this Technical Specification violation in accordance with 10CFR50.73(a)(2)(i)(B). The AAC unavailabilty resulted from voltage regulation problems, an inadequately designed Reverse Power Relay (351S-7), and improperly installed wiring on the 387 bus differential relay. To address the voltage regulation issues, an enhanced prejob brief and procedural guidance have been put in place for controlling the Parr hydro units when adding VCSNS loads to the AAC. The reverse power trip function will be permanently removed to prevent recurrence of AAC unavailabilty due to a reverse power trip. The improperly installed bus differential relay wiring has been corrected.
3972008001 | Columbia | 08/21/2008 | 03/16/2010 | ML10083008 | <strong>Reactor Scram due to Failed Compression Fitting</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2008, an automatic reactor scram occurred at 1606, while the plant was operating at 65% power due to the Digital Electrohydraulic Control (DEH) trip header momentarily depressurizing during post maintenance testing (PMT). All safety systems were available during the event and operated as designed. Plant operators effectively managed the transient. This event did not pose a threat to the health and safety of the public. The direct cause of the reactor scram was instantaneous recompression of an air bubble trapped in the intervalve cavity between the A and B Quadvoter valves during post-maintenance testing (PMT). This allowed backflow of DEH fluid from the emergency trip header into the intervalve cavity during PMT, causing a momentary depressurization of the DEH trip header that resulted in the reactor scram. The root cause of the scram was determined to be a design deficiency in the on-line serviceable Quadvoter assembly which allowed an air bubble to remain in the intervalve cavity following performance of on-line maintenance activities.
4002008001 | Harris | 01/30/2008 | 05/30/2008 | ML08157034 | <strong>Containment Spray Additive System Eductor Test Flow Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>The Containment Spray Additive System flow test results failed to meet the Technical Specification Surveillance Requirement 4.6.2.2.d. flow rate between 19.5 and 20.5 gpm several times between October 21, 2007 and May 18, 2008. The flow rate was immediately adjusted to 20 gpm each time it was found out of tolerance. Due to the number of repeat occurrences and valve re-adjustments to re-establish the 20 gpm flow rate, a Priority 1 Root Cause Investigation was conducted. However during this degraded condition, the Containment Spray Additive System may not have been capable of maintaining the pH between 7 and 11, as required under accident conditions. This could degrade iodine scrubbing capabilities or increase corrosion problems. These failures were determined to be reportable as an LER on 3/31/2008. The first set of problems was caused by air entrapment in the Containment Spray Additive System during Refueling Outage 14. Preventative maintenance program and operating procedure revisions were implemented to check for and remove air from the system after system fill and vent and during each refueling outage prior to Mode 4 ascending. The second set of problems was caused by inadequate system design. Operating position and inherent stem-plug looseness in the eductor flow throttle valve interact to cause flow instability. A system design change and operating procedure changes were implemented to reduce valve instability. Additional design changes will be implemented to eliminate flow instability.
4002008002 | Harris | 08/11/2008 | 10/08/2008 | ML08290057 | <strong>Manual Actuation of the Reactor Protection System due to Main Condenser Exhaust Boot Failure</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2008 the Harris Plant experienced an increase in condenser backpressure and changes in the Steam Generator secondary side chemistry. A decision was made to shut the unit down due to rising condenser backpressure. At approximately 21% power, the unit was manually tripped by operators due to reaching predetermined administrative limits. The plant promptly attained normal operation no-load temperature and pressure, and no unusual conditions or additional actuations were observed for plant equipment following the reactor and turbine trip. The increase in condenser backpressure was caused by a failure of the condenser exhaust boot seal due to aging. The root cause of exhaust boot seal failure was that past experience was not applied to the preparation of the preventative maintenance deferral of the condenser exhaust boot. Immediate corrective actions completed include cleaning the boot seal retaining areas and contact surfaces of the trough, and installing new boot seals. Planned corrective actions to prevent reoccurrence include revising the condenser exhaust boot seal replacement frequency based on operating experience and vendor recommendations. This replacement will include requirements to inspect and remove rough edges from mounting hardware and mating surfaces. All preventative maintenance deferrals prepared since June 2005 that deferred Single Point Vulnerability outage maintenance items will be reviewed to ensure technical adequacy. Additionally, plant staff will revise the Nuclear Generation Group procedure governing Preventative Maintenance and Surveillance Testing Administration to provide guidance on Single Point Vulnerability deferrals and identify the appropriate approval levels.
4002008003 | Harris | 08/19/2008 | 10/17/2008 | ML08303013 | <strong>Manual Actuation of the Reactor Protection System During Shutdown Rod Position Indication Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 08/19/08 while the reactor was shut down in Mode 3 to perform repairs on the main condenser, operators were conducting a partial surveillance test on the Rod Position Indication system. This test was being performed in accordance with Limiting Condition for Operation (LCO) 3.0.5 to restore Operability to the Digital Rod Position Indication (DRPI) system following repairs on a Control Rod Drive Mechanism canopy seal. Upon initial withdrawal of Control Bank C, the Main Control Room received a Rod Control system alarm. The operators entered Technical Specification 3.1.3.3 which requires action to restore DRPI or open reactor trip breakers within eight hours. Local inspection revealed a phase failure on .a Movable Gripper in Power Cabinet 1AC, and reactor trip breakers were opened by operators at 0905. Additional troubleshooting revealed a failed Movable Gripper fuse for phase C. Adequate shutdown margin was maintained and all rods withdrawn as part of this testing were capable of being tripped into the core at all times. The root cause of this event is that the existing preventative maintenance program does not prevent age related failures of bus duct fuses. The program inspects these fuses, but does not replace them unless faults are identified. Corrective actions taken to date are replacement of one failed fuse and three degraded fuses. Planned corrective actions to prevent recurrence include replacing bus duct and DC Hold Cabinet fuses during the next refueling outage and establishing a preventative maintenance item to replace these fuses periodically.
4122008001 | Beaver Valley 2 | 05/24/2008 | 07/23/2008 | ML08207007 | <strong>Unplanned Actuation of the Auxiliary Feedwater System During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2008 at 09:38 during a plant startup power increase in preparation to roll the turbine and synchronize to the grid, Beaver Valley Power Station Unit 2 experienced an Engineered Safety Feature (ESF) actuation P-14 due to Steam Generator (SG) HI-HI water level in the "A" Steam Generator. This ESF actuation initiated automatic actions resulting in full feedwater isolation, trip of the only operating "B" main feedwater pump and start of two Auxiliary Feedwater System pumps. The unplanned automatic initiation of the Auxiliary Feedwater System due to tripping of the Main Feedwater pump was an event reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). The cause of the steam generator high level transient is that the Operations crew on duty during this event was unfamiliar with steam generator level control using bypass feed regulating valves at low power with the main turbine not latched and in response made excessive manual changes in the feedwater flowrate. The safety significance of the event was very low.
4122008002 | Beaver Valley 2 | 09/25/2008 | 11/19/2008 | ML08329050 | <strong>Containment Air Lock Equalization Valve Inadvertently Left Open Following Routine Containment Entry</strong><br /><i>Abstract:&nbsp;</i>At 1038 on September 21, 2008, a crew of three utility personnel entered Beaver Valley Power Station (BVPS) Unit No. 2 Containment through the personnel air lock to perform minor maintenance on the containment sump pump. Approximately 71 minutes later, the crew exited containment after completing their work. On September 25, 2008, it was discovered that the air lock one-inch outside equalizing valve (2PHS-111) was open. 2PHS-111 was then closed. With this equalizing valve open, one of the two containment boundaries provided at the personnel air lock interface was not intact. Subsequent review concluded that this valve was last operated during the containment entry on September 21, 2008. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications. The cause of the air lock valve being left open was the air lock door operating procedure is not a "step by step" level of use procedure. The air lock operating procedures for both BVPS Units have since been converted to be step by step procedures. The safety significance of the event condition was very low.
4122008003 | Beaver Valley 2 | 10/23/2008 | 12/22/2008 | ML08365006 | <strong>Low Head Safety Injection Pump Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2008 at Beaver Valley Power Station Unit No. 2 (BVPS-2) during routine preventative maintenance on the Train "A" Low Head Safety Injection Pump, mechanical maintenance personnel noticed that the pump unexpectedly would not rotate by hand. During subsequent investigation and pump disassembly, it was discovered that the outboard pump casing wear ring and the impeller wear ring were in direct contact, which resulted in galling of the pump's 316 stainless steel wear rings. Due to the projected work scope for this unanticipated repair of pump wear rings and post-maintenance testing, a Notice of Enforcement Discretion (NOED) was requested by FirstEnergy Nuclear Operating Company. The Nuclear Regulatory Commission granted the NOED at 1105 on October 22 to not comply with BVPS-2 Technical Specification 3.5.2 Action B for an additional 36 hours in order to allow time to complete the pump repair actions without shutting down the plant. Additional unexpected difficulties delayed the reassembly of the pump, and a plant shutdown to Mode 4 was performed. This is reportable as a condition prohibited by BVPS-2 Technical Specification 3.5.2, pursuant to 10 CFR 50.73(a)(2)(i)(B), and as a completion of a plant shutdown required by the plant's Technical Specification, pursuant to 10 CFR 50.73(a)(2)(i)(A). The cause of this event resulting in the pump work extending beyond the allowed component out-of-service time was inadequate part dedication. The safety significance of this event was very low.
4132008001 | Catawba 1, Catawba 2 | 01/30/2008 | 03/31/2008 | ML08094012 | <strong>Auxiliary Feedwater Pumps Declared Inoperable Due to Inadequate Design and Configuration of Floor Drain Flow Restrictor Cover Plates</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2008, at 12:20 hours, with Unit 1 and Unit 2 operating at 100 percent power, the Auxiliary Feedwater (AFW) pumps were declared inoperable upon discovery of missing flow restrictor plates in the floor drains of the Unit 1 and Unit 2 interior doghouses. The identified internal flood protection deficiencies were caused by inadequate design and configuration control during original plant design. The flood barriers were corrected by installation of flow restrictor cover plates for the floor drains in the interior doghouses. The health and safety of the public were not affected by this event. This event does involve a safety system functional failure.
4162008001 | Grand Gulf 1 | 01/12/2008 | 03/10/2008 | ML08070070 | <strong>Manual Reactor SCRAM due to Loss of Main Electrical Output Transformer Cooling</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2008, at 1626 hours a manual reactor scram was initiated from 99 percent power due to loss of cooling to the Main Transformers. After the scram reactor water level decreased to Level 2 (-41.6 inches) and Reactor Core Isolation Cooling initiated. There were no inoperable structures, systems, or components at the start of the event that contributed to the event. The normal heat sink (main condenser) remained available and no Main Steam Safety Relief Valves actuations occurred during the event. All control rods fully inserted and all safety systems functioned as designed and responded properly. The cause of this event was the loss of cooling to the Main Transformers caused by loss of Auxiliary Power to the Main Transformer cooling system. Inspection of the complete circuit for Main Transformer Auxiliary Power showed that the “B” phase power cables were found to be burned in two at the transfer switch panel. The cause of the “B” phase power cable failure is attributed to failure of an electrical compression connection on a lug connection. This particular cable and connection has been inservice since plant start-up. Potential root causes were determined to be use of a compression connection for high current applications versus the preferred crimp type connection and an inadequate preventive maintenance strategy to provide early detection. Corrective actions included an inspection of the power panel and replacement of all damaged cabling.
4162008002 | Grand Gulf 1 | 03/21/2008 | 05/15/2008 | ML08136059 | <strong>Reactor SCRAM due to Main Generator Trip Caused by Unit Differential Lockout</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2008 at 1525 hours Grand Gulf Nuclear Station experienced an actuation of the Reactor Protection System (RPS) which resulted in an automatic reactor shutdown (scram) from 100 percent power. The scram was due to main turbine control valve fast closure following a main generator trip caused by "C" phase unit differential lockout. There were no inoperable structures, systems, or components at the start of this event that contributed to the event. The normal heat sink (main condenser) remained available. All control rods fully inserted and all safety systems functioned as designed. The minimum reactor water level recorded during this event was -8.2 inches wide range. The level for initiation of Emergency Core Cooling Systems (ECCS) is -41.6 inches, therefore no ECCS initiation occurred. Six safety relief valves (SRVs) lifted momentarily and then closed at the onset of the event. After SRV closure, reactor pressure was controlled with the main turbine bypass valves and reactor level was maintained the entire time using normal condensate and feedwater. The cause of the event was a main generator trip as the result of a "C" phase unit differential lockout. Troubleshooting which included inspection of the high voltage circuit and check of calibration of both the "A" and "B" relays was initiated; however, no definitive cause for the trip was identified. As a precaution, the suspect "C" phase unit different relay was replaced.
4162008003 | Grand Gulf 1 | 04/10/2008 | 06/05/2008 | ML08157040 | <strong>Increased Buss Voltages Results in Breaker Trip on Over Current of a High Pressure Core Spray Pump Low Flow Valve Resulting in Non-Compliance with Technical Specification 3.6.1.3 Primary Containment Isolation Valve Function</strong><br /><i>Abstract:&nbsp;</i>On March 05, 2008 at 1619, Technical Specification Emergency Core Spray System (ECCS) surveillance testing was being performed of the High Pressure Core Spray (HPCS) pump and system. During the testing, the HPCS low flow valve 1E22-F012 (also a primary containment isolation valve), while stroking from closed to open position, de-energized and the HPCS loss or overload status light energized. The valve was found in the non-closed position and the power supply breaker for the motor actuator for the valve was found tripped open. This condition is considered a violation of Technical Specification 3.6.1.3 Primary Containment Isolation Valve (PCIV) due to exceeding the LCO Required Action Completion Time of four hours to isolate the penetration. The cause of valve 1E22-F012 to fail to close is due to its supply breaker instantaneous over current trip settings being set too low, thus rendering the valve inoperable. Investigation revealed that this condition had existed since the early 1990s when buss voltages had been increased to a higher value to account for under voltage events. Corrective actions were implemented which included replacement of the valve 1E22-F012 power supply breaker and increasing the instantaneous over current trip settings. Breaker settings for the other ECCS motor operator valves that were susceptible to this condition were checked and found to be acceptable.
4162008004 | Grand Gulf 1 | 10/23/2008 | 12/15/2008 | ML08351083 | <strong>Automatic Reactor SCRAM on Decreasing Coolant Level due to Inadvertent Reactor Feed Pump Steam Supply Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2008 at 0721 Grand Gulf Nuclear Station was operating in MODE 1 at approximately 10 percent power when an actuation of the Reactor Protection System (RPS) occurred due to decreasing reactor coolant level. The decreasing reactor coolant level was the result of closure of the "A" Reactor Feed Pump Turbine (RFPT) steam inlet valves. During restoration of the "B" RFPT Overspeed Trip Test a non-licensed operator (NLO) closed the steam supply drain valves on the "A" RFPT train instead of the "B" train. Closure of the drain valves did not cause loss of feedwater to the reactor vessel. Upon discovery of the mistake the NLO tried to correct the error and closed the "A" RFPT steam inlet valves. This led to the loss of feedwater flow to the reactor vessel. A reactor SCRAM was received per design at Level 3 (+11.4 inches) and all control rods fully inserted. Operators manually initiated the Reactor Core Isolation Cooling system to restore and maintain reactor vessel level. No emergency core cooling system initiation setpoint was reached and no safety relief valves lifted. The normal heat sink (main condenser) remained available during this event. The root cause of this event was determined to be a lack of commitment to Human Performance Program implementation.
4162008005 | Grand Gulf 1 | 10/26/2008 | 12/15/2008 | ML08351082 | <strong>Automatic Reactor Scram due toTurbine Control Valve Fast Closure Caused by an Electrical Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2008 at 1125, Grand Gulf Nuclear Station was in Mode 1 operating at approximately 50 percent power when an automatic reactor scram was initiated by the Reactor Protection System (RPS) on detection of fast closure of the Turbine Control Valves (TCVs). After the scram reactor water level decreased to -2.67 inches and was maintained with the reactor feedwater system. There were no inoperable structures, systems, or components at the start of the event that contributed to the event. The normal heat sink (main condenser) remained available and no Main Steam Safety Relief Valves actuations occurred during the event. All control rods fully inserted and all safety systems functioned as designed and responded properly. The cause of this event was due to the Main Generator Thyristor Voltage Regulator (TVR transferring from automatic control to manual control resulting in an unexpected under excited condition which tripped the main generator which then caused a fast closure of the TCV. It was determined that the TVR card manual reference setter was not tracking the automatic reference setter due to a defective manual reference setter motor operated potentiometer (MOP). The root cause of this event was determined to be lack of a preventive maintenance (PM) strategy for the TVR control system to ensure reliability of the voltage control circuits.
4232008001 | Millstone 3 | 08/29/2008 | 10/26/2008 | ML08309038 | <strong>Postulated Fire Scenario Results in Unanalyzed Condition - Pressurizer Overfill</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2008 at 1007 while operating at 100% power, Millstone Power Station Unit 3 identified a potential vulnerability in the fire safe shutdown strategy which, under certain fire conditions, may challenge the ability to meet the performance criteria of the approved fire protection program. It is postulated that under certain fire conditions affecting the control room, the ability to maintain pressurizer level within the indicated range (high) may be challenged and lead to water relief through the pressurizer safety valves. The pressurizer safety valves are not qualified for water relief. The apparent cause of this condition is a deficiency in the original fire protection evaluations to meet the requirements of Branch Technical Position (BTP) CMEB9.5-1 (NUREG-0800) as documented in the Millstone Unit 3 Fire Protection Evaluation Shutdown System Availability Report of 1985 (BTP Compliance Report). A modification is being implemented that will prevent this condition during plant power operations. Additional corrective actions are being addressed in accordance with the station's corrective action program. This condition has had no actual safety consequences as no fire has occurred to challenge the circuits in question. This event involves a postulated fire scenario and subsequent potential failure. This condition had no direct impact on the health and safety of the public or plant personnel. The event does involve an unanalyzed condition related to safe shutdown capability. This condition is being reported under 10 CFR 50.73(a)(2)(ii)(B), "Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety."
4232008002 | Millstone 3 | 10/10/2008 | 12/05/2008 | ML08351075 | <strong>Failure of Four Main Steam Safety Valves to Lift within the Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>With the plant in MODE 1 at 100% power on October 9 and 10, 2008, set pressure "simmer" testing of Millstone Power Station Unit 3 (MPS3) Main Steam Safety Valves (MSSVs) was conducted per plant procedures. During the testing, four MSSVs (3MSS*RV22C, 3MSS*RV22D, 3MSS*RV24A, and 3MSS*RV25C) failed to lift within the (+/- 3%) acceptance criteria of Technical Specification (TS) 3.7.1.1. The failure of four MSSVs to lift within the required set pressure range is attributed to a corrosive oxide locking action between surface layer materials of the disc-seat interface, sometimes referred to as "oxide locking" or "micro bonding". After testing, all twenty MSSVs were left within +/- 1% of TS acceptance criteria to account for potential future drift.
4232008003 | Millstone 3 | 10/11/2008 | 12/10/2008 | ML08357015 | <strong>Automatic Reactor Trip During Shutdown for Refueling Outage 3R12</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2008, while in MODE 1 at approximately 30% power an automatic reactor trip occurred, as Millstone Power Station Unit 3 was reducing power in preparation for the 12th refueling outage. Prior to the reactor trip the plant was experiencing Steam Generator (S/G) level oscillations as the result of removing feedwater system components from service. The operators took manual control of the feedwater system, however, the oscillations increased and the 'A' S/G reached its 'high-high' set point resulting in an automatic turbine trip and feedwater isolation. A reactor trip on 'low-low' S/G level followed. All safety systems operated normally including the automatic start of the auxiliary feedwater pump, and the reactor shut down safely. All secondary systems operated normally. The cause was determined to be the operating crew on shift failed to effectively use the tools necessary to enable an event free shutdown of the plant. The organization with respect to monitoring and measuring crew performance was not effective in implementing programs designed to manage the challenges to the operators. Prior to start up from the refueling outage, training on low power feed station operations for on shift and active licensed operators was conducted. Additionally proper operation of the S/G water level control system and the feedwater regulating valves was verified. Additional corrective actions will be entered into the station's corrective action program. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 50.73(a)(2)(iv)(B).
4232008004 | Millstone 3 | 10/20/2008 | 12/19/2008 | ML09007003 | <strong>Gas Void Discovered in the Emergency Core Cooling System Suction Line</strong><br /><i>Abstract:&nbsp;</i>On October 20,2008, with Millstone Unit 3 at 0% power in Mode 5, as part of Generic Letter 2008-01 activities, ultrasonic testing (UT) performed on a portion of the common suction line from the refueling water storage tank to the suction of the emergency core cooling system (ECCS) pumps indicated the accessible portion of the 24" diameter pipe was 85% full. No immediate actions were necessary since ECCS is not required in Mode 5. Engineering determined for break sizes that would result in low head safety injection there was the potential to transport the gas void/water mixture to specific ECCS pumps during the injection phase of an accident. Of the scenarios with the potential to transport the gas void/water mixture, only those scenarios with a low reactor coolant system pressure were determined to adversely impact the accident mitigation capability of affected ECCS pumps. The cause of this condition was determined to be a latent design error. The original design of the plant did not include a vent path for this section of piping. Subsequent to the discovery of the gas void, the plant was modified to install a vent valve on this line to provide a venting location. The operators utilized this vent valve upon returning the unit to service to fill the common suction line and confirmatory UTs were performed to verify the line was full. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's Technical Specifications, 10 CFR 50.73(a)(2)(v)(B) and (D) as any condition or event that could have prevented fulfillment of a safety function, and 10 CFR 50.73(a)(2)(vii) as any event or condition where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system.
4232008005 | Millstone 3 | 11/05/2008 | 07/07/2010 | ML10201038 | <strong>Containment Penetration Not Fully Closed During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>With the plant in Mode 6 at 0% power on November 5, 2008, operators discovered that a valve (3FWS*V861) relied upon to be closed to meet technical specification requirements during fuel movement in containment was fully closed. Plant Technical Specification (TS)3.9.4.c requires that each penetration providing direct access from the containment atmosphere to the outside atmosphere be closed by an isolation valve blind flange or manual valve or be capable of being closed under administrative control during movement of fire within the containment building. Valve 3FVVS*V8614 is a drain line isolation valve off the feedwater line to the "C" steam generator inside containment and was being credited as closed since a pathway to atmosphere outside containment existed due to maintenance activities on associated positions of the main steam system. The subsequent investigation determined that the valve had been in this condition during fuel movement inside containment that occurred from November 1, 2008 at 0430 until Novemeber 3, 2008 at 0915. The cause of this condition was determined to be a combination of mechanical and physical factors making the valve difficult to operate to ensure full closure. The valve was subsequently closed. Maintenance was performed the valve during refueling outage 3R13 (Spring 2010). Proper operation the valves was validated through post maintenance testing. Since the plant was in a configuration not allowed by the technical specifications, this event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). This a supplement to LER 2008-05-00 to report this condition in accordance with 10 CFR 50.73(a)(2)(v)(C).
4232008006 | Millstone 3 | 11/24/2008 | 01/28/2009 | ML09043039 | <strong>Turbine-Driven Auxiliary Feedwater Pump Steam Trap Isolation Valves Found Closed</strong><br /><i>Abstract:&nbsp;</i>On November 24, 2008 at 0025 hours, with the plant in Mode 1 at 18% power, Millstone Power Station Unit 3 (MPS3) control room operators identified the turbine-driven auxiliary feedwater (TDAFW) pump steam trap isolation valves were closed. Upon discovery of this condition, the TDAFW pump was declared inoperable and Technical Specification Action Statement (TSAS) 3.7.1.2.c was entered. The valves were promptly re-opened, the steam traps blown down, and the TDAFW pump restored to operable status. The TSAS was exited at 0346 hours on November 24, 2008. During the time the steam trap isolation valves were closed, the unit went through two mode changes. Because Technical Specification (TS) 3.0.4 does not permit mode changes while in this condition, the provisions of this TS were not met. The cause of this condition was a failure to restore proper alignment of the TDAFW pump steam trap isolation valves. The turbine shell and chest warming procedure has been revised to correct the identified deficiencies. Since MPS3 was in a configuration prohibited by TS 3.0.4, this event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as any "Operation or Condition Prohibited by Technical Specifications."
4242008001 | Vogtle 1 | 04/21/2008 | 06/20/2008 | ML08175000 | <strong>Group A Pressurizer Heaters Inoperable During Mode Change</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2008 at 0951 EDT, Unit 1 entered Mode 3, from Mode 4, with the pressurizer heaters in Group A inoperable. Unit 1 entered Mode 3 in a condition prohibited by Technical Specification (TS) 3.0.4. The condition was identified during a pressurizer heater capacity test on April 21, 2008 at 1818 EDT, when a Maintenance electrician observed open breakers on the Group A and C heater panels. The Unit 1 Control Room was immediately notified, and Operations entered a Required Action statement for TS 3.4.9, based on inoperability of pressurizer heater Group A while in Mode 3. The heater breakers were subsequently closed within the 72-hour Required Action statement. The primary cause of this event was inadequate work instructions to perform the necessary pressurizer heater work. The functional testing requirement to complete heater resistance measurements was not properly planned in the work order to ensure that the equipment was properly tested before being placed in service. In addition, human performance tools were not used by the individuals involved in the manipulation of the breakers when it was determined the instructions were not adequate. The supplemental electrician associated with the pressurizer heater breaker mispositioning event was unaware of the plant procedure used to document breaker manipulation.
4242008002 | Vogtle 1 | 12/10/2008 | 01/30/2009 | ML09030067 | <strong>Supplemental Worker Fails to Report Custodial Arrest Resulting in Inappropriate Unescorted Access</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2008 at approximately 13:10 hrs Eastern Standard Time (EST), Southern Nuclear Operating Company (SNC) Nuclear Fleet Security contacted Vogtle Electric Generating Plant (VEGP) site Security, regarding the failure of a supplemental worker to self-disclose a custodial arrest that had occurred on April 23, 2004. The supplemental worker had been granted Unescorted Access to VEGP on four separate occasions. The supplemental worker was first badged at VEGP from April 5, 2004 to April 30, 2004, during which time the custodial arrest occurred. The supplemental worker was again granted Unescorted Access from February 22, 2005 to April 2, 2005, from September 15, 2005 to October 6, 2005, and from September 12, 2006 to October 9, 2006. An investigation by SNC Nuclear Fleet Security was performed and it was determined that the supplemental worker failed to disclose the custodial arrest, while under the Unescorted Access (UA) program in April 2004, and during the subsequent requests for Unescorted Access Authorization (UAA). The supplemental worker has been denied UA at all SNC facilities and flagged in the Personnel Access Data System (PADS).
4402008001 | Perry | 01/14/2008 | 03/14/2008 | ML08080045 | <strong>Condition Prohibited by Technical Specifications due to Unrecognized Reactor Core Isolation Cooling Inoperability</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2008, the plant was operating at approximately 100 percent power with the Reactor Core Isolation Cooling system (RCIC) considered operable and in standby readiness. Plant staff performed a review of the RCIC flow controller output on a computer point in preparation for planned maintenance. The flow controller output, monitored on a computer point, had changed from approximately 102.9 percent to approximately 100.2 percent without an observed change on the output meter. Further review of the flow controller output history identified additional instances of similar changes. Based on this information the RCIC system was determined to have been inoperable for about 35 days. Technical Specification Limiting Condition for Operation 3.5.3 was not met since the condition had been previously unrecognized. This condition is reportable as a Condition prohibited by Technical Specifications, 10CFR50.73(a)(2)(i)(B). The most probable cause of the observed flow controller anomaly was identified as an intermittent failure of the connector. The Bailey 701 flow controller and connecter, the power supply, the ramp generator/signal converter, and the computer input circuit board were replaced. Planning is in process to replace the obsolete Bailey flow controllers. Additional changes will be made to improve system reliability through improved monitoring of the flow controller output.
4402008002 | Perry | 02/10/2008 | 04/08/2008 | ML08107024 | <strong>Inoperable Emergency Closed Cooling System Results In Condition Prohibited ByTechnical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2008, at approximately 0830 hours, with the reactor operating at approximately 100 percent of rated thermal power, plant operators determined that the Emergency Closed Cooling subsystem B (ECC B) was inoperable. ECC B had been inoperable due to insufficient minimum flow for approximately 52 hours prior to Technical Specification Required Action being taken to declare the associated systems and components inoperable. The cause of the event is attributed to a bypass valve that was left closed due to a System Operating Instruction that did not include steps to realign flow through the bypass valve when the ECC flow path was isolated. The missing steps resulted from an inadequate classification of procedure changes associated with previously implemented design modifications. Additional causes of the event were inappropriate Clearance tagging and improper impact reviews. An operations system tracking database was, changed to include statements that closing of ECC valves need prior evaluation for ECC operability. Warning placards will be placed on the ECC valves to ensure minimum flow is maintained. Procedure changes to precautions and limitations will address flow paths. Procedures will be revised to add lessons learned. Lessons learned and training on the ECC will be given to appropriate plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's technical specification.
4402008003 | Perry | 05/28/2008 | 09/26/2008 | ML08276046 | <strong>Inoperable High Pressure Core Spray System Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2008, at 1730 hours, with the reactor operating at 100 percent of rated thermal power, plant operators determined that the High Pressure Core Spray (HPCS) system was inoperable. The HPCS system was inoperable due to the Emergency Service Water (ESW) C loop inability to maintain required keep-fill pressure in the event of a loss of offsite power. The cause of the event was excessive leakage through the ESW C system discharge check and discharge valves. The leakage was due to inadequate testing and setup of the discharge valve motor operator during maintenance performed in July 2007. The organization failed to recognize the significance of verifying the discharge valve maintains an acceptable leakage rate. The design basis for the valves was not clearly defined by the Architect Engineer at the time of original installation of the ESW keepfill system in 1985. The discharge check valve was rebuilt with new internal parts. The closed limit switch of the motor operator for the ESW C discharge valve was reset. The butterfly disc was readjusted approximately four degrees into the seat compared to the previous as-found condition. The ESW C system was retested and passed its draindown test. The valves' design basis will be documented in an engineering calculation. This event is reported in accordance with 10 CFR 50.73 (a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
4432008001 | Seabrook | 01/19/2008 | 03/17/2008 | ML08086048 | <strong>Plant Trip due to 345kV Bus Fault</strong><br /><i>Abstract:&nbsp;</i>At 2302 on January 19, 2008 while operating in mode 1 at 100% power, Seabrook Station experienced a turbine trip and subsequent reactor trip due to a fault on 345kV bus 3. This bus is located between the generator step-up transformer and the switchyard circuit beakers. The fault initiated a 345 kV bus lockout, which in turn tripped the main turbine and the circuit breakers associated with the unit auxiliary transformers (UAT), which normally supply the plant's 4,160 volt and 13,800 volt buses. The loss of the UATs initiated an automatic transfer of the plant buses to the alternate 345kV power source via the reserve auxiliary transformers. The transient caused a loss of all four operating reactor coolant pumps (RCP) for approximately one hour. Due to the unavailability of presssurizer spray with all RCPs stopped, the pressurizer power-operated relief valve automatically opened as designed to control reactor coolant system pressure. The operators restored normal pressurizer spray following the restart of one RCP at 0009 on January 20, 2008. The cause of the 345kV bus fault was a failure of the operating shaft in the manually-operated disconnect switch for 345kV bus 3. On January 22, the plant entered mode 5 to repair 345kV bus 3 and returned to service on January 31, 2008. No adverse safety consequences resulted from this event.
4462008001 | Comanche Peak 2 | 03/16/2008 | 05/12/2008 | ML08142002 | <strong>Reactor Trip due to a Sheared Condenser Vacuum Instrument Sensing Line</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2008, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at 100% power. At 1137 hours, the Unit 2 Main Turbine tripped due to a sensed loss of condenser vacuum and the Main Turbine trip caused an automatic reactor trip. All control rods fully inserted, and all three Auxiliary Feedwater pumps started as expected as a result of the reactor trip. All systems responded normally during and following the reactor trip. The cause of this event was a sheared common vacuum instrument sensing line to the Main Condenser 2B due to the sensing line being designed and installed without adequate flexibility. The failure was ultimately the result of a combination of residual stress induced by condenser movement and cyclic stress due to vibration. Immediate corrective actions included repair of the sheared vacuum instrument sensing line and modification of the supports on the Unit 1 and 2 sensing lines. The passive single point failure vulnerability was removed on Unit 2 during the tenth refueling outage and it will be removed on Unit 1 during the next refueling outage. All times in this report are approximate and Central Time unless noted otherwise.
4462008002 | Comanche Peak 2 | 05/22/2008 | 07/14/2008 | ML08204058 | <strong>P-14 Trip Function for Steam Generator 2-02 Narrow Range Level Channel Inoperable due to Mispositioned Hand Switch</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2008, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at 100% power. At 1120 hours, while performing a Main Control Board walk down Operators found the Unit 2 Reactor Coolant System (RCS) Steam Generator (SG) Liquid Level hand switch for Loop 2, Protection Set I in the incorrect position. The incorrectly positioned hand switch rendered the high-high level trip function for SG 2-02 Protection Set I Narrow Range Level Channel inoperable and further review determined that the mispositioned switch had most likely existed since May 14, 2008, a period of time greater than allowed by Technical Specifications. The cause of this event was an inadequate restoration step in the Channel Operational Test procedure. Corrective actions included issuing a Shift Order defining specific switch restoration requirements, revising all l&C procedures that involve manipulation of the SG level control switches, enhancing labeling on the SG level control hand switches, and reviewing the Operations training material associated with the SG water level alternate channel to ensure that it adequately addresses the TS implications. All times in this report are approximate and Central Time unless noted otherwise.
4542008001 | Byron 1 | 03/28/2008 | 06/13/2008 | ML08165045 | <strong>Technical Specification Non-Compliance of Containment Sump Monitor due to Improper Installation During Original Construction</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2008, with Unit 1 in a refueling outage, an Engineer identified a potential operability issue with the containment floor drain sump flow monitor (i.e., 1RF008). He noticed that the sump's cover was flush with the containment floor and had two instrument tubetrack penetrations through its cover with each having an approximately five linear inch narrow gap on its perimeter. These gaps, open to the sump below, would allow Reactor Coolant system (RCS) leakage to flow directly into the sump and bypass the collection system and weir box. With this bypass path, the 1RF008 could potentially not fulfill its design function to detect a one gpm RCS leak within one hour. An investigation revealed that the original design and construction of 1RF008 in the 1976 timeframe should have had it installed three inches higher such that the sump cover would be three inches above floor elevation. This installation detail would have ensured, by being three inches higher than the floor, that an RCS leak to the containment floor in the vicinity of the containment sump cover would be directed to the 1RF008 leakage collection system and weir box and not allowed to bypass it through the penetration openings in the cover. Due to the time frame the installation error was made (i.e., 1976), the investigation was unable to determine the cause for this installation error. The 1RF008 penetration openings have been blocked such that RCS leakage could not enter the sump via the sump cover and the design drawings for the Unit 1 and Unit 2 RF008 will be revised to indicate the as-built installation.
4542008002 | Byron 1, Byron 2 | 12/16/2008 | 02/17/2009 | ML09049017 | <strong>Technical Specification Non-Compliance due to Inadequate Design of Auxiliary Feedwater (AF) Tunnel Access Covers Causing AF Valves within the Tunnel to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>In July 2007, it was identified that a 1987 calculation, detailing available design margin associated with the Auxiliary Feedwater (AF) tunnel access covers, did not account for forces from a Main Steam (MS) line High Energy Line Break (HELB). The calculation scope was limited to loading expected during a station-flooding event. The load from an MS HELB is greater than the load from a station flood. Also, the identified margin for installed concrete expansion anchors was less than the design standard, which requires a Factor of Safety (FOS) greater than or equal to 4.0, yet no actions were taken to recover the desired design margin. An Operability Evaluation was performed which supported operability of the covers using a FOS of 1.0. However, on December 16, 2008, it was determined that use of a FOS of 1.0 for operability could not be supported and the AF tunnel flood seal opening covers were considered to have been inoperable from original construction until temporary modifications were installed in the summer of 2008 to regain margin. The cause of this condition was an inadequately designed component during original construction. An investigation was conducted but could not determine why the 1987 calculation did not consider HELB forces nor document the design standard non-compliance into the Corrective Action Program (CAP). Corrective actions include installation of temporary modifications and scheduled permanent modifications to regain margin and restore compliance with design standards, respectively. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications 3.6.3 Condition C.
4552008001 | Byron 2 | 03/25/2008 | 03/27/2008 | ML08148050 | <strong>Unit 2 Emeraencv Diesel Generators and Auxiliarv Feedwater Pump Automatic Start Resulting from a Loss of Offsite Power Due to a Failed Insulator Causing a Differential Phase overcurrent</strong><br /><i>Abstract:&nbsp;</i>At 6:35 pm CDT, on March 25, 2008, Unit 2 experienced a C-Phase differential over current relay actuation associated with System Auxiliary Transformer (SAT) 242-2, that resulted in the isolation of both Unit 2 SATs (242-1 and 242-2) from their common offsite power feed and their respective Engineered Safety Feature (ESF) buses. All safety equipment responded as designed, including the automatic start of the 2A and 2B Emergency Diesel Generators (DGs) to supply power to the ESF buses and the automatic start of the 2A Motor Driven Auxiliary Feedwater Pump, and auto-transfer of the non-ESF buses from the SATs to the Unit Auxiliary Transformers (UATs). The root cause was identified as the failure of a ceramic insulator on the B-Phase of the 4kV non-segregated bus associated with SAT 242-2. This failure was attributed to internal corona discharges that, over time, led to a breakdown of the insulating material. Due to the configuration of the current transformers associated with the differential relays, a B-phase fault is also sensed by the C-phase differential relay. Post event calibration of the B and C phase relays indicated the C-phase was set more sensitively than the B-phase relay and was expected to actuate first. SAT 242-2 bus duct insulators have received a high potential test to identify other degraded insulators. No other degraded insulators were found with this failure mechanism. The periodic inspection procedures for both the non-segregated and isolated-phase bus ducts will be revised to require the performance of a high potential test of the insulators.
4562008001 | Braidwood 1, Braidwood 2 | 12/16/2008 | 02/17/2009 | ML09048036 | <strong>Technical Specification Non-Compliance due to Inadequate Design of Auxiliary Feedwater (AF) Tunnel Access Covers Causing AF Valves within the Tunnel to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>In July 2007, it was identified that a 1987 calculation, detailing available design margin associated with the Auxiliary Feedwater (AF) tunnel access covers, did not account for forces from a Main Steam (MS) line High Energy Line Break (HELB). The calculation scope was limited to loading expected during a station-flooding event. The load from an MS HELB is greater than the load from a station flood. Also, the identified margin for installed concrete expansion anchors was less than the design standard, which requires a Factor of Safety (FOS) greater than or equal to 4.0, yet no actions were taken to recover the desired design margin. An Operability Evaluation was performed which supported operability of the covers using a FOS of 1.0. However, on December 16, 2008, it was determined that use of a FOS of 1.0 for operability could not be supported and the AF tunnel flood seal opening covers were considered to have been inoperable from original construction until temporary modifications were installed in the summer of 2008 to regain margin. The cause of this condition was an inadequately designed component during original construction. An investigation was conducted but could not determine why the 1987 calculation did not consider HELB forces nor document the design standard non-compliance into a Corrective Action Program. Completed corrective actions include installation of temporary and permanent modifications to regain margin and restore compliance with design standards, respectively. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications 3.6.3 Condition C.
4562008002 | Braidwood 1 | 12/17/2008 | 02/17/2009 | ML09048036 | <strong>Unit 1 Containment Isolation Valve 1PS229B De-energized Open Instead of Closed per Technical Specification 3.6.3</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2008, while performing a pressure test on a portion of the primary sampling system, excessive leakage was identified on containment isolation valve 1PS228B. Technical Specification (TS) 3.6.3 Condition A was entered for 1PS228B, which required the penetration flowpath to be isolated within four hours by closing and de-activating at least one valve. At 13:48 hours, the redundant containment isolation valve, 1P5229B, was de-energized by fuse block removal, and TS 3.6.3 Condition A was considered to be met. A subsequent review determined that 1PS228B was not inoperable, and this was verified on December 19, 2008, by performance of a local leak rate test on the affected containment penetration. Upon reenergization of 1PS229B to allow valve manipulation, the valve indicated Open. A review of 1PS229B identified the valve to be a fail as-is valve upon loss of power. Therefore, while the fuse block for 1PS2298 was removed with the valve open, the valve could not close on a containment isolation signal, and was determined to be inoperable when the fuse block was removed. TS 3.6.3 Condition applied to 1PS2298 which required the valve be isolated within four hours. Valve 1PS229B was failed open for approximately 44 hours without being isolated. The cause of this event was determined to be inadequate procedure guidance to ensure the component was placed in the proper position. The corrective action to prevent recurrence is to revise the operating procedure to add specific controIs to prompt the user to identify the proper isolation valve, the failure mode of the valve if appropriate, and verifications that the actions taken properly isolated the penetration. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
4572008001 | Braidwood 2, Braidwood 1 | 09/02/2008 | 04/09/2009 | ML09099049 | <strong>2A Essential Service Water Train Inoperable due to Strainer Fouling from Bryozoa Deposition and Growth</strong><br /><i>Abstract:&nbsp;</i>On September 2, 2008, the 1A Essential Service Water (SX) pump discharge strainer differential pressure increased significantly during a pump surveillance. The 1A SX train was declared inoperable due to strainer fouling. On September 4, 2008, the 2A SX train was declared inoperable due to the inability to manually backwash the 2A SX strainer. Subsequent inspection identified the presence of live bryozoa in the Circulating Water (CW) forebays (i.e., SX pump suction source). Following cleaning of the forebays, on September 4, 2008, the 1A SX train was restored to operable status, and on September 6, 2008, the 2A SX train was restored to operable status. On October 8, 2008, it was determined that the 2A SX train should have been considered inoperable at the same time the 1A SX train was declared inoperable, based on the 1A and 2A pumps sharing a common suction source. Since the 2A SX train was not returned to an operable status until September 6, 2008, the Limiting Condition for Operation 3.7.8, Condition A, 72 hour Completion Time was exceeded. The causes of this event are: 1) the site organization did not understand the bryozoa life cycle and the bryozoa deposition and growth mechanism downstream of the CW forebay traveling screens, and 2) a lack of questioning attitude existed regarding the SX strainer design to address rapid fouling challenges. The corrective actions include: development and implementation of a lake macro-biological program; and establishment of a process for utilization of a Devil's Advocate in situations where key decisions are made for the performance of the safety related systems. here were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
4572008002 | Braidwood 2 | 12/27/2008 | 02/25/2009 | ML09057036 | <strong>Reactor Trip on Unit Auxiliary Transformer 241-1 Sudden Pressure Relay Actuation due to 2C Heater Drain Pump Motor Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2008, at 14:18 hours, Braidwood Unit 2 Unit Aux Transformer 241-1 sudden pressure relay actuated causing a Unit 2 main generator trip, which resulted in a Unit 2 main turbine trip and subsequent Unit 2 reactor trip. Concurrent with the reactor trip, the 2C heater drain pump (HD) tripped on phase "A" and "C" phase over current. Operator response to the trip was proper and all safety related systems, structures and components operated normally during this event. The auxiliary feedwater system actuated, as expected, to maintain steam generator levels. The investigation of this event determined the initiating event to the reactor trip was a phase-to-phase motor fault at the 2C HD pump motor terminal housing box, which caused a trip of the 2C HD pump on phase over current. Inspection of the motor lead box found the motor lead from one phase ("A" phase) in contact with the bus bar for another phase ("C" phase) due to excessive motor lead length. The root cause of the HD pump trip was determined to be that the procedure guidance for trimming the motor leads was deficient in that a lack of adequate information was provided for the desired motor lead length. The corrective action to prevent recurrence is to revise the existing procedure to provide clear direction on the desired length of power cables. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
4582008001 | River Bend | 01/08/2008 | 03/10/2008 | ML08077016 | <strong>Automatic Actuation of Standby Service Water System due to Inadequate Work Instructions</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2008, at 9:50 a.m. CST, an unplanned automatic actuation of the Division 1 and 3 standby service water (SWP) systems occurred during maintenance. The plant was shut down for a refueling outage at the time of the event. The work being performed at the time of the event involved the replacement of a power supply in the Division 1 containment penetration valve leakage control system. The work procedure required lifting a neutral ground lead. When this action was taken, power was interrupted in other parts of the connected circuitry. This was not an anticipated response. This loss of power caused an invalid initiation signal to the Division 1 SWP system, resulting in the automatic start of the "A" SWP pump. The configuration of the system and its normal response to such a signal inherently caused an actual momentary low pressure condition and subsequent initiation signal to the "C" SWP pump (Division 3). The actuation of the Division 1 SWP subsystem was invalid since the actual monitored parameter did not change. The actuation of the Division 3 subsystem was a valid actuation as it resulted from an actual low pressure condition in the system. This event is being reported in accordance with 10CFR50.73 (a)(2)(iv)(A) as an automatic actuation of the standby service water system.
4582008002 | River Bend | 03/05/2008 | 05/02/2008 | ML08128048 | <strong>Automatic Reactor Scram due to Malfunction of Main Turbine Control System</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2008, at 2:43 p.m. CST, an automatic reactor scram occurred while the plant was operating at 60 percent power. The scram signal was initiated by high steam pressure in the reactor, and all control rods inserted as designed. The initial pressure transient caused the automatic actuation of nine main steam safety-relief valves. Reactor water level momentarily decreased to Level 3 immediately following the scram, resulting in the automatic closure of the containment isolation valves in the suppression pool cleanup system. Reactor pressure and water level were promptly stabilized following the initial transient. A malfunction in the main turbine control system resulting from a loose, oil-contaminated electrical connector apparently produced an errant turbine speed error signal. This signal caused a closure of the turbine control valves, resulting in high reactor steam pressure. The connector was cleaned and reassembled. A preventative maintenance task will be developed to inspect this and similar connectors periodically. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an unplanned actuation of the reactor protection system and the primary containment isolation system.
4582008003 | River Bend | 06/27/2008 | 08/26/2008 | ML08255047 | <strong>Reactor Pressure Trip Unit Inoperable Greater than Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2008, it was determined that a safety-related reactor pressure instrument had been left out of the tolerance range allowed by Technical Specifications during the performance of a scheduled quarterly calibration on April 11, 2008. That condition existed until the next scheduled performance of that test on June 7th. The as-left setting of the instrument during the calibration on April 11th resulted in it being in an inoperable status that was not recognized. This condition existed for longer than the allowable outage time of 14 days in TS 3.3.4.2. The test instrument used during the calibration on April 11th was out of calibration, and this was not recognized until after the June 7th test. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications. Interim job expectations have been instituted regarding the discovery of out-of-tolerance settings during calibration checks.
4612008001 | Clinton 1 | 02/10/2008 | 03/29/2011 | ML11096007 | <strong>Reactor Recirc Pump Trip Initiates Automatic Scram on High RPV Water</strong><br /><i>Abstract:&nbsp;</i>On 2/10/08 the 'B' Reactor Recirculation (RR) Pump unexpectedly tripped from fast speed to off. Reactor Pressure Vessel (RPV) water level increased to the automatic scram setpoint. Operators placed the Reactor Mode Switch in Shutdown but the automatic scram on high RPV water level occurred approximately one second prior. The operator reported reactor power at zero percent and control rods status, but had difficulty verifying four control rods due to anomalous indication on the full core display. When RPV water level decreased below the low RPV water level setpoint, operators entered Emergency Operating Procedure (EOP) 1, RPV Level Control, and then transitioned to EOP 1A, ATWS RPV Level Control, in response to the anomalous position indication of four control rods. During control rod position verification by other crewmembers, all control rods were verified to have fully inserted on the initial scram. The causes of this event are low risk perception in investigating and resolving an unexplained source of voltage in a circuit, and insufficient technical rigor in not specifying tuning of feedwater level control system (FWLCS) following a previous scram. Corrective action includes conducting briefings on the root cause of this event emphasizing risk, consequences and application of appropriate human performance fundamentals, tuning the FWLCS, and revising procedures.
4612008003 | Clinton 1 | 01/21/2008 | 08/23/2010 | ML10244003 | <strong>Excessive Leakage through Feedwater Isolation Valve 1B21F032A</strong><br /><i>Abstract:&nbsp;</i>On 1/28/08, primary containment local leak rate test (LLRT) performed on feedwater check valve, 1B21-F032A, exceeded acceptance criteria. Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.11 requires that the combined leakage rate for both primary containment feedwater penetrations to be less than or equal to 2 gallons per minute (gpm) for the worst of the isolation valves. The measured leakage rate for 1B21-F032A was reported to be 3.75 gpm. Following the identification of the excessive leakage, an internal inspection of the valve was performed and the disc and seat conditions were found satisfactory. The air actuator was stroked with the top of the valve removed and was found not stroking consistently and evenly. The air actuator linkages were cleaned and lubricated resulting in the disc seating properly. The LLRT was performed with satisfactory results on 1/26/08, prior to plant startup. The cause of check valve 1B21-F032A failing leak rate testing is considered to be age-related degradation of lubrication causing increased friction in the actuator. Corrective action includes establishing preventive maintenance activities to lubricate and overhaul the actuators. Reportability of this event was not discovered until 3/24/10 during review of the cause evaluation for another LLRT failure.
4822008001 | Wolf Creek | 01/10/2008 | 03/07/2008 | ML08078041 | <strong>Completion of a Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 01/10/2008 and 01/11/2008 air (voids) was found entrapped on the suction side of the Centrifugal Charging and Safety Injection (SI) pumps. Wolf Creek Operations conservatively declared both trains of the Emergency Core Cooling System (ECCS) inoperable, entered Technical Specification 3.0.3 and the plant entered Mode 3. An ultrasonic examination of piping from the Residual Heat Removal (RHR) discharge to the Centrifugal Charging pumps (CCP) and SI pumps suction line, called the piggy-back line, found a void. The void collected at high points in the piping. These high points were the result of fabrication and construction during the original installation of the piping. Engineering evaluation of the void content in the suction piping concluded that the ECCS would still meet its safety function.
4822008002 | Wolf Creek | 02/14/2008 | 06/24/2010 | ML10181025 | <strong>Technical Specification Allowed Outage Time Exceeded due to Room Cooler Leak</strong><br /><i>Abstract:&nbsp;</i>At 1420 hours Central Standard Time on February 13, 2008, with the "B" train diesel generator out of service for planned maintenance activities, the "A" train Centrifugal Charging Pump (CCP) was declared inoperable due to an associated room cooler tube leak. Technical Specification (TS) Limiting Condition of Operation (LCO) 3.0.3 was entered at 1820 hours due to two trains of Emergency Core Cooling Systems being declared inoperable. A plant shutdown was commenced at 1850 hours. At 1950 hours, the NRC granted a Notice of Enforcement Discretion to allow an additional 15 hours to restore the "A" train CCP and its associated room cooler to OPERABLE status. The power reduction was stopped and the plant was returned to 100% power. TS LCO 3.0.3 was exited. On February 14,.2008, at 0141 hours, the "A" train CCP room cooler was returned to service. The condition causing the need for the enforcement discretion was corrected. The appropriate TS Conditions were exited.
4822008003 | Wolf Creek | 03/17/2008 | 05/13/2008 | ML08142001 | <strong>Manual Reactor Trip due to Loss of Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2008, at approximately 1:00 PM while operating at 100% power, Wolf Creek Generating Station (WCGS) was manually tripped due to loss of steam generator (SIG) level. 4.16-kV busses PB03 and PB04 were cross-tied and being supplied by transformer XPB03. A secondary power cable from transformer XPB03 faulted to ground causing loss of power to all condensate pumps that tripped the main feedwater pump on low suction. The direct cause of the faulted transformer was human error. During previous maintenance the transformer bushing multi-conductor connector was reassembled improperly resulting in a loose connection. Together with the loose connection, the higher current caused by the cross-tied busses overheated the individual conductors and insulation resulting in a fault to ground. The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in WCGS Updated Safety Analysis Report (USAR) section 15.2.7, "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
4822008004 | Wolf Creek | 04/07/2008 | 11/11/2009 | ML09324013 | <strong>Loss of Offsite Power Event When the Reactor Was De-fueled</strong><br /><i>Abstract:&nbsp;</i>On 4/7/2008, during the Wolf Creek Generating Station (WCGS) refueling outage, work was on-going in the WCGS Switchyard. At 1017, a loss of offsite power (LOOP) event was initiated when a relay technician, performing transmission line transfer/breaker failure trip preventative maintenance testing on a 345 kV breaker, closed the wrong set of trip links. The "B" emergency diesel generator (EDG) automatically started and provided the electrical power needed for safety related equipment. At the time of the LOOP, all of the reactor fuel had been off-loaded from the core and was being stored in the spent fuel pool. The control room staff declared a Notification of Unusual Event (NUE). Offsite power was restored at 1024 and the NUE was exited at 1250 on 4/7/2008, when the EDG was manually shut down.
4822008005 | Wolf Creek | 04/26/2008 | 06/23/2008 | ML08184011 | <strong>Unanalyzed Condition Discovered due to Improperly Installed Fuse in Class 1 E Electrical Equipment Room Cooler</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2008, while trouble shooting a loss of the 'B' train Class lE electrical equipment room cooler, it was discovered that the redundant fuse used to ensure the cooler can be started after a control room fire was installed in series with the control power transformer secondary side fuse, not in parallel as per design. In the series configuration, if an electrical short occurs on the Control Room side of the circuit and blows the fuse, the "isolated" portion of the circuit, fed from the redundant fuse, would also lose power. Therefore, the circuit could not be re-energized and the air conditioning unit could not be re-started in the event of a Control Room Fire. At the time of the discovery, Wolf Creek Generating Station was in a refueling outage in Mode 6. The room cooler unit had been replaced in 2003. The vendor incorrectly wired the fuses in series. There were no compensatory measures required since the plant was in Mode 6. The configuration was corrected prior to entering Mode 4.
4822008006 | Wolf Creek | 05/07/2008 | 07/03/2008 | ML08196008 | <strong>Entry into Mode 4 without an Operable Containment Spray System</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage 16, Wolf Creek Generating Station entered Mode 4 on 05/07/08 at 2044 with the "B" containment spray pump inoperable. A post maintenance visual weld examination (VT-2) for leakage had not been completed as required by the In-service Testing Program prior to Mode 4 entry. Technical Specification 3.6.6. Limiting Condition for Operation (LCO) 3.6.6 requires two containment spray trains and two containment cooling trains to be Operable in Modes 1, 2, 3, and 4. The incomplete VT-2 test was discovered early on 5/8/2008 and an entry into the Technical Specification 3.6.6. LCO was made at 0145 on 5/8/08. The VT-2 examination was successfully performed and the containment spray system was declared operable at 0313 on 5/8/2008.
4822008007 | Wolf Creek | 05/11/2008 | 07/10/2008 | ML08198012 | <strong>Two Residual Heat Removal Trains Inoperable in Mode 3 due to Check Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On 5/11/2008, Wolf Creek Generating Station was in Mode 3 coming up in power at the end of Refueling Outage 16. At 0300 on 5/11/2008, leakage was identified from a relief valve located on the Residual Heat Removal (RHR) discharge header. This line is a common injection line for both trains of RHR to the Reactor Coolant System (RCS) Loop 2 and 3 Hot Legs. The leakage from the relief valve was due to a failure of the bellows, which made the valve inoperable. Both trains of RHR were declared inoperable. Technical Specification 3.0.3. was entered and actions were taken to cool down to Mode 4. Mode 4 was entered at 0725 on 5/11/2008. The failure of the RHR relief valve was caused by back leakage from the 'D' Safety Injection Accumulator through an RHR check valve. The RHR relief valve was replaced on 5/11/2008 at 2153. The check valve was flushed and successfully seated on 5/13/2008. The event was of low safety significance. Both RHR trains were available and could have provided flow to the RCS in the event of an accident.
4822008008 | Wolf Creek | 08/04/2008 | 08/25/2009 | ML09245042 | <strong>Potential for Residual Heat Removal Trains to be Inoperable During Mode Change</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2008, during a review for potential void formation to address Generic Letter 2008-01, a concern with the Residual Heat Removal (RHR) system during Mode 4 and Mode 3 was identified. During shutdown conditions, Wolf Creek Generating Station typically lines up one or both of the RHR trains to the Reactor Coolant System (RCS) for shutdown cooling and switches them to RHR Injection mode of operation prior to entering Mode 3 from Mode 4. During the switchover, system procedures require the RHR system to be cooled down, using the mini-flow line through the RHR heat exchanger. The physical location where the mini-flow piping returns to the suction of the RHR system prevents cooling approximately 140 feet of the RHR suction line. The stagnant water in the RHR suction line cools by ambient losses only and can remain high (maximum 350 degrees F) for several hours. The saturation pressure for this hot water can prevent the check valve from the Refueling Water Storage Tank from opening, preventing flow to the suction of the RHR pumps during a Mode 3 Loss of Coolant Accident. The condition with hot water in the RHR suction piping can also occur shortly after initiating RHR Shutdown cooling mode of operation during the cooldown and would exist until RCS temperatures are reduced sufficiently to preclude a concern. Further review of the plant conditions during Refueling Outage 16 showed that not only was the RHR system inoperable during the heat up at the end of the outage, but it also occurred during cool down at the beginning of the outage.
4822008009 | Wolf Creek | 10/21/2008 | 12/19/2008 | ML08365935 | <strong>Inadequate Compensatory Actions for a Fire Area</strong><br /><i>Abstract:&nbsp;</i>Wolf Creek Nuclear Operating Corporation (WCNOC) did not establish compensatory measures as required by its' License and by procedure, when it was discovered that post-fire safe shutdown capability could be adversely affected if a fire occurs in the Control Rod Drive/Motor-Generator Set Room located in the Auxiliary Building (fire area A-27). A fire in area A-27 could cause a pressurizer power operated relief valve to spuriously open. The manual actions established to mitigate this condition would cause a loss of Class 1E 125 VDC power to a number of Train B components that are required for safe shutdown if a fire occurs in area A-27. The compensatory measure that should have been taken was the establishment of an hourly fire watch. This condition was self identified by WCNOC but no compensatory measures were established at that time due to the misapplication of RIS 2004-03.
4832008001 | Callaway | 03/26/2008 | 09/29/2009 | ML09272078 | <strong>Containment Cooler Inoperability</strong><br /><i>Abstract:&nbsp;</i>Containment cooler "A" tripped while switching from fast to slow speed. Investigation revealed that during fast-speed operation, the containment coolers could trip under high-load conditions, especially with a change in speed. Review of operating history confirmed times when at least one or two (out of four) containment coolers were inoperable due to this condition for a longer time than permitted by Technical Specifications. The original design for the containment coolers did not consider worst-case normal operating conditions when sizing the fan motors. This resulted in the fan motors being undersized for fast-speed operation. During accident conditions the fans run in slow-speed. The identified condition could have caused the affected containment coolers to fail to restart automatically in slow-speed following a fast-speed thermal overload trip. A plant modification to the coolers' control circuits was completed which separated the fast-speed and slow-speed thermal overload circuits, thus allowing the fans to automatically restart in slow-speed even if the fast-speed thermal overloads have tripped. Sensitivity studies using the containment analysis code concluded that even with reduced containment cooler availability, the calculated post-accident pressure and temperature peak values would not exceed the peak accident values presented in the Final Safety Analysis Report (FSAR).
4832008002 | Callaway | 05/21/2008 | 11/05/2009 | ML09309064 | <strong>Void Found in Line EM-023-HCB - Residual Heat Removal Pump "A" to Safety Injection Pumps</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2008, Callaway plant personnel discovered a void in piping between a residual heat removal heat exchanger and common suction header for the safety injection pumps (SIPs). The void had existed in the piping since restoration of maintenance on a relief valve on May 5, 2007. The void was found during ultrasonic testing of the piping to verify that the emergency core cooling system (ECCS) was full of water. Review of work history determined the cause of the void was improper filling and venting of the piping. The void was removed by venting the piping on May 21, 2008. This piping where the void was located is used during the recirculation phase of a loss of coolant accident (LOCA), but not during the injection phase of a LOCA. A conservative evaluation of the potential effects of the void determined that the void could have degraded the performance of either both SIPs or both Centrifugal Charging Pumps during the recirculation phase. It was thus conservatively determined that the ECCS was inoperable with the presence of the void, thus constituting an operation or condition prohibited by the Technical Specifications, as well as a condition that could have prevented fulfillment of a safety function.
4832008003 | Callaway | 10/11/2008 | 12/04/2008 | ML08359029 | <strong>Inadvertent P-14 FWIS Actuation followed by Reactor Trip Actuation due to Steam Generator Low-Low Water (NR)</strong><br /><i>Abstract:&nbsp;</i>At 0508 CST on 10/11/08, during plant shutdown for a scheduled refueling outage, with the plant in MODE 4, an actuation of the Reactor Trip System (RTS) occurred as the result of a Steam Generator (SG) Low-Low water level trip. Plant operators were in the process of recovering from a Feedwater Isolation (FWIS) actuation that had occurred in response to a SG high water level trip condition. Previously, at 0500, operators had closed the Main Steam Isolation valves (MSIVs). With the MSIVs closed, the cooldown rate ceased. To restore cooling, an attempt to open the 'A' MSIV was made and believed to be unsuccessful, so the 'A' Atmospheric Steam Dump valve (ASD) was then opened. After the ASD was opened, the 'A' MSIV stroked open. With both the MSIV and ASD open, the 'A' SG water level swelled until the P-14 SG Hi Level protective interlock setpoint was reached, resulting in a FWIS actuation. Operators took action to recover from the FWIS actuation in accordance with off-normal operating procedures, and started the 'B' Motor-Driven Auxiliary Feedwater Pump to restore SG water level. However, due to the cold temperature of the auxiliary feedwater, the SG water level lowered rapidly in response to the additional steam and feedwater flow. A Low-Low water level trip signal then occurred on the 'A' SG, resulting in a RTS actuation and an Auxiliary Feedwater Actuation Signal at 0508.
4832008004 | Callaway | 10/17/2008 | 12/12/2008 | ML08354018 | <strong>Failure to Maintain Containment Purge & Exhaust System in Service During Core Alts w/ Equipment Hatch Open</strong><br /><i>Abstract:&nbsp;</i>At 2331 on October 17, 2008, while the Refuel 16 refueling outage was ongoing, core off-load recommenced with the equipment hatch open and the containment purge and exhaust system not in service. The mini-purge exhaust fan was then started at 0212 on October 18, 2008. Core alterations continued from 2331 on October 17, 2008 to 0212 October 18, 2008 (2 hours, 41 minutes) with the equipment hatch open and the containment purge and exhaust system not in service. On October 19, 2008 Operations, when planning restoration of the load center associated with the containment shutdown purge exhaust fan, determined that this was in violation of Callaway operating procedure OSP-SF-00003 (Rev. 018) step 6.3.4 and Technical Specification (TS) 3.9.4. A root cause investigation was performed to determine causes and corrective actions for the resulting condition prohibited by T/S. The investigation found that the root cause of the failure to have the containment purge and exhaust system in service during core alterations with the equipment hatch open was a failure to adequately or completely implement Callaway Operating License Amendment 152 in procedures. The corrective action to prevent recurrence (CATPR) was to update Operations procedures to address administrative controls for having the equipment hatch open. This CATPR is complete.
4832008005 | Callaway | 11/11/2008 | 12/23/2008 | ML09007023 | <strong>Reactor Manually Tripped due to "B" Main Feed Pump Tripping on Low Lube Oil Pressure</strong><br /><i>Abstract:&nbsp;</i>On 11/11/2008, while operating at 97-percent reactor power, with power increasing following Refuel 16, the "B" main feedwater pump (MFP) turbine tripped. Since the loss of one MFP at greater than 80-percent power challenges the plant's ability to maintain steam generator (SG) water levels to support continued plant operations, the reactor was manually tripped per plant operating procedures. All control rods fully inserted during the event and all safety systems responded as designed. Operation of the Auxiliary Feedwater system restored SG levels. Operation of the main steam supply system provided the heat sink for decay heat removal following shutdown. No primary relief valves or main steam relief valves lifted during the event. No primary to secondary leakage existed. No radioactive material was released. This event was considered an uncomplicated reactor trip. The cause was that the o-rings in the MFP lube oil strainer were a material susceptible to swelling in petroleum-based lubrication systems. An o-ring originally located in one of the MFP lube oil basket strainers swelled, became dislodged, and traveled into a MFP turbine bearing oil supply pressure regulating valve. The corrective actions to prevent recurrence included identification of a replacement for the o-rings. The correct o-rings were installed in both strainers for the "A" and "B" MFP turbine oil system.
4832008006 | Callaway | 12/11/2008 | 06/18/2009 | ML09173018 | <strong>Reactor Trip due to Turbine Trip During Power Reduction Following Loss of 'C' Condensate Pump</strong><br /><i>Abstract:&nbsp;</i>At 2254 on December 11, 2008 the 'C' condensate pump tripped. After confirming the trip, operators began a reduction in power and entered the Callaway off-normal procedure for Feedwater System Malfunction. However, the manual load reduction rate was approximately 31% in one minute, exceeding the procedural guidance of 5% per minute. At 2256 the control rods automatically stepped in and the condenser steam dumps opened as designed. Subsequently, steam generator (SIG) level deviation annunciators actuated for all 4 S/Gs and a turbine trip/reactor trip occurred at 2300. The turbine tripped on a Hi-Hi S/G level feedwater isolation signal (FWIS) from the 'B' S/G, and the reactor trip immediately followed. Additionally, as a result of the FWIS, both main feedwater pumps tripped. Hence, a motor-driven auxiliary feedwater actuation occurred as expected. Investigations were performed for the 'C' condensate pump motor failure and system actuations. The root cause of the motor failure was determined to be a ground fault. The root causes of the system actuations (including the reactor trip) were human performance errors which resulted in the excessively rapid load reduction and a configuration control process deficiency related to field-tuning of the feedwater controller gain settings. The corrective actions to prevent recurrence of these root causes are discussed in Section III.
4832008007 | Callaway | 12/12/2008 | 02/06/2009 | ML09054005 | <strong>Intermediate Range Hi Flux Reactor Protection System Actuation While Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 1042 on 12/12/2008, while in Mode 3, an invalid reactor trip signal was generated during maintenance activities on intermediate range (IR) nuclear instrument SEN0036. In addition to the reactor trip, a feedwater isolation actuation occurred. Reactor Operators manually started motor driven auxiliary feedwater pumps to maintain steam generator levels, prior to an anticipated Auxiliary Feedwater actuation. The IR high flux reactor trip was a result of removal of the control power fuses for IR nuclear instrumentation N-36 while performing work to replace a bistable card for SEN0036. It was desired to de-energize equipment prior to circuit card replacement to protect electronic circuits. When a step was included in the work document to remove the control power fuses it was not understood that a relay would be de-energized which allowed the IR High Flux Reactor trip signal to be generated. Corrective action (CA) will include installing labels and training instrumentation and controls personnel about the effects of pulling control power fuses for nuclear instrumentation.
4832008008 | Callaway | 12/14/2008 | 02/05/2009 | ML09049083 | <strong>Reactor Manually Tripped due to "B" Condensate Pump Tripping due to a Motor Ground Fault</strong><br /><i>Abstract:&nbsp;</i>On 12/14/2008, while operating at 98-percent reactor power with two of three condensate pumps available and running, the control room received steam generator (SG) feed flow/steam flow mismatch annunciators followed by SG level deviation alarms. Immediately thereafter, control room operators confirmed the loss of the "B" condensate pump. With only one condensate pump running at greater than 45-percent reactor power, the reactor was manually tripped. All control rods inserted during the event and all safety systems responded as designed. Operation of the Auxiliary Feedwater system restored SG levels. Operation of the main steam supply system adequately provided the heat sink for decay heat removal following shutdown. No primary to secondary leakage existed. No radioactive material was released. This event was considered an uncomplicated reactor trip. The cause of the "B" condensate pump trip is a stator turn-to-turn winding failure of the pump motor that progressed to a ground fault. The Root Cause is voltage surge damage to motor winding insulation. The Corrective Action to Prevent Recurrence is to install surge capacitors at the condensate pump motor lead boxes to minimize the slope of the voltage transient wave front.
4992008001 | South Texas 2 | 10/16/2008 | 12/11/2008 | ML08359007 | <strong>Incorrectly Stored Fuel Assembly in U2 Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2008, while planning fuel movements in the Unit 2 spent fuel pool (SFP), a Category 11 fuel assembly was discovered in a location where only Category 9 fuel is allowed. Following this discovery, the incorrectly stored fuel was removed from its location and placed in an area of the SFP with no adjacent fuel assemblies. A Category 11 assembly is less reactive than a Category 9 assembly, and the as-found configuration was bounded by the safety analysis. The investigation identified that the error occurred in the mapping of the SFP storage configuration, which is subsequently used to create fuel transfer forms (FTF). Both the FTF preparer and verifier performed inadequate selfchecking and review. Contributing factors included a lack of detailed written guidance for performing this task and that the Reactor Engineer (RE) preparing the FTF did not realize that some fuel assemblies had decayed directly from a Category 8 to a Category 11. This resulted in fuel moves that stored a Category 11 assembly adjacent to Category 9 assemblies, which is not permitted by the Technical Specifications. A procedural guideline to control the process of developing the SFP configuration map is being developed to prevent future occurrences. In addition, all individuals who are responsible for performing this task were briefed on management expectations related to preparation, peer checking, and attention to detail. Both Unit 1 and Unit 2 SFPs were checked for a similar condition. No other occurrences of incorrectly stored fuel were identified.
4992008002 | South Texas 2 | 10/25/2008 | 10/29/2009 | ML09310029 | <strong>Loss of Residual Heat Removal and Valid Actuation of Safety Systems</strong><br /><i>Abstract:&nbsp;</i>At 2344 on October 25, 2008, with Unit 2 in Mode 5 during the end of a refueling outage, a valid Safety Injection actuation signal occurred. The actuation resulted in automatic start of all three Engineered Safety Features Diesel Generators, a Containment ventilation isolation, a Containment phase A isolation and tripping of the running Residual Heat Removal pumps. The actuation was the result of removing a block for the low steam pressure actuation signal during a maintenance activity to replace a circuit card in the Solid State Protection System. The actuation was not part of a pre-planned sequence during testing or reactor operation. The removal of the signal block was unintended. Although the action was unintended, the signal was a valid signal initiated in response to a parameter satisfying the requirements for initiation of the safety function of the system. There was no discharge of the Emergency Core Cooling System (ECCS) into the Reactor Coolant system because the ECCS pumps had been properly removed from service for the plant condition. Residual heat removal capability was restored within 4 minutes of the actuation. The causes of the event were: (1) the outage process did not have specific requirements for processing emergent work or evaluating risk impact on plant conditions; (2) the work planning guidance lacked sufficient rigor; and (3) the work package was complex. Corrective actions include implementing plant procedures to specify requirements for addressing emergent work during outages and assessing the impacts associated with shutdown risk; and revising the Planner's Guide to develop defense-in-depth strategies This event did not have an adverse effect on the health and safety of the public.
4992008003 | South Texas 2 | 10/14/2008 | 01/12/2009 | ML09023017 | <strong>Inoperable Component Cooling Water Train</strong><br /><i>Abstract:&nbsp;</i>At 20:59 on October 14, 2008, Unit 2 Component Cooling Water (CCW) Train A was discovered to be inoperable due to an inoperable level switch in the CCW surge tank. During surveillance testing of the low-low level switch, it did not respond as required. Troubleshooting identified the cause of the failure as a loose wire. Operability was restored at 01:58 on October 16, 2008. Technical Specification 3.7.3 requires that if one train of CCW is inoperable in Modes 1, 2, 3, and 4, it is to be restored to operability within seven days or the unit is to be in at least hot standby within six hours. Previous maintenance that could have affected the wire was completed January 22, 2008. The allowed outage time expired on January 29, 2008. Because these components were inoperable longer than allowed under the Technical Specifications without taking the appropriate action, this event is reportable under 10 CFR 50.73(a)(2)(i)(B). The root cause of the event was an inadequate calibration procedure. The procedure did not require a functionality check of the internal switch contacts after switch calibration restoration. Maintenance procedures for safety-related equipment will be reviewed to identify procedures that are not followed immediately by a functionality check, and will be corrected as necessary. Only CCW Train A of Unit 2 was affected by this condition. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
5282008001 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 02/01/2008 | 04/01/2008 | ML08099064 | <strong>Inadequate Surveillance Test Procedure Resulting in Failure to Meet TS Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2008, during performance of the Component Design Bases Review initiative, engineering personnel determined that surveillance test procedure (STP), "Remote Shutdown Disconnect Switch and Control Circuit Operability," was not adequate to meet the Technical Specification (TS) Surveillance Requirement (SR). TS SR 3.0.3 was entered for the affected components, and risk assessments were performed which supported continued operability until such time as the components could be adequately tested. The direct cause of this condition was that the STP did not ensure that each circuit was verified to meet the requirements of the TS SR. The preliminary root cause analysis is that 10 CFR 50, Appendix R experienced personnel did not provide input during the development of the STP. Corrective actions include performance of new and revised STPs to adequately demonstrate compliance with the TS SR within the schedule permitted by TS SR 3.0.3. There have been two previous similar occurrences of failure to meet TS SRs due to inadequate STPs in the past three years. Corrective actions taken as a result of those conditions would not have prevented this condition.
5282008003 | Palo Verde 1 | 06/05/2008 | 08/04/2008 | ML08225045 | <strong>Technical Specification Required Shutdown - Safety Injection Tank 1A Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2008, at 01:48 Mountain Standard Time (MST), Unit 1 completed a shutdown to Mode 3 followed by a reduction in the reactor coolant system pressure to less than 1837 pounds per square inch as required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.1, Condition C, for an inoperable Safety Injection Tank (SIT) 1A. SIT 1A was declared inoperable at 02:25 on June 5, 2008, during an Operations Shift Manager's review of corrective action documents which identified a leak in the SIT 1A at the joint between the tank head and the SIT vent line nozzle. The actual time of discovery was at approximately 13:30 on June 4, 2008, when a maintenance team reported the completion of an inspection of SIT 1A and that a leak had been identified; therefore, entry into LCO 3.5.1, Condition B was delayed. The leak was repaired by performing an American Society of Mechanical Engineers (ASME) Class III weld repair to the outer surface of the vent nozzle and the tank was returned to service. No similar conditions have been reported in the past three years.
5292008001 | Palo Verde 2 | 05/21/2008 | 04/29/2010 | ML10131022 | <strong>Inoperable Boron Dilution Alarm Monitoring System</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2008, plant staff noted that the Boron Dilution Alarm System (BDAS) had been in alarm (alarm window flashing) for approximately one hour when no actual dilution was occurring. When a BDAS channel is in an alarm condition, the channel loses its ability to alert the control room operators of an inadvertent boron dilution event until the channel is reset manually. Review of alarm logs indicated that during the period from May 8, to May 21, 2008, when Unit 2 was in Modes 5 and 6, either a single BDAS channel or both channels were in alarm on multiple occasions for extended periods without being reset. During these periods, required Technical Specification (TS) 3.3.12 Actions A.1, B.1 and C.1 were not performed and TS Limiting Condition for Operation 3.0.4 was not met when the Operating Mode was changed from Mode 6 to Mode 5. The cause of the event was that licensed operators treated the alarm as a nuisance alarm and failed to reset the BDAS alarms in a timely manner. A night order was issued on May 22, 2008, as an immediate corrective action to direct timely reset of the BDAS alarms. The associated alarm response procedure was subsequently revised adding a note on the significance of the BDAS alarm function. No similar conditions have been by reported by PVNGS in the past three years.
5292008002 | Palo Verde 2 | 05/28/2008 | 07/28/2008 | ML08218035 | <strong>Manual Reactor Trip During Low Power Physics Testing</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2008, at approximately 21:34 (MST), while performing Low Power Physics Testing (LPPT) in Mode 2, Palo Verde Unit 2 was manually tripped as directed by procedure 40AO-9ZZ11, "CEA Malfunctions", when Control Element Assemblies (CEA) subgroup 3 (CEAs 7, 9, 11 and 13) dropped from approximately 120 inches withdrawn to fully inserted. The circuit breaker for subgroup 3 CEAs was found open. The root cause was indeterminate. The probable cause was high resistance on the subgroup breaker contacts. The circuit breaker was replaced. A repetitive task will be added to Operations procedures to cycle subgroup breakers each refueling outage to minimize the likelihood of similar occurrences. A CEA slipped several inches and resulted in a manual reactor trip in Unit 1 on May 8, 2004 and was reported on LER 50-528/2004-003-00.
5292008003 | Palo Verde 2 | 09/16/2008 | 11/17/2008 | ML08337029 | <strong>Technical Specification - Limiting Condition for Operation 3.0.3 for Greater Than 1 Hour</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2008, at 00:03 Mountain Standard Time (MST), Unit 2 was at 100 percent power when the 120 VAC class lE channel C instrumentation and control distribution panel was de-energized to troubleshoot and repair the associated 120 VAC Class1E inverter that had automatically transferred the panel's power supply to the backup voltage regulator on September 15, 2008. This resulted in a loss of the required redundant position indication for 67 of the 89 Control Element Assemblies (CEAs). As a result, LCO 3.0.3 was entered, which required initiation of action within 1 hour to place the unit in MODE 3 within 7 hours. LCO 3.0.3 was exited at 01:31 after the required redundant CEA position indication was restored. No power decrease was initiated. The root cause investigation of the inverter transfer is in progress. Troubleshooting identified the inverter's DC-DC converter circuit board (+)15 VDC voltage regulator did not meet vendor acceptance criteria. The board was replaced and the inverter was returned to OPERABLE status. LER 05000528-2008-002-00 reported an event in which a Unit 1 inverter failure was caused by a failed DC-DC converter and resulted in the unit remaining in LCO 3.0.3 for longer than one hour on April 24, 2008.
5302008001 | Palo Verde 3 | 09/16/2008 | 07/21/2010 | ML10210002 | <strong>Manual Reactor Trip when Removing a Degraded CEDM MG Set from Service</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2008, Unit 3 Operations personnel identified Motor Generator (MG) set 'A' was showing indications of being motorized due to an over-excited condition on MG set 'B'. The Control Element Drive Mechanism (CEDM) MG sets A and B supply power to the CEDM bus and are normally operated in parallel in order to support Control Element Assembly (CEA) movement in group mode. During trouble shooting activities, the 'B' MG set was removed from service while MG set 'A' provided power to the CEDMs. Upon removal from service, an undervoltage condition occurred on the CEDM system that resulted in a main turbine trip and initiated a reactor power cutback. Consistent with contingency actions established in the trouble shooting plan, a manual reactor trip was initiated. The direct cause of the MG set 'B' condition was the failure of a transistor on the excitation voltage power supply circuit board. One design-related root cause was identified for this event. The MG set 'B' excitation voltage regulation and suppression circuit boards were replaced. A plant modification which allows operators to override a failed automatic voltage regulator circuit on a degraded MG set until the load is shifted to the other MG set has been approved and is scheduled to be installed in all three units. Unit 3 was restarted on September 19, 2008.
5302008002 | Palo Verde 3 | 09/27/2008 | 11/26/2008 | ML08344031 | <strong>Manual Reactor Trip due to High Main Turbine Vibrations During Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2008, at approximately 21:51 hours, Mountain Standard Time, Unit 3 control room operators initiated a manual reactor trip from approximately 34% rated thermal power in response to high vibrations on the main turbine. The main turbine vibrations were experienced during a required power reduction resulting from a steam generator chemistry excursion. The event was considered an uncomplicated reactor trip. No automatic engineered safety feature (ESF) actuations occurred during the event and none were required. All safety related buses remained energized from normal offsite power during and following the reactor trip. The cause of the reportable event was the decision by control room operators to initiate a manual reactor trip in response to the main turbine high vibrations. The operators chose to initiate the reactor trip earlier than intended in the planned shutdown in response to the high turbine vibrations. The reactor trip was not necessary to mitigate the consequences of the event. There have been manual reactor trips in the past at Palo Verde Nuclear Generating Station but none with causes similar to this event. As such, the corrective actions for those events would not have prevented this event.