## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192015001 | Oyster Creek | 03/22/2015 | 08/12/2015 | ML15254A04 | <strong>Reactor Scram due to EPR Failure During MPR Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2015 at 1414, an automatic SCRAM from full power operation occurred at Oyster Creek due to a valid RPS actuation on APRM Hi-Hi flux. The APRM Hi-Hi flux was caused by a rise in reactor pressure due to the failure of the Electric Pressure Regulator (EPR). The backup Mechanical Pressure Regulator (MPR) did not limit reactor pressure. <br /><br /> The scram occurred due to inadvertent contact with degraded wiring during troubleshooting to isolate a DC ground identified within the turbine control indication circuitry. The contact caused a loss of signal from the EPR to its controlling Programmable Logic Controller (PLC) resulting in a loss of the EPR. This loss of signal, concurrent with the MPR being out of position, resulted in the subsequent rise of both reactor pressure and APRM flux that caused the SCRAM.<br /><br /> ENS 50916 was submitted on March 22, 2015 as required by 10 CFR 50.72 (b)(2)(iv)(B). This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
2192015002 | Oyster Creek | 05/07/2015 | 07/06/2015 | ML15196A03 | <strong>Reactor SCRAM due to Digital Protective Relay System Lockout</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2015 at 1727 hours, a Main Turbine Trip and subsequent Reactor Scram occurred from a trip of the Main Transformer Differential Lockout Relay, 86T. The Main Transformer Differential Lockout Relay, 86T is a protection function provided by Digital Protection Relay System "B" (DPRS B). The 86T trip signal was sensed arnd cleared, without operator action, in 17 milliseconds (ms) or 1 cycle prior to the 230KV output breakers opening. The results of extensive troubleshooting ruled out an actual fault in the Main Transformers or lso-phase Bus, and determined that the Main Transformer Differential Relay actuation was a spurious trip, and not due to an actual degraded equipment condition. <br /><br /> ENS 51055 was submitted on May 7, 2015 as required by 10 CFR 50.72 (b)(2)(iv)(B). This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).
2192015003 | Oyster Creek | 11/09/2015 | 12/31/2015 | ML16014A73 | <strong>Failure of the #1 Emergency Diesel Generator to Start During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2015, while attempting to commence a #1 Emergency Diesel Generator (EDG) test procedure, the #1 EDG failed to start and the "EDG 1 Disabled" Alarm annunciated in the Main Control Room. Locally, the operator heard relays chattering on the generator end of Diesel Generator #1 and notified the control room that the SEQ alarm was illuminated. Subsequently, a fast start of the #1 Emergency Diesel Generator was attempted but was unsuccessful. The cause of the failure was determined to be a failed zero speed relay (ZSR). The ZSR failure was caused by an internal component failure associated with age degradation of the Time Delay Module of the relay assembly. <br /><br /> The identification of this failure resulted in EDG #1 being declared inoperable and entry into an unplanned 7-day LCO at 0348. The repairs concluded on November 10, 2015 at 0400 and the #1 EDG was declared operable at 0634. <br /><br /> This issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition which was Prohibited by the plant's Technical Specifications since the likely time of failure would have been during the previous EDG#1 run which was conducted on October 26, 2015.
2202015001 | Nine Mile Point 1 | 02/11/2015 | 04/10/2015 | ML15112B18 | <strong>Secondary Containment Inoperable due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2015, at approximately 1935 hours, the secondary containment of the Nine Mile Point Nuclear Station Unit 1 (NMP1) Reactor Building (RB) was breached when station personnel opened both inner and outer airlock doors on RB 340 foot elevation simultaneously while traversing through the airlock. The integrity of the airlock was re-established within 5 seconds when one of the doors was closed and latched. Secondary containment differential pressure was unaffected by this event. The cause of the event is failure to use Human Performance verification tools prior to opening the airlock door. Corrective actions include updating the security training program and subsequent implementation. NMP1 LERs 2014-004, 2014-005 and 2014-006 were provided for similar events that occurred on August 13, October 16, and October 20, 2014, respectively. The three LERs in 2014 occurred at the main airlock into the RB 261 foot elevation. This is the first LER for simultaneous opening of the doors on the RB 340 foot elevation.
2202015002 | Nine Mile Point 1 | 03/03/2015 | 04/21/2015 | ML15119A22 | <strong>Secondary Containment Inoperable due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2015, at approximately 0837 hours, the secondary containment of the Nine Mile Point Nuclear Station Unit 1 (NMP1) Reactor Building (RB) was breached when station personnel opened both inner and outer airlock doors on RB 340 foot elevation simultaneously while traversing through the airlock. The integrity of the airlock was re-established within 5 seconds when the doors were closed and latched. Secondary containment differential pressure was unaffected by this event. The cause of the event is clear and well-advertised barriers and postings for passage through the air lock doors were not followed. Corrective action included disciplinary action for the individual not adhering to the postings and station expectations. NMP1 LERs 2014-004, 2014-005, 2014-006 and 2015-001 were provided for similar events that occurred on August 13, 2014, October 16, 2014, October 20, 2014 and February 11, 2015, respectively.
2202015003 | Nine Mile Point 1 | 08/05/2015 | 10/02/2015 | ML15313A02 | <strong>Secondary Containment Inoperable due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2015 at approximately 1252 hours, the secondary containment at Nine Mile Point Nuclear Station Unit 1 (NMP1) was breached momentarily. Station personnel opened both inner and outer airlock doors on the Reactor Building (RB) 261 foot elevation simultaneously while traversing through the airlock. The integrity of the airlock was re-established within 5 seconds when both doors were closed and latched. Secondary Containment differential pressure was unaffected by the event. <br /><br /> The cause of the event is the failure of an individual to comply with the posted expectations prior to opening the airlock door. Corrective actions taken included disciplinary action for the individual not adhering to the postings and station expectations. <br /><br /> NMP1 LERs 2014-004, 2014-005, 2014-006, 2015-001, and 2015-002 were provided for similar events that involved the simultaneous opening of both airlock doors.
2202015004 | Nine Mile Point 1 | 09/04/2015 | 11/03/2015 | ML15331A03 | <strong>Automatic Reactor Scram due to Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On Friday September 4th, 2015 at 09:16:04, Nine Mile Point Unit 1 automatically scrammed from approximately 100% rated power due to an inadvertent Main Steam Isolation Valve (MSIV) isolation. This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). During quarterly surveillance testing, the MSIV failed to stop its close stroke and reopen automatically per design, due to a failed MSIV pilot test valve. The root cause of the event was an inadequate application of the designed pilot test valve for MSIV control, resulting in the pilot test valve internals binding during the surveillance test. The failed pilot valve spool and cage assembly were replaced. The corrective action to prevent recurrence is to replace the MSIV pilot valves with an industry proven design.<br /><br /> The event described in this LER is documented in the plant's corrective action program.
2372015001 | Dresden 2 | 01/13/2015 | 04/30/2015 | ML15125A01 | <strong>Unit 2 Scram due to Feedwater Level Control Issues</strong><br /><i>Abstract:&nbsp;</i>On January 13, 2015, operators inserted a manual scram on Unit 2 due to increasing reactor water level. It was determined that the Feedwater Level Control (FLWC) system had failed. All control rods inserted, all systems responded as expected. The FWLC system was repaired and the unit was returned to operation on January 16, 2015.<br /><br /> On February 6, 2015, during maintenance activities to continue troubleshooting FWLC alarms, a reactor water level transient was induced. An automatic scram occurred due to low reactor vessel water level. During the transient, High Pressure Coolant Injection (HPCI) was initiated, but proceduralized operator response actions prevented injection. The Unit 2 and 2/3 Emergency Diesel generators started but did not load on to their respective busses as offsite power was not lost.<br /><br /> During both events, main feedwater was maintained in accordance with station operating procedures. These events are being reported under 10 CFR 50.73(a)(2)(iv)(A) "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)... "<br /><br /> The cause of these events has been determined to be spurious power interruption on a historically improperly landed power supply ribbon cable connection for the digital FWLC system. These events are considered of very low safety significance. Corrective actions include repairs to the ribbon cable connection and improvements to the troubleshooting process implementation.
2372015002 | Dresden 2 | 02/07/2015 | 08/07/2015 | ML15223A43 | <strong>2C ERV Failed to Actuate During Extent of Condition Testing</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2015, with the reactor in mode 4, an Electromatic Relief Valve (ERV) actuator failed to open during the performance of an extent of condition test. The testing involved an operator manually actuating the ERV from the main control room with operators and engineers staged in the field. However, when the demand signal was given, the 2C actuator plunger did not move and the valve did not open. The cause of this event was determined to be a lack of maintenance procedural guidance to align, determine excessive wear, and characterize wear of the ERV actuator subcomponents. <br /><br /> Corrective actions involved replacement of all four ERVs with an upgraded design and the development of enhanced inspection/maintenance guidance. <br /><br /> This failure was determined to be of very low safety significance because the cause of the failure only existed on one ERV.<br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(i)(B) "Any operation or condition which was prohibited by the plant's Technical Specifications," and under 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfilment of the safety function of structures or systems that are needed to mitigate the consequence of an accident."
2372015003 | Dresden 2, Dresden 3 | 09/04/2015 | 10/30/2015 | ML15306A44 | <strong>Unit 2 Turbine Building to Reactor Building Interlock Doors Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On 9/4/15 at 08:10 CDT, Technical Specification (TS) 3.6.4.1 Condition A was entered when Security received an alarm that the Unit 2 570' Elevation Turbine Building and Reactor Building interlock doors were open. Security confirmed both doors partially open and contacted Operations. Operations personnel were able to reset the door interlock system and fully close both doors. TS 3.6.4.1 Condition A was exited at 08:49 when both doors were verified closed. During this time, Reactor Building Differential Pressure (dp) remained at -0.65 inches water column, in compliance with TS.<br /><br /> The cause of this event has been determined to be a design flaw that allowed simultaneous opening of the doors. Once opened, the interlock pins, designed to prevent opening of one door with the other open, deployed preventing closure of the doors until the interlock mechanism was bypassed. <br /><br /> Corrective actions include closure of the doors, removal of the interlock from use, and future installation of a modification to eliminate the vulnerability. <br /><br /> The safety significance of this event was low. Reactor Building dp was maintained throughout the event. However, due to the inability to immediately close either door, this event is considered a Safety System Functional Failure. The event is being reported under 10 CFR 50.73 (a)(2)(v)(C), "any event or condition that could have prevented the fulfillment of the safety function of ...systems that are needed to control the release of radioactive material".
2372015005 | Dresden 2 | 09/23/2015 | 03/31/2016 | ML16095A21 | <strong>Unit 2 HPCI Motor Gear Unit Would Not Return to Full Flow During Testing</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2015, operators were performing surveillance testing of the Unit 2 High Pressure Coolant Injection (HPCI) system. After achieving full flow, the system flow rate was lowered to 75 percent per the test procedure. System flow could not be returned to 100 percent upon subsequent adjustments. The system test was stopped and the system declared inoperable at 21:00 CDT.<br /><br /> The initial cause of the failure was determined to be a limit switch failure. The system was successfully tested upon component replacement. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(v)(D) "Any event or condition that could have prevented the fulfillment of the safety function of ... systems that are needed to mitigate the consequences of an accident." The consequences of the failure are of very low safety significance as operator action could mitigate the failure. <br /><br /> The cause of the limit switch failure was determined to be high contact resistance due to deposit build-up. The initial corrective actions included replacement of the faulted switch and testing of remaining in stock switches.
2442015001 | Ginna | 06/30/2015 | 09/24/2015 | ML15271A16 | <strong>Human Performance Error During Data Collection Activity Results in a Condition Prohibited by Technical Specification 3.1.7 "Rod Position Indication"</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2015, during rod movement testing, it was discovered that the data recorder temporarily installed as a secondary method of monitoring the position of control rod L06 was not available due to an incorrect trigger setting. The cause of the incorrect trigger setting was a human performance error during manipulation of the data recorder on June 28, 2015. Prior to this event, the primary method of monitoring position indication for control rod L06, the Plant Process Computer System (PPCS), had also been declared inoperable to perform maintenance due to a hardware malfunction. The malfunction had been resolved prior to this event and PPCS indication was available. However, at the time of the data recorder unavailability PPCS indication for control rod L06 was still administratively considered to be inoperable. Therefore, Ginna was administratively not reviewing the rod control system for indications of rod movement for a rod with an inoperable position indicator (control rod L06) during the time the data recorder was unavailable. It was later determined this condition existed for approximately 36 hours. This was not in accordance with requirements stated in Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.7.A.3.2 Rod Position Indication. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2472015001 | Indian Point 2 | 08/11/2015 | 08/29/2017 | ML17248A46 | <strong>Technical Specification (TS) Prohibited Condition due to an Inoperable Containment Caused by a Service Water Pipe Leak with a Flaw Size That Results in Exceeding the Allowed Leakage Rate for Containment</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2015, during operator investigations inside the reactor containment building, a through wall leak was discovered on the 24 Fan Cooler Unit (FCU) motor cooler service water (SW) return line. The leak was in a 2 inch copper-nickel pipe near a brazed joint upstream of containment penetration SS. The leak was located within the ASME Section XI Code ISI Class 3 boundary and estimated to be approximately 2 gpm. Since the pipe flaw was through wall and was located within the ASME Section XI boundary, it exceeds the flaw allowable limits provided per IWC-3000. The weld leak was evaluated and determined to meet the structural requirements of ASME Code Case N-513-3. The condition was determined to have no impact on SW cooling safety function or adverse impact on piping structural integrity. The pipe is considered a closed loop system inside containment and required to meet containment integrity. An engineering evaluation was performed to determine the potential air leakage out of containment based on the observed SW leakage into containment. This evaluation concluded that the leaking defect could result in post-LOCA air leakage out of containment in excess of that allowed by Technical Specification 3.6.1 (Containment) which requires leakage rates to comply with 10 CFR 50, Appendix J. The direct cause was localized flow accelerated corrosion attack. The apparent cause was higher than required flow conditions which caused localized higher velocities and flow separation at the sharp interior edge of the pipe elbow. The pipe and affected elbow were replaced in accordance with the requirements of ASME Section XI Code during the spring refueling outage in 2016. Flow through the FCU motor coolers was also reduced to prevent the conditions from occurring that lead to flow accelerated corrosion. The event had no significant effect on public health and safety.
2472015002 | Indian Point 2 | 08/18/2015 | 10/19/2015 | ML15300A05 | <strong>Safety System Functional Failure due to Fuses for Residual Heat Removal Heat Exchanger Outlet Valves that Would not Remain Operable under Degraded Voltage Conditions</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2015, the operations shift manager entered Technical Specification (TS) 3.0.3 upon determination that the Residual Heat Removal (RHR) heat exchanger outlet valves (MOV-746 and MOV-747) would not remain operable during a degraded voltage (DV) condition. RHR heat exchanger outlet valves MOV-746 and MOV-747 are normally closed therefore their failure would result in both trains of RHR becoming inoperable. The RHR outlet valves are required to open during a Design Basis Accident for the RHR system to perform its safety function. As a result of NRC inspector questioning, an evaluation of the electrical coordination calculations associated with fuses for MOV-746 and MOV-747 determined the fuses would not support continued operability during a DV condition. The fuses were replaced with fuses that would remain operable under DV conditions and the RHR trains restored to operable status. Direct cause was the electrical coordination calculations for MOV-746 and MOV-747 did not support operability during a DV condition. The apparent cause was that the Industry Operating Experience (OE) (prior NRC violations and findings) was not properly acted upon during the Focused Self-Assessment on CDBI Preparations due to an incorrect assumption. Corrective actions included replacement of fuses, and communication to engineering personnel of the lessons learned from the event. Initiated CR-IP2-2015-03725 recording NRC 2015 CBDI Item 103 and CR-IP2-2015-03702 recording NRC 2015 CBDI Item 104 to addresses EOC findings and calculation updates which will be processed via Engineering Changes. The event had no significant effect on public health and safety.
2472015003 | Indian Point 2 | 12/05/2015 | 02/03/2016 | ML16041A01 | <strong>Manual Reactor Trip due to Indications of Multiple Dropped Control Rods Caused by Loss of Control Rod Power due to a Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2015, control room operators initiated a manual reactor trip (RT) after observing indications consistent with multiple dropped control rods (CR) following an alarm for the trip of Motor Control Center (MCC)-24/24A. No Control Rod indication was available due to MCC-24 being de-energized. All primary safety systems functioned properly except the primary rod control cabinet power supply (PS1) which was in a degraded condition prior to the event and failed to function as required. The plant was stabilized in hot standby. There was no radiation release. The Auxiliary FW system automatically started as designed. The direct cause of the event was loss of MCC-24 due to an internal fault at the line side leads at cubicle 2H where they connect to the bucket stab assemblies (load side fault). This caused the supply breaker feed to open per design and clear the fault. The de-energization of MCC-24 removed the functioning backup Control Rod (CR) power supply and the remaining degraded primary power supply failed to function as required. The apparent cause was an unanticipated loss of power to the CR system due to the degradation of the primary CR power supply (PS1) which failed to function when the operating power supply (PS2) was lost. MCC-24/24A was lost due to a design error that allowed the positioning of a mounting plate too close and obstructing the line side wiring resulting in contact. Vibration over time resulted in degraded wiring insulation which eventually shorted. Corrective actions included inspection and testing of the MCC-24 bus and control wiring. The degraded Rod Control power supply (PS1) was replaced. Maintenance procedures will be revised to provide more in-depth inspection criteria. The event had no effect on public health and safety.
2472015004 | Indian Point 2 | 12/20/2015 | 02/18/2016 | ML16057A17 | <strong>Safety System Functional Failure due to an Inoperable Containment Caused by a Flawed Elbow on the 21 Fan Cooler Unit Service Water Motor Cooling Return Pipe</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2015, operator investigations identified service water (SW) leakage in containment and on December 22, 2015 discovered a through wall leak on a socket welded elbow for the 21 Fan Cooler Unit (FCU) motor cooler SW 2 inch copper-nickel return line. The leak was located in a pipe fitting that is within the ASME Section XI Code ISI Class 3 boundary and estimated to be approximately 1 gpm. Since the pipe flaw was through wall and was located within the ASME Section XI boundary, it exceeded the flaw allowable limits provided per IWD-3000. Engineering determined that since the through wall flaw was located on a socket welded fitting, the ASME Code Case N-513-3 did not apply. The 21 FCU was declared inoperable and Technical Specification (TS) 3.6.6 (Containment Spray and Containment FCU System), entered for one FCU train inoperable and TS 3.6.1 Condition A entered for containment inoperable. The 21 FCU SW return line was isolated. The pipe is part of a closed loop system inside containment and is required to meet containment integrity. Since a containment leakage evaluation was not performed, the pipe flaw was conservatively assumed to result in post-accident containment out leakage in excess of the 10CFR50, Appendix J limits resulting in violation of the containment integrity requirements and therefore is a safety system functional failure. The direct cause was flow assisted erosion-corrosion. The apparent cause was high SW flow conditions that caused high localized velocities and flow separation at the sharp interior edge of the socket welded fitting. Corrective actions included replacement of the affected fitting. The faulted fitting was sent out to a vendor for metallurgical failure analysis. The procedure for FCU SW flow balanced will be revised to reduce the SW flow in FCU motor coolers. The event had no significant effect on public health and safety.
2492015001 | Dresden 3 | 09/05/2015 | 01/22/2016 | ML16028A19 | <strong>Main Steam Line Flow Switches Found Outside Tech Spec Allowed Value</strong><br /><i>Abstract:&nbsp;</i>During quarterly calibration and functional testing of Main Steam (SB) Line High Flow switches, two switches were found to not meet surveillance requirements of Technical Specification 3.3.6.1. <br /><br /> At 1100 CDT on .September 5, 2015, a switch was found to not meet Surveillance Requirement (SR) 3.3.6.1.1. TS 3.3.6.1 Condition A and D completion times were not met and TS 3.0.2 was entered. Maintenance personnel repaired the affected instrument. No loss of safety function occurred due to this failure. <br /><br /> These events are being reported under 10 CFR 50.73(a)(2)(i)(B) "Any operation or condition which was prohibited by the plant's Technical Specifications...". No loss of safety function occurred due to these events. <br /><br /> The degradation of the multiple switches has been determined to be cause by normal wear combined with temperature and humidity. Corrective actions include repairs to Reactor Building Chillers and operator training on TS 3.3.6.1 usage.
2502015001 | Turkey Point 3 | 11/18/2015 | 01/19/2016 | ML16053A09 | <strong>Diesel Generator Start Resulting from Switchyard Protective Relay Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 18, 2015 at approximately 23:33 hours with Unit 3 in Mode 5 during a refueling outage, the 3B Emergency Diesel Generator (EDG) automatically started and loaded on the 3B bus. The cause of the EDG start was a loss of offsite power to the 3A and 3B 4160V busses when the supply breakers to the Unit 3 Startup Transformer automatically opened due to an unexpected protective relay actuation in the Unit 3 switchyard. When the 3A and 3B busses were deenergized, the 3B EDG re-energized the 3B bus, but the 3A sequencer was out of service for preplanned work so the 3A bus was not immediately reenergized. The unit remained in Mode 5 with core decay heat removal provided by the 3B Residual Heat Removal loop. The cause of the event was the unexpected actuation of the protective relay during switchyard work. <br /><br /> The automatic EDG start is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
2512015001 | Turkey Point 4 | 11/30/2014 | 01/29/2015 | ML15050A24 | <strong>Automatic Auxiliary Feedwater System Actuation During a Planned Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2014, at approximately 1354 the Unit 4 reactor was manually tripped as a pre-planned evolution to facilitate the repair of an unidentified steam leak in the High Pressure (HP) Turbine. While Unit 4 was in Mode 3, at approximately 1358 hours, the Auxiliary Feedwater System initiated when the 4C Steam Generator (SG) level reached the low-low SG level setpoint setting. The AFW system was restored to standby alignment at approximately 1454 hours. The causal analysis determined that: 1) The appropriate operating margin to prevent AFW actuation was not established prior to the reactor trip for the planned shutdown, and 2) The just-in-time training did not prepare crews to reduce the probability of having an unnecessary AFW actuation on a planned reactor trip. Corrective actions include: 1) Change the applicable operating procedures to establish available margin to avoid unnecessary AFW actuation during a planned reactor trip, and 2) Develop simulator scenarios that more closely model the plant response during a planned shutdown and train Operators to reduce the probability of an AFW actuation during a planned reactor trip.
2512015002 | Turkey Point 4 | 05/12/2015 | 07/13/2015 | ML15211A23 | <strong>Reactor Trip Resulting from Generator Differential Lockout</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2015 at approximately 0430 hours with Unit 4 at approximately 80% rated thermal power, an automatic reactor trip occurred in response to a turbine trip. The turbine trip was caused by a generator differential lockout that opened the generator output breaker. During the reactor trip response, the Auxiliary Feedwater System automatically initiated as expected. The unit was subsequently stabilized in Mode 3. All systems responded correctly to the trip. The direct cause of the event was an open circuit caused by a loose connection at a main generator current transformer (CT). The root cause was that the vendor recommended torque value for a stud lugged connection was not used during the engineering change (EC) and work order planning process. The tightening requirement for this type of connection is considered to be skill of the craft; therefore, no torque specification was listed in the EC or work instructions. Corrective action includes: 1) The preventive maintenance procedure and electrical specification will be revised to include connection torque requirements per the vendor work instruction manual for the type of terminal used in the CTs and, 2) A preventive maintenance task will be implemented to periodically inspect and test the Unit 3 and 4 main generator CT connections.
2542015001 | Quad Cities 1, Quad Cities 2 | 01/06/2015 | 03/06/2015 | ML15100A00 | <strong>Unit 0 Fuel Oil Transfer Pump Feed Breaker Found Tripped</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2015, Electrical Maintenance was preparing for planned maintenance activities at a 480V Motor Control Center (MCC). One of the technicians identified that the breaker in cubicle A1 was in the tripped position. Breaker A1 is the Unit 2 power supply breaker to the Unit 0 Fuel Oil Transfer Pump (FOTP) for the Unit 0 Emergency Diesel Generator (EDG).<br /><br /> Troubleshooting identified the cause of the breaker trip was due to high resistance contacts on the HGA power transfer relay. This relay was replaced and tested satisfactory on January 8, 2015.<br /><br /> This breaker most likely tripped under load, which would have occurred during the Unit 0 EDG 24 hour endurance run when the EDG was loaded to Unit 2 on December 30, 2014. Since planned maintenance occurred on the Unit 0 EDG prior to the endurance run, the time of inoperability of the Unit 0 EDG started on December 29, 2014 and ended when the failed relay was replaced and tested satisfactory on January 8, 2015, for a total of 10 days. This exceeded the allowed outage time of Technical Specifications 3.8.1 for one EDG inoperable. Therefore, this Licensee Event Report is being submitted in accordance with 10 CFR 50.73 (a)(2)(i)(B) for a condition prohibited by Technical Specifications.
2542015002 | Quad Cities 1, Quad Cities 2 | 02/10/2015 | 04/06/2015 | ML15105A04 | <strong>HPCI Interlock Doors Opened Simultaneously Cause Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2015, at 1055 hours, a maintenance individual notified the control room that both doors in the secondary containment interlock between the Reactor Building (RB) Unit 1 High Pressure Coolant Injection (HPCI) room and the Unit 1 Turbine Building (TB) were opened simultaneously. The failure of this interlock caused a loss of secondary containment (inoperable) per Technical Specification (TS) 3.6.4.1, Condition A. The RB-side door was immediately reclosed, and the secondary containment boundary was reestablished. Operators verified the RB (secondary containment) differential pressure remained negative during this event.<br /><br /> Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the RB-side door and the RB differential pressure was maintained during the event. No RB low differential pressure alarms were received during this event. The RB is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units.<br /><br /> The cause of the interlock failure was due to a bent locking bolt with insufficient strength to withstand the standard practice of challenging that fire doors are locked closed after passing through them. The bent locking bolt caused its door plungers to not engage allowing its door to open while the opposite door in the interlock was being opened.<br /><br /> Corrective actions included repairing the bent locking bolt on the TB-side passive door and realigning the TB-side doors to ensure the plungers would be functional. The locking bolt will be replaced with a higher strength assembly.<br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542015003 | Quad Cities 1 | 03/02/2015 | 04/29/2015 | ML15128A53 | <strong>Main Steam Isolation Valve Local Leak Rates Exceed Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2015, at 2359 hours, with Unit 1 shutdown for refuel outage Q1 R23, the as-found local leak rate tests (LLRT) for the four (4) main steam lines (MSL) were performed following closure of the main steam isolation valves (MSIV). The initial as-found LLRT on the "D" MSL MSIVs exceeded the minimum pathway criteria (smaller leakage in a line) of the Technical Specifications (TS), and the combined total leakage of all MSLs also exceeded the minimum pathway criteria (smaller leakage in each line when combined for all MSIVs) of the TS.<br /><br /> The leaking valves were disassembled and inspected. Although some seat ring wear is a normal occurrence in these valves, the excessive leakage was associated with wear due to the high friction that develops between the plug and the seat as initial contact occurs on valve closure, followed by the sliding action as the plug centers itself in the seat, which is inherent with the "Y"-style globe valve.<br /><br /> The most likely cause for the higher than expected leakages has been determined to be a valve design that is susceptible to localized seat wear during valve closure. The plug tends to drag across the sharp edge of the seat ring, and over time, if the closure strokes allow the plug to drag along the same contact point then wear will occur on the sharp edge of the seat ring.<br /><br /> Corrective actions included flushing, disassembling, inspecting, repairing, and retesting the valves. Future corrective actions include installation of an improved spherical nose plug design to the MSIV plug and seat.<br /><br /> The safety significance of this event was minimal. The total primary containment leakage of 283.59 scfh was well within the allowed leakage limit of 823.79 scfh (0.6La). However, since the "D" MSL MSIV as-found leakage exceeded the TS limit, and the combined total leakage of all main steam lines exceeded the TS limit, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of a past operation or condition which was prohibited by the plant Technical Specifications.
2542015004 | Quad Cities 1 | 03/21/2015 | 05/20/2015 | ML15154A56 | <strong>Automatic Depressurization System Trip Logic Failure</strong><br /><i>Abstract:&nbsp;</i>On 03/21/15, at 0800, with Unit 1 shutdown for refuel outage Q1R23, the Unit 1 Off-Line Automatic Blowdown Logic Test was being performed when two Electromatic Relief Valves (ERVs) failed to actuate since the 'N trip logic for the automatic function of the Automatic Depressurization System (ADS) did not energize.<br /><br /> Maintenance burnished the 'A' trip logic relay contacts and the 'B' trip logic relay contacts. The as-found data on the 'B' trip logic of ADS was lost during this troubleshooting, and it is unknown if the 'B' trip logic of the automatic function would have functioned. Once the relay contacts were burnished, the continuity was checked and found acceptable.<br /><br /> The apparent cause for the loss of the 'A' trip logic system was due to relay contact oxidation buildup. The oxidation buildup was due to inadequate preventative maintenance instructions.<br /><br /> The immediate corrective action consisted of burnishing the relay contacts. Future corrective actions include updating the preventative maintenance procedure and replacing the two relays on the 'A' trip logic system that had the oxidation buildup.<br /><br /> This report is submitted in accordance with 10 CFR 50.73 (a)(2)(v)(D) which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident; and 10 CFR 50.73 (a)(2)(vii)(D) which requires the reporting of any event where a single cause or condition caused two independent channels to become inoperable in a single system designed to mitigate the consequences of an accident.
2542015005 | Quad Cities 1 | 04/02/2015 | 06/01/2015 | ML15161A31 | <strong>Manual Scram due to Steam Leak on Turbine Throttle Pressure Sensing Line</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2015, at 1810 hours, with Unit 1 in Mode 1 and operating at 100% power, an alarm was received in the control room indicating that two of three turbine throttle pressure transmitters on Unit 1 had failed low. Reactor power was reduced to 20% and the main turbine was secured. A steam leak was confirmed to have originated between the turbine throttle pressure transmitter sensing line isolation valve and the 30 inch main steam D-Ring header. Since the steam leak could not be isolated with Unit 1 at power, a manual scram was inserted on Unit 1 at 2133 hours, and the main steam isolation valves (MSIVs) were manually closed. A forced outage was initiated to investigate and perform repairs.<br /><br /> The reactor and turbine responded as designed. Operators performed required actions safely and in accordance with procedures and training. Operators needed to use relief valves to control reactor pressure since the turbine bypass valves were unavailable for normal pressure control after closing the MSIVs to isolate the steam leak at the D-ring. A drywell pressure rise occurred due to a relief valve tailpipe vacuum breaker which had inadvertently stuck open; the relief valve was then closed, a drywell cooler was started, and drywell pressure returned to normal.<br /><br /> The root cause of the failure of the sensing line was determined to be inadequate monitoring of the sensing line supports that allowed each of the clamps to degrade and loosen over time resulting in high cycle fatigue cracking and eventual fracture of the sensing line.<br /><br /> Corrective actions included replacing the 3/4 inch carbon steel section of the failed sensing line, including the isolation valve, and replacing the associated degraded supports. Future corrective actions include conducting focused inspections of small bore piping/tubing on both accessible and inaccessible systems.<br /><br /> The safety significance of this event was minimal. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(iv)(A) which requires the reporting of any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
2542015006 | Quad Cities 1, Quad Cities 2 | 04/28/2015 | 06/24/2015 | ML15188A03 | <strong>Interlock Doors Opened Simultaneously Cause Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2015, at 0935 hours, the control room was notified that the Unit 1/2 emergency diesel generator (EDG) room manual side door and the Unit 1 reactor building (RB) side door, as a part of the personnel interlock to the 1/2 EDG room, were opened simultaneously. The failure of this interlock caused a temporary loss of secondary containment (inoperable) per Technical Specification (TS) 3.6.4.1, Condition A. The 1/2 EDG manual interlock door was closed immediately, and the secondary containment boundary was immediately reestablished. Operators verified the RB (secondary containment) differential pressure remained negative during this event. <br /><br /> Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the 1/2 EDG room manual side door, and since the RB differential pressure was maintained during the event. The RB is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units. <br /><br /> The event involved the mechanical latch on the 1/2 EDG room door that had failed to fully engage into the strike, although it did engage far enough to make up the electrical logic. The apparent cause of the interlock failure was determined to be the 1/2 EDG room door failed to remain closed due to inadequate design of the interlocks. <br /><br /> Corrective actions included troubleshooting and administratively controlling the interlock door. The preventive maintenance frequency of the interlock door will be increased, the door will be replaced, and a modification will be performed to address single point vulnerabilities. <br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542015007 | Quad Cities 1, Quad Cities 2 | 05/27/2015 | 07/24/2015 | ML15222A24 | <strong>Loss of Main Control Room Envelope Boundary due to Damper Inspection</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2015, at 0952 hours, the Main Control Room (MCR) received an unexpected "Control Room HVAC Train 'A' Trouble" alarm. A fire damper inspection was being performed that opened a Control Room HVAC ductwork access hatch that caused the alarm. The hatch was opened and immediately shut, re-establishing the boundary of the Control Room Envelope (CRE). The Control Room Emergency Ventilation (CREV) system was declared inoperable due to opening the ventilation duct hatch without prior administrative controls in place. As a result, Technical Specification 3.7.4, Condition C, was entered and subsequently exited within approximately one minute.<br /><br /> The cause of the inadvertent CRE breach was the design drawing contained in the work package that was reviewed during the Plant Barrier Impairment (PBI) screening did not adequately define the boundaries of the CRE. <br /><br /> Corrective actions included reviewing all open PBI packages. Associated Control Room boundary drawings and procedures will be revised to correctly annotate the proper CRE boundary to include the MCR ventilation ductwork access hatch.<br /><br /> The safety significance of this event was minimal. Given the impact on the MCR envelope, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2542015008 | Quad Cities 1, Quad Cities 2 | 06/19/2015 | 08/17/2015 | ML15239A75 | <strong>Interlock Doors Opened Simultaneously Cause Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2015, at 0153 hours, the control room was notified that the Unit 1/2 emergency diesel generator (EDG) room manual side door and the Unit 1 reactor building (RB) side door, as a part of the personnel interlock to the 1/2 EDG room, were opened simultaneously. The failure of this interlock caused a temporary loss of secondary containment (inoperable) per Technical Specification (TS) 3.6.4.1, Condition A. The 1/2 EDG manual interlock door was closed immediately, and the secondary containment boundary was immediately reestablished. Operators verified the RB (secondary containment) differential pressure remained negative during this event. <br /><br /> Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the 1/2 EDG room manual side door, and since the RB differential pressure was maintained during the event. The RB is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units.<br /><br /> The event involved the mechanical latch on the 1/2 EDG room door that had failed to fully engage into the strike, although it did engage far enough to make up the electrical logic. The apparent cause of the interlock failure was determined to be the 1/2 EDG room door failed to remain closed due to inadequate design of the interlocks.<br /><br /> Corrective actions included troubleshooting and administratively controlling the interlock door. The preventive maintenance frequency of the interlock door will be increased, the door will be replaced, and a modification will be performed to address single point vulnerabilities. <br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542015009 | Quad Cities 1, Quad Cities 2 | 07/27/2015 | 09/24/2015 | ML15289A23 | <strong>Loss of Control Room Emergency Ventilation System due to Air Filtration Unit Damper Failure</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2015, at 1730 hours, while performing toxic gas analyzer surveillance testing on the 'B' Train of the Control Room Emergency Ventilation (CREV) System, technicians noticed that the 'B' Air Filtration Unit (AFU) Booster Fan discharge damper became stuck in a partially open position following the 'B' AFU Booster Fan trip on a high ammonia input signal. Due to the uncertainty of being able to achieve rated airflow for the CREV System caused by recirculation that would result from running the 'A' AFU Booster Fan with the 'B' Booster Fan discharge damper partially stuck open, the CREV System was declared inoperable and surveillance testing was secured. As a result, Technical Specification 3.7.4, Condition A, was entered. <br /><br /> The cause of the damper failure was due to inadequate clearance between the damper seat sealing area and the damper blade to shaft fasteners which resulted in misalignment which caused the damper shaft to bend and the damper to become stuck. <br /><br /> Corrective actions included securing the stuck damper in the closed position and evaluating all CREV System dampers. A preventative maintenance task will be developed to stroke and inspect the dampers to identify binding; modifications will be made if necessary to other CREV System dampers to prevent binding. <br /><br /> The safety significance of this event was minimal. Given the impact on the CREV System, which is common to both Units, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2542015010 | Quad Cities 1, Quad Cities 2 | 12/07/2015 | 02/05/2016 | ML16053A06 | <strong>Loss of Control Room Emergency Ventilation System due to Differential Pressure Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2015, at 0825 hours, Operations attempted to start the safety related Control Room Emergency Ventilation (CREV) system train "B" in support of planned maintenance on the non-safety related train "A". The CREV train "B" did not start. Once the CREV train "B" system failed to start, the non-safety related train "A" was restarted. Proper operation of the CREV system and CREV air conditioning (A/C) systems could not be ensured, so both CREV and CREV AC system were declared inoperable. As a result, Technical Specification (TS) 3.7.4, Condition A, and TS 3.7.5, Condition A were entered. <br /><br /> The cause of the CREV train "B" system failure to start was the differential pressure switch, which is installed in a vibration susceptible location on the ductwork. This differential pressure switch makes up the interlock between the CREV train "B" system and the non-safety related Control Room HVAC train "A". The differential pressure switch's normally open contacts had temporarily welded together not allowing the starting signal to be received by the CREV train "B" system. <br /><br /> Corrective actions included replacing the differential pressure switch. A future corrective action will relocate the differential pressure switch off of the ductwork to minimize the vibration effects. <br /><br /> The safety significance of this event was minimal. Given the impact on the CREV system, which is common to both units, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2552015001 | Palisades | 09/16/2015 | 11/10/2015 | ML15314A66 | <strong>Automatic Reactor Trip Results from a Turbine Trip Initiated from the Digital Electro-Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2015, at approximately 0117 hours, an anomaly within the digital electro-hydraulic (DEH) turbine control system initiated a turbine trip. As designed, the turbine trip actuated the reactor protection system to automatically trip the reactor due to a loss of load and the auxiliary feedwater system started automatically to recover steam generator levels. <br /><br /> The direct cause of the event is the turbine tripped due to actuation of the "DEH controller loss of power" turbine trip logic. Troubleshooting and analysis determined there was a failure of a power supply module on a circuit board in the DEH turbine control system. Subsequent to the power failure on the circuit board, a second failure, either a loss of power to the overspeed protection control (OPC) distributed processing units (DPUs) or a loss of communications between the primary and backup OPC DPUs, occurred resulting in an actuation of the "DEH controller loss of power" turbine trip logic. <br /><br /> The root cause of the event is that the design of the DEH system contains unnecessary trip logic associated with turbine overspeed monitoring. Corrective actions include a modification to remove the DEH system OPC loss of power and loss of communications trip logic.
2592015001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 02/21/2015 | 04/22/2015 | ML15112A41 | <strong>"D" Emergency Diesel Generator Inoperable due to Mispositioned Switch</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2015, at approximately 2300 Central Standard Time, Browns Ferry Nuclear Plant, Units 1 and 2, declared "D" Emergency Diesel Generator (DG) system inoperable due to the control switch being found by Operations personnel in the "pulled out" stop position, which made the "D" DG incapable of automatically starting. It was determined that the "D" DG was inoperable since the last operation of the control switch, approximately eight days earlier. Although this condition caused the "D" DG to be inoperable longer than allowed by the Technical Specifications, the three other Unit 1 and 2 DGs and all four Unit 3 DGs remained available to fulfill the DG safety functions.<br /><br /> Contrary to the original design of the DG control switches, this control switch was replaced in 2004 with one that did not contain a spring return to normal. The cause of the error was an incorrectly filled out Procurement Data Sheet (PDS). Contributing causes included inadequate procedure revision to address the difference in operation, ineffective use of human performance tools and operator fundamentals, and the switch difference had been identified several times previously but not corrected. Corrective actions included correcting the PDS, briefing Operations procedure writers on the details of this event and lessons learned, coaching Operations personnel on the proper use of operator fundamentals and human performance tools when manipulating plant equipment, and replacing the "D" DG control switch with the correct switch.
2592015002 | Browns Ferry 1 | 07/22/2015 | 09/21/2015 | ML15264B12 | <strong>High Pressure Coolant Injection System Inoperable due to Slow Containment Isolation Valve Closing Time</strong><br /><i>Abstract:&nbsp;</i>On July 22, 2015, during the performance of a quarterly surveillance, the Unit 1 High Pressure Coolant Injection (HPCI) inboard steam isolation valve closing times were in the high alert range. Due to the inability to analyze the stroke time deviation within the required Technical Specification (TS) limit of four hours, the valve was subsequently declared inoperable in accordance with TS Limiting Condition for Operation (LCO) 3.6.1.3, Primary Containment Isolation Valves, and the HPCI system declared inoperable. As a result of the steam line isolation, the Unit 1 HPCI system was unable to perform its safety function. However, in an emergency, other systems were available to provide the required safety functions. On July 25, 2015, the inboard steam isolation valve and the Unit 1 HPCI system were declared operable. <br /><br /> The apparent cause of this event was the closing stroke time of the HPCI inboard steam isolation valve increased due to the valve coasting further open after motor cutoff resulting in a greater total distance of travel during valve closure, which is likely due to decrease in stem factor in packing loads. Corrective actions include performing diagnostic tests and limit switch timing determinations for the valves on Units 1, 2, and 3, including online testing the Motor Operated Valves on Units 2 and 3 to determine if they are experiencing a similar condition, and if the packing friction for the HPCI inboard steam isolation valve has changed.
2592015003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 07/14/2015 | 09/14/2015 | ML15257A13 | <strong>Loss of Cooling to the Unit 1 and Unit 2 Shutdown Board Rooms due to Fouled Chiller Coils</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2015, at 1715 Central Daylight Time (CDT), Operations personnel observed Control Bay (CB) Chiller (CHLR) A outlet water temperature to be higher than specified limits. CB CHLR A was declared inoperable. Because CB CHLR B was concurrently inoperable for maintenance, no chilled water within temperature limits was available to electric board rooms housing Unit 1 and 2 4kV Shutdown Boards, therefore, these boards were declared inoperable. This resulted in a Safety System Functional Failure for safety systems on all three Units. The event also resulted in the loss of two trains of Standby Gas Treatment, and the initiation of a Unit 1, 2, and 3 shutdown in accordance with Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.0.3. On July 14, 2015, at 2352 CDT, CB CHLR A was declared operable after cleaning and inspection, and BFN, Units 1, 2, and 3 exited all applicable TS LCOs. <br /><br /> The cause of this event was the failure of plant processes to address increased monitoring following debris/dust-producing events, which allowed fouling of the CB CHLR A condenser coils with dirt and insects. Corrective actions include re-evaluating the CB CHLR significance for Probabilistic Risk Assessment calculations, revising procedures for plant equipment susceptible to natural phenomena to enhance inspection during operator rounds, adding walkdown guidance for inspecting and evaluating the condition of the redundant equipment when walking down equipment to be worked, and creating a conditional walkdown requirement on walkdown sheets to check for insect infestation.
2592015004 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 09/29/2015 | 11/30/2015 | ML15334A32 | <strong>Containment Atmospheric Dilution B Train Supply System Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2015, during excavation for a potable water leak approximately 46 feet downstream of the Containment Atmospheric Dilution (CAD) B train, a hole was discovered in the 2-inch stainless steel underground CAD supply piping. CAD B train was declared inoperable and Technical Specification Limiting Condition for Operation 3.6.3.1 Condition A was entered. A past operability evaluation determined that the CAD B train would not have been able to provide its specified safety function in Modes 1 and 2 with the identified condition. On October 10, 2015, the CAD B train was declared Operable following repairs. A review of the past three years of operating history determined that both CAD A and B trains were concurrently inoperable/unavailable for a period of nine days. Therefore, this event is also considered a Safety System Functional Failure. Based on a probabilistic risk assessment, the safety significance of this event was low for all three operating units. <br /><br /> The cause for the hole in the CAD B train supply piping is unknown and the time of occurrence was indeterminate. This is considered to be a legacy issue. Corrective actions include developing and performing a piping integrity test to identify any other potential holes in the supply piping for the CAD A and B trains.
2592015005 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 10/29/2015 | 12/28/2015 | ML15362A56 | <strong>Inboard Main Steam Isolation Valve Actuators Inoperable for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2015 at 1149 Central Daylight Time, it was discovered upon receipt of a vendor report that the Main Steam Isolation Valve (MSIV) accumulators on all BFN inboard MSIVs are of insufficient size to provide the MSIV actuators adequate air volume, at the required pressure, to close the MSIV during a Loss of Coolant Accident (LOCA). Therefore, availability of Drywell Control Air (DWCA) nitrogen from the Containment Inerting system or from the Containment Atmospheric Dilution system was determined to be necessary for operability of inboard MSIVs. From December 1, 2012, to the time of discovery, there were multiple occasions where BFN Unit 1, 2, or 3 DWCA systems were aligned to receive nitrogen from the Plant Control Air system, resulting in the inoperability of multiple MSIVs for longer than allowed by BFN Technical Specification Limiting Conditions for Operation 3.6.1.3, Condition A. <br /><br /> The causes of this event were the failure of the original design of the MSIV actuators and accumulators to account for elevated drywell pressure during the time that the MSIVs are required to stroke for a Design Basis LOCA, and the failure to incorporate internal and external operating experience into the BFN Air Operated Valve (AOV) program.<br /><br /> Corrective actions are to issue and implement design changes to resolve negative margin issue with Units 1, 2, and 3 inboard MSIVs, to review calculations for accumulators associated with the Automatic Depressurization System relief valves to ensure they address LOCA conditions, and to ensure design basis calculations are developed for all Category 2 AOVs at BFN in addition to the Category 1 calculation reviews already in progress.
2602015001 | Browns Ferry 2 | 06/17/2015 | 08/17/2015 | ML15229A27 | <strong>Failure of the 2A RHR Pump to Manually Start from the Control Room due to a Loose Fastener</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2015, at approximately 1015 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) Operations personnel attempted to place BFN, Unit 2, Residual Heat Removal (RHR) Loop 1 into Suppression Pool Cooling (SPC). Upon actuating Hand Switch 2-HS-74-5A from the Control Room, Operations personnel observed that 2A RHR pump failed to start, and declared RHR Loop 1 inoperable. On June 18, 2015, at 1710 CDT, the pump was started and stopped after completion of troubleshooting, and the RHR Loop 1 was declared operable. <br /><br /> Troubleshooting discovered a loose terminal wire which intermittently prevented 2A RHR from being manually started from the Control Room. An investigation determined the cause to be human performance errors. RHR Loop 1 was inoperable from March 20, 2015, to June 18, 2015, longer than allowed by BFN, Unit 2, Technical Specifications. This loose terminal wire made the pump vulnerable to failure during a seismic event and, therefore, not in compliance with the design basis for the RHR system. This event did not prevent the 2A RHR Pump from manually starting, from the pump breaker, for SPC in the event of an emergency. Both the SPC manual start and the automatic start response to an Emergency Core Cooling System initiation signal were unaffected by this condition. <br /><br /> Corrective Actions for this event were to discipline the individuals responsible, to tighten the loose fastener, and to revise maintenance instructions to reduce the probability of recurrence.
2602015002 | Browns Ferry 2 | 09/16/2015 | 03/17/2016 | ML16081A08 | <strong>High Pressure Coolant Injection System Inoperable due to Manual Isolation of Steam Leak</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2015, at approximately 0156 Central Daylight Time (CDT), a large steam leak occurred in Unit 2 High Pressure Coolant Injection (HPCI) Room. Operators manually closed 2-FCV-73-3 (HPCI Outboard Isolation Valve) to isolate steam and declared the single train HPCI system inoperable. During the time period that the HPCI system was inoperable, other systems were available to provide the required safety functions. Following repairs, HPCI was declared operable at approximately 1045 CDT on September 19, 2015. Subsequent evaluation determined that HPCI would have met its 8-hour mission time with the identified condition. <br /><br /> The cause of the steam leak was degradation of the valve packing on 2-FCV-73-16 (HPCI Turbine Steam Supply Valve) due to installation of improper packing material in April 2013. The steam leak initiators were mechanical extrusion of packing material and high temperature acid corrosion of the valve stem. Following steam leak initiation, catastrophic packing failure occurred due to steam induced high temperature degradation of the PTFE (Teflon) graphite braided packing. The two root causes were conflicting guidance in the Valve Packing Program procedure and the lack of necessary procedural guidance for the station to appropriately address invisible, superheated steam packing leaks. Corrective actions include revising the applicable procedures.
2612015001 | Robinson 2 | 01/28/2015 | 03/30/2015 | ML15089A27 | <strong>Reactor Protection and DC Electrical System Inoperability due to Inadvertent Parallel Connection of Safety Trains</strong><br /><i>Abstract:&nbsp;</i>At 1957 hours EST on 01/28/2015 with H. B. Robinson Steam Electric Plant, Unit No. 2 in Mode 1 at 100 percent power, the plant entered Improved Technical Specifications (ITS) Limiting Condition for Operation (LCO) 3.0.3 due to inoperability of both trains of the Reactor Protection System (RPS). It was discovered that modification work performed during the Fall 2013 refueling outage inadvertently connected in parallel both safety trains of the RPS and both trains of the DC Electrical Distribution System (DC-EDS). This parallel connection rendered both of these systems inoperable because the required independence and redundancy of systems was eliminated.<br /><br /> This condition was present for a time greater than allowed by technical specifications (TS) and is reportable as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B). This condition also rendered inoperable one train of multiple systems designed to mitigate the consequences of an accident and is reportable under 10 CFR 50.73(a)(2)(vii).<br /><br /> Immediate actions taken to restore compliance with regulations included completion of an emergency Work Order that restored the independence of safety trains of both systems and permitted exit of ITS LCO 3.0.3 at 2048 on 01/28/2015. The condition was entered into the site corrective action program and a root cause investigation is in progress.
2612015002 | Robinson 2 | 03/18/2015 | 11/12/2015 | ML15316A69 | <strong>Pressurizer Power Operated Relief Valve (PORV) Limit Switches' Qualified Life Exceeded due to Miscalculation</strong><br /><i>Abstract:&nbsp;</i>At 1703 hours EST on 03/18/2015 with H. B. Robinson Steam Electric Plant, Unit No. 2 in Mode 1 at 100 percent power, it was determined that the limit switches that provide indication in the control room as to the position of the pressurizer power operated relief valves (PORVs) may be at the end of their service life. Further investigation revealed that the qualified life requirements of 10 CFR 50.49 and Regulatory Guide 1.97, Criteria for Accident Monitoring Instrumentation for Nuclear Power Plants, for the limit switches was incorrect in station environmental qualification documentation. The qualified life of the limit switches expired on 2/23/2007. <br /><br /> The normal operation of the PORV limit switches in non-accident conditions is not limited, and they are considered operable in all modes of operation except during a design basis accident. However, the limit switches are considered inoperable for the purposes of meeting Technical Specification (TS) 3.3.3, Post Accident Monitoring Instrumentation. Therefore, this circumstance is reportable as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B). <br /><br /> Standing Instruction 15-005, effective on March 20, 2015, outlines the alternate method for continuous and post-accident monitoring of pressurizer PORV position until the limit switches are returned to service. Work orders have been generated to replace the limit switches during the upcoming refueling outage, currently scheduled to begin on May 12, 2015.
2612015003 | Robinson 2 | 01/19/2015 | 06/09/2015 | ML15161A24 | <strong>Failed Surveillance on Station Battery Charger A-1</strong><br /><i>Abstract:&nbsp;</i>At 0920 hours EST on 01/19/2015 with H. B. Robinson Steam Electric Plant, Unit No. 2 in Mode 1 at 100 percent power, the plant entered Technical Specifications (TS) Surveillance Requirement (SR) 3.0.3 due to the determination that a previously conducted test (06/18/2014) of Station Battery Charger A-1 was found to have failed due to an out of tolerance (OOT) with the measurement and test equipment (M&TE). An immediate determination of operability was conducted and it was determined that the Station Battery Charger A-1 was operable.<br /><br /> On 02/17/2015, a review of reportability for the Station Battery Charger A-1 M&TE issue was approved and concluded that the condition was not reportable since Station Battery Charger A-1 was believed operable from the time of the test conducted on 06/18/2014 even with the M&TE OOT. <br /><br /> On 02/24/2015, an investigation concluded that the entry into SR 3.0.3 was not appropriate, but no review of the change in reportability was conducted. <br /><br /> On 04/14/2015, it was determined that the condition was reportable. This condition was present for a time greater than allowed by TS and is reportable as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B). Compliance with TS 3.8.4 Condition A was restored on 01/19/2015 when Station Battery Charger A-1 was removed from service and Station Battery Charger A was placed in service.
2612015004 | Robinson 2 | 05/18/2015 | 08/27/2015 | ML15238B61 | <strong>Refueling Water Storage Tank (RWST) Discharge Valve Failed to Close on Demand</strong><br /><i>Abstract:&nbsp;</i>At 2311 hours EDT on 05/18/2015 with H. B. Robinson Steam Electric Plant, Unit No. 2 in Mode 6 at zero percent power, the Refueling Water Storage Tank discharge valve (SI-864A) failed to stroke closed on demand from the Reactor Turbine Gauge Board (RTGB) during surveillance testing of Emergency Core Cooling System (ECCS) boundary valves. Troubleshooting revealed the thermal overload relay within the breaker that supplies power to SI-864A was tripped with the breaker closed. In this condition, SI-864A would not have stroked closed on demand from the RTGB as designed, rendering the 'A' ECCS train inoperable. The approximate time and cause of the tripped relay is unknown at present; an investigation is ongoing. <br /><br /> Technical Specification (TS) 3.5.2, ECCS - Operating, requires two ECCS trains operable in Modes 1, 2, and 3, allowing 72 hours to return the inoperable ECCS train to service. The latest satisfactory stroke of SI-864A was on 3/26/14. Since the trip time of the overload relay is unknown, it must be assumed that the valve was inoperable for a period greater than that allowed by TS. Therefore, this circumstance is reportable as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The investigation into the cause of the tripped overload relay is ongoing, and should the results of the investigation yield a definite cause, a follow-up report will be submitted. The thermal overload relay and associated push-button on MCC-5(10J) were replaced during RO29. The health and safety of the public was not in jeopardy as a result of this condition.
2632015001 | Monticello | 04/23/2015 | 06/16/2015 | ML15167A44 | <strong>Operations with a Potential to Drain the Reactor Vessel (OPDRV) Without Secondary Containment Operable</strong><br /><i>Abstract:&nbsp;</i>On April 23 and 25, 2015, during planned Reactor Recirculation System modifications and maintenance, the provisions of NRC Enforcement Guidance Memorandum (EGM) 11-003 (Revision 2) were invoked for Operations With a Potential to Drain the Reactor Vessel (OPDRV) in noncompliance with Technical Specification (TS) 3.6.4.1, "Secondary Containment." These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the TS that is under enforcement discretion as specified in EGM 11-003.<br /><br /> The safety significance of these noncompliances is minimal as EGM 11-003 specifies interim actions that provide an adequate level of safety. Implementation of EGM 11-003 for these actions was a planned activity and as such, no cause determination was performed for the events. Following development of a Technical Specification Task Force traveler a license amendment request will be submitted to resolve this issue as required by EGM 11-003.
2632015002 | Monticello | 05/02/2015 | 08/20/2015 | ML15232A69 | <strong>Loss of Shutdown Cooling due to Improperly Landed Jumper Wire</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2015, the Monticello Nuclear Generating Plant (MNGP) was in Mode 5 for a refueling outage. During performance of surveillances of the non-credited 4kV essential Bus, MNGP experienced a loss of the 4kV Bus and essential Load Center due to an improperly landed jumper wire. Loss of the Load Center deenergized the valve position indication on the Residual Heat Removal (RHR) shutdown cooling inboard isolation valve, causing a subsequent trip of the RHR pump operating in shutdown cooling on a pump suction interlock and a loss of normal shutdown cooling. Control Room operators entered the appropriate abnormal procedures and verified alternate decay heat removal was in service until shutdown cooling could be restored.<br /><br /> Immediate corrective actions included suspension of all work pending approval of the shift manager to ensure outage activities did not further degrade plant conditions and electrical work was limited to protect shutdown cooling. The essential Load Centers were cross tied to restore normal shutdown cooling. Corrective actions include revising procedures to reinforce human performance tools, adequately assess risk involved with electrical work, and ensuring effective barriers are in place to harden residual heat removal function during shutdown conditions.
2632015003 | Monticello | 05/14/2015 | 09/11/2015 | ML15254A51 | <strong>Use of the Reactor Water Cleanup System to Lower Level Without Declaring an Operation with a Potential to Drain the Reactor Vessel (OPDRV) with Secondary Containment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2015, and on April 13 and April 14, 2015 (identified during an extent of condition review), the Reactor Water Cleanup (RWCU) System was used to perform reactor cavity and dryer-separator storage pool inventory reductions. Use of RWCU System constituted an Operation with a Potential to Drain the Reactor Vessel (OPDRV). However, the plant OPDRV procedural guidance did not identify this as an OPDRV. These occurrences are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the Technical Specifications. The cause was determined to be that the plant OPDRV procedure failed to provide adequate guidance to determine OPDRV activities which resulted in actions taken that were not in accordance with NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 2. The plant OPDRV procedure has been revised to reflect the guidance of the EGM.
2632015004 | Monticello | 06/24/2015 | 08/22/2017 | ML17234A64 | <strong>Past Inoperability of Turbine Stop Valve Scram Function Exceeded Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2015 during performance of turbine stop valve scram testing, the relay associated with the scram logic failed to de-energize as expected. Based on this failure to de-energize, stop valve 4 (SV-4) limit switch would not have contributed an input to the scram logic as designed. <br /><br /> Equipment causal evaluation determined setup instructions in work plans and test surveillance provided to electricians were not sufficient to ensure repeatability of the paired stop valve limit switches during replacement, surveillance testing, or performance of troubleshooting. Two contributing causes were identified. (1) Original construction installation details were not precise enough to ensure correct horizontal position alignment and installation of limit switch to actuating rod and (2) repair lessons learned were not incorporated into maintenance repair notes and work plans to document repairs and setup information. Corrective actions include revision of the turbine stop valve closure calibration checks procedure to include stop valve limit switch set up guidance to achieve proper paired switch operation. Additionally, turbine stop valve limit switches SV-1, SV-3, SV-4 were modified with a larger diameter upper switch contact arm roller to increase the engagement of the contact roller and actuating piston rod collar, as evident from SV-2 limit switch maintenance history.
2632015005 | Monticello | 08/03/2015 | 10/02/2015 | ML15275A34 | <strong>Use of the Reactor Water Cleanup System to Lower Level Without Declaring an OPDRV with Secondary Containment Inoperable - Extent of Condition Review</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2015, an extent of condition review for LER 2015-003, "Use of the Reactor Water Cleanup [RWCU] System to Lower Level without Declaring an Operation with a Potential to Drain the Reactor Vessel (OPDRV) with Secondary Containment Inoperable," identified two prior occurrences where this had occurred. On May 26, 2013, during the 2013 Refueling Outage, the RWCU System was used to lower reactor cavity level with the Secondary Containment (SCT) inoperable. On February 4, 2014, during the 2014 recirculation pump seal forced outage, reactor water level was lowered in preparation for startup using the RWCU System while the SCT and the B Standby Gas Treatment subsystem were inoperable. Each occurrence constitutes an operation or condition prohibited by the Technical Specifications, during OPDRV, which are reportable in accordance with 10 CFR 50. 73(a)(2)(i)(B). <br /><br /> The cause was determined to be that the plant procedure controlling OPDRVs failed to provide adequate guidance to determine an OPDRV activity which resulted in actions taken that were not in accordance with NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 2. The plant OPDRV procedure has been revised to reflect the guidance of the EGM.
2632015006 | Monticello | 11/23/2015 | 01/21/2016 | ML16022A10 | <strong>Reactor Scram due to Group 1 Isolation from Foreign Material in the Main Steam Flow Instrument Line</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2015, a trip of the # 11 Reactor Recirculation Pump occurred, followed by a Group 1 isolation which resulted in a reactor scram. A post scram troubleshooting investigation determined a large spike in differential pressure occurred in the 'C' main steam flow instrumentation line at the time of the Group 1 initiation event. <br /><br /> The root cause of this event was determined to be legacy foreign material present in the 'C' main steam flow instrumentation line. This foreign material obstructed the instrumentation line and resulted in the momentary sensed high steam flow. The sensed high steam flow was not due to an actual high steam flow condition in the 'C' main steam line. <br /><br /> Since the presence of foreign material in the instrument line is a legacy issue, the corrective action for the root cause was to remove the foreign material. The corrective action for the trip of the reactor recirculation pump, will be to revise the fleet procedure to require verification of torque on accessible electrical connections for critical components which are bench tested and also to ensure that accessible soldered and crimped electrical terminations are inspected for signs of degradation during bench testing.
2632015007 | Monticello | 11/24/2015 | 01/21/2016 | ML16022A22 | <strong>Loss of Residual Heat Removal Capability</strong><br /><i>Abstract:&nbsp;</i>On November 24, 2015 at 0534 hours, the Monticello Nuclear Generating Plant was at 0% power in Mode 3 (Hot Shutdown) for a forced outage. While initially placing Shutdown Cooling (SDC) in service, the 12 Residual Heat Removal (RHR) pump tripped approximately 8-10 seconds after start due to the closure of the RHR SDC suction isolation valves. When placing SDC in service, flow rapidly increased after opening the RHR Division 2 Low Pressure Coolant Injection (LPCI) outboard injection valve causing a localized pressure transient in the reactor recirculation pump suction piping that resulted in an isolation of the SDC suction line. Reactor pressure vessel (RPV) pressure remained stable at approximately 30 psig. <br /><br /> Prior to attempting to place 'B' SDC in service, the Condensate system and the 'F' Safety Relieve Valve were in service providing decay heat removal. Immediate actions were taken to restore 'B' RHR SDC to operable status, thus an alternative method of decay heat removal was already established by the Condensate system and 'F' Safety Relief Valve.
2652015001 | Quad Cities 2, Quad Cities 1 | 03/05/2015 | 04/22/2015 | ML15121A81 | <strong>Unit 1 HPCI Watertight Door Found Open Results in Unit 2 HPCI Inoperability</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2015, at approximately 1640, the watertight door for the Unit 1 High Pressure Coolant Injection (HPCI) room was found open with no person in attendance. In this condition, the door is not able to perform the flood protection function. With no person in attendance the door would not be shut to prevent internal flood water from entering the Unit 1 HPCI room. This condition would result in the inoperability of equipment in the room it is designed to protect from flooding.<br /><br /> The construction of the adjacent Unit 1 and Unit 2 HPCI rooms provides no flood barrier between the two rooms. Therefore, a condition that results in flood protection being nonfunctional to one HPCI room also has an effect on the opposite Unit HPCI. The Unit 1 HPCI watertight door being found open, with no one in attendance, results in the unplanned inoperability of the Unit 2 HPCI, since the Unit 2 HPCI is required to be operable by Technical Specifications in Mode 1. The Unit 1 HPCI was not required to be operable since Unit 1 was in Mode 5. Therefore, this Licensee Event Report is being submitted in accordance with 10 CFR 50.73 (a)(2)(v)(D) for an event or condition that could have prevented fulfillment of a safety function.
2662015001 | Point Beach 1, Point Beach 2 | 11/19/2014 | 01/19/2015 | ML15019A02 | <strong>Inadequately Sealed Pipe Penetrations Result in Unanalyzed Condition for Internal Flooding</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2014, inadequately sealed piping penetrations were discovered in the Residual Heat Removal (RHR) [BP] piping and valve gallery walls that could have allowed a postulated flooding event to potentially impact both RHR pumps. The same configuration was identified on both Units. Following analysis of the postulated leakage sources and flow paths, it was discovered that there was a time when an unacceptable volume of flood water could have entered the pipe and valve gallery areas challenging operation of the RHR pumps. It was determined that this condition no longer existed as of December 16, 2014, when changes had been made to Operations flood mitigation strategies, and upon installation of seals in upstream pipeway trenches to eliminate certain leakage paths into the RHR pipe and valve gallery areas. Therefore, this item is being reported as a past unanalyzed condition.
2662015002 | Point Beach 1 | 12/02/2014 | 01/30/2015 | ML15030A46 | <strong>Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2014, operators commenced a rapid power reduction of Unit 1 due to noted degradation of Unit 1B Condensate Pump. At 2050 on December 2, 2014, with Unit 1 in Mode 1 at 62% power, operators initiated a manual reactor trip of Unit 1 following securing of the Unit 1B Condensate Pump due to imminent failure. The Auxiliary Feedwater Pumps started as expected on low steam generator level experienced due to the reduced steam demand from the turbine trip in response to the reactor trip. All other plant systems functioned as required.<br /><br /> After the reactor trip, feedwater pump suction pressure remained low. The decision was made to secure both Main Steam Generator Feedwater Pumps. The Main Steam Generator Feedwater Pump A was manually secured. Prior to securing the Main Steam Generator Feedwater Pump B, it automatically tripped. All control rods fully inserted in the core due to the manual trip. There was no Emergency Core Cooling System actuation. Offsite power was maintained throughout the event. The Main Steam Generator Feedwater Pumps were available to be restarted due to the recovered feedwater suction pressure from the running Condensate Pump A.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) for both the manual RPS actuation and also for the automatic initiation of Auxiliary Feedwater.
2662015003 | Point Beach 1, Point Beach 2 | 03/09/2015 | 09/23/2015 | ML15266A45 | <strong>D-107 Battery Charger Failure to Limit Current Results in Operation or Condition Prohibited by Technical Specifications - Revision</strong><br /><i>Abstract:&nbsp;</i>At approximately 1730 on March 9, 2015 with both units at full power, it was discovered that the current limit feature of Battery Charger D-107 was not functioning as expected. Subsequent troubleshooting identified a defective crimp on a wire which was causing an intermittent open circuit that disabled the current limit function. <br /><br /> Evaluation determined that the capability to restore the battery charger to the DC electrical power subsystem to recover a discharged battery following a load shed of the charger may not have been able to be performed as designed. This condition may have resulted in an actual plant condition prohibited by Technical Specifications, Technical Specification 3.8.4. DC Sources-Operating. <br /><br /> No other plant systems were affected by this condition. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2662015004 | Point Beach 1, Point Beach 2 | 06/04/2015 | 08/03/2015 | ML15215A26 | <strong>Emergency Diesel Generator Switchgear Room Exhaust Fan Removal from Service Results in Operation or Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2015 with both units at full power, it was identified that removal of the W-185A(B), G-03(04) Emergency Diesel Generator (EDG) Switchgear Room Exhaust Fan from service may result in the inability to maintain switchgear room temperatures below that required to maintain equipment operable. <br /><br /> Subsequent engineering evaluation has determined that room temperature could have exceeded environmental conditions at which the components would be reasonably expected to function for their respective mission times with the G-03(04) EDG Switchgear Room Exhaust Fan(s) out of service. This condition resulted in a condition prohibited by Technical Specifications, Technical Specification 3.8.9. Distribution Systems-Operating. Additionally, Technical Specification 3.8.9 required action A.1 would have required immediate declaration of the associated supported required feature(s) inoperable. <br /><br /> No opposite train plant systems were affected by this condition. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Secifications, and 10 CFR 50.73(a)(2)(vii), Common Cause lnoperability of Independent Trains or Channels.
2662015006 | Point Beach 1 | 11/28/2015 | 12/28/2015 | ML15362A36 | <strong>Unit 1 Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2015 with Unit 1 in MODE 1 at full power, an automatic reactor trip was actuated as the result of a failure of the main generator automatic voltage regulator (AVR). All control rods fully inserted into the core. The Auxiliary Feedwater Pumps started as expected on low steam generator level. The Auxiliary Feedwater system was secured and decay heat removal was provided by the Condenser Steam Dumps utilizing the Main Feedwater system.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the reactor protection system and auxiliary feedwater system.
2702015001 | Oconee 2 | 07/27/2015 | 09/25/2015 | ML15275A08 | <strong>Valid Emergency Feedwater System Actuation Caused by a Main Feedwater System Block Valve Malfunction</strong><br /><i>Abstract:&nbsp;</i>Upon return from a Unit 2 forced outage, at 0957 hours on July 27, 2015, at approximately 16.6% power and increasing, there was an unexpected water level reduction in the 2B Steam Generator due to a malfunctioning main feedwater block valve that failed to open on demand. The level reduction resulted in a valid Emergency Feedwater System actuation and subsequently, reactor power was decreased so that feedwater/Steam Generator level could be controlled by only the startup control valve. <br /><br /> An investigation determined that 2FDW-40 failed to open due to the Automatic Feedwater Isolation System (AFIS) testing links not being fully closed and engaged. The root cause was due to a procedure use and adherence error by personnel performing the last AFIS Circuitry Test in the Fall of 2013. <br /><br /> This event had a negligible impact on nuclear safety. A planned corrective action is to revise applicable procedures for each Unit. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to the automatic actuation of the Unit's Emergency Feedwater System.
2722015001 | Salem 1 | 01/16/2015 | 10/19/2015 | ML15292A01 | <strong>Fuel Movement in Progress with Fuel Handling Building Ventilation Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 1/16/15, irradiated fuel was being moved in the Salem Unit 1 Fuel Handling Building (FHB) in support of fuel sipping activities. Fuel Handling Building Ventilation system operability was being monitored via a camera focused on the local indication which was displayed in the Control Room as permitted by station procedures. While fuel was being moved, the local differential pressure indicator oscillated between negative and slightly positive. Fuel movement was not secured as required by Technical Specification 3.9.12 when negative building differential pressure (D/P) was not maintained.<br /><br /> A causal evaluation determined that FHB equipment issues led to the FHB D/P alarm being locked in. A separate causal evaluation determined that Operations control room crew members failed to apply fundamentals of control board awareness and effective crew teamwork. Operating crew expectations were reinforced with respect to the assignment of personnel for continuous monitoring of equipment, and the underlying equipment deficiencies were corrected. <br /><br /> This event is reportable under 10 CFR 50.73 (a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specifications.
2722015002 | Salem 1 | 02/12/2015 | 11/16/2016 | ML16321A38 | <strong>Condition Prohibited by Technical Specification for One Channel of Steam Generator Level Indication Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2014, control room operators identified one steam generator (SG) protection level channel indicator as drifting high and approaching its 3 percent level deviation limit. Subsequent troubleshooting performed on October 10, 2014 identified the level transmitter as inoperable due to exceeding its Technical Specification (TS) calibration acceptance criteria. A past functionality evaluation was completed on February 12, 2015. This evaluation determined that the best estimate for when the transmitter would have exceeded its TS calibration acceptance criteria was August 19, 2013.<br /><br /> The cause of the SG protection level channel drifting was due to premature failure of its level transmitter due to a manufacturing defect. Vendor testing confirmed that a center diaphragm oil leak was the cause of the transmitter output drift. <br /><br /> This report is made in accordance with 10CFR50.73(a)(2)(i)(B), Any operation or condition which was prohibited by the plant's Technical Specifications.
2722015003 | Salem 1 | 03/15/2015 | 05/06/2015 | ML15127A38 | <strong>Plant Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 3/8/15, at 1158, the 14 Containment Fan Cooler Unit (CFCU) was declared inoperable following a trip of its low speed breaker on thermal overload protection during a scheduled surveillance test. Unit 1 entered Technical Specification (TS) 3.6.2.3, Action "a." for inoperability of one CFCU. Troubleshooting was unable to identify and correct the cause of the low speed breaker trip within the 7 day TS allowed outage time. Unit 1 entered Mode 3 (Hot Standby) at 1652 on 3/15/15, and Mode 5 (Cold Shutdown) at 1419 on 3/16/15.<br /><br /> The TS required shutdown of Salem Unit 1 was due to the 14 CFCU low speed breaker tripping on startup. Troubleshooting identified failed motor {BK/MO} stator support welds which allowed contact between the rotor and the stator on startup. The 14 CFCU motor was replaced.<br /><br /> This report is made in accordance with 10 CFR 50. 73 (a)(2)(i)(A), "The completion of any nuclear plant shutdown required by the plant's Technical Specifications ... "
2722015004 | Salem 1 | 04/21/2015 | 06/19/2015 | ML15173A03 | <strong>Condition Prohibited by Technical Specification for One Channel of Overtemperature Delta-T Inoperable</strong><br /><i>Abstract:&nbsp;</i>Salem Unit 1 exceeded its Technical Specification (TS) allowed outage time for one channel of Overtemperature Delta-T (OT Delta-T) due to inadequate post-maintenance testing following replacement of a Power Range Nuclear Instrument (PR NI) upper detector current meter. <br /><br /> Corrective actions include an extent of condition review of other PR NI system post-maintenance testing and review of the post- maintenance testing procedure to identify deficiencies. <br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications..."
2722015005 | Salem 1 | 06/22/2015 | 08/19/2015 | ML15231A38 | <strong>Low Containment Spray Additive Tank Sodium Hydroxide Concentration</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2015, at 1406, control room operators were notified by chemistry personnel that the Salem Unit 1 Containment Spray Additive Tank Sodium Hydroxide (NaOH) concentration was less than the minimum concentration by weight as required by Technical Specification (TS). Salem entered TS Action Statement 3.6.2.2.a for low NaOH concentration in the Containment Spray Additive Tank. On June 23, 2015 at 1908, NaOH concentration was returned to its minimum required TS value and the plant exited TS 3.6.2.2.a. <br /><br /> This report is made in accordance with 10 CFR 50.73(a)(2)(i)(B) for "Any operation or condition which was prohibited by the plant's Technical Specifications..." and 10 CFR 50.73(a)(2)(v) for "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: ...(C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident."
2722015006 | Salem 1, Salem 2 | 08/26/2015 | 10/23/2015 | ML15297A02 | <strong>Pressurizer Power Operated Relief Valves and Block Valves Do Not Meet the Requirements of 10 CFR 50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2015, a fire scenario was identified that could cause spurious operation of the Pressurizer Power Operated Relief Valves (PORVs) and also prevent the ability to manually close the associated PORV Block Valves. The fire scenario would invalidate the assumptions in the Safe Shutdown Analysis with respect to Reactor Coolant System Inventory and Pressure Control.<br /><br /> The cause of this issue was a failure to validate previous corrective actions to ensure compliance with 10 CFR 50, Appendix R. Corrective actions include the development and installation of plant modifications to restore compliance with 10 CFR 50, Appendix R. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B), "Any event or condition that results in the nuclear power plant being in an unanalyzed condition."
2722015007 | Salem 1 | 10/07/2015 | 01/29/2016 | ML16029A01 | <strong>Inoperable Control Room Emergency Air Conditioning System due to Failed Charcoal Filter Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2015, Salem Unit 1 was in Mode 1 operating at 100 percent power and Unit 2 was in Mode 6 with fuel movement in progress. The Salem Unit 1 Control Room Emergency Air Conditioning System (CREACS) train was in single train filtration mode supplying air to the common Control Room due to outage activities on Unit 2.<br /><br /> At 0628, the Salem Unit 1 CREACS train was declared inoperable due to failure of its charcoal filter surveillance test, resulting in both units CREACS trains being inoperable. Unit 1 entered Technical Specification (TS) 3.0.3, and Unit 2 suspended fuel movement to comply with TS 3.7.6, Action c.<br /><br /> At 0950, the Unit 2 CREACS train was returned to service and aligned to single train filtration mode supplying air to the common Control Room. Unit 1 exited TS 3.0.3, meeting the requirement of TS 3.7.6.1, Action a., to restore a single train of CREACS to operable. <br /><br /> This event was caused by less than adequate procedure guidance and ownership of the surveillance activity by the maintenance shop responsible for performing the work. The direct cause of the TS entry was the filter failure due to aging. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by the plant's TS, and 10 CFR 50.73(a)(2)(v)(D), as a condition that could have prevented the fulfillment of a safety function.
2752015001 | Diablo Canyon 1 | 12/31/2014 | 02/11/2016 | ML16042A47 | <strong>Both Trains of Residual Heat Removal Inoperable due to Circumferential Crack on a Socket Weld</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2014, while performing a walkdown as part of a surveillance test procedure, plant personnel identified through-wall seepage in a Diablo Canyon Power Plant Unit 1 socket weld inside containment that provides a flow path to a relief valve protecting a common portion of both trains of the residual heat removal system. Subsequent cleanup of the boric acid accumulation revealed active seepage of 30 drops per minute. A visual inspection identified that the source of the seepage was a circumferential crack on the socket weld. <br /><br /> Pacific Gas and Electric Company determined that the root cause of the cracked socket weld was containment fan cooler unit (CFCU) vibration inducing a resonant condition in the residual heat removal piping that generated stresses above the material endurance limit of the socket weld. Corrective actions included replacing two socket welds, modifying pipe supports, and correcting the condition causing the CFCU vibrations. <br /><br /> This condition did not have an adverse effect on the health and safety of the public.
2752015002 | Diablo Canyon 1 | 10/05/2015 | 12/03/2015 | ML15337A55 | <strong>Environmental Qualification of Wide Range Resistance Temperature Detectors Wiring Exceeded</strong><br /><i>Abstract:&nbsp;</i>As part of an apparent cause evaluation, Pacific Gas and Electric Company (PG&E) identified an incorrect insulation configuration, installed in 2010, on the thermal extension piping that houses the wires for the wide range (WR) reactor coolant system (RCS) resistance temperature detectors (RTDs). The insulation configuration, as installed, trapped heat inside the thermal extension piping and overheated the wires. The cause of the incorrect configuration of the insulation was insufficient guidance in the associated work package instructions. <br /><br /> An engineering analysis completed on October 5, 2015, determined that the eight WR RCS RTDs had either failed or were operating outside the environmental qualification temperature range. As a result, on October 5, 2015, PG&E determined that the required number of WR RTDs would not have been operable and therefore a violation of Technical Specification 3.3.3, "Post Accident Monitoring (PAM) Instrumentation," had occurred. <br /><br /> As part of the corrective actions, PG&E replaced all eight WR RTDs, restored the insulation per the design requirements, revised the drawings for Unit 1 WR RTDs to provide adequate level of detail, and revised the work order to include the correct drawing and level of details for proper installation of all WR RTDs. This event did not adversely affect the health or safety of the public.
2772015001 | Peach Bottom 2 | 09/16/2015 | 10/20/2015 | ML15293A15 | <strong>Condition Prohibited by Technical Specification due to Insufficient Remote Shutdown System Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>As a result of surveillance testing performed on 9/16/15, Operations personnel identified that the Reactor Core Isolation Cooling (RCIC) system steam admission valve (MO-2-13-131) would not open when operated from the Remote Shutdown System (RSS) panel. The NRC determined on 9/4/15 that insufficient Surveillance Requirement SR 3.3.3.2.1 testing was being performed for certain functions from the RSS panel. Prompt troubleshooting performed on 9/16/15 identified that a wire within the RSS panel associated with the logic for the MO-2-13-131 valve was not connected. This condition did not impact the normal operation of the MO-2-13-131 valve from the main control room, nor did it impact the automatic function of the MO-2-13-131 valve for licensed events. Only the manual open function of the valve from the RSS panel (located outside of the control room) was affected. The disconnected wire was immediately re-landed and the MO-2-13-131 was verified to operate properly from the RSS panel. The cause of the event is due to insufficient RSS panel testing that did not detect this historically disconnected wire. Surveillance test procedures of the RSS panel functions have been upgraded.
2782015001 | Peach Bottom 3 | 12/31/2015 | 02/26/2016 | ML16057A01 | <strong>Loss of High Pressure Coolant Injection System Function as a Result of Failed Flow Controller Signal Converter</strong><br /><i>Abstract:&nbsp;</i>On 12/31/15, at approximately 0630 hours, during shift turnover panel walk-downs, a licensed operator identified that the High Pressure Coolant Injection (HPCI) flow controller output indication was showing zero percent. The controller was in automatic with the set point at 5000 gpm, which would typically result in a controller output value of 100%. This condition would have prevented the HPCI system from performing its design function in the event of an accident. The HPCI system was declared inoperable and the appropriate Technical Specification Action was entered. Other standby systems (Reactor Core Isolation Cooling and low pressure emergency core cooling systems) remained operable.<br /><br /> Troubleshooting of the flow controller and related circuitry identified a failed signal converter. The signal converter was replaced and the HPCI system was declared operable at approximately 2110 hours on 12/31/15. <br /><br /> There were no actual safety consequences associated with this event.
2802015001 | Surry 1, Surry 2 | 01/27/2015 | 03/30/2015 | ML15103A27 | <strong>Inadequate Missile Protection due to Failure to Procedurally Control Sliding Missile Shields</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2015, with Units 1 and 2 operating at 100 percent power, it was identified that four sliding missile shields on the Main Steam Valve House (MSVH) were not included in the Abnormal Environmental Conditions procedure to be closed upon the threat of high winds. The shields are necessary to meet the design function of the MSVH for protection of the safety-related equipment and must be closed to perform their design function. A missile penetrating the MSVH could have prevented the MS and/or AFW systems from being able to mitigate the consequences of an accident. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(v). The shields were inappropriately excluded from the original revision of the procedure, which has now been revised to include the shields. This event posed no significant safety implications due to the low probability of missile damage inside the MSVH with the shields open. Therefore, the health and safety of the public were not affected by this event.
2802015002 | Surry 1, Surry 2 | 08/14/2015 | 10/12/2015 | ML15293A49 | <strong>Driver Brought Contraband to Protected Area Sally Port</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2015 at approximately 0830 hours, with Surry Power Station Units 1 and 2 operating at 100% power, a Virginia Electric and Power Company (Dominion) Nuclear Security Officer was told by a truck driver that he had portions of a disassembled weapon inside his backpack with the rest of the weapon located inside of his delivery truck. The driver informed the Security Officer of the contraband during a routine delivery truck search in the vehicle sally port, which is the vehicle search area for entry into the station's protected area. The truck driver was denied protected area access and he and the delivery truck were escorted off-site. <br /><br /> At 0850 hours on August 14, 2015, a one-hour notification was made to the NRC pursuant to 10CFR73, Appendix G, item 1(d), for an attempted introduction of contraband into a protected area. This Licensee Event Report is being submitted pursuant to 10CFR73.71(a)(4) for a 60 day follow-up written report.
2802015003 | Surry 1 | 10/13/2015 | 12/11/2015 | ML15352A02 | <strong>Unit 1 Reactor Trip due to Loss of Main Generator Field</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2015 at 1815 hours, with Unit 1 at 100 percent power and Unit 2 at 93.5 percent power at the end of life coastdown, Unit 1 experienced a reactor trip initiated from a turbine trip by main generator trip. The main generator trip was due to a loss of the main generator field that caused a loss of field protection relay to trip. <br /><br /> All three auxiliary feedwater pumps automatically started on low-low steam generator water level providing flow to the steam generators. Main steam trip valves were closed due to primary cooldown in accordance with emergency operating procedures and the plant was stabilized using steam generator power operated relief valves. The direct cause of the loss of main generator field of the Unit 1 generator was an electrical fault in the main generator exciter spacer coupling. Corrective actions to prevent recurrence will be implemented through the corrective action program when the root cause evaluation is completed. <br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System.
2812015001 | Surry 2 | 07/21/2015 | 09/18/2015 | ML15268A08 | <strong>Unit 2 Reactor Trip During Turbine Testing</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2015 at 05:05, with Unit 1 at Hot Shutdown and Unit 2 at approximately 6% power, Unit 2 experienced a reactor trip initiated from a turbine trip during performance of the Turbine Overspeed Protection Control system circuitry testing. The turbine trip was caused by governor valves rapidly opening due to a speed error which had accumulated between the turbine speed and reference setpoint resulting in a rapid increase in impulse pressure. The root cause of this event was inadequate instructions in the Overspeed Protection Control testing section of the operating procedure. The testing will be removed from operating procedures and placed in test procedures that are not performed as part of routine turbine startup. <br /><br /> All systems functioned as required. Initiation of auxiliary or emergency systems was not required. Unit 2 was placed in hot shutdown and the health and safety of the public were not affected. <br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System.
2812015002 | Surry 2 | 09/16/2015 | 11/04/2015 | ML15314A66 | <strong>Unanticipated Start of EDG 2 During Testing</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2015, at 2014 hours with Units 1 and 2 operating at 100 percent power, Emergency Diesel Generator 2 automatically started and assumed power to the Unit 2 'H' emergency bus. The event occurred during quarterly performance of the Emergency Bus Undervoltage and Degraded Voltage Protection Test. The direct cause of the event was the defective "A" single phase relay sticking and preventing the relay contacts from changing state. The procedures for Emergency Bus Undervoltage and Degraded Voltage Protection Tests have been revised to physically validate the state of the emergency bus relays prior to testing additional relays. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv)(A) for valid actuation of an Emergency Diesel Generator.
2822015004 | Prairie Island 1 | 05/31/2015 | 07/23/2015 | ML15205A10 | <strong>Manual Reactor Trip due to Trip of Condensate and Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2015, at 2220 CDT, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 reactor was manually tripped while operating at 100 percent power due to a lockout trip of 11 Condensate Pump followed by a lockout trip of 11 Main Feedwater Pump. The manual reactor trip was directed by the annunciator response procedure for the lockout alarm, C47010-0101, 11 FEEDWATER PUMP LOCKED OUT. This also resulted in a turbine trip as designed. The Operations crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3, at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. <br /><br /> The manual trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels have been returned to normal. <br /><br /> The cause for 11 Condensate Pump Motor failure was due to voids within the insulation resulting from inadequate Vacuum Pressure Impregnation (VPI). The voids allowed partial discharge to occur while in-service, which caused a turn to turn failure and a subsequent groundwall failure. <br /><br /> Corrective action is to determine the best test method(s) for identifying motor insulation degradation and initiate additional actions to perform implementation of these test methods.
2822015005 | Prairie Island 1 | 09/11/2015 | 10/10/2016 | ML16285A38 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2015, Prairie Island Nuclear Generating Plant (PINGP) staff recognized a possible misapplication of its plant procedure C18.1, Engineered Safeguards Equipment Support Systems. When a train of Safeguards Chilled Water System (SCWS) was removed from service, C18.1 Rev 40 required entry into Technical Specification (TS) 3.8.9. It was determined during the past three (3) years there were five (5) separate occasions between the two (2) trains of SCWS where C18.1 directed entry into TS 3.8.9. On each of these dates TS 3.8.9 was not entered and the required actions were not taken to restore to an operable status within the completion time. However, an equally correct application of TS would be to enter TS 3.7.11, and then apply TS 3.0.6. TS 3.0.6 allows for supported systems LCO not met solely to support system LCO not met, only support system LCO are required. The Safety Function Determination Program (SFDP) evaluation was performed and determined that there was no loss of safety function. This is a reportable event under 10 CFR 50.73(a)(2)(i)(b), Operation or Condition Prohibited by Tech Spec with the discovery date of inoperability. <br /><br /> The causal evaluation determined C18.1 was not accurate and usable in part, due to inadequate review of changes to the procedure. <br /><br /> The corrective actions revised C18.1 to invoke TS 3.0.6 as applicable for the Bus is Load Sequencer when SCWS is out of service.
2822015006 | Prairie Island 1, Prairie Island 2 | 08/04/2015 | 10/05/2015 | ML15278A51 | <strong>Quarterly Containment Spray Pump Surveillance Test Method</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2015, it was identified that the quarterly Containment Spray pump surveillance procedures (SP) 1090A[B] and 2090A[B] included steps to use a vent valve under administrative controls to drain the Containment Spray (CS) header before and after the SP was conducted. Previous revisions of the SPs (up to 2014) used a drain valve for the same purpose.<br /><br /> This created an open flow path from the Containment into the Containment Spray rooms in the Auxiliary Building. This configuration was not allowed by Tech Spec 3.6.3 A.1, and is reportable under 10 CFR 50.73(a)(2)(i)(B), operations or condition prohibited by Tech Spec. Additionally, the Containment pressure boundary function was adversely affected by opening the vent/drain valves, and the Containment vessels were inoperable as long as the vent/drain valves were open (in excess of one hour on some occasions). Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material is reportable under 50.73(a)(2)(v)(C). <br /><br /> The apparent cause is that the License Amendment implementation in 2002 for integrating Technical Specifications into Improved Technical Specifications did not identify when and how Tech Spec LCO 3.6.3 ACTIONS modifying note 1 applied to draining of the containment spray header from the Aux Building. <br /><br /> Corrective actions include procedure changes which have been submitted for the affected procedures and revising Tech Spec 3.6.3 Basis, Containment Isolation Valves.
2852015001 | Fort Calhoun | 09/30/2013 | 03/27/2015 | ML15086A56 | <strong>Inadequate Design of High Energy Line Break Barriers</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2015, following a station initiated review of operability evaluations, it was determined that a penetration with inadequate jet impingement protection had been previously identified as part of station extent of condition reviews and constituted an unanalyzed condition, but, had not been reported as required. This issue was discovered during an extent of condition review of high energy line break issues that the station initiated due to previously identified concerns. This issue and the other issues identified during the extent of condition review were corrected prior to plant heatup.<br /><br /> The Shift Manager that approved the operability evaluation believed that the reportability aspect of the penetration had been previously reported to the NRC and that no further report was required. The Shift Manager did not confirm that the reportability had been completed under another LER.<br /><br /> These issues were discovered during the Electrical Environmental Qualification Program Reconstitution Project. The deficiencies were discovered during extent of condition reviews. The deficiencies were properly remediated prior to plant startup in December 2013.
2852015002 | Fort Calhoun | 04/02/2015 | 05/28/2015 | ML15149A49 | <strong>Inoperable Auxiliary Feedwater System Due to Inadequate Procedure Change</strong><br /><i>Abstract:&nbsp;</i>During a review of station procedures a station operator determined that during the performance of OP-ST-AFW- 3009, "Auxiliary Feedwater Pump FW-6, Recirculation Valve, and Check Valve Tests," the restoration steps momentarily crosstie Main Feedwater (not safety related) with Auxiliary Feedwater system (safety related). During AFW system restoration a flowpath from the discharge of both the steam driven AFW pump (FW-10) and electric AFW pump (FW-6) is established to main feedwater. At the time of discovery the test was not being performed, however, the test had been performed during the last operating cycle.<br /><br /> The assessment and application of separation requirements in the associated procedures did not identify the cross tie methods and impacts due to reviewers not understanding piping class separation requirements.<br /><br /> AFW procedures were reviewed to ensure that other AFW procedures allow inappropriate lineups. Four (4) procedures were identified that aligned AFW in a similar manner. The use of the affected procedures has been administratively restricted until they can be corrected.
2852015003 | Fort Calhoun | 04/16/2015 | 06/15/2015 | ML15166A54 | <strong>Containment Spray Inoperable due to Original Design Error</strong><br /><i>Abstract:&nbsp;</i>During design basis reconstitution of the Containment Spray (CS) system, it was discovered that the CS piping inside containment and the containment liner have higher stresses during a postulated Main Steam Line Break (MSLB) or Loss of Coolant Accident (LOCA) than previously analyzed. The preliminary analysis concluded that both CS piping trains inside containment and the containment liner failed to meet the operability requirements of American Society of Mechanical Engineers (ASME) Section III Appendix F without implementing compensatory measures.<br /><br /> A cause analysis was performed and determined that thermal expansion was never considered for the containment riser supports. This is a flaw in the original design of the CS header and rings inside containment.<br /><br /> An operability evaluation was completed in support of plant operation. The operability evaluation conclude that the piping and pipe supports of the CS System as well as the Containment liner are capable of performing their intended safety functions per the operability criteria of ASME BPVC Section III Appendix F following modifications completed under Engineering Change (EC) 65926. Additional evaluation determined that only one pipe support exceeded the code allowable stresses. Final corrective action to fully qualify the CS system will be completed under the stations corrective action program.
2852015004 | Fort Calhoun | 06/05/2015 | 08/03/2015 | ML15215A72 | <strong>Inoperability of Auxiliary Feedwater Trains due to Failure of Steam Generator Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2015, at approximately 1330 Central Daylight Time (CDT), during startup HCV-1107A (Steam Generator (SG) RC-2A Auxiliary Feedwater (AFW) Inlet Valve) was declared inoperable when it failed to move during testing. During the investigation HCV-1108A (SG RC-2B AFW Inlet Valve) was found to hesitate during operation. The valve sealing materials had been replaced during the refueling outage with materials that were not appropriate for the service conditions.<br /><br /> A cause determination determined that the original valve specification for HCV-1107A was not appropriate for the plant application. <br /><br /> HCV-1107A and HCV-1108A were repaired using the original materials. An operability evaluation was completed for use of the original materials for one operating cycle. An engineering solution to the issue will be completed prior to startup from the next refueling outage.
2852015005 | Fort Calhoun | 07/21/2015 | 09/17/2015 | ML15260B35 | <strong>Reactor Coolant Leak at Reactor Coolant Pump Seal due to Cyclic Fatigue</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2015, an increase in reactor coolant system leak rate required station personnel to manually trip the reactor. The walkdown on July 21 determined that the location was the result of a middle seal cartridge inlet pressure tap through-wall crack. The piping is a class 1 pressure boundary. <br /><br /> A design weakness resulted in the vibrations from RC-3A combined with the cantilevered pipe load causing cyclical stresses on the toe of a weld on the seal inlet pressure pipe tap. These stresses initiated a fatigue crack at the toe of the weld on the piping which subsequently propagated inward and progressed through the pipe wall causing the failure. <br /><br /> The seal package for the reactor coolant pump was replaced with a spare unit.
2852015006 | Fort Calhoun | 10/21/2015 | 12/11/2015 | ML15345A27 | <strong>Unanalyzed Fire Vulnerability due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2015, at 1315 Central Daylight Time (CDT), while conducting design reviews, it was discovered that the isolation function, when transferring control from the Main Control Room to the Alternate Shutdown Panel (Al-185) for pressurizer backup heater bank 4, had been identified as a potential circuit failure. <br /><br /> The pressurizer backup heater bank 4 control circuit isolation vulnerability is a latent issue that originated in modification MR-FC-82-066 which installed the control circuit isolation for the pressurizer backup heater bank 4 in 1983. There have been missed opportunities to identify and correct the issue since 1982, however, it was not identified until CR 2015-12195 on October 21, 2015. <br /><br /> The vulnerability has been added to the pre-existing NFPA 805 Fire Protection compensatory measure for Fire Area 41, the Cable Spreading Room. Fire Area 42, the Main Control Room, is continuously staffed which has been credited as the compensatory measure. Additional actions will be implemented by the corrective action program.
2862015001 | Indian Point 3 | 01/08/2015 | 03/03/2015 | ML15069A08 | <strong>Safety System Functional Failure due to Inoperable Refueling Water Storage Tank Level Alarms due to Freezing of the Level Instrument Sensing Lines Caused by a Failed Strip Heater</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2015, the Refueling Water Storage Tank (RWST) level sensing instrumentation lines (LT-920 and LIC-921) were discovered frozen resulting in inoperable low-low level alarms in the Control Room. Entered Technical Specification (TS) 3.5.4 (RWST) Condition C due to both RWST low-low level alarms disabled in the CR. TS Condition C requires at least one channel of RWST low-low level to be restored to operable in one hour. Actions initiated to return one RWST level channel to operable. Entered TS 3.5.4 Condition D (Required Action and associated Completion Time not met) D.1 be in Mode 3 in 6 hours and D.2 be in Mode 4 in 12 hours. Commenced unit shutdown per TS for inoperable RWST level alarms. Repairs and calibrations completed returning the RWST level alarms to operable. TS 3.5.4 exited and power ascension commenced. Loss of both LT alarms is a safety system functional failure as the alarms are credited for operator manual switchover for recirculation. Direct cause was failure of the RWST instrument level alarm strip heater to maintain the temperature in the instrument enclosure. Due to the failure of the heat trace circuit EHT34-1 strip heater to function combined with a period of severe cold weather resulted in the sensing lines for the RWST to freeze. The apparent cause was a high resistance electrical connection at the strip heater wire lug due to thermal cycling and age. Corrective actions included repair of ring lug to strip heater and calibration of level instrumentation. Maintenance procedure 0-ELC-419-EHT will be revised to include inspection/repair of strip heater and ring lug connections within instrument enclosures. An action request (AR) will be initiated for a new model Work Order/PM to inspect strip heater connections and operation. The event had no significant effect on public health and safety.
2862015002 | Indian Point 3 | 02/27/2015 | 07/07/2015 | ML15194A04 | <strong>Technical Specification Prohibited Condition Caused by Four Main Steam Safety Valves outside Their As-Found Lift Set Point Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2015, during the performance of surveillance procedure 3-PT-R006A, three main steam safety valves (MSSV) (MS-46-2, MS-45-4 and MS-47-4) failed their As-Found lift set point test. Per the test, these valves must lift at +/- 3% of their required setting. During the test, 7 other MSSVs tested passed their As-Found test criteria. Technical Specification (TS) 3.7.1 (Main Steam Safety Valves) requires the MSSVs to be operable in accordance with TS Table 3.7.1-1 and Table 3.7.1-2. Due to the number of failures, during power ascension the remaining MSSVs were tested and two failed (MS-46-2, MS-46-3). MSSV MS-46-2 had previously failed and had maintenance performed therefore the failure was considered a post maintenance test failure. MS-46-3 failed its first lift test by 0.6% but met test lift criteria on the second and third test. TS Surveillance Requirement (SR) 3.7.1.1 requires each MSSV be verified to lift per Table 3.7.1-2 in accordance with the In-service Testing Program. Operability of the MSSVs includes the ability to open within the set point tolerances. The direct cause of the failure of these valves was severely worn spindle rods. The apparent cause for the failure of MS-47-4 and MS-46-2 was internal friction due to spindle vibration. The apparent cause of the failure of MS-45-4 was reuse of a worn spindle. The apparent cause of the failure of MS-46-3 is foreign material. Corrective actions included testing all 20 MSSVs and adjusting their set point to be within +/- 1% of design set pressure. Installed new spindles and bronze wear sleeves on valves MS-46-4, MS-46-2, MS-47-4, MS-48-2, MS-49-2, MS-49-1, MS-49-3, and replaced the spindle on valve MS-45-4. The Unit 3 MSSV test frequency will be changed from 4 years to 2 years until all modifications are implemented and IPEC is confident the issue is resolved. The event had no effect on public health and safety.
2862015003 | Indian Point 3 | 04/09/2015 | 06/08/2015 | ML15166A03 | <strong>Technical Specification Prohibited Condition Caused by Failure to Meet Containment Fan Cooler Unit Service Water (SW) Flow Rate due to Improper SW Surveillance Test Configuration Configuration</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2015, while in Mode 5 (cold shutdown) for a refueling outage, during performance of 3-PT-R200 (Essential Service Water Header Flow Balance) the As-Found service water (SW) flow rates for the 31 Fan Cooler Unit (FCU), 32 FCU and 33 FCU were less than the Technical Specification (TS) 3.6.6 (Containment Spray and Containment Fan Cooler System) Surveillance Requirement (SR) 3.6.6.3 flow of 1430 gpm. The SW essential header was re-balanced by adjusting FCU throttle valves to obtain a minimum of 1430 gpm for all five FCUs. On April 9, 2015, an engineering review of test data recorded from test 3-PT-R200, determined that the quarterly test (3-PT-Q016) that verifies FCU flows is not performed in the correct alignment for validating SW flow for the FCUs per TS SR 3.6.6.3. Test 3-PT-Q016 tests SW flow through FCU with SW isolated through the Emergency Diesel Generator (EDG) coolers. This configuration is not consistent with post accident operation in which SW is aligned to the FCUs and EDGs. The apparent cause was improper implementation of improved TS requirements. Corrective action was a revision of procedure 3-PT-Q016 to require validation of FCU SW flow with the EDG SW flow control valves and FCU outlet temperature control valves open. The event had no significant effect on public health and safety.
2862015004 | Indian Point 3 | 05/09/2015 | 09/14/2016 | ML16263A29 | <strong>Automatic Reactor Trip due to a Turbine-Generator Trip Caused by a Failure of the 31 Main Transformer</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2015, an automatic reactor trip (RT) occurred due to a Turbine-Generator trip as a result of a failure of the 31 Main Transformer (MT). All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the condenser. There was no radiation release. The emergency diesel generators did not start as offsite power remained available. The auxiliary feedwater system actuated as expected due to steam generator low level from shrink effects. Control room operators received alarms on the fire detection panel of the activation of the 31 MT and curtain wall deluge valves. Report to operators that there was an explosion and fire on the 31 MT. The plant fire brigade responded to the fire. The 31 MT had failed. Due to collateral influence from the 31 MT failure, the deluge system for the 32 MT and Unit Auxiliary transformer had also activated. In accordance with the emergency plan a Notice of Unusual Event (NUE) was declared at 1801 hours, which was terminated at 21:04 hours. The direct cause was an internal fault of the A Phase high voltage winding in the upper portion of the transformer. The root cause was vendor design/manufacturing deficiency that caused an internal failure that resulted in a fault on the A phase HV side of the transformer and the A phase HV voltage bushing. Key corrective actions included replacement of the 31 MT with a spare transformer, associated acceptance testing, repair of the isophase bus ducting for the 31 MT, inspections, cleaning, testing of the 32 MT, the Unit Auxiliary Transformer, high voltage components, isophase buses and main generator. A 4-year PM was prepared to perform Partial Discharge testing on the Unit 2, and Unit 3 MTs, Unit 2 and Unit 3 Auxiliary Transformers and the Unit 3 GT Auto Transformer. The event had no significant effect on public health and safety.
2862015005 | Indian Point 3 | 06/15/2015 | 09/14/2016 | ML16263A29 | <strong>Automatic Reactor Trip due to a Turbine-Generator Trip Caused by the Trip of 345kV Main Generator Output Breaker 3 due to a Failure of South Ring Bus 345kV Breaker 5</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2015, an automatic reactor trip (RT) occurred due to a Main Turbine-Generator trip as a result of a direct generator trip from the Buchanan switchyard. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the condenser. There was no radiation release. The emergency diesel generators did not start as offsite power remained available. The auxiliary feedwater system actuated as expected due to steam generator low level from shrink effect. Prior to the RT, Con Edison requested that Main Generator Output breaker 1 be opened to support removing 345kV feeder W97 from service for removal of a Mylar balloon on a 345kV conductor at the Millwood substation. After breaker 1 was opened, Main Generator Output breaker 3 opened initiating a direct generator trip signal due to a fault in South Ring Bus breaker 5. Direct cause of the RT was failure of 345kV breaker 5 due to an internal fault which activated protective relays that opened the remaining Main Generator Output breaker 3 which initiated a trip sequence that resulted in a RT. The root cause was Indian Point Energy Center did not provide formal notification of industry operating experience (OE) to Con Edison owner of breaker 5. The specific OE pertained to ITE Type GA breakers. Corrective actions include replacement of breaker 5. Procedure EN-0E-100 (OE Program) was revised to add a section describing how to initiate formal notification to external groups when OE related to components they own and/or control can affect generation. A new site procedure was issued (SMM-LI-126) to formalize the site process for notifying external groups of OE that can affect generation. The event had no effect on public health and safety.
2862015006 | Indian Point 3 | 07/01/2015 | 08/08/2016 | ML16224B01 | <strong>Technical Specification Prohibited Condition due to Two Pressurizer Code Safety Valves Discovered Outside Their As-Found Lift Setpoint Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2015, Engineering was notified by Wyle Laboratories that two of three Pressurizer Code Safety Valves (RC-PCV-464 and RC-PCV-468) were outside their As-Found lift set point test acceptance criteria (2411 - 2559 psig). The As-Found set pressure testing acceptance criterion for operability is 2485 +/-3%. The SVs were removed during the last refueling outage (RO) in the spring of 2015 and sent offsite for testing. Testing was performed within one year of removal as required by the Inservice Testing Program. SV RC-PCV-464 lifted at 2573 psig and SV RC-PCV-468 lifted at 2379 psig which is outside their set pressure range. The remaining SV tested satisfactorily. All three SVs were found with zero seat leakage. During the RO all three SVs were removed and replaced with certified pre-tested spare SVs. The SVs installed during the RO were As-Left tested to 2485 +/-1% with zero seat leakage in accordance with procedure 3-PT-R5A. Technical Specification (TS) 3.4.10 (Pressurizer Safety Valves), requires three pressurizer safety valves to be operable with lift settings set at greater than 2460 psig and less than 2510 psig. TS Surveillance Requirement (SR) 3.4.10.1 requires each PSV to be verified operable in accordance with the Inservice Testing Program. The valves were disassembled and internals inspected. The most probable cause of SV RC-PCV-464 lifting greater than 3% of its nominal setpoint was setpoint drift. The most probable cause of RC-PCV-468 lifting below 3% of its nominal set point was set point drift. Corrective actions included replacement of all three code safeties with pretested spares and disassembly and inspection of valves RC-PCV-464 and RC-PCV-468. The event had no effect on public health and safety.
2862015007 | Indian Point 3 | 07/08/2015 | 09/06/2016 | ML16256A77 | <strong>Manual Reactor Trip due to Decreasing Steam Generator Water Levels Caused by a Miss-Wired Circuit Board in the Main Feedwater Pump Speed Control System</strong><br /><i>Abstract:&nbsp;</i>On July 8, 2015, during surveillance testing, the Control Room received a 6.9kV motor trip alarm due to 31 Condensate Pump (CP) Motor circuit breaker trip on overcurrent. . Operators entered Alarm Operating Procedure 3-AOP-FW-1 due to loss of the 31 CP and initiated a load reduction. During this time the Main Boiler Feedwater Pump (MBFP) suction pressure decreased to its suction pressure cutback controller pressure range and its output decreased MBFP speed control to a minimum. The 31 MBFP speed control signal locked in at this minimum speed signal due to actuation of the MBFP Lovejoy speed control system Track and Hold feature. Due to this minimum 31 MBFP condition, the 31 MBFP recirculation valve opened causing the 31 MBFP check valve to close. With the 31 MBFP unloaded, Steam Generator (SG) water levels decreased and at 15 percent operators manually tripped the reactor. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. Direct cause was the 31 MBFP entered a Hold condition erroneously due to a miss-wired Track and Hold board in the speed control system. The root cause was the procurement for the MBFP Lovejoy Track and Hold boards was at an insufficient quality level commensurate with its criticality. There was a failure to mandate functional testing and wiring verification requirements on the vendor to ensure the procurement of a quality product. Corrective actions included replacement of MBFP track and hold board and 31 CP motor. A new replacement Track and Hold circuit board for both the 31 and 32 MBFP speed control system with the miss-wiring corrected was installed. The quality levels for the Track and Hold boards were revised from Q4 to Q3. MBFP Lovejoy speed control maintenance procedures and site vendor manuals were revised to include more detail. The event had no effect on public health and safety.
2862015008 | Indian Point 3 | 12/14/2015 | 09/06/2016 | ML16256A78 | <strong>Automatic Reactor Trip due to a Turbine-Generator Trip as a Result of a Fault on 345 kV Feeder W96 Tower Lines Caused by Pre-Existing Degraded Insulator</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2015, an automatic reactor trip (RT) occurred due to a Turbine-Generator trip caused by a fault on 345 kV feeder W96 transmission tower IP3-4. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the condenser. The auxiliary feedwater system actuated as expected due to steam generator low level from shrink effect. Inspections identified that an electrical fault damaged the 345 kV Transmission Tower line insulators. Direct cause of the RT was radial flashover of insulators on C phase of the 345 kV feeder W96 line at Transmission Tower IP3-4. The most likely cause is a pre-existing damaged insulator as a result of a prior flashover event that resulted in a repeat flashover due to environmental conditions. A single event with multiple flashovers associated with reduced insulation resistance due to a bird streamer is possible but less likely. Transmission Tower design does not have barriers to prevent avian perching on feeder towers. Corrective actions included inspection of Transmission Tower line insulators and ancillary hardware and replacement of damaged insulators and hardware. The preventive maintenance (PM) scope for the Unit 2 345 kV and 138 kV feeders was revised to include inspection and cleaning of Transmission Tower line insulators and hardware. An action request was generated to implement PM Template ENN-EP-G-004, Attachment 7.7 and Model Work Orders were revised and thermography and corona camera inspections performed. Bird guards will be installed on Entergy owned 345 kV and 138 kV Transmission Towers to preclude the effects of bird streaming. The event had no effect on public health and safety.
2872015001 | Oconee 3 | 01/31/2015 | 03/31/2015 | ML15098A47 | <strong>Unit 3 Manual Reactor Trip due to Unacceptable Main Feedwater Flow Control Valve Oscillations</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2015, Oconee Unit 3 was operating at 100% power in MODE 1 when Control Room operators observed that Main Feedwater flow indicators were oscillating outside of normal parameters. The Control Room supervisor made the decision to manually trip Unit 3 at 1431 hours due to erratic feedwater operation and increasing RCS pressure. A subsequent investigation determined the feedwater flow oscillations were caused by a subcomponent failure of the electrical to pneumatic converter (E/P), 3FDW EP 0007, to properly control feedwater flow for Main Feedwater Control Valve (MFCV) 3FDW-32.<br /><br /> This event was reported as a 4-hour notification to the NRC on January 31, 2015, in Event Notification (EN) number 50781 under 10 CFR 50.72(b)(2)(iv)(B) - Reactor Protection System (RPS) Actuation - Critical. The event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the RPS.
2892015001 | Three Mile Island 1 | 08/06/2015 | 10/05/2015 | ML15278A50 | <strong>Seismically Qualified BWST Aligned to Non-Seismic Piping</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2015 NRC provided TMI-1 the final response to Task Interface Agreement 2015-01 "Assessment of Three Mile Island Nuclear Station's Use of a Non-Seismic Qualified Cleanup Path for the Borated Water Storage Tank." It concluded that opening the boundary valve between the safety related and seismically qualified Borated Water Storage Tank (BWST) and the non-seismically qualified clean-up system piping during power operation mode renders the BWST inoperable. A review of operator logs determined that the BWST was connected and recirculated via the clean-up system while in the power operation mode within the past three years and for a period of time greater than the applicable Technical Specification completion time allowed. This represented a condition prohibited by Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). This event had no effect on public health and safety.
2932015001 | Pilgrim | 01/27/2015 | 03/30/2015 | ML15097A25 | <strong>Loss of 345KV Power Resulting in Automatic Reactor Scram During Winter Storm Juno</strong><br /><i>Abstract:&nbsp;</i>On Tuesday January 27, 2015, at 0402 hours, while in the process of lowering reactor power, with the reactor in the RUN mode at 52 percent core thermal power, Pilgrim Nuclear Power Station (PNPS) experienced a loss of 345KV power resulting in a load reject and an automatic reactor scram. The loss of 345KV power was due to faults from flashovers in the PNPS switchyard. All control rods fully inserted. The Emergency Diesel Generators had been previously started and were powering safety-related buses A5 and A6. The plant stabilized in Hot Shutdown. At the time of the event a significant winter storm (Juno) was buffeting Southern New England.<br /><br /> The root cause of the event is that the design of the PNPS switchyard does not prevent flashover when impacted by certain weather conditions experienced during severe winter storms. A modification of the switchyard is planned to address the susceptibility of the PNPS switchyard to flashovers during severe winter storms.<br /><br /> This event posed no threat to public health and safety.
2932015002 | Pilgrim | 03/12/2015 | 05/12/2015 | ML15135A24 | <strong>Main Steam Safety Relief Valves Determined to be Inoperable Following Evaluation</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2015, after further evaluation of system performance of SRV-3A and SRV-3C, along with results of valve internal conditions identified during physical inspection, the valves were determined to have been inoperable for an indeterminate period during the last operating cycle. Specifically, SRV-3C was determined to be inoperable based on its on-demand performance at low reactor pressures, as well as the visual conditions that were identified during the inspection process. SRV-3A was considered inoperable based on it having similar internal indications as SRV-C when it was disassembled and inspected. SRV-3A was installed in May 2011 and SRV-3C was installed in October 2013.<br /><br /> Additionally, during an extent of condition review of historical SRV performance, the review identified on March 13, 2015 that SRV-3A had failed to open in response to three manual actuation demands on February 9, 2013.<br /><br /> At the time the valves were declared inoperable the reactor was at 100% power. The valves had been replaced in February 2015 during the forced outage relating to winter storm Juno. This event posed no threat to public health and safety.
2932015004 | Pilgrim | 04/23/2015 | 03/08/2016 | ML16075A25 | <strong>480 Volt Bus B6 Auto Transfer Function Degraded</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2015 with the unit shutdown for refueling outage, while performing plant procedure 3.M.3-27, Attachment 1 "Calibration of Bus 61 Relays," there was indication the time delay Agastat relay 27A-B1X/ TDDO contact 3-5 had failed open. The contact never changed state during cycling of the relay. In the event of a degraded voltage condition as detected on bus B1, bus B6 would not have automatically transferred to bus B2 as designed. Bus B6 would have tripped from B1 with degraded voltage and lost power altogether. Bus B6 supplies Class 1E electric power to the Low Pressure Coolant Injection (LPCI) valves (MO-1001-28A/B & MO-1001-29 A/B), Salt Service Water (SSW) Pump C (P208C), 125 and 250 volt direct current (DC) back-up battery chargers (D14 and D15, respectively), Residual Heat Removal Valves (MO-1001-19 and MO-1001-32), Primary Containment Isolation Valves (MO-1001-50, MO-1201-2, MO-1201-80, MO-220-1), and Reactor Recirculation System Valves (MO-202-4A/B and MO-202-5A/B). <br /><br /> The relay was replaced on April 24, 2015. The failed relay was disposed of prior to any failure analysis being performed. Disposal of the relay, without performing the failure analysis, was entered into the corrective action program. <br /><br /> This event was not risk significant and posed no threat to public health and safety.
2932015005 | Pilgrim | 05/22/2015 | 07/21/2015 | ML15212A01 | <strong>Degrading Condenser Vacuum Resulting in Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On Friday, May 22, 2015 at 10:02 hours EDT, with the Reactor Mode Select Switch in the Start-Up position and the reactor at approximately 4 Percent core thermal power, a manual reactor scram was inserted due to degrading Main Condenser vacuum due to high air in-leakage from a crack on a feedwater heater expansion bellows and plant conditions caused by extended operation on the Main Turbine bypass valves. <br /><br /> Following the reactor scram, all rods were verified to be fully inserted and no Emergency Operating Procedure entry conditions existed. All plant systems responded as designed. <br /><br /> The cause of the event is that the design limitations of the Offgas System were exceeded by the unusual combination of plant conditions resulting in degrading main condenser vacuum. Corrective action was taken to mitigate the air in-leakage from the crack on a feedwater heater expansion bellows. In addition, guidance and limitations have been provided for operation with elevated air in-leakage conditions.<br /><br /> This event posed no threat to public health and safety.
2932015006 | Pilgrim | 08/09/2015 | 10/07/2015 | ML15289A23 | <strong>Ultimate Heat Sink and Salt Service Water System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On Sunday, August 9, 2015 at 1627 EDT with the reactor at 90% core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) declared the ultimate heat sink (UHS) and salt service water (SSW) system inoperable due to high sea water inlet temperatures greater than 75°F and entered the Technical Specification (TS) 3.5.13.4 24-hour shutdown Limiting Condition for Operation (LCO) Action Statement. A maximum sea water inlet temperature reading of 75.03°F was observed. The Action for TS 3.5.B.4 was exited at 1653 EDT (26 minutes elapsed time) based on sea water inlet temperature trending below the TS criterion. Plant systems and components operated as required. <br /><br /> The cause of the sea water inlet temperature exceeding the 75°F TS criterion was sustained increased sea water surface temperature in Cape Cod Bay due to summer weather conditions and recirculation of water from the plant's discharge due to wind and tidal conditions.<br /><br /> This condition posed no threat to the public health and safety.
2932015007 | Pilgrim | 08/22/2015 | 10/20/2015 | ML15307A00 | <strong>Single Main Steam Isolation Valve Closure Resulting in Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On Saturday, August 22, 2015, at 1628 [EDT], with the reactor at 100% core thermal power the Pilgrim Nuclear Power Station experienced an automatic reactor scram due to Average Power Range Monitor High Flux signal from the rapid closure of one main steam isolation valve (MSIV). All plant systems responded as designed. <br /><br /> The Root Cause of this event is inadequate worker practices resulting in an excessive load being applied to the unistrut enclosed pneumatic line (during or prior to 2001) causing it to lay on a Main Steam Line subject to vibration. The excessive load caused an initiating crack in the nipple threads that over time resulted in a shear of the line. <br /><br /> The pneumatic supply line nipple was replaced and the line was re-supported. <br /><br /> This event posed no threat to public health and safety.
2932015010 | Pilgrim | 10/05/2015 | 11/19/2015 | ML15335A06 | <strong>Motor-Operated Valve Control Circuit Vulnerability to Information Notice 92-18 Concern</strong><br /><i>Abstract:&nbsp;</i>On Monday, October 5, 2015 at 1725 hours EST, with the Reactor Mode Select Switch in the Run position and the reactor at approximately 100 percent core thermal power, Pilgrim Station identified and reported a vulnerability applicable to 10 CFR 50, Appendix R, Section III.G, Fire Protection of Safe Shutdown Capability. The specific vulnerability involved lack of limit and torque switch protection of motor operated valves (MOVs) during an unlikely scenario of a large scale fire, forced evacuation of the Main Control Room (MCR), and spurious operation of MOVs due to fire damage. This potential vulnerability is identified in NRC Information Notice (IN) 92-18. Discovery of the vulnerability was determined to be reportable. <br /><br /> The cause of the event was evaluated and determined to be the result of incorrect assumptions applicable to the initial evaluation of the IN 92-18 concern and improper use of the Corrective Action Program when discovering new Appendix R open items. Corrective actions taken included the performance of hourly fire watches in the plant areas where MOV local operation is credited for the MOV control cables that could be affected. Valve control circuit modifications are under development and scheduled for implementation. <br /><br /> A fire event did not occur. There was no impact to public health and safety.
2962015001 | Browns Ferry 3 | 02/11/2015 | 04/13/2015 | ML15114A28 | <strong>High Pressure Coolant Injection and Reactor Core Isolation Cooling Inoperable due to No Suction Source Aligned</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2015, at 0820 Central Standard Time, Brown’s Ferry Nuclear Plant (BFN), Unit 3, declared the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems inoperable due to no suction source aligned. During surveillance testing, the Condensate Storage Tank (CST) emergency discharge isolation valve energized and closed when the breaker was closed, isolating both systems from their suction source. It was subsequently determined that contacts on the local hand switch were stuck closed following performance of a previous maintenance task. Operations personnel re-opened the isolation valve using the hand switch in the Control Room, restoring operability to the HPCI and RCIC systems.<br /><br /> The apparent cause of this event was inadequate design review of a 2010 plant modification which allowed latent design vulnerabilities to be introduced into the plant.<br /><br /> The corrective actions to reduce the probability of a similar event occurring in the future were to remove thermal overload heaters from the affected breakers, preventing valve closure when these breakers are closed; to review a sample of recent engineering change packages for quality of Design Review; to repair a faulty hand switch; and to implement a design change for the CST isolation valves for all three BFN units to prevent spurious operation of the isolation valve when the associated breaker is closed.
2962015002 | Browns Ferry 3 | 02/18/2015 | 04/20/2015 | ML15110A01 | <strong>Switch Failure Rendered Automatic Startup of Some Emergency Core Cooling System Pumps Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2015, the Browns Ferry Nuclear Plant (BFN), Unit 3, the 3D Core Spray Pump normal power relay (3-RLY-075-14A-K31B) was found de-energized when it should have been energized during performance of a surveillance. Troubleshooting determined the cause of the relay being de-energized was failure of the MJ(52STA) switch in the associated breaker. The relay is an emergency start permissive for the 3B and 3D Core Spray pumps, the 3D Residual Heat Removal pump, and the D1 Residual Heat Removal Service Water pump. This condition prevented those systems from automatically performing their safety functions under normal power, rendering them inoperable for longer than allowed by Technical Specifications. However, these systems were available and the affected pumps could be manually started to perform their safety functions in the event of an accident. The failed switch only serviced the normal power feed, and automatic starting function was unaffected under emergency power. On February 18, 2015, an engineering evaluation determined the switch had apparently failed on September 17, 2014. On January 24, 2015, the relay and switch were replaced, and the automatic startup function was restored.<br /><br /> Apparent causes of the event are failure to implement all appropriate preventive maintenance or pre-emptive replacement allowing MJ(52STA) switches to fail, and the BFN Breaker Program excluding the associated switchgear components allowing support components to be overlooked with respect to reliability.<br /><br /> Corrective actions include replacing MJ switches in non-spare breakers and revising associated preventive maintenance, and revising the Breaker Program to include essential switchgear components.
2962015003 | Browns Ferry 3 | 01/07/2015 | 06/01/2015 | ML15152A35 | <strong>Traversing Incore Probe Operation Caused Inoperability of Primary Containment Isolation Valves for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2015, Browns Ferry Nuclear Plant (BFN), Unit 3, 3D and 3E Traversing Incore Probes (TIPs) stopped responding to automatic controls. The TIPs were left outside of their in-shield positions to decay for 24 hours, and the 3D and 3E TIP Primary Containment Isolation ball valves were left open. On January 8, 2015, the 3D and 3E TIPs were returned to their in-shield positions and their ball valves were closed.<br /><br /> On April 2, 2015, it was determined that, with the identified condition the 3D and 3E TIPs were incapable of automatically retracting in the event of an accident. The impact to the Primary Containment Isolation Valves (PCIVs) function was not recognized on January 7, 2015, and the required PCIV actions were not taken. Therefore, BFN, Unit 3, operated with two inoperable PCIVs, in violation of Technical Specifications (TS).<br /><br /> The apparent cause of this event was operations procedure 3-OI-94, Traversing Incore Probe System, lacked the appropriate guidance and relevant information to address TIP problems and associated TS applicability. Corrective actions include revising the procedure to provide additional guidance on responding to TIP probe malfunctions, and conducting briefings with operations.
2962015004 | Browns Ferry 3 | 05/12/2015 | 07/13/2015 | ML15194A11 | <strong>High Pressure Coolant Injection System Inoperable due to Failed Pressure Switch</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2015, at approximately 0034 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) maintenance personnel commenced a scheduled High Pressure Coolant Injection (HPCI) Steam Line Supply Low Pressure Functional Test, 3-SR-3.3.6.1.2(3B), on the BFN Unit 3 HPCI system. At 0104 CDT, BFN, Unit 3, received a Primary Containment Isolation System (PCIS) Group 4 isolation of the HPCI system, resulting in the inoperability of the single train HPCI system. Operations personnel entered Technical Specification (TS) Limiting Condition for Operation 3.5.1 Condition C, and verified the Reactor Core Isolation Cooling system was operable. During the period of Primary Containment Isolation, the HPCI system was unable to perform its safety function. However, in an emergency, other systems were available to provide the required safety functions. At 0117 CDT, Operations personnel reset the HPCI system isolation, and declared HPCI operable. <br /><br /> The apparent cause of this event was a deficiency on Pressure Switch (PS) 3-PS-073-0001A or 3-PS-073-0001C which allowed the circuit to complete while 3-PS-073-0001B was taken closed for testing. Corrective actions include troubleshooting PSs, replacement of failed PSs in the affected circuit, and implementation of a strategy to mitigate risk while performing 3-SR-3.3.6.1.2(3B).
2962015005 | Browns Ferry 3 | 08/20/2015 | 10/19/2015 | ML15292A54 | <strong>Automatic Actuation of 3D Diesel Generator due to 4kV Shutdown Board Trip During Testing</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2015, at 1032 Central Daylight Time (CDT), while installing test equipment on the 3ED 4kV Shutdown Board (SD BD), for an online dynamic motor test of the 3D Residual Heat Removal pump motor, the Unit 3 Control Room received degraded voltage alarms and under voltage alarms for the 3ED SD BD. The 3ED 4kV SD BD normal feeder breaker opened, and the 3D Emergency Diesel Generator (DG) fast started and tied onto the board. <br /><br /> Troubleshooting was performed on the 3ED SD BD and on the 3D DG. The failure mode for this event was the clearing of primary and secondary 3ED SD BD metering fuses. The normal feeder breaker was closed, and offsite power to the SD BD was declared operable on August 21, 2015, at 1945 CDT. <br /><br /> A definitive cause could not be identified for the clearing of the fuses. However, corrective actions will be implemented that will address all of the most probable causes, and will minimize the likelihood of recurrence. These actions include performing inspections on circuits used for online dynamic motor testing of motors, removing the potentially faulty test equipment from service, and removing online dynamic motor testing from 4kV motor preventative maintenance.
2982015001 | Cooper Station | 01/26/2015 | 11/05/2015 | ML15320A01 | <strong>Valve Test Failures Result in a Condition Prohibited by Technical Specifications and a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On January 26 and February 11, 2015, five of eight Target Rock safety relief valve (SRV) pilot valve assemblies, removed during Refueling Outage 28, failed to lift within Technical Specification (TS) lift setpoint requirements. The pressure setpoint of the first failed pilot assembly is 1090 psig; the SRV pilot assembly lifted at 1124 psig. The pressure setpoint of the second failed pilot assembly is 1100 psig; the SRV pilot assembly lifted at 1192 psig. The pressure setpoint of the third failed pilot assembly is 1090 psig; the SRV pilot assembly lifted at 1267.7 psig. The pressure setpoint of the fourth failed pilot assembly is 1100 psig; the SRV pilot assembly lifted at 1139 psig. The pressure setpoint of the fifth failed pilot assembly is 1090 psig; the SRV pilot assembly lifted at 1138 psig. Two subsequent lifts were performed for all failed SRV pilot assemblies and the results were within the TS pressure setpoint tolerances. <br /><br /> Initially, the probable cause was corrosion bonding with time being a possible exacerbating factor. Upon further investigation and testing, it has been determined that the direct cause of the failures is corrosion bonding. <br /><br /> Although the TS related to the set point lift pressures of the SRV pilot valve assemblies were exceeded, an analysis of this event indicates that the design basis pressures to ensure safety of the reactor vessel and its pressure related appurtenances were not challenged. Public safety was not at risk. Safety to plant personnel and plant equipment were not at risk.
2982015002 | Cooper Station | 02/19/2015 | 04/16/2015 | ML15111A44 | <strong>Failure of Main Steam Differential Pressure Indicating Switches Results in a Condition Prohibited by Technical Specifications and a Common Cause Inoperability of Independent Trains or Channels</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2015, during performance of surveillance procedures, three of eight Division 2 Main Steam Differential Pressure Indicating Switches failed to trip prior to exceeding limits set in Technical Specifications (TS).<br /><br /> Investigation revealed that the setpoint change calculations and surveillance procedures had been inappropriately revised during implementation of TSTF-493. The applicable setpoint change calculations and surveillance procedures have been revised to pre-TSTF-493 values.<br /><br /> This event is being reported as an operation or condition prohibited by TS, and also as a common cause inoperability of independent trains or channels.<br /><br /> The event has negligible safety significance based on the safety function associated with the main steam high flow isolation signal was preserved through successful testing of five of the eight Division 2 switches.
2982015003 | Cooper Station | 05/30/2015 | 07/28/2015 | ML15216A36 | <strong>Failure of Main Steam Isolation Limit Switches Results in a Condition Prohibited by Technical Specifications and Also a Common Cause Inoperability</strong><br /><i>Abstract:&nbsp;</i>In January 2015, during Quarterly Surveillance Testing on the Main Steam Isolation Valves (MSIVs), inboard MSIV C failed to actuate its associated Reactor Protection System (RPS) relay. The limit switch and associated RPS relay were declared inoperable and the associated RPS channel was placed in trip to satisfy Technical Specifications requirements. <br /><br /> In May 2015, during Quarterly Surveillance Testing on the MSIVs, the inboard MSIV A and inboard MSIV B also failed to actuate their associated RPS relay. The limit switches and associated RPS relay were declared inoperable and the associated RPS channel was placed in trip to satisfy Technical Specifications requirements. <br /><br /> As a result, the plant was in an increased risk of an inadvertent full scram. A decision was made to shut the plant down and replace the limit switches. <br /><br /> The limit switches were removed and are being evaluated for cause. <br /><br /> The event is currently under investigation. CNS will provide a supplement to this Licensee Event Report.
2982015004 | Cooper Station | 05/30/2015 | 07/29/2015 | ML15216A36 | <strong>Isolation of Shutdown Cooling Results in a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2015, at 03:27, Cooper Nuclear Station placed the "B" Loop of Residual Heat Removal (RHR) in the Shutdown Cooling (SDC) mode of operations and entered Mode 4, Cold Shutdown, at 04:15. At 04:58, isolation signals from pressure switches (RR-PS-128A and/or RR-PS-128B) were received and, SDC suction isolation valves RHR-MO-17 and RHR-MO-18 closed, resulting in a loss of SDC. <br /><br /> Investigation revealed the event was initiated by steam flashing in the SDC line. This flashing created pressure transients, causing RHR-MO-17 and RHR-MO-18 to close. The steam flashing occurred due to temperature in the SDC line being at or near saturation temperature causing localized boiling then void collapse with coolant being drawn from the reactor vessel thru the reactor recirculation system. SDC was restored at 05:20 on May 30, 2015. The root cause of the event was determined to be a design vulnerability and subsequent operation of the SDC system that resulted in a trip of the SDC suction valves due to sub-cooling and flashing in the RHR or Reactor Recirculation (RR) system. To prevent recurrence, CNS will initiate an Engineering Change request to move the location of the input pressure signals required to meet requirements of Technical Specification 3.3.6.1, Table 3.3.6.1-1, 6(a) from the RR line to the Vessel Steam Dome.<br /><br /> This is a Safety System Functional Failure.
3012015005 | Point Beach 2 | 10/29/2015 | 12/28/2015 | ML15362A36 | <strong>Main Transformer Lockout and Associated Loss of Buses Results in System Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2015, during Unit 2 refueling outage activities, a main transformer lockout was generated when a short circuit was created while performing a tagout clearance activity. The main transformer lockout resulted in a loss of non-vital 4KV buses, which resulted in actuation of the Steam and Motor Driven Auxiliary Feedwater Pumps.<br /><br /> Unit 1 was at full power and none of the Unit 1 systems were affected by this event. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), for the auxiliary feedwater system actuation.
3062015001 | Prairie Island 2 | 03/07/2015 | 09/24/2015 | ML15272A48 | <strong>21 Fan Coil Unit (FCU) Leak-Containment Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 11 :55 CST on March 7, 2015, Unit 2 was at Mode 4 when a small cooling water leak was identified on the 21 Containment Fan Coil Unit (FCU) east face U-bend on the northeast corner bottom bundle. Unit 2 Containment was declared inoperable per Technical Specifications (TS) 3.6.1, Condition A, Containment inoperable, applicable in MODES 1, 2, 3, and 4. Immediate actions were taken to isolate the FCU within 1 hour from the initial identification of the leak and Containment was declared operable at 1220 CST on March 7, 2015. <br /><br /> This condition is reportable under 10 CFR 50.72(b)(3)(v)(C): Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. ENS 50870 was submitted at 14:05 CST. The plant remains in a safe condition and there was no effect to the health and safety of the public. The NRC Resident Inspector was notified. <br /><br /> The cause has been determined to be under-deposit pitting corrosion resulting in through-wall leaks. The identified leaking faces were replaced on 03/13/2015. The remaining FCU faces subjected to under-deposit pitting corrosion are scheduled to be replaced during the next Unit 2 refueling outage Fall 2015 (2R29). Increased inspections of the FCUs will remain in effect until corrective actions have been implemented.
3062015002 | Prairie Island 2 | 04/03/2015 | 06/22/2016 | ML16174A43 | <strong>21 Feedwater Pump Lockout, Unit 2 Reactor Trip due to Pressure Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2015, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was operating at 100 percent power, when at 0652 CDT, an unexpected annunciator, 47510-0104 21 FEEDWATER PUMP LOCKED OUT was received. The reactor was manually tripped as required by the annunciator response procedure. This also resulted in a turbine trip as designed. The Operations crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3, at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. The Auxiliary Feedwater Pumps actuated as designed on low narrow range steam generator level. Steam Generator levels were returned to normal. <br /><br /> This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation, and 10 CFR 50.72(b)(3)(iv)(A), any event or condition that results in valid actuation of any of the systems listed in paragraph 10 CFR 50.72(b)(3)(iv)(B)(6), PWR auxiliary or emergency Feedwater system. <br /><br /> The cause evaluation determined that the event was caused by pressure fluctuation within the system which resulted in the bourdon tube movement at a high frequency causing wear of the internal components of the pressure switch. Corrective actions: Pressure Switch (PS-16012) was replaced immediately on April 3, 2015, and to install snubbers to reduce process flow fluctuations experienced by Feedwater Pump pressure switches.
3062015003 | Prairie Island 2 | 06/07/2015 | 08/05/2015 | ML15217A01 | <strong>Unit 2 Turbine/Reactor Trip - Low Bearing Oil Pressure</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2015, at 0735, the Unit 2 Reactor automatically tripped while operating at 100 percent power due to an automatic Turbine trip due to low bearing oil pressure. The crew entered the reactor trip emergency operating procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. All safety functions operated as designed. The automatic reactor trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels returned to normal. There was no effect on Unit 1 as a result of this trip. <br /><br /> Normal bearing oil discharge pressure is approximately 19 psi when the turbine is at 1800 rpm and oil is being supplied from the main oil pump. The turbine will trip when 2 out of 3 bearing oil pressure instruments reach 6 psi. Troubleshooting performed in support of the event identified a cracked and broken weld on a reducing flange for the line that supplies high pressure oil to the Seal Oil skid and Auto Stop Oil. This was the component that failed and resulted in the loss of pressure to the turbine oil bearings. Corrective actions taken included repairing the broken weld, restoring the oil skid to operation, performing an extent of condition evaluation, and entering separate corrective actions to inspect piping connections in the Unit 1 and Unit 2 turbine oil reservoirs.
3112015001 | Salem 2 | 01/20/2015 | 03/19/2015 | ML15079A00 | <strong>Condition Prohibited by Technical Specification for One Channel of Overtemperature Delta-T Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 1/20/15, a step change occurred on the high differential band indicator of the Axial Flux Difference recorder. Subsequent troubleshooting of the recorder on 1/26/15 identified a failed isolator that provides input to Channel 4 of Overtemperature Delta-T logic circuitry. This failure rendered Channel 4 of the Overtemperature Delta-T protection circuit inoperable for a period of approximately five and a half days without being placed in a tripped condition. The isolator was replaced and the Overtemperature Delta-T Channel was returned to service.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications..."
3112015002 | Salem 2 | 08/05/2015 | 09/07/2017 | ML17250A15 | <strong>Reactor Trip due to Loss of 4 kV Non-Vital Group Bus</strong><br /><i>Abstract:&nbsp;</i>On 8/05/15, at 1539, Salem Unit 2 experienced an automatic reactor trip. The cause of the reactor trip was due to a trip of the 21 Reactor Coolant Pump (RCP) causing a 21 Reactor Coolant Loop low flow condition. The 21 RCP breaker tripped as designed when the 2B Auxiliary Power Transformer (APT) infeed breaker to the 2H 4 kilovolt (kV) Non-Vital Bus opened. The root cause evaluation did not identify a definitive cause. However the most probable cause of the 2H 4 kV Non-Vital Bus trip was due to a ground fault on the 21 Heater Drain Pump (HDP) motor that was not isolated by its associated neutral overcurrent relay. An automatic start of the Auxiliary Feedwater (AFW) system occurred as expected following the reactor trip due to low steam generator water levels. <br /><br /> Corrective actions include replacement of the 21 HDP motor and its neutral overcurrent relay. <br /><br /> This event is reportable under 10 CFR 50.73 (a)(2)(iv)(A) as an event that resulted in an automatic actuation of the reactor protection system and actuation of the AFW system.
3112015003 | Salem 2 | 11/23/2015 | 03/09/2016 | ML16069A32 | <strong>Both Trains of High Head Safety Injection Inoperable due to a Relief Valve Failure</strong><br /><i>Abstract:&nbsp;</i>At 2136 on November 23, 2015, the Boron Injection Tank (BIT) relief valve 2SJ10 exhibited increased seat leakage during the performance of troubleshooting to determine the cause of low BIT pressure. The increased seat leakage from 2SJ10 initiated a Reactor Coolant System (RCS) leak greater than 10 gallons per minute (gpm). Technical Specification (TS) 3.4.7.2.b action b was entered for RCS unidentified leakage greater than 1 gpm. <br /><br /> The BIT was isolated at 2137 and the leakage was stopped. Isolation of the BIT resulted in loss of the high head safety injection flow path for both trains of high head safety injection, requiring entry into TS 3.0.3. <br /><br /> This event was caused by ineffective use of internal operating experience in the decision making process to reuse the 2CV141, which had been installed on the discharge of the 23 positive displacement charging pump, as a suitable replacement for the 2SJ10 during 2R21. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(v)(D) "Any event or condition that could have prevented the fulfillment of the safety functions of structures or systems that are needed to mitigate the consequences of an accident."
3132015001 | Arkansas 1 | 12/15/2015 | 02/12/2016 | ML16043A25 | <strong>Manual Reactor Trip due to Oscillations in the Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2015, at approximately 0544, Arkansas Nuclear One, Unit 1 (ANO-1), manually scrammed during a scheduled automatic down power to 35% power for planned maintenance. The Integrated Control System (ICS) (JB) was being utilized for the down power. During the down power, oscillations occurred in the Main Feedwater (MFW) (SJ) system. The ICS was placed in manual and efforts were made to dampen the MFW oscillations. The Operators manually tripped the reactor from approximately 43% power when it became evident that an automatic reactor trip was imminent, based on the observed Reactor Coolant System (RCS) (AB) pressure rise caused by the significant reduction in MFW flow.<br /><br /> The direct cause of the manual plant trip is currently considered a result of placing the "B" startup valve in HAND (manual) when the valve was -36% open, which resulted in a significant underfeed condition of the "B" Once-Through Steam Generator (OTSG). There are currently two root causes considered for this condition: (1) inadequate maintenance practices applied to the ICS modules, and (2) inadequate procedural guidance to address ICS malfunctions.
3152015001 | Cook 1 | 06/01/2015 | 07/29/2015 | ML15211A50 | <strong>Plant Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2015, at 0231 hours, a Unit 1 shutdown was completed in accordance with Technical Specification (TS) 3.8.1, AC Sources - Operating, due to the inability to restore 1 AB Emergency Diesel Generator (EDG) to operable status within the required TS completion time. The plant entered normal operating procedures for a planned Unit 1 shutdown and all systems responded as expected with no complications.<br /><br /> The Unit 1 AB EDG was declared inoperable on May 18, 2015, for scheduled maintenance. During a post maintenance test run, the Unit 1 AB EDG tripped after approximately 16 minutes on HI-HI bearing temperature due to a crankshaft bearing No. 4 failure. <br /><br /> The Root Cause has been determined to be that the station accepted leaving air within the lube oil system which left the EDG main bearing No. 4 susceptible to electrical pitting and eventual wiping of the babbitt material. <br /><br /> Corrective actions to preclude repetition include installing high point vent valves and implementing procedure enhancements to ensure the lube oil system is filled with oil and properly vented prior to returning to service, if drained for any reason. <br /><br /> The Unit 1 planned shutdown was reported via Event Notification 51106 in accordance with 10 CFR 50.72(b)(2)(i). The completion of the plant shutdown required by TS is reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(i)(A).
3152015002 | Cook 1 | 06/14/2015 | 03/31/2016 | ML16096A33 | <strong>Technical Specification Violation due to Inoperable Residual. Heat Removal Pump</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2015, Donald C. Cook Nuclear Plant operations personnel identified an oil leak from the Unit 1 East Residual Heat Removal (RHR) pump (Train A) lower motor bearing oil reservoir. An engineering evaluation concluded that the leak rate would preclude the pump from meeting its 30-day mission time during accident conditions, thus rendering the Unit 1 East RHR pump inoperable. Review of oil addition logs concluded that this condition has existed, but was not recognized as such, since March 9, 2015. This exceeds the 72 hours allowed by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.2, Condition A and is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). <br /><br /> Concurrent with the Unit 1 East RHR pump (train A) inoperability while in Mode 1, the Unit 1 AB Emergency Diesel Generator (EDG) (Train B) was inoperable for a scheduled maintenance window commencing May 18, 2015, and ending with a TS required shutdown due to EDG failure. The inoperable AB EDG required the Unit 1 West RHR pump to be declared inoperable in accordance with LCO 3.8.1, Condition B.3 - "Declare required feature(s) supported by the inoperable DG inoperable when its required redundant feature(s) is inoperable." The Unit 1 West RHR Pump was not declared inoperable within four hours as required by TS LCO 3.8.1, Condition B.3. The Unit 1 West RHR pump should have been declared inoperable in accordance with TS LCO 3.8.1 Condition B.3 on three occasions while the Unit 1 AB EDG was inoperable for more than four hours during surveillance testing. Additionally, there were instances of inoperability in the Emergency Core Cooling System (ECCS) Train B constituting a "Loss of Safety Function" and is reportable in accordance with 10 CFR 50.73(a)(2)(v). <br /><br /> The RHR pump oil leak and the EDG have been repaired and are operable. The apparent cause has been determined that Station leadership was not equipped with a consistent methodology to effectively manage risk associated with various station activities that possessed apparent low probability of occurrence. Corrective actions to preclude repetition include enhancements to equipment monitoring and oil level management. Additionally, risk process management improvements were implemented, and a change management plan created to ensure that the correct questioning attitude is taking place during key station meetings.
3152015003 | Cook 1 | 06/18/2015 | 08/12/2015 | ML15225A46 | <strong>Main Feed Pump Technical Specification 3.3.2 Violation</strong><br /><i>Abstract:&nbsp;</i>On June 18, 2015, a review based on U. S. Nuclear Regulatory Commission (NRC) Information Notice (IN) 2015-05, "Inoperability of Auxiliary and Emergency Feedwater Auto-Start Circuits on Loss of Main Feedwater," identified that Unit 1 is susceptible to the subject of the IN. Limiting Condition for Operation (LCO) 3.3.2, "Engineered Safety Feature Actuation System (ESFAS) Instrumentation," does not have a Condition with a provision for two required channels to be inoperable at the same time, which is the case for normal startup and shutdown of the Unit 1 Main Feedwater (MFW) pumps and some types of maintenance and testing.<br /><br /> An evaluation concluded that the Unit 1 MFW system has been operated in a manner such that the automatic initiation of Auxiliary Feedwater on loss of all MFW pumps was disabled on multiple occasions over the past three years. This is contrary to U1 LCO 3.3.2, requirements. <br /><br /> This condition is a legacy discrepancy between Unit 1 Technical Specifications (TS) and the Unit 1 MFW pump design existing since the initial operation of Unit 1.<br /><br /> To correct this condition, the NRC has approved an amendment to Unit 1 LCO 3.3.2 which aligns the plant design and TS requirements.
3152015004 | Cook 1, Cook 2 | 08/26/2015 | 10/23/2015 | ML15300A05 | <strong>Power Operated Relief Valve Technical Specification 3.4.11 Violation</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2015, during a self-assessment, it was identified that a Pressurizer Power Operated Relief Valve (PORV) would be rendered inoperable if its associated Control Air Compressor (CAC) is unavailable. <br /><br /> One of the three PORVs is not provided with a source of back up air. Therefore, when considering a dual unit LOOP concurrent with the unavailability of the CAC, it was recognized that the associated PORV should be considered inoperable. <br /><br /> An evaluation concluded that the Unit 1 and Unit 2 CACs were not available when removed from service for maintenance on multiple occasions over the past three years. Further review concluded that Unit 1 and Unit 2 LCO 3.4.11, conditions B and H were not entered and the associated action requirements were not met for each occasion. Therefore, this event is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B). <br /><br /> To correct this condition, procedures for removing CACs from service are being revised to add a precaution to declare the affected PORV inoperable while the CAC is unavailable.
3162015001 | Cook 2 | 04/23/2015 | 01/15/2016 | ML16020A45 | <strong>Manual Reactor Trip due to a Secondary Plant Transient</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2015, at 0210, Donald C. Cook Nuclear Plant Unit 2 Reactor was manually tripped from approximately 2 percent of rated thermal power during plant restart following a refueling outage. Unit 2 Reactor was manually tripped due to the inability to maintain Average Reactor Coolant System Temperature above the Technical Specification (TS) required minimum Temperature for Criticality when two newly installed Steam Dump Valves failed open while being manually valved into service. The valves were subjected to, but not designed for, two phase flow. <br /><br /> The Root Cause has been determined to be that the modification process failed to identify and document all system operational vulnerabilities. The corrective action to preclude repetition is an enhancement of the Engineering Modifications procedure to require development and inclusion of a narrative to describe system operation, including key interfacing system operation. <br /><br /> The manual Reactor Protection System (RPS) actuation was reported via Event Notification 51004 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), and 10 CFR 50.72(b)(2)(i). The valid RPS actuation and the completion of the plant shutdown required by TS are reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(2)(i)(A) respectively.
3172015001 | Calvert Cliffs 1, Calvert Cliffs 2 | 01/22/2015 | 03/20/2015 | ML15084A00 | <strong>Component Cooling and Shutdown Heat Exchanger Lineup Potential to Exceed Design Basis Temperatures</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2015, it was determined that a certain line-up of component cooling and shutdown cooling heat exchangers could exceed the design basis outlet temperatures for the component cooling water (CCW) system following a design basis accident. Although not a safety concern at the time of discovery because of low ultimate heat sink temperatures (which cools CCW), in the past, the ultimate heat sink temperature has been high enough to create this condition. A review of Control Room logs for previous three years identified periods of time where Unit 1 and Unit 2 were in an unanalyzed line-up with the ultimate heat sink temperature greater than the maximum allowed. This condition results in both component cooling loops being inoperable due to their cross-connected design. The cause of the event was the failure to evaluate some CCW system testing and maintenance line-ups to ensure consistency with the design assumptions. Corrective actions taken to date include revising several Emergency Operating and Abnormal Operating procedures to provide operator direction, and updating the Technical Specification Bases. Additional evaluation(s) will be performed to further define the operable basis for Component Cooling configurations. The system condition is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B), 50.73(a)(2)(i)(B), 50.73(a)(2)(v)(D), and 50.73(a)(2)(vii).
3172015002 | Calvert Cliffs 1, Calvert Cliffs 2 | 04/07/2015 | 06/05/2015 | ML15160A32 | <strong>Calvert Cliffs Unit 1 and Unit 2 Automatic Reactor Trips due to Transmission System Disturbance</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2015 at 1239 Calvert Cliffs experienced a dual unit trip due to an off-site grid disturbance resulting in an undervoltage condition that caused all four Engineered Safety Features (ESF) Buses to trip. Due to this condition, all of the emergency diesel generators (EDGs) started and loaded with the exception of 2B EDG which started but tripped due to a failed electronic speed switch in the startup circuitry. The associated 4 kV ESF bus was repowered from the normal power source. Additionally, while 2A EDG energized its respective 4 kV ESF bus, the associated shutdown sequencer failed to start 21 Saltwater pump which was subsequently manually started. Unit 1 tripped on loss of all power to generator excitation and all required safety systems responded as designed. Unit 2 tripped due to generator loss of load and is classified as an unplanned scram with complications as 24 4 kV ESF bus was de-energized for greater than 10 minutes. The failed 2B EDG speed switch and 2A EDG shutdown sequencer were replaced and tested satisfactorily. Future corrective actions include to design and implement a speed switch modification to eliminate the single-point failure risk, and to procure and install a newly manufactured sequencer in each channel.
3172015003 | Calvert Cliffs 1, Calvert Cliffs 2 | 06/17/2015 | 11/09/2015 | ML15317A00 | <strong>Diesel Generator Inoperable due to Lube Oil Filter Fouling due to Coolant Leakby on a Cylinder Liner</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2015 during 1A diesel generator (DG) Surveillance testing, the 1A2 "lube oil differential pressure high" alarm annunciated on both sides of the engine (side A and side B) shortly after DG start. The DG was shut down and declared inoperable. The cause of the alarms was a leaking cylinder liner which allowed coolant (glycol) to contaminate the lube oil and foul the lube oil filters. The cause of the cylinder leak was determined to be damaged O rings on the leaking cylinder. The damaged O rings were replaced and the 1A DG was satisfactorily tested and returned to Operable status on June 22, 2015. To address the apparent cause of the degraded O rings, a process to ensure O rings are stored flat to prevent twists was implemented. Because the 1A DG was determined to be inoperable for 32 days, the Required Action Completion Times of Technical Specification 3.8.1.B, C, E, F, and J were not met and this event is reportable as an operation or condition prohibited by Technical Specifications. This event is also reportable as an event or condition that could have prevented fulfilment of a safety function, because the inoperability of the second Unit 1 DG for 24 minutes resulted in a loss of safety function for emergency power on Unit 1, and the inoperability of the Unit 2 2B DG for 8 minutes resulted in a loss of safety function for the emergency power to the Control Room ventilation system for Units 1 and 2.
3182015001 | Calvert Cliffs 2 | 12/01/2015 | 03/28/2016 | ML16090A12 | <strong>Manual Reactor Trip due to 22 Steam Generator Feed Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2015 at 1820, Unit 2 turbine driven 22 Steam Generator Feed Pump (SGFP) tripped. Operations attempted to reset 22 SGFP unsuccessfully. Facing lowering steam generator water level, Operations manually initiated a reactor trip. It was determined that 22 SGFP tripped due to a failed coupling. This occurred because excessive misalignment developed between the pump and turbine due to insufficient tensioning of the pump's casing to pedestal studs thus causing 22 SGFP coupling to fail. Investigation determined that the vender supplied stud tensioning values used in tensioning the hold down studs on both Unit 2 SGFPs during the 2015 refueling outage were incorrect and resulted in insufficient clamping force being applied to all the studs. The root cause of the failure was that Engineering personnel failed to address the full scope and critical parameters associated with use of a different tool for installation of studs in lieu of capscrews for 22 SGFP. The coupling for 22 SGFP was replaced and 22 SGFP was realigned. Corrected tensioning values were then applied to all the hold down studs on 21 and 22 SGFPs. Corrective actions include briefings to applicable groups on adherence to procedure requirements for owner's acceptance review of external technical products. Unit 2 was returned to Mode 1 operations at 1326 on December 6, 2015.
3212015002 | Hatch 1 | 01/20/2015 | 09/03/2015 | ML15246A53 | <strong>1A Plant Service Water Pump Misalignment Results in a Condition Prohibited by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2015 it was observed that the 1A Plant Service Water (PSW) Pump was exhibiting unusually high vibrations. The 1A PSW pump was declared inoperable and the 1C PSW pump was placed in service. The cause of the 1A PSW pump high vibrations was due to pump shaft misalignment as a result of inadequate procedural guidance. It was identified that during a work order that rebuilt and replaced the 1A PSW pump in 2010, the seismic restraints were installed offset from the centerline of the pump. The pump column therefore had to be pressed and bridged over in order to appropriately fit the restraints. In this configuration, considerable loads were applied to both the upper and lower restraints causing the supports to eventually break. <br /><br /> It was determined that the 1A PSW pump would not have been able to meet its 30 day mission time based on the broken seismic restraints and the excessive vibration levels found on the pump. If a design basis seismic event would have occurred such that the seismic restraints on the pump would have broken, this would have left the 1A PSW pump unsupported. The pump would therefore not have been able to operate at these elevated vibrations for more than 24 hours. The 1A PSW pump was replaced and maintenance procedures were revised to ensure that the restraints are maintained in the proper configuration whenever future maintenance is performed.
3242015001 | Brunswick 2 | 02/26/2015 | 04/24/2015 | ML15127A16 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 2</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2015, Unit 2 implemented the guidance of EGM 11-003, Revision 2, "Enforcement Guidance Memorandum on Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements During Operations with a Potential for Draining the Reactor Vessel," dated December 13, 2013. Consistent with EGM 11-003, Revision 2, secondary containment operability was not maintained during Operations with a Potential for Draining the Reactor Vessel (OPDRV) activities, and Required Actions C.1 and C.2 of Technical Specification (TS) 3.6.4.1, "Secondary Containment," were not completed. EGM 11-003, Revision 2, was implemented four additional times during the 2015, Unit 2 refueling outage. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by the plant's TSs.<br /><br /> Implementation of EGM 11-003, Revision 2, during the Unit 2 refueling outage was a planned activity. As such, there was no root cause evaluation of the event. Consistent with the guidance provided in EGM 11-003, Revision 2, BSEP will submit a license amendment request to adopt a Technical Specification Task Force (TSTF) traveler associated with generic resolution of this issue within 12 months after the issuance of the Notice of Availability of the TSTF traveler.
3242015002 | Brunswick 2 | 03/10/2015 | 06/26/2015 | ML15196A03 | <strong>Setpoint Drift in Main Steam Line Safety/Relief Valves Results in Three Valves Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2015, BSEP received the results of testing of eleven main steam line safety relief valves (SRVs) removed from Unit 2 during the spring Unit 2 refueling outage. Three of the eleven valves were found to have as-found lift setpoints of their pilot valves outside the +/-3 percent tolerance required by Technical Specification (TS) 3.4.3. One SRV was 3.2 percent high; one SRV was 3.6 percent high, and one SRV was 4.0 percent low. Elevated lift pressures resulted from micro-cracking remaining on the pilot disc surface which allowed a localized region of the platinum coating to degrade, resulting in slight corrosion bonding which raised the breakaway force needed to open the pilot. No cause was identified for the one SRV having a reduced lift setpoint. This event had no adverse impact on nuclear safety. Although the SRV setpoint limits required by the TS were exceeded, the plant condition was bounded by the Brunswick Unit 2 Cycle 21 Reload Safety Analysis, demonstrating that the SRVs could have performed their safety function of limiting reactor vessel overpressure. TS 3.4.3 requires ten of the eleven installed SRVs to be operable. Since only eight SRVs were operable, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation prohibited by the plant's TS. The SRV pilot valves were replaced with certified spares before the startup of Unit 2. A maintenance procedure will be revised, and a different base metal for the pilot valve will be assessed.
3242015003 | Brunswick 2 | 04/08/2015 | 08/05/2015 | ML15233A02 | <strong>Oil Leak Renders Residual Heat Removal Service Water System Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2015, at 1639 Eastern Daylight Time (EDT), licensed personnel were informed that oil leakage on the motor for Residual Heat Removal Service Water (RHRSW) system pump 2C exceeded the amount that would be acceptable in order for the pump to meet its 30-day mission time. Event investigators found that sealant had not been applied to mechanical joints in the bearing housings on the horizontal motor, resulting in oil leaking through the unsealed joints. Based on the historical rate of oil additions, engineering personnel concluded that the bearings would not have been able to operate throughout their full mission time, and licensed personnel declared the 2C RHRSW pump inoperable on that basis. The condition resulted in a failure to comply with Technical Specification (TS) 3.7.1, "Residual Heat Removal Service Water (RHRSW)," and with TS Limiting Condition for Operation (LCO) 3.0.4, and also resulted in a loss of the safety function. The direct cause of this event was lack of sealant in mechanical joints of the bearing housings. The root cause was that the process for identifying and updating maintenance procedures impacted by a safety related engineering change was less than adequate, and a contributing cause was a lack of questioning attitude. Corrective actions for this event included applying sealant to the bearing housings, revising procedures to address safety related engineering changes, and discussing the event with appropriate maintenance personnel.
3252015001 | Brunswick 1 | 02/12/2015 | 12/21/2015 | ML16015A08 | <strong>High Pressure Coolant Injection (HPCI) System Inoperable due to Auxiliary Oil Pump Failure</strong><br /><i>Abstract:&nbsp;</i>At 1336 Eastern Standard Time (EST) on February 12, 2015, the Unit 1 High Pressure Coolant Injection (HPCI) System was declared inoperable due to a failure of the HPCI auxiliary oil pump. During performance of a HPCI weekly inspection, the auxiliary oil pump was started and subsequently stopped running unexpectedly. The HPCI auxiliary oil pump provides hydraulic pressure required to open the HPCI turbine stop valve and the HPCI turbine control valve during initial HPCI startup. Failure of the HPCI auxiliary oil pump prevents the HPCI system from performing its design safety function. <br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. <br /><br /> The cause of the HPCI inoperability was a faulty magnetic motor contactor coil (i.e., M-coil) within the HPCI turbine auxiliary oil pump motor contactor 1-1XDA-B11-M. The failure of the coil was determined to be most likely long term thermal cycling. The coil was replaced, and the HPCI system was returned to operable status on February 20, 2015.
3252015002 | Brunswick 1, Brunswick 2 | 03/21/2015 | 11/16/2015 | ML15329A37 | <strong>Emergency Diesel Generator Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2015, following an engineering evaluation, it was determined that during a period of 12 minutes from 14:05 to 14:17 Eastern Daylight Time on March 21, 2015, emergency diesel generators (EDGs) 3 and 4 could potentially have been unable to tie to their respective emergency busses. This was due to relays in breaker control logic that were susceptible to electrical noise from nearby relays de-energizing that could have prevented the output breakers from properly closing under certain conditions. This is considered a loss of safety function of the onsite standby alternating current power source. Three of four EDGs are required to mitigate an accident on one unit while maintaining the other unit in a safe condition. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The root cause of the event was a procedural inadequacy in the commercial grade dedication process that allowed an unauthorized component modification to go unrecognized. Affected circuits in all four EDGs have been modified. The inadequate procedure has been revised, and site management and key personnel will be briefed on lessons learned from the event.
3272015001 | Sequoyah 1 | 03/11/2015 | 11/24/2015 | ML15335A06 | <strong>Automatic Reactor Trip due to Negative Rate Trip as a Result of a Dropped Control Rod</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2015, at 0621 Eastern Daylight Time Sequoyah Nuclear Plant Unit 1 reactor automatically tripped due to a Negative Rate Trip as a result of Control Bank D Control Rod H-8 dropping into the core. Initial investigation revealed Control Rod H-8 dropped into the core approximately one second before the reactor trip. The dropped control rod caused a rapid decrease in power which was sensed by all four nuclear instrumentation system power range channels. Reactor trip logic is two out of four channels. No power changes or control rod motion were in progress prior to the reactor trip. All safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated as expected. Unit 1 was stabilized in hot standby following the automatic reactor trip. The cause of the reactor trip was due to Control Rod H-8 failing to maintain its commanded position. Trouble shooting was performed on the electrical components associated with Control Rod H-8. The direct cause was a compressed four-pronged pin inside a connector for the control rod drive mechanism (CRDM) circuit. The root cause was failure of a maintenance procedure to provide inspection guidance and acceptance criteria on CRDM vertical panel connections. The corrective action to prevent recurrence includes revising the maintenance procedure and periodic preventive maintenance of CRDM connections. Unit 2 was unaffected by this event.
3272015002 | Sequoyah 1 | 07/24/2015 | 09/22/2015 | ML15268A08 | <strong>Automatic Reactor Trips due to Improper Wire Termination in Main Generator Voltage Regulator Circuit</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2015, at 1351 Eastern Daylight Time (EDT), Sequoyah Nuclear Plant (SQN) Unit 1 reactor automatically tripped following a turbine trip due to actuation of the generator backup relay. The relay actuation was a result of voltage variations on the main generator. A malfunctioning base adjuster follower card was identified on the main generator voltage regulator. After replacement of the base adjuster circuit card, Unit 1 was connected to the grid and ascending in power. On July 27, 2015, at 1040 EDT SQN Unit 1 reactor was at 82 percent power when it automatically tripped following a turbine trip due to actuation of the generator backup relay. An improperly terminated wire was found in the voltage regulator logic drawer which caused high resistance. Prior to restart, the wire was properly connected. Following each of the reactor trips, all safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated from the feedwater isolation signal as expected. The cause of each of the reactor trips was determined to be inadequate standards for multi-wire terminations and verification at the time of the original improper wire termination event in the mid-1990s. Corrective actions to prevent recurrence include adding guidance for multi-wire terminations to Modifications and Additions Instruction M&AI-7.1, Cable Terminations and Repairing Damaged Cables. The condition described in this LER did not have an impact on SQN Unit 2.
3272015003 | Sequoyah 1 | 09/14/2015 | 11/13/2015 | ML15322A05 | <strong>Manual Reactor Trip due to Loss of Power to the Vital Instrument Power Board 1-II</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2015, at 0426 Eastern Daylight Time, Sequoyah Nuclear Plant (SQN) Unit 1 reactor was manually tripped due to a loss of power to the Vital Instrument Power Board (VIPB) 1-II. Prior to the reactor trip, operators were in the process of realigning Vital Inverter 1-II for planned maintenance. During this evolution, VIPB 1-II became de-energized. Operators entered Abnormal Operating Procedure AOP-P.03, "Loss of Unit 1 Vital Instrument Power Board" which required a manual reactor trip. Following the reactor trip, operators restored power to VIPB 1-Il with the normal supply at 0550. All plant safety systems responded as designed, all control rods fully inserted, and auxiliary feedwater automatically initiated from the feedwater isolation signal as expected. It was determined that an Alternating Current (AC) output switch failed causing the loss of power to the VIPB 1-II. The direct cause of the switch failure was due to increased friction of bearing surfaces caused by lack of appropriate lubrication. The lack of lubrication was related to a failure to implement a corrective action following an operating experience review at SQN in 2000 of a similar event at McGuire Nuclear Station. The failure to implement a corrective action was determined to be the root cause of this event. Corrective actions to prevent recurrence include ensuring the existing requirement for management review of all corrective action closures remains in the Corrective Action Program. Unit 2 was unaffected by this event.
3272015004 | Sequoyah 1 | 11/23/2015 | 03/09/2016 | ML16074A39 | <strong>Manual Reactor Trip due to Main Steam Isolation Valve Drifting in the Closed Direction</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2015, at 0844 Eastern Standard Time, Sequoyah Nuclear Plant (SQN) Unit 1 reactor was manually tripped due to plant parameters indicating that the Loop 3 Main Steam Isolation Valve (MSIV) had started drifting in the closed direction. Prior to the reactor trip, the open light indication on the main control board for the Loop 3 MSIV was noted to be extinguished. The light bulb was replaced with no change in indication. At the same time, the Post Accident Monitoring panel indicator for the Loop 3 MSIV displayed full open; however, within two to three minutes, the panel provided dual indication. Subsequently, Operators noted that the reactor coolant system temperature and Loop 3 Steam Generator (SG) pressure were both rising, and the Loop 3 SG flow was lowering. These indications confirmed the Loop 3 MSIV was drifting closed. Following the reactor trip, all plant safety systems operated as designed, all control rods fully inserted, and auxiliary feedwater automatically initiated from the feedwater isolation signal, as expected. Troubleshooting identified a loose termination associated with the Loop 3 MSIV handswitch that would result in a slow loss of air pressure and cause the MSIV to slowly drift in the closed direction. The direct cause was determined to be a loose electrical connection on the MSIV handswitch. The root cause was determined to be inadequate work practices during replacement of the MSIV handswitch in 1994 that resulted in the loose electrical connection. The corrective action to prevent recurrence is revision of the work control planning procedure to ensure specific connection fastener torque values are utilized during work order planning. SQN Unit 2 was unaffected by this event.
3282015001 | Sequoyah 2 | 03/02/2015 | 05/01/2015 | ML15126A27 | <strong>Automatic Reactor Trip due to Failure of Main Generator C-phase Neutral Current Transformer Cable</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2015, at 0645 Eastern Standard Time, Sequoyah Nuclear Plant (SQN) Unit 2 reactor automatically tripped following a turbine trip due to actuation of the main generator 287G differential relay. The relay actuation was a result of a failure of the main generator C-phase neutral current transformer (CT) cable. All safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated from the feedwater isolation signal as expected. A broken splice connection was identified between the 287G differential relay and the C-phase CT. This main generator C-phase neutral CT cable failed open due to a combination of corrosion and periodic physical manipulation. The cause of this event was a lack of inspections in the preventive maintenance (PM) procedure to identify potential failure mechanisms. Prior to restart, both Unit 2 C-phase neutral CTs and one B-phase neutral CT along with all associated neutral side field cables were replaced. Corrective actions to prevent recurrence include replacement of all Unit 1 and Unit 2 main generator CT bolted connections with solder filled splices, covered in Raychem to prevent water intrusion. The condition described in this LER did not have an impact to SQN Unit 1.
3282015002 | Sequoyah 2 | 11/10/2015 | 01/06/2016 | ML16008A96 | <strong>Unanalyzed Condition due to Inoperable Containment Recirculation Drains</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2015, at 1502 Eastern Standard Time (EST), two cold weather suits were inadvertently dropped into the equipment pit portion of the Sequoyah Nuclear Plant Unit 2 reactor cavity, resulting in two containment recirculation drains being declared inoperable. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.15, "Containment Recirculation Drains," and TS LCO 3.0.3 were entered. The first suit was removed from the equipment pit at 1553 EST. At that time, only one of the drains remained inoperable and LCO 3.0.3 was exited. The remaining suit was removed from the equipment pit at 1556 EST, and LCO 3.6.15 was exited. Plant conditions were restored to normal within the allowed LCO times and no plant shutdown was required. The two cold weather suits in the Unit 2 reactor cavity area created the potential for obstructing the flow path for containment recirculation adversely affecting the safety function of the Containment Spray and Emergency Core Cooling Systems that are needed to mitigate the consequences of a design basis accident. The effect of this condition resulted in an unanalyzed condition that significantly degraded plant safety. The apparent cause was failure of the Maintenance personnel to identify and mitigate potential hazards and risks during the pre-job briefs, 2-minute rule, and walk downs. Corrective action includes addition of risk mitigation strategies to the containment access control procedure. Unit 1 was unaffected by this event.
3312015001 | Duane Arnold | 03/21/2015 | 06/25/2015 | ML15181A33 | <strong>Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2015, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference EN#50914).<br /><br /> Following the event, the doors were verified to be functioning properly and no deficiencies were noted on either door. A Root Cause Evaluation was conducted and determined the root cause of this event is that the airlock door interlock is not designed to prevent more than one airlock door from opening under all possible conditions. <br /><br /> This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312015002 | Duane Arnold | 03/31/2015 | 01/28/2016 | ML16034A21 | <strong>Unanalyzed Condition due to Degraded Primary Containment Suppression Pool Coating</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2015, while operating at 100% power, with no structures, systems, or components inoperable, an unanalyzed condition regarding the primary containment suppression pool coating was identified. Specifically, during an inspection of suppression pool (torus) during the October 2014 refueling outage, degradation of the torus coating was discovered. Some of the coating had become delaminated. NextEra Energy Duane Arnold took immediate action to restore the coating to within design parameters during the refueling outage and the degraded condition no longer exists. Extensive analysis was performed to determine effect of the delaminated material. Upon completion of this investigation, it was determined that an unanalyzed condition, a condition prohibited by Technical Specifications, an event or condition that could have prevented fulfillment of a safety function and common cause inoperability existed and is reporting the condition under various sections of 10 CFR 50.73. The root causes of this event were less than adequate coating application specification and work instructions and less than adequate project oversight and control.
3312015003 | Duane Arnold | 04/16/2015 | 06/25/2015 | ML15181A33 | <strong>Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2015, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference EN#50989). <br /><br /> Following the event, the doors were verified to be functioning properly via Surveillance Test Procedure. A Root Cause Evaluation was conducted and determined the root cause of this event is that the airlock door interlock is not designed to prevent more than one airlock door from opening under all possible conditions. <br /><br /> This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312015004 | Duane Arnold | 08/27/2015 | 10/06/2015 | ML15286A05 | <strong>Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2015, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability, of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference EN#52353). <br /><br /> Following the event, the doors were verified to be functioning properly via Surveillance Test Procedure. A Root Cause Evaluation was conducted in May 2015 which determined the root cause of this event is that the airlock door interlock is not designed to prevent more than one airlock door from opening under all possible conditions. <br /><br /> This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312015005 | Duane Arnold | 10/20/2015 | 12/16/2015 | ML15352A03 | <strong>Automatic Start of Both Emergency Diesel Generators due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2015 at 1800, while operating at 100% power, a voltage transient due to a lightning strike resulted in an automatic start of both of the site's Emergency Diesel Generators (EDGs) (IEE Code EK). Neither EDG loaded onto its respective essential bus, as offsite power remained available. The 'A' EDG was secured at 1930 on October 20, 2015. The 'B' EDG was secured at 1947 on October 20, 2015. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and Event Notification Number 51484 was made pursuant to 10 CFR 50.72(b)(3)(iv)(A) due to a valid system actuation. <br /><br /> The apparent cause of the starting of both EDGs was a storm-induced voltage dip (fault). This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312015006 | Duane Arnold | 07/23/2015 | 02/18/2016 | ML16054A80 | <strong>HPCI and RCIC Condensate Storage Tank Suction Transfer Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 23, 2015, while operating at 100% power, with no structures, systems, or components inoperable that contributed to this event, during the performance of Surveillance Test Procedure (STP) 3.5.3-05, RCIC/HPCI Suction Transfer Interlock, the Condensate Storage Tank (CST) Low Level HPCI and RCIC Suction Swap Relay, E41A-K059, as-found time to trip was 19.86 seconds. This was outside the relay design band of 0.0-5.0 seconds. This condition resulted in the HPCl/RCIC CST suction swap function being inoperable. Technical Specification (TS) require HPCI and RCIC to be declared inoperable within 1 hour from the discovery of the inoperable support feature. HPCI and RCIC were not declared inoperable and therefore, this condition meets the reporting requirements of 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(A) and (D).
3332015001 | FitzPatrick | 04/30/2015 | 06/29/2015 | ML15180A20 | <strong>COLR Thermal Limits Exceeded With Elevated Fuel Support Piece</strong><br /><i>Abstract:&nbsp;</i>In February 2015 it was identified that the fuel support piece associated with fuel cell 38-39 was slightly elevated and offset. As a result of the elevation and offset the four fuel assemblies in the affected fuel cell have reduced coolant flow; this has a direct effect on the Minimum Critical Power Ratio (MCPR). On April 30, 2015, an analysis of operating conditions by General Electric Hitachi (GEH) and accepted by the station confirmed that during periods of reduced reactor flow in October 2014 MCPR exceeded limits set by Technical Specification (TS). Since it was exceeded for longer than allowed by TS 3.2.2 this event is reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The fuel support piece became elevated during last refueling outage (September 2014). An interim corrective action to manually correct MCPR ensures the TS limit is not exceeded. The exceedance of the TS limit for MCPR was modified until the analysis was done since the core monitoring program assumes that the fuel support piece is in its normal seated configuration, with normal flow characteristics through the fuel assemblies. <br /><br /> Although the Limiting Condition of Operation was not met, the analysis performed by GEH confirmed compliance with Safety Limit MCPR under all evaluated transient scenarios such that at no time was the most limiting Safety Limit MCPR set by TS 2.1.1.2 challenged.
3332015002 | FitzPatrick | 06/01/2015 | 07/30/2015 | ML15212A27 | <strong>Safety Relief Valve Upward Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>The As-Found test results for the eleven Safety / Relief Valve (S/RV) pilot assemblies removed and replaced during the 2014 Refueling Outage at James A. FitzPatrick Nuclear Power Plant (JAF) identified seven (7) S/RV pilot assemblies that lifted at greater than the allowable tolerance of 1145 psig +/- 3% as required by Technical Specification Surveillance Requirement 3.4.3.1. Due to the recurring nature of these failures, the seven S/RV pilot assemblies are assumed to have been inoperable at some point in the operating cycle that preceded the 2014 Refueling Outage resulting in a condition reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The S/RV design features an electric actuation capability that provides a diversified means of opening the S/RV’s despite the upward setpoint drift. However, the electric lift function is considered a backup to the mechanical S/RV’s and is not credited in the safety analyses. Therefore, the Technical Specification inoperability of the seven (7) S/RV’s also resulted in a condition reportable pursuant to 10 CFR 50.73(a)(2)(v)(D). <br /><br /> The safety consequences associated with this event are considered low due to the electric actuation capability (verified functional for the entire operating cycle), and the expected pressure response relative to the As-Found setpoints of all eleven S/RV pilots.
3332015003 | FitzPatrick | 07/20/2015 | 09/18/2015 | ML15261A51 | <strong>Roof Maintenance Results in Secondary Containment Vacuum Below Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On the morning of July 20, 2015 at 0740 EDT, with the James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100 percent power, the differential pressure (D/P) of the Reactor Building (relative to atmosphere) decreased, resulting in a Technical Specification (TS) surveillance requirement for the Secondary Containment vacuum not being met (>/= 0.25 inches of vacuum water gauge). The decrease in D/P was caused by the opening of the Reactor Building roof envelope during roof replacement activities. The condition of D/P being less negative than 0.25 inches of vacuum water gauge existed for approximately 92 minutes. <br /><br /> When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure, the TS Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was Inoperable. Restoration of the LCO was completed after secondary containment was declared Operable / Degraded. This report is being submitted per 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of safety function to control the release of radioactive material.
3332015004 | FitzPatrick | 09/17/2015 | 11/06/2015 | ML15314A80 | <strong>Concurrent Opening of Reactor Building Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On the morning of September 17, 2015, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment. <br /><br /> This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference ENS 51405). Following the event, the doors functioned properly, and no deficiencies were noted with either door. <br /><br /> There were no radiological releases associated with this event.
3332015005 | FitzPatrick | 09/18/2015 | 11/17/2015 | ML15321A44 | <strong>Damper Failure Leads to Secondary Containment Vacuum Below Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 1408 on September 18, 2015, James A. FitzPatrick Nuclear Power Plant (JAF) was operating at 100 percent power when differential pressure of the Secondary Containment Reactor Building exceeded a Technical Specification requirement. The requirement is for the Secondary Containment to have a >/= 0.25 inch of vacuum water gauge compared to the external environment. During this event, Reactor Building differential pressure decreased below 0.25 inch of vacuum water gauge for approximately 3 minutes. This event was caused by the Refuel Floor Exhaust fan 'A' discharge damper 66AOD-106A going partially closed with concurrent failure of the associated fan discharge damper position indicating switch 66PNS-106A1. This resulted in obstructing exhaust flow from the Reactor Building. To correct the condition the standby exhaust fan was placed in service. <br /><br /> When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure, the Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was Inoperable. Restoration of the LCO was completed within the allowed action completion time. This report is being submitted per 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of safety function to control the release of radioactive material.
3332015006 | FitzPatrick | 09/22/2015 | 02/04/2016 | ML16035A44 | <strong>Transitory Secondary Containment Differential Pressure Excursions</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2015 at 17:03, with James A. FitzPatrick Nuclear Power Plant operating at 100 percent power, the Emergency and Plant Information Computer (EPIC) indicated a spike in Secondary Containment (SC) differential pressure (d/P) during performance of a surveillance test associated with automatic isolation of SC and initiation of the Standby Gas Treatment System. Per the plant data systems SC d/P exceeded the Technical Specification (TS) allowed value, and then immediately trended negative following auto-start of one of the trains of Standby Gas Treatment. <br /><br /> The time period that SC d/P was greater than the TS allowed value is reportable pursuant to 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.73(a)(2)(v)(C), as an event or condition that could have prevented fulfillment of a safety function.<br /><br /> SC was operable following reestablishment of greater than or equal to 0.25 inches of water vacuum, and remains operable. SC d/P excursions during transition from normal to isolation mode of the Reactor Building Ventilation (RBV) System are an expected condition, and attributable to the design of the non-safety related RBV System. The cause of the SC d/P exceeding the TS allowed value has been determined not to be associated with a component failure or equipment malfunction. Similar reportable events were identified during preparation of this report. A comprehensive listing of these occurrences is included in the report.
3332015007 | FitzPatrick | 12/01/2015 | 02/01/2016 | ML16032A22 | <strong>Slow Exhaust Fan Start Leads to Secondary Containment Vacuum Below Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 2036 on December 1, 2015, James A. FitzPatrick Nuclear Power Plant (JAF) was operating at 100 percent power when differential pressure of the Secondary Containment exceeded a Technical Specification requirement. The requirement is for the Secondary Containment to have a >/= 0.25 inches of vacuum water gauge compared to the external environment. <br /><br /> This event was caused by hardened grease in the operating mechanism of the motor starter contactor 71MCC-141-062. This led to a slow start of the above refuel floor Reactor Building exhaust fan 66FN-13B while the intake air supply fans were running. The exhaust fan started, without Plant Operator action, after approximately 60 seconds; however, Reactor Building differential pressure exceeded 0.25 inches of vacuum water gauge for approximately 80 seconds. <br /><br /> When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure, the Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was Inoperable. Restoration of the LCO was completed within the allowed action completion time. This report is being submitted per 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of safety function to control the release of radioactive material.
3332015008 | FitzPatrick | 12/18/2015 | 02/16/2016 | ML16047A41 | <strong>Containment Atmosphere Dilution System Reliability Degraded due to Manufacturer Defect in Temperature Transmitters</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2015, James A. FitzPatrick Nuclear Power Plant (JAF) was operating at 100 percent power when a 10 CFR 21.21(d)(3)(ii) Notification was received from Nutherm International. It identified a defect in Moore Industries temperature transmitters. Specifically, insulation was damaged in the T2 transformer during assembly which could result in premature failure. <br /><br /> These components were installed starting in June 2015 at 27TT-113A and 27TT-113B in the Containment Atmosphere Dilution (CAD) system. The defect caused failures in July and November which resulted in either the "A" or "B" CAD subsystem isolating. Corrective actions included replacing both temperature transmitters with ones that were confirmed to not contain this defect. <br /><br /> Even though these defective temperature transmitters function appropriately until they fail, this defect reduced the reliability of the CAD system to perform its function for its entire mission time. Therefore, this deficiency resulted in a loss of safety function to mitigate the consequences of an accident, reportable per 10 CFR 50.73(a)(2)(v)(D). Also, a single cause affected the safety function of independent CAD trains, reportable per 10 CFR 50.73(a)(2)(vii)(D); and, this condition existed longer then allowed by Technical Specifications 3.6.3.2, reportable per 10 CFR 50.73(a)(2)(i)(B).
3342015001 | Beaver Valley 1 | 04/15/2015 | 06/11/2015 | ML15166A08 | <strong>Manual Reactor Trip and Automatic Auxiliary Feedwater Actuation due to Condensate Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>At 0411 EDT on April 15, 2015 the Beaver Valley Power Station (BVPS) Unit 1 reactor was manually tripped from approximately 85 percent power following a condensate pump trip. Prior to the manual reactor trip the unit was performing an emergent power reduction after the identification of a degrading condition on the "A" condensate pump motor. All control rods fully inserted into the core. The auxiliary feedwater system actuated as designed. The unit was stabilized in Mode 3 with the normal main feedwater system in service and the auxiliary feedwater system properly secured.<br /><br /> The "A" condensate pump trip was caused by the failure of the inboard motor bearing due to lack of oil lubrication. The root cause evaluation determined that responses to technical questions were provided without the appropriate technical rigor or validation of assumptions regarding acceptable oil level for the pump motor.<br /><br /> This event was reported (EN 50985) as an event or condition that results in the actuation of the reactor protection system when the reactor is critical, 10 CFR 50.72(b)(2)(iv)(B) and specified system actuation, 10 CFR 50.72(b)(2)(iv)(A). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the manual actuation of the Reactor Protection System, 10 CFR 50.73(a)(2)(iv)(B)(1), and the automatic actuation of the Auxiliary Feedwater System 10 CFR 50.73(a)(2)(iv)(B)(6).
3352015001 | St. Lucie 1 | 08/09/2015 | 10/07/2015 | ML15301A25 | <strong>Reactor Trip While Performing Reactor Protection System Logic Matrix Test</strong><br /><i>Abstract:&nbsp;</i>On August 9, 2015 with St. Lucie Unit 1 in Mode 1 at 100% reactor power, an unplanned reactor trip occurred. The trip occurred while Operators were performing a reactor protection system (RPS) logic matrix test in which the individuals performing the test did not follow the procedure steps in sequence resulting in a loss of configuration control. As a result, a set of reactor trip circuit breakers (TCBs) was opened before ensuring that all TCBs tested in the previous test section had been closed.<br /><br /> Corrective actions include procedure revisions to the test methodology to ensure configuration control of the TCBs is maintained through additional verification techniques. <br /><br /> This reactor trip event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the reactor protection system (RPS). This event had no significant safety consequence since the RPS successfully performed its intended safety function upon opening the trip circuit breakers.<br /><br /> This event had no effect on the health and safety of the public.
3362015001 | Millstone 2 | 04/17/2015 | 06/16/2015 | ML15175A19 | <strong>Historical Oil Leakage from "C" RBCCW Pump Bearings Challenged Meeting Mission Time</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2015, with Millstone Power Station Unit 2 (MPS2) at 100% power and in operating MODE 1, the Nuclear Regulatory Commission questioned the historic operability of Millstone Power Station Unit 2's (MPS2) "C" Reactor Building Closed Cooling Water (RBCCW) pump because several condition reports had reported the need to frequently add oil to the pump's outboard bearing bubbler between November 2014 and early April 2015. Upon further review, Dominion concluded that operability could not be assured since there may not have been sufficient oil to meet mission time requirements at all times with no compensatory measures in place. Plant Technical Specification 3.7.3.1 "Reactor Building Closed Cooling Water System" requires two reactor building closed cooling water loops shall be operable. Since there were periods of time that plant operators were crediting the "C" RBCCW pump for one of the two required reactor building closed cooling water loops, and operability could not be assured at all times, Dominion is reporting this event pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition that was prohibited by the plant's Technical Specifications. <br /><br /> The cause of the event was that Administrative procedure OP-AA-102, Operability Determination, Attachment 1 contained guidance that allowed that oil leaks would not require an operability determination under certain conditions. Procedure OP-AA-102 has been revised to specify that any time a pump's mission time cannot be met due to oil leakage, the pump should be declared inoperable.
3362015002 | Millstone 2 | 06/11/2015 | 12/11/2015 | ML15356A20 | <strong>Degraded Emergency Core Cooling System Check Valve</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2015, while Millstone Power Station Unit 2 (MPS2) was in MODE 1 operating at 100 percent power, Engineering identified that due to a degraded check valve, the post-accident radioactivity release rates assumed in the FSAR could be affected. While performing 'B' High Pressure Safety Injection (HPSI) pump in-service testing, the measured flow was lower than expected. Because both trains of HPSI, Low Pressure Safety Injection (LPSI) pumps, and Containment Spray (CS) pumps share a common minimum flow recirculation line back to the Refueling Water Storage Tank, back-leakage through one of the idle pump's recirculation check valves was postulated as the cause of the observed drop in recirculation flow. Troubleshooting was performed, and it was determined that the minimum flow check valve associated with the 'A' CS pump, 2-CS-6A, was back-leaking. The associated minimum flow isolation valve was closed to eliminate the flow path. Back-leakage of the minimum flow recirculation check valves on the HPSI, LPSI, and CS pumps was not previously considered in radiological release analysis. This leakage had the potential to adversely affect calculated post-Loss of Coolant Accident recirculation phase radioactivity release rates under some postulated scenarios. <br /><br /> This event is being reported as an event or condition that could have prevented fulfillment of a safety function to control the release of radioactive material under 10 CFR 50.73(a)(2)(v)(C). The cause of the event was a failed open check valve. As a corrective action, the failed check valve 2-CS-6A has been repaired.
3362015003 | Millstone 2 | 11/08/2015 | 01/07/2016 | ML16020A06 | <strong>Valid Actuation of the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2015 during reactor start-up from refueling outage 2R23 with the reactor in mode 1 at approximately 57.5 percent power the operators received indication of an oil leak on the 'C' reactor coolant pump (RCP) motor lower oil reservoir. The operators monitored the 'C' RCP oil level and bearing temperatures. Upon noting the RCP oil level dropping at a rate of approximately 1.7 percent per hour and the lower RCP guide bearing temperature rising, the operators entered abnormal operating procedure (AOP) 2575, Rapid Downpower, and commenced a rapid downpower. The operators manually tripped the reactor at approximately 19 percent power in accordance with AOP 2575 and entered emergency operating procedures. The reactor trip was uncomplicated. All safety systems operated as designed. <br /><br /> The cause of the valid actuation of the reactor protection system (RPS) was the operators manually tripping the reactor via the manual reactor trip push button switches. The AOP was entered due to an oil leak from the tubing to the level transmitter on the 'C' RCP motor lower oil reservoir. The tubing failure mechanism was determined to be high cyclic fatigue. Repairs were completed, the unit was restarted, and returned to service. Additional corrective actions are being taken in accordance with the station's corrective action program. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of any of the systems (RPS) listed in paragraph 10 CFR 50.73 (a)(2)(iv)(B).
3382015001 | North Anna 1 | 02/26/2015 | 04/24/2015 | ML15118A56 | <strong>Automatic Reactor Trip due to Low-Low Level on "B" Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2015, at 1511 hours with Unit 1 operating at 96 percent power in an end of cycle coastdown, an automatic reactor trip occurred. The initiating signal was a low-low level on "B" steam generator caused by the closure of the "B" main feedwater regulating valve (MFRV). Closure of the valve was due to a loss of power on the final driver card for "B" MFRV. At 1639 hours, a 4-hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iv)(B) for "an event causing actuation of the Reactor Protection System when the reactor is critical" and an 8-hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) for "an event causing actuation of the Auxiliary Feedwater System (AFW)." Approximately 30 minutes after the reactor trip with AFW flow throttled, the Turbine Driven (TD) AFW pump, 1-FW-P-2, discharge relief valve (RV) lifted and discharged approximately 200 gallons per minute (gpm) to the ground. The RV opened as a result of the inability of the governor valve for the pump to travel an additional 3/16" in the closed direction. An engineering evaluation determined that the loss of emergency condensate storage tank inventory was a condition reportable per 10 CFR 50.73(a)(2)(i)(B) for an "any operation or condition which was prohibited by Technical Specifications." The health and safety of the public were not affected by either event.
3382015002 | North Anna 1 | 04/02/2015 | 09/03/2015 | ML15253A19 | <strong>Manual Reactor Trip due to Inability to Maintain Main Generator Voltage in Specification</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2015, at 0426 hours, with Unit 1 operating at 100 percent power, a manual reactor trip was initiated due to the inability to maintain main generator voltage in specification. This also resulted in a turbine trip. The operations crew entered the reactor trip procedure and stabilized Unit 1 in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. The inability to maintain generator voltage in specification was due to a failure of a component in a firing circuit downstream of the automatic voltage regulator (AVR). The root cause of the event was firing circuit design vulnerabilities in the AVR were not identified during the design change due to lack of rigor. At 0655 hours, a 4-hour Non- Emergency Report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iv)(B) for "an event causing actuation of the Reactor Protection System when the reactor is critical" and an 8- hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) for "an event causing actuation of the Auxiliary Feedwater System (AFW)." Two of the AVR gate firing modules (GFMs) were replaced and the third GFM was evaluated to not be required and was disabled. The health and safety of the public were not affected by this event.
3382015003 | North Anna 1, North Anna 2 | 05/08/2015 | 07/01/2015 | ML15188A35 | <strong>Both Motor Driven Auxiliary Feedwater Pump House Fans Concurrently Tagged out for Maintenance due to the Design Basis Not Clearly Understood</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2015, at 0358 hours, with North Anna Unit 2 operating at 100 percent power, both of the ventilation fans for the Unit 2 Motor Driven Auxiliary Feedwater (AFW) Pump House were simultaneously tagged out for preventive maintenance. The ventilation fans for the Unit 2 Motor Driven AFW Pump House were returned to operable on May 8, 2015 at 1630 hours. Subsequently, it was determined that tagging out both ventilation fans simultaneously challenged operability of the safety related Motor Driven AFW Pumps as required by Technical Specification 3.7.5. A review determined that the Motor Driven AFW Pump House ventilation fans for both Units had been simultaneously tagged out for maintenance several times during the previous three years. The Turbine Driven AFW Pump was operable during these periods and capable of performing its design function. This issue was determined to be reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) for "any operation or condition which was prohibited by the plant's Technical Specifications." The health and safety of the public were not affected by this event.
3392015001 | North Anna 2 | 10/07/2015 | 12/02/2015 | ML15343A01 | <strong>Emergency Switchgear Outside Design Analysis for High Energy Line Break due to an Unlatched Door</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2015, at approximately 2147 hours, with Unit 2 operating at 100 percent power Mode 1, a high energy line break (HELB) door between the Unit 1 Turbine Building (TB) and the safety related Unit 2 Emergency Switchgear Room (ESGR) was determined to be slightly open and unlatched. The door was immediately latched closed. Investigation determined the door was unlatched for approximately 46 minutes. On October 8, 2015, at approximately 1647 hours, the Unit 2 ESGR was determined to be outside of the design analysis for a Unit 1 High Energy Line Break. At 1823 hours, an 8-hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition and in accordance with 10 CFR 50.72(b)(3)(v)(A) & (D) as a condition that could have prevented the fulfillment of safety functions to shutdown the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. The health and safety of the public were not affected by this event.
3412015001 | Fermi 2 | 02/19/2015 | 06/15/2015 | ML15168A24 | <strong>Secondary Containment Declared Inoperable after Loss of Reactor Building Ventilation from Freeze Protection Actuation</strong><br /><i>Abstract:&nbsp;</i>At 0303 EST on February 19, 2015, Fermi 2 experienced a trip of the non-safety related Reactor Building Ventilation (RBHVAC) during normal steady-state operations due to valid actuation of a freeze protection device. At the time of the trip, site area air temperature was -1 degree Fahrenheit. The plant Technical Specifications (TS) require that Secondary Containment vacuum be maintained greater than or equal to -0.125 inches of water gauge. As a result of the RBHVAC trip, this specification was not maintained for approximately 4 seconds until the safety-related Standby Gas Treatment (SGT) system restored Secondary Containment vacuum to an acceptable value.<br /><br /> At 0450 EST, during restoration activities, Secondary Containment vacuum again degraded to less than -0.125 inches of water gauge for 38 seconds until restored by the SGT system. RBHVAC was restored by resetting the freeze protection feature and the SGT system was returned to a standby condition. In both instances, the lowest observed vacuum was -0.11 inches of water gauge. There were no radiological releases associated with this event. <br /><br /> The cause of the freeze protection actuation was insufficient heat transfer from the heating coil associated with 1 of the 14 freeze protection actuators. An investigation revealed this particular heating coil, installed in 2011, has material properties that differ from the original design specification. This results in a reduced heat transfer rate. The heating coil is scheduled to be replaced before the next winter season.
3412015002 | Fermi 2 | 03/09/2015 | 05/05/2015 | ML15127A17 | <strong>Loss of Both Divisions of the Residual Heat Removal Low Pressure Coolant Injection Functions due to 480 Volt Swing Bus Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 09, 2015, a surveillance test of the 480V Swing Bus 72CF Automatic Throwover Scheme was being conducted. At 1521, the alternate power supply breaker failed to close as expected after the normal power supply breaker was opened, resulting in a loss of power to both Reactor Recirculation (RR) pump discharge valves and both divisions of Residual Heat Removal (RHR) Low Pressure Coolant (LPCI) injection valves. The 72CF throwover scheme was declared inoperable and Limiting Condition for Operation (LCO) 3.0.3 was entered. Reactor power was reduced in preparation for meeting the requirement to be in MODE 2 within 7 hours. 72CF was tagged out to support troubleshooting and repair in accordance with plant procedures.<br /><br /> Troubleshooting found a permissive contact in the close circuit for the alternate power supply breaker to be in the incorrect state. The contact was cleaned and the equipment was returned to service and tested successfully. Following successful completion of the surveillance testing, the throwover scheme was declared operable and LCO 3.0.3 was exited before the 7 hour requirement to be in MODE 2 per LCO 3.0.3.
3412015003 | Fermi 2 | 03/19/2015 | 05/05/2015 | ML15127A17 | <strong>Oscillation Power Range Monitor Upscale Reactor Scram During Single Loop Operation</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2015 at 0702 EST the reactor protection system at Fermi 2 initiated an automatic reactor scram on Oscillation Power Range Monitor (OPRM) Upscale following the manual trip of the north reactor recirculation pump due to a cooling water leak. The reactor protection system performed as expected and all control rods were fully inserted into the core. Reactor water level reached a low of approximately 126 inches above top of active fuel and was restored and maintained in the normal operating band by the feedwater and control rod drive systems. No safety relief valves actuated and reactor pressure was controlled by the main turbine bypass valves. Plant systems responded to the scram as designed and all reactor parameters were maintained within design limits following the event.<br /><br /> The cause of the automatic reactor protection system scram on OPRM Upscale was the neutron flux oscillations following the large core flow reduction and lowering feedwater temperature after the trip of a reactor recirculation pump. This event was documented and evaluated in the Fermi 2 Corrective Action Program. The associated root cause evaluation is in progress and may identify additional corrective actions which will be tracked and implemented by the corrective action program.<br /><br /> This event is reportable in accordance with 10 CFR.50.73(a)(2)(iv)(A) as a critical reactor scram.
3412015005 | Fermi 2 | 08/12/2015 | 03/22/2016 | ML16082A28 | <strong>Secondary Containment Declared Inoperable due to RBHVAC Damper Malfunction</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2015, at approximately 1007 EDT, while restoring the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) System after surveillance testing, an equipment malfunction resulted in improper damper alignment causing the Secondary Containment (SC) pressure to exceed Technical Specification (TS) limits for approximately 5 seconds. SC pressure was restored to within the TS limit of less than or equal to -0.125 inches water column by the Standby Gas Treatment System (SGTS), already in operation, and securing the affected RBHVAC components. The highest SC pressure observed was -0.095 inches water column. <br /><br /> A failure analysis was performed; however, the cause of the failure could not be definitively determined. The most probable cause is setpoint drift of the East RBHVAC supply damper time delay relay resulting in the damper moving out of sequence. The relay was replaced in accordance with the Fermi 2 Corrective Action Program. There were no radiological releases associated with this event.
3412015006 | Fermi 2 | 09/13/2015 | 04/15/2016 | ML16109A09 | <strong>Reactor Scram Due to Loss of Turbine Building Closed Cooling Water</strong><br /><i>Abstract:&nbsp;</i>At 2305 EDT on September 13, 2015, a manual reactor scram was initiated in response to a loss of Turbine Building Closed Cooling Water (TBCCW). Reactor Water Level went below the Level 3 setpoint automatically actuating the Reactor Protection System and Primary Containment Isolation Systems (PCIS). A tube leak in the East TBCCW heat exchanger tripped the running TBCCW pumps which resulted in loss of TBCCW. As a result, the Reactor Feed Pumps lost cooling and had to be secured. At 2310 EDT, the Standby Feedwater system was initiated. The loss of TBCCW cooling tripped all Station Air Compressors, which caused Instrument Air header pressure to degrade and the Secondary Containment (SC) isolation dampers to drift closed. This resulted in a positive SC differential pressure. Operators started the Standby Gas Treatment system and manually inserted a SC isolation signal. SC vacuum was promptly restored to within Technical Specification limits. The degradation of Instrument Air header pressure also caused Main Steam Isolation Valves to drift and be manually closed, which led to an expected loss of Condenser vacuum and resulted in isolation of PCIS Group 1. The East TBCCW heat exchanger was repaired. The Root Cause Evaluation determined that important internal equipment operating history and industry Operating Experience (OE) were not identified and implemented. The following corrective actions to prevent recurrence were identified: current heat exchanger inspection scope, frequency, and techniques will be compared against previous historical failures and plant procedures will be revised in consideration of industry and site OE.
3412015007 | Fermi 2 | 10/04/2015 | 11/24/2015 | ML15328A42 | <strong>Operation with the Potential to Drain the Reactor Vessel with Secondary Containment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2015 at approximately 0956 EDT, an Operation with the Potential to Drain the Reactor Vessel (OPDRV) was unintentionally initiated without secondary containment operable. Plant personnel were starting work to isolate the Reactor Recirculation (RR) pump seal flow switch and rotameter for replacement. The RR pump seal cavity drain valves were opened in accordance with the Safety Tagging Record (STR). Shortly after the valves were opened, the Control Room staff identified a lowering Fuel Pool Skimmer Surge Tank level and an increase in Drywell Floor drain sump level and initiated actions to isolate the RR pump seal cavity. At approximately 1120 EDT, the RR pump seal drain valves were successfully closed and the OPDRV was terminated. The RR pump seal drain flow was approximately 12 gallons per minute and lasted for approximately 84 minutes. Reactor cavity water level and spent fuel pool level remained constant throughout the OPDRV. Personnel who developed the STR failed to recognize that the activity would result in an OPDRV and; therefore, did not require that Secondary Containment be Operable in accordance with Technical Specifications. The event was entered into the corrective action program. This Licensee Event Report is written in accordance with 10CFR50.73(a)(2)(v)(C) and 50.73(a)(2)(i)(B).
3412015008 | Fermi 2 | 02/21/2015 | 03/29/2016 | ML16091A47 | <strong>Turbine Stop Valve Closure and Turbine Control Valve Fast Closure Reactor Protection System Functions Considered Inoperable due to Open Turbine Bypass Valve</strong><br /><i>Abstract:&nbsp;</i>At 0030 EST on February 21, 2015, while operating at 100 percent Reactor Thermal Power (RTP), the West Turbine Bypass Valve (TBV) automatically opened as expected for approximately 1 minute in response to the number two High Pressure Turbine Stop Valve (TSV) cycling from full open to closed and then to 22 percent open due to an actuator malfunction. Technical Specification (TS) 3.3.1.1 requires that the TSV closure and Turbine Control Valve (TCV) fast closure RPS functions be operable at or above 29.5 percent RTP. Per TS Bases 3.3.1.1, TBVs must remain shut while RTP is at or above 29.5 percent to consider all channels of the TSV closure and TCV fast closure Reactor Protection System (RPS) functions operable. As a result, all channels of the TSV closure and TCV fast closure RPS functions were considered inoperable and TS 3.3.1.1 Limiting Condition of Operation (LCO) Condition 'C' was entered. <br /><br /> At 0031 EST the TBV automatically closed and the TSV closure and TCV fast closure RPS functions were no longer considered inoperable and the TS LCO was exited. Reactor Operators lowered RTP to 91.5 percent to isolate and restore the TSV to full open. In this event, during the period of time while the TBV was open, reactor power was maintained above 91.5 percent and the RPS functions were confirmed to be enabled. The actuator malfunction was caused by a failed comparator circuit card in the TSV valve control module. The failed comparator circuit card was replaced.
3412015009 | Fermi 2 | 07/28/2015 | 03/31/2016 | ML16092A26 | <strong>Condition Prohibited by Technical Specification due to Missed Entry into LCO Condition</strong><br /><i>Abstract:&nbsp;</i>At 0400 EDT on July 28, 2015, Fermi 2 operators started a planned Safety System Outage including work on the Division 2 Mechanical Draft Cooling Tower (MDCT) Fan D, which is required for the Division 2 Ultimate Heat Sink (UHS) to be operable. On July 28, 2015 at 2115, MDCT Fan D had been restored and Operators reviewed the Limiting Condition for Operation (LCO) log before exiting the LCO Condition. During this review, it was discovered that LCO 3.7.2 Condition B, for inoperable UHS, was not entered. Note 1 of LCO 3.7.2 directs Operators to enter applicable Conditions and Required Actions of LCO 3.8.1 for emergency diesel generators (EDGs) made inoperable by UHS. Due to the missed LCO 3.7.2 Condition B entry, Required Actions A.1, A.3, and B.1 of LCO 3.8.1 to verify operable offsite power circuits and availability of Combustion Turbine Generator (CTG) 11-1 were not performed within their required completion times. Required Actions A.1, A.3, and B.1 were immediately performed and the equipment was found operable.<br /><br /> The cause of this event was inadequate self-checking and peer-checking during preparation and approval of the LCO log entries, which did not identify the inadvertent deletion of LCO 3.7.2 Condition B and LCO 3.8.1 Conditions A and B. Individual performance issues were addressed and lessons learned were shared.
3412015010 | Fermi 2 | 09/14/2015 | 04/15/2016 | ML16109A09 | <strong>Manual Actuation of Reactor Core Isolation Cooling System Due to a Leak in the Standby Feedwater System</strong><br /><i>Abstract:&nbsp;</i>At 0409 EDT on September 14, 2015, the Reactor Core Isolation Cooling (RCIC) system was manually actuated due to an unisolable leak in the Standby Feedwater (SBFW) system. Prior to that time, the SBFW system and Low-Low Set Safety Relief Valves (SRVs) were being used to maintain Reactor Water Level (RWL) and reactor pressure, respectively, in response to a manual reactor scram. The manual reactor scram event had occurred at 2305 EDT on September 13, 2015, as reported in LER 2015-006-01. Following the manual actuation of RCIC, RWL and pressure were controlled using RCIC and SRVs. The cause of the leak was a failed weld in the SBFW system. The failed weld was repaired.
3412015011 | Fermi 2 | 09/14/2015 | 04/15/2016 | ML16109A09 | <strong>Reactor Protection System and Containment Isolation Actuation due to Reaching Reactor Water Level 3 Setpoint</strong><br /><i>Abstract:&nbsp;</i>At 1847 EDT on September 14, 2015, while Operators were manually controlling Reactor Water Level (RWL) and pressure with Reactor Core Isolation Cooling (RCIC) and Safety Relief Valves (SRVs), the RWL went below the Level 3 setpoint. This resulted in automatic actuation of the Reactor Protection System (RPS) and Primary Containment Isolation Systems (PCIS) while the reactor was shut down in MODE 3. Operators promptly restored RWL with manual operation of RCIC. The manual RWL and pressure control was necessary following a manual reactor scram that had occurred at 2305 EDT on September 13, 2015, as reported in LER 2015-006-01, and a subsequent loss of Standby Feedwater (SBFW) at 0409 EDT on September 14, 2015, as reported in LER 2015-010-00. Following restoration of RWL, Operators continued to manually control RWL and pressure control using RCIC and SRVs. The cause of the event was that an Operator did not inject RCIC in a timely manner to maintain RWL above the Level 3 setpoint. The following corrective actions were identified: remediating the Operator in the simulator under similar conditions; evaluating the simulator response to the plant event and assessing other means of pressure control; communicating lessons learned to all Operations and Site personnel; and initiating assessment of training impact.
3462015001 | Davis-Besse | 02/11/2015 | 11/02/2015 | ML15314A66 | <strong>Borated Water Storage Tank (BWST) Rendered Inoperable due to Use of Non-Seismic Purification System</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2015, with the Davis-Besse Nuclear Power Station operating in Mode 1 at approximately 100 percent full power, during a Nuclear Regulatory Commission (NRC) Component Design Basis Inspection, it was identified the seismic Borated Water Storage Tank (BWST) had been aligned in the past to the nonseismic Spent Fuel Pool (SFP) system for purification. This rendered the BWST inoperable for periods of time longer than allowed per Technical Specification 3.5.4 while the plant was operating in Modes 1 through 4. Since initial plant design, the BWST had been aligned to the non-seismic SFP system at various times for purification of the BWST contents.<br /><br /> The cause of this event was that regulatory requirements for the separation of seismically qualified and nonqualified systems, structures, and components were not adequately incorporated into design basis documents and the Updated Safety Analysis Report. Administrative controls were established to restrict the alignments that could affect the operability of the BWST. All corrective actions have been completed. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition which was prohibited by the plant's Technical Specifications and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function systems needed to mitigate the consequences of an accident.
3462015002 | Davis-Besse | 05/09/2015 | 07/08/2015 | ML15194A01 | <strong>Improper Flow Accelerated Corrosion Model Results in 4-inch Steam Line Failure and Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2015, with the Davis-Besse Nuclear Power Station (DBNPS) operating in Mode 1 at approximately 100 percent power, a steam leak was identified in the Turbine Building. A rapid shutdown was initiated, and the reactor was manually tripped at 1909 hours from approximately 30 percent power. The Steam Feedwater Rupture Control System was manually initiated to isolate the leak and start the Auxiliary Feedwater System. The cause of the leak was failure of a four-inch pipe in the Moisture Separator Reheater System due to Flow Accelerated Corrosion (FAC). An incorrect data input caused the FAC software model to underestimate the predicted wear rate, so inspections were not performed to identify the piping wall thinning prior to failure. Additionally, a previous event was not evaluated to ensure the proposed corrective actions would encompass a validation of all critical data inputs. Corrective Actions include improvements in the fidelity of the data in the FAC Software model, and improvements in the Corrective Action Program with respect to Root Cause Evaluations.<br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of the Reactor Protection System and the Auxiliary Feedwater System.
3462015003 | Davis-Besse | 06/26/2015 | 08/25/2015 | ML15239A29 | <strong>Inadvertent Breaker Operation Renders Control Room Emergency Air Temperature Control System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2015, with the Davis-Besse Nuclear Power Station operating in Mode 1 at approximately 100 percent power, the breaker for motor-operated valve Service Water (SW) 1395, which isolates non-essential SW System loads during accident conditions, was found open, rendering SW Train 2 inoperable, therefore rendering Control Room Emergency Air Temperature Control System (CREATCS) Train 2 inoperable. CREATCS Train 1 was also out of service for maintenance during this time. <br /><br /> No Technical Specification (TS) action is specified for having both CREATCS Trains inoperable, so per TS LCO 3.0.3, action shall be initiated within 1 hour to place the unit in Mode 3 within 7 hours. With the assumed time of mispositioning of the breaker for SW1395, both CREATCS trains were likely inoperable for more than 7 hours with the plant remaining in Mode 1. Therefore, the plant operated in a condition prohibited by TS, which is reportable per 10 CFR 50.73(a)(2)(i)(B). The concurrent inoperability of both CREATCS trains also represents a loss of Safety Function, which is reportable per 10 CFR 50.73(a)(2)(v)(D). <br /><br /> The cause of breaker BF1277 for SW1395 being in the open position was that it was inadvertently bumped. Corrective Actions include installing breaker covers.
3462015004 | Davis-Besse | 08/12/2015 | 10/12/2015 | ML15288A12 | <strong>Operation During Previous Cycle with Axial Power Shaping Rod Fully Inserted</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2015, with the Davis-Besse Nuclear Power Station (DBNPS) operating in Mode 1 at approximately 100 percent power, it was determined that the plant operated the previous operating cycle (Cycle 18) with an Axial Power Shaping Rod (APSR) fully inserted. This issue was identified by the DBNPS fuel vendor while reviewing the previous cycle's quadrant power tilt graph and comparing it to the current cycle's (Cycle 19) expected end of cycle graph, since the plant is currently operating with a known APSR fully inserted. The previous cycle operations started with initial criticality on June 11, 2012, and ended on February 1, 2014. <br /><br /> The most likely cause of the APSR being disconnected during the previous operating cycle is an inadvertent work practice error during the coupling process. Corrective actions include a revision to the APSR coupling procedure to require positive verification of APSR coupling (such as verifying the weight addition of the APSR to the lead screw after the coupling is completed) since visual verification is not practicable. <br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation of the plant in a condition prohibited by the Technical Specifications (TS) because the necessary TS actions were not taken last cycle with the APSR fully inserted.
3482015001 | Farley 1 | 05/05/2015 | 07/02/2015 | ML15183A31 | <strong>Automatic Actuation of the Auxiliary Feedwater System When the 1B SGFP was Tripped</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2015 at 04:22 CDT with Farley Nuclear Plant (FNP) Unit 1 in mode 2 and the 1A Steam Generator Feedwater Pump (SGFP) in the tripped condition, an Auxiliary Feedwater (AFW) autostart signal was received due to a manual trip of the 1B SGFP. The trip of the second SGFP initiated the auto start signal for the Motor Driven Auxiliary Feedwater (MDAFW) pumps due to the auto start signal not being defeated. When the actuation signal was received, both the A and B MDAFW pumps were already in service supplying AFW to the steam generators (SG). The effects of this actuation were that the AFW Flow Control Valves were fully opened and the SG blowdown and SG blowdown sample valves were isolated. These actions occurred successfully and the auto start signal was reset. <br /><br /> The human performance cause of this event was that the operating crew did not meet expectations for effective teamwork to ensure proper decision making. While responding to a degrading condenser vacuum, the operating crew made the decision to trip the 1B SGFP instead of securing it per the standard operating procedure, which would have been adequate for preventing the event. Corrective actions included individual remediation plans. Planned corrective actions include the installation of bump preventer covers with caution placards, and management intervention on teamwork and decision-making.
3482015002 | Farley 1 | 05/07/2015 | 07/02/2015 | ML15183A31 | <strong>Technical Specification Shutdown due to Reactor Coolant Pump Trip</strong><br /><i>Abstract:&nbsp;</i>At 0740 CDT on May 7, 2015, while at 27 percent power in Mode 1, the Unit 1 reactor was shut down and entered Mode 3. This shutdown was required by Technical Specification 3.4.4 Condition A which was entered at 0509 when the 1B Reactor Coolant Pump (RCP) tripped. The cause of the 1B RCP trip was a loss of the 1B electrical bus during the transfer of station loads from 1B Start Up Auxiliary Transformer (SAT) to the 1B Unit Auxiliary Transformer (UAT). <br /><br /> The cause of this event was that jumpers were inappropriately left in place because of a failure to adhere to standards during the project management process for the 1B UAT design change. Lapses in standards occurred at various levels of the organization in project oversight, work planning preparation and review, and proper post modification testing. Immediate actions were the removal of the jumpers and the completion of extensive post modification testing. Additional corrective actions will be taken to reinforce planning and project management standards and strengthen post modification testing development guidance.
3482015004 | Farley 1 | 08/11/2015 | 10/09/2015 | ML15282A59 | <strong>Pressurizer Safety Valve Setpoint Pressure Outside of Technical Specification Tolerance Band</strong><br /><i>Abstract:&nbsp;</i>On 8/11/15 Farley Nuclear Plant (FNP) Unit 1 discovered that a pressurizer safety valve (PSV), which had been removed during the May 2015 maintenance outage and shipped offsite for testing, failed its as-found lift test below the Technical Specification (TS) allowable value. The cause of the test failure was attributed to the seat leakage of the valve that occurred during and after startup from the Spring 2015 Refueling Outage (1R26). This failure constitutes a condition that is reportable pursuant to 10CFR50.73 (a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." The 1B pressurizer safety valve was replaced during a May 2015 planned maintenance outage.
3482015005 | Farley 1, Farley 2 | 11/20/2015 | 07/01/2016 | ML16183A33 | <strong>Condition Prohibited by Technical Specifications due to Turbine Driven Auxiliary Feedwater Design Issue</strong><br /><i>Abstract:&nbsp;</i>On 11/20/2015 at 12:33 CST with Unit 1 operating at 100 percent thermal power the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) failed to start during an inservice test due to a turbine overspeed. The plant entered Technical Specification (TS) 3.7.5 Condition B. The overspeed trip was caused by a design issue that had been introduced into the governor control system in April, 2015, making the TDAFWP inoperable since that time, which was a period of time longer than allowed by TS 3.7.5. The same design change was implemented on the Unit 2 TDAFWP in January, 2015. The Unit 2 TDAFWP was declared inoperable and TS 3.7.5 was entered on 11/22/15 at 07:50 CST. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). <br /><br /> During the time of inoperability, there were two times when Unit 2 was left with a single AFW train in operation, which does not meet the TS Bases requirement for meeting the safety function for removal of residual heat. Therefore for Unit 2 this condition is also reportable per 10 CFR 50.73(a)(2)(v)(B). <br /><br /> The cause of this condition was a misapplication of design inputs. Temporary Modifications were installed on both units to return the TDAFWPs to operable status. Permanent design changes will be pursued. A new user manual will be developed and implemented that is specific to Farley's Unit 1 and Unit 2 TDAFWPs and will have sufficient detail to ensure understanding of the operation of the TDAFWP Woodward 505 Controller.
3522015001 | Limerick 1 | 02/23/2015 | 04/24/2015 | ML15114A23 | <strong>Valid Automatic Actuation of the Reactor Protection System with the Reactor Critical due to One MSIV Closure</strong><br /><i>Abstract:&nbsp;</i>A valid automatic actuation of the reactor protection system (RPS) occurred due to a high reactor pressure condition following an unexpected closure of the 1C Inboard main steam isolation valve (MSIV). The cause of the event was that an undersized fitting was installed on the air supply tubing to the 1C Inboard MSIV, which was not capable of withstanding existing cyclic stresses. The fitting failed due to cyclic fatigue. An inspection of Unit 1 inboard (I/B) and Outboard (O/B) MSIV Primary Containment Instrument Gas (PCIG)/Instrument Air tubing was performed to verify that the correct fittings are installed as specified by the design drawings or subsequent evaluation. The inspection of Unit 2 will occur during the in progress refueling outage. The failed fitting connection was replaced with a more robust fitting that is suitable for the application.
3522015002 | Limerick 1 | 08/27/2015 | 10/22/2015 | ML15295A12 | <strong>Condition Prohibited by Technical Specifications due to Standby Gas Treatment System Subsystem Inoperable</strong><br /><i>Abstract:&nbsp;</i>While operating at full power, a degraded Standby Gas Treatment System (SGTS) subsystem differential pressure (dP) control instrument failed upscale. The subsystem was determined to be operable at the time of the failure. After the corrective maintenance activity it was determined that the failed instrument caused the subsystem to be inoperable. The 0B SGTS subsystem was determined to have been inoperable for a period that exceeded the SGTS Technical Specification (TS) allowable outage time (AOT) based on firm evidence regarding the time of the instrument failure. The cause of the 0B SGTS subsystem inoperability was a degraded SGTS dP control instrument. The degraded SGTS dP control instrument was replaced and the 0B SGTS subsystem was restored to operable status.
3532015002 | Limerick 2 | 04/13/2015 | 06/12/2015 | ML15163A19 | <strong>Valid Manual Actuation of the Reactor Protection System While Shutdown</strong><br /><i>Abstract:&nbsp;</i>An unplanned valid manual actuation of the reactor protection system (RPS) was initiated with the unit shutdown for a refueling outage. The manual scram was directed by procedure when a scram reset attempt failed to fully reset the RPS logic due to a failure of the 2H intermediate range monitor (IRM) channel. The cause of the event was age related degradation and failure of the 2H IRM K50H relay. The 2H IRM K50H relay was replaced. The scram reset procedure (GP-11) will be revised to provide explicit step-by-step instructions regarding verification that all scram conditions are clear.
3532015003 | Limerick 2 | 06/03/2015 | 07/30/2015 | ML15211A16 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Three workers were transporting a laundry cart through an airlock from the reactor enclosure to the refuel floor when the cart bumped the inboard door crash bar which opened the door. The three workers and the cart were inside the airlock when both doors were open. The airlock was closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. The cause of the event was the breakdown of two human performance barriers. The failed barriers were situational awareness and inadequate risk perception. The workers failed to assess the risk associated with overcrowding the airlock with three workers and a laundry cart. This event was not prevented by the design of the reactor enclosure airlocks since there is no mechanical interlock and the door open indicating light does not prevent simultaneous opening of both airlock doors. The airlock doors were closed to restore reactor enclosure secondary containment integrity. The workers were coached regarding the recognition and management of the risk associated with airlock use. Performance management actions were taken by the workers’ management. The work group implemented a limit of two workers simultaneously using the airlock. The lessons learned were communicated to the site.
3532015004 | Limerick 2 | 06/21/2015 | 08/20/2015 | ML15232A73 | <strong>Valid Manual Actuation of the Primary Containment Isolation System</strong><br /><i>Abstract:&nbsp;</i>A valid manual actuation of the primary containment isolation system was initiated in response to a low delta pressure condition in the Unit 2 reactor enclosure secondary containment. The manual actuation affected primary containment isolation valves in more than one system. The cause of the event was a trip of the reactor enclosure ventilation system that resulted in a low reactor enclosure secondary containment delta pressure condition. The cause of the ventilation system trip was a reactor enclosure equipment compartment exhaust (REECE) system flow transmitter output drift to a value less than the low flow trip setpoint. The failed flow transmitter was replaced. The reactor enclosure ventilation system was restored to service and continues to operate normally with a temporary configuration change (TCC) installed. Troubleshooting is planned to support removal of the TCC that was installed to defeat the REECE system low flow trip. The preventive maintenance (PM) activity will be reviewed and revised as necessary.
3532015005 | Limerick 2 | 09/03/2015 | 11/02/2015 | ML15306A08 | <strong>Condition That Could Have Prevented Fulfillment of the High Pressure Coolant Injection System Safety Function</strong><br /><i>Abstract:&nbsp;</i>While operating at full power, the Unit 2 Division 4 high steam flow isolation actuation instrument for the High Pressure Coolant Injection (HPCI) system failed. The instrument failure caused an isolation of the inboard steam supply line primary containment isolation valve (PCIV). The event was initiated by a capacitor failure on an unrelated trip unit located below the HPCI Division 4 high steam flow trip units. The initial failure resulted in collateral damage to one of the HPCI trip units that resulted in a HPCI system steam line automatic isolation. Three trip units were replaced and tested successfully.
3532015006 | Limerick 2 | 11/20/2015 | 12/29/2015 | ML15363A00 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>A supervisor and two carpenters were transporting a loaded scaffold cart through an airlock from the refuel floor to the reactor enclosure when the cart bumped the inboard door crash bar which opened the door. The two carpenters and the cart were inside the airlock when both doors were opened. The airlock was closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. The cause of the event was the failure of the human performance barrier regarding maintaining a questioning attitude. The failure occurred when the workers did not ensure the clearance between the cart and the crash bar was adequate. Also no barrier was used to prevent the cart contact with the crash bar. This event was not prevented by the design of the reactor enclosure airlocks since there is no mechanical interlock and the door open indicating light does not prevent simultaneous opening of both airlock doors. The airlock doors were closed to restore reactor enclosure secondary containment integrity. A work group stand down was conducted to reinforce the importance of hazard recognition and mitigation. The lessons learned were communicated to the site.
3532015007 | Limerick 2 | 12/10/2015 | 06/21/2017 | ML17172A02 | <strong>Condition Prohibited by Technical Specifications due to an Inoperable Reactor Coolant Leakage Detection System</strong><br /><i>Abstract:&nbsp;</i>A modification was performed on the drywell unit coolers condensate flow rate monitoring system during the Spring 2015 refueling outage (2R13) due to obsolescence issues on the system. The modification replaced all six flow sensors and flow transmitters with a more recent design. The condition was identified in December 2015 however the cause of the failure and the corrective actions could not be determined until the Spring 2017 refueling outage (2R14). The system failed to properly indicate drywell unit cooler condensate flow due to the specific Limerick Generating Station operating environment and system configuration. Through a design modification, the Unit 2 reactor coolant system leakage detection system was restored to operable on May 10, 2017, during Limerick Unit 2 2017 Refueling Outage (2R14).
3532015008 | Limerick 2 | 12/19/2015 | 02/17/2016 | ML16048A19 | <strong>Valid Automatic Actuation of the Reactor Protection System due to Main Steam Bypass Valves Opening</strong><br /><i>Abstract:&nbsp;</i>An unplanned valid automatic actuation of the reactor protection system (RPS) when critical occurred during a reactor restart from a planned maintenance outage. The actuation occurred due to a deficient procedure when using digital electro-hydraulic control (DEHC) main steam bypass valve (BPV) jack adjustments to increase reactor pressure. Following a demand for a pressure increase all nine BPVs opened causing a reactor high level trip of the reactor feed pump followed by a reactor low level RPS actuation. The root cause of the event was a failure to identify the risk associated with procedure changes for the DEHC installation modification and the DEHC modification team failed to adequately evaluate DEHC software changes. The corrective actions will revise the procedure change process to validate modification related procedure revisions with risk impact.
3542015001 | Hope Creek | 03/31/2015 | 06/30/2015 | ML15181A24 | <strong>Conditions Prohibited by Technical Specifications due to Core Spray Inoperabilities</strong><br /><i>Abstract:&nbsp;</i>On 03/31/2015 at 1342, the breaker for 'A' Core Spray Pump failed to close during normal surveillance testing. No alarms were received in the Main Control Room when the start pushbutton was depressed. A second start attempt had the same results. Technical Specification (TS) 3.5.1.a was entered for one inoperable Core Spray Subsystem. The breaker was replaced and the surveillance was satisfactorily performed. 'A' Core Spray Subsystem was declared OPERABLE on 03/31/2015 at 2000 and the TS was exited. <br /><br /> Initial troubleshooting indicated that the failure in the breaker most likely existed since the last breaker operation in January 2015. Failure analysis concluded that the spring in the breaker control device failed due to cyclic fatigue, preventing the breaker from closing. Consequently, 'A' Core Spray Subsystem was inoperable for longer than the TS allowed outage time. Therefore, the condition was determined to be reportable per 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by TS. During the review of this event, it was determined that 'B' Core Spray Subsystem was inoperable from 02/09/2015 at 0300 until 02/10/2015 at 1532 (36 hours and 32 minutes) when planned maintenance was performed on the 'B' Emergency Diesel Generator (EDG). This condition is reportable per 10 CFR 50.73(a)(2)(v) as an event or condition that could have prevented the fulfillment of a safety function.
3542015002 | Hope Creek | 04/14/2015 | 06/10/2015 | ML15161A43 | <strong>Operations with a Potential To Drain The Reactor Vessel (OPDRV) Without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On April 14, April 15, April 17, April 20, April 27, and April 29, 2015, with Hope Creek Generating Station (HCGS) in a planned refueling outage and the reactor cavity flooded in OPCON 5, HCGS performed operations with a potential to drain the reactor vessel (OPDRV) without an operable secondary containment. These operations are prohibited by Technical Specification (TS) 3.6.5.1; however, recent NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 2, allowed the implementation of interim actions as an alternative to full compliance. These actions were compiled in a plant procedure for the OPDRV activities performed at HCGS during Refueling Outage (H1R19) in April 2015. These OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on the interim actions taken. Since these actions were deliberate, no cause determination was necessary. Consistent with the guidance provided in EGM 11-003, Revision 2, HCGS will submit a license amendment request to adopt a Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue within four months after the issuance of the Notice of Availability of the TSTF traveler. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
3542015003 | Hope Creek | 05/04/2015 | 07/06/2015 | ML15187A20 | <strong>Conditions Prohibited by Technical Specifications due to Low Pressure ECCS Inoperabilities</strong><br /><i>Abstract:&nbsp;</i>From May 4 through 5, 2015, during a planned Reactor Pressure Vessel (RPV) pressure test following RPV reassembly from refuel outage H1R19, Hope Creek Generating Station (HCGS) did not comply with Technical Specification Action Statement 3.5.2, action a. The plant lineup to support the RPV pressure test is classified as an Operation With the Potential to Drain the Vessel (OPDRV). <br /><br /> Technical Specification (TS) 3.5.2, ECCS Shutdown, requires that at least two Low Pressure ECCS subsystems be OPERABLE in Operational Condition 4. The TS requires that with only one ECCS subsystem operable, two subsystems shall be restored to operable status within four hours or suspend all OPDRVs. Contrary to this requirement, HCGS conducted the RPV pressure test OPDRV activity with only one low pressure ECCS subsystem operable. This condition existed from May 4 at 0400 until May 5 at 1042, a period of 30 hours and 42 minutes. TS compliance was restored on May 5 at 1042 when a second low pressure ECCS system was returned to OPERABLE. The cause of the event was determined to be failure to properly assess the operability status of all the ECCS subsystems which could be used to meet TS 3.5.2. <br /><br /> This conditions is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
3542015004 | Hope Creek | 06/02/2015 | 08/26/2015 | ML15238B65 | <strong>As-Found Values for Safety Relief Valve Lift Set Points Exceed Technical Specification Allowable Limit</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2015, Hope Creek Generating Station (HCGS) received initial results of the 'as-found' setpoint testing for the safety relief valve (SRV) pilot stage assemblies. The initial results indicated that three SRV pilot stage assemblies had exceeded the lift settings prescribed in Technical Specification (TS) 3.4.2.1. The TS requires the SRV lift settings to be within +/- 3% of the nominal setpoint value. During the nineteenth refueling outage (H1R19), all fourteen SRV pilot stage assemblies were removed for testing at an offsite facility. Between June 2 and June 10, 2015, HCGS received the test results for the remainder of the SRV pilot valve assemblies. A total of ten of the fourteen SRV pilot stage assemblies experienced setpoint drift outside of the TS 3.4.2.1 specified values. All of the valves failing to meet the limits were Target Rock Model 7567F two-stage SRVs. This is a condition reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications.<br /><br /> The cause of the setpoint drift for the ten SRV pilot stage assemblies is attributed to corrosion bonding between the pilot disc and seating surfaces, which is consistent with industry experience. This conclusion is based on previous cause evaluations and the repetitive nature of this condition at HCGS and within the BWR industry. <br /><br /> Technical evaluations performed to assess the aggregate safety significance of ten SRVs with out of tolerance initial lift setpoints concluded that this condition had no safety significance.
3542015005 | Hope Creek | 09/28/2015 | 01/05/2016 | ML16005A08 | <strong>Reactor Scram due to Invalid RRCS Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2015, at 20:46, with the Hope Creek reactor operating at 100% power, a human error during surveillance testing resulted in the actuation of the Redundant Reactivity Control System (RRCS), and subsequently, an automatic reactor scram on a valid low water level signal. At the time of the transient, a surveillance test of division 1 of the RRCS system was in progress. The test simulates a high reactor pressure signal. Plant data show the signal was entered in both channels of division 1 of the RRCS system. The resulting system actuation caused a trip of both Reactor Recirculation Pumps, and the actuation of the Alternate Rod Insertion (ARI) function of the RRCS system. As a result of these two actuations, reactor power lowered, causing reactor water level to lower to the Reactor Protection System (RPS) trip set point of +12.5 inches. The RPS initiated an automatic reactor scram. Reactor operators recovered water level to within the desired band using the feedwater system. Reactor pressure was maintained using turbine bypass valves discharging to the main condenser. <br /><br /> This report is being submitted under 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in the actuation of the Reactor Protection System.
3612015002 | San Onofre 2, San Onofre 3 | 11/19/2015 | 01/12/2016 | ML16015A40 | <strong>Spent Fuel Pool Temperature Drifted Below Updated Final Safety Analysis Report (UFSAR) Value</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2015, a review of Operations Logs determined that the San Onofre Nuclear Generating Station (SONGS) Unit 2 Spent Fuel Pool (SFP) temperature had drifted approximately two degrees below the analyzed temperature of 68 degrees F on previous days. This was reported as an unanalyzed condition under 10 CFR 50.72(b)(3)(ii)(B) because the Updated Final Safety Analysis Report (UFSAR) and the spent fuel analysis identified 68 degrees F as the lower temperature design basis for the SFP. This 60-day report is submitted under 10 CFR 50.73(a)(2)(ii)(B). SONGS Unit 2 and Unit 3 are permanently shutdown and defueled. <br /><br /> Further review has identified additional incidents of SFP temperature drifting below 68 degrees F for both units since January 2013. The low temperature resulted from the decreasing residual heat load and cool ocean temperatures. The lower design basis SFP temperature provided in the UFSAR had not been translated into procedures or any other site document. The SONGS Units 2 and 3 spent fuel criticality calculation and UFSAR have been updated to establish a low temperature limit of 50 degrees F. The SFP procedure was revised to provide actions to secure all SFP Cooling Pumps prior to the pool temperature reaching 55 degrees F.<br /><br /> This event did not affect facility operation or safety. The criticality acceptance criteria specified in 10 CFR 50.68 were met at all times.
3642015001 | Farley 2 | 01/09/2015 | 01/14/2016 | ML16014A21 | <strong>Turbine Driven Auxiliary Feedwater Pump in a Condition Prohibited by Technical Specifications due to a Design Issue</strong><br /><i>Abstract:&nbsp;</i>On 1/9/2015 at 1255 CST with Unit 2 operating at 100 percent thermal power the Turbine Driven Auxiliary Feedwater (TDAFW) pump was declared inoperable based on a causal investigation for a November 2014 surveillance test failure. The causal analysis identified that a design vulnerability existed which was the cause of both the November failure and a similar April 2014 failure. This vulnerability with the governor control system created a configuration within the software that had the potential for an expected trip signal to be recognized as a shutdown signal during the start sequence. Due to this condition, the TDAFW Pump could not be relied on to start for some plant conditions in the accident analysis for a Main Steam Line Break (MSLB) such that a reasonable assurance of operability could no longer be supported. Other accident analysis conditions were found to be unaffected. The cause of the design error was missing information in the original design documentation which would have provided an opportunity to develop the design change correctly in 2011. For corrective actions, a temporary modification was made to increase a timer setpoint to eliminate the design vulnerability. This modification will be made permanent through the design change process. Design documents will be revised to add missing information which led to the design vulnerability. <br /><br /> Supplement: A past operability review has been completed and the results are appended to this LER.
3642015002 | Farley 2 | 08/07/2015 | 01/08/2016 | ML16008B04 | <strong>Entry into Condition Prohibited by Technical Specifications due to All Containment Cooling Level Monitoring Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2015 at approximately 02:00 CDT, Farley Unit 2 was operating in Mode 5 at zero percent power in a planned maintenance outage when evidence from troubleshooting became available which led to the discovery that all of the Reactor Coolant System (RCS) Leakage Detection Instrumentation had been inoperable on August 7, 2015 for a period longer than allowed by Technical Specifications (TS). Troubleshooting discovered that the A, B, and D channels of the Containment Cooling Level Monitoring System (CCLMS) had been inoperable since July 6, 2015. On August 7, 2015 the C CCLMS was tagged out at the same time as both the R11 and R12 Containment Radiation Detectors were taken out of service for a period longer than allowed by TS 3.4.15 Condition E and Limiting Condition for Operation (LCO) 3.0.3. This is a condition prohibited by Technical Specifications and is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B). <br /><br /> The cause of this event was an incorrect conclusion regarding the operating conditions of the four Containment Cooler Level Indicators. Corrective actions included the repair of the containment coolers' sensing lines for full restoration of the CCLMS. Repairs were also made to the components associated with the steam leak in containment.
3662015001 | Hatch 2 | 02/09/2015 | 04/02/2015 | ML15092A41 | <strong>Main Steam Isolation Valves (MSIVs) Fail to Meet Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On 02/09/2015 at approximately 0504 EDT, with Unit 2 in Mode 3 at zero percent power due to a scheduled refueling outage, the Unit 2 "A" and "C" outboard main steam isolation valves (MSIVs) failed to close in the required fast stroke time requirements of 3 to 5 seconds. The "2A" outboard isolation valve closed in 6.8 seconds and the "2C" outboard isolation valve closed in 10.3 seconds. The surveillance tests were declared unsatisfactory and the affected Unit 2 "A" and "C" main steam lines were maintained in an isolated configuration as all the MSIVs remained closed.<br /><br /> The cause of the unsatisfactory surveillance testing on the "2A" and "2C" outboard MSIVs was determined to be excess lubrication on the pistons and springs of the 2-way and 4-way valves of the pneumatic manifold assembly of the MSIV actuator. The excess super a-lube applied to the valve internals had become tacky, causing a delay in the opening of the air supply and exhaust paths for the air operator cylinder of the MSIV actuator. As part of a broadness review, additional MSIV actuators on Unit 2 were determined to be susceptible to excess lubrication. All of the associated 2-way, 3-way, and 4-way valves of the pneumatic manifold assemblies were replaced or inspected, cleaned, and re-lubricated. The MSIVs were then reassembled and functionality tested to ensure the isolation valves were capable of meeting their stroke time of 3 to 5 seconds. The associated surveillance tests were satisfactorily completed and the MSIVs were returned to service in concurrence with the startup of Unit 2.
3662015002 | Hatch 2 | 02/16/2015 | 04/15/2015 | ML15105A57 | <strong>Performance of Operations with the Potential to Drain the Reactor Vessel (OPDRV) Without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2015, February 18 through 19, 2015, and February 23 through 24, 2015 operations with the potential to drain the reactor vessel (OPDRV) activities were performed while Unit 2 remained in Refueling Mode (Mode 5) without an operable secondary containment. These activities are prohibited by Technical Specifications (TS) 3.6.4.1. However, recent NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 2 and in Regulatory Issue Summary (RIS) 2012-11 allowed the implementation of interim actions as an alternative to full compliance. These actions are compiled in the operating procedure for the OPDRV activities performed during the 2015 Hatch Unit 2 Refueling Outage in February. <br /><br /> The performance of OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A licensee amendment request (LAR) will be submitted following NRC approval of the Technical Specification Task Force (TSTF) Traveler associated with generic resolution of this issue (TSTF-542).
3662015004 | Hatch 2 | 05/11/2015 | 07/10/2015 | ML15191A26 | <strong>Safety Relief Valves As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2015 at approximately 0923, Unit 2 was at 100 percent rated thermal power (RTP) when the "as-found" testing results of the 2-stage main steam safety relief valves (SRVs) were received which indicated that two of eleven of the Unit 2 SRVs had experienced a setpoint drift during the previous operating cycle which resulted in their failure to meet the Technical Specification (TS) opening setpoint of 1150 +/- 34.5 psig percent as required by TS Surveillance Requirement (SR) 3.4.3.1. <br /><br /> The root cause of the SRV setpoint drift is attributed to corrosion-induced bonding between the pilot disc and seating surfaces. This conclusion is based on previous root cause analyses and the repetitive nature of this condition at Hatch and within the BWR industry. All 2-stage SRVs with platinum coated pilot seats were removed from Unit 2 during the 2015 refueling outage and replaced with 3-stage SRVs with a modified pilot. 3-stage SRVs typically do not exhibit set point drift and the modified pilot reduces instances of vibration induced spurious openings and leak-by. <br /><br /> A 3-stage SRV with a similar modified pilot was installed on Unit 2 during the 2013 refueling outage. Based upon "as-found" testing results, it was seen that pressure lift setpoints were maintained during plant operation.
3682015001 | Arkansas 2 | 10/26/2015 | 12/21/2015 | ML15355A39 | <strong>Purge Radiation Monitor Discovered Inoperable During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2015, the Containment Purge and Exhaust Isolation Process Monitor was discovered to be inoperable due to not having its required sample pump in operation. The Containment Building Purge Radiation Monitor Sample Pump provides flow to the Containment Purge and Exhaust Isolation Process Monitor. Technical Specification 3.3.3.1, Table 3.3-6, requires the Containment Purge and Exhaust Isolation Process Monitor to be operable in Modes 5 and 6. For approximately 5 hours, Arkansas Nuclear One, Unit 2 was in Mode 6 with refueling operations in progress while the Containment Purge and Exhaust Isolation Process Monitor was inoperable. <br /><br /> The apparent cause of this event was a a human performance error associated with the failure to restart the Containment Building Purge Radiation Monitor Sample Pump following manual transfer to its alternate power supply.
3702015001 | McGuire 2 | 10/07/2015 | 12/07/2015 | ML15343A01 | <strong>Auxiliary Feedwater System Actuation While in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2015, an actuation of the Auxiliary Feedwater (CA) system occurred while Unit 2 was in Mode 4 and operators were restoring from testing of the 2A Solid State Protection System (SSPS) Safety Injection (SI) trip functions for the Main Turbine and the Main Feedwater (CF) pump turbines. The CA actuation caused the 2A CA Train flow control valves to fully open and the associated steam generator (SG) sampling and blowdown valves to close. The actuation occurred as designed, and there was no adverse impact to plant operation. <br /><br /> At the time of the CA actuation, the CF pumps were shut down and SG levels were being maintained by the 2A and 2B Motor Driven CA Pumps (MDCAP)s. During restoration from SSPS testing, a conditional step in the procedure did not clearly require the reset of at least one CF pump. Leaving both CF pumps in the tripped state provided the logic for the CA actuation signal. The actuation occurred when the 2A Train CA auto start defeat switch was placed in "reset" as directed by the test procedure. To prevent the CA actuation, the test procedure should have ensured that at least one CF pump was in "reset" before the 2A CA Train auto start defeat switch was placed in "reset". <br /><br /> Procedures PT/1/A/4200/026A and PT/2/A/4200/026A will be revised to clearly define the CF pump as found and restoration configuration based on actual plant conditions.
3732015001 | LaSalle 1, LaSalle 2 | 12/12/2014 | 02/10/2015 | ML15041A83 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2014, both Units 1 and 2 were in Mode 1 at 100% power with no fuel movements in progress. At 1324 hours CST, it was reported that both air-lock doors of the Unit 2 Reactor Building 710' elevation between the Unit 2 diesel generator corridor and the Unit 2 Reactor Building were open at the same time for approximately 10 seconds. While both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 ("Verify one secondary containment access door in each access opening is closed") was not met. Secondary containment was declared inoperable for the time that both interlock doors were open. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to OPERABLE status within 4 hours was entered and exited at 1324 hours CST on December 12, 2014. <br /><br /> The cause was a degradation of the door closure mechanism, and the contributing cause was a less than robust design of the door interlock assembly. Corrective actions from the previous occurrences to identify, procure and install a more robust interlock assembly design were in progress at the time of the event. Additional corrective actions, including periodic preventative maintenance to inspect, tighten, and replace fasteners as necessary, were in place but did not preclude this event.
3732015002 | LaSalle 1, LaSalle 2 | 12/12/2014 | 02/10/2015 | ML15041A83 | <strong>Valve Control Power Breaker-Fuse Coordination Issue Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2014, both Units 1 and 2 were in Mode 1 at 100% power with an NRC Triennial Fire Protection Inspection in progress. During the inspection, breaker-fuse coordination evaluations were conducted for the 250 VDC control power supplies to Reactor Core Isolation Cooling (RCIC) valves that are required to be operated from the Remote Shutdown Panel (RSP) in the event of a fire in the Main Control Room (MCR). The evaluation identified that the power supply breakers to two RCIC valves might trip before the fuses, requiring the breakers to be reset before they could be operated from the RSP. The plant current licensing basis does not identify the contingency actions required to reset the breakers prior to operation from the RSP. RCIC operation from the RSP is the method credited for reactor vessel inventory makeup in the event of a fire in the MCR. This condition is common to both Units. <br /><br /> Documented breaker-fuse analyses were not required by engineering standards in place during original construction. Corrective actions were to implement compensatory measures as identified in Information Notice 97-48, "Inadequate or Inappropriate Interim Fire Protection Compensatory Measures," including communicating the issue to the operating crews and providing direction to the Safe Shutdown Equipment Operator in the event of a fire in the MCR. Measures to reset the breakers will be added to the appropriate procedures until the breakers and/or trip settings are appropriately modified.
3732015003 | LaSalle 1, LaSalle 2 | 02/17/2015 | 04/20/2015 | ML15110A20 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2015, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 5 with no fuel movements in progress. Operations with the potential to drain the reactor vessel (OPDRVs) were in progress in the secondary containment on Unit 2. At 1145 hours CST, it was reported that both air-lock doors between the Unit 1 diesel generator corridor and the Unit 1 Reactor Building were open at the same time for approximately 5 -10 seconds. While both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 ("Verify one secondary containment access door in each access opening is closed") was not met. Secondary containment was declared inoperable for the time that both interlock doors were open. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to OPERABLE status within 4 hours was entered and exited at 1145 hours CST on February 17, 2015.<br /><br /> The cause was a failure of a controller circuit card in the door interlock logic. The circuit card was replaced, which restored the interlock functionality. Corrective actions include determining the cause of vendor quality issues with the controller circuit card and replacing the card with a more reliable model.
3742015001 | LaSalle 2 | 12/29/2014 | 02/27/2015 | ML15058A46 | <strong>High Pressure Core Spray Inoperable due to Division 3 Diesel Generator Cooling Water Pump Casing Leak</strong><br /><i>Abstract:&nbsp;</i>On December 29, 2014, Unit 2 was in Mode 1 at 100% power with a diesel generator (DG) operability test in progress on the 2B DG. During performance of the test, operators noticed a small leak of about one drop per second coming from the casing of the 2B High Pressure Core Spray (HPCS) DG cooling water pump. The 2B DG was declared inoperable at 2330 hours CST on 12/29/2014, as was the supported HPCS system. The Station entered Technical Specification 3.5.1 Required Actions B.1 to verify the Reactor Coolant Isolation Cooling System operable and B.2 to restore HPCS to operable status within 14 days.<br /><br /> The pump casing was examined, and the apparent cause of the leak was determined to be erosion from impeller flow impingement. The pump was replaced and returned to service on January 3, 2015.
3742015002 | LaSalle 2 | 02/14/2015 | 07/15/2015 | ML15218A00 | <strong>Two Main Steam Safety Relief Valves Failed Inservice Lift Inspection Pressure Test</strong><br /><i>Abstract:&nbsp;</i>During the February 2015 Unit 2 refueling outage L2R15, two main steam safety relief valves (SRV) did not pass Technical Specification Surveillance Requirement 3.4.4.1 and Inservice Testing Program lift pressure requirements. Both SRVs lifted below their expected lift pressures. SRV 2B21-F013S was required to lift within plus or minus three percent of 1150 psi (i.e., 1150 psi plus or minus 34.5 psi) and actually lifted at 1099 psi. SRV 2621-F013M was required to lift within plus or minus three percent of 1195 psi (i.e., 1195 psi plus or minus 35.8 psi) and actually lifted at 1145 psi. <br /><br /> Both SRVs were replaced during the outage. A failure analysis was conducted, but did not identify a cause for the valves lifting below their setpoint.
3742015003 | LaSalle 2 | 08/07/2015 | 10/06/2015 | ML15279A19 | <strong>Reactor Recirculation Loop Discharge Isolation Valve Vent Line Leak due to Weld Defect</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2015, Unit 2 was in Mode 3 for a planned maintenance outage. At 1300 hours, during the initial drywell entry, a steam leak was observed on the Reactor Recirculation (RR) system line 2RR94AB-3/4", which is upstream of valve 2B33-F080B (RR Pump Discharge Valve 2B33-F067B Inspection Port - Reactor Side Upstream Stop Valve). At 1345 hours, the leak was determined to be pressure boundary leakage. Technical Specification 3.4.5, "RCS Operational Leakage," Required Actions C.1 and C.2 were entered, which require the unit to be in Mode 3 within 12 hours and in Mode 4 in 36 hours, respectively. Unit 2 entered Mode 4 at 2209 hours on August 7, 2015. <br /><br /> This condition was reported (EN# 51300) on August 7, 2015 to the NRC in accordance with 10 CFR 50.72(b)(3)(ii)(A) for the pressure boundary leakage as a principal safety barrier being in a seriously degraded condition. <br /><br /> The cause of the steam leak was determined to be poor weld quality and vibration induced fatigue. The weld was repaired during the maintenance outage.
3822015004 | Waterford 3 | 06/03/2015 | 04/28/2016 | ML16119A43 | <strong>Inoperability of the Emergency Feedwater Actuation System, Emergency Feedwater (EFW) System, and Atmospheric Dump Valves due to Improper Configuration of the EFW System Flow Control System</strong><br /><i>Abstract:&nbsp;</i>On June 3, 2015, at 1707, following a manual reactor scram from 100% power, an Emergency Feedwater Actuation Signal (EFAS) was automatically actuated to both Steam Generators (SGs). Following flow initiation, the Emergency Feedwater (EFW) Backup Flow Control Valves (BFCVs) for both trains exhibited wide, frequent oscillations. Operators took manual control of both trains and stabilized flow. Both channels of EFAS flow control logic and both trains of EFW BFCVs were subsequently declared INOPERABLE and Technical Specifications (TS) 3.3.2.b and 3.7.1.2.d were entered, respectively. Analysis has determined that the identified valve cycling would have exceeded the assumed nitrogen consumption rate and, without operator intervention, would have exhausted the accumulators prior to the credited 10 hour analyzed mission time. The specified safety functions of both trains of EFW and both Atmospheric Dump Valves (ADVs) would not have been fulfilled. The cause of this event was that tuning of the flow control system was not adequate to cope with changes to system operating parameters. Compensatory measures have been put in place to station a dedicated operator to control the EFW BFCVs in manual following a reactor trip to establish and maintain the SG level in accordance with emergency operating procedures; system modification will follow.
3822015005 | Waterford 3 | 06/03/2015 | 08/21/2015 | ML15233A08 | <strong>Manual Reactor Trip due to Low Steam Generator Levels</strong><br /><i>Abstract:&nbsp;</i>On June 3, 2015, at 1705, the reactor was manually tripped due to low Steam Generator (SG) levels caused by a loss of the 'A' Main Feedwater (MFW) Pump. During the transfer of electrical buses, the 'B' train electrical buses failed to transfer to the Startup Transformer and were de-energized. The loss of 'B' power caused the loss of the remaining MFW pump and the Emergency Diesel Generator (EDG) on that side to automatically start and load the safety buses. The loss of MFW resulted in an Emergency Feedwater Actuation Signal (EFAS) with both SGs being fed by Emergency Feedwater (EFW) to restore level. The Emergency Operating Procedure (EOP) for a reactor trip due to the loss of MFW was entered. This event was caused by (1) the failure to identify the failure mechanism for repeated failures of non-safety related normal level control valves and (2) the relay's timed contact sets not changing state due to an unknown equipment problem. Corrective actions include rebuilding valves with identified similar deficiencies, changing the frequency of the Preventive Maintenance (PM) procedures for level control valves, and establishing a relay replacement PM and identifying electrical control circuit system enhancements.
3822015007 | Waterford 3 | 08/26/2015 | 12/06/2016 | ML16341C14 | <strong>Both Emergency Diesel Generators Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2015, both the 'A' and 'B' Emergency Diesel Generators were declared inoperable, causing entry into Technical Specification 3.8.1.1 action f. <br /><br /> On August 26, 2015, Emergency Diesel Generator (EDG) 'A' was declared inoperable following a trip of EDG 'A' on Generator Differential. Technical Specification (TS) 3.8.1.1 actions b. and d. were entered. Investigation later determined that EDG 'A' tripped on Generator Differential due to a failed Current Transformer. EDG 'B' was subsequently started per TS 3.8.1.1 action b.(1). EDG 'B' was declared inoperable due to the room exhaust fan not starting when the diesel engine was started, and TS 3.8.1.1.f. was entered. Troubleshooting determined that the EDG 'B' room exhaust fan did not start due to HVR-501B (EG B ROOM OUTSIDE AIR INTAKE DAMPER) not opening. Action was taken to isolate air and fail HVR-501B to its open safety position. EDG 'B' was declared operable and TS 3.8.1.1.f. was exited following verification of proper operation of the EDG 'B' exhaust fan. For the EDG 'A' Generator Differential trip, the Apparent Cause was determined to be manufacturer fabrication that was less than adequate to preclude component failure, based on external vendor input. For EDG B the Root Cause was determined to be Adequate preventative maintenance tasks were not put in place for EDG B inlet damper components. The air inlet damper and associated actuator, solenoid valve and relays were considered to be fail safe.
3822015008 | Waterford 3 | 10/03/2015 | 12/02/2015 | ML15336A95 | <strong>Automatic Reactor Trip due to Failed Circuit Card In Control Element Assembly Calculator 2</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2015, at 2307 CDT, Waterford 3 experienced an automatic reactor trip and all Control Element Assemblies (CEAs) inserted into the core. Emergency Feedwater (EFW) actuated following the plant trip as expected, but was not required to maintain Steam Generator level. The plant entered the Emergency Operating Procedure for an uncomplicated reactor trip. <br /><br /> The trip was due to Core Protection Calculators (CPC) Channels B and C generating a High Local Power Density (LPD) / Low Departure from Nucleate Boiling Ratio (DNBR) trip due to erroneous signals from Control Element Assembly Calculator (CEAC) 2. Follow up investigation has determined that the direct cause of this event was a failed resistor on a circuit card in CEAC-2. The card was a High Level Multiplexer Gate (Mux) Card (Systems Engineering Laboratories, Model Number 160-100311) in the Multipurpose Acquisition Control System (MACS) Chassis of the CEAC. The direct cause has been corrected by replacing the card. Corrective actions include replacement of additional high level mux cards in a phased approach, development of a performance monitoring plan to identify CEAC card degradation, a full re-analysis of the CPC/CEAC system for Single Point Failure (SPF) vulnerabilities, and implementation of a CPC/CEAC reliability plan.
3872015001 | Susquehanna 1, Susquehanna 2 | 03/02/2015 | 04/28/2015 | ML15118A63 | <strong>Inoperability of the 'B' Emergency Diesel Generator due to Fuel Oil Leakage</strong><br /><i>Abstract:&nbsp;</i>During a routine surveillance test on March 2, 2015, the 'B' Emergency Diesel Generator (DG) was declared inoperable due to fuel oil leakage from the fuel oil drain line crossover piping. The DG was declared inoperable because it was not known if the DG would have been able to meet its mission time due to the risk of fire from the leaking fuel oil. A prompt operability determination performed when the leak was originally identified on January 31, 2015 did not bound the increased leak rate observed on March 2, 2015. The leaking drain line piping was replaced and the 'B' DG was restored to operable on March 3, 2015.<br /><br /> The direct cause of the fuel oil leakage was determined to be fretting, due to normal engine vibration, from the piping rubbing against a metal clamp used to support the piping. The underlying cause of the fretting was determined to be the inadequate design of the support clamp. The design did not take into account the engine vibration and the possibility of fretting-induced wear from metal-on-metal contact. Immediate corrective action was taken to replace the affected piping and complete the routine surveillance test on the 'B' DG. The support clamp was then replaced with a clamp of a different design to account for engine vibration and fretting-induced wear.<br /><br /> Given the location of the affected drain line piping and the design of the fuel oil system, the fuel oil leakage did not adversely impact the supply of fuel oil to the DG to perform its safety function for the required mission time. There were no actual consequences to the health and safety of the public as a result of this event.
3872015002 | Susquehanna 1, Susquehanna 2 | 04/11/2015 | 06/10/2015 | ML15161A48 | <strong>Secondary Containment Inoperability Due to Failure to Meet Technical Specification Surveillance Requirement 3.6.4.1.1</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2015, at 0051 hours, the ventilation system that maintains Secondary Containment at a minimum negative pressure failed requiring entry into the Action Statement for Technical Specification (TS) 3.6.4.1, Condition A, for failure to meet Surveillance Requirement (SR) 3.6.4.1.1 for Susquehanna Steam Electric Station (SSES) Unit 1 and Unit 2. The Reactor Building (RB) Zone II differential pressure fell below the TS limit of 0.25 inches water column (in. w.c.) vacuum when both RB Zone II exhaust fans (2V205A and B) would not develop flow. Operators found the Zone II exhaust fan B discharge damper control air solenoid valve (SV27578B) to be porting air, such that both exhaust fans could not continue to run. The failed solenoid valve was isolated and replaced. TS 3.6.4.1, Condition A, was exited at 0320 hours when the differential pressure was restored to meet the TS limit of 0.25 in. w.c. vacuum.<br /><br /> The condition was reported as an 8 hour Event Notification #50974 in accordance with 10 CFR 50.72(b)(3)(v)(C) for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. This report is in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event that could have prevented the fulfillment of the safety function.<br /><br /> Storage practices for these solenoid valves will be changed to use an appropriate standard, and the preventative maintenance strategy will be revised.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event. An engineering evaluation concludes no Safety System Functional Failure actually occurred as a result of this event.
3872015003 | Susquehanna 1, Susquehanna 2 | 04/21/2015 | 01/26/2016 | ML16026A57 | <strong>Secondary Containment Inoperability due to Failure to Meet Technical Specification Surveillance Requirement 3.6.4.1.1</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2015, at 2258 hours, the Reactor Building ventilation system was unable to maintain a negative pressure in Zone III of Secondary Containment, resulting in entry into Limiting Condition of Operation (LCO) 3.6.4.1, Condition A, for failure to meet Surveillance Requirement (SR) 3.6.4.1.1 on Units 1 and 2. Because the cause analysis was not complete at the time the original LER was submitted, this supplement is being submitted in accordance with NUREG-1022, Rev. 3, Section 5.1.5, Supplemental Information and Revised LERs, to disclose the final cause determination and corrective actions generated. <br /><br /> Per Technical Specification (TS) 3.6.4.1, Secondary Containment must be maintained at 0.25 inches water column (in. w.c.) vacuum. This event was caused by a unique equipment line up coupled with high winds. The apparent cause was determined to be inadequate risk assessment of the test alignment. Corrective actions included reassessing the risk of this alignment and multi-department reviews of test procedures within the Extent of Condition to ensure risk is properly assessed. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event. An engineering evaluation determined no Safety System Functional Failure actually occurred as a result of this event.
3872015004 | Susquehanna 1, Susquehanna 2 | 04/27/2015 | 06/25/2015 | ML15176A84 | <strong>Secondary Containment Inoperable due to Secondary Containment Boundary Door Found Ajar</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2015 at 2230, with Unit 2 shut down for the 17th Refueling Outage, the Shift Manager approved Operations personnel to perform Attachment C, "Operation of 818 Elevation Floor Plug Checklist," in accordance with procedure OP-134-002, "Reactor Building HVAC Zones 1 and 3." This ventilation system realignment was done in support of Unit 2 outage activites to allow equipment to be moved in and out of the 101 railroad bay door. When in this alignment, Door-721 becomes a Secondary Containment boundary door and the door must remain in the closed position. On April 27, 2015, at 0058 hours, Control Room personnel signed off completion of OP-134-002, Attachment C. On April 27, 2015 at 0850 hours, a plant operator found Secondary Containment boundary Door-721 unlatched and protruding out approximately 0.25 inches from the door frame. The plant operator immediately contacted Control Room personnel of the as-found condition of Door-721. As a result, Technical Specification (TS) 3.6.4.1, Condition A, was entered for Unit 1 and 2 due to Secondary Containment being declared inoperable. At 0915 hours on April 27, 2015, TS 3.6.4.1, Condition A, was exited. <br /><br /> On April 27, 2015, at 1546 hours, an 8 hour ENS (#51017) was made to the Nuclear Regulatory Commission in accordance with 10 CFR 50.72(b)(3)(v)(C) for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. SSES has no redundant Secondary Containment system. TS required Secondary Containment differential pressure was maintained throughout the time period that the Door-721 was not fully closed and latched.<br /><br /> The apparent cause of the event was plant personnel did not comply with the signage on Door-721, nor did they challenge the door after passing through it. As a result, Door-721 did not close properly. <br /><br /> Completed Action: Secondary Containment Door-721 was closed. Key Planned Actions: 1) Issue Site Communications to reinforce expectations to site personnel to comply with door signage and the requirement to gently challenge doors (when entering and exiting) in the power block per the plant standards; and 2) Include the expectations in General Employee Training.
3872015005 | Susquehanna 1, Susquehanna 2 | 05/04/2015 | 06/25/2015 | ML15176A81 | <strong>Loss of Secondary Containment Differential Pressure During Ventilation Damper Testing</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage, a clearance order was applied to Unit 2 Zone Ill Reactor Building ventilation exhaust fan inlet dampers in support of maintenance activities on the system. Upon completion of the maintenance activities, the clearance order was removed on May 4, 2015. During removal of the clearance order, the ventilation dampers were repositioned open in anticipation of restoring the Unit 2 Zone Ill Reactor Building ventilation system to service. Following the removal of the clearance order and damper repositioning, a ventilation damper located at the outlet of an exhaust fan was stroked open as part of a maintenance activity. By stroking this outlet damper open a vent path from Zone Ill was inadvertently established and, as a result, Zone Ill differential pressure degraded to below the Technical Specification (TS) Surveillance Requirement (SR) minimum value of 0.25 inch of vacuum water gauge. Limiting Condition for Operation (LCO) 3.6.4.1 was entered at 1439 on both units. The outlet damper was immediately closed and Zone Ill differential pressure was restored to above the TS SR minimum value after approximately two minutes. LCO 3.6.4.1 was exited at 1452. <br /><br /> The apparent cause of the event was determined to be that Operations shift supervision did not adequately assess the impact to the plant prior to releasing stroking of the Zone III exhaust damper. Key planned corrective actions include revising operating and administrative procedures to require applicable dampers to be closed and status control tags applied when either unit's Zone Ill Reactor Building ventilation system is shutdown. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872015006 | Susquehanna 1, Susquehanna 2 | 09/29/2015 | 03/30/2016 | ML16091A01 | <strong>Loss of Safety Function due to Inoperability of Both Trains of the Standby Gas Treatment System and a Loss of Safety Function of the Control Room Emergency Outside Air Supply System due to Air Flow Controller Found in Manual</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2015, at 0900 hours, the 'B' train of the Standby Gas Treatment System (SGTS) was declared inoperable as part of surveillance test SE-030-002B (24-Month Control Structure Ventilation System Operability Test Div II 'B' SGTS). During the test, personnel also commenced testing of the Unit 1 Reactor Pressure Vessel water level instrumentation per SI-180-306 (24-Month Calibration of RWCU PCIS Secondary Containment Isolation and CREOAS Initiation of Reactor Vessel Water Level 2 and MSIV Isolation on Reactor Vessel Water Level 1 for channels LITS-B21-1N026A and B21-1N026C). At 1030 hours, level instrument LITS-B21-1N026A failed its test acceptance criteria, resulting in entry into the Action Statement for TS 3.3.6.2, Condition A. This failed instrument channel is part of the initiation logic for the 'A' train of SGTS. In accordance with TS 3.0.6, since the SGTS is a support system, a loss of safety function determination was performed and concluded the 'A' train of SGTS was inoperable. With both the 'A' and 'B' trains of SGTS inoperable, the Action Statement for TS 3.6.4.3, Condition D, was entered at 1050 hours. At 1456 hours on September 29, 2015, an 8-hour Event Notification (#51432) was made to the NRC per 10 CFR 50.72(b)(3)(v)(c) for a condition that could have prevented the fullfilment of the safety function of the SGTS. On September 30, 2015, during panel walkdowns, it was identified that the 'B' CREOAS system flow controller was still in manual and had not been restored to auto after completion of SE-030-002B on September 29, 2015. As a result, the TS 3.7.3 Action Statement for CREOAS system was entered for the 'B' train being inoperable. In accordance with 10 CFR 50.73(a)(2)(v)(C), this LER is being submitted for any event or condition that at the time of discovery, could have prevented the fulfillment of the safety function of SGTS and the CREOAS system. <br /><br /> Apparent cause: Loss of safety function was not recognized and mitigated when scheduling a surveillance test concurrent with the planned inoperability of the opposite division. Key corrective action: Revise surveillance procedures for instrumentation involving RPS, ECCS initiation, Primary Containment Isolation System (PCIS) and the Secondary Containment Isolation System, to include information on equipment impacts for instruments removed from service, and that redundant equipment is to be operable. There were no actual consequences to the health and safety of the public.
3872015007 | Susquehanna 1 | 11/12/2015 | 01/08/2016 | ML16011A10 | <strong>Unit 1 'B' Inboard Main Steam Isolation Valve, HV141F022B Closed During Surveillance Test Which Caused a Scram on Unit 1</strong><br /><i>Abstract:&nbsp;</i>On 11/12/2015 at 1132 hours, the Unit 1 'B' Inboard Main Steam Isolation Valve, HV141F022B, closed during the performance of SI-183-207, Quarterly Functional Test of Main Steam Line 'C' Flow Channels FIS-B21-1 N008A&B and Main Steam Line 'D' Flow Channels FIS-B21-1N009A&B. This resulted in an automatic SCRAM of Unit 1 on high reactor pressure. <br /><br /> This event was reported under 10 CFR 50.72(b)(2)(iv)(B) and 10CFR 50.72(b)(3)(iv)(A) per the guidance of NUREG 1022, Revision 3, Section 3.2.6. This event is also being reported as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). <br /><br /> The root cause is that the station did not evaluate recommendations made in 2011 by the Boiling Water Reactor Owners Group Instrument and Controls (BWROG l&C) Maintenance Committee to mitigate Primary Containment Isolation System (PCIS) Group 1 Surveillance Testing Risk. It was also determined as a causal factor that there was not specific guidance contained in SI-183-306 (24 Month Calibration Main Steam C/D) which led to an inaccurate field decision when determining the cause of the extinguished light. <br /><br /> Planned corrective actions include evaluating the BWROG l&C Maintenance Committee Recommendation to mitigate PCIS Group 1 Surveillance Testing Risk and then design and implement the proposed modification. Additionally, l&C personnel will perform a review of the population of BWROG recommendations that were issued between January 2011 and December 2013 to ensure they were evaluated. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872015008 | Susquehanna 1 | 11/10/2015 | 12/15/2015 | ML15349A81 | <strong>Unit 1 'A' Reactor Protection System Electrical Protection Assembly Breaker Underfrequency Trip Setpoint Out of Technical Specification 3.3.8.2.2 Surveillance Allowable Value for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2015, during the completion of an evaluation for a failed surveillance test that occurred on September 22, 2015, a condition was identified that in 2014, a degraded Reactor Protection System (RPS) Electrical Protection Assembly (EPA) breaker logic card had been installed in the Unit 1 Reactor Protection System, resulting in an unplanned inoperability of the 'A' train of the Unit 1 RPS. On September 22, 2015, during the performance of routine surveillance testing of the Unit 1 RPS, the as-found underfrequency (UF) trip setpoint for the EPA breaker in the Unit 1 'A' train of the Alternate RPS power supply, could not be determined because the function did not operate at as low as approximately 40 Hertz (Hz). At approximately 40Hz, the undervoltage characteristic took over and issued the trip. The Technical Specification (TS) 3.3.8.2.2 Surveillance Requirement (SR) underfrequency allowable value is > 57 Hz. The UF trip setpoint test was subsequently attempted multiple times with the same result. Because the UF trip setpoint was not achieved, TS 3.3.8.2.2 was not met. Based on the occurrence of a prior failure on September 3, 2000 for the same logic card with the same symptoms as the failure that occurred on September 22, 2015, it was concluded that there is firm evidence that the condition existed prior to discovery on September 22, 2015. Specifically, the condition existed from the time the logic card was installed in the Unit 1 'A' train of RPS on September 25, 2014. Because this condition existed for a period longer than allowed by TS, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.3.8.2.2. The direct cause of the failure of the 1A Alternate RPS breaker was due to an intermittently degraded circuit logic card. The apparent cause was due to the installation of a poor quality spare electrical protection logic card in 2014. The failed logic card was subsequently replaced and the Unit 1 Alternate RPS EPA breaker was declared operable on September 22, 2015. Planned Action: Evaluate vendor diagnosis and repair results for the failed EPA breaker logic card. There were no actual consequences to the health and safety of the public as a result of this event.
3872015009 | Susquehanna 1 | 11/13/2015 | 01/11/2016 | ML16011A41 | <strong>Pressure Boundary Leakage from an Inadequate Weld Repair in Small Bore Pump Seal Vent Piping</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2015, at 1745 hours during drywell entry, a leak was reported on the "B" Reactor Reactor Recirculation (RXR) Pump Lower Seal Cavity Vent piping. The leak was identified at the inboard pipe-to-union weld and required a weld repair prior to returning to service. The affected piping weld is for 3/4-inch piping, schedule 80 SA-479 TP304 or TP316, union 3000# SA-182 Gr F304 or F316. The affected piping had been in service for approximately 11 months following a previous repair of the weld at this location during the December 2014 forced outage, (e.g., LER 2014-011-00, issued February 11, 2015). <br /><br /> The condition was reported on November 13, 2015 in accordance with 10 CFR 50.72(b)(3)(ii)(A) as a principal safety barrier degradation (EN 51538). This Licensee Event Report (LER) is written in accordance with 10 CFR 50.73(a)(ii)(A) and 10 CFR 50.73(a)(2)(i)(B) as a condition that resulted in a principal safety barrier degradation with evidence of reactor coolant pressure boundary leakage, which is a condition prohibited by the Technical Specifications. <br /><br /> The previous December 2014 weld repair did not fully excavate the weld and remove the J-groove, and thereby eliminate the presence of the crack. <br /><br /> Repair of the cracked weld was performed prior to the restart of Unit 1. The safety significance of this condition is minimal. Given the size of the leak, there were no consequences to the health and safety of the public.
3872015011 | Susquehanna 1, Susquehanna 2 | 12/01/2015 | 01/29/2016 | ML16032A41 | <strong>Secondary Containment Declared Inoperable due to an Airlock Door That Had Not Been Properly Latched</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2015 at approximately 1245, a group of plant employees in transit to Unit 2 Reactor Building Elevation 799' approached Airlock Door 638 with the green light lit and opened the door to enter the airlock. Upon opening the door, the red light came on and the buzzer alarmed. Airlock Door 627R (the other door for the airlock) was not properly latched closed, and when the group opened Door 638, the pressure forced Door 627R open. With both airlock doors open simultaneously, Limiting Condition of Operation (LCO) 3.6.4.1 was briefly entered at 1245.<br /><br /> This event was a failure to meet Surveillance Requirement (SR) 3.6.4.1.3 and was reported in accordance with 10 CFR 50.72(b)(3)(v)(c) and the guidance of NUREG 1022 Rev 3 Section 3.2.7 as a condition that could have prevented fulfillment of a safety function (EN 51576). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(c). <br /><br /> The event was caused by the last individual traversing through Door 627R failing to properly latch and challenge the door. A site-wide communication was issued regarding the importance of secondary containment and re-emphasizing the importance of challenging doors to ensure that they are closed and latched. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872015012 | Susquehanna 1, Susquehanna 2 | 12/06/2015 | 02/02/2016 | ML16034A11 | <strong>Loss of Secondary Containment Differential Pressure due to Icing of the Intake Supply Plenum Screens</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2015, at 0350 hours, the Susquehanna Steam Electric Station (SSES) Unit 1 Reactor Building (RB) Zone I Secondary Containment differential pressure lowered to less than 0.25 inch water column (wc) when the intake supply plenum screens were found to be iced over. The icing was the result of freezing fog, causing the loss of the Zone I ventilation. As such, the Action Statement for Technical Specification (TS) 3.6.4.1 Condition A was entered for failure to meet TS Surveillance Requirement 3.6.4.1.1 of >= 0.25 wc vacuum for Unit 1 and Unit 2. TS 3.6.4.1, Condition A, was exited at 0436 hours when the Unit 1 Reactor Building differential pressure returned to 0.33 inches wc vacuum. In accordance with 10 CFR 50.72(b)(3)(v)(C), on December 6, 2015 at 0528 hours, this condition was determined to be reportable to the Nuclear Regulatory Commission (NRC) as an 8 hour ENS (#51587) for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. SSES has no redundant Secondary Containment system. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C), for an event or condition that at the time of discovery, could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material. <br /><br /> The direct cause of the event was due to environmental conditions that resulted in ice formation on the inlet dampers and plenum screens. The apparent cause was less than adequate procedure guidance. The Unit 1 and 2 off-normal procedures for reactor building differential pressure lacked the correct entry condition for personnel to follow.<br /><br /> Completed corrective actions: Revised RB ventilation off-normal procedures to include an entry condition for a plant computer point alarm and actions for operations to check outside weather conditions for fog, and if necessary, increase monitoring/walkdowns of the inlet plenums and remove ice buildup. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872015013 | Susquehanna 1 | 12/06/2015 | 08/05/2016 | ML16218A44 | <strong>Loss of Differential Pressure in Zone I of Secondary Containment due to Solenoid Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2015 at 0546 hours, operations personnel received alarms in the control room indicating the loss of Zone 1 differential pressure (dP). The dP fell below the Technical Specification required limit of 0.25 inches water column (in. w.c.) when the running Reactor Building Zone 1 Exhaust Fan tripped. This required entry into Condition A of TS 3.6.4.1 for failure to meet SR 3.6.4.1.1 on Unit 1. After restoring dP at 0553 hours, Condition A of TS 3.6.4.1 was exited. <br /><br /> This event was reported to the NRC on December 6, 2015 at 0958 hours in accordance with 10 CFR 50.72(b)(3)(v)(c) under Emergency Notification (EN) 51588. This Licensee Event Report (LER) is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The direct cause of the event was determined to be failure of a solenoid valve in the Zone I exhaust fan subsystem. The apparent cause was determined to be vendor parts quality. Completed corrective actions include replacement of the failed solenoid, component and system monitoring for degradation contributors, failure analysis of the failed component by an independent testing laboratory, review of vendor technical information, and identification of a suitable replacement for this model solenoid. Planned corrective actions include replacing similar solenoids in the Reactor Building HVAC system in an expedited manner. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872015014 | Susquehanna 1, Susquehanna 2 | 12/10/2015 | 08/10/2016 | ML16224A11 | <strong>'A' Control Structure Chiller Discovered Inoperable Beyond Technical Specification Limit due to Refrigerant Overcharge</strong><br /><i>Abstract:&nbsp;</i>On 12/10/2015 the 'A' Control Structure Chiller (0K112A) failed 24 month Technical Specification surveillance test due to being overcharged. The power consumption was outside of the acceptance criteria in relation to the quantity of cooling provided. The failure of the test resulted in Operations declaring the chiller inoperable and required entry into the applicable condition for Technical Specification 3.7.4, Control Room Floor Cooling System. During the engineering evaluation of the event it was discovered that the refrigerant charge for the chiller was increased from 1710 pounds to 2010 pounds in January 2014, resulting in the chiller being inoperable for greater than 30 days. An additional review determined that this condition existed previously from 1996 through October 2013. <br /><br /> This event was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, and 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented fulfillment of a safety function.
3882015001 | Susquehanna 2, Susquehanna 1 | 01/21/2015 | 02/10/2016 | ML16041A41 | <strong>Condition Prohibited by Technical Specifications due to Drift of Reactor Pressure Steam Dome - Low Switches</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2015 during quarterly calibration of The Reactor Steam Dome Pressure - Low switches, PIS-B21-2N021A was found outside of the Technical Specification allowable value. PIS-B21-2N021A was restored to within the allowable value. Subsequent evaluation of the switch's history showed that it had drifted outside of its Technical Specification allowable value six times during the last three years. The historical search also identified other related Unit 1 and Unit 2 switches had drifted outside of the allowable value. In addition, on July 26, 2013, two Unit 2 channels (A and B) were found outside of the Technical Specification allowable values. With both the A and B channels inoperable at the same time, the safety functions of both Core Spray and Low Pressure Coolant Injection (LPCI) were impacted; however, Core Spray and LPCI remained capable of performing their design function as analyzed in the FSAR accident analysis. <br /><br /> Based on the historical information, firm evidence is considered to exist to indicate that the condition existed prior to the time of discovery. Based on this conclusion, the condition is considered to be a condition prohibited by Technical Specifications (10 CFR 50.72(a)(2)(i)(B)), a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)), a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)), and a single cause that could have prevented fulfillment of safety functions of trains or channels in different systems (10 CFR 50.73(a)(2)(ix)(A)).<br /><br /> The apparent cause was determined to be less than adequate design in that the design failed to consider the effects of mechanical hysteresis of the subject devices when operated above their normal operating range and did not recognize the seasonal temperature effects to the set points. Key planned corrective actions include replacing the affected switches with switches that are correct for the application. As an interim action, the calibration frequency for the switches has been increased from quarterly to every 45 days. <br /><br /> There were no actual safety consequences associated with this event.
3882015002 | Susquehanna 2, Susquehanna 1 | 03/13/2015 | 05/11/2015 | ML15131A46 | <strong>Secondary Containment Inoperability due to Failure to Meet Technical Specification Surveillance Requirement 3.6.4.1.1</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2015, at 0919 hours, Secondary Containment became inoperable requiring a Technical Specification (TS) 3.6.4.1, Condition A, entry for failure to meet Surveillance Requirement 3.6.4.1.1 for Susquehanna Steam Electric Station (SSES) Unit 1 and Unit 2. The Reactor Building (RB) Zone 2 differential pressure fell below the TS limit of 0.25 inches water column (wc) vacuum, when an air handling plenum door was open for approximately one minute. The LCO was exited at 0930 hours when the differential pressure returned to 0.34 inches wc vacuum. On March 13, 2015, at 1256 hours, this condition was determined to be reportable as an 8 hour ENS (#50885) in accordance with 10 CFR 50.72(b)(3)(v)(C) for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. SSES has no redundant Secondary Containment system.<br /><br /> The direct cause of the event was due to plant personnel holding the RB plenum door open for approximately one minute while performing radiation surveys.<br /><br /> Key Completed Actions: 1) Signs were added to the affected Unit 1 and Unit 2 exhaust fan plenum doors warning of the Secondary Containment implications, and 2) Plant personnel were coached regarding the use of the RB plenum doors. Key Planned Action: Install signs on all major Reactor Building fan plenum doors to alert plant personnel of the Secondary Containment impacts.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event. An Engineering evaluation concluded that Secondary Containment could have performed its safety function of isolating as assumed in the SSES accident analysis and also of re-establishing 0.25 inches wc vacuum (i.e., drawdown time) within the assumed accident analysis time of 10 minutes.
3882015003 | Susquehanna 2 | 04/10/2015 | 06/08/2015 | ML15160A01 | <strong>Unit 2 Automatic Reactor Scram Caused by Main Turbine Trip Due to Loss of Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2015, at 2100 hours, a planned shutdown for the Susquehanna Unit 2 refueling outage commenced. With shutdown in progress and at approximately 37% power for balance of plant operations, a pre-job brief was conducted in preparation for placing an Auxiliary Boiler in service and placing the Main Turbine Steam Seals on Auxiliary Steam. At 2129 hours, the 'A' Auxiliary Boiler was placed in service per procedure OP-027-001, "Aux Boiler System," and the Main Turbine Steam Seals were placed on auxiliary steam via valve 221008, "SJAE and Steam Seal Aux Supply !so Vlv." At approximately 2330 hours, the procedure was resumed which directed closure of valve 221008 when Auxiliary Boiler temporary load is no longer needed. At this point, temporary load was no longer needed but auxiliary steam was still flowing through valve 221008, supplying steam to the Unit 2 Main Turbine Steam Seals. The valve was subsquenty closed, which isolated steam to the U2 Main Turbine Steam Seals, allowing air in-leakage into the Main Condenser, causing condenser vacuum to degrade. At 2346 hours, Unit 2 automatically scrammed from approximately 37 percent power due to a the Main Turbine trip on loss of condenser vacuum. Root Cause: Personnel involved with auxiliary boiler startup did not adhere to Operator Fundamentals and effectively apply appropriate Human Performance error-reduction tools specific to understanding and anticipating the impact of component operation prior to its operation. Completed Action: Procedure OP-027-001, "Auxiliary Boiler System," was revised to caution operators of the potential for isolating auxiliary steam to the Main steam seals and/or Steam Jet Air Ejectors when securing temporary loading of the auxiliary boilers. Key Planned Action: Provide initial licensed and non-licensed operator classroom and job performance measure or dynamic learning activity training with focus on: STAR, Questioning Attitude, Pre job Brief, and understand and anticipate the impact of component operation prior to its operation. Safety Significance: There were no actual consequences to the health and safety of the public as a result of this event.
3882015004 | Susquehanna 2 | 04/11/2015 | 06/10/2015 | ML15161A00 | <strong>Degraded Condition Due to Reactor Coolant Pressure Boundary Leakage Caused by Vibration and Stiff Pipe Connection</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2015, during the initial drywell walk down following shutdown for a refueling outage, a leak was identified on the Unit 2 "A" Reactor Recirculation Pump seal piping at a seal flange weld associated with the pressure and vent piping to the upper seal chamber (Connection #2). Water was seen spraying out of the top of the pipe in a fan pattern.<br /><br /> This event was reported under 10 CFR 50.72(b)(3)(ii)(A) per the guidance of NUREG 1022, Revision 3, Section 3.2.4 as a degraded condition (EN 50976). This event is also being reported as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(ii)(A) and 10 CFR 50.73(a)(2)(i)(B).<br /><br /> The direct cause of the weld crack was determined to be high cycle, low amplitude vibration fatigue. The apparent cause involved the combined effects of an unrecognized system vibrational mode and a stiff pipe connection to the seal flange. Causal factors included the presence of a stress concentrator (minor lack of fusion) on the root of the weld and two early life cavitation events in 1983. Piping configurations for the Unit 2 pumps were modified to add flexibility in the pipe run between the seal flange and first support and to minimize vibration modes coincident with known pump resonance frequencies 1X, 2X, and 5X. Piping configurations will be modified for Unit 1 during the next refueling outage (the affected connections on Unit 1 are not reactor coolant pressure boundaries).<br /><br /> There were no actual consequences to the health and safet of the public as a result of this event.
3882015005 | Susquehanna 2 | 04/14/2015 | 06/10/2015 | ML15161A00 | <strong>Condition Prohibited by Technical Specifications due to Implementation of Enforcement Guidance Memorandum (EGM) 11-003</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this Licensee Event Report (LER) was an expected condition, which was the result of planned activities in support of a routine refueling outage. As described in the LER, the U. S. Nuclear Regulatory Commission (NRC) provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS).<br /><br /> Between 4/14/2015 and 5/16/2015, Susquehanna Steam Electric Station (SSES) performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities on Unit 2 while in Mode 5 without an operable secondary containment, as expected and allowed by the enforcement guidance. Although NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 2 allows the implementation of interim actions as an alternative to full compliance, this condition is still considered a condition prohibited by TS 3.6.4.1. The OPDRV activities were planned activities that were completed under the guidance of plant procedures and are considered to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request will be submitted following NRC approval of the Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue.
3882015006 | Susquehanna 2, Susquehanna 1 | 07/27/2015 | 09/18/2015 | ML15265A33 | <strong>Secondary Containment Declared Inoperable due to Secondary Containment Boundary Door 104-R Breached</strong><br /><i>Abstract:&nbsp;</i>On Monday, July 27, 2015, Susquehanna experienced Reactor Building differential pressure less than 0.25 inches water column when a Secondary Containment boundary door (Door 104-R) was breached. As a result, Secondary Containment was declared inoperable and Susquehanna entered Technical Specification 3.6.4.1. <br /><br /> This event was reported under 10 CFR 50.72(b)(3)(v) per the guidance of NUREG 1022, Revision 3, Section 3.2.7 . This event is also being reported as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The apparent cause involved a Unit Supervisor (Senior Reactor Operator) failing to follow the standard to verify the impacts of opening the 104-R door. The causal factor was that multiple work groups displayed a less than adequate questioning attitude and use of three-way communication. <br /><br /> Planned corrective actions include General Employee Training (GET) changes, updating maintenance documents associated with the activity being performed when the door was breached, publishing a station communication associated with the event, changing out the lock to Door 104-R so that the lock differs from the lock to access the roof from other locations, and coaching the Unit Supervisor involved in this event. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882015007 | Susquehanna 2 | 09/30/2015 | 11/25/2015 | ML15329A01 | <strong>Primary Containment Isolation Valve Failure due to Sticking/Sluggish Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2015, the Unit 2 Reactor Water Sample Outboard (OB) Isolation Valve (HV243F020) failed Inservice Testing (IST) stroke time surveillance testing. The close stroke was timed at 3.85 seconds (the acceptance criteria requires closure in less than or equal to 2 seconds). This required entry into Limiting Condition for Operation (LCO) 3.6.1.3 Condition A. <br /><br /> Based on the history and cause, Susquehanna concluded that firm evidence existed that the condition existed prior to discovery on September 30, 2015 for a period longer than allowed by Technical Specifications. As a result, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The direct cause was sticking/sluggishness of Solenoid SV24320 resulting in excessive closed stroke time. <br /><br /> The apparent causes were less than adequate corrective action following HV243F020 stroke time failure on July 1, 2015 and less than adequate Preventive Maintenance (PM) strategy for HV243F020/SV24320.<br /><br /> Immediate corrective action included replacing the faulty solenoid valve, and actions are planned to revise the HV243F020 actuator overhaul preventive maintenance scope to include solenoid valve replacement. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882015010 | Susquehanna 2, Susquehanna 1 | 11/12/2015 | 07/06/2016 | ML16188A18 | <strong>Supplemental Report to LER-2015-010-00, Loss of Differential Pressure in Zone II of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2015, at 1132 hours, the Reactor Building Zone II ventilation system was unable to maintain a negative pressure in Zone II of Secondary Containment resulting in failure to meet Surveillance Requirement (SR) 3.6.4.1.1 on Unit 2. <br /><br /> Per Technical Specification (TS) 3.6.4.1, Secondary Containment must be maintained at 0.25 inches water column (in. w.c.) vacuum. In this event, Zone II differential pressure (dP) was oscillating between 0.23 and 0.43 in. w.c. vacuum, which is outside the TS requirement. The oscillations subsided at 1501 and Zone II dP continued to be maintained at approximately 0.35 in. w.c. vacuum. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event. An engineering evaluation determined no Safety System Functional Failure actually occurred as a result of this event. The direct cause of this event was determined to be the change of air flow in the Unit 2 Reactor Building Exhaust Stack. The apparent cause of this event was determined to be a parts defect within a controller used to develop proper differential pressure within Zone 2. Immediate corrective action was taken to restore Zone 2 differential pressure. A planned corrective action to replace the controller has been generated.
3882015015 | Susquehanna 2, Susquehanna 1 | 10/03/2014 | 05/05/2016 | ML16127A01 | <strong>Loss of Safety Function due to Inoperability of Both Trains of the Control Room Emergency Outside Air Supply (CREOAS) System</strong><br /><i>Abstract:&nbsp;</i>This Licensee Event Report (LER) is being submitted to the Nuclear Regulatory Commission (NRC) for an event that occurred on October 3, 2014. On October 2, 2014, the 'B' Control Structure Chiller and the 'B' Control Room Emergency Outside Air Supply (CREOAS) system were declared inoperable for the performance of surveillance test SO-030-B03 (Quarterly Control Structure Chilled Water Flow Verification Loop 'B'). The Action Statement for Unit 2 TS 3.7.3, Condition A, was entered at 1445 hours for one CREOAS subsystem inoperable. The surveillance was completed and the TS Action Statement was exited at 1608 hours. During a closure review of the completed surveillance test on October 2, 2014, it was identified that the results of the test were found to be outside of the test acceptance criteria. Since the Unit 2 TS Action Statement for TS 3.7.3, Condition A had been previously exited at 1608 hours, Operations personnel re-entered the TS Action Statement from the original time of inoperability (1445 hours) until the surveillance test could be re-performed. On October 3, 2014, at 1530 hours, the test was successfully re-performed and the TS 3.7.3 Action Statement was exited. Earlier on October 3, 2014 at 0937 hours, surveillance test SI-280-306 (24 Month Calibration of RWCU PCIS Secondary Containment Isolation and CREOAS System Initiation of Reactor Vessel Water Level 2 and MSIV Isolation on Reactor Vessel Water Level 1 for Changes LITS-B21-2N026A&C) was commenced. As part of the test, the Unit 2 Reactor Vessel Water Level Low-Low, Level 2 instrumentation (LITS-B21-2N026A) was isolated. This resulted in the 'A' train of the CREOAS system also being inoperable because in accordance with TS 3.0.6, the reactor vessel water level instrumentation is a support system for the 'A' train of the CREOAS system. In accordance with 10 CFR 50.73(a)(2)(v)(C), this LER is being submitted for an event or condition that could have prevented the fulfillment of the safety function of the CREOAS system to control the release of radioactive material. Cause: A loss of safety function of the CREOAS system was not recognized or mitigated when TS surveillance test SO-030-B03 carried over into the next day while the planned inoperability of the opposite division of CREOAS occurred during the performance of TS surveillance SI-280-306. Key planned corrective action: Revise station procedure to direct performance of a LOSF review prior to releasing any RPS, ECCS initiation, PCIS or SCIS related surveillance activities. There were no actual consequences to the health and safety of the public as a result of this event.
3892015001 | St. Lucie 2 | 04/11/2015 | 06/10/2015 | ML15173A07 | <strong>Unit 2 Shutdown due to Through Wall Crack and Leak in the 2B2 Safety Injection Tank Discharge Pipe</strong><br /><i>Abstract:&nbsp;</i>On 4/11/2015 at 1204 EDT, a through wall leak was identified during an investigative walk down of the 12-inch diameter Class 2 piping for the 2B2 safety injection tank (SIT) discharge header. Operators declared the SIT inoperable and Technical Specification Limiting Condition of Operation (LCO) 3.5.1 action "b" was entered, which required the SIT to be restored to Operable status within 24 hours or shut down to Mode 3 within the next 6 hours. In accordance with Technical Specifications (TS) and plant procedures, operators subsequently shut down the unit to repair the leak. The shutdown was uncomplicated and all plant safety systems functioned as designed. The leaking piping was replaced and returned to service on 4/18/2015. A sample of the failed pipe was sent to a metallurgical laboratory for examination. Results of optical and electron microscopic evaluations revealed the cause of failure as low stress high cycle fatigue. <br /><br /> This condition is reportable in accordance with the following requirements: 1) 10 CFR 50.73(a)(2)(i)A, "The completion of a nuclear plant shutdown required by the plant's Technical Specifications," and 2) 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." This condition was determined not to have a significant impact on the health and safety of the public, since the identified leakage was well within the plant capability to maintain SIT requirements and was insignificant as compared to either the SIT discharge flow rate or the safety injection flow rate during design basis events.
3892015002 | St. Lucie 2 | 09/17/2015 | 11/16/2015 | ML15329A37 | <strong>2A Emergency Diesel Generator Actuation Logic</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2015, at 1222 hours, with Unit 2 in Mode 5 at the beginning of a refueling outage, an electrical fault on the 2A 6.9 kV bus resulted in the loss of the 2A startup transformer (SUT) and its associated non-safety related 2A2 and safety-related 2A3 buses. The loss of the 2A SUT actuated the under-voltage relays that would have started the 2A EDG, which had been properly removed from service for preplanned maintenance. The root cause was that the protective boots for a bus bar bolted connection on a vertical riser were not installed (left between bus conductors) during initial plant construction. <br /><br /> Immediate corrective actions included extensive inspections and repair of the remaining vertical portions of this bus. Follow-up corrective actions include performing internal visual inspections of remaining vertical sections of nonsegregated buses to ensure that bolted connections have properly installed protective boots. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of an EDG. All safety related systems functioned as designed.<br /><br /> This event had no effect on the health and safety of the public.
3892015003 | St. Lucie 2 | 10/19/2015 | 12/18/2015 | ML16015A00 | <strong>Legacy Wiring Error Impacts Containment Valve Closure Time Surveillances</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2015, during corrective maintenance activities on containment isolation valve FCV-26-3, maintenance personnel discovered that the valve actuator position limit switches were not wired correctly since December 2001. This condition invalidated previous closure time surveillance results for this valve.<br /><br /> This condition is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The wiring discrepancy was caused by a legacy maintenance human performance issue. The limit switch wiring was corrected, the post-maintenance testing was completed satisfactorily, and the valve was returned to service.
3902015001 | Watts Bar 1 | 02/21/2015 | 04/22/2015 | ML15112A72 | <strong>Manual Reactor Trip Initiated due to Rapid Loss of Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2015 at approximately 10:32 am Eastern Standard Time (EST), the Watts Bar Nuclear Plant Unit 1 reactor was manually tripped by control room operators due to a decreasing main condenser vacuum. Subsequent to the reactor trip, the Auxiliary Feedwater system actuated. Control and Shutdown rods fully inserted into the reactor core, and safety systems responded as designed. The unit was stabilized in Mode 3, with decay heat removal via Auxiliary Feedwater and the Steam Generator Atmospheric Dump Valves. The Main Steam Isolation Valves were closed and remained closed during the event.<br /><br /> Tennessee Valley Authority (TVA) has determined that the decreasing condenser vacuum was due to a failure of an expansion joint boot seal in the "C" zone of the main condenser. This seal functions as the expansion joint between the condenser and low pressure turbines. The failure of the seal was due to a non-optimal vulcanization process and inadequate overlap in a joint splice, which significantly weakened the seal and allowed seal water to permeate the seal, further weakening the joint. The failed main condenser boot seal was replaced with a new boot seal on the "C" zone of the condenser. As a preventative measure, the boot seals on the "A" and "B" zones were also replaced.
3902015005 | Watts Bar 1 | 09/16/2015 | 11/16/2015 | ML15320A29 | <strong>Failure to Enter Technical Specification 3.6.12, Ice Condenser Doors, Condition B and Perform Required Actions</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2015, at 0536 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) operations personnel received a report from maintenance personnel that a scaffold was found blocking four (4) intermediate deck doors in the WBN Unit 1 upper ice condenser. Based on this report, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.12 Condition B was entered, requiring that the maximum ice bed temperature is verified to be less than 27 degrees F once per four hours (Action B.1) and to restore the doors to OPERABLE status in 14 days (Action B.2). <br /><br /> Based on a review of maintenance records, maintenance was authorized to build the scaffold on September 8, 2015. Assuming it was built the same day, the fourteen day completion time of TS 3.6.12 Action B.2 was not exceeded. A review of ice bed temperatures between September 8, 2015 and the time the scaffold was removed (September 17, 2015) show that ice bed temperatures never exceeded 27 degrees F as required by TS 3.6.12 Action B.1. <br /><br /> Because the plant staff did not enter TS 3.6.12 Condition B and monitor ice bed temperatures every four hours when the scaffolding was authorized to be built, this condition is reportable as an operation or condition prohibited by Technical Specifications, and is reportable per 10 CFR 50.73(a)(2)(i)(B).
3902015006 | Watts Bar 1 | 10/19/2015 | 12/21/2015 | ML15355A52 | <strong>Source Range Level Trip Channels (N-31 and N-32) Inoperable During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2015, at approximately 1000 Eastern Daylight Time (EDT) with the reactor at 27 percent rated thermal power (RTP), the operating crew identified both Source Range (SR) Level Trip Channels (N-31 and N-32) were in the bypassed position. An incident prompt investigation determined that the SR trip functions were inoperable from the time the reactor trip breakers (RTBs) were closed in Mode 3 on October 19, 2015, at 2139 EDT until reactor power exceeded the P-6 permissive interlock (1.66E-4 percent RTP) on October 21, 2015, at 0623 EDT. Under these conditions Technical Specification (TS) 3.3.1, Required Action J.1, required that the operators take immediate actions to open the RTBs. This action was not performed because the operators were not aware that the SR level trip channels were bypassed at the time the RTBs were closed. As a result, this event is reportable as an operation or condition which was prohibited by the plant's TS. The SR level trip channels were restored to normal position on October 22, 2015, at 1258 EDT.<br /><br /> With reactor power below the P-6 interlock, the intermediate and power range detectors were active and provided protection. However, because the SR level trip channels were inoperable this condition is also reportable as a condition that could have prevented the fulfillment of a safety function needed to shut down the reactor and maintain it in a safe shutdown condition.
3952015001 | Summer 1 | 03/17/2015 | 05/12/2015 | ML15135A23 | <strong>Reactor Building Spray Isolation Valve Failure Renders Train of Reactor Building Spray Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2015 a past operability review determined that XVG03005A-SP, Outside Reactor Containment (ORC) Reactor Building (RB) Spray Sump Isolation Valve A, was inoperable due to failure to fully stroke open during a surveillance test. XVG03004A-SP, Inside Reactor Containment RB Spray Sump Isolation Valve A, and XVG03005A-SP automatically open on receipt of RWST Lo-Lo Level coincident with a SI signal to transfer XPP0038A, Reactor Building Spray Pump A, suction from the RWST to the RB Sumps. XVG03004A-SP and XVG03005A-SP are also logically tied to XVG03001A-SP, RB Spray Pump A RWST Suction Header Valve. The full-open limit switches on XVG03004A-SP and XVG03005A-SP initiate automatic closure of XVG03001A-SP. Since XVG03005A-SP did not stroke fully open, the automatic swapover sequence could not have been completed, rendering the "A" train of RB Spray inoperable.<br /><br /> The cause of XVG03005A-SP to fully stroke open was due to spring pack relaxation and associated torque switch setting tolerances which resulted in the torque switch opening prior to the valve reaching the 100% open limit switch.<br /><br /> The torque switch setting was adjusted from 1 to 1.5 to allow higher developed torque before the switch opens to trip the motor. This adjustment will also reduce the effects from spring pack relaxation.
3952015002 | Summer 1 | 04/09/2015 | 06/08/2015 | ML15160A60 | <strong>Low Oil Level Trip Renders Chiller Non-functional and "A" Train of Charging System Inoperable</strong><br /><i>Abstract:&nbsp;</i>A past operability review determined that HVAC System Mechanical Water Chiller (X11X0001A) had been non-functional during the month of July 2013 due to a vulnerability with component operation resulting in a low oil level condition. The event impacts the operability requirements of the Chilled Water (VU) System and the area room coolers the system supports per TS 3/4.7.9, "Area Temperature Monitoring."<br /><br /> On September 25, 2013, XHX0001A tripped on low oil level following surveillance testing. The "Circuit 2 Low Oil Level" fault occurred due to the compressor oil level dropping below the low oil level indicator switch set point for 60 seconds which initiates shutdown of the component. The cause was low superheat, causing liquid floodback to the compressor and a low evaporator heat load that was insufficient to promote proper oil return in the evaporator. The chiller unit was intermittently operated as the only chiller on the "A" VU train in July 2013. Due to this vulnerable condition the non-functional chiller impacted the operability of the "A" train components served by the "A" train VU system.<br /><br /> On April 9, 2015, the station determined this event was reportable and is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B).
3972015001 | Columbia | 03/02/2015 | 04/30/2015 | ML15120A64 | <strong>Non-Conservative Compensatory Measure for Flooding Barriers</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2015, it was identified that Columbia Generating Station’s (Columbia) barrier impairment procedure which allowed for floor plugs in the room above the Emergency Core Cooling System (ECCS) and Reactor Core Isolation Cooling (RCIC) System pump rooms to be removed was non-conservative and Columbia had been non-compliant with Technical Specifications. Specifically, from December 3, 2014, until December 19, 2014, floor plugs over Residual Heat Removal (RHR) System B pump were removed without an adequate flood barrier resulting in RHR System B being inoperable. The barrier impairment procedure allowed for removal of ECCS or RCIC floor plugs with either a one hour flood tour or installation of a berm as a compensatory measure to maintain operability of the applicable ECCS or RCIC System. A one hour flood tour was initiated per the procedure, and a berm was erected; however both the one hour flood tour and the berm were inadequate. Corrective actions planned to prevent recurrence includes revising the barrier impairment process.
3972015002 | Columbia | 04/29/2015 | 06/26/2015 | ML15188A05 | <strong>Inadequately Fused Non-Class 1E Circuit on Division 1 120/240 VAC Bus</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2015, it was determined that the Division 1 120/240 volts alternating current (VAC) vital instrumentation bus had been inoperable since July 1993. This was the result of a plant modification that added a vendor control panel for the reactor building effluent monitor containing a Non-Class 1E cooling fan with only a single fuse isolation protection. A coordination study was conducted to provide a detailed review for the electrical coordination of the Division 1 120/240 VAC bus. This detailed review revealed that there was an electrical coordination issue with this bus and a Non-Class 1E electrical cabinet cooling fan load that may occur under very limited conditions. In the event that a short circuit occurs in the cooling fan coincident with a loss of off-site power, there was not an adequate isolation device between the Class 1E source and the Non- 1E load such that the fault on the cooling fan could potentially impact the Division 1 120/240 VAC bus and cause an under voltage condition due to the limitations in the short circuit design capacity of the associated inverters.
3972015003 | Columbia | 05/13/2015 | 07/07/2015 | ML15188A41 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 2</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this LER was an expected condition, which was the result of planned activities in support of a routine refueling outage. As described in the LER, the U.S. Nuclear Regulatory Commission (NRC) provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). <br /><br /> Between May 13, 2015 and June 13, 2015, Columbia Generating Station (Columbia) performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities while in Mode 5 without an operable secondary containment, as expected and allowed by NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 2. Although EGM 11-003, Revision 2, allows implementation of interim actions as an alternative to full compliance, this condition is still considered a condition prohibited by Technical Specification (TS) 3.6.4.1. The OPDRV activities were planned activities that were completed under the guidance of plant procedures and work instructions and are considered to have low safety significance based on the interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request will be submitted following NRC approval of the Technical Specification Task Force (TSTF) traveler associated with generic resolution of this issue.
3972015004 | Columbia | 05/22/2015 | 07/20/2015 | ML15202A06 | <strong>Unplanned Loss of 4.16KV Bus 7 Switchgear</strong><br /><i>Abstract:&nbsp;</i>This event is being reported as an unplanned actuation of an emergency diesel generator, in conformance with reporting requirements in 10 CFR 50.73(a)(2)(iv)(A). Refer to Columbia Generating Station's Event Notification No. 51086. <br /><br /> On May 22, 2015, during a refueling outage with the plant in Mode 5, electricians in support of testing on the Division 1 Emergency Diesel Generator installed 3 test meters to monitor the under voltage relay in the Division 1 4.16KV Bus 7 Switchgear (E-SM-7) cabinet. Prior to commencing the testing one of the test leads connecting the test meters to the Bus 7 Switchgear cabinet became detached from the test instrument. When one of the electricians reconnected the test lead, it was inserted into the wrong port on the test instrument, causing a phase-to-phase short which resulted in a momentary loss of Bus E-SM-7. The Bus was being powered from the Startup Transformer. The Backup Transformer sensed the loss and re-powered Bus E-SM-7. In addition, the Division 1 Emergency Diesel auto-started on bus under voltage and was subsequently removed from service when the Standby Service Water pump failed to start as a result of a blown fuse caused by the short. <br /><br /> The Division 2 electrical distribution was providing the electrical power and supporting components required for decay heat removal and inventory control at the time of the event and was not impacted by the event.
3972015005 | Columbia | 06/25/2015 | 08/20/2015 | ML15233A40 | <strong>Reactor Pressure Vessel Level Indication Switch Failures</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2015 it was discovered that Columbia Generating Station's (Columbia) Reactor Protection System (RPS) trip logic was unable to generate a full scram on Reactor Pressure Vessel (RPV) low level because RPS 'A' level 3 indicating switches were mechanically bound high off scale. Immediate actions were taken to comply with Technical Specifications, and a half scram was generated on RPS trip system 'A' to restore full scram capability. Corrective actions include aligning Columbia's maintenance procedures with vendor recommendations, establishing preventative maintenance to ensure correct setting of the indicating switches and verification that level switches are on scale prior to entering the mode of applicability.
3972015006 | Columbia | 07/06/2015 | 12/22/2015 | ML16011A11 | <strong>Postulated Multiple Spurious Operations Scenario That Could Adversely Impact Post-Fire Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>On July 6, 2015, a review of the Fire Protection and Post Fire Safe Shutdown programs found the original assessment of Multiple Spurious Operation (MSO) Scenario 2x incorrectly concluded that the number of circuit failures was above and beyond the technical requirements. This error resulted in no analysis of MSO Scenario 2x, an unanalyzed PFSS condition, and is being reported in conformance with the reporting requirements of 10CFR 50.73(a)(2)(ii)(B). <br /><br /> In addition this was reported to the NRC man 8-hour report (Event Notification No. 51201) in accordance with 10 CFR 50.72(b)(3)(ii)(B). <br /><br /> Corrective actions include a revision to the calculation to include a re-evaluation of MSO Scenario 2x, maintaining the affected line isolated until a permanent solution for MSO Scenario 2x is developed, and procedure changes to provide more technical guidance for evaluation of PFSS MSO scenarios:
3972015007 | Columbia | 11/09/2015 | 01/07/2016 | ML16007A75 | <strong>Reactor Building Pressure Greater than Technical Specifications Requirement</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2015 at 20:40 PST, Secondary Containment (Reactor Building) became inoperable due to pressure increasing above the Technical Specifications (TS) limit of -0.25 inches water gauge (inwg). <br /><br /> At the time of the event the Division 2 Reactor Building Heating, Ventilation and Air Conditioning System (HVAC) was controlling Secondary Containment differential pressure. Power supply E-E/S-299 then failed, causing Division 2 Secondary Containment Pressure controller to lose power. This resulted in the Division 2 Reactor Building Exhaust Fan flow being reduced, causing Secondary containment pressure to rise above TS limit of -0.25 inwg. <br /><br /> Operations personnel manually started the Division 2 SGT lead fan to restore negative pressure. The lead fan operated at max flow (due to the failure of E-E/S-299) resulting in the restoration of Secondary Containment pressure to within TS limits. <br /><br /> The Division 1 HVAC was manually started, allowing Operations personnel to manually secure the Division 2 SGT lead fan and maintain Secondary Containment pressure. <br /><br /> The direct cause for the loss of E-E/S-299 was due to an incorrect lug size installed in the fuse block during initial construction. Current procedures are adequate to prevent a similar error.
4002015001 | Harris | 03/12/2015 | 05/11/2015 | ML15131A56 | <strong>Safety Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2015, while operating at 100% power in mode one, surveillance testing identified the lift setting of main steam (MS) safety valve (SV) 1MS-49 was outside of the technical specification (TS) allowed tolerance. Testing of all other installed MSSVs identified four additional MSSVs that were also outside of the TS allowed tolerance. On April 9, 2015, while shutdown for a refueling outage, pressurizer SV 1RC-127 was found outside its TS allowable tolerance. The primary cause of the SV lift settings being outside of the TS allowed tolerance was setpoint drift incompatible with analysis specified criteria. 1RC-127 was also determined to have an operating history of being outside of tolerance when tested. The valve installed as 1RC-127 was removed from service, and all six valve lift settings have been restored to within the allowable tolerance. The 1% TS tolerance is more restrictive than the American Society of Mechanical Engineers code allowed tolerance of 3%. The primary corrective action to preclude recurrence will be implementation of a revised safety analysis that accommodates increased setpoint drift and supports revised technical specification setpoints. The condition is similar to that reported in licensee event report 2013-002-00. The small deviations beyond the allowable tolerance result in a very low safety significance.
4002015002 | Harris | 04/04/2015 | 06/03/2015 | ML15161A31 | <strong>Breakers to the 'A' and 'B' Train Control Room Normal Intake Isolation Damper Motor Actuators Tripped Open</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2015, Harris Nuclear Plant was shut down for a scheduled refueling outage in mode 5 and was performing the Remote Shutdown System Operability test. Following transfer back to the Main Control Board, the supply breakers to the normal air intake isolation dampers' motor actuators both independently tripped due to high instantaneous current from the attempted direction reversal of their respective motor actuators. These trips caused both dampers to be in the partially open position, rendering the Control Room Envelope (CRE) boundary inoperable. The apparent cause of this event is that the HMCP model breaker/starter combination installed by a Design Change is more sensitive to peak current spikes than the original EF3 model breakers. The contributing cause associated with this event was that industry operating experience (OE) was not adequately reviewed to identify existing OE on the need to raise the trip setting on HMCP model breakers. Immediate corrective action was taken to manually close the dampers and restore integrity of the CRE boundary. The corrective action taken to address the breaker sensitivity observed was that the trip settings for the impacted HMCP model breakers installed by the Design Change were revised to add margin to the trip settings.
4002015003 | Harris | 04/07/2015 | 05/28/2015 | ML15148A52 | <strong>Reactor Pressure Vessel Head Penetration Nozzle Indications Requiring Repair Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2015, and April 9, 2015, the reactor vessel head penetration nozzles were being examined while the Harris Nuclear Plant was shut down for a scheduled refueling outage. Ultrasonic examinations identified indications that required repair in three head penetration nozzles. The indications were approximately 0.233, 0.260, and 0.297 inches long in nozzles 14, 18, and 23 respectively, and axial in orientation. The maximum through-wall extent was approximately 32%. An inspection of the exterior surfaces of the reactor head confirmed there was no leakage. The indications were repaired using the inside diameter temper bead welding process. The repairs restored compliance with the American Society of Mechanical Engineers code requirements.<br /><br /> The cause of the indications was attributed to primary water stress corrosion cracking. Per the requirement of 10 CFR 50.55a(g)(6)(ii)(D)(5), examinations are required to be performed on the reactor vessel head every refueling outage to identify flaws and ensure appropriate repairs are performed. This is similar to the conditions reported in Harris Licensee Event Reports 2013-001-00 and 2013-003-00.
4002015004 | Harris | 05/04/2015 | 08/20/2015 | ML15232A05 | <strong>Failure of 'A' Train Emergency Service Water Pump</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2015, while Harris Nuclear Plant, Unit 1 was shut down for a scheduled refueling outage in mode 5, the Operations Surveillance Test for Safety Injection, Engineered Safety Feature Response Time on Train B, was being performed. During this test the 'A' Emergency Service Water (ESW) pump failed, resulting in a loss of flow and pressure to the 'A' ESW header. The probable root cause of this event was determined to be a misalignment stemming from a combination of potential factors. The contributing cause of this event was determined to be that performance monitoring was not rigorous enough to identify potential pump issues prior to failure. Immediate corrective action was taken to secure the corresponding charging/safety injection pump and emergency diesel generator and to realign the Normal Service Water to the 'A' ESW header. The 'A' ESW pump was rebuilt with new couplings, coupling fasteners, and bearings prior to plant startup that commenced on May 13, 2015. Planned corrective actions include a procedure revision to implement a process for performing vertical alignment checks during ESW pump installation and modifications to improve ESW coupling design.
4002015005 | Harris | 06/16/2015 | 08/17/2015 | ML15230A00 | <strong>Unrecognized Impact of Opening of Barrier Doors on High Energy Line Break Analysis</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2015, while Harris Nuclear Plant (HNP) was operating at 100% in mode 1, two doors between the Reactor Auxiliary Building (RAB) and Main Steam Tunnel (MST) were opened to support a maintenance activity. These doors are credited in the high energy line break (HELB) equipment qualification and internal flooding analyses for HNP; however the opening of these doors is not addressed in these analyses. If a HELB occurred in the MST during a time in which these doors are open, the Essential Services Chilled Water system could become inoperable. <br /><br /> The root cause of this event was determined to be that HNP Engineering failed to develop and implement control measures for hazard barriers credited for mitigating HELB events. Immediate corrective action was taken to close the doors and issue a Standing Instruction that prohibits these doors from being blocked open during modes 1 through 4. Corrective action is planned to develop and implement an engineering change that evaluates the required passive design features needed to support HELB analysis and overall licensing bases. This engineering change will identify required passive design features and establish the necessary process to ensure barriers are appropriately identified and controlled.
4102015001 | Nine Mile Point 2 | 01/12/2015 | 03/12/2015 | ML15078A04 | <strong>Secondary Containment Inoperable due to Sustained High Winds</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2015 at 1939, Nine Mile Point Unit 2 declared secondary containment inoperable due to secondary containment vacuum decreasing below the technical specification limit. The condition is reportable under 10 CFR 50.72 (b)(3)(v)(C) and 10 CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The change in secondary containment vacuum was the result of sustained high winds. Secondary containment was declared operable at 1956 when secondary containment vacuum was restored to greater than 0.25 inches of vacuum water gauge. The apparent cause evaluation identified inadequate system balancing and failure to adjust the inlet damper after filter bag removal for seasonal readiness which allowed a volume increase that was beyond the control capability of the pressure control dampers during a high wind event. Corrective actions taken include adjusting Reactor Building intake dampers to lower supply fan flow to bring recirculation motor operated dampers into their control range and to adjust other system lineups until the dampers begin to modulate.<br /><br /> The event described in this LER is documented in the plant's corrective action program as IR# 2436393. NMP2 LER 2014-005 reported a similar event.
4102015002 | Nine Mile Point 2 | 02/18/2015 | 04/20/2015 | ML15142A72 | <strong>Manual Reactor Scram due to Unexpected Reactor Water Level Change</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2015, at 1406, Nine Mile Point Unit 2 inserted a manual reactor scram due to rapidly rising reactor water level. This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The Reactor Protection System (RPS) was manually actuated, resulting in a reactor scram. The rapidly increasing reactor water level was due to the lifting and separating of two leads on a level recorder being replaced. The root cause of the event was the technical human performance verification tools were not adequately used during the Fix-It-Now (FIN) planning process to validate plant impact since there was a bias towards a level recorder replacement not impacting the control circuit. Corrective actions taken include replacing the failed level recorder and establishing a compensatory action to require FIN Team work packages staged by the FIN team to be peer reviewed by a same-discipline technician.<br /><br /> The event described in this LER is documented in the plant's corrective action program as IR2454892. NMP2 LER 2014-004 reported a similar event.
4102015003 | Nine Mile Point 2 | 06/23/2015 | 03/31/2016 | ML16102A27 | <strong>Primary Containment Isolation Function for some valves not maintained During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2015, Nine Mile Point Unit 2 identified two separate instances where the isolation capability for the Reactor Vessel Low Water Level (Level 2) primary containment isolation valves on both divisions was not maintained during performance of surveillance testing. The events occurred on April 22, 2015, and May 5, 2015. This event is reportable under 10 CFR 50.73 (a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The Surveillance testing on both dates was for valves powered by one division. To prevent an inadvertent full isolation signal from occurring, during the testing on the division, the power supply breakers for the division valves were opened while they were being tested. <br /><br /> The event described in this LER is documented in the station's corrective action program as IR2518177. There are no similar event reports.
4142015001 | Catawba 2 | 04/20/2015 | 06/19/2015 | ML15175A19 | <strong>Auxiliary Feedwater (AFW) System Train 2A and Its Automatic Transfer Function to the Nuclear Service Water System (NSWS) Were Determined to Have Been Inoperable in Violation of Technical Specifications (TS)</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2015, it was determined that TS 3.7.5, "Auxiliary Feedwater (AFW) System", Condition B had been violated. Due to the inability to meet a TS Surveillance Requirement, it was determined that AFW System Train 2A had been unknowingly technically inoperable beginning on November 10, 2014 and ending on February 28, 2015 when Unit 2 entered Mode 4 at the start of its End of Cycle 20 Refueling Outage. The cause of the inoperability was the inability of valves 2CA-60 and 2CA-56 (motor driven AFW Train 2A discharge flow control valves to steam generators A and B, respectively) to automatically open to their safe position. It was also determined that TS 3.3.2, "Engineered Safety Feature Actuation System (ESFAS) Instrumentation", had not been met, resulting in TS Limiting Condition for Operation (LCO) 3.0.3 being unknowingly entered and violated. This was due to AFW System Train 2A being unable to automatically transfer to its assured source of supply (the NSWS). The cause of this event was determined to be a failed sliding link. The failed sliding link was replaced during the refueling outage. During this event, the normal feedwater supply to the steam generators remained available and actuation of the AFW System or transfer of its suction to the NSWS was not required. Had actuation of the AFW System been required, valves 2CA-56 and 2CA-60 were open, except for brief periods as described in this LER. Therefore, with the exception of these brief periods, the AFW System would have performed its safety related function. In addition, AFW System Train 2B remained capable of transferring its suction to the NSWS, had it been required to do so. Therefore, this event had no adverse effect upon the health and safety of the public.
4162015001 | Grand Gulf 1 | 02/07/2015 | 04/07/2015 | ML15098A60 | <strong>Automatic Actuation of the Reactor Protection System (RPS) due to a Fault in the Protective Relaying Circuitry on the "B" Main Transformer</strong><br /><i>Abstract:&nbsp;</i>On Saturday, February 7, 2015, at 1856 hours Central Standard Time, with the plant at 100 percent thermal power, Grand Gulf Nuclear Station experienced an automatic actuation of the reactor protection system (RPS) and subsequent reactor SCRAM. The "B" main transformer differential trip caused a generator lockout. The generator lockout was followed by a turbine control valve fast closure (RPS SCRAM signal), turbine trip and reactor SCRAM. All control rods fully inserted and safety systems operated as designed. Eleven safety relief valves (SRVs) lifted to control pressure. Feedwater was manually secured to transfer to the startup level control mode. There were no emergency core cooling systems (ECCS) actuations required or initiated in response to this SCRAM. Turbine bypass valves opened to stabilize pressure causing reactor water level to fluctuate. Residual heat removal (RHR) group 2 and 3 containment isolation signals were received on low level 3. A hard ground was discovered on the non-safety protective circuitry between the current transformer and control cabinet on "B" main transformer. The faulted cables and other similar cables were determinated and alternate wiring and conduit was installed before placing the transformers back into service. The event posed no threat to public health and safety.
4162015002 | Grand Gulf 1 | 10/01/2015 | 11/30/2015 | ML15329A21 | <strong>Loss of Secondary Containment Differential Pressure During Drawdown Testing</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2015, at approximately 0324 hours with the plant in MODE 1 at 100 percent rated core thermal power, Grand Gulf Nuclear Station experienced a loss of Secondary Containment. Grand Gulf Nuclear Station failed to meet the requirements of Technical Specification Surveillance 3.6.4.1.3 in the tested configuration. Following completion of the failed surveillance test, Secondary Containment was returned to an operable status at 0440 hours on October 1, 2015, by returning the system to a previously known operable configuration. The cause of the October 1, 2015 failed drawdown test was Secondary Containment door seal inleakage during testing. After the leaking Secondary Containment door seals were repaired, a subsequent Standby Gas Treatment drawdown surveillance test was performed. The test was completed with satisfactory results on October 6, 2015, for the previously failed configuration. There was no actual impact to public health and safety due to this event.
4162015003 | Grand Gulf 1 | 10/14/2015 | 12/13/2015 | ML15344A26 | <strong>Technical Specification Surveillance on Primary Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>At 12:20 on October 14, 2015, with the plant in MODE 1 at 100 percent rated core thermal power, Grand Gulf Nuclear Station identified a condition prohibited by the plant's Technical Specifications. Grand Gulf Nuclear Station failed to meet the requirements of Technical Specification 5.5.6, Inservice Testing Program, and Surveillance Requirement 3.6.1.3.9. Specifically, three valves were not Local Leak Rate Tested at or greater than the required test pressure of 16.28 pounds per square inch guage, 110% of the Extended Power Uprate accident pressure. <br /><br /> The cause of the inadequate Surveillance Testing was lack of post Extended Power Uprate testing criteria incorporation into Grand Gulf Surveillance Testing Procedures. Following the inadequate Surveillance Testing in 2013, the valves were subsequently leak rate tested at or greater than the required test pressure of 16.28 psig on October 15, 2015 and October 17, 2015. The subsequent leakage rate testing for all three valves was within the acceptance criteria of Technical Specification Surveillance Requirement 3.6.1.3.9. There was no actual impact to public health and safety due to this event.
4232015001 | Millstone 3 | 02/19/2015 | 04/20/2015 | ML15118A53 | <strong>Unlatched Dual Train HELB Door Results in Potential Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2015, with Millstone Power Station Unit 3 (MPS3) at 100% power and in operating mode 1, an individual on a fire watch rove processed through a dual train high energy line break (HELB) door normally and upon checking the door after passage the individual noted the door did not latch. The Control Room was promptly notified. An operator was dispatched to investigate. The operator exercised the door lock-set mechanism freeing the latch allowing the door to properly latch. The door was inoperable for approximately 7 minutes. Technical Specification 3.0.3 was entered and exited appropriately.<br /><br /> Although no definite failure mechanism was identified, the door was experiencing high usage due to compensatory fire watch roves entering/exiting the door. The door lockset mechanism was manually manipulated and then tested several times satisfactorily by maintenance personnel. Further, the door design has the door swing such that the HELB event would act to open the door when the lockset mechanism fails. Engineering is evaluating the adequacy of the preventive maintenance frequency. Additionally, a design change to reverse the door swing such that the HELB event would cause the door to close and thus not rely on the lock-set mechanism is being considered. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(D), as a condition that could have prevented the fulfillment of a safety function for systems needed to mitigate the consequences of an accident.
4252015001 | Vogtle 2 | 03/14/2015 | 05/13/2015 | ML15133A29 | <strong>Unit 2 Reactor Trip and Safety Injection due to Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2015 at approximately 04:29 AM Eastern Daylight Time (EDT), Vogtle Unit 2 was operating in Mode 1 at 100 percent power when the Loop 3 outboard Main Steam Isolation Valve (MSIV) spuriously closed. The sudden closure of the steam isolation valve caused a rapid pressure reduction in the remaining three Steam Generators (SGs) due to increased steam flow resulting in a Reactor Protection System (RPS) actuation due to rate compensated Low Main Steam Line Pressure Safety Injection and Steam Line Isolation. All control rods fully inserted and all equipment actuated as designed.<br /><br /> The unit was stabilized in Mode 3 with decay heat being removed through the atmospheric relief valves (ARVs) to the environment. The Loop 3 MSIV closure was due to failure of the hydraulic dump solenoid valve which resulted in a loss of hydraulic pressure to the MSIV.<br /><br /> This event had no adverse effect on the health and safety of the public, and is of very low safety significance. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of a system listed in 10CFR 50.73(a)(2)(iv)(B). Unit 1 was unaffected.
4252015002 | Vogtle 2 | 03/14/2015 | 05/13/2015 | ML15133A30 | <strong>Vogtle Unit 2 Inadvertent Auxiliary Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2015 at 1207 Eastern Daylight Time (EDT), Unit 2 was operating in Mode 3 following an unplanned reactor trip and safety injection, a valid Auxiliary Feedwater (AFW) actuation signal was received on B-train Auxiliary Feedwater system during post-trip recovery and unit stabilization. Both Train A and Train B motor driven AFW pumps were in service at the time. Upon receipt of the AFW actuation signal the B-train discharge valves stroked to the full open position. Operators immediately restored AFW discharge valves to their previous positions without any adverse impacts on the unit.<br /><br /> The plant remained in Mode 3 and decay heat continued to be removed via the Atmospheric Relief Valves. Unit 1 was unaffected. This event had no adverse effect on the health and safety of the public, and is of very low safety significance. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of a system listed in 10CFR 50.73(a)(2)(iv)(B).
4402015001 | Perry | 06/16/2015 | 08/11/2015 | ML15226A48 | <strong>Degraded Voltage Relay Found outside the Allowable Value</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2015, at 0452 hours, during performance of surveillance testing, a degraded voltage time delay relay was found outside of the Technical Specification allowable value. <br /><br /> The cause of the Division 3 degraded voltage time delay relay being outside the allowable value was setpoint drift and the calibration setpoint not being centered within the allowable value range. The relay was satisfactorily recalibrated in accordance with procedures and successfully passed the as-left performance test during the remainder of the surveillance testing and was made operable on June 16, 2015, at 1117 hours. Planned corrective actions include centering the time delay relay setpoint within the allowable value and relay removal for analysis and evaluation. <br /><br /> The safety significance of this event is considered to be small. The degraded voltage time delay relay initiates load shedding, isolates the Division 3 bus and starts the Division 3 Emergency Diesel Generator (EDG). The Division 3 EDG is the on-site power source for the High Pressure Core Spray System which is a single train system. Therefore, this event is being reported in accordance with 10CFR50.73(a)(2)(v) as an event or condition that could have prevented the fulfillment of a safety function. <br /><br /> Additionally, as discussed in the Event Analysis section, this event is not considered a safety system functional failure because the as found setpoint was within the analytical design limit.
4452015001 | Comanche Peak 1, Comanche Peak 2 | 02/19/2015 | 04/20/2015 | ML15119A22 | <strong>Unanalyzed Condition During MSSV Testing</strong><br /><i>Abstract:&nbsp;</i>In late September 2014, just prior to the start of 1RF17, testing of Unit 1 Main Steam Safety Valves (MSSVs) was performed in accordance with maintenance procedure MSM-S0-8702. During the conduct of that maintenance, Maintenance personnel leave one of the two doors to the Main Steam-Main Feed room open for personnel egress in the event of a steam leak and for heat stress considerations. Testing of the MSSVs was completed satisfactorily and Unit 1 entered its scheduled refueling outage.<br /><br /> On February 19, 2015, it was determined the conduct of the MSSV testing had inadvertently placed Unit 1 in an unanalyzed condition. Furthermore, placing the Unit in an unanalyzed condition was reportable under 10CFR50.73(a)(2)(ii)(B).<br /><br /> The cause of this event was the MSSV testing work process did not consider the operability of safety related equipment when the Main Steam-Main Feed room doors were open. Corrective actions include revising procedures to provide site personnel with guidance sufficient to avoid situations such as the unanalyzed condition resulting from the MSSV testing.<br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
4462015001 | Comanche Peak 2 | 07/10/2015 | 09/18/2015 | ML15313A02 | <strong>Unit 2 Train B Safety Injection System Inoperable for Longer Than Allowed By TS</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2015 at 1304 Comanche Peak Nuclear Power Plant, Unit 2 exceeded a 72 hour limiting condition for operation (LCO), after being granted a period of enforcement discretion, due to a through-wall leak found on the "B" train of the Safety Injection (SI) system piping at the 3/4" socket weld coupling to valve 2SI-0055. The flaw resulted in declaring the "B" train of SI inoperable. This event was reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specifications. A Notification of Enforcement Discretion (NOED) was granted by the NRC at 0920 on July 10, 2015. The repair process issues leading to the NOED request were the requirement to apply a freeze seal to allow installation of a new vent valve to allow adequate static refill of the system and complete dye penetrant testing of the weld, ultrasonic examination of the suction piping to verify the system full of water, and pump testing to establish operability of the system. The most probable cause of the through-wall leak was determined to be an original weld defect which resulted in a stress concentration that allowed otherwise acceptable tensile loads to cause propagation of a through-wall crack. The corrective action was to grind out the weld and repair (re-weld). <br /><br /> This event had no adverse effect upon the health and safety of the public. <br /><br /> All times in this report are approximate and Central Daylight Time unless noted otherwise.
4462015002 | Comanche Peak 2 | 10/03/2015 | 12/01/2015 | ML15357A03 | <strong>Unit 2 Manual Reactor Trip due to Feedwater Flow Controller Malfunction</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2015, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at approximately 43% power shutting down for the 15th refueling outage. During the shutdown, a Steam Generator (SG) 2-03 level deviation alarm was received. Manual control of the SG 2-03 Feedwater flow control valve was taken, but Operators were unable to control feed flow. At 0958, a manual reactor trip was initiated in anticipation of an automatic turbine trip at the P-14 setpoint. The Motor Driven Auxiliary Feedwater (AFW) pumps were manually started per Operations procedures to control AFW flow, minimize cool down, and maintain SG levels. All systems responded normally during and following the reactor trip. <br /><br /> The cause of this event was determined to be a manufacturing defect in the SG 2-03 feedwater flow control valve positioner upper O-ring. Corrective actions include replacement of all four Unit 2 feedwater flow control valve positioners and establishment of periodic monitoring of feedwater flow control valve demand as an early detection of a positioner failure. <br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
4542015001 | Byron 1, Byron 2 | 01/11/2015 | 03/11/2015 | ML15070A01 | <strong>Byron Unit 1, Inadequate Application of Technical Specifications Related to Main Steam Isolation Valves and Actuator Trains</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2015, at 2055 hours, Byron Station Unit 2 entered Technical Specification (TS) 3.7.2, "Main Steam Isolation Valves (MSIVs)," Condition A, with an associated 8 hour Completion Time for the Unit 2, Train 'A' MSIV due to one of the associated redundant actuator trains being inoperable. This action was consistent with an October 19, 2006 NRC staff interpretation that Surveillance Requirement 3.7.2.2 requires both actuator trains for a single valve to be tested and an MSIV shall be declared inoperable when one of its associated actuator trains is inoperable. A subsequent Byron Station extent of condition review identified two previous occurrences in the prior three years when an actuator train for an MSIV was inoperable and the inoperable train was not restored within the required 8 hour Completion Time. In these instances, TS requirements of 3.7.2 were inadequately applied and should have been imposed. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which is prohibited by the plant's Technical Specifications.<br /><br /> The cause of the event was a departure from Byron Station's previous practice to one that was based on the October 19, 2006 NRC position in regard to entering TS 3.7.2, Condition A, under similar conditions. Corrective actions included communicating to operating crews, revising procedures and implementation of new TS for MSIVs.
4542015002 | Byron 1 | 03/03/2015 | 05/01/2015 | ML15121A03 | <strong>Byron Unit 1 Reactor Trip Resulting from a Phase to Phase Fault on the 1E Main Power Transformer</strong><br /><i>Abstract:&nbsp;</i>At 1101 hours on March 3, 2015, Byron Station Unit 1 tripped from full power due to a phase to phase fault on the 1E Main Power Transformer (MPT) between electrical Phase A and Phase B. Before this trip, the Byron area had experienced severe weather. At the time of the event, the temperature was approximately 30 degrees F; however, temperatures had been around 23 degrees F hours earlier. An ice formation on the Phase B Bus bar that is located directly above the high voltage bushings dropped and caused a phase to phase fault between Phase A and B.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).<br /><br /> The cause of this event was due to latent design vulnerability that existed in the configuration of the Bus bar relative to the MPT bushings. The Bus bar location directly above and parallel to the MPT bushings created a condition that resulted in a phase to phase short when ice from the Bus bar fell across the bushings. The Bus bar is six inches in diameter and located approximately twenty-three feet above the top of the bushings. The 1E MPT high voltage and neutral bushings were replaced during the forced outage. Following successful testing of the 1E MPT, Byron Unit 1 was restarted.
4542015003 | Byron 1 | 10/08/2014 | 08/27/2015 | ML15239A11 | <strong>One Train of the Diesel Generator System Inoperable Longer than Allowed by Technical Specifications due to Loss of Diesel Fuel Oil System Volume</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2014 at 1248 hours, the Byron Station Main Control Room (MCR) received an alarm identifying that fuel oil level was low on one of two Diesel Oil Storage Tanks (DOSTs) associated with the Unit 1, B-train (1B) Emergency Diesel Generator (DG). At 1328 hours, the MCR received an alarm identifying level was also low in the second DOST associated with the 1B DG. Operators determined that the low level condition was due to leakage to the Unit 1, A-train (1A) fuel oil storage system through one of two 1A DOST inlet valves. The Corrective Action Program investigation identified that leakage initially occurred during the 1B DG monthly surveillance conducted on October 22, 2014.<br /><br /> Subsequent analysis concluded that the loss of inventory from the 1B DOSTs to the 1A DOSTs would result in the 1B DG not meeting its design mission time without operator intervention. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for an operation or condition prohibited by Technical Specifications. <br /><br /> The cause of the event was a degraded DOST inlet valve that allowed fuel to transfer from the 1B DOSTs to the 1A DOSTs.
4542015004 | Byron 1, Byron 2 | 08/20/2015 | 10/19/2015 | ML15292A01 | <strong>Unanalyzed Condition due to a Design Deficiency with Pressurizer Power Operated Relief Valve Circuitry That Could Prevent Valve Manual Closure to Mitigate Spurious Operation</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2015 at 1755 hours, a design deficiency associated with pressurizer power operated relief valve (PORV) block valve control circuitry was confirmed in which a design basis fire in the main control room (MCR) or cable spreading rooms (CSR) could prevent the credited fire safe shutdown action (i.e., locally close pressurizer PORV block valve) mitigating a spurious pressurizer PORV opening. <br /><br /> On September 2, 2015, during an extent of condition review, an additional design deficiency was confirmed in which credited fire safe shutdown action (i.e., removing 125 Vdc control power fuses) mitigating a spurious opening of the pressurizer PORVs during design basis fire does not adequately mitigate design basis fire induced hot short. <br /><br /> The causes of these design deficiencies are legacy design errors made during original construction. <br /><br /> Corrective actions include plant configuration changes correcting the specific design deficiencies.<br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.
4542015005 | Byron 1 | 09/18/2015 | 11/17/2015 | ML15321A03 | <strong>Liquid Penetrant Indications in Embedded Flaw Seal Weld Repair of Control Rod Drive Mechanism Penetration 31 During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2015 at 2000 hours, during the Byron Station fall 2015 Unit 1 refueling outage (B1R20), in-service liquid penetration (PT) examinations were performed on the previously repaired control rod drive mechanisms (CRDMs) at penetrations 31 and 43. During the examination of the repair for CRDM penetration 31, one 9/32 inch rounded indication and one 0.010 inch linear indication were documented, exceeding the acceptance criteria of dimensions greater than 3/16 inch for rounded indications and linear indications of any size. The linear indication was repaired with buffing only, while the rounded indication was repaired using both buffing and welding. There were no rejectable indications found on penetration 43. This LER is being submitted in follow-up to ENS 51410 made on September 18, 2015.<br /><br /> The cause of these flaws is attributed to existing weld discontinuities and minor subsurface voids opening to the surface or enlarging due to thermal and/or pressure stresses during plant operation. <br /><br /> This event is being reported under 10CFR50.73(a)(2)(ii)(A) for any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded.
4542015006 | Byron 1 | 10/01/2015 | 11/30/2015 | ML15334A01 | <strong>Mode 3 Entered with Turbine Trip Safety Function Disabled due to Safety Related Relay Leads Lifted</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2015 at 0906, while in Mode 3, Byron Station determined that Unit 1 was in a condition that could have prevented fulfillment of the turbine trip safety function. Electrical leads had been lifted to disable the turbine trip function on both Solid State Protection System (SSPS) trains while Unit 1 was in Mode 5 to support Instrument Maintenance calibrations on turbine generator throttle valves and governor valves. These leads were not reinstalled prior to Mode 3 entry, which occurred at 0059 on October 1, 2015. From the time Mode 3 was entered, Byron Unit 1 was not in compliance with Byron technical specification (TS) 3.3.2, "ESFAS Instrumentation," Condition G. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(v)(D) for any event or condition that could have prevented the fulfillment of a safety function to mitigate the consequences of an accident, and under 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant's technical specifications. This LER is being submitted in follow-up to ENS 51436 made on October 1, 2015. <br /><br /> The cause of the event was the Exceptions Checklist, 1BGP 100-1T3, " Mode 4 to 3 Checklist," utilized for mode changes, lacks the appropriate rigor to ensure exceptions are resolved and challenged prior to removal from the list.
4562015001 | Braidwood 1, Braidwood 2 | 01/13/2015 | 03/12/2015 | ML15071A23 | <strong>Main Steam Isolation Valve Technical Specifications Applicability - MSIV Operability Position Change</strong><br /><i>Abstract:&nbsp;</i>On January 13, 2015, Braidwood Station was reviewing operating experience (OE) related to Main Steam Isolation Valve (MSIV) operability and changed its previous position regarding MSIV operability. Previous MSIV operability practice considered a MSIV operable as long as one of two redundant actuator trains was operable. Revised MSIV operability practice requires both redundant MSIV actuation trains operable. Declaring a MSIV inoperable and entering MSIV TS LCO when single MSIV actuation train is inoperable is consistent with an October 19, 2006 NRC staff interpretation for different plant under a Task Interface Agreement (TIA). An extent of condition review identified two occurrences in the previous three years when a single MSIV actuator train was inoperable and not restored within the required TS 3.7.2 eight hour completion time. In these instances, TS 3.7.2 requirements were inadequately applied under the new interpretation and should have been imposed. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications".<br /><br /> The cause of the event was the legacy MSIV TS and TS Bases did not explicitly address MSIV actuator trains. Corrective actions included communicating to operating crews, procedure revisions and implementing new MSIV TS providing actions for inoperable MSIV actuator trains.
4562015002 | Braidwood 1 | 04/03/2015 | 06/02/2015 | ML15153A39 | <strong>Indication in Control Rod Drive Mechanism Nozzle Weld due to Embedded Flaws Opening Up from Thermal and Pressure Stresses During Operation</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2015, during the Braidwood Station Unit 1 refueling outage (A1R18), an in service liquid penetration (PT) examination was performed on the previously repaired control rod drive mechanism (CRDM) penetration 69. During the examination of the repair for CRDM penetration 69, one 3/8 inch rounded indication was documented exceeding the acceptance criterion (ASME Section III 1971 Edition through the Summer 1973 Addenda) of dimensions greater than 3/16 inch. This LER is being submitted in follow-up to ENS 50953 made on April 3, 2015.<br /><br /> Based on industry experience, the cause of this event was determined to be mechanical discontinuities/minor subsurface voids opening up to the weld surface due to thermal and/or pressure stresses during plant operation.<br /><br /> The indication in penetration 69 was reduced to acceptable size as approved by the NRC in Braidwood Relief Request I3R-09.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), "any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded" since the as found indication did not meet the applicable acceptance criterion referenced in ASME Code Case N-729-1 to remain in-service without repair.
4562015003 | Braidwood 1, Braidwood 2 | 08/20/2015 | 10/19/2015 | ML15292A02 | <strong>Unanalyzed Condition due to a Design Deficiency with Pressurizer Power Operated Relief Valve Circuitry that Could Prevent Valve Manual Closure to Mitigate Spurious Operation</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2015, a design deficiency associated with the pressurizer power operated relief valve (PORV) block valve control circuitry was confirmed, in which a design basis fire in the main control room or cable spreading rooms could prevent the credited fire safe shutdown action (i.e., locally close pressurizer PORV block valve) mitigating a spurious pressurizer PORV opening. <br /><br /> On September 2, 2015, during an extent of condition review, an additional design deficiency was confirmed in which credited fire safe shutdown action (i.e., removing control power fuses) mitigating a spurious opening of the pressurizer PORVs during a design basis fire, does not adequately mitigate a design basis fire induced hot short.<br /><br /> The causes of these design deficiencies are legacy design errors made during original construction. <br /><br /> Corrective actions include plant configuration changes correcting the specific design deficiencies. <br /><br /> This condition is being reported in accordance with 10CFR50.73(a)(2)(ii)(B), any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.
4572015001 | Braidwood 2 | 01/26/2015 | 03/27/2015 | ML15096A49 | <strong>Steam Generator Atmospheric Relief Manual Isolation Valve Fails to Close During Quarterly Surveillance due to Long Term Corrosion</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2015 while performing a quarterly surveillance stroke test of the 2C Steam Generator (SG) Power Operated Relief Valve (PORV), 2MS018C, the associated SG PORV manual isolation valve, 2MS019C, failed to close. The last successful quarterly stroke of 2MS019C was performed on October 27, 2014.<br /><br /> A failure analysis performed concluded that moisture had been present in the valve's gear box for an extended period of time, causing corrosion and pitting in the 2MS019C actuator. The degradation removed enough material to cause the remaining intact cross-sections to fail during the attempt to close the valve on January 26, 2015.<br /><br /> There is the potential that a condition prohibited by technical specifications (TS) existed before discovery, for a time longer than permitted by TS, based on the surveillance frequency. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." Corrective actions included repairing the valve, performing a failure analysis of the actuator gears from 2MS019C, and performing an extent of condition review on similar valves.
4572015002 | Braidwood 2 | 10/05/2015 | 12/04/2015 | ML15338A14 | <strong>Automatic Actuation of Auxiliary Feedwater and Automatic Reactor Trip Signal due to Startup Feedwater Pump Failing to Start on Demand and Motor Driven Feedwater Pump Elevated Bearing Temperature Exceeding Limits</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2015 at 2317 hours, during the planned Unit 2 down power for entry into a refueling outage, the start-up feedwater (FW) pump failed to start. As a result, the motor driven FW pump (MDFWP) was used to supply FW to the steam generators for decay heat removal and cooldown. <br /><br /> On October 5, 2015 at 0038 hours, with the unit in Mode 3, MDFWP high journal bearing temperatures exceeded limits, and the pump was manually secured. Before the operating crew manually started the auxiliary feedwater (AF) system, the 2C steam generator low level reactor trip/AF actuation (Lo-2) setpoint was reached, resulting in an auto actuation of both trains of the AF system and an automatic reactor trip signal. <br /><br /> The cause of the failure of the startup FW pump to start was due to a pump starting interlock not making up. The corrective action planned is to create a post-maintenance test to perform an interlock check following maintenance of the startup FW pump. <br /><br /> The MDFWP elevated bearing temperatures were determined to be normal during low flow conditions experienced during the plant cooldown. Corrective actions completed included revising an operating procedure increasing allowable pump bearing temperatures.
4572015003 | Braidwood 2 | 06/24/2015 | 08/24/2015 | ML15236A33 | <strong>Degraded Valve Causes Loss of Diesel Fuel Oil System Volume for One Train of the Diesel Generator System Resulting in Inoperability Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2015, during the 2B emergency diesel generator (DG) monthly surveillance run, the redundant 2A diesel oil storage tank (DOST) fuel oil level increased. This DOST level change was caused by leak by of the 2A DOST fill valve (2DO001A). Engineering evaluated the 2B DG fuel oil volume with consideration for the 2DO001A leak by and determined that the 2B EDG did not have sufficient fuel oil to satisfy its 7 day mission time specified in Technical Specification (TS) 3.8.3 "Diesel Fuel Oil". <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), for "any operation or condition which was prohibited by the plant's Technical Specifications" since the 2B DG was not declared inoperable and some associated Limiting Condition For Operation Action Requirements (LOCAR) were not completed. <br /><br /> The cause of the event was a degraded DOST fill valve that allowed fuel oil to transfer from the 2B DOST to the 2A DOST during 2B DG operation. <br /><br /> Corrective actions include repairing of 2DO001A and implementing a DOST fill valve leakage monitoring program with associated acceptance criteria, or implementing a plant configuration change to install an additional valve in the flow path.
4582015001 | River Bend | 02/18/2015 | 04/16/2015 | ML15118A56 | <strong>Operations Prohibited by Technical Specifications due to Deficient Local Leak Rate Test Procedures Containing Erroneous Valve Alignments</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2015, while the plant was operating at approximately 98% power, it was discovered that four local leak rate surveillance test procedures each contained a similar error that resulted in an improper test configuration. This deficiency in each procedure erroneously required the closure of the respective motor-operated valve in the packing leak-off line for the outboard main steam isolation valve (MSIV) being tested, when the proper test configuration would require the valve to be open. The net effect of the error was to partially negate the effectiveness of a surveillance test required by Technical Specifications. This condition had existed since the procedures were revised in 1992 to add valve lineup checklists. The incorrect valve position for the subject test procedures was caused by lack of attention to detail when the procedures were developed. An assessment of the effects of the procedure error was conducted, and reasonable assurance was established that the safety function of the outboard MSIVs was not compromised by this condition. The procedures were corrected, and the tests were successfully conducted in the recent refueling outage. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications.
4582015002 | River Bend | 03/07/2015 | 05/05/2015 | ML15149A14 | <strong>Emergency Diesel Generator Start Circuit Actuation due to Loss of Power from Reserve Station Service No. 2</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2015, at 9:40 p.m., while the plant was in cold shutdown, power from the reserve station service line no. 2 to the Division 2 onsite electrical distribution system was lost. The Division 2 diesel generator (EDG) received an automatic start signal due the undervoltage condition on the 4160v bus, but did not start since it was out of service for scheduled maintenance. The Division 2 standby service water pumps were operating at the time for scheduled testing, and subsequently shut down when power was lost. The investigation team concluded that electricians must have made contact with the sudden-pressure trip circuitry wires while working in the cabinet on the reserve station service transformer "D". The apparent cause of this event was inadequate work practices on the part of the electricians, in that they did not take all available precautions prior to performing the voltage check. The workers recognized the adverse conditions, but did not recognize the need to put into place any robust barriers. The electricians' successful past performance of this type of task likely led to overconfidence. Reviewers of the work package didn't challenge the potential risks or identify a most error-likely task. The EDG start logic responded as designed to the loss of power on the Division 2 electrical systems. This event did not involve any interruption of the shutdown cooling function. This event was, thus, of minimal safety significance with respect to the health and safety of the public. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the EDG starting logic.
4582015003 | River Bend | 05/14/2015 | 07/09/2015 | ML15219A19 | <strong>Operations Prohibited by Technical Specifications and Loss of Safety Function due to Inoperability of Division 2 Containment Penetration Leakage Control System</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2015, with the plant operating at 100 percent power, a manual valve in the Division 2 penetration valve leakage control (LSV) subsystem was found out of position. Subsequent investigation concluded that this condition had existed since before the plant was started up from a refueling outage on March 26, 2015, causing that subsystem to be inoperable for a period greater than the 30-day allowable outage time in Technical Specifications. The valve (SWP-V912) is in the service water supply to the air compressor on that skid. The mispositioning of the valve was caused by an error in equipment configuration control. Additionally, the investigation determined that, during the intervening period, there were two short planned outages of the Division 1 subsystem. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications, as well as 10 CFR 50.73(a)(2)(v)(C) as a loss of the LSV safety function during those periods when the Division 1 subsystem was out of service. The two periods during which the Division 1 LSV subsystem was inoperable totaled approximately 7.5 hours. Otherwise, it was capable at all other times to perform the design safety function. At no time during the period from plant startup on March 26 until the Division 2 subsystem was restored to an operable status was there an actual demand for the system to operate. This event was thus of minimal significance to the health and safety of the public.
4582015004 | River Bend | 05/21/2015 | 07/15/2015 | ML15212A11 | <strong>Potential Loss of Safety Function of Onsite AC / DC Distribution Systems due to Postulated Main Control Building Heat-up Following Loss of Ventilation Cooling System</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2015, with the plant operating at 100 percent power, the operations shift manager was notified of the discovery of an error in the plant design basis regarding the safety-related heating, ventilation, and air conditioning (HVAC) system in the main control building. Specifically, a calculation for the heat-up of certain building areas following the postulated failure of the HVAC system had not been updated when new AC / DC inverters were installed in 2009. This resulted in the possibility for exceeding the equipment qualification temperatures in the areas containing safety-related components in the DC distribution system, potentially resulting in the failure of that equipment under certain conditions. The investigation determined that an erroneous entry in the reference documents listed in the building heat-up calculation prevented the recognition of the calculation as an affected document when the 2009 design change was being developed. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event involving the potential inability to perform the safety function of the onsite AC and DC distribution systems. An analysis performed for this investigation developed a preliminary adjustment of ES-246 for updated heat loads. New system modeling indicates that, under the postulated loss of main control building HVAC concurrent with a loss of coolant accident, a failure of the safety-related AC and DC distribution systems due to heat buildup in the inverter rooms or AC switchgear rooms would be unlikely. This condition is, thus, of minimal safety significance to the health and safety of the public.
4582015005 | River Bend | 06/01/2015 | 07/29/2015 | ML15231A18 | <strong>Automatic Reactor Scram due to Low Reactor Water Level Following a Loss of Instrument Power</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2015, at 9:09 p.m. CDT, with the plant operating at 90 percent power, an unplanned automatic reactor scram occurred due to low reactor water level. This event resulted from the loss of a non-safety related instrument power panel, apparently caused by an internal electrical transient in a 125-volt AC / DC inverter. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as the automatic actuation of the reactor protection system. All reactor control rods inserted normally, and control of reactor parameters was promptly established using the main turbine bypass valves and the main feedwater system. An expected general containment isolation signal occurred when reactor water level decreased to Level 3. The "A" reactor recirculation pump shifted to slow speed as designed, while the "B" pump tripped off. The runback feature of the reactor recirculation flow control valves failed to operate due the loss of instrument power. No plant parameters requiring the actuation of the emergency diesel generators, the main steam safety-relief valves, or the emergency core cooling systems were exceeded. This event was, thus, of minimal safety significance to the health and safety of the public.
4582015006 | River Bend | 07/17/2015 | 09/14/2015 | ML15272A17 | <strong>Operations Prohibited by Technical Specifications due to Error in Initial Operability Evaluation</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2015, with the plant operating at 92 percent power, it was determined that an operability evaluation previously performed for a safety-related instrument in the primary containment isolation circuitry was in error, which resulted in the failure to take actions required by the Technical Specifications. On July 8, 2015, a scheduled surveillance test was performed on one channel of the primary containment isolation logic. During the test, an error message was displayed on the associated trip unit. The operators and technicians researched the vendor manual, consulted the cognizant engineers, and determined that the error message was not indicative of any inability of the system to perform its design safety function. Subsequent review found that the first operability determination on the condition report was in error, and that the trip channel was not actually capable of performing as designed. The trip unit was declared inoperable, and taken out of service to be replaced. The channel was again declared operable on July 18 at 2:44 a.m. The elapsed time between the receipt of the error message on July 8 and the restoration to an operable status exceeded the allowable outage time of Technical Specifications. The cause of the error in the first operability determination was the use of an outdated vendor manual for the initial troubleshooting. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications. During the time that the trip unit was inoperable, redundant channels in the isolation logic remained capable of performing the safety function. This event was, thus, of minimal safety significance to the health and safety of the public.
4582015007 | River Bend | 11/17/2015 | 01/18/2016 | ML16050A38 | <strong>Potential Loss of Safety Function of High Pressure Core Spray due to Failure of Main Control Building Ventilation Chiller</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2015, at 11:55 p.m. CST, with the plant operating at 71 percent power, the high pressure core spray system (HPCS) was declared inoperable following the failure of the operating chiller in the Division 1 control building ventilation (HVK) system. HVK chiller "C" was in service when the building operator found a freon leak in the system. The leakage was determined to be of such magnitude as to cause the chiller to be inoperable, and the operators took action to shift the building cooling loads to the standby Division 2 chiller. Maintenance technicians disassembled the service water flow control valve on the chiller, and found that the cause of the freon leak was failed rubber diaphragm in the valve actuator. No positive identification of the failure mode of the diaphragm could be made, so it was shipped to the valve vendor for further analysis. This condition potentially caused the HPCS system to be incapable of performing its safety function, and is, thus, reportable in accordance with 10 CFR 50.73(a)(2)(v)(D). The maximum time needed to perform the chiller realignment has been conservatively estimated to be 76 minutes. Calculations have determined temperatures in the Division 3 equipment rooms will remain below the 122F limit of the equipment for at least 24 hours. This event had no actual adverse effect on the ability of the Division 3 HPCS electrical system to perform its design safety function since there was more than sufficient time to align the other chiller in the same division to provide control building switchgear room cooling.
4582015008 | River Bend | 11/19/2015 | 01/18/2016 | ML16050A39 | <strong>Potential Loss of Safety Function of High Pressure Core Spray due to Failure of Main Control Building Ventilation Chiller</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2015, at 7:24 a.m. CST, with the plant operating at 97 percent power, the high pressure core spray system (HPCS) was declared inoperable following the failure of the operating chiller in the Division 2 control building ventilation system (HVK). Chiller "D" was in service when the building operator found an oil leak on that machine. The chiller subsequently tripped on low oil pressure. The "A" chiller in the Division 1 subsystem automatically started as designed. The loss of cooling to the various equipment rooms in the control building requires that the supported equipment in those areas be declared inoperable. The Technical Specifications for the Division 3 DC distribution system requires that the HPCS system be immediately declared inoperable. This condition potentially causes the HPCS system to be incapable of performing its safety function. Maintenance technicians identified the source of the oil leak as a failed seal on the compressor drive shaft. The apparent cause of the seal failure was the age-related degradation of a setscrew holding one of the rotating elements of the seal, allowing it to get out of position and disrupt the integrity of the seal face. In this event, the "A" chiller automatically started as designed, and it was confirmed to be operating correctly within 10 minutes. The HVK system continued to support the safety function of Division 3 electrical equipment after chiller trip, since the time required to restore an operable chiller is significantly less than the time limit for restoration of equipment room cooling. This event had no actual adverse effect on the ability of the Division 3 HPCS electrical system to perform its design safety function since there was more than sufficient time to align the other chiller in the same division to provide control building switchgear room cooling. This event, thus, did not constitute an actual loss of the ability of the HPCS system to perform its design safety function.
4582015009 | River Bend | 11/27/2015 | 05/18/2016 | ML16155A05 | <strong>Automatic Reactor Scram due to Partial Loss of Offsite Power Caused by Fault in Local 230kV Switchyard</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2015, at 4:31 a.m. CST, with the plant operating at 100 percent power, an automatic reactor scram occurred following the loss of power to both divisions of the reactor protection system (RPS). This condition resulted from a single-phase fault in the local 230kV switchyard. The initial response of the protective relays for the switchyard caused the breakers connected to the north 230kV bus in the switchyard to trip. The fault caused a voltage transient on the in-plant switchgear sufficient to trip the scram relays in the Division 2 RPS, resulting in a half-scram. The action of the protective relays continued, eventually causing the de-energization of reserve station service line no. 1. This lead to the loss of Division 1 RPS and a full reactor scram. The Division 1 and 3 emergency diesel generators started as designed to restore power to their respective safety-related onsite electrical distribution subsystems. No safety-related systems were out of service at the time of the scram, and reactor pressure and water level were promptly stabilized. All reactor control rods inserted properly. Multiple actuations of the main steam safety-relief valves (SRVs) occurred during the event. The nuclear steam supply system vendor reported this action was likely due to a localized pressure transient in the SRV instrumentation lines. SRV tailpipe temperature recorders indicated that all valves re-seated correctly following the initial transient. The cause of the event was an animal-induced fault in the 230kV switchyard that resulted in the automatic trip of the north bus feeder breaker to the RSS No. 1. The fault also caused the south bus feeder breaker to trip, de-energizing RSS No. 1.
4582015010 | River Bend | 12/11/2015 | 02/08/2016 | ML16053A09 | <strong>Potential Loss of Safety Function of High Pressure Core Spray due to Failure of Main Control Building Ventilation Chiller</strong><br /><i>Abstract:&nbsp;</i>On December 11, 2015, at 4:16 a.m. CST, with the plant operating at 83 percent power, the high pressure core spray system (HPCS) was declared inoperable following the failure of the operating chiller in the Division 2 control building ventilation system (HVK). Chiller "D" was in service when it tripped automatically due to a high bearing temperature signal. The "C" chiller in the Division 1 subsystem automatically started as designed, and was confirmed to be operating correctly within approximately 5 minutes. The Technical Specifications for the Division 3 DC distribution system requires that the HPCS system be immediately declared inoperable. This condition potentially causes the HPCS system to be incapable of performing its safety function. The investigation determined that, during a recent corrective maintenance activity, too much oil was added to the chiller prior to its return to service. A subsequent load increase on the chiller caused excess oil to migrate into the compressor sump, where it contributed to the high bearing temperature condition. The HVK system continued to support the safety function of Division 3 electrical equipment after chiller trip, since the time required to restore an operable chiller is significantly less than the time limit for restoration of equipment room cooling. This event had no actual adverse effect on the ability of the Division 3 HPCS electrical system to perform its design safety function since there was more than sufficient time to align the other chiller in the same division to provide control building switchgear room cooling. This event, thus, did not constitute an actual loss of the ability of the HPCS system to perform its design safety function.
4612015001 | Clinton 1 | 02/06/2015 | 04/07/2015 | ML15098A47 | <strong>Division 1 and Division 2 Reactor Water Cleanup System High Differential Flow Instruments Become Incapable of Performing Their Safety Function</strong><br /><i>Abstract:&nbsp;</i>On 2/6/15 at 2300 CST, the Division 1 Reactor Water Cleanup (RT) system differential flow indicator (1E31R614A) was observed to be reading greater than 10 gallons per minute (gpm) different from its sister channel, resulting in it failing its channel check. Operators declared this instrument inoperable in accordance with Clinton Power Station Technical Specification (TS) 3.3.6.1, Primary Containment and Drywell Isolation Instrumentation, requiring placing the channel in trip within 24 hours per Required Action D.1. At 2355, the Division 2 RT differential flow indicator (1E31R614B) indicated out of specification, requiring entry into Required Action E.1 for two channels inoperable. With both channels inoperable, the leakage detection system was incapable of performing its containment isolation function for RT differential flow. At 0036 on 2/7/15, a fill and vent of the Division 1 RT leak detection instrumentation was completed, restoring Division 1 to an operable status. At 0225 on 2/7/15, a fill and vent of the Division 2 RT leak detection instrumentation was completed, restoring Division 2 to an operable status. An eight-hour ENS notification (#50794) was made at 0637 CST in accordance with 10CFR50.72(b)(3)(v)(C). This event is also reportable under 10CFR50.73(a)(2)(v)(C).
4612015003 | Clinton 1 | 04/30/2015 | 06/29/2015 | ML15187A17 | <strong>Condition Prohibited by Technical Specification 3.9.4 for Failing to Disarm Control Rod Drive prior to Fuel Moves in Mode 5 with One Control Rod Position Indication Channel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2015, during Mode 5 (Refueling), Position Indication Probes (PIP) were installed for two control rods to simulate a "full-in" position in support of generic PIP replacements. Operations staff evaluated Technical Specifications (TS) prior to work package approval and tracked Limiting Condition for Operation (LCO) 3.9.4, [Control Rod Position Indication], Required Actions. At 1052, the Core Alterations Checklist was completed satisfactorily. Core Alterations commenced at 1103. The on-coming shift identified a potential discrepancy during log reviews and an operator was dispatched to verify requirements of LCO 3.9.4 Required Action A.2.2 were met for the two affected control rods. At 1837, the operator notified the Main Control Room that one of the two control rods was not hydraulically isolated. At 1842, actions were completed to hydraulically disarm the affected control rod. Required Action A.2.2, "Initiate action to disarm the control rod drive associated with the fully inserted Control Rod Drive" was not met during a seven hour and thirty-nine minute period. The cause of this event was that the Core Alterations Checklist did not reference LCO 3.9.4. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
4612015004 | Clinton 1 | 06/25/2015 | 08/22/2016 | ML16238A47 | <strong>Trip of Emergency Reserve Auxiliary Transformer Static VAR Compensator Causes Positive Secondary Containment Pressure following Lightning Strike on 138 kV Offsite Source</strong><br /><i>Abstract:&nbsp;</i>On 6/25/15 at 0301 CDT, the Main Control Room received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) caused by a voltage transient on the 138 kV offsite source due to thunderstorms in the area. The Division 1 Safety Bus was manually aligned from the reserve source to its normal source. As a result of the voltage transient, the Division 1 Fuel Building Ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no running VF fans, secondary containment differential pressure rose to slightly greater than 0 inches water gauge which exceeded the Technical Specification (TS) requirement of greater than 0.25 inches vacuum water gauge. Secondary Containment differential pressure was restored within TS requirements at 0320 CDT by reopening the VF isolation dampers and restarting the VF supply and exhaust fans. The ERAT SVC was returned to service at 0457 CDT. ENS notification 51179 was made at 0927 ET in accordance with 10 CFR 50.72(b)(3)(v)(C). This event is being reported as a condition that could have prevented fulfillment of a safety function under 10 CFR 50.73(a)(2)(v)(C).
4612015005 | Clinton 1 | 05/03/2015 | 03/16/2016 | ML16081A13 | <strong>Containment Ventilation Radiation Monitors Inoperable During Operations with the Potential for Draining the Reactor Vessel Activities</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2015, Clinton Power Station Unit 1 was in Mode 5, with planned maintenance work commencing which removed the containment building ventilation (VR) system and the drywell purge (VQ) system from service. These systems remained out of service until 0940 on May 12, 2015. Between 1858 on May 3, 2015 and 0709 on May 6, 2015, various Operations with the Potential for Draining the Reactor Vessel (OPDRVs) activities were conducted. With the VR and VQ ventilation systems shut down and the system isolated, the radiation monitors located in the ventilation system ducts were not available to perform their isolation function as required by Technical Specification (TS) 3.3.6.1, Primary Containment and Drywell Isolation Instrumentation, and TS 3.3.6.2, Secondary Containment Isolation Instrumentation. The TS Required Actions were not entered causing a condition prohibited by the TS. This condition was identified as a non-cited violation in NRC Inspection Report 2015-003, dated November 6, 2015. The cause of the violation is due to a change in interpretation of an operable duct monitor.<br /><br /> A daily order was issued and procedure OP-CL-108-104-1001, "ITS LCO/ORM OR/ODCM OR Evaluations and Guidance for Safety Function Determination," has been revised to clarify the operability requirements of the monitors when the affected ventilation systems are secured.
4822015001 | Wolf Creek | 01/28/2015 | 03/25/2015 | ML15099A39 | <strong>Personnel Error Causes Two Inoperable Residual Heat Removal Trains</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2015, the nightshift operations crew implemented a clearance order to support planned maintenance on two Residual Heat Removal (RHR) System valves that included closing valves EJHV8716A and EJHV8809A. At 0534 hours on January 28, 2015, Condition C of Limiting Condition for Operation (LCO) 3.5.2 was entered upon determining that less than 100% of the Emergency Core Cooling System (ECCS) flow equivalent to a single OPERABLE ECCS train was available with valve EJHV8716A closed. Entry into LCO 3.0.3 in accordance with Required Action C.1 was made on two separate occasions. Action was taken to restore valves EJHV8716A and EJHV8809A to the open position and exit LCO 3.0.3.<br /><br /> The licensed operators involved with the preparation and implementation of the clearance orders did not recognize that current plant conditions could not support the proposed activity. The individuals involved with this event had their qualifications removed until remediation occurred. Red switch boxes have been placed on the control boards in the control room on the valves in procedure AP 26C-004, "Operability Determination and Functionality Assessment," Section A.16 that can cause an entry into LCO 3.0.3.
4822015002 | Wolf Creek | 04/16/2015 | 08/26/2015 | ML15246A12 | <strong>Two Control Room Air Conditioning Trains Inoperable due to Failure to Meet Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>From January 3, 2013, through August 13, 2013, the Conditions and Required Actions of limiting condition for operation (LCO) LCO 3.7.11, LCO 3.0.3 and LCO 3.0.4 were not met.<br /><br /> On April 16, 2015, an apparent cause evaluation on Condition Report (CR) 92274, "Application of TS SR 3.0.1," identified the potential that the acceptance criteria in procedures STS PE-010A/B, "Control Room NC System Flow Rate Verification [A/B] Train," may not have been met when the acceptance criteria was revised on January 3, 2013 from > 18,360 cfm and < 22,440 cfm to a new value of > 21,012 cfm. Review of information determined that the prior performances of STS PE-010A/B did not meet the new acceptance criteria. Additionally, procedure STS PE-010B was not performed until July 8, 2013 and procedure STS PE-010A was not performed until August 13, 2013. <br /><br /> The apparent cause of this event is the information in Operability Evaluation OE GK-12-017, which addressed a separate issue on the same equipment, enabled control room operators and engineering personnel to rationalize the assumption that the change to the acceptance criteria was bounded and did not impact the ability to meet SR 3.7.11.1.
4822015003 | Wolf Creek | 05/03/2015 | 07/01/2015 | ML15194A03 | <strong>Manual Reactor Trip due to High Steam Generator Level Transient at Low Power</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2015 at 1021 Central Daylight Time (CDT), Wolf Creek Generating Station (WCGS) was at approximately 25% power during startup from Refueling Outage 20. The 'C' steam generator received a Hi-Hi level signal while the Reactor Operator was manually transferring feedwater control from the Main Feedwater Regulating Valve (MFRV) bypass valves to the MFRVs. This resulted in a main turbine trip, feedwater isolation, and auxiliary feedwater actuation. A manual reactor trip was initiated at 1022 CDT. The root cause was the lack of a reliable and consistent standardization between the operating crews to control the transfer of the steam generator feedwater flow between the MFRV bypass valves and MFRVs and a sense of urgency by the control room operators. <br /><br /> The event is bounded by analyses as reported in the Wolf Creek Generating Station (WCGS) Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow."
4822015004 | Wolf Creek | 05/05/2015 | 09/14/2015 | ML15265A03 | <strong>Incorrect Decision Results in Two Containment Isolation Valves being in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2015, it was discovered that the motive force (air supply) was not removed for two containment shutdown purge valves as required by Technical Specification 3.6.3, "Containment Isolation Valves." The motive force was restored to allow the performance of procedure STS KJ-001A, "Integrated Diesel Generator and Safeguards Actuation Test - Train A," on April 26, 2015. After performance of procedure STS KJ-001A, the motive force was not removed for the two containment shutdown purge valves. The plant entered Mode 4 on April 28, 2015 at 0144 Central Daylight Time (CDT). <br /><br /> Upon discovery, the air supply valves for the two containment shutdown purge valves were locked closed, removing the motive force. The cause of the event was the decision to only track components listed in the manual Locked Component Log during plant start-up, allowed a mode change with components out of position. The safety significance of the event was low as each penetration flow path had a redundant valve that was closed with the motive force removed.
4832015001 | Callaway | 07/23/2015 | 12/02/2016 | ML16340A73 | <strong>Completion of a Shutdown Required by the Technical Specifications - TS 3.4.13</strong><br /><i>Abstract:&nbsp;</i>On July 23, 2015, plant operators became aware of indications of an increase in the Reactor Coolant System (RCS) unidentified leak rate. The indications included containment radiation alarms as well as increasing containment humidity and sump levels. An RCS inventory balance indicated an unidentified leak rate of 1.2 gpm leak which is greater than the Technical Specification limit of 1 gpm for unidentified leakage. Actions were taken to determine the source of the leak. A containment entry was made, and a steam cloud was identified to be coming from the Pressurizer Spray Valve cubicle. The plant was shut down in order to comply with requirements of the Technical Specifications. <br /><br /> It was determined that the leak was due to seat leakage through the RCS Pressurizer CVCS Auxiliary Spray Supply Drain valve BBV0400 and then through the non-safety related pipe flange immediately downstream of the valve. The valve was tightened which reduced the leakage to 60 drops per minute. The flange gasket was replaced. The root cause of the leak was determined to be that valve BBV0400 was not fully closed at normal closing force in RF20. The valve was replaced in April 2016 during Refueling Outage RF21. Additionally, a plant procedure was revised to require that selected valves (including BBV0400) are closed in MODE 3 using normal force or additional force if leakage is identified.
4832015002 | Callaway | 07/23/2015 | 09/07/2016 | ML16251A27 | <strong>Manual Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>During plant cooldown in response to conditions reported to the NRC on July 23, 2015 in Event Notification 51253, Callaway was in Mode 3 (Hot Standby) and on the way to Mode 5 (Cold Shutdown). In accordance with cooldown procedures, Callaway was operating with one Main Feedwater Pump (MFP) when the pump speed unexpectedly lowered to 0 RPM. The pump was manually tripped in response to the condition. This led to a decrease in water level in the steam generators. Operators manually activated the Auxiliary Feedwater System to maintain water level in the steam generators. This system actuation is reportable per 10CFR50.73(a)(2)(iv)(A). <br /><br /> Fault tree analysis and subsequent testing identified the most probable cause for the loss of the 'B' MFP is a software defect introduced during the software development process for the digital feedwater control system installed in 2013. Plant operating procedures have been revised to allow for a rapid start of the startup MFP during a plant shut down. Additionally, procedures were revised to allow for the startup MFP to be placed in a ready state when only one MFP is required based on power level. These procedure revisions will provide defense in-depth against unnecessary Auxiliary Feedwater System actuations in the future.
4832015003 | Callaway | 08/11/2015 | 01/21/2016 | ML16021A44 | <strong>Reactor Trip Caused by Transmission Line Fault</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2015, at 01:39 Callaway plant tripped from 100% power due to an incorrect, automatic response to a transmission line fault on the Montgomery-Callaway 8 line by transformer bus differential relaying. This resulted in Reactor Protection System (RPS) and Auxiliary Feedwater System actuations. The plant response to the trip was as expected except for a problem encountered with Auxiliary Feedwater flow control valve ALHV0007 subsequent to the plant trip. <br /><br /> This event was caused by the inadvertent inclusion of jumpers in the current transformer (CT) circuits of the main transformers that were installed as part of Main Transformer Replacement Modification 09-0044 implemented in Refuel 19. Following the event, the inadvertently placed CT jumpers were removed and the plant was successfully restarted.<br /><br /> The root cause of the incorrect main transformer CT wiring was that a drawing originally depicting the wiring configuration was not revised properly when it was converted from a generic Standardized Nuclear Unit Power Plant System (SNUPPS) drawing (E-03MA02) to a Callaway-specific drawing (E-23MA02) in the 1983 timeframe. This eventually resulted in design and testing errors during modification development. <br /><br /> Corrective actions include additional design, testing and job reviews, as well as reviews of similar drawings to identify and correct missing information.
4832015004 | Callaway | 08/11/2015 | 10/12/2015 | ML15285A01 | <strong>Auxiliary Feedwater Control Valve Inoperable due to Faulty Electronic Positioner Card</strong><br /><i>Abstract:&nbsp;</i>Between 11/18/2014 and 12/3/2014, the 'B' MDAFW train was inoperable due to an improperly functioning positioner card installed on the control valve in the AFW flow path to the 'D' steam generator, i.e., valve ALHV0005. The 'A' MDAFW train and the TDAFW train were inoperable for short durations at different times between 11/18/2014 and 12/3/2014, although neither of those redundant trains was inoperable at the same time. During the short windows of TDAFW unavailability, only a single MDAFW train was operable, resulting in a loss of safety function. <br /><br /> On 08/11/2015, an unexpected turbine trip / reactor trip occurred due to a latent design error in the current transformer (CT) wiring for the main transformers. The reactor trip was reported to the NRC in Event Notification 51308. While responding to the reactor trip, the 'B' train motor-driven auxiliary feedwater (MDAFW) flow control valve in the auxiliary feedwater (AFW) flow path to the `A' steam generator, i.e., valve ALHV0007, could not be manipulated from the main control room. It was determined that ALHV0007 would have performed its specified safety function; however, during the extent of condition review, it was determined that ALHV0005 was inoperable from 11/18/2014 until 12/3/2014. The 72-hour Completion Time of Condition C of Technical Specification 3.7.5 was exceeded from 11/18/2014 until a new positioner card was installed on ALHV0005 on 12/3/2014. <br /><br /> The direct cause of the ALHV0005 failure was a failure of a bridge rectifier on the valve's electronic positioner circuit card. This type of positioner card was also installed on ALHV0007. The root cause of the card failures was determined to be a vendor design deficiency. The defective positioner cards have been replaced and measures have been taken to remove defective spares from future plant use.
4982015001 | South Texas 1 | 12/21/2015 | 02/18/2016 | ML16067A08 | <strong>Manual Reactor Trip due to Lowering Steam Generator Levels and Valid Auxiliary Feedwater System Actuation Following a Manual Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2015, at 1519 hours, Operators manually tripped the Unit 1 Main Turbine due to excessive load swings caused by Main Turbine Governor Valve 2 (GV2) oscillations. Prior to and following the trip of the Main Turbine, the Steam Dumps did not respond as expected, resulting in a Main Feedwater Isolation at 1524 hours due to rising Steam Generator (SG) level. Operators initiated a manual reactor trip at 1533 hours due to lowering SG levels. Approximately six seconds after the reactor trip, the Auxiliary Feedwater (AFW) system automatically actuated on a SG low level signal. <br /><br /> The cause of the GV2 oscillations was an intermittent ground on the signal wire to the Linear Variable Differential Transmitter (LVDT) for GV2. The fluctuations in steam flow due to the GV2 oscillations caused the spring clips in the valve positioners that modulate the Group 1 Steam Dumps to become dislodged, causing the Group 1 Steam Dumps to be unresponsive. As corrective actions, the LVDT and associated cabling for GV2 was replaced and the Group 1 Steam Dump valve positioners were repaired. The manual actuation of the Reactor Protection System and subsequent automatic AFW actuation are both reportable under 10 CFR 50.73(a)(2)(iv)(A). The event was of very low risk significance and no radioactive release occurred; therefore, there was no adverse effect on the health and safety of the public.
4992015001 | South Texas 2 | 03/04/2015 | 05/05/2015 | ML15133A32 | <strong>Technical Specification Action Statement Time Exceeded due to Turbine-Driven Auxiliary Feedwater Pump Test Failure Not Recognized</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2015 at 1631 hours, a review performed by the Operations Surveillance Coordinator discovered that a surveillance performed on March 4, 2015 on the Unit 2 turbine-driven auxiliary feedwater (AFW) pump 24 did not meet the surveillance acceptance criteria for as-found discharge pressure. An operability review was subsequently performed and on March 12, 2015 it was determined that AFW pump 24 was inoperable as of March 4, 2015 at 1507 hours. As a result, the Technical Specification allowed outage time of 72 hours was exceeded and the Configuration Risk Management Program was not applied; this is reportable per 10CFR50.73(a)(2)(i)(B). During the period of AFW pump 24 inoperability, a second auxiliary feedwater pump was also inoperable on March 9, 2015 resulting in a condition that could have prevented the fulfillment of the safety function of systems that are needed to remove residual heat which is reportable per 10CFR50.73(a)(2)(v)(B). AFW pump 24 was not recognized as inoperable due to human error. As a corrective action, the operators were coached and counseled and remediated by Operations Management.<br /><br /> An actual demand for AFW did not occur during the period of inoperability; therefore, there was no adverse effect on the health and safety of the public.
5292015001 | Palo Verde 2 | 01/11/2015 | 03/25/2015 | ML15091A39 | <strong>Condition Prohibited by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.5, Engineered Safety Features Actuation System (ESFAS)</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2015, at 0024, Unit 2 received a plant computer monitoring system (RJ) alarm on point SASB22, indicating the setpoint for the bistable relay that compares pressures between Steam Generators (SGs) was approaching the technical specification (TS) allowable limit for SG Pressure Difference-High. SASB22 does not alarm to control room annunciators (RK) and went unnoticed until late in the shift. Operators then verified the annunciator for SG differential pressure (DP) was not alarming and SG pressures were normal. The significance of the RJ alarm was not apparent because the value was displayed in units of voltage versus DP.<br /><br /> On January 24, 2015, further questioning determined the setpoint for the bistable that monitors differential pressure between SGs had exceeded its allowable value. Channel B SG Pressure Difference-High was declared inoperable and SG Level 2-Low was placed in bypass per LCO 3.3.5, Condition A.<br /><br /> The direct cause of the event was setpoint drift of the SASB22 bistable relay caused by potentiometers that had not recently been wiped clean. The root cause was the lack of an annunciated alarm for SASB22 and associated alarm response procedure to ensure the alarm condition was promptly acknowledged, understood, and correctly addressed within TS time limitations.<br /><br /> No previous similar events have been reported to the NRC by PVNGS in the prior three years.
5302015001 | Palo Verde 3 | 04/07/2015 | 06/05/2015 | ML17026A25 | <strong>Leakage from Reactor Coolant Pump 2A Suction Pipe Instrument Nozzle</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2015, at 0032, with Unit 3 in Mode 5, during a scheduled boric acid walk-down inspection of the Unit 3 reactor coolant system (RCS), engineering personnel at the Palo Verde Nuclear Generating Station (PVNGS) identified white residue on a one inch instrument nozzle on the reactor coolant pump 2A suction pipe. Isotopic analysis confirmed the white residue resulted from leakage of RCS coolant and, at 0330 on April 8, 2015, engineering personnel determined that RCS pressure boundary leakage had occurred resulting in a condition prohibited by Technical Specification 3.4.14, RCS Operational Leakage.<br /><br /> The cause of the event was determined to be primary water stress corrosion cracking of the Alloy 600 instrument nozzle. To correct the condition, the nozzle was repaired with an American Society of Mechanical Engineers (ASME) approved and NRC endorsed half-nozzle repair method.<br /><br /> PVNGS reported a similar problem in licensee event report number 50-530/2013-001-00 on December 6, 2013, when RCS pressure boundary leakage was identified on a Unit 3 reactor vessel bottom mounted instrument nozzle.
5302015002 | Palo Verde 3 | 05/01/2015 | 06/26/2015 | ML15188A34 | <strong>Condition Prohibited by Technical Specification 3.0.4 due to an Inoperable Atmospheric Dump Valve (ADV)</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2015, following completion of refueling activities, PVNGS Unit 3 entered Mode 4 and continued to Mode 3 in preparation for plant startup. On May 2, 2015, when plant conditions needed to test atmospheric dump valves (ADV) with steam were achieved, testing of ADVs was initiated. At 1739 on May 2, 2015, testing determined that ADV SGB-HV-178 (ADV-178) would not stroke more than approximately 13 percent open. Operations personnel declared ADV-178 inoperable and entered Technical Specification Limiting Condition of Operation (LCO) 3.7.4, Atmospheric Dump Valves, Condition A. An investigation determined ADV-178 was inoperable when Unit 3 entered Mode 4. <br /><br /> Inspection of ADV-178 determined internal sealing rings were improperly installed during maintenance performed in the refueling outage. The valve was repaired and tested and declared operable at 0853 on May 7, 2015. The causes of the event were human error by maintenance personnel and inadequacies with the procedure used to perform the valve maintenance. Corrective actions will revise work instructions to provide detailed guidance for valve reassembly and to require verifications of proper re-assembly. <br /><br /> A similar event was reported in LER 50-529/2012-003-00 which resulted when testing in Mode 3 following refueling activities identified an inoperable steam supply valve for the steam driven auxiliary feedwater pump.
5302015003 | Palo Verde 3 | 05/30/2015 | 07/29/2015 | ML15212A90 | <strong>Damaged High Pressure Safety Injection Pump Motor Journal Bearing</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2015, emergent maintenance on the Unit 3 train A high pressure safety injection (HPSI) pump motor outboard journal bearing performed under Nuclear Regulatory Commission (NRC) approved notice of enforcement discretion 15-4-01 exceeded the Technical Specification Limiting Condition for Operation (LCO) completion time for LCO 3.5.3, Emergency Core Cooling Systems - Operating, Condition C.1. The HPSI pump had been removed from service on May 27, 2015, at 0628, for planned routine maintenance. During maintenance, it was discovered that the motor outboard journal bearing was damaged. The bearing was replaced and the pump was declared operable on May 30, 2015, at 1710. <br /><br /> The root cause was work instruction weaknesses which resulted in improper reassembly of the HPSI pump motor during planned maintenance in the Unit 3 spring 2015 refueling outage. Immediate corrective actions replaced the damaged outboard motor bearing and properly reassembled the pump and motor. To prevent recurrence, maintenance procedures will be revised to provide enhanced guidance for pump and motor reassembly. An additional action will determine training enhancements needed to address weaknesses with maintenance personnel knowledge. <br /><br /> No previous-similar events have been reported to the NRC by PVNGS in the prior three years.
5302015004 | Palo Verde 3 | 05/01/2015 | 02/05/2016 | ML16039A29 | <strong>Condition Prohibited by Technical Specifications 3.0.4 and 3.7.2 due to an Inoperable Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2015, at approximately 2106, the Unit 3 main steam isolation valve SGE-UV-181 (MSIV-181) B actuator train was declared inoperable and Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.2, Condition A, was entered due to a failed fitting on the air supply line. To correct the condition the failed fitting was replaced and an additional pipe support was installed on the air-line. Following retests, the MSIV-181 B actuator train was restored to operable status and LCO 3.7.2, Condition A, was exited on August 15, 2015, at approximately 1830. A similar air-line fitting failure had occurred on the Unit 3 MSIV-181 B actuator train on May 19, 2015. The investigation of this condition following the second failure determined the MSIV-181 B actuator train air-line configuration was modified in the spring 2015 Unit 3 refueling outage and was inoperable from the time Unit 3 entered Mode 4 on May 1, 2015, at 0258, following the outage because the air-line tubing was not adequately supported following the design change. <br /><br /> The cause of the failure was lack of adequate guidance to perform a walk down during the PVNGS design equivalent change (DEC) process. The lack of a local inspection of actual plant conditions resulted in the latent condition (i.e., vibratory displacement of the affected air-line combined with inadequate tubing support) remaining unnoticed prior to the component failure. Immediate corrective actions to replace the failed fittings and add additional support were completed on August 15, 2015. An additional corrective action will revise procedural guidance and associated documents. <br /><br /> No similar conditions have been reported by PVNGS in the last three years.