## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192016001 | Oyster Creek | 01/04/2016 | 01/24/2017 | ML17038A00 | <strong>Failure of the #1 Emergency Diesel Generator During Surveillance Testing due to a Cooling Water System Leak</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2016, during the biweekly load test surveillance, the Emergency Diesel Generator (EDG) #1 tripped after 26 minutes of operation and an unexpected Main Control Room alarm was received. <br /><br /> Locally, at the EDG enclosure, it was discovered that the rubber pipe coupling that connects the coolant surge tank to the right bank cooling water pump inlet tee had ruptured and that the EDG #1 control circuitry processed the trip on low coolant pressure.<br /><br /> EDG #1 was declared inoperable and in accordance with Technical Specification (TS) 3.7.C.2 Limiting Condition for Operation (LCO), the unit entered a seven day action period. The EDG #1 was returned to service on January 5, 2016, at 0130 hours, following successful hose replacement and completion of the load test surveillance. <br /><br /> The Root Cause investigation determined that an activity to replace the rubber pipe coupling on a 12-year frequency was not established during the initial implementation of Exelon's Electro-Motive Division Diesel Generator Performance Centered Maintenance (PCM) template. <br /><br /> This event resulted in an Operation or Condition that was Prohibited by the Plant's Technical Specifications and is therefore being reported under 10CFR50.73(a)(2)(i)(B).
2192016002 | Oyster Creek | 03/16/2016 | 06/23/2017 | ML17187A13 | <strong>Control Rod Drive Cooling Water System Isolation Scram Time Testing Was Not Performed</strong><br /><i>Abstract:&nbsp;</i>On 03/16/2016, it was identified that isolating or reducing cooling water to the Hydraulic Control Units (HCUs) for three control rods should have been considered a modification since it had the potential to impact the scram times of the control rods. Even though scram time penalties were applied for the three control rods where the cooling water flow was either isolated or reduced, the control rods should have been scram time tested, as directed by the Generic Electric (GE) Service Information Letter (SIL) 173, Supplement 1, Revision 1. <br /><br /> By not completing scram time testing for the control rods whose cooling water was isolated or reduced, the station was in violation of the requirements of Technical Specifications Section 3.2, since the issue was not identified previously and the affected control rods were not declared inoperable and isolated. <br /><br /> This event resulted in an Operation or Condition that was Prohibited by the Plant's Technical Specifications (TS) and is therefore being reported under 10CFR50.73(a)(2)(i)(B).
2192016003 | Oyster Creek | 04/30/2016 | 06/29/2016 | ML16187A32 | <strong>Manual SCRAM Inserted due to Leakage from the 'D' Reactor Recirculation Pump Seal</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2016, at 1804 hours, during the plant startup following the 1M38 maintenance outage, a reactor SCRAM was manually inserted by the Control Room Operators during post maintenance testing following work on the 'D' Reactor Recirculation Pump (RRP) mechanical seal. The SCRAM was initiated since leakage was discovered by a rising trend in drywell unidentified leakage during plant startup. The seal had been replaced during the maintenance outage. The SCRAM was selected as the preferred method of shutting down the reactor due to low decay heat conditions following the outage. <br /><br /> ENS 51895 was submitted on April 30, 2016, as required by 10 CFR 50.72 (b)(2)(iv)(B). This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), for any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).
2192016004 | Oyster Creek | 09/29/2016 | 11/15/2016 | ML16327A06 | <strong>Technical Specification Violation due to Main Steam Safety Valve Setpoint Discovered out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>Oyster Creek Nuclear Generating Station was in Cold Shutdown on 09/29/16 for Refueling Outage 1R26 when a condition was discovered during routine laboratory as-found testing that a Safety Valve (SV) (EIIC:RV) removed on 09/27/16 as part of refueling outage maintenance activities did not meet required setpoint tolerances. There were no structures, systems or components out of service that contributed to this event. <br /><br /> In accordance with American Society of Mechanical Engineers (ASME) Operation and Maintenance (O&M) Code requirements, two (2) of the nine (9) SVs installed in the plant were scheduled for removal during the refueling outage (1R26) and sent for as-found laboratory testing. Based on information received from the laboratory performing SV as-found testing, Site Engineering personnel determined that SV setpoint deficiencies existed with one (1) of the two (2) SVs removed and sent for testing. Per ASME O&M Code Mandatory Appendix I Section I-1320, two additional SVs were removed from the plant and sent for as-found testing and both met the required setpoint acceptance criteria. One (1) of the four (4) SVs tested exceeded the setpoint tolerance of +/-3% (+/-36 psig) as specified in the Technical Specifications (TS), Paragraph 2.3.F. This resulted in a condition prohibited by TS and is considered reportable pursuant to 10 CFR 50.73(a)(2)(i)(B).
2192016005 | Oyster Creek | 09/19/2016 | 09/22/2017 | ML18037A09 | <strong>Technical Specification Prohibited Condition Caused by One Electromatic Relief Valve Inoperable for Greater than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2016, after achieving Cold Shutdown for the 1R26 Refuel Outage, as found testing was performed on all five (5) Electromatic Relief Valves (EMRVs). The "E" EMRV did not open from the Main Control Room (MCR), and no change in indication was observed. Per the work activity, technicians were dispatched to the Drywell to verify that the valve did not move upon receiving an open signal from the MCR. <br /><br /> A cutout switch in the valve actuator was stuck in the open position, thereby preventing a solenoid from actuating to open the valve. The cutout switch did not operate as required because the hinge pin lock star washers were not installed in the cutout switch assembly. Without the lock star washers installed, the hinge pins interfered with the solenoid frame holes creating mechanical binding. Based on this information it is suspected that the "E" EMRV would have been inoperable for longer than the Technical Specification Allowed Out of Service Time (AOT) of 24 hours. Therefore, this issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition which was Prohibited by the plant's Technical Specifications.
2202016001 | Nine Mile Point 1 | 06/01/2016 | 07/12/2016 | ML16202A14 | <strong>Secondary Containment Inoperable due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On Wednesday June 1, 2016, at approximately 1046, the secondary containment of the Nine Mile Point Unit 1 (NMP1) Reactor Building was momentarily breached when workers opened both airlock doors on elevation 261 simultaneously. The integrity of the airlock was re-established within 5 seconds when one of the doors was closed and latched. The cause of this event is personal accountability. With clear understanding of the expectations for using the airlock doors in conjunction with all mechanical barriers (lights, buzzers, monitors) functioning properly, the individual failed to use human performance tools to verify the airlock was not already being used by other individuals. This condition is reportable under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.73(a)(2)(v)(C).
2202016002 | Nine Mile Point 1 | 07/28/2016 | 09/26/2016 | ML16277A14 | <strong>Isolation of Both Emergency Condensers due to Loss of UPS 162B</strong><br /><i>Abstract:&nbsp;</i>On Thursday July 28, 2016, at approximately 2357 hours with power level at approximately 100 percent, Nine Mile Point Unit 1 (NMP1) experienced a loss of Uninterruptible Power Supply (UPS), UPS 162B which resulted in loss of Reactor Protection System (RPS) Bus 11. Numerous half scram and half isolation signals were generated in addition to the isolation of both # 11 and # 12 Emergency Condensers (ECs). EC # 12 was returned to standby on 7/29/2016 at 0041 hours and EC # 11 was returned to standby on 7/29/2016 at 0045 hours. The causes of this event were the failure of a UPS capacitor and the bypass power transfer set point being set too low for the type of transient. Corrective actions include immediate replacement of the failed capacitor, installation of new higher temperature rated capacitors and adjusting the low voltage bypass power transfer set point. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(v)(B).
2372016001 | Dresden 2, Dresden 1 | 02/09/2016 | 04/08/2016 | ML16104A03 | <strong>Secondary Containment Differential Pressure Transient</strong><br /><i>Abstract:&nbsp;</i>On 2/9/16 at 19:00 CST, the operating heating boiler shutdown. At 19:15, the Main Control Room (MCR) received alarms for low reactor building (RB) differential pressure (DP). As directed by procedure, Operators verified local gauge readings and equipment configuration. At 21:42, local gauge readings were averaged at -0.24 inches wc which required entry into Tech Spec 3.6.4.1.A due to RB DP being greater than Technical Specification required -0.25 inches wc by local average on the refuel floor. At 22:05, U3 RB ventilation was secured, and at 22:07 TS 3.6.4.1.A was exited when RB DP returned below -0.25 inches wc. <br /><br /> The cause of the event was determined to be a degraded area DP controller that restricted exhaust flow, preventing the system from maintaining RB DP greater than TS allowed value. <br /><br /> Corrective actions include calibration of the area DP controller, enhancements to operational response procedures, a review of the associated maintenance strategy, and review for potential component upgrades.
2372016002 | Dresden 2 | 05/16/2016 | 09/30/2016 | ML16278A00 | <strong>Unit 2 HPCI Inlet Steam Drain Pot Piping Leak Resulting in HPCI Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 5/16/2016 at approximately 1120 CDT during planned maintenance on Division II of the Low Pressure Coolant Injection (LPCI) system, a through-wall steam leak was observed in the Unit 2 High Pressure Coolant Injection (HPCI) inlet drain pot drain piping. The leak was identified to be on the Inlet Drain Pot line leading to the Main Condenser upstream of the HPCI Inlet Drain Pot 2A Inboard Drain Valve, Air Operated Valve (AOV) 2-2301-29, which is ASME Code Class 2 piping. The cause of the through-wall leak was liquid droplet impingement erosion thinning of chrome moly piping. HPCI was declared inoperable following isolation of the degraded piping per Technical Requirements Manual (TRM) 3.4.a. This event is of low safety significance. Corrective Actions included replacing the piping with stainless steel, ensuring similar sections of piping are replaced or scheduled for replacement, and reviewing Extent of Condition. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident."
2372016004 | Dresden 2 | 11/08/2016 | 01/09/2017 | ML17010A28 | <strong>Reactor Building Differential Pressure Less than Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On 11/8/16 at 0510 CST, during Under Voltage surveillance testing Bus 33-1 was secured causing Standby Gas Treatment (SBGT) [BH] to start, and the Reactor Building (RB) Ventilation system [VA] automatically isolated. During the evolution RB pressure relative to outside was less than 0.25 inches water column (in WC) vacuum which is required by Technical Specifications (TSs). TS Limiting Condition for Operation (LCO) 3.6.4.1, "Secondary Containment", Condition A was entered. At 0532 CST, the Unit 2 RB Equipment Access Inner door was closed and RB differential pressure was observed to increase above 0.25 in WC vacuum, and Condition A was exited. <br /><br /> TS LCO 3.6.4.1 was not applicable to Unit 3 which was in Mode 5 with no recently irradiated fuel moves or any operations with a potential for draining the reactor vessel (OPDRVs) in progress.<br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(v)(C), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material."
2442016001 | Ginna | 02/11/2016 | 04/07/2016 | ML16104A02 | <strong>Loss of Station Auxiliary Transformer 12A resulting in automatic start of Emergency Diesel Generator A due to undervoltage signals to safeguards buses 14 and 18.</strong><br /><i>Abstract:&nbsp;</i>On 02/11/2016 at 2305, Ginna Station experienced a loss of Station Auxiliary Transformer 12A, causing Emergency Diesel Generator A to automatically start due to undervoltage signals to safeguards buses 14 and 18. Station Auxiliary Transformer 12A failed due to a high side phase to phase internal fault with relays for overcurrent and differential current actuated. All plant systems responded as designed. Control room operators stabilized the plant per abnormal operating procedures. The plant was placed in 100/0 electrical lineup on the off-site circuit 767 with Emergency Diesel Generator A secured. Station Auxiliary Transformer 12A was replaced with a spare and the plant was restored to normal off-site power line-up on 02/20/2016 at 0018. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv)(A) as a valid system actuation that was not part of a pre-planned sequence during testing.
2472016001 | Indian Point 2 | 03/04/2016 | 05/02/2016 | ML16131A63 | <strong>Technical Specification Prohibited Condition Caused by One Main Steam Safety Valve Outside Its As-Found Lift Set Point Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2016, during the performance of surveillance procedure 2-PT-R006, Main Steam Safety Valve (MSSV) MS-45B failed to lift within the Technical Specification (TS) as-found required range of +/- 3% of the setpoint pressure. Valve MS-45B lifted at 1125 psig, 29 psig outside its acceptance range of 1034 to 1096 psig and 5.7% above its 1065 psig setpoint. The valve was declared inoperable, then subsequently restored to operability upon two successful lifts within the required setpoint range without the need for adjustment. Nine other MSSVs that were tested lifted within the as-found required setpoint range. The apparent cause for the failure was internal friction due to spindle rod wear, which causes the spindle rod to bind against internal components. Corrective actions were modification of MS-45B and twelve other MSSVs, and the replacement of their spindle rods. The event had no effect on public health and safety.
2472016002 | Indian Point 2 | 03/07/2016 | 02/28/2017 | ML17062B00 | <strong>Automatic Actuation of Emergency Diesel Generators (EDGs) due to 480 VAC Bus Undervoltage Condition and Loss of Residual Heat Removal (RHR) While in Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2016, while performing set-up activities for 2-PT-R084C, "23 EDG 8 Hour Load Test," the normal supply breaker to 480 Volt AC Bus {ED} 3A tripped on overcurrent. This caused 480 Volt AC Buses 3A and 6A to de-energize since, as part of the test set-up activities, the tie breaker (3AT6A) between Buses 3A and 6A was closed and the normal supply breaker for Bus 6A was opened. This resulted in a loss of both 21 and 22 Residual Heat Removal (RHR) {BP} pumps. As designed, all Emergency Diesel Generators (EDGs) {EK} received automatic initiation signals to start. All required 480 Volt AC buses automatically re-energized by design, with the exception of Bus 3A, which had an overcurrent lockout. Operators manually started 22 RHR pump to restore RHR cooling. However, prior to restoring the normal supply power to Bus 3A, 23 EDG tripped on overcurrent which resulted in a second loss of RIM event. The cause for the Bus 3A supply breaker tripping was inadequate procedural guidance resulting in excessive loads being energized on Buses 3A and 6A. The direct cause for 23 EDG tripping was cracked solder joints on the automatic voltage regulator (AVR). Corrective actions included revising 2-PT-R084C and replacing the voltage regulator. The event had no effect on public health and safety.
2472016003 | Indian Point 2 | 03/07/2016 | 05/06/2016 | ML16133A03 | <strong>Technical Specification (TS) Prohibited Condition Due to an Inoperable 21 Main Boiler Feedwater Pump Discharge Valve for Greater Than the TS Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2016, during a refueling outage the control switch for the 21 Main Boiler Feedwater Pump (MBFP) was positioned to trip and the 21 MBFP tripped as designed but the MBFP discharge valve BFD-2-21 failed to fully close. MBFP discharge valve BFD-2-21 was declared inoperable and Technical Specification (TS) 3.7.3 (Main Feedwater Isolation) Condition C (One or both MBFP discharge valves inoperable) was entered. Troubleshooting on the valve determined the close torque switch contact finger was out of position within the contact holder. This misalignment allowed the contact finger to move out of the proper position causing Motor Operated Valve (MOV) BFD-2-21 to fail to close. Direct cause was valve BFD-2-21 close torque- switch was out of position. The apparent cause was the MOV preventive maintenance procedure lacked the level of detail and direction to provide the appropriate guidance to recognize the susceptibility associated with the orientation of the close torque switch contact finger bracket opening and spreading of the "U" shape bracket. Corrective actions included replacement of the defective torque switch, inspection and testing. A case study from this event will be developed and included in the continual ESP training. The adequacy of the guidance on work instruction on the arrangement/alignment of the contact "U" shape brackets will be evaluated and the necessary guidance provided. The event had no significant effect on public health and safety.
2472016004 | Indian Point 2 | 03/29/2016 | 05/31/2016 | ML16159A21 | <strong>Unanalyzed Condition due to Degraded Reactor Baffle-Former Bolts</strong><br /><i>Abstract:&nbsp;</i>During a scheduled refueling outage that commenced on March 7, 2016, an inspection of the reactor vessel internals that is required by MRP-227-A was performed. As a result of the inspection, 227 baffle-former bolts were identified to have either visual anomalies or ultrasonic indications or could not be examined by ultrasonic testing. A visual inspection of the baffle-former plates and edge bolts showed no discernible material degradation or distortion. All other MRP-227-A inspections of the reactor vessel internals showed no other failures or premature degradation.<br /><br /> The root cause of the failed baffle-former bolts is primarily Irradiation Assisted Stress Corrosion Cracking (IASCC) in combination with applied stresses and fatigue loads. Failure analyses will be conducted to confirm the cause for the degradation of the baffle-former bolts.<br /><br /> At the time of discovery, the unit was in a safe and stable condition with all fuel removed from the reactor vessel. The event had no impact on public health and safety.
2472016005 | Indian Point 2 | 03/26/2016 | 05/25/2016 | ML16159A29 | <strong>Technical Specification (TS) Prohibited Condition due to a Surveillance Requirement Never Performed for Testing the Trip of the Main Boiler Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2016, during a refueling outage, an NRC inspector identified that the trip of the MBFPs is not tested in accordance with Technical Specification 3.7.3 (Main Feedwater System) Surveillance Requirement (SR) 3.7.3.3. This was discovered as a result of an assessment of the failure of the Main Boiler Feedwater Pumps (MBFPs) steam stop valves to close after the reactor trip on December 5, 2015. <br /><br /> TS SR 3.7.3.3 requires testing the MBFP trip function every 24 months on an actual or simulated actuation signal. Surveillance tests 2-PT-V024DS60.and 2-PT-V24DS61 are performed every 24 months, but only test up to the limit switch contact that actuates the MBFP turbine trip solenoid valves and does not include the trip of the pump. A review determined the requirement to verify the trip of the MBFPs was added to the TS during the implementation of the improved TS (ITS) conversion program in 2004 but the corresponding testing was not added to the surveillance tests. The direct cause was human error for failure to ensure testing was established to meet new ITS SRs. The apparent cause of the error is indeterminate due to the time passed since TS conversion by Amendment 238 on November 21, 2003. Corrective actions include revision of Surveillance tests 2-PT-V024DS60 and 2-PT-V24DS61 to test tripping of the MBFPs. The MBFPs will be tested per the revised procedures prior to startup from the outage. The event had no significant effect on public health and safety.
2472016006 | Indian Point 2 | 03/28/2016 | 05/27/2016 | ML16159A19 | <strong>Technical Specification Prohibited Condition due to Inoperable 138 kV Offsite Circuits Caused by a Disconnected Safety Injection Signal to the Station Auxiliary Transformer Load Tap Changer</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2016, during shutdown for a refueling outage, while performing testing of the safety injection (SI) system, the Station Auxiliary Transformer (SAT) Load Tap Changer (LTC) failed to increase per design upon actuation of an SI signal. The condition was acceptable for the current mode but is unacceptable when the offsite AC electric power distribution and SI System is required to be operable. An investigation was performed and it was discovered on March 28, 2016, that the SAT control cabinet terminal blocks W105 and W106 had their links open thereby preventing proper operation of the LTC. A review of tests and Work Orders (WO) did not identify any previous failed tests or any WO with instructions to open the links. The last successful test of LTC operation was performed on February 26, 2014. The direct cause of the event was open links for the SAT LTC SI signal. The most probable apparent cause was maintenance activities by either IPEC or supplemental personnel that left the SAT states links W105 and W106 open during the 2014 spring outage (2R21). A review was performed of 42 Work Order (WO) tasks conducted during the 2014 spring outage. None of the WO tasks required work on the SAT LTC links or required work in the specific area of the states links. Corrective actions included closure of the SAT LTC Terminal Block states links and testing. The control links for the Unit 3 SAT will be inspected to verify they are in the correct position. All troubleshooting work orders will require concurrent verification that any equipment manipulation is restored to its original configuration. The SAT LTC Preventive Maintenance (PM) procedure will be revised to insure steps are added to require independent verification for all LTC SI logic control link manipulation. The event had no significant effect on public health and safety.
2472016007 | Indian Point 2 | 06/10/2016 | 08/09/2016 | ML16229A18 | <strong>Safety System Functional Failure and Common Cause Inoperability of the Emergency Core Cooling System due to Violation of Containment Sump Debris Barrier Integrity</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2016, Entergy management was advised by the NRC that during a tour in containment while the unit was in Mode 4, the inspector identified two open barrier gates for the Emergency Core Cooling System (ECCS) sump. Personnel were moving scaffolding from inside the crane wall to areas outside the crane wall through the two open barrier gates. Having both sump barrier gates open violated ECCS operability basis which requires the sump barrier system to be operable in Modes 1-4. The inspector notified the operator touring with him of the observation. The operator subsequently coached the Radiation Protection (RP) door guard to ensure that one of the gates be closed at all times. The apparent cause was a latent organizational weakness associated with the use of procedure OAP-007 (Containment Entry and Egress) which had not been communicated well within the organization. The failure mode was personnel not being aware of all available information. The scaffold supervisor was not aware of his requirement to serve as containment coordinator and provide the required briefing on gate closure. The RP brief was focused on the locked high radiation requirements not gate control. Corrective actions included closing and securing one gate, briefing RP personnel on the event, the lessons learned and management expectations. This event will be included in all 3R19 supplemental supervisors qualifications required reading list. Procedure OAP- 007 will be revised to include a checklist for entry briefings to include GS-191 requirements. The event had no significant effect on public health and safety.
2472016008 | Indian Point 2 | 06/24/2016 | 08/23/2016 | ML16239A39 | <strong>Technical Specification Required Shutdown due to Not Completing Repairs to a Defect in a Service Water Pipe to the 21 Component Cooling Water Heat Exchanger within the TS AOT</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2015, a leak was discovered on Service Water (SW) weld F-1924, which joins a cement-lined carbon steel elbow to a Copper/Nickel (Cu/Ni) Heat Exchanger pipe nozzle on the 21 Component Cooling Water Heat Exchanger. Code case N-513-3 was applied to the pipe defect to justify continued operability and preparations initiated for a weld repair during the upcoming spring refueling outage (RO) starting March 7, 2016. On March 19, 2016, weld repair was performed on the weld F-1924 and satisfactory nondestructive examination was completed. On June 12, 2016, a new leak was discovered in the same SW pipe repair area. During the subsequent repair, cracking was experienced in the ERCuNi filler metal which extended the duration of the repair and forced a Unit shutdown to comply with the TS 72 hour AOT. The direct cause was recurring longitudinal solidification cracks that developed during welding of copper-nickel to carbon steel pipe. The apparent cause was that the team assigned to prepare and execute the weld repair plan failed to ensure all risks and issues were identified and managed properly. Key corrective actions included weld repair using a new vendor weld procedure and ERNiCu-7 filler material, communication of the lessons learned to all site personnel reinforcing standards and expectations for readiness for critical work. Incorporate recommendations for improving risk management process effectiveness by incorporating actions taken in response to INPO IER L2-16-9. The event had no effect on public health and safety.
2472016009 | Indian Point 2 | 07/06/2016 | 09/06/2016 | ML16256A78 | <strong>Automatic Reactor Trip due to Actuation of the Trip Logic of the Reactor Protection System During Preparation for Testing</strong><br /><i>Abstract:&nbsp;</i>On July 6, 2016,Instrument and Control (I&C) technicians were preparing to perform 2-PT-2M3A (RPS Logic Train B Actuation Logic Test and Tadot). Prior to starting the test, the I&C technicians were unable to locate key #184 that was identified in the test as associated with the reactor trip breaker B bypass key switch. Control Room staff recommended obtaining key #183 associated with reactor trip breaker A bypass key switch to use in lieu of key #184. To ensure the key would work prior to starting the test, the train B bypass key switch was positioned by an I&C technician to the Defeat position. Because reactor trip Bypass Breaker B was in the racked out position, when the key switch was taken to the Defeat position, it caused the normal Reactor Trip Breaker B to open, which initiated a reactor trip (RT) and auxiliary feedwater system actuation. The direct cause was an I&C technician turned the key interlock to defeat on switchgear Channel B Reactor Protection Logic without having the BYB Bypass breaker racked in and closed. The root cause was Indian Point personnel emphasized work culture production goals without fully recognizing the need to maintain fundamental standards and expectations for nuclear workers. Key corrective actions included site all-hands meeting discussing the event, lessons learned, reinforced expectations and the Fleet Refocus Initiative. As an interim action, all essential work that effects generation was required to have direct oversight by a superintendent or above, all work start authorizations provided by operations undergo a work challenge utilizing a new checklist from this event. Complete the actions associated with the Fleet Refocus Observation program. The event had no effect on public health and safety.
2472016010 | Indian Point 2 | 11/21/2016 | 02/28/2017 | ML17069A17 | <strong>Safety System Functional Failure due to an Inoperable Containment Caused by a Through Wall Defect in a Service Water Supply Pipe Elbow to the 24 Fan Cooler Unit</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2016, as a result of investigating an increased level rise in the Waste Hold-Up Tank (WHUT), Operators identified a corresponding rise in containment sump level. A containment entry was made to investigate the source of the sump level rise and determined the source was a through wall leak in a Service Water (SW) supply pipe elbow to the 24 Fan Cooler Unit (FCU). The leak constituted a breach of a closed system within containment. Technical Specification (TS) 3.6.1 (Containment) was entered and containment declared inoperable. TS 3.6.6 (Containment Spray and Fan Cooler System) was entered when the 24 FCU was secured and SW to the 24 FCU was isolated. Inspections identified a through wall leak on a SW supply pipe elbow to one of the 24 FCU water boxes. The leak is on a 3 inch carbon steel epoxy-lined elbow. The pipe fitting is in an ASME ISI Code Class 3, nuclear safety related piping system. The direct cause was failure of the interior coating allowing brackish river water to corrode the carbon steel fitting. The root cause was the maintenance coating procedure requirements for post-coating inspections were inadequate. Key corrective actions included removal of the defective elbow and weld repair, recoating and re-installation. Maintenance procedure 0-SYS-409-GEN will be revised to mandate detailed inspections and/or testing of surface preparation and applied coatings to ensure proper coverage and adhesion. The event had no effect on public health and safety.
2492016001 | Dresden 3 | 06/27/2016 | 08/25/2016 | ML16239A39 | <strong>Alert Declared from Unit 3 HPCI Auxiliary Oil Pump Motor Fire</strong><br /><i>Abstract:&nbsp;</i>On 6/27/16 at approximately 1042 CDT, the High Pressure Coolant Injection (HPCI) Auxiliary Oil Pump (AOP) motor failed and was discovered on fire during the performance of the quarterly operability run of the HPCI system. The fire was extinguished manually at 1045 CDT with a carbon dioxide fire extinguisher. At 1050 CDT, an ALERT was declared. The fire did not adversely impact the operation of any system other than HPCI which was inoperable prior to the fire due to the operability run. At 1319 CDT, the ALERT was terminated. The unit remained at full power throughout the evolution. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident."
2502016001 | Turkey Point 3 | 02/08/2016 | 08/15/2016 | ML16243A04 | <strong>Loose Breaker Control Power Fuse Caused 3B Emergency Containment Cooler to be Inoperable Longer Than Allowed</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2016 at approximately 0147 hours, during a surveillance test, control room indications identified that 3B Emergency Containment Cooler (ECC) fan tripped. Troubleshooting found the control power fuse for the fan's power supply breaker was loose in its fuse holder. Investigation revealed that the fuse holder clips had been widened during work activities associated with the installation of the new breaker during the prior Unit 3 refueling and maintenance outage. The most probable cause of the loose fuse was improper insertion. The installation procedure did not validate fuse holder gap, fuse alignment, and fuse tightness after its last removal and insertion prior to placing the new breaker in service. Inadequate contact during the surveillance test caused the fan trip. The 3B ECC would not have reliably met its safety function mission time and so was determined to be inoperable for approximately 72 days exceeding the 72 hour Technical Specification allowed outage time. In addition, on several occasions during the 72-day period one of the other two ECCs was inoperable concurrently for testing. Corrective actions include: 1) The fuse holder clips were adjusted to provide a tight fit. 2) A review determined additional similar breakers will be inspected for fuse tightness. 3) Future installation and preventive maintenance of similar breakers will check for fuse tightness and correct if necessary. Safety significance is considered low based on a risk assessment showing Incremental Conditional Core Damage Probability and Incremental Conditional Large Early Release Probability are below the NRC acceptance criteria for minimal risk impact.
2512016001 | Turkey Point 4 | 05/03/2016 | 06/30/2016 | ML16194A34 | <strong>Technical Specification Action Not Taken for Unrecognized Inoperable Reactor Protection Instrument Channel</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2016 Engineering personnel identified the potential past inoperability of Reactor Protection System Overtemperature Delta T and Overpressure Delta T Channel III. Corrected coefficients were input to a Loop C resistance temperature detector (RTD) and resulted in a significant change to the setpoint. Evaluation confirmed that the Channel III setpoint had exceeded the Technical Specification (TS) allowable value and was inoperable for approximately five days. Because the inoperable condition was not recognized at the time, the TS required actions were not taken. During the five-day period, an additional channel was inoperable and not tripped during test/adjustment activities for a cumulative period of approximately four hours. This resulted in a loss of the specified safety function during the four-hour period. The root cause is the absence of a controlled engineering document describing the derivation of RTD coefficient data. Corrective actions: 1) Revise the RTD replacement procedure to require validation of the correct methodology for deriving RTD coefficients, and 2) Establish a controlled calculation that contains the basis and methodology for deriving RTD coefficients.
2542016001 | Quad Cities 1, Quad Cities 2 | 01/12/2016 | 05/01/2017 | ML17121A15 | <strong>Secondary Containment Differential Pressure Momentarily Lost due to Air Line Failure (RWCU Hx Rm)</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2016, at 13:40 hours, The Main Control Room received alarms indicating a low differential pressure in the reactor building. The alarms occurred during an entry to the Unit 2 Reactor Water Cleanup (RWCU) Heat Exchanger (HX) room. A negative reactor building pressure was restored within one minute (alarm cleared at 13:41 hours) by immediately securing a reactor building supply fan. Since both Units 1 and 2 share a common reactor building (RB), the loss of differential pressure (RB pressure went positive) for approximately one (1) minute impacted both Units 1 and 2 secondary containments. <br /><br /> The cause was a sheared air line inside the Unit 1 RB ventilation exhaust plenum which depressurized the air header supplying operating air to all three Unit 1 reactor building exhaust fan isolation dampers and causing the dampers to fail open, including the one on the standby fan. <br /><br /> Corrective actions included replacing the sheared air line, and the addition of a preventive maintenance task for replacement of equivalent air lines on all RB supply and exhaust fan dampers. The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10CFR 50.73(a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542016002 | Quad Cities 1, Quad Cities 2 | 01/15/2016 | 05/01/2017 | ML17121A15 | <strong>Secondary Containment Differential Pressure Momentarily Lost due to Air Line Failure (RWCU Pump Rm)</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2016, at 20:38 hours, The Main Control Room received alarms indicating a low differential pressure in the reactor building. The alarms occurred during an entry to the Unit 2 Reactor Water Cleanup (RWCU) pump room. A negative reactor building pressure was restored within two minutes (approximately 20:40 hours) without operator action. Since both Units 1 and 2 share a common reactor building (RB), the loss of differential pressure impacted both Units 1 and 2 secondary containments.<br /><br /> The cause was a sheared air line inside the Unit 1 RB ventilation exhaust plenum which depressurized the air header supplying operating air to all three Unit 1 RB exhaust fan isolation dampers and causing the dampers to fail open, including the one on the standby fan.<br /><br /> Corrective actions included replacing the sheared air line, and the addition of a preventive maintenance task for replacement of equivalent air lines on all RB supply and exhaust fan dampers. The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10CFR 50.73(a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2552016002 | Palisades | 03/24/2016 | 05/23/2016 | ML16144A68 | <strong>Both Control Room Ventilation Filtration Trains Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0211 hours on March 24, 2016, both control room ventilation filtration system trains were declared inoperable in accordance with Technical Specification (TS) 3.7.10, Condition B, due to the inability to fully close control room envelope (CRE) boundary door-15. Mitigating actions were implemented that ensured CRE occupant radiological exposures would not exceed limits and CRE occupants would be protected from chemical and smoke hazards. After maintenance was performed, door-15 was fully closed and both control room ventilation filtration system trains were declared operable for this condition at 1828 hours on March 24, 2016. <br /><br /> Inadvertent operation of the normal opening/closing handwheel of door-15 to the closed position, prior to the door being fully closed, caused the door's locking bolts to extend out from inside the door body to the locked closed position. This created interference between the door and the door frame that prevented the door from being closed. An interlock prevents the door's locking bolts from moving, using the normal opening/closing handwheel, when the locking bolts are extended and the door is open. Due to the lack of detail in the operating instructions posted on the door, and the personnel being unaware of the interlock, they continued to try and manipulate the locking bolts via the handwheel. Continued operation of the handwheel, with the interlock activated, potentially caused a failure of a bushing inside the door's operating mechanism. The failed bushing prevented normal and emergency operation of the door's locking bolts. <br /><br /> The failed bushing inside the door's operating mechanism was replaced. Additional corrective actions include sharing lessons learned from this event, adding adequate detail to the operating instructions posted on the door, and modification to the door's preventative maintenance program to include bushing inspection and, if needed, replacement.
2592016001 | Browns Ferry 1 | 04/22/2016 | 06/21/2016 | ML16173A25 | <strong>Failure of 4kV Shutdown Board Normal Feeder Breaker Results in Actuations of Emergency Diesel Generators and Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2016, at 1358 Central Daylight Time (CDT), during transfer of the 4160 V (4kV) Shutdown Bus from Alternate to Normal, the Normal Feeder Breaker (BKR 1722) failed to close when the Alternate Feeder Breaker was manually tripped. 4kV SD Bus 2 de-energized, resulting in the loss of 1B and 2B Reactor Protection System (RPS) as well as Steam Jet Air Ejector 1B. Emergency Diesel Generators (EDG) C and D started, but did not tie to the 4kV Shutdown Boards due to Operations personnel immediately re-closing the Alternate breaker and re-energizing 4kV Shutdown Bus 2. Invalid actuations of several Containment Isolation Valves also occurred during this event due to the loss of RPS. At 1530 CDT, EDG C and D were shut down. BFN, Unit 1, was returned to normal operating conditions. <br /><br /> The cause of this event was loose wires in the closing control circuit for BKR 1722 due to work in the vicinity of the control circuit termination points. Corrective actions were to terminate loose wires, using a ring type lug instead of a forked spade type lug, in the closing control circuit for BKR 1722; and to verify Shutdown Bus 2 transferred successfully to BKR 1722. A briefing was provided to Electrical personnel who perform modifications to discuss the potential consequences of installing tie wraps and performing other activities that could adversely affect existing wiring.
2592016002 | Browns Ferry 1 | 04/20/2016 | 09/19/2016 | ML16263A22 | <strong>High Pressure Coolant Injection Safety System Functional Failure due to Inoperability of Primary Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 18, 2016, the Unit 1 High Pressure Coolant Injection (HPCI) System was removed from service for a scheduled maintenance outage. In support of maintenance activities, the HPCI steam line inboard primary containment isolation valve (PCIV) was placed in the closed position. Following the maintenance outage, warmup of the HPCI System commenced on July 20. During this evolution, unexpected system pressure conditions and responses were encountered that indicated the PCIV was not open. Failure to open the valve resulted in the inability to restore HPCI System operability and a reportable safety system functional failure. Because the valve is a PCIV located inside primary containment, the station planned and manually shutdown the reactor on July 26 for troubleshooting and corrective maintenance. A local leak rate test determined the PCIV function was ineffective, and disassembly of the valve found the valve stem severed. Following repair, the PCIV functions and HPCI System were declared operable on July 31 and August 1, respectively. Unit 1 was returned to full power on August 4. <br /><br /> The cause of this event was a tensile failure of the valve stem. The cause analysis concluded that the failure occurred on April 20, 2016, when the valve was stroked for in-service testing. Based on this the PCIV was inoperable longer than allowed by Technical Specifications. Corrective actions include valve repair, procedure revisions to provide additional margin to prevent back-seating, revision of guidance for high speed valve open limit switch settings, and evaluation of the extent of condition population. The safety significance of this event was determined to be low.
2592016003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 08/03/2016 | 10/03/2016 | ML16277A09 | <strong>Fire Safe Shutdown Procedures Do Not Consider Potential for Fire-Induced Failure of 4kV Shutdown Board Under-Voltage Trip Functions</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2016, at 1300 Central Daylight Time (CDT), during reviews to respond to a NRC information request for the 2016 NRC Triennial Fire Protection Inspection regarding Emergency Diesel Generator A (EDG) alignment in Fire Safe Shutdown (FSS) procedure 0-FSS-9 (Electrical Battery Board Room 2A and 250V Battery Rooms EL 621’), it was discovered that the National Fire Protection Association (NFPA) 805 analysis and FSS procedures do not consider the potential for fire-induced failure of the 4kV Shutdown Board under-voltage trip function for EDG power supply alignments. Fire-induced failure of the board undervoltage trip function may result in the need for Operations personnel to perform additional actions. These actions, to trip board loads, are currently not included in the FSS procedures. <br /><br /> The cause of this condition was a human error which occurred during the transition of the fire protection program from Appendix R to NFPA 805. Corrective actions are to revise fire protection calculations, update fire protection models, provide coaching to the individuals involved, and add interim compensatory measures to FSS procedures in order to account for this condition. The risk significance of this condition was determined to be very low.
2592016004 | Browns Ferry 1 | 10/08/2016 | 04/28/2017 | ML17118A00 | <strong>Incorrect Tap Settings for the Unit 1 480V Shutdown Board Transformers Results in Inoperability of Associated 480V Shutdown Boards</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2016, during the performance of preventive maintenance of the transformer winding turns ratio test on the 480V Shutdown Board transformer TS1B, it was discovered that the transformer was set on the incorrect tap. This would result in lower than minimum required voltages at the electrically downstream buses and equipment during a postulated loss of coolant accident coincident with degraded voltage conditions. Transformers TS1A and TS1B and their associated 480V shutdown boards were determined to be inoperable since installation prior to Unit 1 restart from an extended outage in 2007. This event is being reported as a condition which was prohibited by the plant's Technical Specifications, a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition, remove residual heat, or mitigate the consequences of an accident, and a condition that resulted in the nuclear plant being in an unanalyzed condition that significantly degrades plant safety.<br /><br /> The cause of this event was the technicians did not use the correct drawings to install the transformers because they were incorrectly classified and listed as "documentation only" drawings. There were no steps in the work order to correctly set the taps. Corrective actions were to re-set the taps for the transformers in accordance with the applicable drawing, validate other similar transformer settings, and revise the classification for the applicable drawing.
2592016005 | Browns Ferry 1 | 11/30/2016 | 01/30/2017 | ML17030A31 | <strong>Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2016, the Tennessee Valley Authority was presented with as-found testing results indicating that three of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear, Unit 1, exceeded the +/- 3 percent setpoint required for their operability. Troubleshooting determined that the MSRV discs failed by corrosion bonding to their valve seats. The valve discs were previously platinum coated to prevent this, but the valve seat's rough Stellite surface caused the coating to delaminate. <br /><br /> These three MSRVs were found to have been inoperable for an indeterminate period of time between October 29, 2014, and October 1, 2016, and longer than permitted by Technical Specifications. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, activation through the Automatic Depressurization System, or MSRV Automatic Actuation Logics was not affected. The valves remained capable of performing their required safety function. <br /><br /> Corrective Actions were to replace all Unit 1 MSRV pilot valves, to analyze the pilot valves of the inoperable MSRVs, and to revise procedures to verify the pilot disc finish meets its requirements prior to valve assembly.
2602016001 | Browns Ferry 2 | 06/17/2016 | 02/21/2017 | ML17052A03 | <strong>High Pressure Coolant Injection Safety System Functional Failure due to a Blown Fuse and a Failed Relay</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2016, while performing a High Pressure Coolant Injection (HPCI) Time Delay Relay Calibration surveillance, an abnormal indication of no voltage to the Time Delay Relay coil was received. The electricians backed out of the procedure and informed Operations. Later that day, upon performing procedure step 7.3[17], fuse BFN-2-FU2-073-0039B cleared and a HPCI Logic Power Failure alarm was received. The loss of logic power rendered Unit 2 HPCI system inoperable. The most likely cause of the blown fuse was an equipment ground induced by the TM200 timer used in the calibration procedure for timing pick-up of the time delay relays. While the HPCI Time Delay Relay calibration was being performed, there was already a known ground on Battery Board 2. The corrective action is to revise the calibration procedures to reconfigure the setup of the test equipment to reduce the probability and consequences of a ground induced by the test equipment. <br /><br /> During troubleshooting of the blown fuse, relay 2-RLY-073-23A-K43 was replaced. It was later identified during bench testing that this relay was faulty as the result of normal breakdown of the coil insulation over time. This breakdown was attributed to end-of-life failure. The immediate corrective action to address the relay failure was replacement of the relay. To address the end of life failure of this relay, a preventative maintenance (PM) task was created to replace this relay every 16 years.
2612016001 | Robinson 2 | 01/19/2016 | 03/21/2016 | ML16081A43 | <strong>Inoperability of Motor-Driven Auxiliary Feedwater Pumps due to Insufficient Lube Oil Cooling</strong><br /><i>Abstract:&nbsp;</i>At 1540 hours EST on 01/19/2016 with H. B. Robinson Steam Electric Plant, Unit No. 2, in Mode 1 at 100 percent power, Motor-Driven Auxiliary Feedwater (MDAFW) pump "B" failed its surveillance test due to flow switch FSL-1633B failure to indicate service water flow to the Oil Cooler and Packing Channel Cooler. It was discovered that flow was blocked due to stem and disc separation on the MDAFW pump "A" and "B" cooling flow return isolation valve, SW-115. This blockage rendered both MDAFW trains inoperable for a period longer than allowed by plant Technical Specifications (TS). TS 3.7.4, Auxiliary Feedwater (AFW) System, requires four AFW flow paths and three AFW pumps be operable in Modes 1, 2, and 3, and Mode 4 when steam generator is used for heat removal, allowing 24 hours to restore one of two inoperable MDAFW pumps to operable status. Since two MDAFW pumps were inoperable due to common cause for approximately 52 hours, this condition is reportable as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B), and reportable under 10 CFR 50.73(a)(2)(vii), Common Cause Inoperability of Independent Trains or Channels. The total duration of both trains of MDAFW being unavailable was limited to approximately 3 hours. <br /><br /> An investigation concluded that the failed valve (SW-115) was likely installed in poor condition, without documentation, and outside of design specifications prior to 1978. The valve has been replaced with a valve meeting current design specifications. The health and safety of the public was not jeopardized as a result of this condition.
2612016002 | Robinson 2 | 04/13/2016 | 06/13/2016 | ML16165A31 | <strong>Unanalyzed Condition Related to Main Steam Line Break Inside Containment</strong><br /><i>Abstract:&nbsp;</i>At 1430 hours EST on 4/13/2016 with H. B. Robinson Steam Electric Plant, Unit No. 2 in Mode 1 at 100 percent power, it was determined that the source document for the mass and energy release parameters used to determine the containment pressure and temperature response to a main steam line break inside containment does not adequately account for all possible single active failure scenarios in the steam or feedwater line isolation provisions. The source document addresses the active failure of the main feedwater regulating valves to close in the faulted steam generator feedline, but not the failure of a feedwater regulating bypass valve to close in that feedline. An active failure of a feedwater regulating bypass valve whereby the valve fails to close will increase the secondary mass available for release to the containment structure. This can result in higher peak containment pressure that could challenge the containment design pressure. This condition is only a concern when the feedwater regulating bypass valves are in the open position in Modes 1, 2, or 3, and they fail to close on an engineered safeguards actuation signal. Administrative controls and corrective actions have been implemented to maintain design control of the feedwater regulating bypass in these modes of operation.
2612016003 | Robinson 2 | 08/11/2016 | 10/10/2016 | ML16285A38 | <strong>Failure of Lake Robinson Tainter Gates to Fully Open During Performance of Functionality Testing</strong><br /><i>Abstract:&nbsp;</i>The prevention of flood intrusion on plant grade at H. B. Robinson Steam Electric Plant, Unit No. 2 (RNP), is achieved through lake level control that is performed by two electrically-operated Tainter Gates under normal operation. On 06/06/2016 and 07/07/2016 with RNP in Mode 1 at 100 percent power, Tainter Gates B and A were respectively identified as degraded due to the failure to meet their functionality test requirements (excessive binding of the lift gate chains due to corrosion). RNP License Renewal program requires full travel test for the radial arm Tainter Gates to demonstrate functionality of the gates and identify any issues with operation. The Tainter Gates have been repaired, tested and rendered compliant with their original licensing basis function. On August 11, 2016 (ENS #52174), it was determined this event or condition placed RNP in an unanalyzed condition that significantly degrades plant safety. <br /><br /> No actual Probable Maximum Precipitation Design Basis Event (PMP DBE) occurred during the period of time the Tainter Gates were in a degraded condition. Thus, this LER only considers the loss of the Emergency Diesel Generators (EDGs) and the resulting Extended Loss of Alternating Power (ELAP), if a PMP DBE had occurred. This report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(v)(D), "Prevention of Fulfillment of Safety Function," and 10 CF CFR 50.73(a)(2)(ii) (B), "Degraded or Unanalyzed Condition."
2612016004 | Robinson 2 | 08/24/2016 | 10/24/2016 | ML16298A10 | <strong>Reactor Trip During the Performance of a Visual Inspection of the Main Turbine Trip Block</strong><br /><i>Abstract:&nbsp;</i>At 1338 hours EDT On 08/24/2016, with the Unit in Mode 1 at 100 percent power, H. B. Robinson Steam Electric Plant, Unit 2 (RNP), experienced an automatic turbine trip followed by an automatic reactor trip during the performance of a visual inspection of the Main Turbine Trip Block. Following the reactor trip, the Auxiliary Feedwater System actuated as expected on low steam generator level. There were no other equipment performance issues.<br /><br /> The cause of this event is attributed to the absence of a standard that would govern risk assessment and control of work activities around trip sensitive equipment. The perceived low significance nature of the risk in conjunction with the evolution comprising only a visual inspection and the procedural silence with respect to data gathering activities in the proximity of trip sensitive equipment, taken together gave rise to the unintended turbine trip, and a subsequent reactor trip. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to the event resulting in an automatic actuation of the Reactor Protection System (RPS) and Auxiliary Feedwater System (AFW).
2612016005 | Robinson 2 | 10/08/2016 | 02/22/2017 | ML17054C34 | <strong>Reactor Trip and Automatic System Actuation due to Weather-Related Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>At 1302 hours Eastern Daylight Time (EDT) on 10/08/2016 with the plant in Mode 1 at 100 percent power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2), experienced a grid perturbation. As a result, HBRSEP2 experienced a reactor trip due to low voltage on the 4kV buses. Plant safety systems responded with the emergency buses separating from offsite power due to emergency bus undervoltage. The emergency diesel generators (EDG) started and powered the 480V emergency buses. 'A' service water pump did not start on the blackout sequencer; however, sufficient service water flow was available from the three operating service water pumps. This failure did not aggravate this event. The site declared an Unusual Event (UE) at 1317 EDT for loss of power to emergency buses. At 0011 EDT on 10/09/16, the UE was terminated. <br /><br /> Once the power grid was stable, plant personnel commenced restoration of offsite power to allow shutdown of the EDGs. During this evolution, at approximately 2323 EDT on 10/08/2016, an automatic actuation of the 'B' auxiliary feedwater (AFW) pump occurred due to improper breaker coordination that satisfied the autostart logic for the AFW system. <br /><br /> The apparent cause of the voltage transient in the HBRSEP2 switchyard is a failed fault detection relay, which prevented the grid fault from being immediately isolated. The failed relay has been replaced.
2632016001 | Monticello | 03/22/2016 | 05/25/2017 | ML17146A19 | <strong>High Pressure Coolant Injection System Cracked Pipe Nipple Caused Oil Leak</strong><br /><i>Abstract:&nbsp;</i>The High Pressure Coolant Injection (HPCI) system was inoperable during a pre-planned maintenance activity when a significant oil leak in HPCI system oil piping occurred because of a cracked oil pipe nipple. The leak was of sufficient size that if it occurred outside the pre-planned maintenance, HPCI would have been declared inoperable. The equipment failure analysis concluded that the most likely cause was that HPCI pipe nipple was exposed to significant loads, sufficient to initiate a crack, likely from applied wrench torques during oil leak repair activities in 2005. With the presence of the crack and crack propagation mechanism, the engineering evaluation determined that HPCI was inoperable from January 9 through March 24, 2016, i.e. 75 days. The organizational root cause was that management and individuals were tolerant of leaks on the HPCI system. As a result, station personnel did not effectively advocate prompt repair of the HPCI oil leak. <br /><br /> The cracked HPCI oil pipe nipple was replaced. Results of the extent of condition review identified two other pipe nipples and two elbows with thread leakage (no crack present). The pipe nipples were replaced and the elbows were reused. The HPCI system was tested successfully after the repairs.
2632016002 | Monticello | 08/04/2016 | 12/19/2016 | ML16354A65 | <strong>Inadequate Appendix R Fire Barrier Impacts Safe Shutdown Capability</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2016, while performing a Fire Protection/Appendix R self-assessment, it was discovered that the floor between the Cable Spreading Room (CSR) and the Plant Administration Building (PAB) basement is not an adequate Appendix R fire barrier. Because the CSR and the PAB are located in the same Fire Area (FA), a fire in the PAB could spread to the CSR requiring evacuation of the control room (CR). When the CR is evacuated, alternate shutdown activities are performed at the Alternate Shutdown System (ASDS) Panel. The travel path used to access the ASDS Panel following control room evacuation traverses the same fire area in the PAB. <br /><br /> This unanalyzed condition resulted from the determination that because of the inadequate fire barrier, a fire in the PAB would now require use of an alternate shutdown strategy to safely shutdown the reactor. However, the alternate shutdown strategy requires that the operators traverse from the control room through the PAB Fire Area to access the alternate shutdown equipment. This path could be impacted by the PAB fire.<br /><br /> In response to this discovery an hourly fire watch was established.
2632016003 | Monticello | 11/27/2016 | 05/25/2017 | ML17146A19 | <strong>HPCI Declared Inoperable due to Excessive Water Level in Turbine</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2016, the Monticello Nuclear Generating Plant (MNGP) was operating at 100% power. While troubleshooting was in progress for a minor leak on the High Pressure Coolant Injection System (HPCI) turbine, it was discovered that the HPCI turbine exhaust drain pot level switch was not functioning per design to support removal of condensate from the HPCI turbine. Subsequently, HPCI was declared inoperable at 1447 hours due to excessive water level within the HPCI turbine.<br /><br /> Previously, on November 17, 2016, a steam leak was identified on the packing of the HPCI turbine steam supply valve. Following valve packing maintenance on November 21, 2016, the valve was cycled cold (without steam flow), resulting in seat leakage that slowly admitted steam into the HPCI exhaust piping. The steam condensed to water and accumulation began to form in the HPCI turbine. Subsequent troubleshooting found the HPCI exhaust drain pot level switch electrical rocker assembly off its pivot point due to a manufacturer defect (missing spot weld). With the inability to pivot, the level switch became non-functional and thus failed to alert the control room and provide the automatic function to drain condensate from the HPCI exhaust piping. The HPCI exhaust piping was drained of condensate and a temporary modification replaced level switch. HPCI was restored to operable status at 1726 hours on December 1, 2016.
2652016001 | Quad Cities 2 | 03/21/2016 | 05/19/2016 | ML16155A12 | <strong>Main Steam Isolation Valve Local Leak Rate Tests Exceed Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2016, at 2200 hours, with Unit 2 shutdown for refuel outage Q2R23, the as-found local leak rate tests (LLRT) for the four (4) main steam lines (MSL) were performed following closure of the main steam isolation valves (MSIV). The initial as-found LLRT on the "A" and "C" MSL MSIVs exceeded the minimum pathway criteria (lesser leakage in a line) of the Technical Specifications (TS), and the combined total leakage of all MSLs also exceeded the minimum pathway criteria (lesser leakage in each line when combined for all MSIVs) of the TS. <br /><br /> Corrective actions included flushing, disassembling, inspecting, repairing, and retesting the valves. Future corrective actions include installation of an improved spherical nose plug design to the MSIV plug and seat, and installation of an anti-rotation device to the MSIV pilot. <br /><br /> Valves 2-0203-2A and 2-0203-1C were disassembled and inspected. The most likely cause for the higher than expected leakages has been determined to be a valve design that is susceptible to a degraded main plug / seat interface during valve closure. A contributing cause was susceptible pilot plug / seat misalignment, due to pilot disc stem nut wear.<br /><br /> The safety significance of this event was minimal. The total primary containment leakage of 315.866 scfh was well within the allowed leakage limit of 1372.99 scfh (La). However, since the "A", "B", "C" and "D" MSL MSIV as-found leakage exceeded the TS limit, and the combined total leakage of all MSLs exceeded the TS limit, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of a past operation or condition which was prohibited by the plant Technical Specifications.
2652016002 | Quad Cities 2 | 04/25/2016 | 06/24/2016 | ML16183A26 | <strong>High Pressure Coolant Injection System Declared Inoperable due to Valve Packing Leak</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2016, at 06:07 hours, the High Pressure Coolant Injection (HPCI) System was isolated to stop a packing leak on the Motor Operated (MO) HPCI Outboard Main Steam Isolation Valve (MO 2-2301-5). The packing leak was causing a two (2) foot steam plume to impinge on the valve limit switch compartment, potentially impacting the motor operator for the MO 2-2301-5 valve. Due to the uncertainty on how the steam impingement would affect the valve limit switch compartment, Operations conservatively isolated the steam leak by closing the HPCI Inboard Main Steam Isolation Valve (MO 2-2301-4). With the steam supply isolated, HPCI was declared inoperable and Technical Specification (TS) 3.5.1 Condition G was entered. <br /><br /> The cause of the packing leak was a non-modern style packing installed in 2007 to repack valve MO 2-2301-5. This packing material was susceptible to premature degradation. <br /><br /> Corrective actions included repacking the valve with modern packing and performance of valve diagnostic testing. <br /><br /> The safety significance of this event was minimal. Given the impact on the HPCI system, this report is submitted for Unit 2 in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2652016003 | Quad Cities 2 | 05/25/2016 | 07/25/2016 | ML16230A23 | <strong>Drywell/Suppression Chamber Differential Pressure, Primary Containment Oxygen Concentration Technical Specification Compliance</strong><br /><i>Abstract:&nbsp;</i>On 05/23/16 Low Level Alarm 2A Recirc Motor occurred due to a low oil level condition for the 2A recirculation pump motor. As a result, the Station determined that a drywall entry was required to investigate the condition, make any needed repairs, and refill the oil reservoir. NRC provided that Station personnel did not comply with Technical Specifications (TS) 3.6.2.5 (DW to Suppression Chamber DP) and 3.6.3.1 (Primary Containment O2 concentration) since while in MODE 1, at the end of the 32 hour Completion Time (24 hour Action A, plus the 8 hour Action B) during the actual plant evolutions for power ascension, these Required Actions were not met because the associated Applicability for each TS were not met since the Unit remained in MODE 1. <br /><br /> The cause of the issue was Station personnel understanding and application of the subject TS as used in context under this infrequent plant condition, differed from the NRC's understanding and application of the subject TS. The specific difference is with the application of the term, "start-up," as used in the LCO Applicability. <br /><br /> Corrective actions included issuance of an Operations Standing Order, and revision of pertinent Operating procedures to ensure these Tech Specs are properly implemented. <br /><br /> The safety significance of this event was minimal. Given the impact on the Drywall/Suppression Chamber Differential Pressure, and Primary Containment Oxygen Concentration Technical Specifications, this report is submitted for Unit 2 in accordance with the requirements of 10 CFR 50.73{a)(2)(i)(B), which requires the reporting of a past operation or condition which was prohibited by the plant Technical Specifications.
2662016001 | Point Beach 1 | 03/15/2016 | 05/12/2016 | ML16133A17 | <strong>Unit 1 Degraded Condition</strong><br /><i>Abstract:&nbsp;</i>At 0649 on March 15, 2016 with Unit 1 shut down in MODE 5 for refueling activities, a boric acid indication upstream of the valve seating surface on the inlet of the valve body of 1CV-200B, Letdown Orifice B Outlet Control Valve was identified as a through-wall flaw. The flaw location was within the reactor coolant system (RCS) pressure boundary as defined by 10 CFR 50.2, "Definitions." The valve body is original plant equipment.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(A) for material defects in the primary coolant system that were not acceptable in accordance with ASME Section Xl.
2662016002 | Point Beach 1 | 04/01/2016 | 05/31/2016 | ML16152A09 | <strong>Operation or Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2016 the 345/13.8kV high voltage station auxiliary transformer (1X-03) tripped on a differential current relay (1-87A/X-03) actuation. Review of this event determined that there were three instances over the past three years when the required action completion time for not satisfying the Limiting Conditions For Operation of Technical Specification 3.8.1 (AC Sources - Operating) and 3.8.2 (AC Sources - Shutdown) would have been exceeded with the latent error present. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by technical specifications.
2662016003 | Point Beach 1 | 04/02/2016 | 06/01/2016 | ML16153A15 | <strong>Operation or Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2016, Unit 1 entered MODE 4 from MODE 5 without satisfying all of Technical Specification 3.6.6, Containment Spray and Cooling System Limiting Conditions for Operation (LCO) as required by LCO Applicability 3.0.4. <br /><br /> LCO Applicability 3.0.4 does not permit entry into a MODE of applicability when an LCO is not met, unless the associated actions to be entered permit continued operation in the MODE for an unlimited time or after performance of an acceptable risk assessment and the appropriate risk management actions have been established. After entering MODE 4, it was discovered that components were not operable, contrary to LCO 3.0.4. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by technical specifications.
2692016001 | Oconee 1 | 03/06/2016 | 05/05/2016 | ML16139A84 | <strong>RPS Actuation - Unit 1 Reactor Trip Initiated by a Generator Lockout/Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At 1512 on March 6, 2016, Oconee Nuclear Station (ONS) Unit 1 experienced a Reactor Trip, initiated by an electrical bushing failure on the Unit 1 Main Step-up Transformer that resulted in a transformer fire. The plant response to the trip was evaluated, and was found to be acceptable. The reactor trip is a RPS actuation and requires an LER per 10 CFR 50.73(a)(2)(iv)(A). <br /><br /> Due to the transformer fire a "Notification Of Unusual Event" was declared at 1520. The fire eventually led to a transformer overhead line failure that caused a switchyard bus lockout and the loss of one emergency power path for the site. The second emergency power path and multiple offsite sources remained operable during the event. The emergency classification was upgraded to an "Alert" condition at 1658, upon determining that the fire had an impact on safety related equipment.<br /><br /> The 4-hour notification related to this reactor trip was bounded by the notifications made for the Emergency Classifications described above (See Event Notification 51770). <br /><br /> Post trip conditions and Emergency event conditions were controlled and maintained within the allowances of Technical Specifications with no personnel injuries or challenges to other safety system actuations. The transformer deluge system activation along with the response of onsite and offsite fire teams promptly contained the fire.
2692016002 | Oconee 1, Oconee 2, Oconee 3 | 10/25/2016 | 12/16/2016 | ML17048A52 | <strong>Containment High Range Radiation Monitors Inoperable due to Potential Thermally Induced Current Effects</strong><br /><i>Abstract:&nbsp;</i>On October 25, 2016, the Containment High Range Radiation Monitors (CHRRMs) for each unit were declared inoperable as they could not meet the accuracy requirements of Regulatory Guide (RG) 1.97 for Type E post-accident monitoring (PAM) instrumentation. Oconee Nuclear Station (ONS) Engineering determined that a High Energy Line Break (HELB) in the East Penetration Room of each Unit could cause a false high reading on the CHRRMs RIA-57 and RIA-58 for that Unit. The false high reading would be due to the potential for Thermally Induced Currents (TIC) to affect the accuracy of the radiation monitor readings as discussed in NRC Information Notice 97-45, Supplement 1. <br /><br /> This condition existed for as long as the CHRRMs were installed with none of the actions required in Technical Specification (TS) 3.3.8 taken. Therefore the Completion Times of TS 3.3.8 were exceeded and the condition is reportable under 10 CFR 50.73(a)(2)(i)(B) as plant operation prohibited by Technical Specifications. <br /><br /> ONS will review Fleet and Industry Operating Experience when determining the best path forward for restoring operability of the CHRRMs.
2692016003 | Oconee 1 | 11/25/2016 | 01/24/2017 | ML17030A04 | <strong>Engineered Safeguards Protection System Automatic Actuation Output Logic Bypassed</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2016, at 0645, with Unit 1 in MODE 3 during startup from a refueling outage, the Operations Control Room crew recognized that the Unit 1 Engineered Safeguards Protective System (ESPS) Voters 1 and 2 were bypassed, rendering both automatic actuation output logic subsystems inoperable. For Unit 1 plant conditions at the time, Oconee Technical Specification (TS) 3.3.7 Limiting Condition for Operation (LCO) required the automatic actuation output logic for Containment Isolation Valves, Reactor Building (RB) Cooling and RB Spray to be OPERABLE. Additionally, Unit 1 had made MODE changes from MODE 5 to MODE 4, and MODE 4 to MODE 3 that were not allowed by TS 3.0.4. At 0728, all ES Voters were placed in Operate and TS 3.3.7 was exited. The manual initiation functions required by TS 3.3.6 remained OPERABLE, therefore the condition did not constitute a loss of safety function. A recent procedure revision and inadequate procedural guidance for unit startup and MODE.changes resulted in the unanticipated ESPS configuration. Corrective actions include revision of procedures for unit startup and MODE change verification. Due to Unit 1 operating in a configuration prohibited by TS, this event is reportable to the NRC and an LER is required per 10 CFR 50.73(a)(2)(i)(B) 'Any operation or condition which was prohibited by plant Technical Specifications.'
2722016001 | Salem 1 | 05/03/2016 | 07/05/2016 | ML16187A33 | <strong>Unanalyzed Condition due to Degraded Reactor Baffle to Former Bolts</strong><br /><i>Abstract:&nbsp;</i>With Salem Unit 1 in a defueled condition during a planned refueling outage, anomalies were identified on baffle to former bolts while conducting a scheduled visual inspection of Reactor Vessel Internals. Due to the visual anomalies, PSEG commenced ultrasonic inspection of the baffle to former bolts to determine the extent of condition and determine a repair plan. <br /><br /> Based on initial results of the analysis of the ultrasonic inspection data received on May 03, 2016, this condition was determined to be reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B), since the as-found conditions were not previously analyzed. <br /><br /> As a result of the inspection approximately 190 baffle to former bolts were identified as needing replacement.
2722016004 | Salem 1 | 08/05/2016 | 10/04/2016 | ML16278A48 | <strong>Containment Fan Coil Units Inoperable for Longer than Allowed by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2016, while performing the scheduled stroke time surveillance testing of the 11 Service Water (SW) Accumulator Discharge Valves, the 11SW535 stroked closed in 3.17 seconds, placing it in the 'Required Action Range' for a stroke time less than 5 seconds. Evaluation determined that the actual valve stoke time did not impact the functionality of the system. Investigation determined that the air supply valve to the 11SW535 had been replaced on May 11, 2016 and that the appropriate retest (stroke time testing of the 11SW535) had not been performed. This affected the operability of 11 and 12 Containment Fan Coil Units (CFCU) after both CFCU's had previously been declared operable. <br /><br /> The 11 and 12 CFCU's were required to be operable upon entry into Mode 4 (while returning the unit to service from 1R24) on July 24, 2016 at 1009. Upon entry into Mode 4, the 13 CFCU was inoperable and had been tagged for maintenance. Inoperability of the 13 CFCU continued until July 28, 2016 at 0103. Additionally the 11 and 12 CFCU's continued to be inoperable until the 11SW535 was retested satisfactorily. Both the 11SW535 and the 11 and 12 CFCU's were declared operable August 6, 2016 at 1826. Technical specification (TS) 3.6.2.3 Requires 5 CFCU's to be operable in Modes 1, 2, 3, and 4. TS 3.6.1.1 requires primary containment integrity be maintained in Modes 1, 2, 3, and 4. The action times for both TS's were not met. This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications....."
2722016005 | Salem 1 | 08/11/2016 | 10/11/2016 | ML16285A34 | <strong>Instrumentation Channels Inoperable for Longer than Allowed by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2016, the channel check for the 13 Loop Over Temperature Delta Temperature (OTDT) was unsat and the channel was declared inoperable. Investigation revealed that the Pressurizer (PZR) Pressure Channel III, input to 13 OTDT, had not been calibrated to the correct acceptance criteria. The PZR pressure Channel III was declared inoperable. During 1R24 on April 21, 2016, PZR channel III had been out of specification during calibration and was adjusted in accordance with the procedure acceptance criteria. Evaluation of the out of specification condition identified that the procedure acceptance criteria was incorrect. The need to re-perform the calibration was identified. Due to inadequate communication of the surveillance status and inaccurate assumptions by individuals the test was not re-performed. The unit was returned to service on July 30, 2016 (entered mode 1) without the channel recalibration being performed. The 13 loop OTDT channel and the PZR pressure channel III were required to be operable in modes 1, 2, and 3. The inoperable channels impacted three Technical Specifications (TS). TS 3.3.2.1, Engineered Safety Feature Actuation System (ESFAS) and TS 3.3.1.1, Reactor Trip System Instrumentation both require that the inoperable channel be placed in the tripped condition within 6 hours. The inoperability of PZR pressure channel III also impacted the function of 1PR1 power operated relief valve (PORV). TS 3.4.3, Relief Valves, requires that with one inoperable PORV, that the PORV is restored to operable within 1 hour or close its associated block valve, remove power from the block valve, and restore the PORV to operable status within the following 72 hours....... The action times for each of these technical specifications were not met. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications...."
2722016006 | Salem 1 | 12/08/2016 | 04/09/2018 | ML18099A28 | <strong>Technical Specification (TS) for Containment Integrity Not Met</strong><br /><i>Abstract:&nbsp;</i>On December 8, 2016 the Containment (CTMT) Air Particulate Detector (APD), Normal Containment Isolation Valves (CIV) were closed to support a planned maintenance activity and the Back Up (B/U) manual isolation valves were opened under administrative controls to support continued operation of the APD. The normal isolation valves and the backup isolation valves were restored to their normal positions on December 29, 2016. The B/U isolation valves were open for 21 days rather than the originally reported 27 days.<br /><br /> On November 14, 2017 NRC Integrated Inspection Report 05000272/2017003 was issued documenting a Green Non- Cited Violation (NCV) of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.1, Containment Integrity. The report states that having the B/U manual CIV's open for 27 days constituted a violation of TS LCO 3.6.1.1, Containment Integrity, in that the valves were not operated in an intermittent manner as specified by the TS. <br /><br /> This supplement provides information not available when the original LER was submitted.
2772016001 | Peach Bottom 2, Peach Bottom 3 | 09/12/2016 | 11/11/2016 | ML16316A11 | <strong>Leak in High Pressure Service Water Pipe Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 9/12/16, an engineering evaluation concluded that a flaw identified on a 1" diameter stainless steel pipe associated with the High Pressure Service Water (HPSW) System could have failed during a seismic event. Failure of the pipe would cause flooding of the '2C' Residual Heat Removal (RHR) pump room and impact operation of equipment in the room if needed during a design basis event. The 1" diameter pipe supplies sample water to the '2C' HPSW radiation monitor sample pump. The flaw was identified on 8/16/16 when a 120 drop per minute leak was observed. The leak was the result of a crack located in the pipe at the toe of a fillet weld connecting the pipe to a coupling on an 18" diameter pipe that returns HPSW water to the plant discharge canal. <br /><br /> There were no actual consequences as a result of the leak. The pipe was replaced and the equipment was returned to service.
2782016001 | Peach Bottom 3 | 09/26/2016 | 11/22/2016 | ML16327A05 | <strong>Leak in High Pressure Coolant Injection Drain Pipe Results in a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On 9/26/16, at approximately 1845 hours, investigation of a water leak on a 3/4" diameter drain line for the High Pressure Coolant Injection (HPCI) turbine determined there was a through-wall flaw resulting in a leak of approximately 2 drops per minute. The pipe is classified as ASME Code Class 2 exempt and operates above 200 degrees F. As a result, the HPCI system was declared inoperable. The flaw was the result of a liquid drop impingement erosion process caused by the flow characteristics upstream of the orifice. The pipe section was replaced and the HPCI system was declared operable on 9/28/16 at approximately 2102 hours.<br /><br /> There were no actual consequences as a result of the leak.
2802016001 | Surry 1, Surry 2 | 05/11/2016 | 07/11/2016 | ML16216A15 | <strong>Emergency Service Water Pump Inoperable due to Corrosion of Valve Support</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2016 at 0638 hours, with Surry Power Station Units 1 and 2 operating at 100% power, the Emergency Service Water Pump (ESWP) 1B cooling water discharge valve flange was found to be cracked, and the pump was declared inoperable. During flange and valve support repair activities, four bolts on the cooling water discharge valve support base plate were found to be failed due to corrosion. The flange was replaced and the support base plates were anchored with stainless steel bolts. ESWP 1B was returned to operable status on April 9, 2016 at 1105 hours. The cause of the flange and support failure was corrosion of the base plate and anchor bolts from repetitive exposure to service water. On May 11, 2016, an Engineering evaluation determined that the piping and support had been non-functional for prior operability based on the potential for lateral displacement during a seismic event. Therefore, this report is being submitted, pursuant to 10 CFR 50.73(a)(2)(i)(B), for operations prohibited by Technical Specifications, and pursuant to 10 CFR 50.73(a)(2)(v)(B), an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. Based on the risk assessment of this event, the risk impact was determined to be of very low significance, and, as a result, the health and safety of the public were not affected.
2812016001 | Surry 2 | 10/09/2016 | 12/02/2016 | ML16350A10 | <strong>Unit 2 Reactor Trip due to Generator Differential Lockout</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2016 at 0254 hours, with Unit 1 and Unit 2 at 100 percent power, Unit 2 experienced an automatic reactor trip initiated by a turbine trip due to generator differential lockout relay actuation. At the time of the trip, high wind and heavy rain conditions existed due to the effects of Hurricane Matthew. All three auxiliary feedwater pumps automatically started on low-low steam generator water level as expected. All plant systems functioned as required, and Unit 2 was stabilized at hot shutdown. The trip response was not affected by any previously inoperable systems, structures, or components. <br /><br /> The direct cause of the generator differential lockout was an electrical ground overcurrent initiated by water accumulation in the "A" phase of the "A" station service transformer leads termination enclosure. Affected electrical enclosures were drained, the system was tested, and modifications to the enclosures to prevent recurrence of water intrusion were completed prior to returning Unit 2 to power operation on October 13, 2016. <br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System.
2822016001 | Prairie Island 1, Prairie Island 2 | 12/21/2015 | 02/18/2016 | ML16049A51 | <strong>Unanalyzed Condition due to Non-Compliant Fire Protection Manual Operator Actions</strong><br /><i>Abstract:&nbsp;</i>On 12/21/2015 with Unit 1 (U1) in Mode 1 at 100% power and Unit 2 (U2) in Mode 3, a technical review of a new weak link calculation as part of the transition to National Fire Protection Association's Performance Based Standard for Fire Protection for Light Water Reactor Electronic Generating Plants (NFPA 805) identified a non-emergency unanalyzed condition reportable under 10 CFR 50.72(b)(3)(ii)(B). Specifically, several motor operated valves (MOVs) credited to be manually operated from outside the control room in the event of a fire in the control room or relay room could be damaged in a postulated fire if hot shorts were to bypass the torque and limit switches. Also, MOVs associated with the Gland Steam system of both U1 and U2 had been added to F5 Appendix B but never analyzed in the event of a hot short. These conditions could impact the ability of plant operators to implement procedure F5 Appendix B, Control Room Evacuation (Fire). The identified MOVs are located in Fire Area (FA) 13 (Control Room) and FA 18 (Relay and Cable Spreading Room). New hourly fire watch impairments were created in these areas as compensatory measures. The fire detection systems in the control room and relay room remain in service. The site submitted Event Notification (EN) 51616. <br /><br /> Reviews of the list of MOVs susceptible to hot shorts bypassing the torque and limit switches continued and additional valves were noted to be affected by this failure mechanism. As a compensatory measure, new hourly fire watch impairments were created for FA 31 ("A" Train Hot Shutdown Panel & Air Compressor/Auxiliary 695 Feedwater Room), FA 32 ("B" Train Hot Shutdown Panel & Air Compressor/Auxiliary 695 Feedwater Room), FA 58 (Auxiliary Building Ground Floor U1) and FA 73 (Auxiliary Building Ground Floor U2). EN 51616 was updated on 01/14/2016. The public health and safety was not impacted.
2822016002 | Prairie Island 1, Prairie Island 2 | 01/29/2016 | 03/25/2016 | ML16085A18 | <strong>Listed System Actuation - Motor-Driven Cooling Water Pump Auto-Start</strong><br /><i>Abstract:&nbsp;</i>At 1110 Central Standard Time (CST) on 1/29/2016, the Prairie Island Nuclear Generating Plant (PINGP) performed a planned overspeed post-maintenance test (PMT) of 22 Diesel-Driven Cooling Water Pump (DDCLP) in accordance with plant maintenance procedure. During the overspeed trip test PMT, 22 DDCLP tripped as expected, and 121 Motor-Driven Cooling Water Pump (MDCLP) unexpectedly started automatically ("auto-started") on low pressure in the cooling water pump discharge header. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system that does not normally run and that serves as ultimate heat sink.<br /><br /> The cause of the 121 MDCLP auto-start was a low-pressure transient in the cooling water pump discharge header resulting from the trip of 22 DDCLP. There was no safety injection signal from PINGP Unit 1 nor Unit 2 when 121 MDCLP started. The health and safety of the public was not at risk.<br /><br /> Corrective actions to be taken for this event include revising plant procedures to ensure 121 MDCLP is running prior to performing the overspeed trip test PMT and to ensure the pump is running or in pullout position to prevent auto-start of 121 MDCLP when stopping a DDCLP.
2822016003 | Prairie Island 1, Prairie Island 2 | 01/07/2016 | 03/04/2016 | ML16109A32 | <strong>Unanalyzed Condition - Procedures Credited by Appendix R Calculations Not in Place</strong><br /><i>Abstract:&nbsp;</i>On 1/7/2016, Prairie Island Nuclear Generating Plant (PINGP) reviewed corrective actions associated with the transition to National Fire Protection Association "Performance-Based Standard for Fire Protection for Light Water Reactor Electric Generating Plants" (NFPA 805). PINGP discovered no cold shutdown repair procedure existed to restore power to train B reactor coolant system (RCS) vent valves to reduce RCS pressure in event of fire in Fire Area (FA) 59 (Auxiliary Building Mezzanine Floor Unit 1) and FA 74 (Auxiliary Building Mezzanine Floor Unit 2). The PINGP Appendix R safe shutdown analysis (SSA) credits such actions for train B RCS vent valves for a fire in these areas. PINGP established compensatory measures for affected equipment and, with automatic detection and suppression capability, these measures ensured protection of potentially affected equipment. The health and safety of the public was not at risk. PINGP submitted Event Notification (EN) 51642 on 1/7/2016 as this event is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. On 04/14/2005, a revision of the SSA was approved that credited a cold shutdown repair 'as a compliance strategy for FA 59 and 74, but no repair procedure existed in the event of a fire in FA 59 nor FA 74. <br /><br /> On 1/11/2016, F5 Appendix D "Impact of Fire Outside Control/Relay Room" was issued and includes cold shutdown repair procedures for Train B RCS vent valves. Lack of technical rigor to ensure procedure F5 Appendix D included actions required by the SSA is the identified cause.
2822016004 | Prairie Island 1, Prairie Island 2 | 04/21/2016 | 06/21/2016 | ML16173A43 | <strong>Missing Fire Barrier between Fire Area (FA) 59 and 85 / Fire Hazard Analysis Drawings Do Not Match Boundary Description</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2016, during a walkdown of fire barriers for the National Fire Protection Association (NFPA) 805 project, it was determined that the fire barrier between Fire Area (FA) 59 (Auxiliary Building Mezzanine Unit 1) and FA 85 (Holdup Tank/ Demineralizer Area) is not a rated barrier due to unsealed combustible pathway penetrations in the barrier.<br /><br /> The walkdown also identified that penetrations in the fire barriers between FA 68 (Unit 1 Annulus) and FA 60 (Auxiliary Building Operating Level Unit 1), FA 68 and FA 61A (Auxiliary Building Hatch Area), FA 72 (Unit 2 Annulus) and FA 75 (Auxiliary Building Operating Level Unit 2), and FA 72 and 61A are not sealed with fire rated materials.<br /><br /> Both conditions were reported under 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degrades plant safety due to the missing fire barrier between redundant Appendix R safe shutdown trains. <br /><br /> The apparent cause was determined to be that the Engineering Manual 3.4.2 does not require Appendix R program owner review of Fire Protection Engineering Evaluations that depend on Appendix R Safe Shutdown analysis. The corrective action is to revise the Engineering Manual 3.4.2 to require Appendix R review when the program is impacted.
2822016005 | Prairie Island 1, Prairie Island 2 | 08/21/2016 | 10/07/2016 | ML16281A20 | <strong>121 Motor Driven Cooling Water Pump Auto Start</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2016, at 1740 CDT, the Prairie Island Nuclear Generating Plant (PINGP) 2RY Transformer locked out. During the event, 121 Motor Driven Cooling Water Pump (MDCLP) stopped due to the loss of power and then automatically restarted when sequenced by the load sequencer. The pump auto started on low pressure in the cooling water pump discharge header. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system.<br /><br /> The cause of the 121 MDCLP auto-start was a low-pressure condition in the cooling water pump discharge header resulting from 2RY Transformer lockout. There was no safety injection signal from PINGP Unit 1 nor Unit 2 when 121 MDCLP started. The health and safety of the public was not at risk. The most likely cause of 2RY Transformer lockout is that the breathers on 2RY Transformer dog house were not adequately maintained. Breathers were not adequately maintained due to design limitations that did not allow proper internal inspection.<br /><br /> Immediate actions taken, 2RY Transformer dog house dried out and internal components were tested to validate the functionality of the equipment. Results were satisfactory. Corrective actions, 2RY Transformer Dog house breathers and outdoor bus breather were replaced per work order prior to returning the transformer to service. Also, the Preventative Maintenance (PM) procedure was updated to perform the full internal inspection during the future PM's (bus duct or transformer).
2822016006 | Prairie Island 1, Prairie Island 2 | 12/18/2016 | 02/15/2017 | ML17046A65 | <strong>121 Motor Driven Cooling Water Pump Auto Start</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2016, at 0818 CDT, the Prairie Island Nuclear Generating Plant (PINGP) had a fire in the PINGP Switch Yard due to 8H8 Breaker-CT (Current Transformer) catastrophic failure. During the event, 121 Motor Driven Cooling Water Pump (MDCLP) auto-started on low header pressure (80 psi) as designed, and supplied load to the Cooling Water (CL) Header to increase header pressure. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system. <br /><br /> The cause of the 121 MDCLP auto-start was a low-pressure transient in the cooling water pump discharge header that was caused by the trip of the Containment & Auxiliary Building Chiller. When the chiller tripped, Unit 2 Containment Fan Coil units automatically swapped to cooling water. This additional load on the CL system, which caused system pressure to drop below 80 psi. The health and safety of the public was not at risk.
2852016001 | Fort Calhoun | 02/10/2016 | 04/08/2016 | ML16099A27 | <strong>Technical Specification Violation due to Installation of an Unqualified Part in a Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2016 Fort Calhoun Station became aware of a part 10 CFR 21.21 notification from Canberra Industries, Inc. for purchase orders related to Radiation Monitoring (RM) equipment. An investigation identified Time Delay Relay (PO 185167) had been installed in RM-052 Containment and Auxiliary Building Stack Gaseous Swing Radiation Monitor since July 23, 2013. During the period since installation conditions existed such that the maximum number of Technical Specification required radiation monitors allowed out of service was exceeded for periods in excess of the Limiting Condition of Operation. <br /><br /> On 03/19/16 the Time Delay Relay was replaced with a qualified part (WO 578335) and all necessary surveillance testing completed satisfactorily restoring RM-052 to an operable condition.
2852016002 | Fort Calhoun | 05/10/2016 | 10/21/2016 | ML16295A23 | <strong>Unanalyzed Condition Shutdown Heat Exchanger Isolations</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2016, at 1138 Central Daylight Time (CDT), during scheduled maintenance, an unanalyzed condition was discovered as a result of maintenance on Shutdown Cooling Heat Exchanger valves. This condition could have led to the inability of the Component Cooling Water (CCW) system to perform its design function of providing a cooling medium for the Containment atmosphere under Loss Of Coolant Accident (LOCA) conditions. <br /><br /> As part of the maintenance, HCV-484, Shutdown Heat Exchanger AC-4A CCW Outlet Valve, and HCV-481, Shutdown Cooling Heat Exchanger AC-4B CCW Inlet Valve, were open. Under these conditions, with the assumed single failure loss of DC control power and accident condition of a LOCA, CCW would be allowed to flow through both shutdown cooling heat exchangers, bypassing a portion of the flow to the Containment Cooling Units. These conditions are not assumed under plant design basis calculations, and therefore placed the plant in an unanalyzed condition. Both HCV-484 and HCV-481 were returned to service and the condition no longer exists.
2852016003 | Fort Calhoun | 06/22/2016 | 08/22/2016 | ML16235A50 | <strong>Unplanned Turbine Trip During DCS Modification due to Failure to Identify and Disable the Transmitter Deviation Based Trip</strong><br /><i>Abstract:&nbsp;</i>An automatic turbine trip occurred resulting in an automatic Reactor Protective System (RPS) actuation from mode 1 at 100% power due to loss of turbine load at 0841 Central Daylight Time on June 22, 2016. System actuation and responses were as designed. There were no Safety Systems inoperable that contributed to this event. The trip occurred during Post Modification Testing activities on the turbine Emergency Trip System (ETS) pressure loop trip. Engineering failed to identify and disable the transmitter deviation based trip. The differences between the substituted input values selected for testing and the output of the signal selector block were sufficient to trigger the two transmitters-in-deviation trip for the ETS loop.
2862016001 | Indian Point 3 | 11/03/2016 | 01/26/2017 | ML17047A46 | <strong>Safety System Functional Failure due to an Inoperable Containment Caused by a Flaw on the 31 Fan Cooler Unit Service Water Return Coil Line Affecting Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2016, as a result of a containment sump pump alarm, operations obtained from Chemistry a sample which indicated a Service Water (SW) leak due to abnormal chlorides levels. Technical Specification (TS) 3.6.1 (Containment) was entered and containment declared inoperable. Inspections identified a through wall leak on the 31 SW Fan Cooler Unit (FCU) from FCU coil 3 which feeds a SW return line header. TS 3.6.6 (Containment Spay and Fan Cooler System) was entered when the 31 FCU was secured and SW to the 31 FCU was isolated. TS 3.6.1, Condition A was exited after the 31 FCU was secured and SW was isolated to the 31 FCU. The leak is at a 3 inch butt-welded joint that is ISI Class 3, nuclear safety related. Leak rate estimate was 0.16 gpm. The direct cause was a leak in a SW pipe due to a through-wall flaw as a result of corrosion. The root cause is indeterminate. The specific cause for the pipe joint defect requires the component to be removed and a metallurgical failure analysis performed. Corrective actions included installation of a leak limiting clamp. The clamp is being monitored daily and UT monitoring will be performed every 90 days until the pipe is repaired. The pipe will be replaced in the next refueling outage in 2017. The affected pipe will be analyzed after removal. The event had no effect on public health and safety.
2872016001 | Oconee 3 | 06/28/2016 | 08/26/2016 | ML16250A00 | <strong>Unit 3 Reactor Building Cooling Unit Inoperability Exceeds Technical Specification Completion Time</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2016, the 3C Reactor Building Cooling Unit (RBCU) was discovered to be running in reverse when operating in the low speed mode and Technical Specification (TS) 3.6.5, Condition B, was entered (only low speed is applicable to TS operability). The RBCU was restored to operable on June 29, 2016. It was determined that the inoperability was caused by a wiring error (rolled leads) that occurred during the preceding outage. This provides firm evidence that the RBCU was inoperable from the time Mode 2 was entered (May 15, 2016) until RBCU operability was restored on June 29, 2016. This duration exceeds the 7.5 day cumulative Completion Time allowed by TS 3.6.5. During start-up from the outage, the plant entered Modes 2 and 1 with the RBCU inoperable, which is prohibited by TS 3.0.4. These conditions constitute plant operation prohibited by Technical Specifications and are reportable as an LER per 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The cause was determined to be personnel error by the technicians' improper application of the configuration control process. The technicians received remedial training and a procedure change was initiated to enhance configuration control aspects in the maintenance procedure. <br /><br /> The safety function associated with TS 3.6.5 was available during the inoperability of the 3C RBCU.
2932016001 | Pilgrim | 04/12/2016 | 06/09/2016 | ML16168A03 | <strong>Both Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2016 at 0050 hours, with the reactor at 100% power and the mode switch in RUN, Pilgrim Nuclear Power Station (PNPS) entered an unplanned 24-hour Limiting Condition for Operation (LCO) Action Statement per Technical Specification 3.5.F.1 due to both emergency diesel generators (EDG) being inoperable. With EDG B out of service for a planned LCO maintenance window, EDG A was declared inoperable due to identification of an approximate leak of 130 drops per minute (dpm) from the line to the jacket water pressure indication.<br /><br /> The apparent cause of the EDG A jacket water pressure boundary leak was stress corrosion cracking (SCC) that eventually led to failure of a bulkhead pipe fitting. The apparent cause was confirmed by the failure analysis performed. Corrective action was taken to replace the leaking bulkhead pipe fitting on EDG A to restore EDG Operability. An additional corrective action is planned to replace the opposite train EDG jacket water bulkhead pipe fitting. <br /><br /> There was no impact to public health and safety.
2932016002 | Pilgrim | 04/19/2016 | 08/18/2016 | ML16250A01 | <strong>Online Maintenance Test Configuration Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2016, at approximately 1450 hours, it was discovered that a maintenance activity performed between 2010 hours on August 26, 2014 and 0143 hours on August 27, 2014, had rendered the Startup Transformer (X4) and the standby Emergency Diesel Generators (EDG) (X-107A&B) unable to automatically supply power to Buses A5 and A6, due to the breaker interlock that would prevent Startup Transformer breakers (152-504 and 152-604) and standby EDG breakers (152-509 and 152-609) from closing, when Bus A8 to Bus A5 breaker (152-501) and Bus A8 to Bus A6 breaker (52-601) are in the TEST position and CLOSED. During the maintenance activity, the plant was operating at 100 percent power and the Unit Auxiliary Transformer (X3) was providing power to Emergency Buses A5/A6. <br /><br /> The functional testing of negative sequence relays (146-600/A and B) and 23kV feed undervoltage relays (127-600A/1 and 2, and 127-600B/1 and 2) created a test configuration, lasting less than 1-hour, whereby power to Buses A5 and A6 was not automatically available from either the startup transformer or from the EDGs. As a result, Limiting Conditions for Operation (LCO) Action Statement 3.9.6.2 was not met. <br /><br /> The root cause is that the decision to perform the described surveillance testing online, instead of during cold shutdown, lacked sufficient rigor to ensure compliance with Technical Specifications. Corrective actions will establish and institutionalize expectations and accountability for station leadership regarding consequence-biased decision-making and effective risk management. There was no impact to public health and safety.
2932016003 | Pilgrim | 05/12/2016 | 11/17/2016 | ML16333A00 | <strong>Spent Fuel Storage Design Feature Exceeded</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2016, at 16:47 EDT, an assessment of Boron Areal Density Gauge for Evaluating Racks (BADGER) testing results for spent fuel storage racks revealed a single panel, RR35 South with a gap in neutron absorber material that exceeds spent fuel storage design feature assumptions. The assumptions ensure compliance with Technical Specification (TS) Section 4.3.1.1.b to maintain a spent fuel pool K-effective (Keff) of less than or equal to (< or =) 0.95. An extent of condition review indicates additional at-risk rack locations that may further challenge compliance with TS 4.3.1.1.b.<br /><br /> The cause of the noncompliance with TS 4.3.1.1.b is Boraflex degradation greater than assumed in the criticality safety analysis. Interim actions include declaring the spent fuel pool rack cells adjacent to the panel RR35 South inoperable, installing blade guides into cells adjacent to panel RR35S, and prohibiting fuel movement in Boraflex racks. An additional corrective action was taken to perform a criticality evaluation of the spent fuel pool (SPF). <br /><br /> This LER supplement is issued to identify that an additional criticality evaluation has been performed to conservatively identify fuel storage configurations within the Boraflex fuel storage racks that will ensure the Boraflex racks Keff will be able to be maintained < or = 0.95. Fuel movement will be required to establish these configurations.
2932016004 | Pilgrim | 05/10/2016 | 07/11/2016 | ML16202A05 | <strong>Salt Service Water Pump B Past Operability - Operation or Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2016 with the reactor at 100% power and the mode switch in RUN, a condition report was written to evaluate past operability of the Salt Service Water (SSW) Pump P-208B power supply breaker overload relay based on thermography results obtained on October 25, 2013. A similar high temperature condition was identified during the February 29, 2016 thermography surveillance that resulted in declaring the pump inoperable on March 4, 2016 and completing the replacement of the overload relay on March 5, 2016. SSW Pump P-208B is currently operable.<br /><br /> The past operability review covers the period of time between the 2013 thermography surveillance and March 5, 2016 when the pump breaker overload relay was replaced. Based on the lack of detailed information in the 2013 surveillance, past operability of the pump could not be assured. A review of out-of-service time for SSW Pumps P208A and P208C indicates that one instance occurred where less than two SSW pumps were Operable to feed the SSW A Loop Header for a period in excess of SSW Technical Specification requirements. This represents a reportable condition. <br /><br /> The cause of the overload relay high temperature readings was evaluated and determined to be a high resistance connection on the overload relay heater assembly. Inadequate predictive maintenance monitoring was identified as the apparent cause for not periodically assessing breaker status or replacing the breaker overload relay prior to March 5, 2016. Testing the overload relay that was removed from service is planned. This testing is expected to be completed by August 15, 2016. Results will be reported in a supplement to this report. <br /><br /> There was no impact to public health and safety.
2932016005 | Pilgrim | 08/15/2016 | 10/13/2016 | ML16298A38 | <strong>Ultimate Heat Sink and Salt Service Water System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2016 at 1552 EDT, with the reactor at about 70 percent core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) declared the ultimate heat sink (UHS) and salt service water (SSW) system inoperable due to high sea water inlet temperatures greater than 75 degrees Fahrenheit (F). PNPS had already taken action, in accordance with plant procedures, to reduce power from 100 percent in an effort to keep from exceeding the Technical Specification (TS) Limit. PNPS entered a 24-hour shutdown Limiting Condition for Operation Action Statement (LCO-AS) for Salt Service Water (SSW) inlet temperature exceeding the TS limit in TS 3.5.6.4. The LCO-AS was subsequently exited at 1651 hours when the temperature of SSW trended to below the TS limit. <br /><br /> Under certain design conditions, the SSW system is required to provide cooling water to various heat exchangers such as the Reactor Building Closed Cooling Water (RBCCW) and Turbine Building Closed Cooling Water (TBCCW) systems. When the inlet temperature to these supplied loads exceeds the 75 degree F limit established in the TS, the SSW system is conservatively declared inoperable until the temperature trends below this value. This condition existed for 59 minutes reaching a maximum of 75.1 degrees F. The cause of the sea water inlet temperature exceeding the 75 degree F TS criterion was sustained increased sea water surface temperature in Cape Cod Bay due to summer weather conditions and recirculation of water from the plant's discharge due to wind and tidal conditions. <br /><br /> There was no impact to public health and safety from this condition.
2932016006 | Pilgrim | 08/16/2016 | 10/13/2016 | ML16298A39 | <strong>"C" Main Steam Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 8/16/2016, during performance of Main Steam Isolation Valve (MSIV) stroke time testing, with the plant operating at approximately 60% power, "C" inboard MSIV closure time was 7.4 seconds, exceeding the maximum closure time of 5 seconds referenced in Final Safety Analysis Report (FSAR) Table 5.2-4. The MSIV was declared inoperable. In accordance with the plant Technical Specifications (TS) the "C" outboard MSIV was closed and isolated. A team was formed to perform troubleshooting and determine corrective actions. With one main steam line inoperable the plant was limited to less than 75% power. On 8/21/16 the plant was shut down and entered a forced outage to repair the "C" inboard MSIV. The air pack was replaced and post maintenance tests were satisfactorily performed to restore the valve to Operable status. <br /><br /> On 8/30/16 Pilgrim Nuclear Power Station conservatively concluded that, based on the historical issues with the "C" inboard MSIV, the valve had been inoperable since stroke time testing was performed on May 24, 2016. <br /><br /> There was no impact to public health and safety from this condition.
2932016007 | Pilgrim | 09/06/2016 | 11/04/2016 | ML16320A00 | <strong>Manual Reactor Scram due to Feedwater Regulating Valve Malfunction</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2016 at 0827 EDT, with the reactor at approximately 91 percent core thermal power, operators manually scrammed the reactor when the benchmark for a reactor water level of +42 inches increasing was reached. Following the scram, all rods fully inserted and the Average Power Range Monitors were downscale, indicating the reactor was shut down. The Main Steam Isolation Valves closed on a Primary Containment Isolation Signal Group 1 isolation and were subsequently reopened to maintain reactor pressure.<br /><br /> The reason for the increasing reactor water level was the malfunction of Feedwater Regulating Valve 'A' (FRV 'A'). The reactor operator at the control panel placed FRV 'A' in remote manual in an attempt to stabilize the feedwater flow oscillations. This had no effect on the performance of FRV 'A'. The operators experienced feedwater flow oscillations from FRV 'A' that resulted in reactor water level high and low level alarms on the control panel. Shortly after this, the benchmark reactor water level of +42 inches increasing was reached and operators manually scrammed the reactor. <br /><br /> There was no impact to public health and safety.
2932016008 | Pilgrim | 09/28/2016 | 12/09/2016 | ML17010A03 | <strong>Emergency Diesel Generator 'A' Past Inoperability</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2016, while performing the pre-start checks prior to running the Emergency Diesel Generator (EDG)-A for the monthly Technical Specification (TS) surveillance, the oil level in the EDG radiator fan right angle gearbox was found to be low and additional checks found the gearbox oil pressure relief valve in a loose state which provided a pathway for gear oil to be pumped out of the gear box while the EDG was operating. EDG-A was declared inoperable, the relief valve was repaired, pressure tested and the pressure adjusting threaded union was staked to eliminate any risk from vibration induced motion in the future, the gearbox oil was replaced and the EDG run for a post-maintenance test.<br /><br /> A Functional Failure Determination completed on October 11, 2016 determined that the EDG would not have been able to run for its stated mission time of 30 days. This condition existed for a period of 28 days since the last surveillance test on August 31, 2016 which is greater than the TS Allowed Out of Service Time (AOT) of 72 hours. However, the Station Black Out Diesel Generator was available during this time frame. This issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition which was Prohibited by the plant's TSs. <br /><br /> On September 15, 2016 EDG-B was made inoperable to perform its monthly operability run. This created a situation where for a brief period of time both EDGs were inoperable which is a condition that could have prevented the fulfillment of the safety function of a system needed to shut down the reactor and maintain it in a safe condition, remove residual heat, and mitigate the consequences of an accident which is reportable in accordance with 50.73(a)(2)(v)(A), 50.73(a)(2)(v)(B), and 50.73(a)(2)(v)(D). EDG-B remained available and could quickly have been restored by manual action to an operable condition if needed during the operability run. <br /><br /> There was no impact to public health and safety from this condition.
2932016009 | Pilgrim | 11/07/2016 | 01/06/2017 | ML17017A20 | <strong>HPCI Declared Inoperable due to Failure of IST Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2016, at 1609 [EST], with the reactor at 100 percent core thermal power and steady state conditions, the High Pressure Coolant Injection (HPCI) system was declared inoperable. Pilgrim Nuclear Power Station was performing planned quarterly testing per Technical Specifications 4.13.A.1. During a review of the HPCI pump data taken during the test, it was determined that the recorded vibration reading on the main pump outboard horizontal point (P4H) was 0.8335 in/sec which exceeds the IST required action range high limit of less than or equal to 0.830 in/sec. Accordingly, the HPCI pump was declared inoperable.<br /><br /> The Limiting Condition for Operation Action Statement 3.5.C.2 was entered and planned troubleshooting into the cause of the high vibration was started. This event is reportable under 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. <br /><br /> There was no impact to public health and safety from this condition.
2932016010 | Pilgrim | 04/15/2017 | 06/14/2017 | ML17174A67 | <strong>MSIV Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2016, at 1500 [EST], with the reactor at approximately 22 percent power, the Main Steam Isolation Valves (MSIVs) 2C and 2D were discovered to have steam leaks while performing a steam tunnel walkdown. MSIV 2D, which had a body to bonnet steam leak, was declared inoperable and Technical Specifications (TS) Limiting Condition for Operation Action Statement (LCOAS) 3.7.A.2.b was entered at 1530 on December 15, 2016. Outboard MSIV 2D and inboard MSIV 1D both were closed and deactivated to isolate Main Steam Line D. On December 16, 2016, at 1524 [EST] Operations entered TS LCOAS 3.7.A.2.b for a packing steam leak on outboard MSIV 2C. Actions were also taken to close and deactivate the inboard MSIV 1C, which included a controlled plant shutdown to reduce reactor pressure below the MSIV closure scram bypass setpoint. <br /><br /> On April 15, 2017, during Refueling Outage 21(RFO 21), MSIV 1D failed it's Local Leak Rate Test (LLRT). In addition, the MSIV 1C also failed its LLRT. As a result it was concluded that MSIV 1D and MSIV 1C exceeded their leakage criteria during RFO 21. Therefore, Pilgrim Nuclear Power Station is making this submittal to provide the NRC with additional information regarding the condition of the plant's MSIV's. <br /><br /> There was no impact to public health and safety from this condition.
2962016001 | Browns Ferry 3 | 01/19/2016 | 03/21/2016 | ML16078A13 | <strong>Inoperable Residual Heat Removal Pump Results in Condition Prohibited by Technical Specifications and Safety System Functional Failure</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2016, at approximately 1100 Central Standard Time (CST), during troubleshooting of the Main Control Room (MCR) green light indication on the 3A Residual Heat Removal (RHR) Pump Motor Breaker Transfer Switch (MBTS), it was discovered that the 3A RHR Pump MBTS had malfunctioned, potentially preventing the pump from starting from the MCR. The 3A RHR Pump was declared inoperable. On January 20, 2016, at approximately 0030 CST, the 3A RHR Pump was declared operable following replacement of the 3A RHR Pump MBTS.<br /><br /> A Past Operability Evaluation concluded that the 3A RHR Pump was inoperable from January 9 to January 20, 2016, exceeding the Technical Specification allowed outage time. During this time, the 3B and 3D RHR Pumps were also inoperable on January 14, 2016, from 0127 to 0215 CST, resulting in a Safety System Function Failure. A Probabilistic Risk Assessment determined there was a negligible increase in risk. <br /><br /> The cause of this event was failure of the transfer switch to fully latch due to binding resulting from the MBTS being installed greater than its twenty-one year service life with no Preventative Maintenance (PM) performed. Corrective actions include verifying similar transfer switches are latched in the NORMAL position on BFN, Units 1, 2, and 3, and creating a PM activity with a replacement schedule for these switches.
2962016002 | Browns Ferry 3 | 02/22/2016 | 07/28/2016 | ML16211A05 | <strong>Improperly Installed Switch Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2016, during routine maintenance of the Browns Ferry Nuclear, Unit 3 Core Spray (CS) system, relays on the 3ED 4kV Shutdown Board were found de-energized. This resulted in loss of the automatic start function of the 3B and 3D CS Pumps, the 3D Residual Heat Removal (RHR) pump, and the D1 Residual Heat Removal Service Water (RHRSW) pump, with normal power to the 3ED 4kV Shutdown Board. Troubleshooting determined the relay was de-energized due to a failure of the 6-6C contacts on the MJ(52STA) switch associated with the 3ED 4kV Shutdown Board, and a binding of the 52STA Cam Linkage. This was caused by a misalignment of the switch to linkage interface, due to improper installation. The switch was subsequently replaced. Alignment verification instructions will be added to switch replacement procedures. <br /><br /> The duration of inoperability the 3B and 3D CS pumps, 3D RHR pump, and D1 RHRSW pump, was determined to be from the last successful actuation of the switch on October 28, 2015, until February 20, 2016, when Unit 3 was placed in Mode 4. Manual start of these pumps remained available. Automatic start capability of the other Unit 3 CS, RHR, and RHRSW pumps was unaffected by this condition, and the required safety functions of the impacted systems continued to be met.
2962016003 | Browns Ferry 3 | 02/23/2016 | 04/25/2016 | ML16116A37 | <strong>Main Steam Isolation Valve Leaking in Excess of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2016, at approximately 0405 Central Standard Time, during performance of Primary Containment Local Leak Rate Testing (LLRT) of the Main Steam lines, the 3B Outboard Main Steam Isolation Valve (MSIV) failed its as-found LLRT. Because the MSIV failed to meet the leak rate limit, Browns Ferry Nuclear Plant, Unit 3, operated longer than allowed by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.3. In addition, TS LCO 3.0.4 was not met for each applicable Mode change since the last recorded as-found MSIV leak rate test on March 16, 2014, when the leak rates were below the leak rate limit. <br /><br /> The cause of the event was wear on the seating surface of the pilot poppet seat. Corrective action included replacing the valve stem containing a new pilot poppet, resurfacing the seat and restoration of the valve actuator. <br /><br /> The safety significance of this condition was minimal since the 3B Inboard MSIV was available to perform the safety function.
2962016004 | Browns Ferry 3 | 04/06/2016 | 06/06/2016 | ML16158A13 | <strong>Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2016, the Tennessee Valley Authority was presented with as-found testing results indicating that three of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear, Unit 3, exceeded the +/- 3 percent setpoint required for their operability. Troubleshooting determined that the MSRV discs failed by corrosion bonding to their valve seats. The valve discs were previously platinum coated to prevent this, but the valve seat's rough Stellite surface caused the coating to flake off.<br /><br /> It was determined that the MSRVs were inoperable from March 19, 2014 to February 20, 2016. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, or activation through the Automatic Depressurization System or MSRV Automatic Actuation Logics was not affected. The valves remained capable of performing their required safety function.<br /><br /> Corrective Actions were to replace all Unit 3 MSRVs, to analyze the pilot valves of the inoperable MSRVs, and to revise procedures to verify the pilot disc finish meets its requirements prior to valve assembly.
2962016005 | Browns Ferry 3 | 04/18/2016 | 06/17/2016 | ML16169A06 | <strong>Automatic Depressurization System Valve Inoperability Exceeded Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2016, during a scheduled surveillance, the power to the Main Steam Line (MSL) B Relief Valve failed to transfer to its alternate feeder breaker when the normal feeder breaker was opened. The Automatic Depressurization System (ADS) function of the MSL B Relief Valve was declared inoperable. It was determined that the ADS valve was inoperable from March 26, 2016 to April 19, 2016. The valve's ability to open under normal power was not affected. Five of the six ADS valves remained operable. Only four ADS valves are required to meet the ADS function in the Loss of Coolant Analysis described in the Final Safety Accident Report. <br /><br /> The unavailability of the ADS alternate power source was directly caused by a bus stab on the back of the Molded Case Circuit (MCC) breaker not fully engaging with the bus. This was apparently caused by improper performance of previous post-maintenance testing. The stab was adjusted, the MCC breaker was returned to service, and the MSL B Relief Valve's ADS function was declared operable upon verification of its alternate power supply. <br /><br /> Corrective actions were to determine which load-feeding MCC breakers have a normal and alternate power source, and revise their preventative maintenance procedures to verify that post-maintenance testing includes power source isolation prior to closing the breaker under load. Breaker bus stabs will be replaced.
2962016006 | Browns Ferry 3 | 06/08/2016 | 08/05/2016 | ML16218A47 | <strong>High Pressure Coolant Injection System Found to be Inoperable During Testing</strong><br /><i>Abstract:&nbsp;</i>During a surveillance test on June 8, 2016, the BFN, Unit 3, High Pressure Coolant Injection (HPCI) Turbine Stop Valve Mechanical Trip Valve behaved erratically upon turbine start. Troubleshooting and maintenance on the valve led to discovery of a condition that could have resulted in the HPCI system being unable to perform its required safety function in a Mode where HPCI Operability was required. <br /><br /> The inoperability was caused by the HPCI Turbine Stop Valve Mechanical Trip Valve's Reset Spring, which was deformed and weakened from years of continuous compression. The spring was replaced and the system was returned to service on June 10, 2016. <br /><br /> Corrective actions to prevent recurrence include revising preventive maintenance procedures to specify replacement of the Trip Tappet, Piston, and Reset Spring on a defined periodicity. Additionally, procedures will be revised to require testing the as-left breakaway force a minimum of three times to ensure repeatability. Preventative maintenance procedures will also be revised to clarify that lift force checks after spring compression adjustments shall be conducted with the auxiliary oil pump running.
2982016001 | Cooper Station | 04/25/2016 | 12/15/2017 | ML17354A14 | <strong>De-Energized High Pressure Coolant Injection Auxiliary Lube Oil Pump Caused by Relay Failure Results in Loss of Safety Function, a Condition Prohibited by Technical Specifications, and a 10 CFR Part 21 Report</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2016, while performing a walkdown of Control Room panels, it was noticed that the green indication light for High Pressure Coolant Injection (HPCI) auxiliary lube oil pump (ALOP) was not illuminated. A non-licensed operator was dispatched to the HPCI ALOP starter and reported that the local indication lights were not illuminated. HPCI was declared inoperable at 2117 Central Daylight Time (CDT) resulting in entry into Technical Specifications (TS) Limiting Condition of Operation 3.5.1, Condition C, HPCI System Inoperable. <br /><br /> Investigation determined that the coil in the electrical relay for the ALOP, which had recently been replaced during a preventive maintenance window, had failed after 133 hours of service. The cause of the failure was determined to be the prior pre-installation checks performed by NuTherm on the relay were inadequate to prevent the type of infant mortality failure that occurred in this case. HPCI was declared operable at 1314 CDT on April 26, 2016, after the coil was replaced. <br /><br /> This event is being reported as a loss of safety function due to HPCI being a single-train safety system, as a condition prohibited by TS and in accordance with 10 CFR Part 21.<br /><br /> The potential safety consequences of this event were minimal due to both the limited duration the condition existed and the redundant/diverse core cooling systems which remained operable.
2982016002 | Cooper Station | 04/26/2016 | 06/27/2016 | ML16190A11 | <strong>De-Energized High Pressure Coolant Injection Auxiliary Lube Oil Pump Caused by Light Bulb Failure Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2016, it was noted that the green off light for High Pressure Coolant Injection (HPCI) auxiliary lube oil pump (ALOP) in the Control Room, was not illuminated. A non-licensed operator was dispatched to the HPCI ALOP starter and reported the green bulb appeared to have shattered in the socket. HPCI was declared inoperable at 1754 Central Daylight Time (CDT) resulting in entry into Technical Specifications Limiting Condition of Operation 3.5.1, Condition C, HPCI System Inoperable.<br /><br /> Investigation found the 125 volts direct current fuse open circuited and the local indication green light and socket were damaged. The cause of the failure was determined to be a lack of engineering knowledge which led to a design change in 1984 in the HPCI ALOP starter circuitry that diminished the robustness of the circuit with respect to a specific failure modality; direct short circuiting within the indication bulb itself. The HPCI system was restored to operable status on April 28, 2016, at 1245 CDT. <br /><br /> This event is being reported as a loss of safety function due to HPCI being a single-train safety system. The potential safety consequences of this event were minimal due to the limited duration the condition existed and the redundant/diverse core cooling systems which remained operable.
2982016003 | Cooper Station | 09/14/2016 | 11/09/2016 | ML16326A26 | <strong>Scaffold Construction Places Plant in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2016, during testing of the Reactor Recirculation Motor Generator Ventilation Air Operated Isolation Valves (AOV), HV-AOV-265 failed to close as required by Technical Specifications. Operations declared HV-AOV-265 inoperable and entered Limiting Condition for Operation (LCO) 3.6.4.2, Condition A, and commenced preparations to transition the plant to single loop operation, including reducing the plant to approximately 50 percent power. Upon investigation, it was discovered that the air supply line to the valve was pinched between the valve actuator and a scaffold that was erected to support work on a nearby component. After modifying the scaffold and replacing the pinched airline, the valve was tested satisfactorily and Operations exited the LCO and activities to prepare for transition to single loop operation were terminated. <br /><br /> The root cause of the event is that personnel involved in the planning, construction, and inspection of the scaffold built for a nearby component were not aware of the unique external movement path of the valve actuator. To prevent recurrence, the procedure will be revised to include specific guidance for the planning, building and inspection of scaffolds in the vicinity of HV-AOV-265 and other AOVs having actuators of similar design. Signage has been installed to warn personnel of the external movement of these AOVs.
2982016004 | Cooper Station | 09/25/2016 | 11/22/2016 | ML16342C57 | <strong>Closure of Multiple Main Steam Isolation Valves due to High Flow Signal</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2016, at 20:40 hours, during reactor cooldown for Refueling Outage 29, Cooper Nuclear Station control room operators closed the inboard Main Steam Isolation Valves (MSIV) to minimize steam flow to control the reactor cooldown rate. Reactor pressure was controlled using the Main Steam Line Drains; and the condensate/feed system was available for reactor water level control. <br /><br /> On September 25, 2016, at 01:03 hours, while equalizing pressure across the MSIVs to below 200 psid, a differential pressure of 190 psid was established. Upon opening MS-AO-80A, a Group 1 isolation was immediately received due to a Main Steam Line high flow signal. The control room operators subsequently equalized pressure and successfully opened MS-AO-80A, as well as the remaining MSIVs, at 18:52 hours.<br /><br /> The cause of the event was insufficient procedure guidance exists regarding limitations on opening the MSIVs. To correct this, the applicable procedure has been revised to change the differential pressure limitations for opening MSIVs from 200 psid to 80 psid. <br /><br /> The safety significance of the event is low and did not pose a threat to the health and safety of the public.
2982016005 | Cooper Station | 10/01/2016 | 11/22/2016 | ML16350A10 | <strong>Implementation of Enforcement Guidance Memorandum 11-003, Revision 3, Causes Conditions Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage 29 (RE-29), Cooper Nuclear Station implemented the guidance of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3, "Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements During Operations with a Potential for Draining the Reactor Vessel," dated January 15, 2016. Consistent with EGM 11-003, Revision 3, secondary containment operability was not maintained during Operations with a Potential for Draining the Reactor Vessel activities, and Required Action C.2 of Technical Specification (TS) 3.6.4.1 was not completed. <br /><br /> EGM 11-003, Revision 3, was implemented four times during RE-29. These conditions are being reported as conditions prohibited by TS.<br /><br /> Implementation of EGM 11-003, Revision 3, during RE-29 was a planned activity. As such, there were no root cause evaluations of the events. Consistent with the guidance provided in EGM 11-003, Revision 3, Nebraska Public Power District will submit a license amendment request to adopt a Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue within 12 months after issuance of the Notice of Availability of the TSTF traveler.
2982016006 | Cooper Station | 10/23/2016 | 12/19/2016 | ML16365A00 | <strong>High Vibration on Control Room Emergency Filter System Fan Results in Inoperability and Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2016, while conducting refueling and Operations with a Potential for Draining the Reactor Vessel activities, Control Room Emergency Filter System (CREFS) Supply Fan A (SF-C-1A) experienced high vibration. A vibration analysis was performed and results indicated that vibration readings were elevated across all points for the motor and fan. Consequently, Operations declared CREFS inoperable at 19:08 hours. At 19:53 hours, SF-C-1B was started, CREFS was transferred to the alternate supply, and SF-C-1A was secured. At 23:41, Event Notification 52315 was made to the Nuclear Regulatory Commission Operations Center. <br /><br /> The fan was repaired on October 24 and 25, 2016, and a vibration analysis was performed on October 26, 2016, with satisfactory results. Operations declared CREFS operable at 1341 on October 27, 2016. <br /><br /> The root cause was the preventive maintenance strategy for the fan was ineffective to ensure shaft to bearing engagement is maintained. To prevent recurrence, the applicable maintenance plan will be revised to include verification that the bearings are adequately engaged to the fan shaft. <br /><br /> This is a Safety System Functional Failure.
2982016007 | Cooper Station | 10/28/2016 | 12/19/2016 | ML16365A00 | <strong>Isolation of Shutdown Cooling due to Relay Maintenance Results in a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2016, during replacement of relay PCIS-REL-K27 at Cooper Nuclear Station (CNS), the action of installing a new relay onto the shared plastic DIN rail disturbed the mounting rail in a manner that caused contacts of the adjacent relay, PCIS-REL-K30, to open. This caused Shutdown Cooling (SDC) isolation valve RHR-MO-17 to close, which actuated the logic to trip the running 'A' Residual Heat Removal (RHR) pump. <br /><br /> Operations declared 'A' RHR SDC subsystem inoperable at 09:24 hours and entered Limiting Condition for Operation (LCO) 3.9.7, Condition A, and Condition C. Alternate Decay Heat Removal remained in service throughout the event. Event Notification 52327 was made to the Nuclear Regulatory Commission Operations Center. <br /><br /> While SDC was out of service, PCIS-REL-K27 work was completed. SDC was declared operable at 05:30 hours on October 29, 2016, and was placed in service at 18:30 hours, and the LCO was exited. <br /><br /> The root cause of the event is that CNS did not identify the risk from mechanical agitation during Primary Containment Isolation System (PCIS) relay installation; therefore, the risk was not adequately evaluated or mitigated. To prevent recurrence, CNS will revise Procedure 0.50.5 to list the relays or other devices which could impact SDC when in service.<br /><br /> This is a Safety System Functional Failure.
2982016008 | Cooper Station | 11/08/2016 | 01/05/2017 | ML17025A07 | <strong>Purchase and Installation of Incorrect Actuator Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2016 at 11:27 hours, Cooper Nuclear Station (CNS) declared Reactor Core Isolation Cooling (RCIC) inoperable for surveillance testing and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.3, Condition A. Subsequently at 11:41 hours, RCIC was declared inoperable due to a water leak from the lube oiler cooler lower flange. <br /><br /> During investigation it was determined that valve RCIC-AOV-PCV23, which was replaced during Refueling Outage 29, was full open causing excessive cooling water pressure to the lube oil cooler. This valve regulates cooling water to the lube oil cooler. Initial examination revealed that the actuator was purchased with a closed travel stop instead of the required open travel stop. The work order was revised to fabricate and install an open travel stop. On November 10, 2016, following valve modification, RCIC passed surveillance testing, was declared operable, and TS LCO 3.5.3, Condition A, exited. <br /><br /> The root cause evaluation determined that the correct air operated valve was not purchased because the material master purchase order text and associated drawing didn't detail the requirement of an open travel stop. <br /><br /> To prevent recurrence, CNS will revise the material master purchase order text to state that the valve includes a travel stop in the open direction to limit valve travel. In addition, the drawing will be modified to show the correct travel stop with a note emphasizing the design function of the travel stop.
2982016009 | Cooper Station | 12/07/2016 | 02/02/2017 | ML17047A46 | <strong>Control Room Emergency Filter System Fan Removed from Service due to Human Error Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2016, the Control Room Emergency Filtration System (CREFS) was inadvertently removed from service during the conduct of a scheduled surveillance activity performed by a Control Room Operator. Consequently, Operations declared CREFS inoperable at 22.40 hours. Investigation revealed that the running CREFS supply fan had been turned off in error during the conduct of a surveillance procedure. Upon discovery of this, Operations returned the supply fan to service and declared CREFS operable at 22:47 hours. Event Notification 52416 was made to the Nuclear Regulatory Commission Operations Center. <br /><br /> The root cause was attributed to human error. <br /><br /> To prevent recurrence, applicable operations procedures will be revised to require peer checking during normal operations for all Control Room manipulations directed by these procedures. <br /><br /> This is a Safety System Functional Failure.
2982016010 | Cooper Station | 07/11/2016 | 02/15/2017 | ML17054C82 | <strong>Inadequate Compensatory Measures Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>From July 11, 2016, to July 15, 2016, the Torus area and Reactor Building floor drain valve control switches were placed in the OPEN position, per alarm card FP-1/C-4, due to fire detector FP-TD-19-2 being impaired. Subsequently, it was determined that by placing the floor drain valve control switches to OPEN, the automatic flood protection function that is credited in Cooper Nuclear Station's internal flooding analysis, was defeated. During the time the detector was impaired, there were no credited compensatory actions taken to ensure Division 1 Core Spray (CS) and Division 1 Residual Heat Removal (RHR) systems were protected from postulated flooding caused by a high-energy line break. As such, it was determined that both Division 1 CS and Division 1 RHR were inoperable for a period greater than allowed by Technical Specifications. <br /><br /> The cause was determined to be that when the flooding requirements in the Reactor Building changed, a review of alarm cards did not identify alarm card FP-1/C-4 as needing updated. <br /><br /> Alarm card FP-1/C-4 was revised to remove taking radwaste valves out of AUTO for each quad. In addition, the applicable procedure has been revised to ensure actions taken will ensure operability is maintained for environmentally qualified components in each of the Reactor Building quads; and a review of fire panel alarm cards will be performed for similar occurrences where monitoring is the only action taken.
3062016001 | Prairie Island 2 | 12/17/2015 | 02/12/2016 | ML16043A39 | <strong>Unit 2 Reactor Trip due to a Ground Fault Resulting in a Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On 12/17/2015 at 1234 Central Standard Time (CST) with Unit 2 (U2) in Mode 1 at 100 percent power, the U2 electric generator tripped due to a ground overvoltage protection relay (59/2G) actuation, which resulted in an automatic reactor trip and expected Auxiliary Feedwater System actuation. At 1307 CST a fire alarm was received in the U2 containment. Personnel were unable to verify the status within 15 minutes and the site declared an Unusual Event, HU2.1, at 1318 CST. The licensee notified the NRC Resident Inspector, state and local authorities and made an Event Notification to the NRC for the Unusual Event and the U2 reactor trip as required under 10 CFR 50.72(a)(1)(i) and 10 CFR 50.72(b)(2)(iv)(B). Subsequently, the Unusual Event was terminated on 12/17/2015 at 1450 CST after a containment entry determined there was no smoke or fire. The original Event Notification was updated to cancel the Unusual Event and to add reporting under 10 CFR 50.72(b)(3)(iv)(A) for the expected Auxiliary Feedwater system actuation. Decay heat removal was via forced circulation with Auxiliary Feed and Steam Dumps providing secondary cooling. Offsite power remained available. The health and safety of the public was not at risk.<br /><br /> A troubleshooting plan was initiated which determined an actual ground fault existed internal to the new U2 electric generator, installed during the Fall 2015 U2 refueling outage, causing a U2 reactor trip and the expected Auxiliary Feedwater actuation. The cause of the ground fault of the U2 electric generator was determined to be foreign material, specifically a hex socket and hex key introduced at the vendor's manufacturing facility during installation of a temporary dust cover on collector end of the generator rotor.
3112016001 | Salem 2 | 04/20/2015 | 03/21/2016 | ML16081A36 | <strong>AFW Loop Response Time Exceeded Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2016, while reviewing outage data, plant staff recognized that anomalous data collected in October 2015, for the 21 Auxiliary Feed Pump time response loop resulted in failure to meet a surveillance, rendering that channel of Auxiliary Feedwater automatic actuation inoperable. In November 2015, the isolation valve for the pressure override defeat pressure transmitter was found closed. The pressure transmitter provides an input into the 21 AFW Pump run-out protection circuit. With the isolation valve closed, it would take longer to sense pump discharge head and consequently the opening of the auxiliary feed pump flow control valves would be slower than normal. This condition resulted in 21 Auxiliary Feedwater Pump loop time response greater than Technical Specification (TS) acceptance criteria. The failed channel was not recognized and the TS action was not taken, resulting in a condition prohibited by TS. The investigation revealed that the condition most likely existed since April 20, 2015, when maintenance activities were performed on the auxiliary feedwater pump discharge pressure transmitter. The isolation valve was opened and the surveillance was performed satisfactorily. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications."
3112016002 | Salem 2, Salem 1 | 02/04/2016 | 09/07/2017 | ML17250A15 | <strong>Automatic Reactor Trip due to Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On 2/4/16 at 11:21, Salem Unit 2 automatically tripped from approximately 74% power. Power had been reduced at the beginning of dayshift to support a 500 KV transmission line outage. The reactor trip was due to a Main Turbine trip caused by a Main Generator Protection signal initiated by a main generator automatic voltage regulator (AVR) volts/hertz over excitation protection relay. All emergency core cooling systems and emergency safeguards feature systems functioned as expected. As found calibration data for the generator protection logic relay were found out of specification low. An evaluation determined the cause of the event to be that the organization failed to develop and implement corrective actions to resolve the previously identified cause of poor manufacturing/vendor quality identified in the causal evaluation following a similar Unit 1 trip on 12/21/2012 trip due to STV-1 relay setpoint drift. <br /><br /> This report is being made in accordance with 10 CFR 50.73 (a)(2)(iv)(A.), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," specifically automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System for this event.
3112016003 | Salem 2 | 02/14/2016 | 04/14/2016 | ML16105A26 | <strong>Automatic Reactor Trip due to Main Generator Protection Trip</strong><br /><i>Abstract:&nbsp;</i>On 2/14/16 at 20:58 Salem Unit 2 automatically tripped from 100% power on Generator Protection. The trip was initiated due to a Main Turbine trip caused by a Main Generator Protection signal. All emergency core cooling systems and emergency safeguards feature systems functioned as expected. The motor driven and steam driven auxiliary feed pumps started as expected on steam generator low level. Operators stabilized the plant in Mode 3 with decay heat removal via the main steam dump valves and auxiliary feed water system. Condenser vacuum remained available for the duration of the event. Operators also ensured a normal offsite electrical power lineup. Investigation identified a Stator Water Cooling valve leak dripping onto a relay, shorting the relay wiring terminations. This caused the turbine generator trip. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System and the Auxiliary Feedwater System.
3112016004 | Salem 2 | 02/14/2016 | 04/18/2016 | ML16109A09 | <strong>Auxiliary Feedwater Pump Auto Start</strong><br /><i>Abstract:&nbsp;</i>On 2/16/16 at 0827 22 Steam Generator Feed Pump (SGFP) tripped while operators were transferring the steam supply to the pump from heating steam to main steam. Trip of 22 SGFP initiated emergency safeguard feature (ESF) actuation for start of the 21 and 22 Auxiliary Feedwater (AFW) Pumps. This event occurred during Unit 2 start-up following a unit trip from generator protection. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Auxiliary Feedwater System. Notification of this event was provided via ENS report 51738.
3112016005 | Salem 2 | 06/28/2016 | 08/29/2016 | ML16244A05 | <strong>Automatic Reactor Trip due to Main Generator Protection Trip</strong><br /><i>Abstract:&nbsp;</i>On 6/28/16 at 04:22 Salem Unit 2 automatically tripped from 100% power on Generator Protection. The reactor trip was initiated due to a Main Turbine (MT) trip caused by a Main Generator Protection signal. All emergency core cooling systems and emergency safeguards feature systems functioned as expected. The motor driven and steam driven auxiliary feedwater pumps started as expected on steam generator low level. Operators stabilized the plant in Mode 3 with decay heat removal via the main steam dump valves and auxiliary feedwater system. <br /><br /> Investigation identified that a broken current transformer core ground wire internal to the A Main Power Transformer (MPT) was intermittently touching the X1 and X2 low voltage connections inside the transformer bushing compartment causing a ground fault. This caused the turbine generator trip. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System (RPS) and the Auxiliary Feedwater System (AF).
3112016006 | Salem 2 | 08/31/2016 | 10/31/2016 | ML16305A38 | <strong>Automatic Reactor Trip due to Trip of the 21 Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 hours on August 31, 2016, the 21 Reactor Coolant Pump (RCP) tripped resulting in an automatic reactor trip on low flow in one reactor coolant loop above the P-8 permissive (36% power permissive). As expected, the 21, 22 and 23 Auxiliary Feedwater (AFW) pumps started on low steam generator level following the unit trip. Unit 2 was stabilized in Mode 3 at normal operating temperature and pressure with the 22, 23 and 24 RCPs in-service. <br /><br /> The trip of the 21 RCP was caused by a Service Water (SW) leak that developed on the 22 Containment Fan Coil Unit (CFCU) motor cooler. The SW leaked on to the 21 RCP motor lead containment penetration and the motor leads in the termination box. This caused the A and C phase instantaneous overload relays to actuate causing the trip of the RCP and the subsequent reactor trip on low flow in one reactor coolant loop.<br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System (RPS) and the Auxiliary Feedwater System (AF).
3132016001 | Arkansas 1, Arkansas 2 | 03/19/2016 | 05/18/2016 | ML16139A79 | <strong>Non-Functional External Penetration Flood Seals</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2016, two block-out penetrations separating the Arkansas Nuclear One, Unit 1 (ANO-1) Turbine Building from the Auxiliary Building were determined to be non-functional. The penetrations are located in the floor of Turbine Building elevation 354 ft. Below the penetrations is the Auxiliary Building, housing safety related equipment. <br /><br /> On March 17, 2016, it was identified that two penetration seals did not match approved fire penetration or approved flood seal details. Further investigation, completed on March 19, 2016, revealed that the two block-out penetrations were not grouted and represented a previously unknown vulnerability in a credited external flood barrier. <br /><br /> The apparent cause of this event was less than adequate project management control for the size and scope of the External Flood Mitigation Project associated with post Fukushima Dai-ichi resolutions and requirements set forth by the NRC. <br /><br /> Mitigating strategies and extent of condition reviews have been implemented for the identified conditions. Permanent repair of the deficient flood barriers is complete minus cure time. Actions to correct programmatic aspects of this condition are in progress.
3132016002 | Arkansas 1 | 06/13/2016 | 08/11/2016 | ML16224A76 | <strong>Tornado Missile Vulnerability Resulting in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2016 during evaluation of protection of required equipment from the damaging effects of tornados, Arkansas Nuclear One (ANO) identified non-conforming conditions where certain required equipment on Unit 1 was not adequately protected from tornado missiles. This is a legacy design construction issue. <br /><br /> On June 13, 2016 at 1609 central time, Operations declared the affected equipment inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance", along with the required compensatory measures and declared the affected equipment operable but non-conforming thereafter. <br /><br /> The cause of this issue was a lack of clarity and changing requirements during the original licensing of the plant that led to inadequate understanding of the original regulatory guidance. <br /><br /> Corrective actions include implementation of compensatory strategies and extent of condition reviews for the identified conditions.
3132016003 | Arkansas 1 | 08/24/2016 | 06/09/2017 | ML17163A27 | <strong>Tornado Missile Vulnerabilities Resulting in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On August 24, September 11, September 15, 2016, and April 17, 2017, during performance of an extent of condition evaluation related to the protection of Technical Specification (TS) equipment from external flood hazards, Arkansas Nuclear One, Unit 1 (ANO-1), identified non-conforming plant design conditions such that specific ANO-1 TS equipment was considered to not be adequately protected from tornado missiles. These are legacy design issues. <br /><br /> On August 24, 2016 at 0945, September 11, 2016 at 1504, September 15, 2016 at 0958, and April 17, 2017 at 1319, Operations declared the affected components inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, “Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,” along with necessary compensatory measures, and subsequently declared the affected equipment operable but non-conforming. <br /><br /> The cause of this event was unclear and changing regulatory requirements during original plant licensing that led to an inadequate understanding of the regulatory guidance with respect to tornado missile protection design requirements. <br /><br /> Interim corrective actions include implementation of compensatory strategies. Plant modifications and license basis changes are being evaluated to resolve outstanding issues.
3132016004 | Arkansas 1 | 09/30/2016 | 11/29/2016 | ML16334A41 | <strong>Decay Heat Removal System Socket Weld Leak due to a Vibration-Induced Fatigue Crack</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2016, at Arkansas Nuclear One, Unit 1 (ANO-1), during refueling outage 1R26 with both trains of Decay Heat Removal (DHR) in service, a 0.125 gpm leak was identified in the DHR system at a one-inch drain line. This leak was on a section of cross-connect piping shared by both trains of the DHR system. The consequence of the leak was that both trains of the DHR system were declared inoperable. <br /><br /> The leakage was due to a fatigue crack caused by vibration of the drain line due to a pipe support that was not designed for system vibration. <br /><br /> Other systems and components in ANO-1 and ANO, Unit 2 (ANO-2) exposed to elevated system vibration were evaluated with respect to this condition. As a result of this evaluation, socket welds on other drains and vents in the ANO-1 DHR system were cut out and replaced, and pipe supports were modified where needed to withstand system vibration.
3152016002 | Cook 1 | 07/15/2016 | 09/09/2016 | ML16256A78 | <strong>Rod Position Indication Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2016, with the Donald C. Cook Nuclear Plant Unit 1 Reactor operating in Mode 1 at 100 percent power, while performing the Unit 1 Full Length Control Rod Operability Surveillance Test, acceptance criteria for Control Bank 'D' was not met. When given an insertion demand of eight steps, Control Rod K14 only indicated inserting one step. All other Rods responded as expected. A further evaluation determined that failure was caused by the apparent saturation of the Analog Rod Position Indication (NARPI) signal conditioning module for Rod K14. The performance of a Temperature Compensation adjustment on the K14 NARPI module on April 30, 2016, saturated the NARPI module and prevented it from responding to rod motion demand. Thus, the K14 NARPI module was inoperable from the moment it was saturated on April 30, 2016, at 2232 until it was replaced and restored to operable status on July 15, 2016, at 1740. <br /><br /> Therefore, the NARPI module for Control Rod K14 was inoperable for a period greater than allowed by Technical Specification 3.1.7, and is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any Operation or Condition Prohibited by Technical Specifications.
3162016001 | Cook 2 | 07/06/2016 | 10/04/2016 | ML16281A48 | <strong>Manual Reactor Trip due to Moisture Separator Heater Expansion Joint Failure</strong><br /><i>Abstract:&nbsp;</i>On July 6, 2016, with the Donald C. Cook Nuclear Plant Unit 2 Reactor operating in Mode 1 at 100 percent power, the control room received a report of a steam leak on the Unit 2 B Right Moisture Separator Reheater (MSR) crossover piping and damage to the turbine building structure. This information resulted in a decision by the crew to manually trip the Unit 2 Reactor at 0038. The cause of the steam leak was the sudden failure of the balance bellows on the Unit 2 B Right MSR crossover expansion joint, which also resulted in damage to the west wall of the turbine building. <br /><br /> The Root Cause was determined to be an organizational failure to recognize the risk significance of, and to adequately correct or mitigate, previously identified vibration issues with the Unit 2 B Right MSR crossover expansion joint tie rod and bellows in a timely fashion. <br /><br /> This event is being reported in accordance with 10CFR 50.73(a)(2)(iv)(A) as a manual actuation of the Reactor Protection System and an automatic actuation of the Auxiliary Feedwater system.
3162016002 | Cook 2 | 12/13/2016 | 02/09/2017 | ML17045A00 | <strong>Emergency Diesel Generators Declared Inoperable due to a Manufacturing Design Issue</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2016, the Unit 1 AB Emergency Diesel Generator (EDG) developed a fuel oil leak from a fuel injector pump Delivery Valve Holder (DVH) during a maintenance run of the diesel. On December 21, 2016, with Unit 1 in Mode 1 at 100 percent power and Unit 2 in Mode 4 during a refueling outage, it was determined that the failed DVH on the Unit 1 AB EDG was due to a design and manufacturing issue. Subsequently the Unit 1 CD EDG, Unit 2 AB EDG, and Unit 2 CD EDG were conservatively declared inoperable due to multiple affected diesel fuel pump DVHs being installed on each EDG.<br /><br /> The Root Cause was determined to be due to insufficient Corrective Action Program oversight by Engineering to ensure product quality and issue resolution in relation to a previous EDG DVH failure in 2013. Testing is being conducted to determine the resulting impact to associated EDGs. The affected DVHs have been replaced.<br /><br /> A Loss of Safety Function was reported via Event Notification 52456 for Unit 2 in accordance with 10 CFR 50.72(b)(3)(v)(D). The Loss of Safety Function is required to be reported in a Licensee Event Report in accordance with "50.73(a)(2)(v)(D) Event or Condition that Could Have Prevented Fulfillment of a Safety Function."
3172016001 | Calvert Cliffs 1 | 01/25/2016 | 03/21/2016 | ML16083A36 | <strong>Manual Reactor Trip due to High Secondary Side Sodium Levels due to a Condenser Tube Leak</strong><br /><i>Abstract:&nbsp;</i>At 0313 on January 25, 2016, Operators initiated a manual reactor trip on Unit 1 due to high levels of sodium in the Feedwater and Condensate systems that exceeded the threshold levels in Abnormal Operating Procedure 10, Abnormal Secondary Chemistry Conditions. Subsequent investigation determined the high sodium levels were due to a condenser tube leak located in 13A Condenser. The failed condenser tube and several adjacent tubes were plugged and Unit 1 was returned to power operation at 2220 on January 25, 2016. During the 2016 Unit 1 refueling outage eddy current testing confirmed a circumferential crack on the failed condenser tube. The apparent cause is that the condenser tube failure was vibration induced. Radial stakes were installed to help limit future vibration. A causal analysis will be completed following the Unit 1 refueling outage.
3172016002 | Calvert Cliffs 1 | 02/20/2016 | 04/14/2016 | ML16106A30 | <strong>Pressurizer Safety Relief Nozzle Dissimilar Metal Weld Flaw Exceeded American Society of Mechanical Engineers Code Allowable Limit</strong><br /><i>Abstract:&nbsp;</i>On February 20, 2016, during Calvert Cliffs Inservice Inspections of Unit 1 dissimilar metal welds, an evaluation of recorded ultrasonic examination (UT) data identified the presence of one axially oriented flaw in a 4 inch Unit 1 pressurizer [PZR] safety relief nozzle [NZL] to safe end weld. The indicated flaw exhibited characteristics indicative of primary water stress corrosion cracking (PWSCC). The flaw was inner diameter connected and measured 81.6 percent through-wall. This measured axial flaw depth did not meet the American Society of Mechanical Engineers (ASME) Code allowable limit. The UT of this weld done in 2006 and 2010 had determined the axial flaw depth was only approximately 8 percent through-wall. After re-analysis of the prior UT data, the root cause was determined to be limitations in sizing data collection and analysis techniques prior to 2016 that were unable to connect the detected inner . diameter indication to the full through-wall extent of ultrasonic signal response of the flaw. The weld was repaired using a full structural weld overlay repair method using PWSCC resistant material deposited around the circumference of the weld area. Two other Unit 1 welds that had previously shown potential PWSCC were examined with the new techniques and showed no change in their indication characteristics and remain within ASME Code allowable limits.
3172016003 | Calvert Cliffs 1 | 05/31/2016 | 07/29/2016 | ML16216A14 | <strong>Unit 1 Automatic Trip on Loss of Load due to Spurious Steam Generator High Level Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2016 at 1626, Calvert Cliffs Unit 1 experienced an automatic reactor trip. The cause of the trip was a spurious high level steam generator signal due to a failed Steam Generator 11 Channel B High Level Turbine Trip Under Voltage Logic Module, 12/4BL-XA27. The spurious high level trip signal resulted in a turbine trip followed by an automatic reactor protection system trip on loss of load. The failed under voltage logic module was sent off-site to the vendor to conduct a failure analysis. The analysis identified two most probable causes for the failure. The first most probable cause was due to an intermittent failure of an integrated circuit of the under voltage logic module. The second most probable cause was due to an inadvertent solder bridge between a pin on the integrated circuit chip and the board. A refurbished logic module was installed and subsequently tested prior to the unit returning to power. The corrective action planned to prevent recurrence is to replace the current Engineered Safety Features Actuation System (which includes the non-safety high level turbine trip) with a system that will eliminate single point vulnerabilities within this system.
3172016004 | Calvert Cliffs 1 | 11/13/2015 | 07/20/2016 | ML16204A37 | <strong>High Energy Line Break Barrier Breeched due to Human Performance Error Causing Both Service Water Trains to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>The Unit 1 Service Water (SRW) Room high energy line break (HELB) door was opened on 10/19/2015 and 10/21/2015 to conduct a maintenance activity. The door was opened twice for approximately three and a half minutes each time. With the HELB door blocked open, the affected equipment located behind the barrier door should have been considered inoperable. Affected equipment included the 13 motor driven auxiliary feedwater pump, both trains of saltwater air compressors and both trains of SRW. Since both SRW trains were inoperable, a loss of safety function occurred, an unanalyzed condition existed and a common cause failure of independent trains existed for the time that the HELB door was opened. The HELB door was blocked opened because Maintenance Planners did not include the proper barrier controls in the work order that opened the HELB door, because they were unaware of the barrier control procedure requirements. The apparent cause of the event was that the assigned change management agent (an Engineer) failed to inform Maintenance Planners of the implementation of the barrier procedure. Affected groups were briefed about the barrier control procedure. Corrective action for the human performance issue was handled through the performance management system.
3182016001 | Calvert Cliffs 2 | 12/03/2016 | 01/24/2017 | ML17026A37 | <strong>Automatic Reactor Trip due to Main Turbine Electro-Hydraulic Control Fluid Leak</strong><br /><i>Abstract:&nbsp;</i>On December 3, 2016, Operations was conducting a Performance Evaluation of the auto start feature of Unit 2 Main Turbine Electro-Hydraulic Control (EHC) Pumps. At 2223, the standby EHC pump started per the procedure and a normal rise in pressure was noted. At 2224, Unit 2 Main Turbine tripped automatically which was followed by an automatic reactor protection system trip. The Main Turbine tripped on a Main Generator Directional Power Relay trip following the closure of all Unit 2 Main Turbine Governor Valves and Intercept Valves. This was due to an EHC leak on 21 Main Turbine Governor Valve Actuator Emergency Trip Fluid Check Valve which caused a rapid decrease in EHC header pressure. The trip was an uncomplicated reactor trip as all safety functions performed as expected. The failed emergency trip fluid check valve was sent off site to a lab for forensic investigation. This analysis determined the check valve failed due to Inter Granular Stress Corrosion Cracking (IGSCC). The most likely cause of the IGSCC on this check valve was exposure to ammonia during some previous maintenance activity. Corrective actions include replacement of all similar Unit 2 EHC valves during the 2017 refueling outage and establishment of a preventive maintenance strategy to periodically replace similar EHC valves. Unit 2 was returned to full power at 1647 on December 5, 2016.
3212016001 | Hatch 1 | 02/11/2016 | 04/08/2016 | ML16099A34 | <strong>Performance of Fuel Movement with Inoperable Rod Position Indication System in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 02/11/16, Unit 1 fuel movement activities were restarted after repairs to the main grapple camera. A refueling interlock of the main grapple was encountered while moving a double blade guide, caused by the disconnection of 20 Rod Position Information System (RPIS) Position Indicating Probes (PIPs). The operating crew began troubleshooting and determined that bypassing the RPIS probe "full-in" would clear the interlock. However the crew used a section of the site specific procedure for control rod withdrawal during refuel that wasn't applicable at the time. <br /><br /> The RPIS indications were bypassed and the movement of the double blade guide was recommenced at 12:00 followed by fuel movement. After a review of Technical Specifications 3.9.4, it was determined that fuel movement should not be performed with the RPIS probe disconnected and bypassed because the associated control rods were not disarmed with a tagout. Fuel movement activities were then halted.
3212016002 | Hatch 1 | 02/13/2016 | 04/11/2016 | ML16103A13 | <strong>Performance of Operations With the Potential to Drain the Reactor Vessel (OPDRV) Without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On February 13 through 15, 2016, February 15 through 16, 2016, and February 17 through 18, 2016 operations with the potential to drain the reactor vessel (OPDRV) activities were performed while Unit 1 remained in Refueling Mode (Mode 5) without an operable secondary containment. These activities are prohibited by Technical Specifications (TS) 3.6.4.1. However, recent NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 and in Regulatory Issue Summary (RIS) 2012-11 allowed the implementation of interim actions as an alternative to full compliance. These actions are compiled in the operating procedure for the OPDRV activities performed during the 2016 Hatch Unit 1 Refueling Outage in February. <br /><br /> The performance of OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A licensee amendment request (LAR) will be submitted following NRC approval of the Technical Specification Task Force (TSTF) Traveler associated with generic resolution of this issue (TSTF-542).
3212016003 | Hatch 1 | 02/16/2016 | 04/14/2016 | ML16105A21 | <strong>Reactor Coolant System Piping Has Unacceptable Weld Indication Discovered During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>During the 2016 Unit 1 R27 refueling outage, plans were put in place to upgrade the 1631-1RC-12BR-E-5 (1631-E5) design weld overlay (WOL) to a full structural weld overlay (FSWOL) in order to allow for code qualified examinations. On February 16, 2016 at 0631 EST, during surface preparation work, axial indications were found on the WOL. Evaluation of the indications found in the weld overlay suggests that the non-satisfactory PT examination was a result of the propagation of the original flaw that was found on the 1E Recirculation Loop Piping. The original indication had propagated into the Inconel Alloy 82 WOL material installed in 1988. It was determined that the as-found condition of the flaw did not meet ASME Section XI acceptance criteria. The indications were removed from the WOL and 1B31-E5 was upgraded to a full structural weld overlay using intergranular stress corrosion cracking (IGCSS) resistant Alloy 52 weld material.
3212016004 | Hatch 1 | 03/30/2016 | 05/26/2016 | ML16147A34 | <strong>Safety Relief Valves As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2016, Unit 1 was at 100 percent rated thermal power (RTP) when "as-found" testing results of the 3-stage main steam safety relief valves (SRVs) indicated two of the eleven Unit 1 SRVs had experienced a setpoint drift during the previous operating cycle which resulted in their failure to meet the Technical Specification (TS) opening setpoint pressure of 1150 +/- 34.5 psig as required by TS Surveillance Requirement (SR) 3.4.3.1. The test results showed that two SRVs were slightly out of spec low due to setpoint drift. <br /><br /> The SRV pilots were disassembled and inspected while investigating the reason for the drift. SNC has determined that the abutment gap closed pre-maturely. The pre-mature abutment gap closure is most likely due to loose manufacturing tolerances leading to SRV setpoint drift.
3232016001 | Diablo Canyon 2 | 05/30/2016 | 07/28/2016 | ML16210A52 | <strong>Reactor Trip Breakers Manually Opened During Shutdown due to a Control Rod Movable Gripper Fuse Failure</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2016, at 0930 PDT, with Unit 2 in Mode 4, "Hot Shutdown," licensed operators responding to a difference greater than 12 steps between digital rod position indication (DRPI) and demand position indication in the control room, manually opened the Reactor Trip Breakers in accordance with plant procedures. The plant operators stabilized the plant and technicians identified a failure of a control rod moveable gripper fuse. At 1611 PDT, plant operators made an 8-hour, nonemergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A). Plant technicians replaced the fuse and plant operators confirmed proper operation by performance of surveillance testing. <br /><br /> The cause was attributed to Surveillance Test Procedure (STP) R-1C, "Digital Rod Position Indicator Functional Test," which did not explicitly specify actions to identify improper DRPI indications prior to exceeding a 12-step difference between rod demand and rod position indication. <br /><br /> Corrective actions to prevent recurrence include revision of STP R-1C to include guidance regarding verification of rod motion prior to exceeding 12 steps and operator training of the changes to the procedure. <br /><br /> This event did not adversely affect the health and safety of the public.
3242016001 | Brunswick 2 | 06/15/2016 | 08/08/2016 | ML16231A01 | <strong>Mispositioned Valves Result in Residual Heat Removal Service Water System lnoperability</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2016, at 05:15 Eastern Daylight Time, Unit 2 was in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. At that time, Operations personnel were preparing to run the Residual Heat Removal Service Water (RHRSW) system in the suppression pool cooling mode. While performing the valve lineup, an alarm was received on low RHRSW suction pressure. Two instrument valves connected to the "B" and "D" RHRSW pump suctions were found closed. This resulted in the pump start logic being unable to sense RHRSW pump suction pressure, which prevented the pumps from being able to start. With the pumps unable to start, the associated RHRSW division was inoperable. It is most likely that the valves were mispositioned during a previous operation of the "B" RHRSW division. The event resulted from procedures which did not adequately control the position of the instrument valves. Corrective actions for this event included repositioning the valves to their correct configuration and revising applicable procedures.
3242016002 | Brunswick 2 | 07/05/2016 | 08/29/2016 | ML16242A19 | <strong>High Pressure Coolant Injection System Inoperable due to Failed Relay Coil</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2016, at 1640 Eastern Daylight Time (EDT), the Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable due to apparent failure of the HPCI Auxiliary Oil Pump. The HPCI Auxiliary Oil Pump provides hydraulic pressure required to open the HPCI Turbine Stop Valve and the HPCI Turbine Control Valve during initial HPCI startup. Failure of the HPCI Auxiliary Oil Pump prevents the HPCI system from performing its safety function. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. <br /><br /> The HPCI system inoperability was due to loss of control power for the Auxiliary Oil Pump. The loss of control power was caused by a failed motor overload alarm relay coil; which caused current flow in excess of the control power fuse rating. The HPCI system was restored on July 6, 2016, at 1050 EDT. The alarm relay coil failure was age related. The corrective actions include creation of preventive maintenance tasks to replace the Unit 1 and 2 HPCI motor overload alarm relay coils on an appropriate frequency.
3252016001 | Brunswick 1 | 02/07/2016 | 04/06/2016 | ML16104A39 | <strong>Electrical Bus Fault Results in Lockout of Startup Auxiliary Transformer and Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2016, at 1312 Eastern Standard Time (EST), Unit 1 was in Mode 1 (i.e., Run) at 88 percent of rated power in end-of-cycle coastdown. At that time, an electrical fault occurred on a balance of plant 4160-volt bus, resulting in a lockout of the Startup Auxiliary Transformer (SAT) and a loss of both Reactor Recirculation pumps. Licensed personnel inserted a manual scram per procedure. Emergency Diesel Generators supplied emergency electrical busses until offsite power was restored at 1628 EST. The loss of power and reactor water level changes resulted in automatic closures of various Primary Containment Isolation Valves (PCIVs). The electrical fault resulted in an electrical explosion; therefore, an Alert was declared at 1326 EDT. The immediate cause of this event was a fault in a non-segregated electrical bus connected to the SAT. The root causes were insufficient detail in applicable maintenance instructions for inspecting the non-segregated bus housing and inadequate instructions for terminating electrical cables in a circuit breaker cubicle. Corrective actions include repairing equipment damaged by the electrical fault and revising the procedures and work instructions.
3252016002 | Brunswick 1, Brunswick 2 | 03/04/2016 | 08/08/2016 | ML16230A23 | <strong>Emergency Diesel Generator 3 Inoperable due to Failure to Auto-Start</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2016, at 1235 Eastern Standard Time (EST), Emergency Diesel Generator (EDG) 3 was declared inoperable. At this time, EDG 1, Emergency bus E1, and balance of plant (BOP) bus 1D were inoperable due to planned maintenance. Two inoperable EDGs represents a loss of safety function, for the onsite standby power source. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. In addition, it was determined that EDG 3 was inoperable for greater than Technical Specifications (TSs) Completion Times. Therefore, this condition is also being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the TSs. Additionally, on March 3, work was ongoing to restore power to BOP bus 1D when an error in the restoration sequence resulted in an invalid auto-start of EDGs 2 and 4. Because the invalid auto-starts of EDGs 2 and 4 are directly related to the events associated with this LER, it is being reported, herein, per 10 CFR 50.73(a)(2)(iv)(A) rather than the optional 60-day telephone notification. <br /><br /> The root cause of the EDG 3 inoperability is a design vulnerability associated with relaxation of the EDG 3 fuse holder fingers which was not properly mitigated. The corrective action to prevent recurrence will be to implement a design change to address the vulnerability.
3252016003 | Brunswick 1 | 03/09/2016 | 05/02/2016 | ML16132A07 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2016, Unit 1 implemented the guidance of EGM 11-003, Revision 3, "Enforcement Guidance Memorandum 11-003, Revision 3, Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements during Operations with a Potential for Draining the Reactor Vessel," dated January, 15, 2016. Consistent with EGM 11-003, Revision 3, secondary containment operability was not maintained during Operations with a Potential for Draining the Reactor Vessel (OPDRV) activities, and Required Actions C.1 and C.2 of Technical Specification (TS) 3.6.4.1, "Secondary Containment," were not completed. EGM 11-003, Revision 3, was implemented four additional times during the 2016, Unit 1 refueling outage. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by the plant's TSs.<br /><br /> Implementation of EGM 11-003, Revision 3, during the Unit 1 refueling outage was a planned activity. As such, there was no root cause evaluation of the event. Consistent with the guidance provided in EGM 11-003, Revision 3, BSEP will submit a license amendment request to adopt a Technical Specification Task Force (TSTF) traveler associated with generic resolution of this issue within 12 months after the issuance of the Notice of Availability of the TSTF traveler.
3252016004 | Brunswick 1, Brunswick 2 | 07/21/2016 | 09/06/2016 | ML16271A18 | <strong>Tornado Missile Vulnerability Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2016, Units 1 and 2 were in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. At that time, Engineering personnel determined that a conduit in the Emergency Diesel Generator building was vulnerable to a tornado missile. The conduit contains cables associated with Unit 2 Nuclear Service Water (NSW) pump "B". If the cables were disabled by a tornado missile, NSW pump 2B would be inoperable. The plants' Technical Specifications (TS) require three of the site's four NSW pumps to be operable. Thus, any of the other NSW pumps removed from service for longer than the TS-allowed out of service time would be a condition prohibited by the TS. It has been found that this condition occurred. Enforcement Guidance Memorandum (EGM) 15-002 was implemented, and NSW pump 2B was considered operable but nonconforming. The tornado missile vulnerability has existed since original plant construction. Immediate compensatory measures included verifying that station procedures address tornadoes, high winds, and potential loss of vulnerable equipment, and confirming or receiving training on procedures to be used if a tornado watch or warning is issued. Planned corrective actions include implementing more comprehensive compensatory actions and permanently eliminating the vulnerability to a tornado missile.
3252016005 | Brunswick 1, Brunswick 2 | 10/03/2016 | 12/05/2016 | ML16349A61 | <strong>Drywell High Range Radiation Monitors Inoperable due to Thermally Induced Current Phenomenon</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2016, Units 1 and 2 were in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. At that time, Engineering personnel were reviewing the plant response to NRC Information Notice 97-45, Supplement 1, on signal cables for the Drywell High Range Radiation Monitors (DWHRRMs). These cables are susceptible to thermally induced current (TIC), which can degrade the accuracy of DWHRRMs. The review resulted in DWHRRMs being declared inoperable on both units. The DWHRRMs were included in Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.3.1 beginning in 1984. As a result of the TIC effect on the DWHRRM cables, BSEP Unit 1 and Unit 2 have operated longer than the TS allowed completion times for inoperable DWHRRMs. This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant TSs. The event resulted from the inherent characteristics of the cables and DWHRRMs. An existing site procedure directs the use of alternate indications for assessment of drywell or fuel cladding conditions, and this procedure will remain in place as a compensatory action. Corrective actions will include replacing the cables on a schedule to be developed after assessment of available options.
3252016006 | Brunswick 1, Brunswick 2 | 12/13/2016 | 05/03/2017 | ML17123A29 | <strong>Control Room Air Conditioning Units Inoperable due to Corroded Supports</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2016, Units 1 and 2 were in Mode 1 (i.e., Run mode) at 98 percent and 97 percent of rated thermal power, respectively. At that time, shift personnel were notified that structural supports for the 2D Control Room air conditioning system condenser were corroded. An operability assessment found the affected air conditioning system inoperable due to the effect on its seismic qualification. Technical Specifications (TS) 3.7.4, Condition A, was entered. On January 30, 2017, the 1D air conditioning system was found with similar conditions. The duration of the condition and the fact that more than one air conditioning system was inoperable simultaneously resulted in the plant operating in a condition prohibited by the TS and in a loss of the safety function. This event resulted from a lack, in some cases, of station personnel being cognizant of risks related to resolving complex, long-standing issues that continue to degrade over time. All affected support steel was replaced by February 2, 2017. The remaining air conditioner was inspected and found acceptable. Administrative actions will be taken to identify high consequence plant issues and periodically reassess priorities.
3272016001 | Sequoyah 1 | 02/09/2016 | 04/11/2016 | ML16104A39 | <strong>Automatic Safety Injection due to Low Steam Line Pressure on Loop 2 Main Steam</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2016, at 1415 Eastern Standard Time, Sequoyah Nuclear Plant (SQN) Unit 1 experienced a Low Steam Line Pressure Safety Injection (SI) signal. At the time of the event, Operations was warming the main steam (MS) line downstream of the main steam isolations valves (MSIV) via the Loop 2 MSIV bypass valve. During this controlled evolution, a sudden drop in MS line pressure occurred that actuated the two-out-of-three logic as sensed on all three Loop 2 steam line pressure bi-stables. All safety systems responded as designed and the SI was terminated per procedure.<br /><br /> Prior to the event, Unit 1 was recovering from a forced outage involving a Main Generator Blower repair that began on December 26, 2016. Unit 1 was maintained in Mode 3 during this time. The most probable cause of the SI actuation was determined to be water accumulation in MS Loop 2 upstream of the MSIV as a result of steam condensation not being drained during the extended Mode 3 forced outage. <br /><br /> Troubleshooting was initiated and Unit 1 was placed in Mode 4 to facilitate draining of Loop 2 and 3 MS lines. Corrective actions include actions to address operating for extended periods of time in Mode 4 and above with MSIVs closed.
3272016003 | Sequoyah 1, Sequoyah 2 | 05/03/2016 | 07/05/2016 | ML16187A05 | <strong>Control Room Door Unable to Close Causes Inoperable Control Room Envelope Boundary</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2016, at 0833 Eastern Daylight Time, Security received an open door alarm regarding a Main Control Room (MCR) door. At 0847, Security notified the MCR staff of the door alarm and that the door was incapable of closure. At this time, both Control Room Emergency Ventilation System (CREVS) trains were declared inoperable in accordance with Technical Specification (TS) 3.7.10, Condition B, due to the inoperability of the Control Room Envelope (CRE). Attempts to close the door were made, and it was identified that a screw had become wedged at the base of the door preventing it from latching. At 0855, the screw was removed and the door verified to close as designed. CREVS was determined to be operable and TS 3.7.10, Condition B was exited. <br /><br /> The screw was the bottom screw from the door latch guard and appears to have stripped loose and fallen into the rubber seal around the base of the MCR door frame preventing closure of the door. Corrective actions include replacing the missing screw on the door latch guard and evaluating existing preventive maintenance instructions associated with CREVS boundary doors to ensure screws are tightened, as needed, on a routine basis.
3272016004 | Sequoyah 1, Sequoyah 2 | 05/16/2016 | 10/03/2016 | ML16281A10 | <strong>Emergency Diesel Generator Fire Dampers and Crankcase Pressure Switches Not Analyzed for Withstanding the Effects of a Tornado</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2016, at 2105 Eastern Daylight Time (EDT), Sequoyah Nuclear Plant (SQN) identified a nonconforming condition involving the Emergency Diesel Generator (EDG) fire dampers installed for Units 1 and 2. Specifically, it has been identified that if a tornado causes a differential pressure across the east and west sides of the EDG Building, the associated ventilation fire dampers have not been analyzed to withstand the corresponding high air flow rate that could result from this condition and could possibly fail in a way that impedes airflow for EDG cooling. On June 8, 2016, at 1526 EDT, SQN determined that a tornado could potentially cause actuation of the EDG crankcase pressure trip due to a low barometric condition that could result in an EDG lockout condition. The EDG lockout condition prevents subsequent EDG starts (normal or emergency) until operators manually reset the lockout condition locally at the EDG. Corrective actions include establishing compensatory measures to block the fire dampers in the open position in the event that a Tornado Watch/Warning is issued for the Hamilton County, Tennessee area. In addition, a compensatory measure has been established, that upon notification of a Tornado Warning, the EDGs will be emergency started and operated during the time the Tornado Warning is in effect to bypass the crankcase pressure trip function and allow the EDGs to perform their required safety function. The apparent cause of these events is misjudgment regarding the intent of the Regulatory Issue Summary 2006-23. The corrective actions developed in response to the RIS were too narrowly focused on ductwork and ventilating dampers withstanding the effects of a tornado.
3272016005 | Sequoyah 1 | 06/07/2016 | 08/17/2016 | ML16230A47 | <strong>Hydrogen Mitigation System Train A Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2016, at 0914 Eastern Daylight Time (EDT), main control room operators were notified by workers, in the field, that a breaker associated with two A train hydrogen ignitors was discovered in the open position. Surveillance Requirement 3.6.8.1 requires greater than or equal to 33 ignitors energized in each train. With the breaker open, there were less than 33 ignitors operable. Technical Specification (TS) 3.6.8, Hydrogen Mitigation System (HMS), Condition A was entered. At 0916 EDT, June 7, 2016, the breaker was closed restoring operability to the two hydrogen ignitors and TS 3.6.8 Condition A was exited. A past operability evaluation, determined that the breaker panel associated with the two ignitors was last accessed on March 11, 2016, as part of the performance of a work order. It is assumed that the breaker became aligned to the open position during this work. Therefore, one train of the HMS was inoperable for longer than allowed by TSs. However, Train B HMS remained operable during this event.<br /><br /> The cause for the breaker being in the open position is indeterminate. Corrective actions include issuing information to Operations and Maintenance personnel regarding the learnings from this event and the need for a questioning attitude while supporting troubleshooting and maintenance activities.
3272016006 | Sequoyah 1 | 06/25/2016 | 09/12/2016 | ML16256A33 | <strong>Improper Calibration of Reactor Trip Instrumentation Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2016, a channel calibration was performed to return the Delta-T/Tavg Channel IV instrument to operable status following digital filter processor card replacement. Instrumentation & Control (I&C) maintenance personnel performed the channel calibration using a digital multi-meter (DMM) that defaulted to a lower impedance setting than the DMM normally used for the calibration. This impacted the set points. As a result, Delta-T/Tavg Channel IV was adjusted incorrectly and returned to service (the Overtemperature delta-T (OTDT) trip function was taken out of the tripped condition) on June 25, 2016, at 0215 Eastern Daylight Time. On June 27, 2016, Reactor Engineering noticed that Tavg had taken a step change lower following the card replacement. On June 29, 2016, operators authorized performance of a functional test for Delta-T/Tavg Channel IV and Unit 1 entered Technical Specification (TS) 3.3.1 Conditions A and E. During the functional test, Delta-T/Tavg was found to be out of TS tolerance. Following adjustment, on June 29 at 2205 operators declared Delta-T/Tavg Channel IV operable. On July 14, a past operability evaluation determined Channel IV of the OTDT trip function was in a noncompliance state longer than allowed by TS. The cause of the event was l&C maintenance personnel were not trained with the operation of the Fluke 8845A DMM. Corrective actions include adding labeling to all Fluke 8845A DMMs to call attention to the impedance function of the device, briefing technicians on operation of the Fluke 8445A DMM, and revising the procedure associated with measuring & test equipment (M&TE) to require a training performance analysis worksheet for all new M&TE.
3272016007 | Sequoyah 1, Sequoyah 2 | 08/02/2016 | 10/03/2016 | ML16277A25 | <strong>Unanalyzed Condition due to Emergency Gas Treatment System Not Meeting Single Failure Criteria</strong><br /><i>Abstract:&nbsp;</i>On August 2, 2016, during review of the Emergency Gas Treatment System (EGTS) circuits, Engineering discovered that the EGTS may automatically swap from the flow control path in A-Auto to the Standby flow control path upon the start of a design basis event (DBE). The intended design of the EGTS swap-over circuit was to detect an actual failure of the control path in A-Auto and swap to the Standby control path. The unnecessary automatic swap to Standby could prevent the EGTS train, configured in A-Auto, from performing its required safety function during a DBE. On August 5, at 1658 eastern daylight time (EDT), the condition was resolved when the automatic swap-over circuit was disabled. On August 17, at 1722 EDT a past operability evaluation determined the configuration of the EGTS flow controllers constituted an unanalyzed condition that significantly degraded plant safety due to the EGTS not meeting single failure criteria. Engineering analysis determined that the failure of both trains of EGTS controllers would not result in exceeding 10 CFR 100 limits. The cause of the event was that the EGTS control circuitry was not designed to account for situations that should have been anticipated. Corrective actions include implementing a permanent modification to disable the EGTS automatic swap-over function.
3272016008 | Sequoyah 1, Sequoyah 2 | 08/10/2016 | 10/07/2016 | ML16281A42 | <strong>Closed Fire Damper Renders Both Trains of the Control Room Emergency Ventilation System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2016, at 1000 Eastern Daylight Time (EDT), the Maintenance Instrument Group (MIG) performed a surveillance instruction (SI) that resulted in a fire protection damper associated with the Control Room Emergency Ventilation System (CREVS) actuating to a closed position. On August 11, at 1015 EDT, the fire damper was discovered in the closed position. The closure of the fire protection damper resulted in both trains of CREVS being inoperable due to the loss of air circulation and habitability of the Technical Support Center and Relay Room. Both units entered Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Conditions A and G. Condition G requires immediate entry into LCO 3.0.3. At 1159 EDT, on August 11, actions were taken to open the fire damper and both trains of CREVS were declared operable. This allowed both units to exit LCO 3.0.3 and LCO 3.7.10, Conditions A and G. <br /><br /> The cause of the event was determined to be inadequate breaker alignment instructions in the SI. Corrective actions include revising the SI to require the associated breaker to be open prior to performance of the SI.
3272016009 | Sequoyah 1 | 12/30/2016 | 05/05/2017 | ML17125A20 | <strong>Manual Reactor Trip During Startup due to a Control Rod Misalignment</strong><br /><i>Abstract:&nbsp;</i>On December 30, 2016, at 1307 Eastern Standard Time (EST), with Unit 1 undergoing a reactor startup, control room operators initiated a manual reactor trip due to a control rod misalignment on control rod, H-6. At the time of the event, the reactor was subcritical. The manual reactor trip was initiated because control rod, H-6, did not respond when rods were being withdrawn. All systems functioned as expected following the trip, with all control rods fully inserting into the core. <br /><br /> The apparent cause was the site did not incorporate Westinghouse operating experience (OE) associated with mechanical binding of a stationary gripper into site procedures. As a result, site procedures did not have a method to ensure the stationary grippers were not bound during initial rod movement. No hardware concerns existed. Unit 1 was returned to service on December 31, 2016, with no anomalies occurring during startup. <br /><br /> Corrective actions include revisions to site procedures to incorporate OE and provide guidance for shutting down the reactor versus a reactor trip. These actions are being tracked in the site's corrective action program. There were no safety consequences as a result of the event.
3312016001 | Duane Arnold | 06/19/2016 | 08/18/2016 | ML16232A60 | <strong>Two Instances of Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2016, while operating at 82% power, two secondary containment access airlock doors were briefly opened simultaneously during a surveillance test. This event was a momentary inoperability of secondary containment integrity, which is an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification made pursuant to 10 CFR 50.72(b)(3)(v)(C). (Reference EN#52022). Following the event, the door· controls were adjusted and verified to function properly. On June 29, 2016, at 100% power, workers opened two doors concurrently when entering a secondary containment access airlock. The individuals promptly closed their respective doors. The event was a brief inoperability of secondary containment integrity as above, notifications were made, and repairs completed. (Reference EN#52053)<br /><br /> The root causes were determined to be inadequate procedural guidance and equipment design not being able to prevent the simultaneous opening of an inner and outer door at all times, under all possible conditions. Corrective actions include modification of the interlock tests, and replacement of key door interlock components. <br /><br /> These events did not result in a safety system functional failure. There were no radiological releases associated with these events.
3312016002 | Duane Arnold | 04/28/2016 | 12/06/2016 | ML16342C56 | <strong>Unplanned RCIC Inoperability Results in Safety System Functional Failure</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2016, at 1055, while operating at 100% power, with no structures, systems, or components inoperable that contributed to this event, during the performance of Surveillance Test Procedure (STP) 3.3.6.1-28, Reactor Core Isolation Cooling (RCIC) System Steam Line Flow - High Channel Functional Test, the RCIC turbine received an unplanned trip signal and subsequent turbine stop valve closure. The cause of the event was a human performance error associated with verifying the correct installation location of the relay block. The turbine trip resulted in the unplanned inoperability of RCIC, therefore, this condition meets the reporting requirements of 10CFR50.73(a)(2)(v)(D). At 1353 on April 28, 2016, the RCIC turbine was reset and RCIC was declared available. The safety significance of this event was low since all Emergency Core Cooling Systems were operable during the time the RCIC turbine was tripped.
3312016003 | Duane Arnold | 10/18/2015 | 12/06/2016 | ML16342C56 | <strong>Main Steam Isolation Valve Leakage Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2016, with the unit shutdown for a planned refueling outage (Mode 5, Refueling, 0% power), an evaluation of data from the scheduled Main Steam Line Isolation Valve (MSIV) (System Code SB) and Main Steam Line Drain valve penetration Local Leak Rate Testing (LLRT) determined the 'as found' maximum pathway leakage for the 'B' Inboard MSIV, CV-4415, and the Outboard Main Steam Line Drain valve, MO-4424, was in excess of the Technical Specification (TS) 3.6.1.3 leakage limit of <= 100 scfh for a single MSIV and <= 200 scfh for combined pathway leakage. The cause was determined to be a failure to perform periodic internal inspections of the MSIVs and a non-optimal valve design for the steam line drain application. Corrective actions included reworking CV-4415 to restore its leakage limit to below TS limits. Corrective actions are planned to replace MO-4424 with an optimal valve design. This event was of low safety significance had no impact on public health or safety. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
3332016001 | FitzPatrick | 01/23/2016 | 03/23/2016 | ML16083A50 | <strong>System Actuations During Manual Scram in Response to Frazil Ice Blockage and Residual Transfer</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2016, James A. FitzPatrick Nuclear Power Plant (JAF) was ascending in power when screenwell water level started to lower. At 89 percent power, at 22:23, Operators began taking compensatory measures to reduce power and mitigate water level lowering. At 22:40, a manual scram was initiated.<br /><br /> The scram was complicated by a residual transfer that resulted in non-vital equipment trips. This event resulted in the manual actuation of the Reactor Protection System, High Pressure Coolant Injection, Reactor Core Isolation Cooling, Main Steam Isolation Valves and automatic actuation of Emergency Diesel Generators, Emergency Service Water, and containment isolations in multiple systems, reportable per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> The lowering screenwell water level was caused by frazil ice blockage at the intake structure. The frazil ice stopped affecting screenwell water level after the manual scram. Corrective actions include strengthening mitigating actions in response to frazil ice. <br /><br /> The residual transfer was caused by lubrication hardening in the lower control valve assembly of the 71PCB-10042 breaker. Corrective actions included replacing or reworking the lower control valve assembly.
3332016002 | FitzPatrick | 02/25/2016 | 04/25/2016 | ML16116A24 | <strong>Sticking DC Pilot in Solenoid Valve Cluster Assembly Results in Slow MSIV Closures</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2016, James A. FitzPatrick Nuclear Power Plant (JAF) initiated a manual Scram in response to lowering screenwell water level due to frazil ice blockage, and subsequently closed the Main Steam Isolation Valves (MSIV). A post Scram review identified that MSIV 29AOV-86B closed slowly. On January 26, 2016, testing per ST-1B identified that MSIV 29AOV-86C closed slowly. In both cases, the inboard MSIVs performed satisfactorily. <br /><br /> Troubleshooting identified that the problem originated in the solenoid valve cluster assemblies (SVCA) and they were replaced and tested successfully. A failure analysis was performed by Exelon PowerLabs on the SVCAs. On February 25, 2016, the Exelon PowerLabs analysis concluded that the DC pilot valves, 29SOV-86B3 and 29SOV-86C3, exhibited slow vent times. Additional corrective actions include changing the preventative maintenance frequency from 8 years to 6 years and initiating further investigation through the component's vendor. <br /><br /> Two MSIVs exceeded the closing time of Technical Specification Surveillance Requirement (SR) 3.6.1.3.6. This condition caused two independent channels of a system used to control the release of radioactive material to become inoperable; reportable per 10 CFR 50.73(a)(2)(vii).
3332016003 | FitzPatrick | 06/07/2016 | 08/03/2016 | ML16216A16 | <strong>Concurrent Opening of Reactor Building Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On the morning of June 7, 2016, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment. <br /><br /> This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference ENS 51985). Following the event, the doors functioned properly, and no deficiencies were noted with either door. <br /><br /> There were no radiological releases associated with this event.
3332016004 | FitzPatrick | 06/24/2016 | 08/23/2016 | ML16236A39 | <strong>Transformer Fault Results in Manual Scram and Secondary Containment Vacuum Below Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2016, at 1205, several 600V electrical busses lost power when James A. FitzPatrick Nuclear Power Plant was operating at 100% power. A fault in transformer 71T-5 caused a trip of circuit breaker 71-10340. Power was lost to 2 of 3 Reactor Building Closed Loop Cooling (RBCLC) pumps and 2 of 3 lube oil pumps for the Motor-Generator (MG) Set for 'A' Reactor Water Recirculation (RWR). The 'A' RWR pump tripped immediately causing reactor power to reduce to approximately 50%. The remaining RBCLC pump was inadequate to maintain the MG Set fluid drive oil temperature for the 'B' RWR pump so Operators initiated a manual scram at 1236. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> The power loss also affected Reactor Building Ventilation (RBV). This system supports the requirement of Technical Specification Surveillance Requirement 3.6.4.1.1 for a differential pressure in Secondary Containment. At the loss of RBV, Secondary Containment automatically isolated and the Standby Gas Treatment system was manually initiated. However, during this short transition the differential pressure requirement was not met. This report is being submitted per 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The apparent cause of the 71T-5 fault was inadequate preventative maintenance which allowed the transformer to remain in service beyond expected service life.
3332016005 | FitzPatrick | 09/19/2016 | 11/17/2016 | ML16323A20 | <strong>Degraded Damper Actuator Prevented Control Room Ventilation Exhaust Fan Start</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2016, the Control Room Ventilation exhaust fan 70FN-4A did not start when it was being placed into service. The fan outlet isolation damper actuator 70MOD-108A(OP) failed to give the fully-open permissive signal to start the fan. Gentle pressure on the actuator linkage allowed the fan to start. Prior to this, on August 16, 2016, during post-maintenance testing, 70FN-4A did not start. Troubleshooting adjusted the linkage and the fan started as appropriate. However, the intermittent fan start issue was caused by the degraded damper actuator 70MOD-108A(OP). Corrective action replaced 70MOD-108A(OP). <br /><br /> This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3352016001 | St. Lucie 1, St. Lucie 2 | 06/02/2016 | 07/29/2016 | ML16230A00 | <strong>Inadequate Legacy Evaluation for Containment High Range Radiation Monitor Nonconformance with Design Accuracy Requirements Resulted in Latent lnoperability and Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2016, St. Lucie Units 1 and 2 were in Mode 1 at 100% power. At 1500 hours FPL declared the containment high range radiation monitors (CHRRMs) inoperable on both Units. FPL determined that the resolution of the NRC Information Notice (IN) 97-45 industry Operating Experience (OE) concerning CHRRMs cabling was less than adequate. The assumed CHRRMs design accuracy could not be assured during some postulated design basis accidents due to the errors introduced by thermal induced currents and water intrusion/cable blistering within the associated detectors' cabling, resulting in inoperable CHRRMs. The Technical Specifications (TSs) require preplanned alternate means for containment radiation monitoring for inoperable CHRRMs; these requirements were not implemented until June 2016. FPL also submitted a TS 6.9.2 Special Report for two channels of inoperable CHRRMs. <br /><br /> This legacy event was caused by the inadequate evaluation and improper tracking of actions required to fully close the nonconformance identified in the 1997 Information Notice. CHRRMs are used for information, they are not used to control radioactive releases or mitigate accidents. Their inoperability had no significant impact on the health and safety of the public. <br /><br /> FPL plans to replace the CHRRMs cabling susceptible to the phenomenon identified in NRC Information Notice 97-45 and its supplement 1.
3352016002 | St. Lucie 1 | 08/05/2016 | 10/04/2016 | ML16302A06 | <strong>Safety Injection Check Valve Leakage Exceeding Technical Specification Limits and Allowed Outage Time Resulted in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2016, during Unit 1 restart following a maintenance outage, operators observed excessive seat leakage past a Reactor Coolant System (RCS) pressure isolation check valve. The flow path was promptly identified and isolated. A leak test was planned and performed at higher RCS pressure to quantify the leakage. The seat leak test at normal operating pressure was halted when an appropriate differential pressure was not achieved for testing. As a result, V3217, Safety Injection Loop 1A2 Check Valve, was declared inoperable, and Unit 1 was placed in Mode 5 COLD SHUTDOWN to complete repairs. The leakage past V3217 was caused by inadequate maintenance practices and procedures that did not ensure V3217 was within acceptable tolerances and correctly assembled in 2013. <br /><br /> Corrective actions include revisions to procedures for check valve maintenance, check valve trending and check valve preventive maintenance. <br /><br /> This event is reportable pursuant to.10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Since this condition was identified with Unit 1 in HOT STANDBY prior to reactor startup, the leaking check valve had no direct nuclear safety significance or impact to the environment. <br /><br /> This event had no effect on the health and safety of the public.
3352016003 | St. Lucie 1 | 08/21/2016 | 09/08/2017 | ML17251A13 | <strong>Generator Lockout Relay Actuation During Power Ascension Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2016, during Unit 1 restart following a maintenance outage, an unexpected actuation of the Main Generator Inadvertent Energization Lockout Relay caused the main generator to trip, resulting in an automatic reactor trip. The generator lockout prevented the automatic transfer of station auxiliaries to the available startup transformer power, requiring the emergency diesel generators to start and power the safety related buses. Reactor coolant pumps normally powered through the non-safety buses were deenergized, and decay heat removal was via natural circulation and Auxiliary Feedwater. The lockout relay actuation was caused by a latent error introduced during a 2013 design modification where the maintenance configuration control procedure did not prevent a wire from being inadvertently removed from the circuit. <br /><br /> Corrective actions included restoration of the affected circuit, implementation of procedure guidance to verify the inadvertent energization relay state following Main Generator manual synchronization and revisions to the maintenance configuration control procedure. <br /><br /> This licensee event report is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for system actuations of the reactor protection system, the emergency diesel generators and the auxiliary feedwater system. <br /><br /> This event had no effect on the health and safety of the public.
3362016001 | Millstone 2 | 04/27/2016 | 06/27/2016 | ML16187A32 | <strong>Turbine Driven Auxiliary Feedwater Pump Room HELB Door Left Open</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2016, with Millstone Power Station Unit 2 (MPS2) in MODE 1 at 100% power, plant personnel inadvertently left the door to the turbine driven auxiliary feed pump room open. This condition existed for less than one hour. The door is a high energy line break (HELB) barrier. With the door open there is no HELB protection for the motor driven auxiliary feedwater (AFW) pumps thus potentially rendering both trains of AFW inoperable. <br /><br /> The cause is human performance error. The door is conspicuously labeled on each side that it is a HELB boundary door and must be closed except for entry and exit from the room. Corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This condition is being reported pursuant to 10 CFR 50.73(a)(2)(v) as any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) remove residual heat; and (D) mitigate the consequences of an accident.
3362016002 | Millstone 2 | 08/11/2016 | 09/20/2016 | ML16271A40 | <strong>Manual Reactor Trip due to Loss of Two Circulating Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2016 at 09:59 while operating in MODE 1 at 100% power, operators manually tripped the Millstone Power Station Unit 2 reactor due to degraded condenser vacuum caused by the loss of two out of four circulating water pumps (CWPs) ('A' and 'C' CWPs). The reactor trip was uncomplicated and decay heat removal was via the steam dumps to the condenser. All control rods inserted on the reactor trip. All safety systems functioned as required. <br /><br /> The 'A' and 'C' CWPs stopped due to a loss of normal control power in the associated variable frequency drive (VFD) system. Both backup uninterruptible power supplies (UPS) in the VFDs associated with the 'A' and 'C' CWPs failed to function resulting in the 'A' and 'C' CWPs stopping. This coincided with a grid disturbance that occurred during a storm. The loss of two out of four CWPs caused a reduction in condenser vacuum. The operators manually tripped the reactor due to degrading condenser vacuum. <br /><br /> The associated UPSs were replaced. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
3382016001 | North Anna 1, North Anna 2 | 01/23/2016 | 03/16/2016 | ML16099A38 | <strong>Emergency Diesel Generators Automatic Start Due to Loss of Power to "C" Reserve Station Service Transformer</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2016, at approximately 1703 hours, with Units 1 and 2 operating at 100 percent power Mode 1, the North Anna 34.5kv Bus 3, offsite power feed to the "C" Reserve Station Service Transformer, was lost due to the opening of the L102 breaker. This resulted in the loss of power to the Unit 1H and Unit 2J emergency buses and the automatic start of the 1H and 2J emergency diesel generators (EDG). The Unit 1H emergency bus off-site power was restored and the 1H EDG was secured and returned to automatic. The 2J EDG continued to carry the 2J bus until repairs to L102 were completed and the 72 hour limiting action for Unit 2 was exited at 1706 hours on 1/24/16. The direct cause for-the opening of the L102 breaker was an internal switch contact failure due to moisture. At 1948 hours on January 23, 2016, an 8-hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72(b)(3)(iv)(A) as a condition that resulted in valid actuation of Engineered Safety Features (ESF). Units 1 and 2 continued to operate safely during the event. The health and safety of the public were not affected by this event.
3382016002 | North Anna 1, North Anna 2 | 03/09/2016 | 05/05/2016 | ML16133A33 | <strong>Chemical Addition System Outside of Technical Specification Due to Excessive Unseating Thrust on MOVs</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2016, at approximately 1034 hours, with Unit 1 at 100 percent power in Mode 1 and Unit 2 at 0 percent power in Mode 6 for a scheduled refueling outage, 2-QS-MOV-202B failed to stroke open when functionally tested due to excessive unseating thrust. An extent of condition review and engineering evaluation determined that 2-QS-MOV-202A maintained its function. An extent of condition review and engineering evaluation of the Unit 1 valves determined that 1-QS-MOV-102B maintained its function and 1-QS-MOV- 102A did not. Design Changes (DC) (DC NA-16-00023 for Unit 1 and DC NA-16-00021 for Unit 2) were implemented to provide additional valve operating margin prior to returning the valves to service. Based on as-found testing and engineering evaluation, Sodium Hydroxide (NaOH) injection for both units would have been supplied in the event of a Design Basis Accident (DBA) and the safety function of the Chemical Addition System was maintained. The health and safety of the public were not affected by this event.
3382016003 | North Anna 1 | 04/29/2016 | 06/16/2016 | ML16175A42 | <strong>Engineered Safety Feature Actuation due to Loss of Power to "A" Reserve Station Service Transformer</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2016, at approximately 2214 hours, with Units 1 and 2 operating at 100 percent power Mode 1, a fault occurred on Switchyard Transformer 3 34.5kV leads resulting in 34.5 kV Bus 5 lockout relays actuating causing the offsite power feed to the "A" Reserve Station Service Transformer to be lost. This resulted in the loss of power to the Unit 1 "J" Emergency Bus and the automatic start of the 1J Emergency Diesel Generator (EDG). The cause was an external event involving wildlife contacting the load side leads of Transformer 3. The 1J Emergency Bus was transferred to its 2B Station Service alternate supply and the 1J EDG was secured and returned to automatic. Post incident inspection and testing of Transformer 3 and Bus 5 were completed satisfactory and subsequently returned to service. At 0048 hours on April 30, 2016, an 8-hour Non-Emergency Report was made to the NRC in accordance with 10.CFR 50.72(b)(3)(iv)(A) as a condition that resulted in valid actuation of Engineered Safety Features (ESF). Units 1 and 2 continued to operate safely during the event. The health and safety of the public were not affected by this event.
3392016001 | North Anna 2 | 07/30/2016 | 09/21/2016 | ML16271A40 | <strong>Technical Specification Required Shutdown due to Reactor Coolant System Leak</strong><br /><i>Abstract:&nbsp;</i>On July 29, 2016, with Unit 1 and Unit 2 at 100 percent power in mode 1, Unit 2 Reactor Coolant System (RCS) unidentified leakage was noted to take a 0.05 gallons per minute step increase coincident with a similar increase in Unit 2 containment sump in-leakage. Subsequent containment entries identified a through wall leak existed in the controlled bleed-off piping associated with the Reactor Coolant Pump seal for 2-RC-P-1C. Due to the pressure boundary leakage, this event was reported at 1517 hours on July 30, 2016, in accordance with 10 CFR 50.72(b)(2)(i), for "The initiation of any nuclear plant shutdown required by the plant's Technical Specifications" and 10 CFR 50.72(b)(3)(ii)(A) for "Any event or condition that results in the condition of the nuclear power plant including its principle safety barriers, being seriously degraded." While in Mode 5, the controlled bleed-off piping associated with the RCP seal for 2-RC-P-1C was replaced. The health and safety of the public were not affected by this event.
3412016001 | Fermi 2 | 01/06/2016 | 01/23/2017 | ML17024A30 | <strong>Turbine Stop Valve Closure and Turbine Control Valve Fast Closure Reactor Protection System Functions Considered Inoperable due to Open Turbine Bypass Valves</strong><br /><i>Abstract:&nbsp;</i>At 1514 EST on January 6, 2016, while operating at 100 percent Reactor Thermal Power (RTP), the East and West Turbine Bypass Valves (TBV) automatically opened as expected for 3 minutes and 32 seconds in response to the number one High Pressure Turbine Stop Valve (TSV) drifting from full open to 25 percent open due to an actuator malfunction. <br /><br /> Per Technical Specification (TS) Bases 3.3.1.1, TBVs must remain shut while RTP is at or above 29.5 percent to consider all channels of the TSV closure and Turbine Control Valve (TCV) fast closure Reactor Protection System (RPS) functions operable.<br /><br /> Reactor Operators lowered RTP to 91.0 percent and at 1518 EST the TBV automatically closed and the TSV closure and TCV fast closure RPS functions were no longer considered inoperable. TS 3.3.1.1 requires that the TSV closure and TCV fast closure RPS functions be operable at or above 29.5 percent RTP. In this event, during the period of time while TBVs were open, reactor power was maintained above 91 percent and the RPS functions were confirmed to be enabled. <br /><br /> The actuator malfunction was caused by faulty connectors within the actuator. The faulty connectors were replaced.
3412016002 | Fermi 2 | 01/22/2016 | 03/22/2016 | ML16082A45 | <strong>Both Residual Heat Removal Low Pressure Coolant Injection Divisions Inoperable due to Inoperable Injection Valve</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2016, at 1923 EST, both divisions of the Residual Heat Removal (RHR) system were declared inoperable for the Low Pressure Coolant Injection (LPCI) mode of operation due to a failure of the division 1 LPCI outboard injection motor operated valve (MOV), E1150F017A. While performing the division 1 RHR pump and valve operability surveillance test, E1150F017A closed properly but failed to open during its required stroke time test. With this valve closed and unable to automatically open, LPCI injection into the Reactor Pressure Vessel (RPV) from both divisions of RHR would be prevented if the LPCI loop select logic selected the division 1 recirculation loop for injection; therefore, this failure rendered both divisions of RHR inoperable for the LPCI function. Technical Specification limiting condition for operation (LCO) 3.5.1, Condition K, was entered, which requires immediate entry into LCO 3.0.3. The cause of the failure was subsequently identified as a foreign material (screw) that affected the function of the MOV contactor. The root cause was determined to be less than adequate inspection procedures and susceptibility of the contactor to foreign material. Inspection of all other susceptible equipment is ongoing to tighten loose screws and a modification is planned to install Foreign Material Exclusion (FME) barriers.
3412016005 | Fermi 2 | 08/02/2016 | 09/30/2016 | ML16274A06 | <strong>Secondary Containment Pressure Exceeded Technical Specification due to Reactor Building HVAC Restart During High Winds</strong><br /><i>Abstract:&nbsp;</i>On August 2, 2016, at 1015 EDT, while restoring the east train of Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) after a surveillance test on Division 2 Standby Gas Treatment System (SGTS), the Technical Specification (TS) for the Secondary Containment (SC) pressure boundary was not met for approximately 1 second. The maximum SC pressure observed was approximately 0.120 inches of vacuum water column. The TS requirement is to maintain SC vacuum greater than or equal to 0.125 inches of vacuum water column for SC operability. All plant equipment responded as required to the changing conditions and RBHVAC and SGTS already in operation returned the SC pressure to within the TS limits; therefore, the Limiting Condition for Operation was met. There were no safety consequences or radiological releases associated with this event. <br /><br /> The cause of this momentary loss of SC was determined to be the combined effect of the RBHVAC startup sequence with high winds outside the Reactor Building (RB). For corrective actions, Fermi 2 has implemented a plant modification to the RBHVAC system to improve its ability to maintain RB pressure negative during the RBHVAC startup sequence. In addition, Fermi 2 will adopt Technical Specification Task Force Traveler (TSTF) 551, "Revise Secondary Containment Surveillance Requirements," when it is approved, to eliminate the need to declare SC inoperable due to momentarily exceeding the TS vacuum limit.
3412016006 | Fermi 2 | 08/25/2016 | 10/20/2016 | ML16295A10 | <strong>Inadequate Interpretation of Technical Specifications Related to Mechanical Draft Cooling Tower Fan Brake System Leads to Condition Prohibited by Technical Specifications, Loss of Safety Function, and Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>At 1629 EDT on August 25, 2016, it was determined that an inadequate interpretation of Fermi 2 Technical Specification (TS) 3.7.2 was being utilized. For an Ultimate Heat Sink (UHS) divisional reservoir to be operable, two Mechanical Draft Cooling Tower (MDCT) fans in that division are required to be operable. The MDCT fans have a brake system to prevent fan overspeed during a tornado. Fermi 2 procedures had directed personnel to declare the MDCT fans and UHS reservoir inoperable due to nonfunctionality of the brake system only if a tornado watch or warning was in effect for the area near Fermi 2. The correct interpretation of TS 3.7.2 would be to declare the MDCT fans and UHS reservoir inoperable any time the brake system was nonfunctional. Following discovery of the inadequate interpretation of TS, a review of the brake system for the past three years was performed. The review identified 15 occurrences where the brake system was nonfunctional and should have resulted in entry to TS 3.7.2. These 15 occurrences resulted in operations or conditions prohibited by TS since TS Required Actions were not completed within their Completion Times. In addition, 5 of the 15 were also instances where the plant configuration was such that it could have prevented the fulfillment of the safety function of structures or systems. Finally, 4 of the 15 were instances where the plant was in an unanalyzed condition. There were no radiological releases associated with this event. There was no credible threat of a tornado during any of the 15 occurrences. The safety significance was determined to be very low. The cause of the event was an incorrect proceduralized TS interpretation. Corrective actions were taken to revise the procedure.
3412016009 | Fermi 2 | 04/24/2016 | 12/20/2016 | ML16356A14 | <strong>Emergency Diesel Generator Inoperable due to Open Circuit on Loss of Power Instrumentation</strong><br /><i>Abstract:&nbsp;</i>At 1644 EDT on April 24, 2016, while operating at 100 percent Reactor Thermal Power, the potential transformer (PT) primary fuses on Bus 64C were found blown, resulting in half of the Loss of Power (LOP) instrumentation relays tripping on Bus 64C. Initially, the LOP instrumentation was incorrectly considered OPERABLE; however, later reviews of the condition determined that the LOP instrumentation was inoperable. Later reviews also concluded that the Division 1 Alternating Current (AC) Source was inoperable from 1644 to 1920 on April 24, 2016, and the Division 1 Emergency Diesel Generator (EDG) 12 was inoperable starting at 1644 on April 24, 2016, until it was restored at 1818 on May 8, 2016, during a Forced Outage following replacement of the blown PT fuses. On six occasions from April 26-30, 2016, Division 2 EDGs 13 and/or 14 were inoperable for planned surveillances. Therefore, this is an event or condition that could have prevented the fulfillment of a safety function to remove residual heat and mitigate the consequences of an accident. Furthermore, failure to enter applicable Limiting Conditions for Operation resulted in a condition prohibited by Technical Specifications. The cause of the event was concluded to be a low energy transient event resulting in the blown PT primary fuses. The incorrect initial operability determination was caused by Operators being unfamiliar with this equipment condition. Operators completed a Department Event Free Day Reset and Event Review and will receive additional training on this condition.
3412016011 | Fermi 2 | 10/28/2016 | 12/20/2016 | ML16356A28 | <strong>Standby Liquid Control Inoperable due to Sodium Pentaborate Concentration Outside of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2016, at 1500 EDT, Fermi 2 Operators declared both subsystems of Standby Liquid Control (SLC) inoperable due to the sodium pentaborate concentration in the SLC storage tank being outside of the Technical Specification (TS) requirements. The sodium pentaborate concentration had been measured in response to the receipt of the SLC storage tank high level alarm. The demineralized water isolation valves that could cause a dilution of the tank were verified to be closed. Actions were initiated to add sodium pentaborate to the SLC storage tank to raise the concentration. SLC was declared operable at 1935 EDT following a measurement that verified that sodium pentaborate concentration had been restored to within the TS requirements. The cause of the event was determined to be leak-by of the demineralized water isolation valves that had caused an increase in SLC storage tank level and, therefore, a decrease in sodium pentaborate concentration. The leak-by had been occurring for some time and had gone undetected. The cause of the leak-by not being detected was determined to be inadequate system monitoring. Corrective actions were completed to replace the demineralized water isolation valves and revise the chemistry specification to clearly specify action levels for the tank level and sodium pentaborate concentration and provide margin to the TS limits. Corrective actions were also completed to revise the SLC system monitoring plan to incorporate trending of tank level and boron concentration. The safety significance of this event is very low and the event did not pose a threat to the health and safety of the public or plant personnel. There were no radiological releases associated with this event.
3412016012 | Fermi 2 | 11/02/2016 | 12/20/2016 | ML16356A28 | <strong>Unanalyzed Condition for Control Rod Drop Accident at Low Reactor Power</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2016, a non-conservatism in the current Fermi 2 design and licensing basis of the control rod drop accident (CRDA) was identified. The current analysis assumes that the fission products released as a result of a CRDA are transported to the condenser and then released from there. An unanalyzed condition was identified where a forced release from the Gland Seal Exhausters (GSEs) could occur which would exceed dose limits in 10 CFR 100.11 and Standard Review Plan 6.4 when operating at low reactor power conditions. The postulated fuel damage and associated release is only credible for low power conditions of less than 10% power. Fermi 2 was at 97% power at the time of discovery and, therefore, the condition did not exist. However, a review of past operating conditions identified five instances in the past three years where Fermi 2 operated at less than 10% power. Based on a subsequent engineering analysis, for each of those five instances, plant conditions and available equipment were such that dose limits would have been met even if a postulated CRDA had occurred during those times; therefore, there was no adverse impact to public health and safety or to plant employees. There were no radiological releases. The cause of the event was that the original design and licensing basis analysis of the CRDA did not evaluate the direct release of steam from the GSEs, and, therefore, the plant was not designed to mitigate the potential consequences associated with that release path. For corrective actions, the plant startup checklist was revised to impose restrictions on future startups based on the engineering analysis. Fermi 2 plans to pursue modifications which would eliminate this potential release path.
3462016001 | Davis-Besse | 01/29/2016 | 03/29/2016 | ML16091A11 | <strong>Reactor Trip During Nuclear Instrumentation Calibrations, and Steam Feedwater Rupture Control System Actuation on High Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On January 29, 2016 at 1322 hours, with the Davis-Besse Nuclear Power Station operating at approximately 100 percent power, an automatic reactor trip occurred due to the actuation of the Reactor Protection System (RPS). Nuclear Instrumentation calibration for RPS Channel 2 was in progress. RPS Channel 2 was in bypass and Channel 1 was inoperable/tripped due to an existing Reactor Coolant System (RCS) temperature element (RTD) issue. A fuse failure in an input to RPS Channel 4 caused RPS Channel 4 trip on Flux/Delta-Flux/Flow, resulting in the reactor trip. Post trip, the Steam Feedwater Rupture Control System (SFRCS) actuated due to high Steam Generator (SG) 1 level, initiating the Auxiliary Feedwater (AFW) System. The cause of the SFRCS actuation was an improper response by the Integrated Control System (ICS) after the reactor trip. ICS Rapid Feedwater Reduction (RFR) circuit did not actuate and the ICS SG/Reactor Demand Hand/Auto Station transferred from automatic control to manual. <br /><br /> Corrective actions include: RPS Channel 4 power failed fuse replaced, RCS RTD replacement next refueling outage, ICS RFR switch module replaced, ICS Hand/Auto Station modification. This report is being submitted as an event that resulted in automatic actuation of the RPS, and an automatic actuation of AFW per 10CFR50.73(a)(2)(iv)(A).
3462016002 | Davis-Besse | 01/30/2016 | 03/29/2016 | ML16091A11 | <strong>Unanticipated Steam and Feedwater Rupture Control System Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2016, with the plant in Mode 3, with the Auxiliary Feedwater System (AFW) in operation and proceeding with Post Trip recovery actions from the January 29, 2016 Steam Feedwater Rupture Control System (SFRCS) High Level Trip (reference Licensee Event Report (LER) 2016-001) when a SFRCS Steam Generator (SG) 1 High Reverse Differential Pressure (D/P) Trip was unexpectedly received. The trip was a result of a feedwater isolation valve being opened to align the Motor Driven Feed Pump's (MDFP) discharge to SG 1. The unexpected SFRCS SG 1 Reverse D/P Trip resulted in the closure of the appropriate Main Steam and Main Feedwater (MFW) valves, as designed. AFW Pumps 1 and 2 remained in operation, as expected and the plant was verified to be stable. <br /><br /> The cause of this event was inadequate procedural guidance contained in the Trip Recovery Procedure with a corrective action to revise the procedure. This report is being submitted as an event that resulted in an automatic actuation of the SFRCS, therefore, reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A).
3462016003 | Davis-Besse | 03/30/2016 | 05/31/2016 | ML16154A14 | <strong>Leak from Reactor Coolant Pump Seal Piping Flexible Hose due to Undetected Manufacture Weld Defect</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2016, with the Davis-Besse Nuclear Power Station shutdown for a scheduled refueling outage in Mode 6 with the Reactor Coolant System depressurized, approximately one half teaspoon of dry boric acid was identified on the Reactor Coolant Pump (RCP) 1-1 first stage seal cavity vent line flexible braided piping connection, which was determined to be reactor coolant pressure boundary leakage. This leak was from the welded end connection of the small bore ASME Section III Class 2 flexible braided piping assembly between the RCP seal and the first isolation valve. <br /><br /> The most probable cause of this leak was a weld solidification through-wall crack at the flange to hose / bellows tube pressure boundary weld that occurred during manufacture. The post manufacture testing was not adequate to detect this extremely small pressure boundary defect. Corrective actions include inspecting the other RCP seal vent line flexible hoses, replacement of RCP 1-1 seal vent line flexible piping assembly with one that passed a more stringent leak test, and revising procurement requirements to incorporate this more stringent leak test.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(A) as degradation of a principal safety barrier and 10 CFR 50.73(a)(2)(i)(B) as operation or condition prohibited by Technical Specifications.
3462016004 | Davis-Besse | 04/05/2016 | 08/30/2016 | ML16245A29 | <strong>Reactor Coolant System Hot Leg Resistance Temperature Detector Wire Insulation Degradation</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2016, at 0243, with the Davis-Besse Nuclear Power Station (DBNPS) in Mode 5, it was discovered that the six dual-element Resistance Temperature Detectors (RTD) on both Reactor Coolant System (RCS) Hot Legs had varying degrees of wire insulation degradation. The cause of the RTD insulation degradation was accelerated aging due to high temperatures as a result of improper configuration of piping insulation on the RTD during the previous refueling outage. Corrective actions taken include replacing five of the six RCS Hot Leg RTDs. The sixth RTD was determined to be suitable for continued operation and is planned to be replaced during the next Refueling Outage. <br /><br /> The Electrical Conductor Seal Assemblies (ECSA) taken from the removed RTDs were evaluated for reuse on replacement RTDs. It was discovered that the Midlock Ferrules were installed backwards on two RTDs during the past refueling outage. The cause was determined to be less than adequate installation instructions. Corrective actions are to revise the Maintenance procedure and implement further training.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(v)(A), and 10 CFR 50.73(a)(2)(vii).
3462016005 | Davis-Besse | 05/10/2016 | 07/11/2016 | ML16194A34 | <strong>Plant Startup with Anticipatory Reactor Trip System in Main Turbine Bypass</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2016, the Davis-Besse Nuclear Power Station (DBNPS) was in Mode 1 and increasing power following refueling outage activities. At 0528 hours, it was identified that all four of the Anticipatory Reactor Trip System (ARTS) channel switches were in the bypass position for the Main Turbine function while at approximately 53 percent power. These switches are required by the Technical Specifications to be in the normal/enabled position when above 45 percent power. The switches were restored to Normal and the applicable Technical Specifications exited at 0552 hours. An Operations Standing Order was issued to require paired periodic walk downs of all Control Room panels to ensure a comprehensive understanding of plant status awareness. Walk downs were also performed to independently identify any additional concerns or omissions in plant startup activities. The root cause of this event is the operators failed to effectively work as a team to ensure a safety system was in an operable condition when required. Corrective actions include implementation of the Operations Section Continuous Improvement Plan and revision of applicable procedures. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3462016006 | Davis-Besse | 06/16/2016 | 08/15/2016 | ML16230A48 | <strong>Potential to Trip Emergency Diesel Generator on High Crankcase Pressure</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2016, the Davis-Besse Nuclear Power Station (DBNPS) was in Mode 1·and100 percent reactor power. At 1137 hours, during review of industry operating experience, an issue was identified for the potential impact of low barometric pressure associated with a tornado on the Emergency Diesel Generators (EDGs). The EDGs are equipped with a crankcase positive pressure trip with a set point of approximately 1 inch of water. It was determined that a design basis tornado could create sufficient low pressure to potentially actuate the crankcase positive pressure trip due to different vent paths between the EDG Room and the EDG crankcase. If the crankcase pressure trip occurs before the EDG starts on an emergency signal due to the tornado, the crankcase pressure trip would cause an EDG lockout. The EDG lockout would then prevent either an EDG normal or emergency start until operators could manually reset the lockout. This condition could potentially affect both EDGs simultaneously. <br /><br /> This was an original EDG protective logic circuitry design issue that did not anticipate the interaction between the crankcase pressure trip and the outside atmospheric pressure. Corrective actions included temporarily disabling this trip and longer-term plant modification to make the change permanent. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(v)(A) through (D).
3462016007 | Davis-Besse | 06/21/2016 | 08/22/2016 | ML16236A24 | <strong>Pressurizer Code Safety Valve Setpoint Test Failures</strong><br /><i>Abstract:&nbsp;</i>The two pressurizer safety valves (PSVs) at the Davis-Besse Nuclear Power Station (DBNPS) were replaced during an outage in Spring, 2016 with tested spares. The removed PSVs were sent to an offsite vendor for testing and refurbishment. In June, 2016 the test results were received showing both PSVs lifted higher than the allowed one percent tolerance above the 2500 psig setpoint (2525 psig) for As-Found testing. Because both valves had As-Found setpoints above the Technical Specifications (TS) allowed value, a past operability evaluation was performed, which concluded that both valves were inoperable during their time in service. <br /><br /> Based on the as-found lift setting pressures (2559 psig and 2554 psig), there was no adverse effect on transients described in the Updated Safety Analysis Report that can produce a Reactor Coolant System (RCS) overpressurization. The cause of this event was due to setpoint drift and narrow allowable setpoint range. Procedures will be revised to establish more restrictive testing requirements. The PSVs were replaced and a TS change will be submitted to provide for current ASME acceptance test criteria for the PSV setpoint. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) and 10 CFR 50.73(a)(2)(i)(B).
3462016008 | Davis-Besse | 06/30/2016 | 02/27/2017 | ML17060A23 | <strong>Application of Technical Specification for the Safety Features Actuation System Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2016, at 0829, with the Davis-Besse Nuclear Power Station in Mode 1 and at approximately 100 percent power, a level transmitter for Safety Features Actuation System (SFAS) Channel 1 was declared inoperable for scheduled maintenance and Technical Specification (TS) Limiting Condition of Operation (LCO) 3.3.5 Condition A was entered. At 2342 hours a power supply in SFAS Channel 2 failed and a separate TS LCO 3.3.5 Condition A was entered. Upon recognition that two channels of SFAS were inoperable, TS LCO 3.3.5 Condition B was entered at 0245 and then exited at 0330 with the use of compensatory actions to restore SFAS Channel 1 operability. After further review, it was determined the compensatory actions could not be credited and TS LCO 3.3.5, Condition B was reentered at 1325. SFAS Channel 1 was restored and declared operable at 1351 hours.<br /><br /> Causes of the event were the Shift Manager failed to initially recognize that TS LCO Conditions A and B had been met; followed by Station Personnel failing to effectively implement required processes. The root cause was that Station Management failed to recognize that a normalized deviation had occurred that resulted in TS noncompliance. Corrective Actions include specific refresher training to all applicable personnel, revising relevant documents, and developing an event Case Study for training purposes. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant's Technical Specifications.
3462016009 | Davis-Besse | 09/10/2016 | 11/09/2016 | ML16319A09 | <strong>Reactor Trip due to Rainwater Intrusion and Auxiliary Feedwater Actuation on High Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On September 10, 2016, with the Davis-Besse Nuclear Power Station (DBNPS) operating at approximately 100 percent power, rainwater intrusion into the Main Generator Automatic Voltage Regulator (AVR) cabinet due to an open roof vent caused a lockout of the Main Generator, resulting in a trip of the Main Turbine and Reactor. Following the Reactor trip, the Steam Feedwater Rupture Control System (SFRCS) actuated due to high Steam Generator 1 level and initiated the Auxiliary Feedwater System. The most probable cause of the SFRCS actuation was a failed operational amplifier in the Integrated Control System (ICS), causing the ICS to not reduce Feedwater flow to Steam Generator 1 following the Reactor trip. <br /><br /> Completed corrective actions include closing the roof vents, sealing the top of the AVR cabinet, improved configuration control of the vents, and replacement of the failed ICS module. Scheduled corrective actions include presenting a case study to improve recognition of elevated risk issues, and review of the ICS by a multi-functional team to address system performance concerns.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the Reactor Protection System, and an automatic actuation of the Auxiliary Feedwater System.
3482016001 | Farley 1 | 04/13/2016 | 06/09/2016 | ML16161B27 | <strong>Condition Prohibited by Technical Specifications due to 600V Load Center Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 4/12/2016 at 0312 CDT, with Unit 1 (U1) at 100 percent power and Unit 2 (U2) in Mode 5, the U2 supply breaker for 1-2R 600V Load Center (LC) was racked out and the control power fuses removed for both U2 supply breaker and U1 supply breaker to support replacing an agastat relay on the U2 supply breaker. On 4/13/2016 at 0456 CDT the U1 supply breaker for the 1-2R 600V LC, tripped open when the control power fuses were restored and would not reclose. Technical Specifications (TS) 3.8.9 Condition A was entered for Unit 1 at 0456 on 4/13/2016 and exited at 0938 on 4/13/2016. Investigation attributed the cause to dirty contacts on the cell switch located in the U2 supply breaker cubicle. This condition would have prevented the U1 supply breaker from reclosing if a loss of offsite power had occurred between 04/12/2016 at 0312 and 4/13/2016 at 0938, leaving the 1-2R LC de-energized. This caused the LC to be inoperable for Unit 1 for more than the time allowed by TS 3.8.9 and is reportable per 10 CFR 50.73(a)(2)(i)(B). This is not reportable for Unit 2 due to the unit being in Mode 5 and having the necessary portion of the electrical power distribution subsystems operable. <br /><br /> Corrective Action: The U2 supply breaker cell switch was cycled which cleaned the contacts and the U1 supply breaker closed. Post maintenance testing verified operability. Until replacement of the U2 supply breaker cell switch, administrative controls are in place to declare U1 supply breaker inoperable when racked out until the interlock feature is verified.
3482016002 | Farley 1 | 10/01/2016 | 11/30/2016 | ML16335A45 | <strong>Automatic Reactor Trip and Safety Injection due to Closure of Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 10/1/2016 at 0512 CDT with Unit 1 at 99 percent power the plant experienced a turbine trip and automatic reactor trip as a result of inadvertent closure of the 1A Steam Generator Main Steam Isolation Valve (MSIV). This caused a rapid pressure reduction in the remaining two Steam Generators' steam lines, resulting in a Safety Injection (SI). The 1A MSIV closure was caused by failure of its test solenoid in conjunction with other air system leakage, which vented air pressure from the 1A MSIV actuator. An inadequate technical justification allowed the improper deactivation of the preventive maintenance (PM) task of the test solenoid valve in 2004. Decision making by control room personnel not to strictly adhere to an Annunciator Response Procedure was a contributing cause to the reactor trip being automatic versus manual, and led to the SI. Following the reactor trip and SI the 1A MSIV test solenoid was replaced and check valves on the 1A MSIV steam line were tested and replaced. The technical justifications of a sample of previously extended or deleted PMs strategies will be reviewed and corrected. The PM for the Unit 1 solenoid will be reinstated. Procedure use and adherence standards have been reinforced with Operations personnel, simulator just-in-time training was conducted for all crews, and further causal analysis is planned to investigate operations fundamental performance gaps. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system, Emergency Core Cooling System (ECCS) injection into the Reactor Coolant System, and automatic actuation of the AFW system.
3482016003 | Farley 1 | 10/13/2016 | 12/12/2016 | ML16347A11 | <strong>Pressurizer Safety Valve Setpoint Pressure Outside of Technical Specification Tolerance Band</strong><br /><i>Abstract:&nbsp;</i>On 10/13/2016 it was discovered that a Unit 1 pressurizer safety valve (PSV), which had been removed during the October 2016 refueling outage and shipped offsite for testing, failed its as-found lift test. The PSV lifted below the Technical Specification (TS) 3.4.10 allowable lift setting value. Seat leakage of the PSV is the most likely cause of the setpoint drift. <br /><br /> It is likely that the PSV was outside the TS limits longer than allowed by the Required Action Statement (15 minutes) during the Cycle 27 applicable modes of operation. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) for a condition which was prohibited by the plant's Technical Specifications. <br /><br /> The PSV was replaced during the October 2016 refueling outage.
3482016004 | Farley 1 | 10/20/2016 | 12/19/2016 | ML16354B55 | <strong>Unapproved Environmental Qualification Material Caused Inoperability of One Containment Cooling Train</strong><br /><i>Abstract:&nbsp;</i>On 10/20/2016 with Unit 1 in Mode 6 during a refueling outage, motor field cables on the 1C Containment Cooler were found to contain splice material that was Environmentally Qualified (EQ) but not approved for use in containment. The material had been installed as part of a design change during the previous refueling outage. This unapproved material could have exposed the associated connectors to potential accident environments and was an untested configuration for EQ purposes. As a result, operability of the 1C Containment Cooler cannot be supported for cycle 27. During Cycle 27 the 1C Containment Cooler was the selected cooler for B train for periods that exceeded the required action completion time for Technical Specification (TS) 3.6.6 for one containment cooling train being inoperable. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The cause was a Human Performance error that resulted in selection of an incorrect splice kit for a design change. The corrective actions were the installation of an appropriately EQ qualified splice suitable for use inside containment, and the establishment of expectations to have a corporate environmental qualification specialist review design packages when working with EQ component replacements.
3482016005 | Farley 1 | 11/01/2016 | 12/28/2016 | ML16363A39 | <strong>Toxic Gas Event</strong><br /><i>Abstract:&nbsp;</i>On 11/1/2016 at 1743, Farley declared an Alert based on ammonia levels on the radiation side of the Auxiliary Building in the Recycle Evaporator room. The declaration was based on toxic gas emergency action level (EAL) HA3 which states, "Release of toxic, asphyxiate, or flammable gases within or contiguous to a VITAL AREA which jeopardizes operation of systems required to maintain safe operations or establish or maintain safe shutdown." The source was identified as a failed valve in Auxiliary Steam supply to the Recycle Evaporator system, which had previously been abandoned in place. The ammonia leak was subsequently isolated. Ammonia levels were reduced and the event was terminated at 2340 on 11/1/2016. The failure was determined to be due to ammonia-copper interaction in the brass valve material. <br /><br /> This report is being submitted under 10 CFR 50.73(a)(2)(x) for an event that hampered site personnel in performance of duties necessary for operation of the power plant due to a toxic gas release.
3482016006 | Farley 1 | 11/08/2016 | 12/19/2016 | ML16354B54 | <strong>Manual Reactor Trip due to Loss of Speed Control on 1A Steam Generator Feed Pump</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2016, Joseph M. Farley Nuclear Plant Unit 1 was reducing power to remove the main generator from service. The 1A steam generator feed pump did not respond to control steam generator levels as expected when the miniflow valve was opened per procedure. Steam generator levels lowered due to lower feed flow, and at 1331 the reactor was manually tripped from 32 percent power to prevent reaching the low steam generator level automatic reactor trip setpoint. The motor driven auxiliary feed pumps also started automatically, as expected, with the manual reactor trip. The main steam isolation valves were closed to limit the unit cool down, decay heat removal was accomplished with the atmospheric relief valves, and the unit was maintained in mode 3. The controller failure was caused by the speed reference adjust and speed controller (C2) card being out of tolerance due to a failed A2 operational amplifier on the card, which was caused by infant mortality. The C2 card was replaced, and the new card was verified to be within the required tolerance. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
3482016007 | Farley 1 | 11/17/2016 | 11/20/2017 | ML17324B30 | <strong>Plant Shutdown Required by Technical Specifications due to Inoperable Steam Flow Transmitters</strong><br /><i>Abstract:&nbsp;</i>On 11/17/2016 at 1859 with Unit 1 in Mode 1 at 99 percent power, the plant initiated a shutdown in accordance with Limiting Condition for Operation (LCO) 3.0.3 for having no operable steam flow channels for the C Steam Generator (SG). The two steam flow channels did not meet acceptance criteria for Technical Specification (TS) 3.3.2. The shutdown was completed and the plant entered Mode 3 as required by LCO 3.0.3. This is reportable as a plant shutdown required by TS in accordance with 10 CFR 50.73(a)(2)(i)(A). This is also reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B) and an event or condition that could have prevented fulfillment of a Safety Function per 10 CFR 50.73(a)(2)(v)(D). <br /><br /> This condition was discovered during an engineering verification of beginning of cycle full power scaling values for steam flow normalization. The root cause was that necessary vendor manual instructions to calibrate different transmitters had not been captured into site procedures. The signal comparator card was replaced, and the channels were resealed and restored to operable status. Instructions will be incorporated into currently planned work orders for upcoming transmitter calibrations and installations to check and adjust as needed. Also, procedures are being revised to incorporate all missing vendor requirements for all models of Foxboro transmitters.
3482016008 | Farley 1 | 11/27/2016 | 01/23/2017 | ML17023A27 | <strong>Manual Reactor Trip due to Generator Voltage Swings</strong><br /><i>Abstract:&nbsp;</i>On 11/26/16 at 2357 while Unit 1 was operating at 100 percent reactor power the main generator began to experience voltage and load swings, which were caused by a problem with the main generator. The unit was manually tripped at 0026 on 11/27/16 to protect the generator from potential damage. All control rods fully inserted and Auxiliary Feedwater (AFW) auto-started as expected. The Turbine Driven AFW (TDAFW) was secured at 0037, with Motor Driven AFW pumps continuing to provide flow to ensure adequate heat sink. The TDAFW auto-started a second time at 0041 on a valid actuation signal when Steam Generator levels decreased to the TDAFW actuation setpoint. The TDAFW system was secured a second time at 0047. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system and an automatic actuation of the AFW system.<br /><br /> The swings were caused by an intermittent failure of the voltage isolation transducer. The voltage isolation transducer was replaced prior to the plant restarting. The transducer module is being sent off for failure analysis to aid in determination of the cause of this failure.
3482016009 | Farley 1, Farley 2 | 12/07/2016 | 02/02/2017 | ML17033B23 | <strong>Tornado Missile Vulnerabilities Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 12/7/16 Units 1 and 2 were in Mode 1 at 100 percent rated thermal power. Engineering personnel determined that the Unit 1 and Unit 2 Service Water Intake Structure (SWIS) intake and exhaust ventilation hoods were not adequately protected from tornado generated missiles. Subsequent evaluations on 1/26/17 resulted in the determination that the emergency diesel generator (EDG) fuel oil storage tank (FOST) vents were also not adequately protected from tornado generated missiles. Operations subsequently declared the affected systems inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance" and the required compensatory measures, and then declared the affected equipment operable but non-conforming. <br /><br /> This condition is an original plant design legacy issue. Immediate compensatory measures included actions to take if needed as described in severe weather procedures, and monitoring of system parameters on the MCB in accordance with annunciator response procedures. A risk based evaluation will be performed or plant modifications will be undertaken to establish compliance with the site's tornado missile protection design basis.
3522016001 | Limerick 1 | 01/25/2016 | 03/23/2016 | ML16083A23 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Unit 1 reactor enclosure secondary containment integrity was briefly declared inoperable when both doors on a reactor enclosure 201' elevation pipe tunnel airlock were simultaneously opened. The cause of the event was a degraded closing mechanism on the airlock inboard door. The airlock doors were closed to restore reactor enclosure secondary containment integrity. The degraded inboard door closing mechanism was repaired.
3522016002 | Limerick 1, Limerick 2 | 02/10/2016 | 04/11/2016 | ML16102A03 | <strong>Condition Prohibited by Technical Specifications due to Inoperable Safeguard Batteries During Cell Replacements</strong><br /><i>Abstract:&nbsp;</i>The Unit 1 Division 1 125 VDC Safeguard Battery was rendered inoperable due to installation of temporary seismic restraints that had not been approved for use. This historical issue was identified during a preventive maintenance activity to replace the battery. The investigation identified fifteen reportable events over a three year period. The cause was incomplete scoping of the engineering analysis performed to support battery cell replacements. The analysis did not include the impact of battery replacement activities on the battery rack. The battery cell rack support strategy was revised and a technical evaluation was performed for the seismic qualification of the battery rack during battery cell replacement. The battery cell replacement procedure (M-095-005) will be revised to address the updated technical evaluation and ensure seismic qualification of the battery rack is maintained during maintenance activities.
3522016003 | Limerick 1 | 03/20/2016 | 05/18/2016 | ML16139A42 | <strong>Plant Shutdown Required by Technical Specification Due to a Pressure Boundary Leak</strong><br /><i>Abstract:&nbsp;</i>Reactor coolant system pressure boundary leakage was identified by a drywell leak inspection team during a planned shutdown for a Unit 1 refueling outage. This event resulted in a plant shutdown required by Technical Specifications. The Unit 1 'A' RHR Shutdown Cooling Return Check Valve equalizing line developed a crack at the toe of a weld due to high cyclic fatigue induced by vibration from the reactor recirculation system. The Unit 1 welds were reworked to EPRI 2x1 at select locations on the "A" and "B" RHR Shutdown Cooling Return check valve equalizing lines for HV-051-1F050A and 50B. The similar Unit 2 welds on equalizing lines for HV-051-2F050A and 50B will be examined and reinforced. The scope will be added into the next refueling outage (2R14) currently scheduled for April 2017.
3532016001 | Limerick 2 | 06/01/2016 | 07/27/2016 | ML16209A26 | <strong>Manual Actuation of the Reactor Protection System When Critical due to Wiring Design Error</strong><br /><i>Abstract:&nbsp;</i>A manual actuation of the reactor protection system (RPS) when the reactor was critical was initiated during Plant Process Computer (PPC) modification testing at power. A modification wiring design error caused an actuation of both reactor recirculation pump (RRP) trip relays when a circuit isolation switch was closed. The direct cause of the event was a circuit wiring design error implemented in the field that caused energization of the RRP adjustable speed drive (ASD) trip coils. The root cause of the event was a failure of station personnel to appropriately apply Technical Human Performance (THU) error prevention techniques to identify the design error and prevent its installation and testing as part of the modification. The isolation switch for the mis-wired circuit was opened to enable reset of the ASD trip coils. The 2A and 2B ASDs were returned to service. The corrective actions are to change the circuit design to correct the design error. The human performance aspects of the event will be addressed through several management actions that include reinforcement of proper standards and behaviors related to THU error techniques with station personnel.
3542016001 | Hope Creek | 04/07/2016 | 10/04/2016 | ML16278A09 | <strong>High Pressure Coolant Injection System Found to be Inoperable During Testing</strong><br /><i>Abstract:&nbsp;</i>A review of plant conditions from April 2016, revealed a condition that could have prevented the fulfillment of a safety function. On April 7, 2016, at 0352, with the Hope Creek reactor operating at 100% power, the High Pressure Coolant Injection (HPCI) system turbine over-speed assembly did not respond as expected during post maintenance testing. The HPCI system was in the process of post maintenance testing following a planned maintenance window, and was inoperable at the time of the event. During system testing, the HPCI turbine was momentarily tripped by the over-speed assembly, and then reset itself with no operator action. Subsequent investigation found that the HPCI over-speed assembly reset spring did not have the correct preload. A review of the maintenance completed during the scheduled system outage determined that there was no maintenance performed on the over-speed assembly. Therefore, the condition could have been present prior to the start of the maintenance window on April 5, 2016 at 0205.<br /><br /> This report is being submitted under 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of a safety function of systems that are needed to mitigate the consequences of an accident. No specific cause was identified; however there is industry operating experience that the reset spring will relax over time, reducing the preload.
3542016002 | Hope Creek | 08/06/2016 | 11/30/2016 | ML16335A34 | <strong>High Pressure Coolant Injection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2016, at 21:34, with the Hope Creek reactor operating at 100% power, the High Pressure Coolant Injection (HPCI) system turbine governor valve did not respond as expected during system surveillance testing. The system was declared inoperable and an 8-hour immediate notification was made under 10 CFR 50.72(B)(3)(v)(d). Subsequent investigation found that HPCI turbine governor was not functioning due to corrosion products in the governor, preventing movement of the pilot valve. Additional research determined that the turbine governor did not respond properly on July 3, 2016 during the collection of an oil sample. Based on this, the HPCI system was inoperable for a period of 39 days from July 3, 2016, until August 11, 2016, when repairs to the governor were completed. The HPCI system Technical Specification has an allowed outage time of 14 days. <br /><br /> This report is being submitted under 10 CFR 50.73(a)(2)(i)(B), as a condition which is prohibited by the plant's Technical Specifications, and under 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of a safety function of systems that are needed to mitigate the consequences of an accident. The cause of the event is the accumulation of corrosion products in the HPCI turbine governor due to excessive moisture content in the HPCI system control oil.
3542016003 | Hope Creek | 10/22/2016 | 03/08/2017 | ML17067A50 | <strong>As-Found Values for Safety Relief Valve Lift Set Points Exceed Technical Specification Allowable Limit</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2016, Hope Creek Generating Station (HCGS) received results that the 'as-found' set-point tests for safety relief valve (SRV) pilot stage assemblies had exceeded the lift setting tolerance prescribed in Technical Specification (TS) 3.4.2.1. The TS requires the SRV lift settings to be within +/- 3% of the nominal set-point value. During the twentieth refueling outage (H1R20), all fourteen SRV pilot stage assemblies were removed for testing at an offsite facility. Between October 22 and October 28, 2016, HCGS received the test results for all fourteen of the SRV pilot valve assemblies. A total of ten of the fourteen SRV pilot stage assemblies experienced set-point drift outside of the TS 3.4.2.1 specified values. All of the valves failing to meet the limits were Target Rock Model 7567F two-stage SRVs. This is a condition reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. <br /><br /> The cause of the set-point drift for the ten SRV pilot stage assemblies is attributed to corrosion bonding between the pilot disc and seating surfaces, which is consistent with industry experience. This conclusion is based on previous cause evaluations and the repetitive nature of this condition at HCGS and within the BWR industry.
3542016004 | Hope Creek | 10/23/2016 | 12/20/2016 | ML16355A19 | <strong>Operations with a Potential to Drain the Reactor Vessel (OPDRV) Without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On October 23, October 24, and October 31, 2016, with Hope Creek Generating Station (HCGS) in a planned refueling outage and the reactor cavity flooded in OPCON 5, HCGS performed operations with a potential to drain the reactor vessel (OPDRV) without an operable secondary containment. These operations are prohibited by Technical Specification (TS) 3.6.5.1; however, NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 3, allowed the implementation of interim actions as an alternative to full compliance. These actions were compiled in a plant procedure for the OPDRV activities performed at HCGS during Refueling Outage (HR20) in October 2016. <br /><br /> These OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on the interim actions taken. Since these actions were deliberate, no cause determination was necessary. Consistent with the guidance provided in EGM 11-003, Revision 3, HCGS will submit a license amendment request to adopt a Technical Specification Task Force (TSTF) traveler associated with generic resolution of this issue within four months after the issuance of the Notice of Availability of the TSTF traveler. <br /><br /> These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
3542016005 | Hope Creek | 11/05/2016 | 03/13/2017 | ML17072A13 | <strong>Reactor Protection System Actuation While the Reactor Was Shutdown</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2016, at 0404, a Reactor Protection System (RPS) actuation occurred due to a valid scram discharge volume high water level signal. This actuation was the result of a Redundant Reactivity Control System (RRCS) Alternate Rod Insertion (ARI) signal that was inadvertently generated during testing. The reactor was in cold shutdown at the time of the RPS actuation, with all control rods inserted. The Reactor Coolant System (RCS) pressure was 830 psig to support excess flow check valve testing, and shutdown cooling was removed from service. When the RRCS/ARI actuated, the B reactor recirculation pump tripped as expected, and the scram air header depressurized as expected. The depressurization of the scram air header is a design feature of the ARI. The ARI signal established the control rod drive (CRD) system scram flow path. This resulted in a high water level in the scram discharge volume (SDV), an expected response. High water level in the scram discharge volume is an actuation signal for the RPS. <br /><br /> This is a condition reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of a listed system. The cause of the RRCS/ARI actuation is inadequate procedural guidance which resulted in a personnel error associated with partial procedure performance.
3542016006 | Hope Creek | 11/09/2016 | 05/04/2017 | ML17124A40 | <strong>Mode Change Without B Channel Reactor Level Instrumentation Operable</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2016, at 0420 with the Hope Creek reactor in Operational Condition 2, Startup, the B channel reactor level instrumentation was found to be inoperable. The inoperable instrumentation was discovered as reactor level was being lowered into the normal band in preparation for plant startup. Hope Creek had made a mode change from Operational Condition 4, Cold Shutdown, to Operation Condition 2, Startup, on November 9, 2016, at 0317, approximately 1 hour prior to discovering the inoperable instrumentation. <br /><br /> The B Channel reactor level instrumentation is required to be operable in order to enter Operational Condition 2 to support the B division of the Reactor Protection System (RPS), the Emergency Core Cooling Systems (ECCS), and the Primary Containment Isolation System (PCIS). The cause was determined to be an improperly filled reference leg for the B channel reactor level instrumentation. This report is being made under 10 CFR 50.73(a)(2)(i)(B), as a condition which was prohibited by the plant's Technical Specifications.
3642016001 | Farley 2 | 05/11/2016 | 07/05/2016 | ML16187A38 | <strong>Manual Reactor Trip due to High Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On 5/11/2016 at 0653 CDT, with Unit 2 (U2) at 29 percent power, the Hi-Hi Steam Generator (SG) setpoint was reached. This caused the main feedwater valves to isolate, the running main feedwater pumps to trip, automatic start of the Motor Driven Auxiliary Feed Pumps, and the main turbine to trip automatically. The reactor was manually tripped per procedure. This event is reportable as required by 10 CFR 50.73(a)(2)(iv)(A) due to a manual actuation of the Reactor Protection System and the automatic actuation of the Auxiliary Feedwater system. <br /><br /> The cause of the manual reactor trip was determined to be inadequate control of the feedwater system, leading to an overfilling of the Steam Generators. Corrective actions included additional training provided to the startup control room team on manipulations that affect the feedwater system. Also, more specific guidance on feedwater system operation and control during Startup from Hot Standby to Power Operations will also be incorporated into operating procedures.
3662016001 | Hatch 2 | 04/13/2016 | 06/08/2016 | ML16160A24 | <strong>2C EDG Fuel Oil Relief Valve Leakage Caused Train Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 03/17/2016, with Unit 2 at 100 percent rated thermal power (RTP), a fuel oil leak was observed at the inlet to the fuel oil relief valve during the performance of the 2C Emergency Diesel Generator (EDG) semi-annual surveillance. The 2C EDG was declared inoperable until the relief valve was replaced. Investigation revealed that the leak was due to a through wall indication in the threaded area of the relief valve. Inspection indicated that the failure was consistent with flaws observed in cases of fatigue failures. Site analysis of the failure provided reasonable assurance of historic operability; however a vendor was engaged to perform an independent review with a detailed seismic model of the system. <br /><br /> On 4/13/2016, the vendor analysis indicated that a seismic event could cause the degraded fuel oil relief valve to adversely affect EDG operation. The analysis concluded that although the 2C EDG could have met its 7-day mission time with the existing leakage rate, a design basis earthquake could reduce the ability of the diesel to maintain the minimum fuel header pressure and sufficient amount of fuel for 7 days. Thus the seismic qualification of the 2C EDG was degraded, but the safety function of the emergency AC system would only be challenged under certain circumstances with a seismic event. <br /><br /> Corrective actions will establish periodic replacement of similar fuel oil relief valves on the EDGs.
3662016002 | Hatch 2 | 05/23/2016 | 07/14/2016 | ML16196A35 | <strong>Group I Isolation Received During Turbine Testing</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2016, at 1009 EDT, while personnel were performing turbine testing with Unit 2 offline for planned maintenance, an event resulted in the actuation of containment isolation valves in more than one system. In response to this unexpected signal, 2B21-F016 (Steam Line Drain Line Inboard Isolation Valve), 2B21-F019 (Steam Line Drain Line Outboard Isolation Valve), and 2B31-F019 (Reactor Water Sample Inboard Isolation Valve) went closed, all of which are primary containment isolation valves actuated by Group I Isolation. The Group I Isolation signal initiated based on low condenser vacuum during the turbine testing procedure, a valid condition for actuation that was expected to have been bypassed in the logic during the performance of this procedure. Inadequate procedure usage caused these systems to actuate in a way that was not part of the planned evolution. Although the Unit was shut down when this signal was received, and primary containment isolation was not required to mitigate the consequences of an event, this isolation signal has been determined to have been valid due to the initiation in response to actual plant conditions or parameters which satisfy the requirements for initiation of the system.<br /><br /> As a corrective action, the operating procedure will be revised to clarify the required conditions to perform Turbine Trip Testing.
3662016003 | Hatch 2 | 08/18/2016 | 10/13/2016 | ML16287A78 | <strong>2C Emergency Diesel Generator Inoperable due to Low Lube Oil Pressure</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2016 at 1006, while performing the monthly Emergency Diesel Generator (EDG) surveillance, the 2C EDG tripped on low lube oil pressure. The station entered a 72 hour Required Action Statement (RAS) for Unit 2 Limiting Condition of Operation (LCO) 3.8.1.b. The other four EDGs were successfully started for surveillance testing in accordance with Tech Specs to preclude a common cause failure mode. Further inspections were performed and the cross drive shaft between the pump flexible drive gear and the engine driven lube oil pump was found sheared. The cross drive shaft assembly was replaced and the 2C EDG was declared operable on August 24, 2016 after subsequent functional and post maintenance testing. <br /><br /> Investigations into the failure revealed that the initial cross drive shaft fracture existed prior to the monthly surveillance performed on August 18. The time frame for which the 2C EDG was able to perform its safety function for its 7-day mission time is indeterminable due to the failure mechanism of the cross drive shaft. A loss of safety function is being reported due to the 2C EDG being potentially inoperable during a time in which either the 1B swing EDG was inhibited from Unit 2 or the 1B/2A EDG was inoperable due to normal equipment maintenance and testing. Additionally, this report constitutes a Part 21 notification per 10 CFR 21.21(d).
3662016004 | Hatch 2 | 11/07/2016 | 01/04/2017 | ML17004A23 | <strong>Condition Prohibited by Technical Specifications due to Inoperable PCIV</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2016 at 2355 EST, while performing a main control board panel walkdown, it was discovered that the High Pressure Coolant Injection (HPCI) vacuum breaker motor operated isolation valve 2E41F111 had been left in the open position with its breaker turned off. Upon further review of the associated tagout, it was determined that this primary containment isolation valve (PCIV) had been in this inoperable configuration greater than allowed LCO time of 4 hours. The 2E41F111 was then declared inoperable and the 2E41F104 redundant penetration motor operated isolation valve was closed and deactivated to meet the required action per Unit 2 Technical Specifications (TS) LCO 3.6.1.3, Condition A.1. <br /><br /> The inoperable as-found condition of the 2E41F111 PCIV was due to supervision failing to recognize that the tagout preparer did not possess the proper skill set to perform the task. Although the 2E41F111 was left in the open position with its breaker turned off, the manual HPCI turbine exhaust valve 2E41F021 was tagged in the closed position per the tagout instructions. Therefore, closure of the 2E41F021 ensured the affected piping was isolated such that primary containment boundary functions were maintained. Expectations were instituted to ensure individuals assigned with preparing tagouts associated with TS equipment are trained on the basics of TS.
3682016001 | Arkansas 2 | 09/16/2016 | 04/27/2018 | ML18117A49 | <strong>Failure of One Emergency Diesel Generator and Subsequent Required Shutdown of Arkansas Nuclear One, Unit 2</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2016, Arkansas Nuclear One, Unit 2, initiated a plant shutdown due to the inability to restore one of the Emergency Diesel Generators (EDGs) to an operable status prior to exceeding the Limited Condition Operation action time. It was determined the EDG was inoperable due to the lack of sufficient lubrication in the inboard generator bearing leading to bearing failure. The lack of lubrication was determined to be caused by the failure to establish adequate governance to ensure safety-related, non-complex, work order instructions were written to maintain configuration of the EDG sight glass scribe mark. It was further determined that the insufficient bearing oil level condition had existed since the performance of maintenance activities in June of 2016. The corrective action plan addresses the root cause, contributing cause, extent of condition, and extent of cause.
3692016001 | McGuire 1 | 03/22/2016 | 07/22/2016 | ML16208A06 | <strong>Degraded Condition due to Rejectable Flaw on U1 Charging Line</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2016, while Unit 1 was in end of cycle (EOC) refueling outage 1EOC24 (Mode 5), a manual ultrasonic (UT) examination of the Chemical and Volume Control System (NV), Charging Line to the 1A Reactor Coolant System (NC) cold leg confirmed a previously identified circumferential indication associated with weld 1NC1F-1374. The current examination results had shown that the indication had changed since the previous examination during 1EOC23 and concluded that the indication no longer met American Society of Mechanical Engineers (ASME) Section XI Code requirements. This condition is reportable under 10CFR50.73(a)(2)(ii)(A) as a degraded condition. <br /><br /> A specific cause for the condition could not be determined. A metallurgical examination concluded that the cause of the UT result could have been influenced by pre-existing welds associated with a legacy modification.<br /><br /> The affected NV piping on Unit 1 was replaced during refueling outage 1EOC24.
3732016001 | LaSalle 1, LaSalle 2 | 02/10/2016 | 04/11/2016 | ML16102A14 | <strong>Secondary Containment Inoperable due to Reactor Building Ventilation Damper Failure</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2016, Unit 1 was in Mode 1 at 91 percent power and Unit 2 was in Mode 1 at 100 percent power. At 2207 hours CST, it was reported that the Unit 1 reactor building ventilation exhaust damper 1VR05YA failed and began to show dual indication. As a result, the Unit 1 reactor building ventilation exhaust fans tripped off, causing a positive reactor building differential pressure on both units. The damper and secondary containment were declared inoperable, and Technical Specification 3.6.4.1 Required Action A.1 was entered on both units to restore secondary containment to operable status within four hours. In addition, Technical Specification 3.6.4.2 Required Action A.1 was entered to isolate the penetration with one closed or deactivated automatic valve within eight hours. <br /><br /> The cause was an intermittent failure of a solenoid on one of the two half damper blades on the 1VR05YA exhaust isolation damper. This led to the exhaust damper blade half intermittently changing its position, which resulted in secondary containment pressure going positive. The solenoid valves on both halves of the 1VR05YA exhaust damper were replaced, and the failed solenoid was sent to a vendor for failure analysis.
3742016001 | LaSalle 2 | 02/17/2016 | 04/18/2016 | ML16109A21 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2016, Unit 2 was in Mode 1 at 100 percent power and Unit 1 was in Mode 5 for refueling outage L1R16 with no fuel movements or operations with the potential to drain the reactor vessel (OPDRV) in progress. At 1035 hours CST, both air-lock doors of the Unit 2 Chemistry Lab corridor / Unit 2 Reactor Building interlock were open at the same time for approximately five seconds. While both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 to verify one secondary containment access door in each access opening is closed was not met for Unit 2. Secondary containment was declared inoperable for the period of time that both interlock doors were open. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to OPERABLE status within four hours was entered and exited. <br /><br /> The cause was failure of the relays on the door controller circuit card. The controller circuit card was replaced, which restored the interlock functionality. Corrective actions include determining the cause of vendor quality issues with the controller circuit card relays and procurement of a more reliable controller circuit card following the identification of the cause of the relay failures from vendor analysis.
3822016001 | Waterford 3 | 07/03/2016 | 09/01/2016 | ML16245A92 | <strong>Incorrect Core Protection Calculator Addressable Constant Entered Because of Inadequate Procedure Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 3, 2016, the Core Protection Calculator (CPC) Tilt Exceeded alarm was received. This required the Azimuthal Power Tilt values to be adjusted for the actual condition. During the adjustment of the Type 1 addressable constants, it was discovered that the CPC Tilt value for CPC C, PID 063, had been improperly inputted following a failure and restoration of the CPC C on July 1, 2016. The value entered was 1.0064 when the value should have been 1.0102. The inputted values were taken from the last known functional printout in the CPC C book but were not verified against the addressable constant change log and did not account for any subsequent changes made by operations. The value entered was lower than intended, and because of this low value, there were several times over the next 2 days that actual Azimuthal Power Tilt was greater than the value assumed by CPC C. This should have resulted in entry into TS 3.2.3.a. The plant operated for approximately 29 hours outside of the allowed TS actions per TS 3.3.1 and 3.2.3.a. This also resulted in CPC C Local Power Density (LPD) and Departure from Nucleate Boiling Ration (DNBR) calculating a non-conservative value. <br /><br /> The Apparent Cause was that the CPC Functional Test procedure contains vague guidance on how to verify inputted addressable constants are correct. This resulted in this condition by implying to personnel that only using the CPC printed page of addressable constants to verify inputted addressable constants was correct and did not also prompt use of the CPC change log. Corrective actions include revising the procedure to provide specific guidance on how to verify inputted addressable constants are correct.
3822016002 | Waterford 3 | 08/12/2016 | 11/30/2016 | ML16335A41 | <strong>Both Trains of Essential Services Chilled Water Inoperable due to Failing to Maintain Exiting Chilled Water Temperature in Specification Resulting in Event or Condition That Could Have Prevented Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2016, at 1704 CDT, the shift operating crew noted that Essential Chiller B outlet temperature exceeded the allowed maximum Technical Specification (TS) Surveillance Requirement (SR) 4.7.12.1.b limit of 42 degrees Fahrenheit (deg F) and Essential Services Chilled Water Loop B (Loop B) was declared inoperable. Essential Services Chilled Water Loop A (Loop A) had previously been declared inoperable on August 11, 2016. The shift operating crew entered TS 3.0.3 due to both trains of Essential Services Chilled Water being inoperable. Essential Chiller AB was subsequently aligned to Loop B and TS 3.0.3 was exited on August 12, 2016, at 1802, when outlet temperature was verified to be less than or equal to 42 deg F. <br /><br /> The Essential Chiller A elevated temperature was due to a failed capacity control module. The apparent cause was inadequate preventative maintenance (PM) strategy. Corrective action to replace the module and return Essential Chiller A to service is complete. In addition, the PM to replace the module will be performed more frequently. The Essential Chiller B elevated chilled water temperature was due to incorrect guide vane setup. The incorrect setup resulted in adjusting the thermostat too high. The high thermostat setting prevented the chiller from maintaining outlet temperature less than 42 deg F following a large demand increase. The apparent cause was that inadequate guidance exists for guide vane actuator linkage setup. Corrective actions to properly set up the linkage, set the thermostat, return Essential Chiller B to service, develop actuator installation instructions, and revise post-maintenance tests are complete. Additional actions include establishing new maintenance and troubleshooting procedures.
3872016001 | Susquehanna 1, Susquehanna 2 | 02/22/2016 | 04/18/2016 | ML16109A23 | <strong>Secondary Containment Declared Inoperable due to an Airlock Doors Open due to Random Occurrence</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2016 at approximately 1345, a contract employee leaving the Unit 1 Reactor Building swiped his keycard and received a green light to enter the airlock. Upon opening the airlock door, he discovered two Susquehanna employees entering the airlock from the opposite side. The statement from the Susquehanna employees indicates that the green light to enter the airlock was observed. They were entering the airlock to traverse to the Unit 1 Reactor Building when the door on the Unit 1 Reactor Building side opened. After this incident, the airlock indication was tested and all equipment checked satisfactorily. <br /><br /> With both airlock doors open simultaneously, Secondary Containment was briefly inoperable due to failure to meet Surveillance Requirement (SR) 3.6.4.1.3. <br /><br /> This event was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented fulfillment of a safety function (EN 51750). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C).<br /><br /> The cause of the event was determined to be random occurrence. There were no corrective actions required to address the cause. Although human performance issues were not involved, actions have been taken to improve human performance associated with airlock door use.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016002 | Susquehanna 1, Susquehanna 2 | 03/02/2016 | 04/18/2016 | ML16109A25 | <strong>Secondary Containment Declared Inoperable due to an Airlock Doors Open due to Random Occurrence</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2016 at approximately 1330, contract employees leaving the Unit 2 Reactor Building verified a green light, but received an alarm when the door was about one quarter of the way open. The contract employees identified that workers had opened the door on the other side of the airlock. The workers on the other side were contract employees who indicated the green light was verified prior to the individual and crew entering the airlock. The airlock door on the other side opened as they were entering. After this incident, the airlock indication was tested and all equipment checked satisfactorily <br /><br /> With both airlock doors open simultaneously, Secondary Containment was briefly inoperable due to failure to meet Surveillance Requirement (SR) 3.6.4.1.3. <br /><br /> This event was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented fulfillment of a safety function (EN 51750). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C).<br /><br /> The cause of the event was determined to be random occurrence. There were no corrective actions required to address the cause. Although human performance issues were not involved, actions have been taken to improve human performance associated with airlock door use. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016003 | Susquehanna 1, Susquehanna 2 | 03/08/2016 | 05/06/2016 | ML16127A08 | <strong>Unit 2 Zone 3 HVAC Unable to Maintain Zone 3 Differential Pressure Greater than 0.25 in WG</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2016 at 0232 hours Secondary Containment Zone Ill ventilation differential pressure lowered to 0.16" inch of vacuum water gauge (WG) when securing Unit 1 Zone Ill ventilation for a routine preventative maintenance activity. Required differential pressure per Surveillance (SR) 3.6.4.1.1 could not be maintained in the intended alignment and Technical Specification (TS) 3.6.4.1 was entered for Unit 1 and Unit 2. Zone Ill ventilation was restored to the original alignment and Zone Ill differential pressure recovered to > 0.25" WG at 0335 hours. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(v)(C) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as an event or condition that could have prevented fulfillment of a safety function. There is no redundant Susquehanna Secondary Containment System. <br /><br /> There were no actual or potential consequences to the health and safety of the public as a result of this event. An engineering evaluation concludes no safety system functional failure (SSFF) actually occurred as a result of this event. <br /><br /> The apparent cause is less than adequate design of the outside air dampers. The corrective action for this condition is an engineering change that allows the closing of the upper and lower damper sections to be operated separately for the reactor building HVAC supply systems.
3872016004 | Susquehanna 1, Susquehanna 2 | 03/14/2016 | 05/10/2016 | ML16131A73 | <strong>Momentary Loss of Secondary Containment due to Both Airlock Doors on Elevation 779 of the Unit 2 Reactor Building being Opened at the Same Time</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2016, an individual was attempting to enter the Unit 2 Reactor Building airlock on Elevation 779 through Door 115R, when the opposite airlock door (Door 602) opened due to air pressure/vacuum created when Door 115R was opened. The airlock alarmed at 0925 hours due to both airlock doors (Door 602 and 115R) being open at the same time. The individual immediately closed Door 115R. An inspection of Door 602 was performed which identified that the strike plate on the door was not maintaining the door latched. Door 115R was maintained closed while Door 602 was being repaired. Door 602 was repaired by tightening the screws of the cover plate on the door's mortise. Operations declared the door to be operable at 0957 hours on March 14, 2016. <br /><br /> In accordance with 10 CFR 50.73(a)(2)(v)(C), this LER is being submitted for an event or condition that could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material. No entry into Technical Specification 3.6.4.1, Action Statement A, was made because at the time the Control Room was made aware of the event, both airlock doors were closed and Secondary Containment had been re-established.<br /><br /> The direct cause of the event was due to a loose cover plate on the door's mortise. The latch on Door 602 was repaired and the door was declared operable. There were no actual consequences to the health and safety of the public as a result of this event.
3872016005 | Susquehanna 1, Susquehanna 2 | 03/15/2016 | 05/16/2016 | ML16137A04 | <strong>Secondary Containment Declared Inoperable Due to Airlock Doors Open Due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2016 at approximately 1020 hours, a Susquehanna employee was entering the Unit 2 Reactor Building to complete fire watch rounds. Other individuals were following the fire watch employee through the airlock. The fire watch employee failed to wait until all individuals were in the airlock and the entry door closed before opening the exit door. The fire watch rounds are on a timeline and, with the outage traffic, the fire watch individual felt time pressure. <br /><br /> With both airlock doors open simultaneously, Secondary Containment was briefly inoperable due to failure to meet Surveillance Requirement (SR) 3.6.4.1.3. <br /><br /> The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C).<br /><br /> The cause of the event was determined to be a human performance error related to perceived time pressure. The individual was coached and general actions have been taken to improve human performance associated with airlock door use. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016006 | Susquehanna 1 | 03/16/2016 | 05/10/2016 | ML16131A70 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this Licensee Event Report (LER) was an expected condition, which was the result of planned activities in support of a routine refueling outage. As described in the LER, the U. S. Nuclear Regulatory Commission (NRC) provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). <br /><br /> Between 3/16/2016 and 4/11/2016, Susquehanna Steam Electric Station (SSES) performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities on Unit 1 while in Mode 5 without an operable secondary containment, as expected and allowed by the enforcement guidance. Although NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 allows the implementation of interim actions as an alternative to full compliance, this condition is still considered a condition prohibited by TS 3.6.4.1. The OPDRV activities were planned activities that were completed under the guidance of plant procedures and are considered to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request will be submitted following NRC approval of the Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue.
3872016007 | Susquehanna 1, Susquehanna 2 | 03/05/2016 | 05/03/2016 | ML16125A02 | <strong>Inoperability of Swing Bus Transfer Switch due to Deformed Bolt on Linkage</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2016 during surveillance testing, Automatic Transfer Switch (ATS), 1ATS229, failed to close in on the alternate supply resulting in a loss of the Division 2 Class 1E Engineered Safeguards System (ESS) 480V Motor Control Center (MCC) 113229 and entry into Technical Specifications 3.3.3.1, 3.5.1, and 3.6.1.3. Based on the cause of the failure, Susquehanna believes that there is firm evidence that the transfer switch would have failed on its next actuation following testing on February 5, 2016. Based on this conclusion, the condition existed for a period longer than allowed by Technical Specifications. As a result, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Susquehanna also determined that work associated with the Division 1 transfer switch (1ATS219) was performed while the Division 2 switch was unknowingly inoperable resulting in simultaneous inoperability of both divisions. Since both divisions were inoperable for a period of time between February 5, 2016 and March 5, 2016, this is also considered a condition that could have prevented fulfillment of a safety function and is reportable in accordance with 10 CFR (a)(2)(v)(D). <br /><br /> The direct cause was determined to be a deformed bolt on the upper linkage. The apparent cause was the upper linkage rod being too long causing the deformation of the bolt. Corrective actions include revising the preventive maintenance activities for the transfer switch. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016008 | Susquehanna 1, Susquehanna 2 | 04/01/2016 | 05/19/2016 | ML16144A02 | <strong>Inoperability of Diesel Generator due to Misalignment of MOC Switch Contacts due to Inadequate Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2016 at 20:24, Unit 2 entered Technical Specification 3.8.1 due to the A Diesel Generator (DG) being inoperable due to misaligned contacts on a Mechanism-Operated Cell (MOC) switch resulting in Fan 1V222A starting without a time delay. Based upon review of the history and cause, the condition likely existed since the supply breaker was replaced on July 19, 2010. The A DG was still able to perform its intended safety function; however, since the condition results in inability to meet Surveillance Requirement 3.8.1.18, the A DG must be considered inoperable during periods when 1V222A would have been available to start (without a time delay). As a result, this event is reportable as a condition prohibited by Technical Specifications, in accordance with 10CFR50.73(a)(2)(i)(B), since the inoperability is assumed to have existed for a period of time greater than allowed by the Technical Specifications. A review of historical information for the last three years identified instances in which one of the other DGs (B, C, or D) was inoperable. Based on this information, this condition is also reportable as a condition that could have prevented fulfillment of a safety function in accordance with 10CFR50.73(a)(2)(v)(D). <br /><br /> The direct cause of the MOC switch contacts not aligning properly was mis-adjustment of the MOC switch linkage. The apparent cause of the MOC switch contacts not aligning properly is inadequate post maintenance testing (PMT) for the breaker swap because PMT did not check MOC switch contact alignment. Procedures will be revised to include visual inspection to ensure the MOC switch contacts are properly aligned during post maintenance testing. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016009 | Susquehanna 1 | 03/31/2016 | 05/26/2016 | ML16147A43 | <strong>Valid Primary Containment Isolation Actuation During Local Leak Rate Testing due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2016 at approximately 06:03, while performing lineups for Local Leak Rate Testing (LLRT), the Control Room received a Division two (2) Primary Containment Isolation System (PCIS) alarm along with a Division two (2) Heating Ventilation Air Conditioning (HVAC) isolation, and Standby Gas Treatment (SBGT) and Control Room Emergency Outside Air Supply System (CREOASS) initiation. This was shortly followed by the Division one (1) Primary Containment Isolation System (PCIS) alarm along with a Division one (1) Heating Ventilation Air Conditioning (HVAC) isolation, and Standby Gas Treatment (SBGT) and Control Room Emergency Outside Air Supply System (CREOASS) initiation. <br /><br /> The valid actuation signal was the result of the performance of four (4) LLRT procedures concurrently for four (4) separate drywell pressure instruments. These instruments are divisional with each powered by a different channel. Placing each in "TEST" mode, resulted in bringing both the Division one (1) and Division two (2) isolation logic. The cause of the valid actuation signal was less than adequate procedure use and adherence by Operations staff members. Corrective action included coaching and remediation of an individual involved in confirming the position of the test switch, communication to the Operations organization and revision to the LLRT procedures.<br /><br /> There was no operational impact as a result of this this event due to the plant being in Mode 5. This event resulted in a eight (8) hour Emergency Notification System (ENS) communication pursuant to 10 CFR 50.72(b)(3)(iv)(A). This Licensee Event Report (LER) is being communicated pursuant to 10 CFR 50.73(a)(2)(iv)(A).
3872016010 | Susquehanna 1, Susquehanna 2 | 04/06/2016 | 05/31/2016 | ML16153A19 | <strong>Secondary Containment Declared Inoperable due to Airlock Doors Open due to Medical Emergency</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2016 at 13:30, a medical emergency on the refuel floor (Elevation 818) required having both doors open at the same time for multiple airlocks along the travel path required to move the affected individual from the refuel floor to a location outside the reactor building to allow transport to a local hospital by ambulance. The evolution was performed under the cognizance of the Field Unit Supervisor (FUS) and the Control Room. The Control Room declared Secondary Containment inoperable and entered the applicable Technical Specification (TS) 3.6.4.1 condition for Unit 1 and Unit 2 during the time when both doors in a required airlock were open. <br /><br /> This event was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) in EN 51851. The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of the event was a medical emergency on the refuel floor which required both secondary containment airlock doors to be open at the same time in several airlocks along the travel path to transport the individual out of the Reactor Building and to a local hospital. Since the event was due to a medical emergency, no corrective actions are required. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016011 | Susquehanna 1 | 03/17/2016 | 08/05/2016 | ML16218A08 | <strong>Valve Inoperability for a Period Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 17 and 19, 2016, two safety related check valves would not properly close during surveillance testing. After investigation, it was discovered that interference between the hinge arm and internal seat ring was preventing the valves from closing. This condition first presented itself in 2014 during the same surveillance, but was believed to be resolved. <br /><br /> No immediate reporting requirements are associated with this event. This Licensee Event Report (LER) is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). <br /><br /> The direct cause of the event was determined to be interference between the hinge arm and internal seat ring. The apparent cause of this event was determined to be a material deficiency introduced at the time of manufacture. A causal factor of less than adequate receipt inspection was identified. Completed corrective actions included rework of the valves. An extent of condition evaluation determined the equivalent valves on Unit 2 are not affected.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016012 | Susquehanna 1, Susquehanna 2 | 03/29/2016 | 05/26/2016 | ML16147A07 | <strong>Secondary Containment declared inoperable due to loss of differential pressure as a result of a solenoid failure.</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2016 at approximately 2256 hours, Susquehanna Steam Electric Station (SSES) Unit 2 Secondary Containment Zone II ventilation differential pressure (dP) was not maintained above the Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.1 required vacuum of 0.25 inches of water gauge (in. w.g.) with respect to outside atmosphere due to closure of reactor building exhaust fan discharge damper and subsequent trip of the reactor building exhaust fan. The Unit 1 and Unit 2 Secondary Containment systems were declared inoperable and Action Statement for TS 3.6.4.1 was entered. Secondary Containment dP was restored to greater than 0.25 in. w.g. at approximately 2321 hours, following the start of the "A" reactor building exhaust fan. Further investigation determined the damper closure was the result of a solenoid valve failure. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(v)(C) as an event that could have prevented fulfillment of a safety function. SSES has no redundant Secondary Containment System. <br /><br /> Corrective actions for this event include revision of the preventive maintenance (PM) scope for Reactor Building Heating Ventilation Air Conditioning (HVAC) solenoid valves and evaluation of a more robust solenoid valve for Reactor Building HVAC system.
3872016013 | Susquehanna 1, Susquehanna 2 | 04/12/2016 | 06/09/2016 | ML16161A47 | <strong>Secondary Containment Declared Inoperable due to Simultaneous Opening of Double Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2016 at approximately 2020 hours, a Susquehanna employee was in the process of exiting the Unit 1 Reactor Building via a double door airlock leading to the Unit 1 Turbine Building. The individual inserted his badge into a security related badge reader to access the airlock and received a green light. While opening the Reactor Building side door, employees from the Turbine Building side entered the airlock. The airlock air horn alarm activated as designed since both doors were simultaneously opened. The individual did not observe the airlock indication light prior to entry, which is designed to indicate red while the airlock is being utilized. <br /><br /> With both airlock doors open simultaneously during a period in which Secondary Containment was required, Surveillance Requirement (SR) 3.6.4.1.3 was not met. <br /><br /> This Licensee Event Report (LER) is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition which could have prevented the fulfillment of a safety function. <br /><br /> The direct cause of the event was determined to be less than adequate situational awareness, since the individual stated they did not confirm the airlock was acceptable to enter via the airlock door status light. The individual was coached and reinforcement of the expectations related to Secondary Containment Boundary doors was provided in work group meetings to improve human performance associated with airlock door use. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016014 | Susquehanna 1, Susquehanna 2 | 04/13/2016 | 06/09/2016 | ML16161A47 | <strong>Secondary Containment Declared Inoperable due to Airlock Doors Open due to a Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2016 at approximately 21:15, a supplemental Radiation Protection Technician (RPT) attempting to enter the Unit 1 Reactor Building (RB1) opened the inner (RB1 side) airlock door without ensuring the outer door from the Unit 1 Turbine Building (TB1) was closed behind him. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. <br /><br /> The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The direct cause of the event was a lack of situational awareness that led to the failure of the RPT to notice the work crew entering the airlock behind him, as well as his failure to ensure the outer airlock door was fully closed prior to opening the inner door. <br /><br /> Corrective actions included coaching the RPT and reinforcing expectations for passing through airlocks during RP shift crew briefings. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016015 | Susquehanna 1, Susquehanna 2 | 04/22/2016 | 06/15/2016 | ML16167A30 | <strong>Secondary Containment Declared Inoperable due to Airlock Doors Open due to a Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2016 at approximately 11:30, a Nuclear Plant Operator (NPO) was entering a Unit 1 Reactor Building access door and noticed another worker entering the airlock door behind him with a cart. The NPO stated that he was trying to be helpful and opened the reactor building side (inner) door. The NPO stated that they did not notice that the turbine building side (outer) door was still open. Both doors were open at the same time for approximately one second. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. <br /><br /> The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The direct cause of the event was less than adequate verification practices to ensure compliance with Secondary Containment door requirements. <br /><br /> Corrective actions include holding the individual accountable for less than adequate verification practices. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016016 | Susquehanna 1, Susquehanna 2 | 11/16/2016 | 01/12/2017 | ML17012A33 | <strong>Bus Synchronizing Select Hand Switch Failure due to Less Than Adequate Life Cycle Management</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2016 at 10:45, Unit 1 and 2 entered Technical Specification (TS) 3.8.1 Conditions B, C, D, E, and G and TS 3.0.3 due to failure of a bus synchronizing select hand switch. <br /><br /> The failed switch prevented manual transfer between electrical sources to the Emergency Safety Switchgear (ESS) buses resulting in both offsite sources and all four diesel generators (D/Gs) being declared inoperable due to failure to meet Surveillance Requirement (SR) 3.8.1.8 and SR 3.8.1.16. This condition was reported as a condition that could have prevented fulfillment of a safety function in accordance with 10 CFR 50.72(b)(3)(v)(A), (B), (C), and (D) (EN 52369). The condition also requires this Licensee Event Report (LER) in accordance with the corresponding 10 CFR 50.73 requirements. <br /><br /> The direct cause was mechanical failure of an internal subcomponent of the bus synchronizing select hand switch. The apparent cause was less than adequate life cycle management. The failed switch was replaced as a corrective action. Replacement of other synchronization selector switches within the extent of condition will also be completed. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016018 | Susquehanna 1 | 04/22/2016 | 03/03/2017 | ML17062A83 | <strong>Inoperability of RCIC due to an Oil Leak Caused by an Unidentified Gasket Issue</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2016 at approximately 14:00, a two to three drop per second leak from the Reactor Core Isolation Cooling (RCIC) Turbine Lube Oil Filter, 1F212B, was identified which was subsequently determined to make RCIC inoperable. Unit 1 had entered Mode 1 at approximately 11:25 on April 22, 2016, and RCIC was considered to have been inoperable prior to the transition to Mode 1. As a result, the condition was considered a violation of Technical Specification (TS) 3.0.4 and reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The cause of the leak was determined to be an unidentified gasket issue. Corrective actions included repair of the oil leak and replacement of both filter elements and all gaskets.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016019 | Susquehanna 1 | 06/06/2016 | 08/03/2016 | ML16216A37 | <strong>Pressure Boundary Leakage from an Inadequate Weld Repair in Small Bore Pump Seal Vent Piping</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2016, at 0556 hours during a drywell entry, a leak was reported on the Unit 1 B Reactor Recirculation Pump Lower Seal Vent Line. The leak was identified at the inboard pipe-to-union weld and required replacement prior to returning to service. The affected piping weld is for 3/4-inch piping, Quality Class Q (ASME Class 2) and is part of the Reactor Coolant Pressure Boundary. <br /><br /> The cause of the event was determined to be the result of a crack in the pipe-to-union weld on the pump side of the connection. The crack was determined to have initiated and propagated as a result of an undetectable lack of fusion at the weld root along with an unrecognized cyclic or vibratory loading. A complete replacement of the pump seal cooler assembly to remove the welded connection was completed prior to the restart of Unit 1.<br /><br /> The condition was immediately reported as a plant shutdown required by Technical Specifications (TS) pursuant to 10 CFR 50.72(b)(2)(i) and degraded condition pursuant to 10 CFR 50.72(b)(3)(ii)(A) (EN 51983). This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(A), 10 CFR 50.73(a)(2)(i)(A), and 10 CFR 50.73(a)(2)(i)(B), as a condition resulting in a principal safety barrier degradation, plant shutdown required by Technical Specifications, and as a condition prohibited by Technical Specifications.
3872016020 | Susquehanna 1 | 06/08/2016 | 08/03/2016 | ML16216A37 | <strong>Reactor Coolant Pressure Boundary Leakage at LPRM Housing as a Result of IGSCC</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2016 at approximately 02:26, while performing under vessel inspections, a Reactor Coolant Pressure Boundary (RCPB) leak was found at the Local Power Range Monitor (LPRM) 24-09 housing above the housing flange, on the LPRM housing tube. The leakage was determined to be non-isolable from the reactor vessel.<br /><br /> The cause of the RCPB leakage was determined to be lntergranular Stress Corrosion Cracking (IGSCC). Corrective actions to repair the leak have been completed. In addition, a visual inspection was performed on all the Unit 1 LPRM, Intermediate Range Monitor (IRM), and Source Range Monitor (SRM) In-core monitor housings and no further issues were identified. <br /><br /> There was no operational impact as a result of this event due to the plant being in Mode 4 at the time of discovery. This event resulted in an eight (8) hour Emergency Notification System (ENS) communication pursuant to 10 CFR 50.72(b)(3)(ii)(A). This Licensee Event Report (LER) is being communicated pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(ii)(A) as a condition prohibited by Technical Specifications and as degradation of a principal safety barrier.
3872016021 | Susquehanna 1, Susquehanna 2 | 06/22/2016 | 08/17/2016 | ML16230A12 | <strong>Secondary Containment Declared Inoperable due to Airlock Doors Open due to a Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2016 at approximately 15:01, an engineer passing through a Unit 1 Reactor Building airlock inadvertently unlatched an outside airlock door, resulting in an airlock alarm indicating both doors were open simultaneously. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. <br /><br /> The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C).<br /><br /> The cause of the event was the individual inadvertently utilized their key card for the wrong door and when opening the intended door, differential pressure caused a momentary violation of secondary containment. <br /><br /> Corrective actions included coaching the engineer and reinforcing to all Engineering personnel the expectations for passing through airlocks. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016022 | Susquehanna 1, Susquehanna 2 | 10/04/2016 | 12/01/2016 | ML16336A45 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2016 at approximately 0318, the Operations Shift Manager determined that a breach of Secondary Containment occurred due to a security officer opening door 571O while Airlock Door 813 was propped open. Airlock Door 813 was propped open for ongoing work. Secondary Containment was once again operable at the moment the security officer closed Door 571O. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of the event was less than adequate adherence to safety postings and barriers, specifically in regards to Secondary Containment boundaries. <br /><br /> Corrective actions included documented coaching of the security officer. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016023 | Susquehanna 1, Susquehanna 2 | 09/26/2016 | 11/21/2016 | ML16326A23 | <strong>Secondary Containment Declared Inoperable due to Airlock Doors Open due to a Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2016 at approximately 11:55, the Control Room was informed of an airlock violation on the Refuel Floor. This violation resulted when an escorted individual who was part of a group opened the airlock exit door while the remainder of the group was still entering the airlock. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. <br /><br /> The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of the event was less than adequate verification practices to ensure that Secondary Containment door requirements were utilized. <br /><br /> Corrective actions included coaching of the group of escorted individuals and the escorting individual. Additionally, direction for communication of airlock expectations will be added to plant escort expectations. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016024 | Susquehanna 1, Susquehanna 2 | 10/19/2016 | 12/14/2016 | ML16349A11 | <strong>Refuel Floor Radiation Exhaust Monitor Isolation Setpoint Above Technical Specification Limit due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2016, during performance of surveillance procedure SI-079-335, 24 Month Calibration of Refuel Floor High Exhaust Duct High Radiation Monitor Channel R-D12-1K615B, the as-found HiHi trip setpoint of the Unit 1 Refuel Floor High Exhaust Duct B Radiation Monitor was found at 36 mR/hr. This exceeds the Technical Specification 3.3.6.2, Secondary Containment Isolation Instrumentation and Technical Specification 3.3.7.1, Control Room Emergency Outside Air Supply (CREOAS) System Instrumentation, Allowable Value of <= 25 mR/hr. Based upon investigation, this condition was determined to have existed since prior to the previous 24 month calibration of the instrument on 11/15/14. <br /><br /> The cause of this condition was determined to be less than adequate use of Human Performance Tools, including Self-Checking, Verification Practices and Procedure Use and Adherence by the maintenance crew performing the surveillance on 11/15/14. As a result of not properly using these tools, the setpoint graph was mislabeled resulting in incorrect setpoint calculation. <br /><br /> This condition requires reporting in accordance with 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(v)(C) as a condition prohibited by Technical Specifications and as a condition that could have prevented fulfillment of a safety function. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872016025 | Susquehanna 1, Susquehanna 2 | 11/30/2016 | 01/26/2017 | ML17030A13 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2016 at approximately 0921, a Talen Security Officer attempted to exit the Unit 1 Air Lock via Security door 585 on elevation 676. A Talen Mechanical Maintenance employee knocked on the Turbine Building door to gain his attention. The Security Officer then stopped from proceeding into the Reactor Building and was allowing the Reactor Building door to close when the mechanic opened the Turbine Building air lock door without verifying a green light. This caused an alarm for a momentary breach of Secondary Containment. The mechanic then closed the door without proceeding into the airlock. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C).<br /><br /> The cause of the event was failure to follow station expectations when entering an airlock and less than adequate verification practices. <br /><br /> Corrective actions included documented coaching of the mechanic.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882016001 | Susquehanna 2, Susquehanna 1 | 03/29/2016 | 05/24/2016 | ML16145A12 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors Due to Degraded Latch Mechanism</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2016 at approximately 23:00, two employees leaving the Unit 2 Turbine Building entered the Turbine Building to Reactor Building airlock. Prior to opening the airlock door, employees verified a green light was present, indicating the opposite airlock door was closed. The first employee entered the airlock while the other employee held the Turbine building door. As the second employee entered into the airlock, the airlock alarm was heard. As this time, a rush of air was observed from the Reactor Building side of the airlock, forcing the door open (Door 120A). Both individuals quickly closed the doors. The individuals then proceeded through the Reactor Building door to the nearest phone and informed the Control Room of the event. Having both airlock doors momentarily open simultaneously, results in a potential loss of safety function and requires reporting under 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of this event was determined to be normal wear of the Door 120A (Reactor Building airlock door) door latch. Corrective actions to address this issue include repair of the door latch mechanism.
3882016002 | Susquehanna 2, Susquehanna 1 | 03/29/2016 | 05/26/2016 | ML16147A32 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors Due to Degraded Latch Mechanism</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2016 at approximately 23:13, an employee leaving the Unit 2 Turbine Building entered the Turbine Building to Reactor Building airlock. Prior to opening the airlock door, employee verified a green light was present, indicating the opposite airlock door was closed. The employee entered the airlock and the airlock alarm was heard. At this time, a rush of air was observed from the Reactor Building side of the airlock, forcing the door open (Door 120A). The individual quickly closed both doors. The individual then proceeded through the Reactor Building door to the nearest phone and informed the Control Room of the event. Having both airlock doors momentarily open simultaneously results in a potential loss of safety function and requires reporting under 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of this event was determined to be normal wear of the Door 120A (Reactor Building airlock door) door latch. Corrective actions to address this issue include repair of the door latch mechanism.
3882016003 | Susquehanna 2, Susquehanna 1 | 04/19/2016 | 06/17/2016 | ML16172A17 | <strong>Secondary Containment Inoperability due to Failure to Meet Surveillance Requirement 3.6.4.1.1</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2016, at 2159 hours, Secondary Containment became inoperable, requiring an action of Technical Specification (TS) 3.6.4.1 to restore the system to an operable status in four hours. The TS 3.6.4.1 Condition A for an inoperable Secondary Containment was entered because Reactor Building (RB) Zone II differential pressure (dP) was below the required TS limit of >/= 0.25 inches of vacuum water gauge (in. w.g.), which does not meet the Surveillance Requirement (SR) 3.6.4.1.1. The Zone II supply system outside air (intake) louver XD-27586 was then adjusted and the Zone II dP returned to a steady 0.29 in. w.g. of vacuum, which was above the required TS limit. The TS 3.6.4.1, Condition A for inoperable Secondary Containment was exited at 2222 hours. <br /><br /> The event was reported to the NRC on April 20, 2016 in accordance with 10 CFR 50.72(b)(3)(v)(C) under Event Notification 51872, for the loss of a safety function. There is no redundant Secondary Containment system. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C), for an event or condition that could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material. No actual consequences to the health and safety of the public occurred and this event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator. <br /><br /> The cause of this event was determined to be less than adequate Operating Procedure instructions for the RB HVAC systems, for instructions that follow fan swaps. Planned corrective action includes revising Operating Procedure instructions for the Units 1 and 2 RB HVAC systems.
3882016004 | Susquehanna 2, Susquehanna 1 | 05/13/2016 | 09/29/2016 | ML16273A15 | <strong>Unit 2 Experienced an Electrical Transient Resulting in a Manual SCRAM</strong><br /><i>Abstract:&nbsp;</i>At 23:55 on 5/12/16, Unit 2 experienced an electrical transient resulting in a loss of 2B246 Reactor Building Engineered Safeguard System (ESS) Division 480 volt Motor Control Center (MCC) and 2Y246 208/120 Volt Alternate Current (AC) Instrument Panel. With the loss of the Reactor Building ESS Division 480 volt MCC, several drywell cooling fans were lost leading to an increase in drywell pressure. At 0110 on 5/13/16 Unit 2 was manually scrammed. All rods inserted as expected. Reactor water level lowered to -27 inches and was immediately restored by normal feedwater level control. Level 3 (+13 inch) Primary Containment Isolation System (PCIS) isolations occurred, along with an initiation of the Reactor Core Isolation Cooling (RCIC). <br /><br /> The direct cause of the transient was found to be a phase to ground short between a cable and a protruding screw in MCC bucket 2B246091, Drywell Area Unit Cooler 2V411B Breaker. The apparent cause is the vendor did not comply with Specification E1116, Rev 3 with this order of buckets. Immediate corrective actions included the repair of 2B246 which has been completed. A plan has been developed to review a sample of the 480 VAC MCC breakers and is being tracked by maintenance and system engineering.
3882016005 | Susquehanna 2 | 05/13/2016 | 07/12/2016 | ML16194A25 | <strong>Unit 2 HPCI Manually Overridden Prior to a Manual Scram During a Plant Transient</strong><br /><i>Abstract:&nbsp;</i>On 5/13/2016 at 0055, the Unit 2 Unit Supervisor directed manually overriding High Pressure Coolant Injection HPCI (HPCI) immediately prior to a manual scram during a plant transient.<br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(v) <br /><br /> There were two causes of this event. First, the Unit Supervisor made a decision to prematurely override HPCI to minimize distractions later in the shutdown without procedural guidance to do so. Second, weaknesses in teamwork and oversight prevented the mistake from being corrected by the crew. Immediate corrective actions include removing qualifications from the individuals involved and communicating expectations with the remaining crews. Additional corrective actions being taken include incorporating this event into initial licensed operator training and a Human Performance Improvement Plan will be created to address gap noted in the crew's performance.
3882016006 | Susquehanna 2, Susquehanna 1 | 09/22/2016 | 11/17/2016 | ML16323A00 | <strong>Loss of Secondary Containment due to Damper Controller Sticking</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2016 at 03:20, a Nuclear Plant Operator (NPO) reported that Reactor Building Zone II differential pressure (dP) was steady at 0.15 inches water gauge (WG) resulting in entry into Technical Specification 3.6.4.1. Operations determined that the flow control damper (PDD27522A) for the "A" Zone II equipment exhaust fan (2V206A) was sticking, resulting in Zone II dP not being properly controlled. The linkage for the damper was agitated and the damper moved to control dP as designed. Operations placed the "B" division fan (2V206B) in service. Following the fan swap, dP held steady at 0.31 inches WG with 2V206B in service and 2V206A in standby. Technical Specification 3.6.4.1 was cleared at 03:42.<br /><br /> This event was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented fulfillment of a safety function (EN 52255). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of the event was age related degradation of the brass bushing and grease hardening in the damper linkage. Corrective actions include initiating work orders to disassemble, inspect, and replace the brass bushings for the remaining similar dampers. A Preventive Maintenance strategy will be evaluated following completion of the inspections of the remaining dampers. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3902016001 | Watts Bar 1 | 01/12/2016 | 03/09/2016 | ML16069A20 | <strong>Channel Mode Switch in Incorrect Position Renders Lower Containment Atmosphere Particulate Radiation Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2016, at 1645 Eastern Standard Time (EST), Watts Bar Nuclear Plant (WBN) Maintenance personnel were performing a 92 day Channel Operational Test for radiation monitor 1-RM-90-106A, Lower Containment Atmosphere Particulate Radiation Monitor, and found the mode switch in the "DIFF" position, which was not expected. The surveillance was stopped and an investigation was conducted. It was determined that the design requires the mode switch to be in the "INT" position to be operable. The mode selector switch was placed in the "INT" position and the surveillance was completed. The radiation monitor was restored to OPERABLE status at 1743 EST on January 12, 2016. <br /><br /> Placing the mode selector switch in the "DIFF" position resulted in 1-RM-90-106A being INOPERABLE due to the loss of alarm function of the monitor. Investigation determined that the switch had been repositioned on December 8, 2015. Because the containment particulate radiation monitor was inoperable for a period of time greater than permitted by Technical Specification 3.4.15, this condition is reportable as an operation or condition prohibited by Technical Specifications per 10 CFR 50.73(a)(2)(i)(B). During the time the monitor was inoperable, other means of leak detection (e.g., containment pocket sump level indication, reactor coolant system inventory balance) remained available.
3902016002 | Watts Bar 1 | 03/05/2016 | 05/04/2016 | ML16125A05 | <strong>Technical Specification Action Not Met for Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2016, at 1512 Eastern Standard Time (EST), Watts Bar Nuclear Plant (WBN) Unit 1 entered Technical Specification (TS) 3.6.3, Containment Isolation Valves, Condition A for a containment isolation valve being inoperable. During a containment walkdown, leakage was found on valve 1-FCV-61-122, Glycol Cooled Floor Return Header Isolation and the valve was declared inoperable. TS 3.6.3 Condition A requires that a penetration flow path with one containment isolation valve inoperable to be isolated by use of at least one closed and de-activated automatic valve, closed manual valve, blind flange, or check valve with flow through the valve within 4 hours. The penetration associated with this containment isolation valve was not isolated until 2113 EST on March 5, 2016. The cause of this event was operations staff misunderstanding the applicability of the Note associated with TS 3.6.3, which allows administrative controls under certain conditions.<br /><br /> Because the action specified by TS 3.6.3 was not completed within four hours, this condition is reportable as an operation or condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B).
3902016003 | Watts Bar 1 | 03/11/2016 | 05/10/2016 | ML16131A04 | <strong>Technical Specification Surveillance Requirement Not Met During Emergency Core Cooling System Venting</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2016, Watts Bar Nuclear Plant (WBN) Unit 1 concluded that a condition prohibited by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.2, ECCS - Operating, had occurred during recent performances of TS Surveillance Requirement (SR) 3.5.2.3. Due to inadequacies with gas quantification methodologies for Safety Injection (SI) and Residual Heat Removal (RHR) system discharge piping, the ability to meet TS SR 3.5.2.3 could not be demonstrated, which is required in accordance with TVA's response to NRC Generic Letter 2008-01, "Managing Gas Accumulation In Emergency Core Cooling, Decay Heat Removal, and Containment Spray Systems." This condition existed from March 2012 to December 2015. In a subsequent analysis, WBN determined that the worst case gas accumulation in SI and RHR discharge piping would not have affected the ability of the SI and RHR systems from performing their safety functions. However, because the required actions of TS LCO 3.5.2 were not taken within the required times, WBN was in a condition prohibited by Technical Specifications. <br /><br /> TVA is reporting this issue pursuant to 10 CFR 50.73(a)(2)(i)(B).
3902016004 | Watts Bar 1 | 03/22/2016 | 05/23/2016 | ML16144A37 | <strong>Automatic Reactor Trip Due to Actuation of Over Temperature Delta Temperature Bistables</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2016, at 1131 Eastern Daylight Time, the Watts Bar Nuclear Plant Unit 1 (WBN1) reactor tripped due to the actuation of the Over Temperature Delta Temperature bistables. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated. All control rods inserted upon the reactor trip and safety systems functioned as expected. <br /><br /> An investigation into the cause of the trip determined that a failure of a Valve Position Limit up/down counter circuit card in the Analog Electro-Hydraulic Turbine Control System resulted in the closure of the turbine high pressure governor valves, resulting in an automatic reactor trip and turbine trip on WBN1. The failed card was replaced and WBN Unit 1 was returned to service. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
3902016005 | Watts Bar 1 | 10/22/2015 | 07/13/2016 | ML16195A19 | <strong>Both Trains of Unit 1 Emergency Gas Treatment System Inoperable During Unit 2 Testing</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2016, Watts Bar Nuclear Plant (WBN) Unit 1 determined through engineering analysis that both trains of emergency gas treatment system (EGTS) were inoperable for 8 minutes, 10 seconds during preoperational testing of Unit 2 EGTS. The inoperability of A and B trains of Unit 1 EGTS took place on October 22, 2015, while Unit 1 was in Mode 1 and two trains of EGTS were required to be operable in accordance with technical specification (TS) limiting condition for operation (LCO) 3.6.9, "Emergency Gas Treatment System (EGTS)." At the time of the event, Unit 2 was in "no Mode," prior to initial fuel loading. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D), "Event or Condition That Could Have Prevented Fulfilment of a Safety Function."
3902016006 | Watts Bar 1 | 05/13/2016 | 06/30/2016 | ML16183A19 | <strong>Undersized Room Cooler Fan Shaft Results in Loss of Centrifugal Charging Pump</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2016, Watts Bar Nuclear Plant Unit 1 (WBN1) determined that a condition prohibited by Technical Specifications had previously occurred. During the Fall 2015 WBN1 outage, maintenance performed on the 1B-B centrifugal charging pump (CCP) room cooling fan introduced a condition that resulted in a subsequent bearing failure of the room cooling fan on December 4, 2015. This condition would have prevented the 1B-B CCP pump from performing its specified function for its designed mission time. Based on the reduced reliability of the fan, the 1B-B CCP was considered to be inoperable from October 7, 2015 until the fan was repaired and returned to service on December 6, 2015. During this time period, there were several short time periods when the 1A-A CCP was inoperable. <br /><br /> An investigation into the cause of the failure was completed on April 21, 2016. The cause of the fan bearing failure was an undersized fan shaft, resulting in the 1B-B CCP fan having excess shaft to bearing clearance which caused the bearing inner ring to loosen from the eccentric locking collar. These excessive clearances allowed the fan bearing inner ring to slide on the shaft. The sliding rotation of the inner ring on the shaft resulted in excessive heat being generated within the bearing leading to catastrophic failure. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(v)(D).
3902016007 | Watts Bar 1 | 11/05/2015 | 06/20/2016 | ML16172A02 | <strong>Technical Specification Action Not Met for Rod Position Indication</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2016, Watts Bar Nuclear Plant (WBN) Unit 1 concluded that a condition prohibited by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.8, Rod Position Indication, had occurred during the dropped rod event on November 05, 2015. The Surveillance Requirement for TS 3.1.8 states that each Analog Rod Position Indication, (ARPI), agrees within 12 steps of the group demand position for the full indicated range of rod travel. Since the ARPI was indicating correctly for the dropped rod and was verified by diverse indications, it was considered operable. However, the Bases for TS 3.1.8 states that for the position indication to be operable, the Rod Position Indication System indicates within 12 steps of the step counter demand position as required by TS 3.1.5, Rod Group Alignment Limits. In the case of a dropped control rod, the Rod Position for the affected rod would not be within 12 steps of the demand counter. Since WBN Unit 1 at the time of the dropped rod was in a mode of applicability, the above conditions would have been met warranting entry into TS 3.1.8 Condition A. Because the actions of TS 3.1.8 were not taken within the required times, WBN Unit 1 was in a condition prohibited by TS.<br /><br /> TVA is reporting this issue pursuant to 10 CFR 50.73(a)(2)(i)(B).
3902016008 | Watts Bar 1, Watts Bar 2 | 05/17/2016 | 07/15/2016 | ML16197A55 | <strong>Emergency Diesel Generator Manual Start due to Loss of Voltage on the 6.9kV Shutdown Board 1B-B</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2016, at 1630 hours while restoring from a plant modification related to installation of new protective relays designed to detect open phase conditions on the 6.9kV shutdown boards, the feeder breakers for the 6.9kV Shutdown Board 1B-B tripped resulting in a loss of bus voltage. The feeder breakers tripped due to actuation of the loss of voltage relays in the shutdown board protective relay trip logic circuit resulting in separation of offsite power from the 6.9kV Shutdown Board 1B-B. The 1B-B emergency diesel generator did not auto start during this event because it was out of service due to planned maintenance.<br /><br /> In response to the loss of power on the 6.9kV Shutdown Board 1B-B, the operators immediately entered Abnormal Operating Instruction, 0-AOI-43.02, Loss of Unit 1 Train B Shutdown Boards, and manually started emergency diesel generators 1A-A, 2A-A, and 2B-B. All equipment operated properly. The emergency diesel generators were not required to be paralleled to their respective boards because offsite power was available. <br /><br /> Offsite power was restored to the 6.9kV Shutdown Board 1B-B at 1802 hours on May 17, 2016. Event Notification 51940 was issued May 17, 2016. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
3902016009 | Watts Bar 1 | 11/21/2016 | 11/30/2016 | ML16335A26 | <strong>Failure to Complete Surveillance Requirements Causes a Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2015, Watts Bar Nuclear Unit 1 (WBN1) operations personnel did not conduct a surveillance of the Train B Essential Raw Cooling Water (ERCW) supply inboard containment isolation valve, which represented the late date for this surveillance. WBN1 personnel recognized the potential for this surveillance to go late on November 15, 2015, and therefore the provisions of Technical Specification (TS) Surveillance Requirement 3.0.3 could not be applied. Failure to complete the surveillance required entering TS Limiting Condition for Operation (LCO) 3.6.3 and completing Required Action A.1, but the required action to isolate the affected penetration flowpath was not performed until January 30, 2016. This condition was not recognized as reportable until May 18, 2016. <br /><br /> This supplement clarifies the reportable event and reconciles event dates.
3902016010 | Watts Bar 1, Watts Bar 2 | 06/08/2016 | 08/08/2016 | ML16221A18 | <strong>Emergency Diesel Generator Crankcase Pressure Switches Not Analyzed to Withstand the Effects of a Tornado</strong><br /><i>Abstract:&nbsp;</i>At 1526 Eastern Daylight Time on 6/8/2016, a determination was made involving the potential impact of a tornado on the Emergency Diesel Generators (EDGs). The EDGs are required to be operable to provide power to ensure that acceptable fuel design limits, reactor coolant system pressure boundary limits, and containment integrity are not exceeded during abnormal transients. Further, the EDGs are designed with a crankcase pressure trip (setpoint of 1 inch water), which is bypassed following an emergency start. Engineering has determined that a tornado could potentially cause actuation of the crankcase pressure trip due to a low barometric condition. If an emergency start signal has NOT previously occurred, then during a tornado, actuation of the crankcase pressure trip would energize the shutdown relay causing an EDG lockout condition. The EDG lockout condition prevents subsequent EDG starts (normal or emergency) until operators manually reset the lockout condition locally at the EDG. This condition could potentially affect all four EDGs simultaneously. <br /><br /> A compensatory measure has been established, that upon notification of a Tornado Warning, the EDGs would be 'emergency started' and run during the time the Tornado Warning was in effect. This action bypasses the crankcase pressure trip function and allows the EDGs to perform their required safety function.
3902016011 | Watts Bar 1 | 08/03/2016 | 12/09/2016 | ML16344A07 | <strong>Loss of Centrifugal Charging Pump due to Repeat Failure of Associated Room Cooler</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2016, Watts Bar Nuclear Plant Unit 1 (WBN1) determined that a condition prohibited by Technical Specifications (TS) had occurred. During maintenance of the 1B-B centrifugal charging pump (CCP) room cooler, the bearing was found in a degraded condition requiring repair. This fan is required to support Operability of the 1B-B CCP. Based on the inability of the CCP to meet its calculated mission time of 10 days, the 1B-B CCP was considered to be inoperable from July 24, 2016 until restoration of the 1B-B CCP room cooler on August 5, 2016. This represents a condition prohibited by Technical Specifications due to the 1B-B CCP being inoperable for greater than its allowed outage time. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).<br /><br /> The cause of the bearing degradation and fan failure was over tensioning the fan belts due to a 2011 revision to a maintenance procedure which improperly removed the established method for belt tensioning. This method had been added to the procedure in 1995 as an action to prevent recurrence of a similar over tensioning event. <br /><br /> The 1B-B CCP room cooler had been rebuilt in December 2015 after a similar bearing failure had occurred as reported in LER 390/2016-006.
3912016001 | Watts Bar 2 | 04/14/2016 | 06/13/2016 | ML16165A24 | <strong>Loss of Automatic Containment Isolation for the Steam Generator Blowdown Sampling Lines</strong><br /><i>Abstract:&nbsp;</i>From March 18, 2016, when Watts Bar Nuclear Plant Unit 2 first entered Mode 4 to April 14, 2016 with the plant in Mode 3, it was determined that a condition prohibited by Technical Specifications (TS) existed. During this time both automatic and manual closure of the containment isolation valves and the sample isolation valves for the Steam Generator Blowdown (SGBD) sampling lines were disabled due to improperly installed electrical jumpers in the valve control circuits. The misplaced jumpers bypassed the Phase A containment isolation signals, the auto/manual start signals for the Auxiliary Feedwater (AFW) pumps, and the control valve seal-in circuits. Containment isolation on a Phase A signal is used to control potential release of radioactive material to the environ in the event of a Design Bases Accident. The AFW pump auto/manual start signals are used to isolate the SGBD sampling lines to preserve steam generator inventory. The seal-in circuits are used to allow the operator to manually position the valves in either the open or closed position from the main control room. This event occurred prior to initial reactor criticality. There was no loss of safety function. <br /><br /> The isolation valves for the SGBD sample lines were returned to service on April 14, 2016. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii)(B) and (C).
3912016002 | Watts Bar 2 | 05/11/2016 | 09/02/2016 | ML16246A11 | <strong>Turbine Driven Auxiliary Feedwater Pump Inoperable for Longer than Allowable Outage Time due to Turbine Speed Control Failure</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2016, during performance of Surveillance Requirement (SR) 3.7.5.2, the Turbine Driven Auxiliary Feedwater pump (TDAFWP) failed to achieve required rated speed of 3950 rpm ± 25 rpm due to an equipment failure. The TDAFWP was declared inoperable, and Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5, Condition B, was entered. The equipment was repaired, the TDAFWP was re-tested successfully and returned to service. TS LCO 3.7.5 was exited on May 4, 2016. <br /><br /> On May 11, 2016, a past operability evaluation concluded that the TDAFWP had been inoperable from March 30 through April 17, 2016, during periods of time when the TDAFWP was required for Mode 3 operations. This is reportable as a condition prohibited by TS. <br /><br /> During the same time period, the 2A-A Motor Driven Auxiliary Feedwater Pump (MDAFWP) experienced an oil leak through the inboard bearing housing vent cap that resulted in the need to add approximately 4 ounces of oil on a daily basis. The MDAFWP was determined to be operable.
3912016003 | Watts Bar 2 | 05/28/2016 | 09/02/2016 | ML16246A12 | <strong>Turbine Driven Auxiliary Feedwater Pump Inoperable for Longer than Allowable Outage Time due to Governor Valve Spring Over-Tensioning</strong><br /><i>Abstract:&nbsp;</i>The Unit 2 Turbine Driven Auxiliary Feedwater (TDAFW) pump auto-started upon a planned Reactor Trip at 0154 Eastern Daylight Time (EDT) on May 28, 2016. At 0157 EDT the Reactor Operator noted that TDAFW forward flow to Steam Generators 1 and 3 were approximately 800 gallons per minute, and placed the associated Level Control Valves in the closed position. At approximately 0203 EDT the Main Control Room received Alarm Window 60-A, TDAFW Pump Electrical Overspeed Trip. Operators walked down the TDAFW pump and determined that the turbine had tripped, by confirming that the Trip and Throttle Valve was no longer latched, and declared the TDAFWP inoperable. The equipment was repaired, the TDAFWP was re-tested successfully and returned to service. Technical Specification (TS) Limiting Condition for Operation 3.7.5 was exited on May 30, 2016. <br /><br /> The plant conditions at the time of the event were Unit 2 in Mode 3 at Normal Operating Temperature/Normal Operating Pressure following manual reactor trip from Mode 1. The reactor trip was unrelated to this event. <br /><br /> On June 29 2016, a past operability evaluation concluded that the TDAFWP had been inoperable from March 30 through May 30, 2016. This is reportable as a condition prohibited by TS.
3912016004 | Watts Bar 2 | 06/05/2016 | 08/04/2016 | ML16217A39 | <strong>Reactor Trip and Safety Injection Actuation Caused by Turbine Governor Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2016 at 1227 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant Unit 2 was in MODE 1 at approximately 12.5 percent power when a safety injection (SI) actuation occurred, followed by an automatic reactor protection system (RPS) trip. No primary safety barriers (Reactor Coolant System, containment and fuel clad) were challenged and no primary or secondary safety or relief valves actuated during the event. The Unit 2 plant trip was considered a complicated trip due to SI actuation. Safety equipment operated as expected and SI was promptly terminated. <br /><br /> The reactor trip and SI were caused by a turbine governor valve failing open, causing a steam header pressure rate of decrease SI actuation signal.
3912016005 | Watts Bar 2 | 06/20/2016 | 08/19/2016 | ML16232A13 | <strong>Main Feedwater Pump Trip on Loss of Condenser Vacuum Leads to Turbine Trip and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2016, the 2B Main Feedwater Pump (MFP) tripped on a loss of vacuum in the 2B MFP turbine condenser, resulting in a loss of normal feed, and the subsequent trip of the main turbine. While operators were reducing power to within the capacity of Auxiliary Feedwater (AFW), the reactor tripped at 1540 Eastern Daylight Time (EDT) on Steam Generator Water Level (SGWL) Lo Lo in Steam Generator No.4. SG water level lowered rapidly due to shrink from the relatively cold AFW following the trip. <br /><br /> All control and shutdown rods fully inserted. All safety systems responded as designed. The trip response was uncomplicated. <br /><br /> The trip was caused by a human performance error during the drain down of the 2A MFP turbine condenser which resulted in a loss of vacuum on the 2B MFP turbine.
3912016006 | Watts Bar 2 | 08/13/2016 | 10/07/2016 | ML16281A42 | <strong>Turbine Driven Auxiliary Feedwater Pump Auto Start on Lo-Lo Steam Generator Level Following Planned Unit Trip</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2016 Watts Bar Nuclear Plant Unit 2 (WBN2) was being stabilized following a pre-planned reactor trip. Both motor driven auxiliary feed water pumps and the turbine driven auxiliary feed water pump (TDAFW pump) were in operation maintaining steam generator (SG) water level between 6 - 50 percent in accordance with the Reactor Trip Response Procedure. <br /><br /> At 0333 Eastern Daylight Time (EDT) the TDAFW pump was secured by procedure and SG water level lowered to the Lo-Lo Alarm setpoint (17 percent). With the Unit at 0 percent power, a trip time delay of 3 minutes is present for auxiliary feedwater actuation. At 0337 EDT, the TDAFW pump automatically started with SG water levels less than the Lo-Lo alarm setpoint (lowest level reached was 15 percent). <br /><br /> The cause of the event was a failure to brief the auto start feature of the TDAFW pump at Lo-Lo SG water level of 17 percent when briefing the control band for the SGs is between 6 to 50 percent.
3912016007 | Watts Bar 2 | 08/23/2016 | 10/21/2016 | ML16295A21 | <strong>Manual Reactor Trip due to Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2016, at 1356 Eastern Daylight Time (EDT), during power ascension testing, Watts Bar Nuclear Plant (WBN) Unit 2 reactor was manually tripped due to a loss of main feedwater. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All control and shutdown rods fully inserted. All safety systems responded as designed. <br /><br /> The loss of main feedwater was due to a leak on a hydraulic fitting associated with the Main Feedwater Pump Turbine High Pressure Governor valve, resulting in the valve going partially closed with reactor power at 48 percent. With the governor valve partially closed, feedwater flow was reduced such that the unit needed to be manually tripped. Subsequent investigation determined the leak to be caused by the installation of incompatible fittings associated with the governor valve that occurred during plant construction.
3912016008 | Watts Bar 2 | 08/30/2016 | 10/28/2016 | ML16302A29 | <strong>Reactor Trip Resulting from Failure of 2B Main Bank Transformer</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2016, at 2110 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) Unit 2 reactor tripped on turbine trip as a result of an electrical fault. All control rods fully inserted and no safety or relief valves lifted. The Auxiliary Feedwater system actuated as designed. <br /><br /> The electrical fault was caused by an internal fault on the low voltage side of the 2B Main Bank Transformer (MBT) which resulted in a fire. The electrical fault was cleared by the 2B MBT sudden pressure and phase differential relays. Automatic fire suppression operated as expected and a fire fighting team was established by the fire brigade with assistance from local fire departments. The fire was extinguished at 2230 EDT. <br /><br /> The failed 2B MBT was removed from the plant and the spare MBT was connected in its place. The unit was returned to power and replacement transformers are being procured by the Tennessee Valley Authority for long term reliability.
3952016002 | Summer 1 | 07/22/2016 | 04/25/2018 | ML18116A69 | <strong>Pressurizer Heater Inoperable Longer than Technical Specification Limiting Condition for Operation 3.4.3</strong><br /><i>Abstract:&nbsp;</i>On July 22, 2016, a past operability review determined that the Pressurizer Backup Group 2 Heaters were inoperable for 94 hours, from 0600 on June 15, 2016, to 0400 on June 19, 2016. On June 18, 2016, the breaker (XSW1DB 05) that provides safety class 1E power to Pressurizer Backup Group 2 Heaters was found with its charging springs discharged. The closing coil plunger was found mechanically bound due to foreign material. The closing latch was unable to reset and the contacts did not allow the spring charging motor to energize and recharge the closing springs. The failed breaker XSW1DB 05 was swapped with a spare breaker and the Pressurizer Backup Group 2 Heaters were returned to service at 0400, June 19, 2016. <br /><br /> The time for which the Pressurizer Backup Group 2 Heaters were inoperable exceeds Technical Specification 3.4.3.a Limiting Condition for Operation of 72 hours. Therefore, this report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B).
3952016003 | Summer 1 | 09/13/2016 | 04/25/2018 | ML18116A69 | <strong>Steam Propagation Door Discovered Propped Open</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2016 at 20:30 a steam propagation door (DRIB/107) to Chiller Room C was discovered propped open without all required compensatory actions during routine operator rounds. The door was determined to be open for approximately 3 hours and 22 minutes. The propped open door could have rendered both trains of Chilled Water nonfunctional if a High Energy Line Break (HELB) event occurred. This could have subsequently rendered both trains of High Head Safety Injection inoperable due to the loss of chilled water cooling to safety related room coolers. Technical Specification 3.0.3 was entered until the door was secured at 20:42. The cause of the event was due to a human performance error. Station Shift Test Specialist authorized the door to be propped open without verifying programmatic contingencies were established. This condition is reportable under 10CFR50.72(b)(3)(v) and 10CFR50.73(a)(2)(v)(D) as any event or condition that at the time of discovery could have prevented the fulfillment of a safety function. An 8 hour event notification (EN 52240) was made. <br /><br /> VCSNS has supplemented the previous License Event Report with the Final Results from an Engineering Technical Report. The report concludes that a HELB event postulated to occur during the times when the non-conforming HELB barrier configuration existed would not have impacted the operability of equipment in the Battery/Battery Charger Rooms or the functionality of equipment in the Chiller Pump Room and at least one of the three Chiller Rooms.
3952016004 | Summer 1 | 09/14/2016 | 02/01/2017 | ML17033B59 | <strong>Steam Propagation Barrier Degrade due to Missing Orifices</strong><br /><i>Abstract:&nbsp;</i>LER-2016-003 documented a steam propagation door (DRIB/107) to the Chiller Room for XHX0001C-VU propped open on September 13, 2016 without compensatory actions during routine operator rounds. <br /><br /> As part of the extent of condition on September 14, 2016 the station discovered an additional degradation to the steam propagation barriers. Steam propagation barriers (orifices) were not installed as designed between the Chiller rooms and Chilled Water (VU) pump room floor drains therefore, in the as-found configuration, there was no separation between the rooms. When any chiller room door was open, even with administrative contingencies in place, the other chiller rooms and pump rooms were not protected from a High Energy Line Break (HELB). The station has completed an evaluation to determine the impact on the rooms during a HELB event. This event is reportable under 10CFR50.73(a)(2)(v)(D) as any event or condition that could have prevented the fulfillment of a safety function and 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specification (TS).
3952016005 | Summer 1 | 10/04/2016 | 12/05/2016 | ML16340B35 | <strong>Steam Propagation Barrier Degraded due to Removal of Ventilation Duct Access Panel for Surveillance Activities</strong><br /><i>Abstract:&nbsp;</i>LER-2016-003 documented a steam propagation door (DRIB/107) to the Chiller Room for XHX0001C-VU propped open on September 13, 2016 without compensatory actions during routine operator rounds.<br /><br /> As part of the Extent of Condition Evaluation, the station discovered an additional degradation to the steam propagation barriers. Ventilation access panels were found with missing fasteners. While investigating this, on October 4, 2016, it was discovered that access panels were removed periodically, while the plant was at power, to conduct surveillance activities. Removal of these panels could have resulted in steam entering Environmental Qualification (EQ) mild areas during a postulated steam line break. The station has conducted a preliminary evaluation of the impacted rooms. The preliminary results indicate that steam propagation through an open fire damper inspection panel during a postulated High Energy Line Break (HELB) would not affect the capability of the structures, systems, and components (SSC) in the impacted rooms to perform their required functions. This License Event Report will be supplemented when results are finalized. This event is reportable under 10CFR50.73(a)(2)(v)(A)&(D) as any event or condition that could have prevented the fulfillment of a safety function.
3952016006 | Summer 1 | 10/19/2016 | 12/15/2016 | ML16350A27 | <strong>Circuit 1 Hot Gas Bypass Valve Failure Renders A-Train Chiller Non-functional and A-Train Charging Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2016, a past operability review determined that HVAC System Mechanical Water Chiller A-Train (XHX0001A) had been non-functional from June 26, 2016, through July 20, 2016, due to Circuit 1 Hot Gas Bypass Valve (XVM16484A-VU) failing open. The failure of XVM16484A-VU to successfully isolate, adversely impacted the A-Train Chiller's ability to transfer the total design basis accident heat load of the system. The event impacts the operability requirements of the area room coolers that the Chilled Water (VU) system supports per Technical Specification (TS) 3/4.7.9, "Area Temperature Monitoring." <br /><br /> On July 20, 2016, Virgil C. Summer Nuclear Station personnel identified via trending that XHX0001A Chiller Circuit 1 cooling capacity was limited to approximately 65 tons. Further troubleshooting identified that the condition was due to XVM16484A-VU failing open intermittently. The past operability review found that XHX0001A was unable to provide design basis heat load cooling capacity and therefore was considered non-functional.<br /><br /> XVM16484A-VU was replaced and post maintenance testing was completed satisfactorily.<br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B), operation or condition prohibited by technical specifications.
3972016001 | Columbia | 03/28/2016 | 07/25/2016 | ML16207A70 | <strong>Manual Reactor Scram following Loss of Reactor Closed Cooling</strong><br /><i>Abstract:&nbsp;</i>At 1322 PDT on March 28, 2016, a manual reactor scram was initiated in response to a loss of Reactor Closed Cooling (RCC). The loss of RCC was due to the opening of a Service Water (SW) valve at the inlet side of the Fuel Pool Cooling heat exchanger during performance of a partial surveillance without proper isolation of the RCC system piping from the heat exchanger. The cross-connection of the two systems caused depressurization and loss of flow from the RCC system into the non-pressurized SW piping. The SW valve was closed and the reactor was scrammed. Safety system responses to the scram signal were normal, with all control rods being fully inserted. Reactor decay heat was removed via bypass valves to the Main Condenser. No safety relief valves lifted and no emergency core cooling systems injected following the reactor scram. <br /><br /> The root cause was determined to be that plant Operators did not properly evaluate plant configuration when performing a partial surveillance including the marking as "N/A" (not applicable) of procedural steps, in accordance with plant procedures. Human performance aspects of the event were quickly addressed and additional corrective actions include reinforcing and monitoring procedure standards, and updating work control procedures at the station.
3972016002 | Columbia | 10/03/2016 | 09/27/2017 | ML17270A19 | <strong>Valve Closure Results in Momentary Increase in Secondary Containment Pressure</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2016 at 1008 PDT, the Secondary Containment (Reactor Building) became inoperable due to pressure increasing above the Technical Specification limit of -0.25 inches of water gauge (inwg). While the plant was at 100% power, a Reactor Building exhaust valve (REA-V-1) unexpectedly closed, resulting in a loss of Secondary Containment vacuum for approximately four minutes. Operations personnel manually started the Standby Gas Treatment System A and quickly restored Secondary Containment to less than -0.25 inwg. While Technical Specification limits were exceeded for this short time period, the resulting pressure excursion was bounded by analytical results; and thus, there were no safety consequences for this condition. This event was reported under reporting criterion 10 CFR 50.72(b)(3)(v)(C) as Event Notification #52276. <br /><br /> The cause of the REA-V-1 closure was a loose termination point on the termination board, resulting in an intermittent loss of power to the valve. The corrective action for this event was to tighten the loose termination point screw.
3972016003 | Columbia | 11/20/2016 | 08/29/2017 | ML17241A22 | <strong>Failure of Fan to Start Results in Momentary Increase in Secondary Containment Pressure</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2016 at 1402 PST, Secondary Containment [NH] (Reactor Building) became inoperable due to pressure increasing above the Technical Specification limit of -0.25 inches of water gauge (inwg). While the plant was ascending in power, the Reactor Building exhaust air fan unexpectedly failed to start in manual during post-maintenance testing. Prior to this event, Reactor Building Heating, Ventilation and Air Conditioning [VA] (HVAC) System A was running. Per station procedures, System A was stopped and System B was to start. The fan’s failure to start resulted in no Reactor Building fans running, and increased Reactor Building pressure. For a time period of less than one minute, Secondary Containment pressure was not maintained less than or equal to -0.25 inwg. Immediate recovery actions by Operations personnel included manually starting Reactor Building HVAC System A, which quickly restored Secondary Containment pressure to less than or equal to -0.25 inwg at 1403 PST. While TS limits were exceeded for this short time period, the resulting pressure excursion was bounded by analytical results; and thus, there were no safety consequences for this condition. This event was reported under reporting criteria 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) as Event Notification #52382. <br /><br /> The cause of the exhaust fan's failure to start was degraded lubrication on the closing mechanism of the fan's circuit breaker [BKR]. Corrective actions for this event include replacement of the circuit breaker and updates to preventative maintenance dates of the station's 480 volt circuit breakers. There were no other event-related equipment malfunctions.
3972016004 | Columbia | 12/18/2016 | 06/08/2017 | ML17164A44 | <strong>Automatic Scram due to Off-site Load Reject</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2016 at 11:24 hours, an automatic scram occurred due to a fault on an off-site transmission network. A reactor scram was automatically initiated by the plant response to the transient. <br /><br /> All rods fully inserted, Main Steam Isolation Valves [SB,V] automatically closed due to loss of power to both Reactor Protection System [JC] busses. All safety systems operated as designed. Two Safety Relief Valves [SB,V] were initially cycled automatically, then several manually to maintain Reactor Pressure Vessel [AC] pressure. Reactor water level was maintained with Reactor Core Isolation Cooling [BN], Control Rod Drive [AA] flow, and High Pressure Core Spray [BG]. <br /><br /> The entity responsible for the off-site transmission network, Bonneville Power Administration (BPA), performed a cause evaluation for the loss of off-site power. The cause evaluation stated the event was caused by three sequential 500-kV breaker failures. BPA took immediate corrective actions to restore the off-site transmission network. The root cause evaluation addressing the plant response was performed by plant personnel.
4002016001 | Harris | 07/07/2016 | 09/01/2016 | ML16245A80 | <strong>Inadequate Protection from Tornado Missiles Identified due to Nonconforming Design Conditions</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2016, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Shearon Harris Nuclear Power Plant identified nonconforming conditions in the plant design such that specific TS equipment did not meet current design basis for protection against potential tornado missile impact. Identified systems were declared inoperable and Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," was implemented. Compensatory measures were implemented within the time allowed by the applicable Limiting Condition(s) for Operation and the associated systems were then declared operable but nonconforming. <br /><br /> The two systems identified with credible impacts were the 'A' train Emergency Diesel Generator and the Main Steam Safety Relief Valves. Actions will be taken to establish compliance, either by plant modification or by employing a methodology for addressing tornado missile noncompliances. <br /><br /> Due to the historical nature of the issue, a specific cause for the identified vulnerabilities was not determined.
4002016002 | Harris | 07/22/2016 | 09/20/2016 | ML16263A25 | <strong>'A' Essential Services Chilled Water Chiller Trip due to Oil Leak from Failed Tube Fitting</strong><br /><i>Abstract:&nbsp;</i>On July 22, 2016, the 'A' Essential Services Chilled Water (ESCW) chiller tripped due to low oil pressure and was declared inoperable. The cause was oil leakage from a recently replaced brass tube fitting connecting the high-pressure side of an oil pressure differential sensing line to the lubrication system. An equivalent stainless steel fitting was installed in place of the brass, and the 'A' ESCW chiller was then declared operable. <br /><br /> This failed brass fitting was a recently installed like-for-like replacement component following a similar 'A' ESCW chiller trip on July 15, 2016, caused by low oil pressure as a result of leakage through the original brass tube fitting. <br /><br /> The cause of the failed tube fitting was fatigue crack growth resulting from vibration, with stress corrosion cracking having a secondary role. The material was replaced with stainless steel, and further analysis to address the vibration is ongoing.
4002016003 | Harris | 09/21/2016 | 10/05/2016 | ML16279A50 | <strong>Containment High-Range Radiation Monitors Declared Inoperable due to Potential for Temperature Induced Current</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1998, the NRC issued Information Notice (IN) 97-45, Supplement 1, to alert licensees of the potential of erratic indications from high-range radiation monitors as result of a problem with the associated coaxial cables. These erratic indications could mislead operators assessing radiation levels in the containment building during accident scenarios. The erratic indications result from positive and negative current flow when exposed to transient temperature conditions, such as those postulated during a loss-of-coolant accident or a main steamline break. This phenomenon is known as temperature induced current (TIC), and could result in false high radiation readings for approximately 15 minutes following a design basis accident. <br /><br /> On September 21, 2016, Shearon Harris Nuclear Power Plant (Harris) declared both Containment High-Range Radiation Monitors (CHRRMs) inoperable. The CHRRMs utilize Rockbestos cables similar to those described in IN 97-45, Supplement 1. The use of these cables by Harris is historical, going back at least 20 years. To address, Harris will either test the cables to quantify a correction factor, replace the impacted cables with cables less susceptible, or complete a License Amendment Request to restore compliance.
4002016004 | Harris | 10/08/2016 | 12/07/2016 | ML16342B68 | <strong>Reactor Trip and Safety Injection During Turbine Control Testing at Low Power</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2016, the Shearon Harris Nuclear Power Plant was reducing power to enter a planned refueling outage (RFO-20). The plant was at approximately 8 percent power in Mode 1 when the unit experienced an unplanned reactor trip with a safety injection (SI) and main steam line isolation (MSLI). A malfunction of the turbine controller during turbine mechanical overspeed trip testing caused an excessive draw of steam flow from the Steam Generators (SGs). This caused the Engineering Safety Features Actuation System instruments to detect a valid change in SG pressure and initiate a rate compensated Low Steam Line Pressure signal. This signal initiated a SI and MSLI, which in turn initiated reactor trip, turbine trip, feedwater isolation, and closed the main steam isolation valves. <br /><br /> Degraded equipment within the turbine controller resulted in excessive opening of the governor valves; this was caused by an inadequate supply of hydraulic oil to meet the increased system demand during testing. Insufficient hydraulic accumulator capacity was available to support system demand. One accumulator was known to be out-of-service; a second was discovered post-event. Also, a hydraulic oil pressure switch used for turbine control was not functioning properly. The equipment deficiencies have been corrected. Changes have been made to the testing procedure to validate at least four accumulators are in service prior to testing. The Power Operation (Mode 2 to Mode 1) procedure will also be revised to validate at least four accumulators are in service. A new calibration procedure will be implemented for the deficient oil pressure switch to ensure better quality control over verifying switch function.
4002016005 | Harris | 10/08/2016 | 12/07/2016 | ML16342C39 | <strong>Offsite Power Undervoltage Caused Actuation of Several Systems</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2016, at approximately 1310 EDT, while in Mode 4 for a planned refueling outage, Shearon Harris Nuclear Power Plant experienced an undervoltage (UV) condition in the switchyard for about 1.5 seconds. This triggered the UV relays for both emergency 6.9 kV buses and for several of the non-nuclear safety 6.9kV auxiliary buses, resulting in the respective supply breakers opening. At the time of the UV, the site was experiencing high winds and rain from the effects of Hurricane Matthew. Both Emergency Diesel Generators started and loaded as designed. Operations restored offsite power at 2154 EDT after verifying stable grid behavior for an extended period. Additionally, the Containment Ventilation Isolation system and the Auxiliary Feedwater system actuated and performed as designed.<br /><br /> The site declared an Unusual Event at 1328 EDT for loss of offsite power to emergency buses for greater than 15 minutes. At 2049 EDT, the Unusual Event was terminated.<br /><br /> The causes of the UV were determined to be a line fault on the Cape Fear - West End 230 kV line and equipment deficiencies associated with the Cape Fear 230 kV Substation protection relays which prevented immediate clearing of the fault.
4002016006 | Harris | 10/15/2016 | 12/14/2016 | ML16349A54 | <strong>Reactor Vessel Closure Head Penetration Nozzle Indications Attributed to Primary Water Stress Corrosion Cracking and a Weld Fabrication Void</strong><br /><i>Abstract:&nbsp;</i>Between October 15 and October 19, 2016, the Shearon Harris Nuclear Power Plant (SHNPP) reactor vessel closure head penetrations were being examined. SHNPP was shut down for a scheduled refueling outage (RFO) for cycle 20 (RFO-20). <br /><br /> Nondestructive examinations identified four rejectable indications impacting four penetration nozzles. Indications associated with nozzles 30, 40, and 51 were indicative of primary water stress corrosion cracking (PWSCC), with the largest indication having an axial extent of 0.372 in. with a through-wall extent of 0.247 in. (39 percent). The fourth indication was identified on nozzle 23 by dye penetrant testing. This indication had a rounded profile indicative of a weld fabrication void, and was 0.307 in. on the major dimension. The weld was fabricated during the previous outage, RFO-19. The void was originally identified during RFO-19 and was acceptable. However, the void has since opened to unacceptable dimensions due to normal operating conditions. <br /><br /> A leak path assessment and a bare metal visual examination of the reactor vessel head top was completed, with no leakage identified. The three PWSCC indications were repaired using the inside diameter temper bead weld method. The fabrication void was removed via localized grinding, with no additional welding necessary. All repairs were completed prior to exiting the refueling outage.
4002016007 | Harris | 10/26/2016 | 02/09/2017 | ML17040A53 | <strong>Containment Spray System Valve Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2016, the Shearon Harris Nuclear Power Plant was in a planned refueling outage. Operations was in the process of restoring the containment spray system following maintenance. During this restoration process, operations started the 'B' containment spray pump with Refueling Water Storage Tank (RWST) level below 23.4 percent. As a result, the logic to initiate containment spray switchover to the containment sump was satisfied, opening the containment sump suction valve, which established a flowpath that allowed water to be transferred from the RWST to the containment sump. Operations secured the 'B' containment spray pump and re-closed the containment sump suction valve to restore the plant to the desired configuration. During the event, the containment spray system was aligned for recirculation of the spray pump discharge back to the RWST, so no water flowed through the spray header. <br /><br /> The primary cause of the event was a procedural deficiency. The procedure did not establish a physical barrier to prevent the containment sump valves from opening in Modes 5, 6 and defueled. The corrective actions include revising the procedure to remove power to the containment sump valves to prevent them from opening in Modes 5, 6 and defueled.
4102016001 | Nine Mile Point 2 | 04/07/2016 | 06/06/2016 | ML16172A02 | <strong>Secondary Containment Inoperable due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2016, at approximately 1730 hours, the secondary containment of the Nine Mile Point Unit 2 (NMP2) Reactor Building was breached when workers opened both inner and outer airlock doors, SA262-2 and SA262-3, simultaneously. The integrity of the airlock was re-established within 4 to 5 seconds when one of the doors was closed and latched. This resulted in a momentary loss of Secondary Containment Operability (TS 3.4.3). Secondary containment differential pressure never exceeded the minimum Technical Specification limit of 0.25 inch of vacuum water gauge. The causal analysis identified that the existing notice providing airlock door usage instructions is not effective in preventing doors being opened simultaneously in all situations. Corrective actions taken include revising the notice signage at all airlock doors to increase wait time from 5 seconds to 10 seconds to allow personnel traversing the airlock to exit. NMP2 has submitted LER 2014-007, Revision 1 for similar conditions.
4132016001 | Catawba 1 | 04/26/2016 | 06/23/2016 | ML16179A20 | <strong>Mispositioned Breaker for Residual Heat Removal Loop Suction Results in Inoperable Train of Emergency Core Cooling System</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2016, Operators did not receive the expected results from a relay while performing the 1B train Emergency Core Cooling System (ECCS) Cold Leg Recirculation interlock test. Investigation found the breaker for the residual heat removal pump's loop suction valve incorrectly positioned open. ECCS 1B was declared inoperable. Subsequently, the breaker was closed after it was verified not to have been tripped open. <br /><br /> The last manipulation of this breaker was determined to have been during the coordination for pressure boundary valve testing and standby readiness alignment during the previous refueling cycle (December 2015). A past Operability Evaluation concluded the breaker being open led to a condition prohibited by Technical Specifications, and also a condition that could have prevented the fulfillment of a safety function for Unit 1 ECCS while the 1A emergency diesel generator was inoperable for greater than four hours during this time period. This event was determined to be reportable on April 26, 2016.<br /><br /> The cause of this event is that the test procedure for pressure boundary valve testing did not contain specific procedural guidance for establishing a suction source for the 1B train residual heat removal (RHR) pump. The test procedure required coordination with another procedure to ensure the breaker for the 1B train RHR pump loop suction valve was returned to the closed position. Corrective actions include procedural revisions to these procedures.
4162016001 | Grand Gulf 1 | 03/17/2016 | 05/16/2016 | ML16138A29 | <strong>Valid Engineered Safety Feature Actuation and Temporary Loss of Residual Heat Removal</strong><br /><i>Abstract:&nbsp;</i>At 1515 [CDT] on March 17, 2016, with Unit 1 in Mode 5 for a refueling outage, Grand Gulf Nuclear Station (GGNS) experienced an electrical fault and subsequent undervoltage condition on the 115kV offsite power source supplying the onsite Division 2 Engineered Safety Feature (ESF) transformer, ESF 12, and bus. The fault was present long enough to cause an actuation of the Division 2 Load Shedding and Sequencing (LSS) System and subsequent start of the Division 2 Standby Diesel Generator (SDG). The in-service B train of Residual Heat Removal (RHR) was load shed, as designed, and, within 7 seconds, the Division 2 SDG restored power to the Division 2 bus. RHR B was restored within 3 minutes and 13 seconds. Core alterations, in progress at the time, were suspended and fuel bundles were placed in their proper positions. The ESF 11 transformer was paralleled with SDG 2. The Division 2 bus was then placed back to the ESF 11 offsite electrical feed and the Division 2 SDG was secured. The apparent cause was determined to be that the 115kV line was not equipped with pilot scheme protective relaying. Protective relaying is scheduled to be installed in 2017.<br /><br /> Alternate Heat Decay Removal (ADHR) remained available throughout this time period. No changes in Spent Fuel Pool or Reactor Cavity temperature were observed. All safety systems operated as expected for the loss of power to ESF12 and Division 2 LSS System. The automatic start of the Division 2 Standby Diesel Generator is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) and the temporary loss of RHR (Shutdown Cooling) is being reported pursuant to 10 CFR 50.73(a)(2)(v)(B).
4162016002 | Grand Gulf 1 | 03/29/2016 | 08/21/2018 | ML18233A56 | <strong>Automatic Actuation of the Reactor Protection System due to B Main Transformer Wiring</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2016, at 1123 Central Daylight Time, Grand Gulf Nuclear Station was operating in Mode 1 and ascending in power at approximately 37 percent rated thermal power when an unplanned uncomplicated automatic reactor SCRAM occurred. A generator lockout was received due to a Main Transformer 'B' Differential Relay Trip which was followed by a turbine control valve fast closure, turbine trip, and reactor SCRAM. The Reactor Protection System and all other safety systems functioned as designed. The direct cause of this event was the premature actuation of the "B" Main Transformer Current Differential Relay (1N41-M703B) that resulted in a main generator lockout, turbine trip, and automatic Reactor SCRAM. The root cause of this event is maintenance fundamental procedures for lifting and landing leads and troubleshooting were not followed by supplemental personnel performing transformer re-wiring project to maintain configuration control. Corrective actions included correcting the transformer wiring issue, revision of procedures, and strengthening maintenance training and qualification processes. This event posed no threat to public health and safety.
4162016003 | Grand Gulf 1 | 04/07/2016 | 06/06/2016 | ML16158A10 | <strong>Loss of Secondary Containment Safety Function During Routine Roof Inspection</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2016 the Grand Gulf Nuclear Station, while at 100 percent reactor thermal power, experienced a loss of Secondary Containment safety function during the performance of routine Secondary Containment building roof inspection. During the inspection activity the roof hatch, which allows access/egress to the roof, was left open for approximately 20 minutes. Based on a review of the work activity it is believed this error has occurred a minimum of 30 times in the past 5 years. <br /><br /> The direct cause of the event was the failure to close the hatch. The apparent cause of the event was the failure to establish adequate work instructions to maintain control of the hatch and to ensure Secondary Containment was maintained OPERABLE. Corrective actions include closure of the hatch and the establishment of the appropriate control over the hatch in the work instructions. <br /><br /> There were no actual nuclear safety consequences or radiological consequences during the event. <br /><br /> This condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C). A 10CFR 50.72 notification was not performed because the event was not identified until after compliance was restored.
4162016004 | Grand Gulf 1 | 06/17/2016 | 08/16/2017 | ML17228A25 | <strong>Automatic Reactor Scram During Turbine Stop and Control Valve Surveillance due to Reactor Pressure and Power Oscillations</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2016, at 0256 Central Daylight Time, Grand Gulf Nuclear Station experienced an automatic reactor scram. Prior to the scram, Grand Gulf Nuclear Station was operating in Mode 1 at approximately 65% rated thermal power and performing the Turbine Stop and Control Valve Operability Surveillance. During the surveillance, after the 'B' Turbine Stop valve was closed per procedure, the 'D' Turbine Stop Valve unexpectedly closed. The 'A' and 'C' Turbine Control Valves were then challenged to control Turbine and Reactor pressure resulting in Reactor pressure and power oscillations. The causes of this event were inadequate procedural guidance and the failure to use conservative decision making strategy. Corrective actions included replacement of the defective solenoid valves, and the revision of the applicable testing and Operations performance standards procedures.
4162016005 | Grand Gulf 1 | 06/25/2016 | 08/16/2017 | ML17228A27 | <strong>Automatic Reactor SCRAM</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2016, at 1407 Central Daylight Time, Grand Gulf Nuclear Station was operating in Mode 1 at approximately 98.75 percent rated thermal power, performing final power ascension to 100% power with Reactor Recirculation Flow Control Valves, when an unplanned automatic reactor SCRAM occurred. All safety systems responded per design. Two Safety Relief Valves opened at the onset of the event to control reactor pressure and reseated properly. All control rods inserted when the signals generated by the Reactor Protection System were received. There were no Emergency Core Cooling System actuations. The shift immediately entered the appropriate Off Normal Event Procedures. The plant was stabilized with pressure control on the main turbine bypass valves and level control on the start-up level control valve. The cause of this event was a failed operational amplifier installed on circuit card that provided input to the Turbine Control System Channel 1. Corrective actions include the replacement of the rate limiter circuit cards with re-furbished cards. Future corrective actions will include the implementation of a modification to replace the turbine control system with a digital control system. There were no actual nuclear safety consequences or radiological consequences during the event.
4162016006 | Grand Gulf 1 | 06/30/2016 | 03/27/2017 | ML17086A17 | <strong>Multiple Valid Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2016 at 1715 CDT, Grand Gulf Nuclear Station (GGNS) experienced an electrical power supply loss from Service Transformer 21 which resulted in power supply being lost to Division 2 (16AB Bus) and Division 3 (17AC Bus) ESF buses. This resulted in a valid actuation of Division 2 and Division 3 Diesel Generators on bus under voltage. They both automatically started and energized their respective ESF buses as designed. During this event, the loss of power to the Division 2 (16AB Bus) resulted in a Division 2 RPS bus power loss, which actuated a Division 2 RPS half SCRAM signal. <br /><br /> The power loss also resulted in a loss of the Instrument Air pressure resulting in some Control Rod Scram Valves to drift open. This in turn caused the Scram Discharge Volume to fill to the point where a Division 1 RPS half SCRAM signal was initiated from Scram Discharge Volume level high on Channel 'A'. This resulted in a valid full RPS Reactor SCRAM while not critical. Instrument Air pressure was restored and the SCRAM signal was reset at 1733 CDT. Appropriate off normal event procedures were entered to mitigate the transient. All safety systems performed as expected. <br /><br /> The Direct Cause was a failure of the taped insulation on the 'C' phase 34.5 kV Service Transformer power supply cable to the BOP 23 Transformer. The Apparent Cause was an outer tape wrap insulation failure that left a moisture path between the braid, connecting the splice, and the center conductor. A temporary three phase overhead line was installed to bypass the faulted 34.5 kV cable section. A planned corrective action to install a permanent underground replacement was generated.
4162016007 | Grand Gulf 1 | 09/08/2016 | 06/29/2017 | ML17180A31 | <strong>Technical Specification Shutdown Because of the Loss of the Residual Heat Removal Pump</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2016 at 02:58, Grand Gulf Nuclear Station entered three TS LCO Action Statements because RHR 'A' pump was declared inoperable. <br /><br /> LCO Action Statements entered: <br /> 1) 3.5.1 for one low pressure ECCS injection/spray subsystem, <br /> 2) 3.6.1.7 for one RHR containment spray subsystem, and <br /> 3) 3.6.2.3 for one RHR suppression pool cooling subsystem. All have 7 day Completion Times. <br /><br /> A decision was made to shutdown the plant to repair the RHR 'A' pump because, based on the troubleshooting and testing plan, the pump could not be repaired and returned to service with the LCO Completion Times. At 0300 CDT on 09/08/16, GGNS initiated the transition to Mode 4. <br /><br /> The Direct Cause was the pump's inability to develop a TS differential pressure of 131 psid. <br /><br /> The Apparent Cause revealed defects in the manufacturing process which led to inter-column leakage; misalignment between rotating and stationary elements; and machined registered fits that were out-of-tolerance.<br /><br /> The failed pump was removed and sent to the vendor facility for failure analysis. A replacement pump was installed and tested satisfactorily. RHR 'A' was returned to operable.
4162016008 | Grand Gulf 1 | 09/09/2016 | 08/16/2017 | ML17228A23 | <strong>Entry into Mode of Applicability with the Alternate Decay Heat Removal System Inoperable</strong><br /><i>Abstract:&nbsp;</i>Entergy manually shutdown the Grand Gulf Nuclear Station (GGNS) reactor on September 8, 2016, at approximately 1104 hours, to replace Residual Heat Removal (RHR) Pump 'A' after it failed its technical specification surveillance. The reactor entered MODE 4, Cold Shutdown, at approximately 0509 hours on September 9, 2016. Residual Heat Removal Train 'B' was placed in shutdown cooling mode (SDC) to maintain Reactor coolant temperature 110 degrees Fahrenheit (F) to 120 F on September 9, 2016 at 0332. At the time of entry into MODE 4, and throughout the time period the 'A' RHR pump was inoperable, the Alternate Decay Heat Removal (ADHR) System was not available because the ADHR heat exchangers tube-side cooling water system had been clearance-tagged CLOSED to support cleaning of the heat exchanger tubes since August 10, 2016. This condition was not identified until September 23, 2016, after the 'A' RHR train was returned to OPERABLE status. The Direct Cause of the event is the Plant Service Water (PSW) supply isolation valves for the ADHR Heat Exchangers were not returned to the normal OPEN position after Heat Exchanger cleaning. The root causes were the inconsistent reinforcement of nuclear professional behaviors in the Operators and insufficient detail in operating procedures associated with the operation of the ADHR system. Corrective actions included the strengthening and reinforcement site of administrative controls to ensure personnel understood and adhered to the site's standards for nuclear professional behaviors for Operations personnel, and the revision of site operational procedures to include directions to verify PSW flowrate through the ADHR H/X when placing the system in STANDBY.
4162016009 | Grand Gulf 1 | 03/27/2016 | 08/16/2017 | ML17228A27 | <strong>Entry into Mode of Applicability with the Oscillation Power Range Monitor Upscale Settings Incorrectly Set</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2016, Entergy, while returning the GGNS Unit 1 to power operations at the conclusion of Refueling Outage 20, reactor thermal power was allowed to exceed 16.8 percent without first calibrating the Oscillation Power Range Monitor (OPRM) to include the new limits required by the adoption and implementation of the Maximum Extended Load Limit Line Plus (MELLLA+) operating range. Specifically, the OPRM Upscale setting requirements specified in Technical Specification 3.3.1.1, Reactor Protection System (RPS) Instrumentation, Table 3.3.1.1-1, Reactor Protection System Instrumentation, Function 2, Average Power Range Monitors, Sub-Function f. OPRM Upscale were not fully met. The direct cause of this event was the failure to ensure the required procedure changes were incorporated and performed prior to the unit entering the mode of applicability. The apparent cause was personnel involved with the modification did not communicate adequately and follow-up to ensure technical information was incorporated into the appropriate procedures. Corrective Actions include: Updating of the procedures, correctly setting and fully testing the OPRM upscale settings, performance of briefings with personnel on the lessons learned, and conducting follow-up reviews to ensure the briefings were understood. This event is reportable as a licensee event report (LER) in accordance with 10CFR50.73(a)(2)(i)(B).
4232016001 | Millstone 3 | 01/25/2016 | 03/16/2016 | ML16082A26 | <strong>Automatic Reactor Trip on Reactor Coolant System Low Flow due to Loss of 'B' Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2016 at 0147 hours an automatic reactor trip occurred at Millstone Power Station Unit 3 while the unit was in Mode 1, operating at 100 percent power due to a trip of the 'B' Reactor Coolant Pump. The 'B' Reactor Coolant Pump tripped on a ground fault, which in turn caused the Unit 3 reactor to trip on reactor coolant system low loop flow (Reactor Protection System actuation). All control rods fully inserted into the reactor. The auxiliary feedwater pumps started as designed on low steam generator level and operators maintained steam generator level. All other post trip actions were standard and all safety systems operated as expected. <br /><br /> The 'B' Reactor Coolant Pump trip was caused by failure of one of three motor capacitors on the Reactor Coolant Pump motor. The failed capacitor on the affected Reactor Coolant Pump motor was replaced and the integrity of the motor windings, cabling, breaker, and associated protective relays were verified. Based on an assessment of the event, the risk impact was determined to be very small. There were no radiological challenges and the health and safety of the public were not affected. <br /><br /> The actuation of the reactor protection system and the automatic start of the auxiliary feedwater pumps is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4232016002 | Millstone 3 | 01/25/2016 | 03/23/2016 | ML16092A06 | <strong>Feedwater Isolation Signal Defeated due to Wiring Error</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2016 an automatic reactor trip occurred on Millstone Power Station Unit 3 [LER 2016-001-00]. Following the Millstone Power Station Unit 3 reactor trip, (Mode 3, 0% power), while operators were performing feedwater isolation actuation verification steps, it was identified that the 'C' Feedwater Isolation Valve, 3FWS*CTV41C, did not auto-close as expected. Operators subsequently closed 3FWS*CTV41C from the control room. <br /><br /> Troubleshooting identified that a temporary jumper, associated with a maintenance activity completed in November 2014, was inadvertently left installed due to a human performance error. This jumper bypassed the input from the Solid State Protection System to isolate 3FWS*CTV41C upon receipt of an actuation signal. This input is required by Technical Specification 3.3.2 and Table 3.3-3, Engineered Safety Features Actuation System Instrumentation. The function to automatically isolate 3FWS*CTV41C was thus defeated. However, the safety function to isolate feedwater was met due to redundant valves in series that operated correctly via the 'C' feed regulating valve and the 'C' feed regulating bypass valves. Also, the containment isolation function was not lost as the valve, 3FWS*CTV41C, was capable of remote operation from the control room. <br /><br /> This condition is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) as any operation or condition that is prohibited by the plant's Technical Specifications. The jumper was removed and the valve was verified to be OPERABLE.
4232016003 | Millstone 3 | 04/09/2016 | 06/08/2016 | ML16165A48 | <strong>Loss of Safety Function-Supplementary Leak Collection and Release System</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2016, while in MODE 1 and reducing power to enter a scheduled refueling outage (RFO), MiIlstone Power Station Unit 3 (MPS3) performed the 'B' train Supplementary Leak Collection and Release System (SLCRS) Negative Pressure Verification Surveillance. This test was completed with unsatisfactory results. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.6.1 was entered. Later, on April 9, 2016, with the reactor in MODE 1 and approximately 24 percent power, MPS3 operators conducted the 'A' train SLCRS Negative Pressure Verification Surveillance with unsatisfactory results. Because both trains of SLCRS failed the required surveillances, TS LCO 3.6.6.2 was entered. Operations continued with the planned plant shutdown associated with the RFO and entered COLD SHUTDOWN, MODE 5 at 1241 on April 10, 2016. <br /><br /> SLCRS did not meet the acceptance criteria due to the aggregate impact of a number of dampers not providing effective isolation. SLCRS was restored to operable condition prior to entering MODE 4 when starting back up from RF017. Detailed procedural steps are being developed for verifying the closed position of SLCRS isolation dampers and being incorporated into the damper post maintenance testing matrix. Associated surveillance procedures are being revised to improve monitoring program for SLCRS isolation dampers.<br /><br /> Since both trains of SLCRS failed to meet TS acceptance criteria, this condition is reportable pursuant to 10CFR50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function for systems or structures to control the release of radioactive material, and 10CFR50.73(a)(2)(v)(D) to mitigate the consequences of an accident.
4232016004 | Millstone 3 | 05/15/2016 | 07/13/2016 | ML16208A05 | <strong>Manual Reactor Trip due to Low Hydrogen Gas Pressure In Main Generator</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2016, with Millstone Power Station Unit 3 (MPS3) operating in MODE 1 at 74% power, the operators observed decreasing hydrogen pressure in the main turbine generator. Upon field investigation it was determined there was an active hydrogen leak from the main generator. The operators manually tripped the reactor and vented the hydrogen from the main generator. The reactor trip was uncomplicated. The auxiliary feedwater (AFW) pumps started as designed on low steam generator level and operators maintained steam generator level. <br /><br /> The active hydrogen leak was the direct cause of the manual reactor trip. The hydrogen leak was caused by a dislodged plug on a port on the main generator. MPS maintenance procedures did not contain adequate procedural guidance in that there was no specific direction for installation, i.e., torque value and verifications. The procedures will be revised to include specific direction to tighten the plugs and applicable verifications (i.e., torque value, peer checking). Additional corrective actions are being taken in accordance with the station's corrective action program. <br /><br /> The actuation of the RPS and the automatic start of the AFW pumps is being reported in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4232016005 | Millstone 3 | 06/12/2016 | 08/09/2016 | ML16230A00 | <strong>Technical Specification Required Shutdown and Manual Reactor Trip due to Steam Generator Level Oscillation</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2016, with Millstone Power Station Unit 3 operating in MODE 1 at 100% power, operators identified the third stage of the "A" Reactor Coolant Pump (RCP) seal had failed, which resulted in an unidentified Reactor Coolant System leak greater than the Technical Specification (TS) limit of 1 gallon per minute. Operators initiated a plant shutdown as required by TS 3.4.6.2 ACTION Statement b. During the downpower, steam generator levels were not adequately maintained and the Engineered Safety Features Actuation System generated a Turbine Trip and Feed Water Isolation on Steam Generator Water Level - High-High being exceeded on the 'B' steam generator. In response, operators manually tripped the reactor at 23:37 (MODE 1, at approximately 20 % power). The auxiliary feedwater system started as designed. Safety systems functioned as expected. There were no radiological challenges as a result of the event. The plant entered COLD SHUTDOWN on June 14, 2016 at 01:29. <br /><br /> The cause of the unidentified leak was a failed third stage on the "A" RCP seal. The seal was replaced. The cause of the feedwater transient and resultant manual reactor trip was due to operator performance in controlling steam generator level. This is being addressed in the Corrective Action Program.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Additionally, the plant shutdown is being reported in accordance with 10 CFR 50. 73 (a)(2)(i)(A) as the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
4252016002 | Vogtle 2 | 05/25/2016 | 07/21/2016 | ML16203A33 | <strong>Unit 2 Trip on Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2016 at approximately 0206 Eastern Daylight Time, the Unit 2 was operating in Mode 1 and 100 percent power when the reactor tripped due to low-low level in Steam Generator 1. All control rods fully inserted into the core and all safety systems actuated as designed.<br /><br /> The unit was stabilized in Mode 3 with decay heat being removed through the main steam lines to the steam dumps and to the condenser. The low-low level in Steam Generator 1 was due to a human performance error by technicians performing a loop calibration on the Steam Generator 1 level instrumentation. This error resulted in a perceived high level into the Steam Generator Water Level Control system. In response, the Feedwater regulating valve closed which lowered actual level in Steam Generator 1. <br /><br /> Because all control rods fully inserted into the core and all the safety systems actuated as designed, this event had no adverse effect on the health and safety of the public, and is of very low safety significance. This event is reportable per 10 CFR 73(a)(2)(iv)(A), due to the actuation of a system listed in 10CFR 50.73(a)(2)(iv)(B).
4402016001 | Perry | 01/24/2016 | 12/21/2016 | ML16364A20 | <strong>Pressure Boundary Leakage, Level 8 Automatic SCRAM, and APRM Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>At 2100 hours, on January 23, 2016, the Perry Nuclear Power Plant (PNPP) commenced a reactor shutdown to investigate unidentified leakage in the drywell. At 2122 hours, drywell unidentified leakage exceeded Technical Specification (TS) limits necessitating a plant shutdown as required by TSs. At 0357 hours, on January 24, 2016, while performing the shutdown required by plant TSs, the average power range monitors (APRM) became inoperable due to a calibration setpoint being out of tolerance in the nonconservative direction following a transfer of the reactor recirculation pumps to slow speed. This resulted in a loss of safety function for the APRMs. At 1007 hours, on January 24, 2016, with the plant at 8 percent power, during a feedwater shift to place the motor feed pump in service, reactor water level rose to the level 8 setpoint and the reactor protection system (RPS) automatically initiated, shutting down the reactor. Following the shutdown, a small leak was identified on the reactor recirculation loop "A" pump discharge valve vent line. The recirculation loop is part of the reactor coolant system; this resulted in a degraded condition and a condition prohibited by TS due to pressure boundary leakage. <br /><br /> The cause of the recirculation loop vent line leak was that the weld connecting the root appendage was not performed per the design drawing. The APRM calibration issue was caused by a change to the feedwater flow input to the heat balance. The cause of the reactor level rise and subsequent high water level scram was due to operator error in monitoring and manipulating feedwater system indications and controls.<br /><br /> The safety significance of this event is considered to be small. These events are being reported under; 50.73(a)(2)(i)(A), for completion of any plant shutdown required by the plant's TS; 50.73(a)(2)(ii)(A) for a condition resulting in the plant's principle safety barrier being seriously degraded; 50.73(a)(2)(i)(B) for a violation of Technical Specifications; 50.73(a)(2)(iv)(A) for actuation of the RPS while critical; and 50.73(a)(2)(v)(A) for a loss of safety function.
4402016002 | Perry | 02/08/2016 | 04/08/2016 | ML16104A02 | <strong>Manual Reactor SCRAM Due to Spurious Opening of Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2016, at 1503 hours, control room operators initiated a manual reactor protection system (RPS) actuation in response to rising temperature in the suppression pool. All control rods full inserted. Prior to the RPS actuation the plant was in mode 1 at approximately 96 percent rated thermal power. At 1500 hours, multiple safety relief valves (SRVs) partially opened due to an invalid reactor pressure vessel (RPV) pressure signal. Control room indications showed two SRVs remained open resulting in a suppression pool temperature rise. Suppression pool cooling was initiated and a plant cooldown to Mode 4 was initiated. <br /><br /> The direct cause of the event was a momentary pressure perturbation limited to the RPV B reference leg that caused the connected transmitters to sense RPV pressure and level changes that resulted in SRV actuation. Corrective actions include revision to plant procedures for operation of the RPV reference legs and associated purge panels, and changes to the time constants for the affected RPV transmitters. <br /><br /> The safety significance of this event is considered to be very small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in a manual actuation of the RPS.
4402016003 | Perry | 02/11/2016 | 12/21/2016 | ML16364A21 | <strong>Loss of Safety Related Electrical Bus Results in a Loss of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2016, at approximately 1505 hours with the plant in mode 4, an indicated loss of power to the division 1 4160 volt bus, EH11, occurred. An invalid undervoltage signal tripped the bus supply breaker, and the bus loads shed, as expected. The invalid undervoltage signal resulted in a loss of shutdown cooling. The division 1 diesel generator (DG) started and loaded the EH11 bus. Subsequently the division 1 DG was manually shutdown due to cooling water not being available. This de-energized all division 1 equipment, including the train supplying shutdown cooling at the time. To comply with Technical Specification 3.4.10 the alternate decay heat removal (ADHR) system was credited as the alternate method of decay heat removal for the inoperable shutdown cooling system; even though other systems were available, the ADHR system was not filled and vented, thus, it was not immediately available. Shutdown cooling was re-established 42 minutes later from division 2. <br /><br /> A manufacturing defect in a fuse caused the event. A 10 CFR Part 21 report was filed by the supplier on March 22, 2016. This is being reported under 50.73(a)(2)(iv)(A) as an invalid actuation and 50.73(a)(2)(i)(B) for an operation or condition prohibited by technical specifications. <br /><br /> Corrective actions were taken to replace and analyze the defective fuse. Fuses with the same batch will be sent for analysis. The vendor's 10 CFR Part 21 analysis is also being tracked. <br /><br /> The safety significance is determined to be an event of very small risk significance based on a qualitative defensive in-depth risk assessment.
4402016004 | Perry | 12/28/2016 | 02/24/2017 | ML17055C35 | <strong>Loss of Safety Function due to Two Inoperable Standby Liquid Control Subsystems</strong><br /><i>Abstract:&nbsp;</i>On December 28, 2016, at 2119 hours (EST), standby liquid control (SLC) subsystem A was declared inoperable in accordance with the surveillance instruction for performance of a routine surveillance test. At 2229 hours, control room operators received an out-of-service alarm for SLC discharge valve B. With both subsystems inoperable, the SLC system was in a condition that required reporting under 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D). At 2335 hours, the surveillance was completed and subsystem A was declared operable. <br /><br /> The cause for subsystem B inoperability was an indicated loss of continuity to one of the two firing circuits in the discharge valve due to a loose connection between a pin and jack on the connector. This was not a safety system functional failure since continuity was interrupted to only one of the two redundant firing circuits for discharge valve B and if an initiation signal was sent to the valve, it would have operated as designed and supported chemical injection to the vessel. The risk of this event is considered small in accordance with the regulatory guidance. The power supply cable was replaced and post maintenance testing was completed satisfactorily. The preventative maintenance task will be revised to include a step to inspect connection pins and jacks when changing the firing assembly. Additionally, the cable on the discharge valve for SLC subsystem A will be replaced and sent to FirstEnergy BETA Laboratory for analysis when the valve is replaced during the next refueling outage. The analysis will be used to determine if a new preventative maintenance task is necessary for periodic replacement of these cables.
4432016001 | Seabrook | 03/02/2016 | 04/26/2016 | ML16123A11 | <strong>Automatic Reactor Trip due to Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2016 at 0253 while operating at 100% power, Seabrook Station experienced an automatic reactor trip due to a turbine trip. A failure of inverter ED-I-11 caused a voltage transient in the power supplies for the Turbine Control System (TCS). The TCS is designed with redundant inverters so that the loss of one inverter will not cause a system failure. However, during this event, the inverter failure caused a voltage increase which exceeded the voltage limits of the TCS power supplies causing them to momentarily shut down. Loss of the TCS power supplies initiated an automatic turbine trip signal, which in turn actuated an automatic reactor trip as designed. Other plant equipment functioned as expected and no adverse consequences resulted from this event. <br /><br /> The direct cause of the event was a failure of inverter ED-I-11 which resulted in an overvoltage condition to the turbine control system. At this time, the cause of the failure of the inverter has not been determined. If additional troubleshooting identifies a cause, this LER will be supplemented. Immediate corrective action was implementation of a temporary modification to energize the power panel normally fed by ED-I-11 to eliminate single point vulnerability. Planned corrective actions are to continue troubleshooting and repair of inverter ED-I-11, install overvoltage protection for the TCS cabinets and upgrade the TCS power supplies to higher voltage rated units.
4432016002 | Seabrook | 03/02/2016 | 04/26/2016 | ML16123A11 | <strong>Emergency Feedwater System Actuation on Steam Generator Low-Low Level</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2016 at 1312 hours, during a plant cooldown, a valid actuation of the emergency feedwater system (EFW) occurred when B steam generator levels reduced to 20%. The lowering level was a result of the unanticipated tripping of the start up feed pump on low condensate storage tank level while it was the feed source to the steam generators. The start up feed pump was restarted and feed flow had been restored when the actuation took place. No adverse consequences resulted from this event. <br /><br /> The cause of the event is the on-shift operating crew was processing multiple procedure sections in parallel resulting in steps being performed out of sequence. Corrective action is to develop and deliver a case study outlining the event and clearly establishing operations leadership positions on procedure use.
4452016001 | Comanche Peak 1 | 06/22/2016 | 08/22/2016 | ML16245A23 | <strong>Safety Chiller Inoperable for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 1005 on June 9, 2016, during routine periodic predictive maintenance thermography activities, the 'A' phase connection to the Unit 1, Train A Safety Chiller was identified to be at an elevated temperature. Inspection found three of the six electrical connections associated with the chiller to be un-torqued. Subsequent investigation found the affected connections should have been torqued on May 10, 2016 as part of restoration actions following planned preventive maintenance. On June 22, 2016 an evaluation was completed that determined the Unit 1, Train A Safety Chiller was inoperable from May 28, 2016 to June 9, 2016.<br /><br /> The cause of this event was the restoration and post work activities by Maintenance personnel did not ensure that the Unit 1, Train A Safety Chiller was properly configured per procedure and ready to be turned over to Operations. Corrective actions included replacing the Phase 'A' cable and dashpot relay and re-torqueing the Phase 'B' and 'C' dashpot relay terminations. The applicable procedure will be revised before the next scheduled performance to have the equipment specific thermography inspection performed as a part of the maintenance restoration/post work activities. <br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
4452016002 | Comanche Peak 1, Comanche Peak 2 | 09/13/2016 | 02/22/2017 | ML17062A30 | <strong>Unanalyzed Condition Involving Potential Moderate Energy Line Break</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2016, and September 14, 2016, during plant walk downs by Engineering and the NRC Senior Resident inspector, pressurized fire protection piping in the Service Water Intake Structure was found to not be shielded against a Moderate Energy Line Break (MELB), resulting in inoperability of one train of Service Water for both units.<br /><br /> During extent of condition walk downs conducted on October 6, 2016, October 10, 2016, November 17, 2016, December 5, 2016, and December 22, 2016, additional piping in the Unit 1 and Unit 2 Safeguards and Auxiliary Buildings was found to not be shielded against a MELB, resulting in inoperability of one train of various safety related equipment for both units. The most likely cause of this event was the methodology used to conduct the initial MELB walk downs was flawed and allowed some MELB threats to be missed. Corrective actions include shielding the affected piping, performing a 100 percent walk down of rooms containing MELB piping identified for shielding, and revising the systems interaction program maintenance procedure. <br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
4542016001 | Byron 1, Byron 2 | 03/04/2016 | 05/03/2016 | ML16124A04 | <strong>Auxiliary Feedwater Diesel Intake Design Deficiency Related to Turbine Building High Energy Line Break Resulted in an Unanalyzed Condition due to Insufficient Validation of Vendor Analysis Inputs</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2016, during the Braidwood NRC Component Design Basis Inspection, a concern was raised regarding why it was acceptable for the diesel driven Auxiliary Feedwater (AF) pump engine combustion air intake to be located in the turbine building, a non-safety related structure. On March 7, 2016, the additional evaluations that were completed for Byron determined that the existing configuration did not adequately support diesel engine operation with high energy line break (HELB) conditions in the turbine building, and at 0400 hours Operations entered Technical Specification Limiting Condition for Operation 3.7.5, "Auxiliary Feedwater (AF) System," Condition A, "One AF train inoperable," for one train (B-train) of AF inoperable for both Units 1 and 2. The AF trains were declared operable following a corrective action to install a temporary configuration change to provide an engine combustion air intake from the auxiliary building.<br /><br /> The cause of the event was insufficient validation of vendor analysis inputs in 1993 while reviewing the AF diesel engine's ability to function during a turbine building HELB event. <br /><br /> The corrective actions planned are to develop and install a permanent modification to re-route the AF diesel engine intakes for Unit 1 and 2.
4552016001 | Byron 2 | 10/12/2016 | 02/15/2017 | ML17046A01 | <strong>Manual Reactor Trip due to Circuit Breaker Failure That Caused Actuation of Feedwater Hammer Prevention System with Automatic Isolation of Feedwater to Two Steam Generators and Low Steam Generator Levels</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2016 at 1338 hours, Byron Station Operations initiated a manual reactor trip of Unit 2 due to decreasing water levels in the loop B and loop C Steam Generators. A trip of a bus feed breaker resulted in the loss of power feed to multiple normally energized relays associated with the Feedwater (FW) Water Hammer Prevention System (WHPS) circuit, which resulted in automatic closure of related Feedwater Isolation Valves.<br /><br /> The apparent cause of the feed breaker trip was due to a manufacturing defect on the feed breaker amptector circuit board. <br /><br /> The corrective actions planned include revising refurbishment testing requirements for the main feed breaker and performing modifications in subsequent refuel outages to the FW Water Hammer Prevention System to address power supply single point vulnerability. <br /><br /> The Unit 2 Reactor Protection System was actuated by the manual reactor trip and the Auxiliary Feedwater system actuated automatically as expected. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4562016001 | Braidwood 1, Braidwood 2 | 03/04/2016 | 04/28/2016 | ML16119A29 | <strong>Auxiliary Feedwater Diesel Intake Design Deficiency Related to Turbine Building High Energy Line Break Resulted in an Unanalyzed Condition due to Insufficient Validation of Vendor Analysis Inputs</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2016, during the NRC Component Design Basis Inspection, a concern was raised regarding why it was acceptable for the diesel driven auxiliary feedwater (AF) pump engine combustion air intake to be located in the turbine building, a non-safety related structure. On March 6, 2016, the additional evaluations that were completed determined that the existing configuration did not adequately support diesel engine operation with high energy line break (HELB) conditions in the turbine building, and at 2000 hours, Operations entered Technical Specification Limiting Condition for Operation 3.7.5, "Auxiliary Feedwater (AF) System," Condition A, "One AF train inoperable," for one train (B-train) of AF inoperable for both Units 1 and 2. The AF trains were declared operable following a corrective action to install a temporary configuration change to provide engine combustion air intake from the auxiliary building. <br /><br /> The cause of the event was insufficient validation of vendor analysis inputs in 1993 while reviewing the AF diesel engine's ability to function during a turbine building HELB event. <br /><br /> The corrective actions planned are to develop and install a permanent modification to re-route the AF diesel engine intakes for Unit 1 and 2.
4562016002 | Braidwood 1, Braidwood 2 | 05/25/2016 | 07/19/2016 | ML16201A33 | <strong>Inadequate Protection from Tornado Missiles Identified due to Non-Conforming Design Conditions</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2016, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornadoes, Braidwood identified non-conforming conditions in the plant design such that specific TS equipment on both units was considered to not be adequately protected from tornado missiles. <br /><br /> On May 25, 2016 at 1415 Operations declared the affected equipment inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance" and the required compensatory measures, and then declared the affected equipment operable but non-conforming. <br /><br /> The cause of this issue was a lack of clarity and changing requirements during the original licensing of the plants which led to inadequate understanding of the original NRC regulatory guidance. <br /><br /> The corrective actions planned are to complete the EGM 60-day comprehensive compensatory measures to demonstrate a discernible change from its pre-discovery actions, to modify the refueling water storage tank hatches to eliminate the tornado missile vulnerability, and to obtain and implement a license amendment for an analytical solution dispositioning tornado generated missile nonconforming conditions.
4562016003 | Braidwood 1 | 10/02/2016 | 11/23/2016 | ML16328A12 | <strong>Indication in Control Rod Drive Mechanism Nozzle Weld due to Embedded Flaws Opening Up from Thermal and Pressure Stresses During Operation</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2016, during the liquid penetrant examination on the weld build up for control rod drive mechanism (CRDM) Penetration 69 during refueling outage A1R19, two rejectable rounded indications were documented. The first was a 7/32 inch rounded indication on the reactor head portion of the weld build up which was 4 inches from the transition of the head to penetration. The second was a 1/4 inch rounded indication located at the transition of the head to penetration. The transition is the point where the vertical portion of the penetration meets the horizontal area of the reactor head. This LER is being submitted in follow-up to ENS 52275.<br /><br /> Based on industry experience, the cause of this event was determined to be mechanical discontinuities/minor subsurface voids opening up to the weld surface due to thermal and/or pressure stresses during plant operation. <br /><br /> The indications in penetration 69 were reduced to an acceptable dimension by manual buffing. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), "any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded" since the as found indication did not meet the applicable acceptance criterion referenced in ASME Code Case N-729-1 to remain in-service without repair.
4582016001 | River Bend | 01/05/2016 | 03/07/2016 | ML16084A14 | <strong>Potential Loss of Secondary Containment Safety Function due to Failure of Auxiliary Building Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On January 5, 2016, at 10:58 p.m. CST, with the plant operating at 100 percent power, the main control room alarm indicating high pressure in the auxiliary building actuated. Operators confirmed that the building pressure was out of specification. Secondary containment was declared inoperable, and the Division 2 standby gas treatment system was started. This action restored building pressure to the acceptable range, and secondary containment was declared operable at 12:27 a.m. on January 6. An inspection of the auxiliary building normal ventilation system found that discharge dampers on the exhaust fans were degraded, and the flow control damper on the supply fans was not operating correctly. In order to restore the normal ventilation system to service, the troubleshooting plan for this condition temporarily altered the operating configuration of the system to close the suction damper on the idle exhaust fan. This prevents backflow through the idle fan, allowing the system to control building pressure within the required operating range. Corrective maintenance is being planned to restore the material condition of the normal ventilation system. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event that caused the secondary containment to be potentially incapable of performing its safety function.
4582016002 | River Bend | 01/09/2016 | 03/07/2016 | ML16084A14 | <strong>Automatic Reactor Scram and Division 2 Primary Containment Isolation due to Offsite Grid Electrical Transient</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2016, at approximately 2:37 a.m. CST, with the plant operating at 100 percent power, an automatic reactor scram occurred concurrent with the closure of all main steam isolation valves (MSIVs). That action was the result of an electrical transient caused by a phase-to-phase fault on a nearby 230kV transmission line. The transient caused a momentary decrease in the voltage on both reactor protection system busses, which also power the MSIV control solenoids. The Division 2 primary containment isolation logic was also actuated, causing the Division 2 valves in balance-of-plant systems to close. Both divisions of the standby gas treatment system automatically started due to the shutdown of the normal annulus pressure control system. Both reactor recirculation pumps downshifted to slow speed. The company's transmission department investigated the event. Although no definite source of the fault was found, it was concluded that a lightning strike likely caused the transient. The fault occurred on a 230kV transmission line approximately three miles from the station. The fault lasted for 5.4 cycles before it was isolated by automatic breaker action, and caused the voltage on the switchgear supplying the RPS busses to decrease to approximately 34 percent of normal. This transient was sufficient to trip the scram solenoids and the MSIV solenoids. No plant parameter limits requiring the automatic actuation of any of the emergency core cooling systems or the emergency diesel generators were exceeded. This event, thus, was of minimal significance to the health and safety of the public. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an actuation of the reactor protection system and the primary containment isolation logic.
4582016003 | River Bend | 01/19/2016 | 06/08/2017 | ML17163A20 | <strong>Operations Prohibited by Technical Specifications due to Reactor Control Blade Drift During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2016, at 5:28 a.m. CST, while conducting core alterations, an alarm was actuated in the main control room alarm indicating that a reactor control blade had drifted out of the fully inserted position. At the time, a fuel bundle was being raised out of the core, and the control blade in the same cell drifted out one notch with no "withdraw" command present. This condition actuated a corresponding alarm on the refueling platform, and system interlocks stopped the platform hoist with the fuel bundle partially withdrawn. When the control blade moved from the fully inserted position, the Technical Specification applicability for the intermediate range neutron monitoring system was inadvertently entered, while a certain function of those instruments was not operable. This event constituted operations prohibited by Technical Specifications, and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). After a detailed assessment of the situation, the fuel bundle and the control blade were returned to their original positions. The drive mechanism for the control blade was disabled, and the control blade remained fully inserted for the remainder of the fuel cycle. In the recent refueling outage that commenced on January 28, 2017, the control blade was removed and inspected. This event was caused by the development of a bulge in one or more of the wings on the affected control blade that caused sufficient friction to support the blade without the collet fingers in the drive mechanism being engaged. No other control blades were affected at the time of the original event in January 2016. The operational cycle was successfully completed with the blade fully inserted. This event was, thus, of minimal safety significance to the health and safety of the public.
4582016004 | River Bend | 01/29/2016 | 03/29/2016 | ML16097A41 | <strong>Actuation of the Division 1 Emergency Diesel Generator and Primary Containment Isolation Logic Due to Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On January 29, 2016, at 1518 CST, with the plant in cold shutdown, power was lost on reserve station service (RSS) line no. 1. This is one of two sources of offsite power required by Technical Specifications. The power loss de-energized the Division 1 onsite AC safety.- related switchgear, causing an automatic start of the Division 1 emergency diesel generator (EDG). The Division 1 reactor protection system (RPS) bus was also de-energized, causing a half-scram signal. Approximately 8 minutes later, a full actuation of the RPS occurred due to high water level in the control rod drive hydraulic system scram discharge volume header. All reactor control rods were already fully inserted. The loss of Division 1 RPS also caused the actuation of the Division 1 primary containment isolation logic. The Division 1 isolation valves in the balance-of-plant systems closed as designed. Both trains of the standby gas treatment system actuated. The loss of RSS No. 1 was caused when company transmission department personnel working in the local 230kV switchyard executed a deficient work instruction while modifying relay settings. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as the automatic actuation of the Division 1 EDG, the Division 1 primary containment logic, and the reactor protection system (while subcritical). At the time of the event, the shutdown cooling system was operating on the Division 2 subloop, which was unaffected. The Division 1 EDG performed as designed. This event was, thus, of minimal significance to the health and safety of the public.
4582016005 | River Bend | 02/24/2016 | 04/25/2016 | ML16126A22 | <strong>Potential Loss of Safety Function of Onsite AC Sources and Operations Prohibited by Technical Specifications due to Uncorrected Circuit Breaker Control Logic Design Causing Intermittent Failure to Close</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2016, with the plant in cold shutdown, the operations shift manager was made aware of a notification regarding a certain model of Masterpact 480-volt circuit breakers that described a failure mode that could potentially prevent the automatic closure of the breakers. Assessment of this information determined that the susceptible breakers included those powering the emergency ventilation fans in the Division 1 and 2 emergency diesel generator rooms and two auxiliary building unit coolers. This condition required that both diesel generators and both trains of shutdown cooling and to be declared inoperable. This constituted a condition that could potentially prevent fulfillment of the safety function of onsite AC power sources and decay heat removal. The Division 2 residual heat removal loop was operating in shutdown cooling, satisfactorily maintaining reactor coolant temperature. The cause of the event is that station personnel failed to recognize the breakers' vulnerability to this failure mode. This directly resulted in the failure to take corrective action prior to this industry notification. The cause of the untimely corrective actions is that the breakers were incorrectly determined to be operable in 2014 when the condition was discovered. All the affected breakers were modified to eliminate the failure mode prior to the subsequent plant startup.
4582016006 | River Bend | 05/13/2016 | 07/12/2016 | ML16208A05 | <strong>Potential Loss of Safety Function of Multiple Systems due to Design Deficiency in 480-volt Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>At 1200 CDT on May 13, 2016, while the plant was operating at 100 percent power, the shift manager was notified of a design inadequacy that could potentially prevent both divisions of the standby gas treatment system (GTS) from performing its design function. Under certain specific conditions, the 480-volt circuit breakers supplying the GTS fans may not re-close following a trip signal. In the postulated condition in which a start signal is followed by an immediate (within 0.075 seconds) trip signal, the breaker could fail to close at the next attempt. As a result of this condition, both divisions of GTS were declared inoperable. The initial investigation of this condition determined that circuit breakers in the main control building air conditioning system (HVC) and the diesel generator building ventilation system (HVP) are also susceptible to this postulated failure mechanism. This defect has the potential to similarly cause the HVC and HVP systems to be incapable of performing their safety function. The affected circuit breakers in those systems have been modified to correct the deficiency. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) and (a)(2)(v)(D) as operations prohibited by Technical Specifications and an event that could have caused a loss of safety functions of the affected systems. The specific scenario in which this failure mechanism could plausibly have occurred is a highly unlikely event. Additionally, standing orders were already in place at the time of this event that directed the operators to take compensatory actions to preserve the safety function of the affected systems. Those orders will remain in effect until all modifications are complete. Thus, this condition does not represent a significant challenge to the health and safety of the public.
4582016007 | River Bend | 05/25/2016 | 10/04/2016 | ML16285A40 | <strong>Operations Prohibited by Technical Specifications due to Failure to Implement Required Actions Within Completion Time</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2016, it was determined that there had been a violation of Technical Specifications during a recent planned maintenance outage of the Division 1 diesel generator (DG). During that outage, three material deficiencies of various subcomponents were discovered while conducting maintenance tasks. The initial operability screening of each deficiency determined that the as-found condition did not, by itself, cause the DG to be inoperable. However, the associated condition report for each item was flagged as "inoperable." These determinations should have, thus, caused the operators to invoke the requirements of the TS to perform common cause evaluations to assure that the same conditions did not exist on the operable Division 2 DG. This action was not performed. Human performance evaluations of the operators involved in the condition report screening concluded that a cognitive, undocumented decision was made that the individual deficiencies did not meet the threshold of requiring a common cause evaluation. This event constituted operations prohibited by Technical Specifications, and is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B). The investigation of this event discovered a previous similar occurrence during a planned maintenance outage of the Division 2 DG in February 2014 which constituted operations prohibited by Technical Specifications, but which was not reported at the time. That event was later determined to have not defeated the safety function of the DG, and was, thus, of minimal significance with respect to the health and safety of the public
4612016001 | Clinton 1 | 01/20/2016 | 03/18/2016 | ML16082A28 | <strong>Continuous Containment Purge Exhaust Fan Trip due to Unvalidated Assumptions in Work Planning Resulted in an Unanalyzed Condition of Primary to Secondary Containment Differential Pressure and Safety System Functional Failure</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2016 at 1311, during planned clean and inspect maintenance activities on the 4160/480 Volt Unit Substation K (0AP52E), the Unit Substation K switchgear breaker 0AP52E-5D for Continuous Containment Purge (CCP) exhaust fan "A" was racked out which resulted in tripping off the CCP "B" exhaust fan. This event caused Clinton Power Station (CPS) to enter one hour Required Action A.1 under Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.1.4, Primary Containment Pressure, due to primary to secondary containment differential pressure being greater than +0.25 psid. Operations staff took appropriate actions to rack in breaker 0AP52E-5D to restart CCP "B" exhaust fan, restore primary to secondary containment differential pressure within limits at 1339. Event Notification #51669 was transmitted to the NRC on January 20, 2016 at 1731. The root cause of this event is the station did not validate assumptions resulting in an inadequate work package. Corrective actions include updating the maintenance planning checklist, performing a read and sign and presenting a case study to maintenance planning personnel on this event. This event is reportable under 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition and 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function.
4612016002 | Clinton 1 | 02/13/2016 | 04/13/2016 | ML16106A30 | <strong>Trip of Fuel Building Ventilation Exhaust Fan Due to Moisture Formation Resulting In the Loss of Secondary Containment Vacuum</strong><br /><i>Abstract:&nbsp;</i>On 02/13/2016 at 0206 (CST) the plant was at 99 percent reactor power when Fuel Building Exhaust Fan "A" (1VF04CA) tripped due to indicated high Secondary Containment (SC) vacuum during routine venting of the drywell per plant procedures. Following the fan trip, SC vacuum degraded, eventually exceeding the Technical Specification (TS) limit of 0.25 inch vacuum water gauge. The TS Limiting Condition for Operation (LCO) 3.6.4.1 Required Action A.1 and an Emergency Operating Procedure were entered. Plant Operations subsequently started the Standby Gas Treatment System (VG) and restored Secondary Containment within TS limits. An investigation determined that ice formed in the sensing line causing an inaccurate Secondary Containment vacuum reading on the indication and control loop for 1VFO4CA. This caused 1VF04CA to trip which in turn led to a loss of Secondary Containment vacuum. A cause evaluation established that prior instrument sensing line designs did not recognize the potential to trap water in the sensing line to the Secondary Containment pressure instrumentation. Corrective actions will include completing an engineering change to install an alternate Fuel Building Ventilation (VF) system sensing line design to prevent moisture accumulation line to ensure accurate indication and control of Secondary Containment pressure. This event is reportable under 10 CFR 50.73(a)(2)(v)(C).
4612016003 | Clinton 1 | 03/24/2016 | 05/23/2016 | ML16146A54 | <strong>Bypassing Both Divisions of Reactor Water Cleanup Leak Detection System is a Reportable Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2016, it was determined that placing both Reactor Water Cleanup System (RT) Leak Detection System (LD) bypass switches in the Bypass position per plant procedure when the RT Filter/Demineralizer (F/D) was placed in service following backwash and pre-coat operations on- January 25, 2016 was a reportable condition. Both divisions of the RT LD were bypassed for seven minutes. Backwashing and pre-coating a RT F/D is a normal system operation and not considered maintenance. A review of the Updated Safety Analysis Report (USAR) determined that the associated isolation functions are credited to mitigate the consequences of an RT pipe break accident described in USAR Chapter 6. Therefore, placing both divisions of RT LD in Bypass constituted a condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. The direction for bypassing the RT LD system had been included in procedures since 1989 but did not constitute a reportable event until the issuance of NUREG-1022, Rev. 3 in 2013. The failure to report this condition was caused by not revising plant procedures when the Exelon fleet reporting requirements were revised to align with NUREG-1022, Rev. 3.
4612016004 | Clinton 1 | 03/30/2016 | 05/27/2016 | ML16153A24 | <strong>Trip of Emergency Reserve Auxiliary Transformer Static VAR Compensator Causes Positive Secondary Containment Pressure Following Lightning Strike on 138 kV Offsite Source</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2016, at approximately 1545 CDT, the Main Control Room (MCR) received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) caused by a voltage transient on the 138 kV supply. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Action A.1 and A.2 were entered. As a result of the voltage transient, the Division 1 Fuel Building ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no operating VF fans, Secondary Containment (SC) vacuum rose to slightly greater than 0 inches water gauge (WG) which exceeded the TS requirement of greater than 0.25 inches vacuum WG. The MCR entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. The likely cause of the voltage transient on the 138 kV line was a lightning strike that occurred during thunderstorms in the area on the day of the event. SC vacuum was restored within TS requirements at 1550 CDT by starting the Standby Gas Treatment System. Corrective actions have been initiated to improve reliability of the 138 kV source. This event is being reported as a condition that could have prevented fulfillment of a safety function under 10 CFR 50.73(a)(2)(v)(C).
4612016005 | Clinton 1 | 04/02/2016 | 05/31/2016 | ML16155A08 | <strong>Insulator Failure on the Reserve Auxiliary Transformer Results in a Loss of Secondary Containment Vacuum</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2016, at approximately 1257 CDT the Main Control Room (MCR) received numerous annunciators that indicated a trip of the Reserve Auxiliary Transformer (RAT) and associated Static VAR Compensator (SVC). The MCR entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Actions A.1 and A.2. The Division 1 Fuel Building ventilation (VF) system isolation dampers closed due to loss of power causing a trip of VF supply and exhaust fans. With the VF fans inoperable, Secondary Containment (SC) vacuum rose to slightly greater than 0 inches water gauge (WG) which exceeded the TS requirement of greater than 0.25 inches vacuum WG. The MCR entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control, and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. SC vacuum was restored within TS requirements at 1300 by starting the Standby Gas Treatment (VG) system. The RAT was successfully returned to service following replacement of the broken 'A' phase insulator stack on the 345 kV Circuit Switcher 4538. The cause of this event was identified as the failure of the 'A' phase 4538, 345 kV Circuit Switcher insulator due to a manufacturing defect. The corrective actions included performing a risk review of all Ohio Brass Insulators for potential failure impact and creating a replacement strategy to replace the high risk and critical insulators. Replacement of the remaining Ohio Brass insulators in the switchyard will be completed by the end of C1R17.
4612016006 | Clinton 1 | 04/21/2016 | 06/10/2016 | ML16165A49 | <strong>Missed Surveillance Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2016, in preparation to reduce power in order to restore the `B' turbine driven reactor feed pump (TDRFP) Operations detected that Technical Specification (TS) Surveillance Requirement (SR) 3.3.2.1.2 had not been performed eight days earlier. On April 13, 2016 Operations lowered reactor power below the Control Rod Withdrawal Limiter (RWL) High Power Setpoint (HPSP) to remove 'B' TDRFP from service due to high vibrations. TS SR 3.3.2.1.2 requires a functional test of the 4-Notch Control Rod Withdraw Limit of the RWL within one hour of resetting the HPSP during a power reduction; if it has not been completed within the previous 92 days. The SR was last performed on April 26th, 2015 and was required to be performed on April 13, 2016. TS 3.3.2.1 Required Action A.1 requires with one or more RWL channels inoperable, to immediately suspend control rod withdrawal. Contrary to this requirement, control rods were withdrawn to restore power above the HPSP following restoration of the 'B' TDRFP to service. The cause of the event was that the SRO responsible for the down power on April 13, 2016 did not validate, by preventative maintenance identifier (PMID), that the required surveillance was current. Corrective actions included applying Management Associated Results Company, Inc. (MARC) principles to the individuals involved.
4612016007 | Clinton 1 | 05/17/2016 | 07/15/2016 | ML16201A23 | <strong>Main Steam Line Flexible Hose Intergranular Stress Corrosion Cracking Identified During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2016 with the plant in Mode 4 during Refueling Outage C1R16 personnel entered the drywell to perform a system walkdown. At 0945 CDT water was identified leaking from flexible hoses located at the inner elbows of main steam line (MSL) B and MSL C. It was determined that the leakage was from the flexible hoses associated with the MSL flow instrumentation. The degraded flexible hose on MSL B was previously replaced in 2008 and on MSL C in 2007. An analysis determined the failure mechanism of the degraded flexible hoses as Intergranular Stress Corrosion Cracking (IGSCC). Main Steam Line C flexible hose had previously failed in 2007 due to IGSCC. Corrective actions taken for that event did not prevent a recurrence of the condition identified during C1R16. The leaking flexible main steam line hoses and the remaining flexible hoses on the MSLs B and C were replaced during C1R16. The remaining inner elbow flexible hoses on MSLs A and D have been scheduled for replacement during the next refueling outage C1R17. This condition is reportable under 10 CFR 50.73(a)(2)(ii)(A), as a condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded.
4612016008 | Clinton 1 | 05/18/2016 | 07/15/2016 | ML16201A23 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this LER is the result of planned activities in support of Refueling Outage C1R16 at Clinton Power Station (CPS). As described in the LER, the NRC provided enforcement guidance, applicable to boiling water reactor licensees, that addresses the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). On May 18, 2016 and May 23, 2016, CPS performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities while in Mode 5 without an operable Secondary Containment. These activities were performed within the guidelines of NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 which allows the implementation of interim actions as an alternative to full compliance, provided several conditions are met. The OPDRV activities were planned activities that were completed following the guidance of the EGM and are considered to have low safety significance based on interim actions taken. Since these actions were preplanned, no cause determination was necessary. As required by the EGM, a license amendment request will be submitted following NRC approval of the Technical Specifications Task Force traveler associated with generic resolution of this issue.
4612016009 | Clinton 1 | 06/24/2016 | 08/22/2016 | ML16238A47 | <strong>Trip of Fuel Building Fans due to Damper Failure Results in Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2016 at 1511 (CST) Clinton Power Station (CPS) was operating at 99 percent reactor power when the MCR received two Fuel Building (VF) trouble alarms. An unexpected damper closure resulted in Secondary Containment (SC) vacuum degrading, eventually exceeding the Technical Specification (TS) limit of 0.25 inch vacuum water gauge. TS Limiting Condition for Operation (LCO) 3.6.4.1, Secondary Containment, Required Action A.1 and Emergency Operating Procedure (EOP) - 08, Secondary Containment Control were entered. At 1512, SC vacuum was restored within TS limits with the auto start of VF supply fan 1VF03CB and exhaust fan 1VF04CB. An initial Investigation determined that the 'A' Exhaust Fan Isolation Damper 1VF11YA had failed to the closed position on loss of air due to failure of the associated air supply solenoid, 1FSVVF005. The apparent cause of this event is the failure of the ASCO solenoid valve, 1FSVVF005, due to a slightly deformed and worn core which resulted in sticking. The failed solenoid valve 1FSVVF005 was replaced and the VF system ventilation was restored. In addition, parts quality testing, and preventative maintenance programs are being established to replace VF solenoid operated valves on a periodic basis. The temporary loss of SC is reportable under 10CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material.
4612016010 | Clinton 1 | 10/14/2016 | 03/06/2017 | ML17067A41 | <strong>Failure to Complete Technical Specification Required Actions Within the Completion Time Resulted in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2016, Clinton Power Station (CPS) determined subsequent to the 3rd Quarter NRC Exit Meeting that a condition prohibited by Technical Specification (TS) 3.7.6, "Main Turbine Bypass System," had occurred associated with a failure to complete a TS Required Action within the associated Completion Time. Specifically, testing of Main Steam Turbine Bypass Valve (TBV) Numbers 4, 5, and 6 was not performed within the required test interval and the TBVs were appropriately declared inoperable as required by TS Surveillance Requirement.(SR) 3.0.1. Thermal Limit penalties were applied as required by Limiting Condition for Operation (LCO) 3.7.6. A Surveillance Frequency Change was processed in accordance with TS Program 5.5.16, "Surveillance Frequency Control Program," in June 2016 to change the Frequency for SR 3.7.6.1 from 31 days to 12 months. TBVs 5 and 6 were subsequently declared OPERABLE and the thermal limit penalties removed without performing the required SR 3.7.6.1, contrary to TS SR 3.0.1 Bases. The apparent cause of this event was determined to be that no specific requirement exists in either plant procedures or industry guidance which prohibits declaring a component or system OPERABLE based solely on an extension of the required surveillance test interval. Corrective actions include testing the valves with an alternate method and completing administrative procedure changes. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
4612016011 | Clinton 1 | 11/17/2016 | 01/13/2017 | ML17018A12 | <strong>Incorrect Calculation Method Used to Demonstrate Control Room Habitability</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2016, during the NRC Component Design Basis Inspection (CDBI), Clinton Power Station (CPS) determined that design calculation C-020 "Reanalysis of Loss of Coolant Accident (LOCA) Using Alternate Source Terms," incorrectly took credit for the dual Main Control Room ventilation (VC) supply inlets being single failure proof (SFP). This assumption allowed the calculation to reduce one of the dose terms by a factor of 4 in accordance with the guidance of Regulatory Guide 1.194, "Atmospheric Relative Concentrations for Control Room Radiological Habitability Assessments at Nuclear Power Plants". However, the inlets to VC at CPS are not SFP. This calculational error, when corrected, resulted in a calculated dose of greater than the 5 rem Total Effective Dose Equivalent (TEDE) allowable dose to occupants of the control room. A cause evaluation identified USAR sections that described the VC system were not clear regarding whether the intake structures were SFP. A standing order was issued for compensatory measures in the event of an emergency until calculations were prepared to demonstrate MCR operator dose limits can be met without compensatory measures. Actions have been initiated to finalize the MCR Operator dose analysis assuming single failure of outside air intake dampers and to revise the USAR to indicate that intake structures are not independently SFP. This event is reportable under 10 CFR 50.73(a)(2)(ii)(B), "Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety."
4612016012 | Clinton 1 | 12/05/2016 | 02/01/2017 | ML17037D19 | <strong>Residual Heat Removal (RHR) "C" Pump Failure During Surveillance Testing as a Result of Breaker Latch Check Switch Adjustment Results in a Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2016 at 2011 hours during a surveillance test of the Residual Heat Removal (RHR) "C" pump, a Westinghouse DHP Breaker for the RHR "C" pump failed to close. This occurrence resulted in a failure of RHR "C" pump to start. The pump was declared INOPERABLE and Technical Specification (TS) Limiting Condition of Operation (LCO) 3.5.1, "Emergency Core Cooling System -Operating," Required Action A.1 was entered to restore the pump to OPERABLE status in seven days. Performance records indicate the breaker was installed on March 11, 2016 in the RHR "C" pump cubicle and successfully operated on March 11, June 9, and September 6, 2016, prior to failure. An investigation determined that the breaker latch check switch contacts were not closed and that the latch check switch setting was out of procedural limits. The most likely time that the switch would have become out of adjustment would have been during transport of the breaker to the RHR "C" pump breaker cubicle on March 11, 2016. The apparent cause of the failure was an inadequate verification of the latch check switch setting performed prior to installation of the breaker in the cubicle. Corrective measures have been initiated that include revising plant procedures to record latch check switch adjustment value. The condition described in this report is reportable under 10CFR50.73(a)(2)(i)(B) as an "operation or condition which was prohibited by the plant's Technical Specifications."
4822016001 | Wolf Creek | 01/28/2016 | 11/10/2016 | ML16326A17 | <strong>Power Potential Transformer Overloading Results in Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2014, at approximately 1326 Central Daylight Savings Time (CDT) during a scheduled 24-hour Run, the 'B' Emergency Diesel Generator (EDG) unexpectedly tripped and a fire was observed in the electrical cabinet (NE106). This resulted in an unplanned entry into a 72 hour shutdown Limiting Condition of Operation (LCO) and an ALERT emergency classification. The source of the fire was the Power Potential Transformer (PPT). On 1/28/16, a Hardware Failure Analysis concluded that the failure of the PPT was due to overloading which resulted from failure of a diode in the power rectifier of the EDG excitation system. Failure of the diode was induced by a governor actuator malfunction on June 9, 2014. <br /><br /> The PPT and associated cabling were replaced. All power diodes in each power rectifier were replaced. Further corrective actions are being tracked by Condition Report (CR) 88665.
4822016002 | Wolf Creek | 11/16/2016 | 01/16/2017 | ML17024A06 | <strong>Loss of Switchyard Bus Results in Emergency Diesel Generator Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2016, at approximately 2109 Central Standard Time, while in Mode 5, a fault occurred which isolated the East Switchyard Bus from the Train "A" emergency AC plant bus NB01. During Refueling Outage 21, a modification to Transformer #7 allowed the offsite power through Transformer #7 to NB01 to be fed from either the East or West Switchyard Busses through 2 different breakers. After the loss of the East Switchyard Bus, the second breaker unexpectedly tripped which resulted in a loss of offsite power to NB01. An undervoltage condition was detected on NB01, which caused the Train "A" emergency diesel generator to start and to power NB01 as designed. The apparent cause of this event was that wiring in the Transformer #7 primary differential protective relay was landed on the incorrect termination point. <br /><br /> The wiring error on the primary differential protective relay was corrected and its functionality was verified. The secondary differential protective relay wiring was verified to be correct. The East Switchyard Bus, Transformer #7, and its differential relays were all restored to service.
4832016001 | Callaway | 04/20/2016 | 10/17/2016 | ML16294A12 | <strong>Control Room Air Conditioning Inoperability due to Essential Service Water Pressure Transient</strong><br /><i>Abstract:&nbsp;</i>On 4/20/2016, Callaway received preliminary analysis results showing that during a Design Basis Accident (DBA) the 'B' Train Control Room Air Conditioning System (CRAGS) would experience a pressure transient in the associated cooling water system greater than what is experienced during Engineered Safety Feature Actuation Signal (ESFAS) testing. This condition could damage the NC unit's gaskets, as evidenced during ESFAS testing completed on 4/14/2016, resulting in the affected CRAGS and Control Room Emergency Ventilation System (CREVS) trains not being capable of performing their required safety function. This event is being reported as a condition prohibited by Technical Specifications, an unanalyzed condition, and a condition that could have prevented fulfillment of a safety function. <br /><br /> The root cause of the event is that the original Essential Service Water (ESW) system design did not appropriately account for water column separation and collapse pressure transients inherent during operation. Following the 'B' train ESFAS testing on 4/14/2016, more robust gaskets were installed in affected components. A complete evaluation of the pressures and dynamic forces experienced by all ESW system subcomponents will be performed. The results will be compared to current design limits, and appropriate modifications will be performed to ensure sufficient margin exists in the plant design.
4982016001 | South Texas 1 | 01/26/2016 | 03/22/2016 | ML16098A32 | <strong>Unit 1 Manual Reactor Trip due to Loss of Main Feedwater to C Train Steam Generator When the Steam Generator Feedwater Regulating Valve Failed Closed</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2016, at 2324 hours, the Control Room received a Steam Generator Steam Flow/Feed Flow mismatch alarm. Operators found Steam Generator (SG) Train C Feedwater Regulating Valve closed and in manual. SG C Feedwater Regulating Valve could not be manually reopened. At 2325 hours, Operators manually tripped the Unit 1 reactor due to lowering level on SG C. The Auxiliary Feedwater (AFW) system automatically actuated on a SG low level signal and operators took manual control of AFW at 2327 hours.<br /><br /> The cause of loss of Main Feedwater to SG C was a failure of the Manual 7300 Series Tracking Driver (NTD) circuit card which forced SG C Feedwater Regulating Valve closed and prevented the operators from taking manual control or switching back to automatic valve control. As a corrective action, the Manual NTD circuit card was replaced. The manual actuation of the Reactor Protection System and subsequent automatic AFW actuation are both reportable under 10 CFR 50.73(a)(2)(iv)(A). The event was of very low risk significance and no radioactive release occurred; therefore, there was no adverse effect on the health and safety of the public.
4982016002 | South Texas 1 | 05/01/2016 | 06/29/2016 | ML16200A22 | <strong>Unit 1 Automatic Reactor Trip and Auxiliary Feedwater System Actuation Following Turbine Trip due to Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2016 at 2020 hours, STP Unit 1 experienced a Main Generator lockout due to a ground relay actuation resulting in an automatic turbine trip that lead to an automatic reactor trip. Visual inspections revealed that a rubber boot located where Main Generator phase B enters the isolated phase bus duct was degraded. A piece of the boot was hanging down and intermittently contacting the generator bushing causing a resistance path to ground, resulting in a Main Generator lockout and turbine trip signal. With the reactor at greater than fifty percent power, the automatic reactor trip was initiated in response to the turbine trip. The Auxiliary Feedwater (AFW) system actuated in response to low Steam Generator level. All safety systems operated as expected.<br /><br /> As immediate corrective actions, the A, B and C phase rubber boots were replaced in Unit 1. The cause evaluation determined that the design of the rubber boot and its retaining ring is inadequate. Design change packages are being developed to permanently remove the rubber boots and retaining rings for both Unit 1 and Unit 2. <br /><br /> The automatic actuation of the Reactor Protection System and automatic AFW actuation are both reportable under 10 CFR 50.73(a)(2)(iv)(A). The event was of very low risk significance and no radioactive release occurred; therefore, there was no adverse effect on the health and safety of the public.
5282016001 | Palo Verde 1 | 04/11/2016 | 06/09/2016 | ML16165A49 | <strong>Leakage from Reactor Coolant Pump 2B Discharge Pipe Instrument Nozzle</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2016, at 2335, with Unit 1 in Mode 5, during a planned extent-of-condition inspection of the Unit 1 reactor coolant system (RCS), engineering personnel at the Palo Verde Nuclear Generating Station (PVNGS) identified white residue on a one-inch instrument nozzle on the reactor coolant pump 2B discharge pipe. Isotopic analysis confirmed the white residue resulted from leakage of RCS coolant and, at 0535 on April 11, 2016, engineering personnel determined that RCS pressure boundary leakage had occurred resulting in a condition prohibited by Technical Specification 3.4.14, RCS Operational Leakage. <br /><br /> The cause of the event was determined to be primary water stress corrosion cracking of the Alloy 600 instrument nozzle. To correct the condition, the nozzle was repaired utilizing a Mechanical Nozzle Seal Assembly. A final repair of the nozzle will be addressed in the Corrective Action Program. <br /><br /> PVNGS reported similar events in licensee event report numbers 50-530/2015-001-00 (on June 5, 2015, when RCS pressure boundary leakage was identified on a Unit 3 RCP 2A suction pipe instrument nozzle) and 50-530/2013-001-00 (on December 6, 2013, when RCS pressure boundary leakage was identified on a Unit 3 reactor vessel bottom mounted instrument nozzle).
5282016002 | Palo Verde 1 | 09/07/2016 | 11/04/2016 | ML16309A61 | <strong>Reactor Trip due to Partially Open Pressurizer Main Spray Valve</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2016, at 2131, with Unit 1 in Mode 1 and 100 percent power, the reactor was manually tripped and reactor coolant pumps were secured due to a control malfunction which prevented closure of a pressurizer spray valve. This event initiated from an unsuccessful attempt to transfer a non-class 120VAC instrument power bus from its normal source to its emergency/alternate source. The transfer was attempted to facilitate an inspection of an electrical load center which was sprayed with water earlier in the day by a leaking sprinkler head following Fire Protection (FP) Department routine testing of a FP water line. <br /><br /> The cause of the spray valve malfunction was a failed pneumatic volume booster in the spray valve actuator system combined with a current to pressure converter (I/P) calibration offset which resulted from a voltage transient during the unsuccessful electrical transfer. These conditions caused the spray valve to stay approximately five percent open when it received a close demand from the spray valve controller. The I/P converter and pneumatic volume booster were replaced and the spray valve was returned to service. Additional corrective actions will adjust preventive maintenance frequency on the pneumatic volume boosters. <br /><br /> In the past three years, PVNGS has not reported a similar event to the NRC.
5282016003 | Palo Verde 1 | 09/21/2016 | 11/21/2016 | ML16326A42 | <strong>Inoperable Containment Isolation Valve SGA-UV-1134 due to Failure to Close During Testing</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2016, at 0142 Mountain Standard Time (MST), containment isolation valve SGA-UV-1134 failed to stroke closed from the control room during containment isolation valve testing. The failure resulted in an unplanned entry into Technical Specification Limiting Condition of Operation (LCO) 3.6.3, Containment Isolation Valves. On September 22, 2016, it was concluded the valve was in a configuration that rendered the pneumatic operator incapable of operating the valve, including remote operation and automatic closure in the event of a main steam isolation system signal. The valve had been in this configuration since last operated on June 28, 2016. Therefore, the valve was inoperable longer than the required 4-hour completion time of LCO 3.6.3 Condition C. On September 22, 2016, at 1457 MST, SGA-UV-1134 was properly closed, declared operable, and LCO 3.6.3 was exited. <br /><br /> This event was caused by human error when procedural guidance was not used to return SGA-UV-1134 to its neutral locked configuration following testing on June 28, 2016. Actions have been initiated to ensure proper procedural guidance is used to lock SGA-UV-1134 in the future. <br /><br /> On June, 26, 2015, LER 50-530/2015-002 reported a condition prohibited by LCO 3.0.4 that occurred on May 1, 2015, when Unit 3 entered Modes 4 and 3 while in the applicability of LCO 3.7.4. On May 2, 2015, automatic dump valve, SGB-HV-178, was stroked with steam while in Mode 3 and discovered to be inoperable due to human error incurred during post-maintenance assembly prior to entering Mode 4.
5292016001 | Palo Verde 2 | 08/09/2016 | 10/10/2016 | ML16285A41 | <strong>Main Steam Isolation Valve Actuator Train Inoperable due to Low Nitrogen Pre-Charge Pressure</strong><br /><i>Abstract:&nbsp;</i>On August 9, 2016, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.2, Condition A was entered for Unit 2 main steam isolation valve SGE-UV-171 (MSIV 171) train A actuator to perform a nitrogen pre-charge check. The check identified low nitrogen pre-charge pressure on the train A accumulator. An engineering evaluation determined that the MSIV 171 train A actuator was inoperable since July 30, 2016 due to a nitrogen leak on the accumulator. This inoperability period exceeded the 7-day required action completion time for one MSIV actuator train. The MSIV 171 train A actuator was restored to operable status and LCO 3.7.2, Condition A was exited on August 9, 2016. The accumulator leak was repaired on October 5, 2016. Insufficient monitoring, trending, and understanding of reservoir hydraulic fluid level trends in relation to the nitrogen pre-charge required for MSIV operability led to the extended inoperability period. Operator training will be revised to improve understanding of the system and the limitations of the hydraulic fluid level alarm. Additional corrective actions will revise procedures to provide enhanced rigor for the control of operations condition monitoring thresholds for an MSIV to ensure appropriate response times. Maintenance procedures will also be revised to provide more explicit guidance to minimize the potential for leaks. In the past 3 years, PVNGS has not reported a similar event to the NRC.
5302016001 | Palo Verde 3 | 12/24/2015 | 01/10/2017 | ML17010A41 | <strong>Control Room Essential Filtration System Air Filtration Unit Failure Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2016, PVNGS received Unit 3 "B" train (3B) control room essential air filtration unit (AFU) carbon sample test results that exceeded the acceptance criteria of the Technical Specification (TS) Ventilation Filter Testing Program. The Unit 3 control room (CR) staff declared the AFU inoperable and entered TS Limiting Condition for Operation (LCO) 3.7.11, control room essential filtration system (CREFS). The carbon filter replacement and testing was completed, and the Unit 3 CR staff declared the 3B CREFS AFU operable on July 24, 2016. <br /><br /> The investigation determined the 3B CREFS AFU was inoperable since December 17, 2015, which exceeded the Required Action Completion Time for Conditions A and C of LCO 3.7.11 on December 24, 2015 and Condition E during movement of irradiated fuel. The direct cause of this event was exposure of the 3B CREFS AFU carbon filter to a high amount of volatile organic compounds (VOCs) during a CR renovation project. The apparent cause was a lack of knowledge and recognition by PVNGS personnel to identify and properly mitigate the effects of the project on the CREFS AFU resulting in inadequate guidance for controlling all potential sources of VOCs. Applicable change process and work control procedures have been revised to ensure flooring and furniture replacements that could impact the CREFS AFU are evaluated as potential sources of VOCs prior to performing work. <br /><br /> No previous similar events have been reported by PVNGS in the last three years.
5302016002 | Palo Verde 3 | 12/15/2016 | 06/27/2017 | ML17178A38 | <strong>Emergency Diesel Generator Failure Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2016, the Unit 3 train B (3B) diesel generator (DG) experienced a failure during the performance of a monthly surveillance test. At 0356 Mountain Standard Time, a master connecting rod mechanically failed and caused significant damage to the 3B DG. Unit 3 control room staff declared the 3B DG inoperable and entered Technical Specification Limiting Condition for Operation (LCO) 3.8.1, AC Sources - Operating, Condition B. To support repairs, Palo Verde Nuclear Generating Station (PVNGS) received two license amendments to extend the LCO 3.8.1, Condition B required action completion time for the 3B DG from 10 days to 62 days.<br /><br /> The root cause analysis determined the 3B DG master connecting rod failed due to high cycle fatigue caused by misalignment of the crankshaft bore introduced by a previous failure that occurred in 1986. The failure mechanisms that paused the 1986 and 2016 3B DG failures are not present in any other PVNGS DG. As a corrective action, the crankshaft was removed from the 3B DG and alignment was restored to within manufacturer specifications. All damaged components were replaced or repaired, testing was completed, and the 3B DG was declared operable on February 10, 2017. As an additional corrective action, PVNGS will perform more frequent testing on DG master rods to ensure effective identification of fatigue cracks prior to failure. PVNGS will also perform master rod bearing clearance and master rod stud preload checks.