## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192017001 | Oyster Creek | 11/20/2016 | 05/03/2017 | ML17129A60 | <strong>Automatic SCRAM due to APRM High Flux During Turbine Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On 11/20/2016 at approximately 0342 EST, an automatic reactor SCRAM occurred at 92% power due to Average Power Range Monitor (APRM) high flux. Oscillations of the turbine control valves and bypass valves were experienced during planned testing of the Turbine Master Trip Solenoid Valve at 95% power. Power was reduced from 95% to 92% by the Main Control Room Operators in an effort to stop the observed oscillations. The control valves did not respond properly during the power reduction, leading to an unexpected rise in reactor pressure and the subsequent scram on high flux. <br /><br /> There were no safety consequences impacting the plant or public safety as a result of this event. All control rods fully inserted and the plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
2192017002 | Oyster Creek | 07/03/2017 | 08/31/2017 | ML17249A12 | <strong>Manual Reactor Scram due to Degrading Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On July 3, 2017, at approximately 10:15 AM following a grid disturbance, a manual scram was inserted due to degrading main condenser vacuum because of an improper configuration of the Augmented Off-gas (AOG) System. <br /><br /> The loss of main condenser vacuum resulted when Operations personnel failed to execute procedural requirement to align the AOG system into a shutdown lineup. The loss of vacuum was caused by degraded Steam Jet Air Ejectors (SJAE) performance due to a blocked discharge path. <br /><br /> The AOG system tripped 11 hours earlier following a grid disturbance. During the trip, operations personnel failed to re-align the AOG treatment system to a shutdown lineup resulting in the AOG Flame Arrestor siphoning into the inlet piping which filled the lower section of the off-gas hold up line with water.
2192017003 | Oyster Creek | 07/03/2017 | 08/31/2017 | ML17249A12 | <strong>Automatic Scram While Subcritical due to Low Reactor Level</strong><br /><i>Abstract:&nbsp;</i>On July 3, 2017 at approximately 10:30 hours with the reactor subcritical after a manual scram, an automatic reactor scram occurred due to low Reactor Pressure Vessel (RPV) water level. Prior to this event, Main Control Room (MCR) Operators established reactor water letdown, reset the manual scram and were placing RPV water level control in automatic using a Low Flow Feedwater Regulator Valve (LFRV). Reactor pressure control was automatically being maintained with turbine bypass valves. A low reactor water level occurred when a bypass valve opened as expected to lower reactor pressure. <br /><br /> Operations personnel had reset the scram signal without fully evaluating other plant conditions. Upon resetting the scram with reactor water level not yet stabilized, an automatic scram was received on low reactor water level. The automatic scram initiation signal occurred with the plant in a shutdown mode.
2192017004 | Oyster Creek | 08/31/2017 | 02/16/2018 | ML18046A07 | <strong>Reactor Protection System Channel Disabled During Test Box Use</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2017, during a review of industry Operating Experience (FERMI 2, LER 2017-001) for the use of a Reactor Protection System (RPS) test box during main turbine surveillance testing, it was determined that Oyster Creek station procedures failed to implement the required action specified by Technical Specifications (TS) section 3.1,1. note (nn) during testing. The surveillance tests associated with the Turbine Trip and Generator Load Rejection functions were revised in 2013 to use an RPS test box in order to minimize operational risks associated with the receipt of half scram signals during testing. The installation of the RPS test box caused two of the four required instrument channels for the Turbine Trip Scram function to be bypassed during testing. <br /><br /> In accordance with station Technical Specifications, the required action to verify sufficient channels remained operable was not documented as complete within the action time specified in TS Table 3.1.1, note (nn). This issue was identified under normal operating conditions, and is reportable under 10 CFR 50.73(a)(2)(i)(B).
2192017005 | Oyster Creek | 10/09/2017 | 03/12/2018 | ML18078A29 | <strong>Failure of the Emergency Diesel Generator #2 During Surveillance Testing due to a Broken Electrical Connector</strong><br /><i>Abstract:&nbsp;</i>On 10/09/17, during the bi-weekly Emergency Diesel Generator (EDG) #2 Load Test, a Generator Lockout signal (86G) was received which tripped the EDG output breaker. This failure resulted in EDG #2 being declared inoperable, and entry into an unplanned 7-day Limiting Condition for Operation (LCO) at 0312. <br /><br /> Troubleshooting identified a broken electrical ring lug connector on a current transformer that provides an input to the protective relay logic. The investigation determined the connector failure was due to fatigue cracking that was initiated by stresses caused by bending and twisting of the electrical lug. The ring lug was most likely distressed during initial installation in the 1990's. The condition that led to the EDG #2 trip existed for greater than the allowed outage time in the plant's Technical Specification (TS) and is reportable under 10 CFR 50.73(a)(2)(i)(B).
2202017001 | Nine Mile Point 1 | 12/10/2016 | 02/08/2017 | ML17044A00 | <strong>Manual Reactor Scram due to High Turbine Vibration</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2016 at 08:48, Nine Mile Point Unit 1 performed a manual scram of the reactor due to increased vibrations on the main turbine. Following the scram, the High Pressure Coolant Injection (HPCI) System automatically initiated. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). <br /><br /> During performance of a load drop to 95% power in support of Turbine Stop Valve Testing, main turbine bearing vibrations rose on several bearings. The Unit 1 Reactor was scrammed and the main turbine was secured when main bearing #1 reached procedural limits. The root cause of the event was a steam leak from a threaded pipe/cap connection that was not seal welded when originally supplied from the manufacturer. The connection has now been seal welded.<br /><br /> A combination of tight tolerance in conjunction with the location of the steam leak resulted in the vibrations when power level was changed. <br /><br /> The event described in this LER is documented in the plant's corrective action program.
2202017002 | Nine Mile Point 1 | 03/20/2017 | 08/18/2018 | ML18242A07 | <strong>Manual Reactor Scram due to Pressure Oscillations</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2017 at 02:27, Nine Mile Point Unit 1 performed a manual scram of the reactor due to pressure oscillations. This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The Unit was offline and reactor shutdown was in-progress at the time of the scram. The cause of the scram was manual scram. The scram was required at approximately 4% reactor power when pressure oscillations occurred exceeding the procedurally required limit. The apparent cause of this event was Mechanical Pressure Regulator (MPR) oscillations caused by a combination of the fouling of the MPR's pressure sensing bellows line and a bypass relay linkage passing through a worn bushing which created a friction induced sticktion of the linkage. <br /><br /> The event described in this LER is documented in the plant's corrective action program.
2202017003 | Nine Mile Point 1 | 09/06/2017 | 11/02/2017 | ML17325A99 | <strong>Automatic Reactor Scram due to Reactor Vessel Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2017 at 1157, Nine Mile Point Unit 1 experienced an automatic reactor scram due to reactor vessel low water level. The automatic Reactor Protection System (RPS) actuation and reactor scram is reportable per 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). Following the automatic scram all plant systems responded per design including High Pressure Coolant Injection (HPCI) System automatic initiation. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. <br /><br /> The root cause of the scram was a failed power supply within the Proportional Amplifier, PAM-ID23E. This power supply failure resulted in the output from the module dropping out causing the #13 Feedwater Pump Flow Control Valve to close. The corrective action taken was the replacement of the failed Feedwater Level Control module, PAM-ID23E.
2372017002 | Dresden 2 | 11/01/2017 | 02/15/2018 | ML18052A48 | <strong>Primary Containment Inboard and Outboard Feedwater Isolation Valves Exceed Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2017 at 1225 CDT, with Unit 2 shutdown for refueling outage D2R25, both the 2-220-58A Feedwater (FW) Inboard Check Valve and the 2-220-62A FW Outboard Check Valve failed Local Leak Rate Testing (LLRT) acceptance criteria. Technical Specification (TS) 5.5.12, 'Primary Containment Leakage Rate Testing Program,' establishes limits for Primary Containment leakage. Based upon the results of the LLRT, Dresden Unit 2 may not have met the limits for primary containment leakage during the last operating cycle as specified in TS 5.5.12.C. The cause of the failure was the inability to fully seat the valve disc in the seat assembly for testing. Corrective actions included replacing valve assemblies using the latest maintenance practices and installing larger test taps for improved testing. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS, under 10 CFR 50.73(a)(2)(ii)(A) as an event that resulted in the condition of the plant including its principal safety being seriously degraded, and under 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function of a system that is needed to control the release of radioactive material.
2442017001 | Ginna | 04/23/2017 | 03/23/2018 | ML18088A17 | <strong>During Surveillance Testing, Lift Pressure Setpoints on Three Main Steam Safety Valves Found Outside Technical Specifications Limits due to Narrowness of As-Found Acceptance Band</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2017, with the plant in Mode 1, during in-place testing of main steam safety valve (MSSV) 3509, the as-found lift pressure did not meet the acceptance criteria of +1% / -3% of setpoint (1140 psig), required by Technical Specifications (TS) surveillance SR 3.7.1.1. This was the second unsatisfactory MSSV as-found lift pressure, as MSSV 3508 had failed to meet the same as-found acceptance criteria during earlier in-place sequential testing (on April 21, 2017). Later, on May 5, 2017, a third MSSV (3512) tested at a vendor's facility failed to meet the same as-found acceptance criteria. (All three of the MSSVs have the same manufacturer and model number.) The most probable cause of exceeding the MSSV upper acceptance limit is the programmatic issue of the narrowness of the as-found acceptance band. A contributing cause was minor stiction on the disc. The as-found settings of all three MSSVs remained within analytical bounds; therefore, operation of the facility in this condition had no impact on the health and safety of the public. <br /><br /> TS LCO 3.7.1, "Main Steam Safety Valves (MSSVs)," requires eight MSSVs to be operable in Modes 1, 2, and 3. Since the acceptance band is fixed and the stiction affecting the three lift pressures may have occurred over a period of time, it is assumed that at least one required MSSV was not operable in the past for a time greater than allowed. Therefore, this occurrence is considered reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS.
2472017001 | Indian Point 2 | 06/26/2017 | 08/22/2017 | ML17240A16 | <strong>Manual Reactor Trip due to Decreasing Steam Generator Levels Caused by Main Boiler Feedwater Pump Turbine Low Pressure Governor Valves Failed Closed</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2017, Operations commenced a downpower from 100 percent to 93 percent reactor power to support performance of the Main Turbine Stop and Control Valve Test. With reactor power at 94 percent, the 22 Main Boiler Feed Pump Turbine (MBFPT) speed control trouble alarm annunciated coincident with pump speed swings of 800 revolutions per minute (rpm). The operators ceased the downpower and placed the 22 Main Boiler Feedwater Pump (MBFP) in Manual speed control to control the rpm swings. This was unsuccessful, and the rpm swings continued. The 22 MBFPT low pressure (LP) governor valves were observed to be cycling from full-closed to full-open. The decision was made to take local pneumatic control of the 22 MBFP to stabilize pump speed. Two minutes after establishing local pneumatic control, the LP governor valves went to full closed. With the rapid reduction in 22 MBFP speed, the pump was no longer delivering feedwater flow to the SGs. An automatic main turbine runback signal should have been generated on a low speed signal; however, there was no turbine runback actuation. In response, the operators commenced a manual runback to reduce main turbine load, but the decreasing SG levels reached 15 percent, and at 1531 hours a manual reactor trip was initiated. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of the reactor trip was that the shoulder screws used on the 22 MBFPT LP governor valve servomotor linkage had backed out and detached. This caused the LP governor valves to fail closed, shutting off the turbine steam supply. This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission (NRC) on June 26, 2017 under 10 CFR 50.72(b)(2)(iv)(B), 50.72(b)(2)(xi), and 50.72(b)(3)(iv)(A).
2472017002 | Indian Point 2 | 06/26/2017 | 08/22/2017 | ML17240A16 | <strong>Auxiliary Feedwater Flow Indication Inoperable for Longer Than the Allowed Technical Specification Completion Time due to Failure of Complete Restoration Following Calibration</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2017, Instrumentation and Control (I&C) maintenance had a scheduled activity to calibrate the 22 Steam Generator (SG) Auxiliary Feedwater (AFW) flow indicator (FI-1201). The tag-out was applied by Operations at 0748 hours on the two flow transmitter root stop valves. l&C personnel began to calibrate FI-1201 at approximately 1000 hours. The calibration Procedure requires isolation of the high and low isolation valves and opening of the equalizing valve to allow venting of any pressure going to the transmitter. The calibration was performed and all as-found readings were within acceptance range. The test equipment was removed. The transmitter restoration was completed with the exception of filling and venting the transmitter FI-1201 and placing it back in service. Due to the root valves being tagged out, the source of water was isolated preventing proper filling and venting of the transmitter. The l&C supervisor discussed the restoration of the transmitter with the Operations shift manager, and it was agreed that Operations would complete restoration of the transmitter when the tag-out was removed. The l&C supervisor noted this and marked NA for the steps to return the transmitter back in service. This is a common practice when performing transmitter calibrations as a part of larger work windows because the tag-out must first be removed for a source of water to be available for restoration. However, the l&C supervisor did not obtain the Shift Manager's initials, which is required by Procedure. Consequently, Operations did not restore the transmitter to service, resulting in FI-1201 remaining inoperable for greater than the Technical Specification 3.3.3 allowed completion time of 30 days. It should be noted that in spite of inoperability of FI-1201, since FI-1201 is indication only, there was no actual loss or degradation of water flow to the steam generators at any time and thus had no impact on SG heat removal capability.
2472017003 | Indian Point 2 | 06/27/2017 | 08/23/2017 | ML17241A04 | <strong>Technical Specification Violation of Section 3.3.1 RPS Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2017, during reactor startup, power was raised from Mode 3 to Mode 2 and above the P-6 (Intermediate Range Neutron Flux) interlock with the P-6 Switches in the wrong position. With P-6 inoperable this was a violation of the requirement of Technical Specification (TS) Limiting Condition of Operation (LCO) 3.3.1 and resulted in a 60 Day Licensee Event Report (LER). LCO 3.3.1, Table 3.3.1-1, Item 17 states that the Intermediate Range Neutron Flux, P-6 shall be operable.<br /><br /> On June 27, 2017, during performance of 2-PT-V63A, Reactor Protection System (RPS) Logic Train 'A' Partial Functional Test, Instrumentation and Control (I&C) Technicians left two Intermediate Range P-6 switches in the wrong position, which resulted in an unplanned entry into LCO 3.3.1, due to inoperable RPS instrumentation. This inoperable RPS instrumentation resulted in a TS LCO 3.3.1 violation when reactor power was raised from Mode 3 to Mode 2.
2492017001 | Dresden 3 | 09/12/2017 | 12/27/2017 | ML17363A21 | <strong>Unit 3 Standby Liquid Control System Inoperable due to a Manufacturing Defect Causing a Piping Leak</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2017 at 1131 hours (CDT), at Dresden Nuclear Power Station (DNPS), both Unit 3 Standby Liquid Control system subsystems were declared inoperable when control room personnel were notified of a through wall leak on the common discharge piping. Technical Specification (TS) 3.1.7, "Standby Liquid Control System," Condition B was entered. The pipe repair schedule projected that the work could not be completed within the allowed Completion Time of TS 3.1.7 and DNPS requested a Notice of Enforcement Discretion (NOED) to allow Unit 3 to remain at power during the repair. The NRC granted the NOED on September 12, 2017, at 1746 hours. The system was restored to operable status by replacing the piping on September 12, 2017, at 2035 hours within the time allowed by the NOED. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by TS. The cause of the event was a manufacturing defect. Corrective actions include replacing the failed piping (completed) and performing extent of condition pipe inspections.
2502017001 | Turkey Point 3, Turkey Point 4 | 03/18/2017 | 05/16/2017 | ML17136A37 | <strong>Loss of 3A 4kV Vital Bus Results in Reactor Trip, Safety System Actuations and Loss of Safety Injection Function</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2017 at approximately 1107 hours, the Turkey Point Unit 3 reactor tripped from 100% power as a result of an electrical fault on the 3A 4kV vital bus. The Auxiliary Feed Water System actuated as expected, and the 3A Emergency Diesel Generator started but did not load, as designed, due to the lockout of the 3A 4kV bus. The 3A 4kV bus remained de-energized and the reactor was stabilized in Mode 3. Both Unit 4 High Head Safety Injection (HHSI) pumps were out of service for maintenance. The 3A HHSI pump was unable to be powered from the 3A 4kV bus resulting in a loss of the Safety Injection safety function for approximately 2.5 hours on both Units 3 and 4. The safety function is achieved by operation of two of the four pumps which are shared by both units. The loss of the 3A 4kV bus was caused by an electrical fault created by a conductive foreign material that had entered the current-limiting reactor cubicle that bridged an air gap between an uninsulated bus bar and the cubicle wall. The foreign material was a carbon fiber mesh used to reinforce a Thermo-Lag installation taking place in the 3A 4kV switchgear room. Corrective actions include: 1) The Thermo-Lag installation procedure will be revised to incorporate additional precautions for handling Thermo-Lag materials, and 2) the Engineering product risk and consequence assessment process will be revised to ensure a review is conducted of Safety Data Sheets for material being considered in the design. This event had no effect on the health and safety of the public.
2512017001 | Turkey Point 4 | 09/10/2017 | 11/07/2017 | ML17311A66 | <strong>Manual Reactor Trip due to Lowering Steam Generator Level Caused by Loss of Flow Regulating Valve Positioner Control</strong><br /><i>Abstract:&nbsp;</i>On September 10, 2017 at approximately 1855 hours, the Turkey Point Unit 4 reactor was manually tripped from 88% power due to lowering level in Steam Generator (SG) C. The reactor was stabilized in Mode 3. Auxiliary Feed Water actuated as expected on low level in SG C and was secured at approximately 1933 hours. At the time of the event, the Turkey Point site was experiencing high winds with rain associated with Hurricane Irma. The B and C Main Feedwater Regulating Valves (MFRV) had been in manual control when the C MFRV failed closed. The cause of the event was a degraded signal due to water intrusion into the C MFRV valve positioner hand selector switch enclosure resulting from a less than adequate design and installation. Corrective actions include modifications to the Unit 3 and 4 MFRV hand selector switch enclosures and enclosure penetrations, and repair of a failed component associated with the 4C MFRV. Additionally, the terminal/pull box specifications will be revised to improve direction for installation activities. Safety significance is very low because the unit responded as designed to the trip.
2542017001 | Quad Cities 1, Quad Cities 2 | 01/24/2017 | 03/22/2017 | ML17081A28 | <strong>Secondary Containment Interlock Doors Opened Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2017, at 10:00 hours, Operations was notified that both doors in the secondary containment interlock on the 595 foot elevation between the Reactor Building (RB) and the Unit 2 Reactor Feed Pump room (located inside the Turbine Building (TB)) were opened simultaneously for approximately 3 seconds. The failure of this interlock caused a loss of secondary containment per Technical Specification (TS) 3.6.4.1, Condition A. The doors were immediately reclosed, and the secondary containment boundary was immediately reestablished. Operators verified the RB (secondary containment) differential pressure was maintained operable at greater than 0.10 inches of water vacuum. <br /><br /> Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the doors and since the RB differential pressure was maintained during the event. The RB is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units. <br /><br /> The cause of the interlock failure was due to a dirty contact that caused the interlock relay to stick. This allowed the second door to open before the first door was secured. Corrective actions included inspecting and cleaning of the interlock relay contacts. Steps will be added to the Preventative Maintenance Work Orders to perform a visual inspection and cleaning of interlock relays. <br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542017002 | Quad Cities 1 | 03/27/2017 | 04/25/2019 | ML19115A13 | <strong>Four Main Steam Isolation Valves (MSIVs) Closure Times Exceeded</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2017, during refueling outage Q1R24 at 0840 hours, the Unit 1 Main Steam Isolation Valve (MSIV) as-found closure time test results indicated that four MSIVs failed to close within the required Technical Specification (TS) time of less than or equal to five seconds. The safety significance of this event was minimal. <br /><br /> The cause of two of the four MSIV slow closure timing events was inadequate procedure on how to apply Super O-Lube to valve stem bottom O-ring of the airpack manifold solenoid, and the cause of the other two slow closure timing events was environmental conditions in the Unit 1 MSIV Room. <br /><br /> Corrective actions included replacing the 1-0203-1B and 1-0203-1D MSIV airpack manifolds in Q1R25, revising the MSIV airpack manifold maintenance procedure regarding the amount of Super O-Lube to be applied, and revising operating procedures to prevent MSIV closure time drift observed to occur at MSIV room temperatures below 90 degrees F.<br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), which requires reporting of any operation or condition that was prohibited by the plant's TS.
2542017003 | Quad Cities 1, Quad Cities 2 | 09/21/2017 | 11/17/2017 | ML17321A06 | <strong>Control Room Emergency Ventilation Air Conditioning Piping Refrigerant Leak due to High Cycle Fatigue</strong><br /><i>Abstract:&nbsp;</i>On 09/21/2017 at 1550, Operations started Control Room Emergency Ventilation (CREV) Air Conditioning (AC) for Tracer Gas Testing. Per Operations instructions, Mechanical Maintenance went to inspect the Control Room Emergency Ventilation system for refrigerant leaks before Tracer Gas Testing was started. Mechanical Maintenance reported a refrigerant leak on the discharge piping of the compressor, right above the inlet to the condenser. The leak was at the expansion joint of a fitting. The safety significance of this event was minimal.<br /><br /> The cause of the refrigerant leak on the Control Room Emergency Ventilation compressor discharge pipe fitting into the condenser was due to high cycle fatigue.<br /><br /> The corrective action was to replace the failed Control Room Emergency Ventilation compressor discharge pipe fitting. <br /><br /> The CREV AC system is a single train system. Given the impact on the CREV AC system, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2542017004 | Quad Cities 1, Quad Cities 2 | 11/07/2017 | 01/05/2018 | ML18005A27 | <strong>Unit 1 HPCI Did Not Trip due to Wear Debris in the Turbine Stop Valve Oil Resetting Solenoid</strong><br /><i>Abstract:&nbsp;</i>During performance of the High Pressure Coolant Injection (HPCI) Pump Operability Test, the Unit 1 HPCI turbine did not trip when the Remote HPCI Turbine Trip pushbutton was depressed. Operations shut down HPCI by isolating the steam supply valves to trip the HPCI turbine. The Unit 1 HPCI system was declared inoperable, but remained available. The cause was determined to be accumulation of wear debris within the HPCI turbine stop valve oil resetting solenoid valve causing the valve to stick in the energized position. This wear debris was a result of a manufacturing deficiency. <br /><br /> The immediate corrective action was to replace the turbine stop valve oil resetting solenoid valve. Follow-up corrective action is to evaluate the preventative maintenance frequency for the HPCI turbine stop valve oil resetting solenoid valve. <br /><br /> The safety impact of this condition was minimal. The HPCI system was still available to function, despite the issue with the HPCI Turbine Stop Valve oil resetting solenoid. The event is being reported because HPCI is a single train system and the loss of HPCI could potentially impact the plant's ability to mitigate the consequences of an accident.
2552017001 | Palisades | 03/29/2017 | 03/26/2018 | ML18085A09 | <strong>Inadequate Protection from Tornado Missiles Identified due to Nonconforming Design Conditions</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2017, during an evaluation of protection of Technical Specification (TS) equipment from the damaging effects of tornado missiles, nonconforming conditions were identified in the plant design. Specifically, TS equipment did not meet current design basis for protection against potential tornado missile impact. Identified components/systems were declared inoperable and NRC Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado Generated Missile Protection Noncompliance," was implemented. Initial compensatory measures were implemented, per the guidance of NRC Interim Staff Guidance DSS-ISG-2016-01 Appendix A, within the time allowed by the applicable Limiting Conditions for Operation (LC0s) and the associated systems were then declared operable but nonconforming. On January 31, 2018, an additional nonconforming condition related to tornado missile vulnerability was identified by an engineering contractor as part of confirmatory walk-downs to supplement the actions already taken to address tornado missile vulnerabilities. Six systems, containing TS required equipment, did not meet current design basis for protection against potential tornado missile impact. Credible tornado missile impacts could affect the following systems; Service Water, Fuel Oil, Emergency Diesel Generators, Auxiliary Feedwater, Component Cooling Water and Control Room Ventilation Filtration. Subsequently, comprehensive compensatory measures were implemented per the guidance of NRC Interim Staff Guidance DSS-ISG-2016-01 Appendix A.<br /><br /> Due to the historical nature of the issue, a specific cause for the identified vulnerabilities was not determined.
2552017002 | Palisades | 05/19/2017 | 07/17/2017 | ML17198A18 | <strong>Reactor Protection System Actuation While the Reactor Was Shutdown</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2017, at 0206 hours, an unexpected Reactor Protection System (RPS) actuation occurred during pre-startup testing. The reactor was shutdown at the time, with all control rods inserted. The portion of the test that was in progress is designed to actuate the RPS from a loss of load input signal. To facilitate this part of the test with the reactor in a shutdown mode, one of two conditional steps in the procedure is to be taken. The generator motor operated disconnect 389 (MOD-389) is required to be in the open position, or protective trip circuity for the generator is required to be bypassed. Due to a conditional step of the test procedure being misinterpreted by a Nuclear Control Operator (NCO), MOD-389 was left in the closed position and the generator protective trip circuity was not bypassed. This resulted in the RPS actuation occurring prior to the preplanned sequence. The RPS responded as designed. All components operated as expected for the plant conditions. <br /><br /> The cause of the unexpected RPS actuation was human performance errors during procedure performance, e.g., lack of self-validation/verification, misinterpretation of information, and lack of peer check verification. <br /><br /> Corrective actions from the event include the removal of the NCO's licensed operator qualifications until remediated and initiation of a standing order requiring peer check verification for all procedure conditional steps until the applicable administrative procedure is revised. Additionally, a case study of the event will be included in a 2017 operations high intensity training session.
2592017001 | Browns Ferry 1, Browns Ferry 2 | 12/21/2016 | 02/21/2017 | ML17052A50 | <strong>Signal Timer for 4kV Shutdown Board C Inoperable for Longer Than Allowed by Technical Specifications due to Detached Restraining Strap</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2016, at 1228 Central Standard Time (CST), during a performance of the 4KV Shutdown Board (SDBD) C Undervoltage and Time Delay Relay Calibration and Functional Test, personnel discovered a detached restraining strap on a 4kV SDBD C Degraded Voltage Relay Timer. At 1835 CST, Operations personnel declared the relay inoperable. The timer retaining strap was replaced, and the relay was declared operable on December 22, 2016, at 1251 CST. <br /><br /> A Past Operability Evaluation determined that the timer was inoperable from October 5, 2016, until December 22, 2016, exceeding the Technical Specification allowed outage time. <br /><br /> The most likely cause of this event was human error. Rounding of the screw attaching the retaining strap to the backplane of the electrical cabinet in which the timer was housed allowed the retaining strap to become detached. This deficiency was not corrected despite testing and Quality Control verification. Corrective Actions include replacing the retaining strap using a longer screw, identifying relays previously installed under similar plant modifications, and ensuring that work packages for future installation of relays with seismic retaining straps contain steps to obtain adequate screw engagement during strap installation.
2592017002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 03/02/2017 | 05/01/2017 | ML17118A01 | <strong>Unauthorized Firearm Introduced into the Protected Area</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2017, an unauthorized firearm was introduced into the protected area (PA) after passing through the search process undetected. This led to the declaration of a Notification of an Unusual Event for a security condition that does not involve a hostile action. This event is reportable due to the actual introduction of a contraband firearm into the PA.<br /><br /> Immediate actions include the following: The individual who introduced the firearm was removed from the PA, their badge was disabled, their access was revoked, and their personal vehicle searched for additional contraband. A post-event fitness for duty test was attempted but the individual declined after numerous failed attempts to provide a sample. The Nuclear Security Officers (NSOs) on-duty when the individual entered the PA were disqualified. The Search Lane where the individual entered was closed for Maintenance to inspect its x-ray machine, which was found to be working as designed. Two NSOs are now assigned to each lane's search monitor to view the items being processed through the x-ray machine, and any unidentifiable items are physically searched. A fleet-wide policy of random physical searches of personnel and packages has been implemented. Additionally, over 800 lockers, cubicles, and other areas, were searched for contraband. No other contraband or unauthorized items were found.<br /><br /> The cause was determined to be that the training provided to NSOs drove the identification of contraband instead of driving the NSO to conduct a physical search when they cannot positively identify all materials using the x-ray image. The corrective action to prevent recurrence is to revise task practical evaluation training and the Personnel Access Control procedure to include acceptance criteria for performing successful material searches.
2592017004 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 09/10/2017 | 11/09/2017 | ML17313A84 | <strong>Safety System Functional Failures due to the Inoperability of Both Unit 1 and 2 Control Bay Chillers</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2017, at 1520 Central Daylight Time (CDT), Operations personnel declared Unit 1/2 Control Bay (CB) Chiller (CHLR) A inoperable after observing that its outlet water temperature exceeded its specified limits. On September 10, 2017, at 1151 CDT, the Unit 1/2 CB CHLR B was declared inoperable after failing to start and providing a flashing error code to an operator in the field. The concurrent inoperability of both Unit 1/2 CB CHLRs required Browns Ferry Nuclear Plant (BFN) to declare the immediate inoperability of the electrical equipment in the affected electric board rooms, including all four Unit 1/2 4160 V Shutdown Boards, resulting in a Safety System Functional Failure, and entry into Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.0.3 for BFN, Units 1, 2, and 3. On September 10, 2017, at 2110 CDT, the Unit 1/2 CB CHLR B was restored to operable status following a capacitor replacement, and LCO 3.0.3 was exited. <br /><br /> The Unit 1/2 CB CHLR A failure was caused by a thermistor failure, likely due to a break in the cable system. The Unit 1/2 CB CHLR B failure was due to a capacitor failing to hold its charge. Corrective actions include changing the preventive maintenance frequency interval for CB CHLR capacitor replacement from 10 years to 4 years. In addition, the concurrent Unit 1/2 CB CHLR failures were caused by a design which lacked defense-in-depth, where removing one Unit 1/2 CB CHLR from service for unplanned corrective maintenance created a single-point failure risk. A design change has been proposed to install a cross-tie between the Unit 3 Chillers and the Unit 1/2 Chillers to provide cooling in the event that Unit 1/2 CB CHLR A and B were to both become inoperable.
2602017001 | Browns Ferry 2 | 02/16/2017 | 04/14/2017 | ML17104A23 | <strong>High Pressure Coolant Injection Safety System Functional Failure due to a Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2017, the spurious failure of a fuse protecting a High Pressure Coolant Injection (HPCI) system flow controller rendered the HPCI system inoperable. Operators replaced both the line and neutral fuses, and restored HPCI availability. Following a period of monitoring the current flow through the fuse and HPCI system operation tests, Operations declared the Unit 2 HPCI system to be Operable on February 17, 2017. <br /><br /> Since HPCI is a single-train safety system, any period of unplanned inoperability constitutes a safety-system functional failure affecting accident mitigation, and is reportable. However, in the event of an emergency, the Reactor Core Isolation Cooling (RCIC) system remained operable, and all other Emergency Core Cooling Systems and the Automatic Depressurization System were available throughout this event to facilitate core cooling. <br /><br /> Failure analysis indicates that the fuse failed when its internal resistor lead and its tension/retraction spring became uncoupled at their soldered junction, as a result of age-induced solder creep. Corrective Actions include the prompt replacement of the failed fuses, determining the population of fuses on the HPCI system and RCIC system that should be replaced on a one-time basis, and to initiate work orders to replace these fuses.
2602017002 | Browns Ferry 2 | 02/23/2017 | 04/24/2017 | ML17114A25 | <strong>Inoperable Primary Containment Isolation Valve Resulting in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2017, radiography results for the Browns Ferry Nuclear Plant (BFN), Unit 2, Reactor Core Isolation Cooling (RCIC) system stop check valve, 2-HCV-071-0014 (71-14 valve), showed the valve to be in the fully open position. In this position, the valve was incapable of performing its design function as a Primary Containment Isolation Valve (PCIV). In order to isolate the affected primary containment penetration flowpath, the RCIC Steam Line Outboard Isolation Valve was closed and deactivated to secure flow through the adjacent PCIV check valve in the exhaust line in accordance with plant Technical Specifications (TS) Limiting Conditions for Operation (LCO) for Primary Containment Isolation.<br /><br /> It is assumed in the Past Operability Evaluation (POE) that the 71-14 valve had been inoperable from April 2015 to February 2017, in violation of TS LCO 3.6.1.3. During this time period, another check valve (upstream of the 71-14 valve) remained capable of isolating the affected penetration. The 71-14 valve was repaired during the BFN, Unit 2, Cycle 19 Refueling Outage which began on February 25, 2017. <br /><br /> The cause of this condition was determined to be inadequate minimum allowable internal clearances for the 71-14 valve. The 71-14 valve internals were machined to minimum allowable material as an interim action to mitigate risks. The corrective action to prevent recurrence is to replace the 71-14 valve with a new valve design that is not susceptible to the same internal binding potential.
2602017003 | Browns Ferry 2 | 03/29/2017 | 05/30/2017 | ML17150A02 | <strong>Manual Reactor Scram Initiated During Startup due to Multiple Rods Inserting</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2017, at 1842 Central Daylight Time (CDT), during Unit 2 start-up, Operations personnel received annunciators for an Intermediate Range Monitor (IRM) Downscale and a Control Rod Withdrawal Block. Operations personnel noticed that IRM 'G' was reading downscale and adjusted the range down one position with no immediate reaction. At 1844 CDT, an upscale spike on IRM 'G' caused a half scram on Reactor Protection System (RPS) 'A' trip system. After verifying that the IRM 'G' High-High trip signal was cleared, Operations personnel reset the half scram on RPS 'A'. An immediate, concurrent trip signal from IRM 'F' was then received on the RPS '13' trip system, resulting in multiple rods inserting into the core. When Operations personnel identified multiple rods inserting, a manual reactor scram was inserted at 1844 CDT. <br /><br /> The root cause was determined to be a lack of performing electromagnetic and radio-frequency interference noise testing to detect nuclear instrumentation abnormalities. <br /><br /> Corrective Action to Prevent Recurrence is to perform routine pre-outage and outage-related preventive maintenance tasks for noise-induced cable tests to verify the noise has been removed.
2602017004 | Browns Ferry 2 | 05/08/2017 | 07/07/2017 | ML17188A15 | <strong>Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2017, the Tennessee Valley Authority was presented with as-found testing results indicating that four of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Plant, Unit 2, were outside the +/- 3 percent setpoint band required for their operability. Troubleshooting determined that three MSRVs exceeded their setpoints when their valve discs failed by corrosion bonding to their valve seats. The valve discs were previously platinum coated to prevent this, but the valve seat's rough Stellite surface caused the coating to delaminate. This was the first Unit 2 MSRV service interval to implement the improved surface treatment since a resolution to the delamination issue was identified in 2015. The valve which failed below its setpoint band was determined to have a faulty pilot spring. <br /><br /> These four MSRVs were found to have been inoperable for an indeterminate period of time between April 9, 2015, and February 25, 2017, and longer than permitted by Technical Specifications. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, activation through the Automatic Depressurization System, or MSRV Automatic Actuation Logics were not affected. The valves remained capable of performing their required safety function. <br /><br /> Corrective Actions were to replace all thirteen Unit 2 MSRV pilot valves with pilot valves which had the platinum coating applied in accordance with the revised procedure, and to analyze the pilot valves of the inoperable MSRVs. The pilot spring was replaced inside the valve which failed below its specification.
2612017001 | Robinson 2 | 04/03/2017 | 06/02/2017 | ML17152A32 | <strong>Auxiliary Feedwater System Actuation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At 2155 hours Eastern Daylight Time on 4/3/2017 with the plant in Mode 3 at zero percent power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2), experienced an actuation of the Auxiliary Feedwater (AFW) System during turbine trip logic surveillance testing. <br /><br /> Subsequent investigation determined that the surveillance test was performed without verifying AFW actuation signals were defeated, as required by the test procedure. During performance of the test the AFW system actuated when the only running main feedwater (MFW) pump was tripped as part of the test. Since the AFW defeat switches were not in the defeat position, the AFW system actuated as designed in response to the tripped MFW pump. Main feedwater was restored and the AFW pumps were secured. <br /><br /> The direct cause of the AFW system actuation was inadequate procedure adherence during turbine trip surveillance testing.
2612017002 | Robinson 2 | 10/24/2017 | 12/14/2017 | ML17349A02 | <strong>Plant Vital Area Security Vulnerability Discovered Without Compensatory Security Measures</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2017 at 1350 EDT, with the plant in Mode 1 at 100 percent power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2), discovered an uncompensated security vulnerability that could have allowed unauthorized or undetected access to a vital area (VA) of the plant. Compensatory measures were promptly established and an immediate investigation was conducted, which did not reveal any evidence of unauthorized entry or tampering. <br /><br /> The cause of this event is attributed to the absence of work instructions to contact security to establish compensatory measures prior to beginning work activities high on a VA barrier wall. The vulnerability was the result of authorized work. All workers involved were validated to have proper permissions to access the area. No unauthorized access to the VA occurred during the time period that the vulnerability existed. This event did not have any nuclear or personal safety implications. <br /><br /> This report is being submitted in accordance with the requirements of 10 CFR 73.71(d), which refers to Appendix G, "Reportable Safeguards Events," Section 1(c).
2632017001 | Monticello | 04/15/2017 | 06/13/2017 | ML17164A17 | <strong>Reactor Scram and Group II Isolation due to 11 Reactor Feed Pump (RFP) Removal from Service with 12 RFP Isolated</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2017 at 0436 hours, the 11 Reactor Feedwater Pump (RFP) was removed from service and the discharge valve closed. With the discharge valve closed and 12 RFP previously isolated no flow path was lined-up for the Condensate pumps to supply water to the vessel. Reactor water level lowered resulting in valid Reactor Protection System (RPS) actuation and Primary Containment Group II Isolation signals. The 11 RFP discharge valve was reopened to reestablish a flowpath to restore level. The RPS and Group II isolation logic was reset when cleared. Two apparent causes were identified: 1) Failure to identify and address the unusual Feedwater System configuration prior to execution of the 11 RFP shutdown. 2) Guidance for shutdown of the RFP did not take into account the state of the other train when shutting down a RFP. The corrective actions were: 1) Revise plant startup and shutdown procedures to ensure abnormal equipment lineups are addressed to avoid unexpected interactions. 2) Revise the Feedwater System operation procedure to maintain a flow path when the opposite train Reactor Feed Pump is isolated.
2632017002 | Monticello | 04/15/2017 | 06/13/2017 | ML17165A34 | <strong>Main Steam Isolation Valve Closure Time Outside of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2017 at approximately 10:56 am, with the plant at 0% power in Mode 4 (Shutdown), while performing a plant shutdown procedure the "D" outboard Main Steam Isolation Valve (MSIV), AO-2-86D was functionally tested. The Monticello Nuclear Generating Plant (MNGP) Technical Specifications (TS) Surveillance Requirement (SR) 3.6.1.3.6 requires that the isolation time of each MSIV is > 3 seconds and < 9.9 seconds. During the functional test the "D" Outboard MSIV closing time was measured at approximately 40.7 seconds. The valve was declared inoperable and subsequently repaired. The failure was attributed to the air pack pilot valves. <br /><br /> This component failure is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.6.1.3 "Primary Containment Isolation Valves," since AO-2-86D may have been inoperable for greater than the TS 3.6.1.3, Required Action A.1, Completion Time of 8 hours to isolate a main steam line, and the Completion Time for TS 3.6.1.3, Required Action F, to be in Mode 3 in 12 hours and Mode 4 in 36 hours when the completion time of A.1 is not met. There were minimal safety consequences associated with the condition since the primary containment isolation function was maintained.
2632017003 | Monticello | 04/20/2017 | 06/14/2017 | ML17166A13 | <strong>Main Steam Isolation Valve Leakage Exceeds Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2017 during outage 1R28 Local Leak Rate Testing (Appendix J), AO-2-86C, "13 Outboard Main Steam Isolation Valve," had an unacceptable as-found leak rate. The measured leakage rate was 187.8 standard cubic feet per hour (scfh) which exceeds the Monticello Nuclear Generating (MNGP) Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.12 limit of 100 scfh. AO-2-86C was declared inoperable and the valve was subsequently disassembled to make repairs. The valve's stem, discs, upper/lower wedges, disc retainer, and wedge pin were replaced and retested. The as-left leak rate after completion of the work was 2.64 scfh. <br /><br /> This component failure is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.6.1.3, "Primary Containment Isolation Valves," since AO-2-86C likely had been inoperable for greater than the TS 3.6.1.3, Required Action A.1, Completion Time of 8 hours to isolate a main steam line, and the Completion Time for TS 3.6.1.3, Required Action F, to be in Mode 3 in 12 hours and Mode 4 in 36 hours when the completion time of A.1 is not met. There were minimal safety consequences associated with the condition since the primary containment isolation function was maintained by the inboard valve.
2632017004 | Monticello | 06/19/2017 | 08/16/2017 | ML17229B30 | <strong>High Pressure Coolant Injection Steam Stop Valve Failed to Open During Test</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2017 following a planned High Pressure Coolant Injection (HPCI) system maintenance, a HPCI start attempt was performed per the quarterly test procedure. HPCI failed to start during the test due to the steam stop valve HO-7 not opening caused by HO-7 oil relay not functioning properly. Since the component was not the subject of the maintenance activity, the HPCI failure was reported to the NRC under Emergency Notification System, Event Number 52814. <br /><br /> The HO-7 oil relay was repaired and the HPCI system was returned to operable status at 13:30 on June 23, 2017.
2632017005 | Monticello | 07/23/2017 | 09/20/2017 | ML17264A32 | <strong>Diesel Generator Emergency Service Water System Automatic Transfer to Alternate Shutdown Panel</strong><br /><i>Abstract:&nbsp;</i>On July 23, 2017, the Emergency Diesel Generator (EDG) lube oil cooler immersion heater temperature switch failed (in the on position) which together with residual heat from 12 EDG operation actuated the EDG engine temperature switch resulting in a valid start signal to the 12 EDG Emergency Service Water (ESW) System pump and transfer of pump control to the Alternate Shutdown System panel. In accordance with 10 CFR 50.73(a)(2)(iv)(A) an automatic actuation of the ESW System is reportable. The apparent cause of the 12 EDG hot engine condition was a failed temperature switch for the immersion heater in concert with operating the 12 EDG. From the time of the problem identification through the 12 EDG surveillance test, lube oil temperature was monitored by Operations and never exceeded the normal operating band when the EDG was in the shutdown ready-to-start configuration and during the EDG monthly surveillance run. Therefore, the 12 EDG remained operable. The immediate corrective action was replacement of the failed temperature switch. A long-term corrective action is to evaluate the immersion heater and associated control circuit to determine if the temperature switch design and preventative maintenance frequency are appropriate. Corrective action will be taken based on the results of this evaluation.
2632017006 | Monticello | 11/14/2017 | 04/18/2018 | ML18109A00 | <strong>Loss of Reactor Protection System Scram Function During Main Steam Isolation Valve and Turbine Stop Valve Channel Functional Tests due to Use of a Test Fixture</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2017, it was identified that the use of the Reactor Protection System (RPS) test fixture described in some operations procedures would result in the loss of an RPS reactor Scram function. Technical Specification 3.3.1.1 requires that RPS Instrumentation for Table 3.3.1.1-1 Function 5, Main Steam Isolation Valve-Closure and Function 8, Turbine Stop Valve-Closure, remain operable. It was concluded that a closure of three of four Main Steam Lines or Turbine Stop Valves would not necessarily have resulted in a full Scram during testing depending on the combination of closed valves occurring during the bypass condition. Operations procedures were revised to incorporate the use of the test fixture in December, 2008 for the Turbine Stop Valve Closure Scram Test Procedure and February, 2009 for the Main Steam Isolation Valve Closure Scram Test Procedure. The operations procedures were inappropriately revised due to an inaccurate mental model that it was acceptable to use the test fixture on all RPS functions to prevent a half Scram.<br /><br /> The operations procedures were quarantined until revisions were issued in December, 2017 that removed use of the test fixture.
2652017001 | Quad Cities 2 | 05/15/2017 | 07/14/2017 | ML17194A81 | <strong>High Pressure Coolant Injection Minimum Flow Valve Failed to Open</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2017, at 19:18 hours, station Operations personnel were performing a High Pressure Coolant Injection (HPCI) Pump Operability Test which ensures the HPCI Minimum Flow Valve opens as pump flow decreases. When the HPCI Turbine was tripped, the Minimum Flow Valve did not open as expected when system flow was reduced to the low flow setpoint. Operators took steps to open the valve manually, but upon release of the control switch, the valve returned to the closed position. The valve was then left in the closed position. The HPCI system was declared inoperable and Technical Specification 3.5.1 Condition G was entered. <br /><br /> The cause of the Minimum Flow Valve failing to open was attributed to the HPCI Pump Discharge Flow Indicating Switch, specifically, intermittent failure of the high side micro switch caused by residual material from the manufacturing process. The Flow Indicating Switch, which had been installed for three months, was replaced and the HPCI Pump Operability Test was successfully re-performed. The failed switch was then sent to Exelon's Power Labs for failure analysis. <br /><br /> The safety significance of this event was minimal. Given the impact on the HPCI system, this report is submitted for Unit 2 in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The HPCI system is a single train system and the loss of HPCI could impact the plant's ability to mitigate the consequences of an accident.
2662017001 | Point Beach 1, Point Beach 2 | 09/18/2017 | 11/16/2017 | ML17320A01 | <strong>Control Room Barrier Inadvertently Disabled</strong><br /><i>Abstract:&nbsp;</i>At 1724 [CDT] on 9/18/17 Door-061, South Control Room Door (DR) was inadvertently disabled. The door became wedged open against its backstop during control room ventilation testing. Door-061 is a barrier that functions to maintain the control room envelope (NA). The barrier was subsequently disengaged from the backstop allowing it to close. The door was inspected and returned to operable status at 1750 [CDT]. While the door was stuck open, the control room was in an unanalyzed condition, a condition that could have prevented fulfillment of a safety function, and a common cause inoperability of independent trains or channels. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), 10 CFR 50.73(a)(2)(v)(A), 10 CFR 50.73(a)(2)(v)(D), and 10 CFR 50.73(a)(2)(vii) for a degraded barrier that affected the control room envelope.
2662017002 | Point Beach 1 | 10/29/2017 | 12/13/2017 | ML17347A77 | <strong>Operation or Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2017, Unit 1 entered MODE 3 from MODE 4 without satisfying all of Technical Specification 3.7.5, Auxiliary Feedwater (AFW) Limiting Conditions for Operation (LCO) as required by LCO Applicability 3.0.4 for the Turbine Driven Auxiliary Feedwater (TDAFW) pump system. <br /><br /> LCO Applicability 3.0.4 does not permit entry into a MODE of applicability when an LCO is not met, unless the associated actions to be entered permit continued operation in the MODE for an unlimited time or after performance of an acceptable risk assessment and the appropriate risk management actions have been established. After entering MODE 3, it was discovered that components were not operable, contrary to LCO 3.0.4.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), for an operation or condition prohibited by Technical Specifications.
2662017003 | Point Beach 1 | 10/30/2017 | 12/13/2017 | ML17347A77 | <strong>Degraded Condition</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2017, with Unit 1 in MODE 3 for refueling activities, a boric acid indication downstream of 1CV-309B, 1P-1B Reactor Coolant Pump (RCP) Labyrinth Seal 1DPT-124 Upper Root Valve was identified as a through-wall flaw. The flaw location on the root valve to differential pressure transmitter (DPT) instrument tubing welded joint was within the reactor coolant system (RCS) pressure boundary. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(A) for material defects in the primary coolant system that were not acceptable in accordance with ASME Section XI.
2692017001 | Oconee 1, Oconee 2, Oconee 3 | 06/16/2017 | 08/09/2017 | ML17256A51 | <strong>Loss of Both Keowee Hydroelectric Units due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2017, during implementation of a modification to Keowee Hydroelectric Station Governor Actuator Cabinets 1 and 2, breakers were inadvertently repositioned in each of the governor control system for Keowee Hydroelectric Units 1 and 2 (KHU1 and KHU2), rendering both units inoperable. The condition was discovered following an unsuccessful start of KHU2 for commercial operation. The KHUs are the onsite emergency power source for the Oconee Nuclear Station.<br /><br /> It was concluded that this constituted a loss of safety function from the time when both KHUs were inoperable until the dedicated offsite power source was aligned to the emergency busses; a period of approximately 7 hours. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(v)(A-D). <br /><br /> Technical Specifications (TS) were followed based on time of discovery; however, a subsequent review of computer logs provided firm evidence that both KHUs were inoperable for longer than allowed by TSs based on "past inoperability," requiring this event to be reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.<br /><br /> The direct cause of this event was attributed to the reposition due to inadvertent contact of two 24 VDC breakers. The risk impact of this event was determined to be insignificant and corrective actions are planned to prevent recurrence.
2722017001 | Salem 1 | 11/09/2017 | 01/08/2018 | ML18008A07 | <strong>Containment Integrity Inoperable for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2017 at approximately 2300, Salem Unit 1 was operating in MODE 3 when operators found steam leaking into the mechanical penetration area outside containment. Operators entered S1.OP-AB.STM-0001, Excessive Steam Flow, and dispatched operators to locate and isolate the leak. Operators determined the steam was from the 14 steam generator through normally closed valves 14GB47 and 14GB48 steam generator blowdown {WI} line nitrogen supply valves. The steam leak was isolated at 2314 when operators closed normally open manual valve 14GB3. <br /><br /> This report is made per 10CFR50.73(a)(2)(i)(B), Any operation or condition which was prohibited by the plant's Technical Specifications. <br /><br /> This was caused by human performance. Procedures will be revised to assure containment integrity exceptions are tracked and open valves are closed while sampling during the sparging process.
2772017001 | Peach Bottom 2, Peach Bottom 3 | 01/09/2017 | 12/21/2018 | ML19010A03 | <strong>Emergency Diesel Generator Exhaust Stacks Nonconforming Design for Tornado Missile Protection</strong><br /><i>Abstract:&nbsp;</i>On 1/9/17, it was determined that the site's Emergency Diesel Generators do not conform with the licensing basis for protection against tornado generated missiles. The exhaust stacks for the four on-site diesel generators extend approximately seven feet above the roof of the diesel generator building. In the event of a tornado, debris generated from the tornado could strike the exhaust stacks and, if at a sufficient mass and velocity, could crimp the exhaust stacks in a manner that would affect diesel generator operation. An extent of condition review identified unprotected cables that could be impacted by a tornado and affect the ability to maintain safe shutdown. <br /><br /> As a result of the non-conforming conditions, on 1/9/17 at 1530, all four emergency diesel generators were declared inoperable and on 11/1/18, the Reactor Core Isolation Cooling system and the RHR Suppression Pool Cooling system were declared inoperable. Compensatory measures were put in place and, in accordance with NRC guidance contained in EGM 15-002, the equipment was returned to an operable but non-conforming status. <br /><br /> Long-term corrective actions are being evaluated in accordance with EGM 15-002 and the plant's licensing basis. There are no actual consequences as a result of the non-conforming condition.
2782017001 | Peach Bottom 3 | 10/23/2017 | 12/20/2017 | ML17355A00 | <strong>Reactor Pressure Boundary Leakage due to Weld Failure in One-Inch Diameter Instrument Line</strong><br /><i>Abstract:&nbsp;</i>On 10/23/2017, during a walkdown of containment at the start of the Unit 3 refueling outage, a leak was identified in a socket weld for a 1-inch diameter instrument line. The line is connected to discharge piping for the 'B' recirculation pump and is part of the reactor coolant system pressure boundary. Because the leak was misting, the leakage rate could not be quantified. However, the reactor coolant system unidentified leakage prior to plant shutdown was 0.18 gpm. RCS pressure boundary leakage while in Mode 1 is a violation of Technical Specification 3.4.4 and is a reportable condition.<br /><br /> The cause of the event was a lack of fusion defect in the weld when it was done in the late 1980's. Normal vibration of the line since it was installed resulted in the crack initiating at the weld defect and propagating to the surface. The section of pipe and associated fitting were replaced, along with welds in similar sections of piping. There were no actual safety consequences as a result of this event.
2802017001 | Surry 1 | 08/09/2017 | 10/06/2017 | ML17297A45 | <strong>Unit 1 Shutdown due to an Unisolable Leak in Reactor Coolant Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2017, with Unit 1 at 100% power, a Reactor Coolant System (RCS) leak rate calculation determined the unidentified leak rate increased by 0.08 gallons per minute. On August 8, a leak was observed at an RCS hot leg sample system valve, and Unit 1 power level was reduced to investigate leakage indications. The root isolation valve for the sample system valve was closed; however, leakage could not be verified as completely isolated. Further evaluation determined the leak to be through wall at the inlet of the sample system valve. Based upon the source of the leak and possible continued leakage, a Technical Specification shutdown clock was entered on August 9, at 13:38 hours. At 16:37 hours, Unit 1 was placed in Hot Shutdown.<br /><br /> The cause of the event was the RCS pressure boundary leakage at the tubing/socket weld area of the hot leg sample system valve. With the unit in Hot Shutdown, the leak was isolated and repaired, and Unit 1 was returned to power operation on August 11, 2017. An apparent cause evaluation is being conducted. The event was reported as a plant shutdown required by Technical Specifications pursuant to 10 CFR 50.72(b)(2)(i) and degraded condition pursuant to 10 CFR 50.72(b)(3)(ii)(A). This report is being provided pursuant to 10 CFR 50.73(a)(2)(i)(A) and 10 CFR 50.73(a)(2)(ii)(A).
2852017001 | Fort Calhoun | 03/13/2017 | 05/11/2017 | ML17131A26 | <strong>Unprotected Vital Area Barrier due to Maintenance</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2017 at 16:00 hours, an unattended opening into a room classified as a vital area was identified by Security management. The unattended opening was created when a physical barrier was removed during decommissioning work within a vital area. The cause was determined to be an inadequate procedure(s) such that this action was not recognized by station personnel as a potential breach of a vital area pathway, therefore no compensatory measures were initiated prior to main steam discharge piping elbow removal. Upon recognition, the appropriate compensatory measures were implemented and a one hour report of Reportable Safeguards Events under 10 CFR 73.71(b)(1) and 10 CFR 73.71 Appendix G Section I (EN 52609) was submitted to the NRC.
2862017001 | Indian Point 3 | 05/14/2017 | 07/13/2017 | ML17202D07 | <strong>Single Flow Barrier Access Point Found Unbolted</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2017, at 0233 hrs, Indian Point Unit 3 entered Mode 4 as part of coming out of outage 3R19 and preparing for power operations. Operations test group was preparing for performance of 3-PTCS004, Residual Heat Removal (RHR) Check Valve Testing. The team gathered for a pre-job brief in accordance with the requirements of EN-HU-102, Human Performance Traps &Tools Procedure. At the time the only allowable access point to the Inner Crane Wall was through the double gate combination of Gates D and E, which require one gate to be maintained closed and secured at all times. Workers needed to enter inside of the Crane Wall to perform a portion of the valve lineup required by 3-PT-CS004. After unbolting and opening the gate, the two operators and a contract Radiation Protection (RP) Technician went through gate C despite a posted sign stating that the gate was not to be utilized in modes 1 through 4. While the valve manipulations were in progress the NRC Resident Inspector was also conducting a tour of the Vapor Containment (VC) and identified that gate C was opened. This gate being open in this plant condition resulted in a safety system functional failure, since with the gate unsecured this made the containment sumps inoperable.
2862017002 | Indian Point 3 | 06/11/2017 | 08/09/2017 | ML17227A13 | <strong>Manual Isolation of Chemical and Volume Control System Normal Letdown to Stop a Valve Leak Resulted in an Exceedance of Technical Specification 3.4.9 Condition A Limit for Pressurizer Level</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2017, while at 100 percent reactor power, Operations placed Chemical and Volume Control System (CVCS) Demineralizer Diversion Valve CH-TCV-149 in DIVERT to allow the 32 Mixed Bed Demineralizer to be removed from service and align the 31 Mixed Bed Demineralizer for service. Within about two minutes after returning CH-TCV-149 to AUTO, which placed the 31 Mixed Bed Demineralizer in service, Letdown Backpressure Control Valve CH-PCV-135 demand had gone to 0 percent (full open demand) while letdown backpressure had increased, reaching 302 psig. Operations was alerted to a leak that had developed on 32 Mixed Bed Demineralizer Inlet Isolation Valve CH-352. In an effort to isolate the leak, CH-TCV-149 was placed in DIVERT. Due to the elevated pressure at CH-TCV-149 with CH-PCV- 135 fully open, placing CH-TCV-149 in DIVERT coupled with the elevated line pressure created a pressure transient in the letdown line upstream of the CVCS Reactor Coolant Filter. Reactor Coolant Filter Inlet Isolation Valve CH-305 experienced this pressure transient, which resulted in the valve developing a significant leak at the body to bonnet joint. Abnormal Operating Procedure (AOP) 3-AOP-LEAK-1 was entered, and normal letdown was manually isolated to stop the CH-305 leak. Excess letdown was placed in service to balance reactor coolant inventory at a Pressurizer water level of 61 percent. This exceeded the 54.3 percent limit of Technical Specification 3.4.9 Condition A, and Operations declared the Pressurizer inoperable. The inoperability of the Pressurizer is reportable as a safety system functional failure under 10 CFR 50.73(a)(2)(v). The direct cause of this event was elevated system pressure due to loading of the Reactor Coolant Filter from materials when the 31 Mixed Bed Demineralizer pathway was aligned. The elevated operating pressure in the CVCS letdown stream challenged the integrity of diaphragm valves CH-352 and CH-305, requiring the isolation of normal letdown.
2862017003 | Indian Point 3 | 06/30/2017 | 08/29/2017 | ML17248A46 | <strong>Condensate Storage Tank Declared Inoperable Per Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2017, at 0130 hours [EDT], the Condensate Storage Tank was declared inoperable per Technical Specification 3.7.6. A pinhole sized through wall leak was discovered on the downstream side of CD-123, the 32 Auxiliary Boiler Feed Pump Bearing Cooling Relief Valve, which was unisolable to the Condensate Storage Tank. <br /><br /> The pinhole leak was identified following the performance of 3PT-Q120B, 32 Auxiliary Boiler Feed Pump Functional Test. All Operability and Acceptance Criteria of 3PT-Q120B were sat. The relief valve was removed from the system and sent to a vendor for evaluation. After the vendor evaluation, it was determined that the valve pinhole area leak was due to a casting defect. <br /><br /> This event was determined to be reportable as a Loss of Safety Function pursuant to10 CFR 50.72(b)(3)(v)(B) - Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.
2862017004 | Indian Point 3 | 11/03/2017 | 01/10/2019 | ML19017A06 | <strong>Reactor Trip due to Main Generator Loss of Field</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2017, at 2022 hours, with reactor power at 100 percent, Indian Point Unit 3 experienced an automatic reactor trip on a turbine trip, which was in response to a main generator trip. The main generator trip was initiated by actuation of the Generator Protection System due to a main generator loss of field. <br /><br /> All control rods fully inserted and all required safety systems functioned properly. The Auxiliary Feedwater System (AFWS) automatically started as expected on steam generator low level to provide feedwater flow to the steam generators. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of the loss of the main generator field was a failed Thyristor Firing Module drawer in the Automatic Voltage Regulator (AVR) system of the Main Generator Exciter System. The root cause was determined to be an inadequate refurbishment of obsolete power supplies in the AVR system. A plant modification has removed the obsolete power supplies from the design of the AVR system.<br /><br /> This event had no effect on the health and safety of the public. The event was reported to the Nuclear Regulatory Commission (NRC) on November 3, 2017 under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System when the reactor is critical and a valid actuation of the AFWS.
2872017001 | Oconee 3 | 07/24/2017 | 09/20/2017 | ML17271A13 | <strong>Unit 3 Reactor Protection System Actuation - Reactor Trip due to Turbine Trip from Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>On 7/24/17, with Oconee Nuclear Station (ONS) Unit 3 operating at 100 percent power, Transmission Department Relay personnel were in the ONS 525kV Switchyard Relay House performing preventive maintenance on a Breaker Failure Relaying device for Power Circuit Breaker PCB-57. This is a nonsafety PCB that isolates a commercial transmission line from the commercial bus in the 525kV switchyard. The maintenance was intended to actuate the protective relaying for PCB-57. The crew inadvertently connected test equipment to the adjacent relaying for PCB-58. The activation of the PCB-58 relay resulted in a Unit 3 separation from the electrical grid and a generator "Lockout." The lockout generates a turbine trip which in turn trips the reactor via the Reactor Protection System (RPS). This actuation of the RPS is reportable per 10 CFR 50.73(a)(2)(iv)(A). <br /><br /> Post trip plant response was normal and plant conditions were controlled and maintained within the allowances of Technical Specifications with no personnel injuries or safety system actuations. <br /><br /> A cause analysis attributed the cause of this event to human error in that test equipment was inadvertently connected to relaying for the incorrect PCB. The cause analysis corrective actions will address the likelihood of comparable human errors from occurring.
2892017001 | Three Mile Island 1 | 12/05/2016 | 02/03/2017 | ML17034A37 | <strong>Low Temperature Over-Pressurization (LTOP) Technical Specification Requirements Were Not Met</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2016 Three Mile Island Unit 1 was in a cold shutdown condition for a planned maintenance outage to replace the Reactor Coolant Pump 1A seal package. The reactor coolant system (RCS) was being filled and vented prior to pressurizing the RCS. Plant limits and precautions were not adhered to with respect to protecting the RCS from Low Temperature Overpressurization (LTOP) conditions by having RCS inventory too high with the Make-up system pump (MUP) breakers racked-in. This plant condition violated TMI-1 Technical Specification 3.1.12.1 and existed for approximately 3 hours until recognized. Once recognized, RCS inventory (Pressurizer level) was reduced within an hour per the TS action statement. The cause was attributed to operators not reviewing, understanding and complying with procedure limits and precautions for the plant condition. Corrective actions include coaching involved individuals on procedure use and adherence, and, procedure revisions to include actionable steps to improve LTOP Technical Specification compliance. This event is reported as a condition prohibited by Technical Specifications pursuant to 10 CFR 50.73(a)(2)(i)(B). This event had no effect on public health and safety.
2892017002 | Three Mile Island 1 | 12/07/2016 | 02/06/2017 | ML17038A40 | <strong>Leak At High Pressure Connection on Reactor Coolant Pump "A" Thermal Barrier</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2016 Three Mile Island Unit 1 was in the hot shutdown condition following a planned maintenance outage that replaced the Reactor Coolant Pump (RCP) 1A seal package when a reactor coolant system (RCS) leak was discovered on a welded connection of the Reactor Coolant Pump 1A thermal barrier. The identified leak was determined to be approximately 0.5 gpm, located on the RCS pressure boundary and nonisolable. Operators returned Unit 1 to a cold shutdown condition to repair the leak. The most probable cause for the leak is a latent weld defect that reduced the fatigue strength of the connection, coupled with RCP-1A startup vibration leading to failure. Immediate corrective action involved a weld repair modification to the leak location. Extent of condition applied to five similar locations that were examined with no weld defects identified. Additional corrective actions are planned to implement a weld repair modification to five similar connections on the RCPs during the Fall 2017 maintenance & refueling outage (T1R22). This event is reported as a degraded condition pursuant to 10 CFR 50.73(a)(2)(ii)(A). This event had no effect on public health and safety.
2892017003 | Three Mile Island 1 | 09/05/2017 | 11/06/2017 | ML17311A14 | <strong>Primary Containment Declared Inoperable due to Both Airlock Doors Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On September 5, 2017 Three Mile Island Unit 1, was operating at 100% full power and preparing for a scheduled maintenance and refueling outage. During a planned entry through the primary containment personnel airlock of the equipment hatch, both doors were open simultaneously for less than one minute due to failure of the interlock mechanism. The breach of containment was immediately recognized and the inner door of the equipment hatch airlock was closed. Personnel were dispatched to the outer door and closed the door. Investigation determined the interlock linkage designed to prevent both doors from being opened simultaneously failed due to a bent ratchet pawl. During the refueling and maintenance outage (when containment integrity was not required), the equipment hatch airlock interlock linkage failure was able to be repeated. Corrective action included a weld repair and adjustment to the ratchet pawl interlock linkage. Post maintenance testing of the interlock, including local leak rate testing (LLRT) of the airlock, was performed satisfactorily. This event is reportable as a degraded condition to a principal safety barrier, and, a condition that could have prevented fulfillment of a safety function to control the release of radioactive material, and, a condition prohibited by technical specifications. The event had no significant impact on public health and safety.
2892017004 | Three Mile Island 1 | 12/06/2017 | 10/31/2019 | ML19310D77 | <strong>Items Nonconforming to Design for Tornado Missile Protection</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2017 Three Mile Island Unit 1, determined that both Emergency Diesel Generators do not conform with the licensing bases for protection against tornado generated missiles. The vent on the common Fuel Oil Supply Tank that serves both Emergency Diesel Generators could be damaged by debris generated from a tornado that could affect emergency diesel generator operation. An extent of condition review identified three additional items that are nonconforming to the design for tornado missile protection: vent stacks for each Emergency Diesel Generator Day Fuel Tanks, the Borated Water Storage Tank and steam piping near the main feed pumps that could affect Secondary Pressure Control. Upon determination of the initial nonconformance for the Fuel Oil Supply Tank Vent on December 6, 2017, both Emergency Diesel Generators were declared inoperable. Compensatory measures were put and verified in place in accordance with the NRC Enforcement Guidance Memorandum EGM 15-002, both emergency diesel generators were returned to an operable but nonconforming status and an 8 hour ENS Notification was made to the NRC. This condition has been in existence since original licensing of the plant. It is not known if it was overlooked or considered acceptable at the time of the original licensing process. There are no actual consequences as a result of the nonconforming conditions.
2932017001 | Pilgrim | 01/16/2017 | 07/17/2017 | ML17220A06 | <strong>Reactor Building Isolation Dampers Failed to Isolate</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2017, with the reactor at 100 percent power and the mode switch in RUN, Pilgrim Nuclear Power Station (PNPS) was performing surveillance testing of secondary containment isolation dampers when dampers AO-N-82 and AO-N-83, refueling floor supply isolation dampers, failed to fully close when the control switches were taken to close. <br /><br /> The failure of dampers AO-N-82 and AO-N-83 to fully close resulted in a loss of safety function for secondary containment, causing immediate entry into Limiting Condition for Operation (LCO) Action Statement (AS) 3.7.C.2.a, at 1155 hours. This LCO AS was exited at 1206 hours when the dampers were verified closed. <br /><br /> An 8-hour non-emergency notification was made in accordance with 10 CFR 50.72(b)(3)(v), any event or condition that at the time discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. In addition, this notification is being conservatively made by PNPS in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition that was prohibited by Technical Specifications. <br /><br /> The reactor building isolation dampers were cleaned, lubricated and post-work tested. PNPS has returned the dampers to operable status. Planned action to prevent recurrence is to revise the preventive maintenance strategy. <br /><br /> There was no impact to public health and safety from this condition.
2932017002 | Pilgrim | 03/27/2017 | 05/25/2017 | ML17163A17 | <strong>Isolation of HPCI</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2017, at 1825 [EDT], with the reactor at 100 percent core thermal power and steady state conditions, plant personnel caused a High Pressure Coolant Injection (HPCI) System isolation. Pilgrim Nuclear Power Station was performing planned testing on the Reactor Core Isolation Cooling (RCIC) when the HPCI System isolated. Accordingly, the HPCI System was declared inoperable. <br /><br /> The Technical Specifications Limiting Condition for Operation Action Statement 3.5.C.2 was entered and planned troubleshooting into the cause of the HPCI isolation was started. This event is reportable under 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. <br /><br /> There was no impact to public health and safety from this condition.
2932017003 | Pilgrim | 03/31/2017 | 11/13/2017 | ML17325A98 | <strong>Supplement to Suppression Pool Declared Inoperable due to High Water Level</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2017, at 1155 [EDT], with the reactor at 97 percent core thermal power and steady state conditions, operators were restoring a valve lineup after performing planned operations when a pathway was created through valve manipulation that allowed water in the Condensate Storage Tank to be diverted to the suppression pool. The rise in suppression pool water level exceeded the maximum water level specified in Technical Specifications (TS) and caused a lowering of the drywell to suppression pool differential pressure. <br /><br /> With suppression pool water level and differential pressure both outside of TS limits, Limiting Condition for Operation Action Statements 3.7.A.5 and 3.7.A.8.c were both entered and investigation into the cause of diverting water into the suppression pool was initiated. Water level was restored to within TS limits at 1540 [EDT]. <br /><br /> An 8-hour non-emergency notification was made in accordance with 10 CFR 50.72(b)(3)(v)(D), any event or condition that at the time discovery had the potential to have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.<br /><br /> The initial LER was submitted under 10 CFR 50.73(a)(2)(i)(B), operation or condition prohibited by TS, but it was subsequently determined it should have been submitted under 10 CFR 50.73(a)(2)(v)(D), any event or condition that at the time of discovery had the potential to have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident, to more precisely describe this condition. <br /><br /> There was no impact to public health and safety from this condition.
2932017004 | Pilgrim | 04/05/2017 | 06/02/2017 | ML17163A17 | <strong>Secondary Containment Testing Led to Loss of Safety Function to Both Trains of Standby Gas Treatment System</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2017, at 0030 hours [EDT] with the Reactor in the Run Mode at approximately 97 percent power, both trains of the Standby Gas Treatment System (SBGTS) were made inoperable during the performance of a surveillance test of secondary containment prior to the refueling outage.<br /><br /> With both trains of SBGTS inoperable while in the Run mode, this event is reportable per the requirements of Title 10, Code of Federal Regulations (CFR) 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D), any event that could have prevented the fulfillment of the safety functions to "control the release of radioactive material" and "mitigate the consequences of an accident." <br /><br /> This event had no impact on the health and/or safety of the public.
2932017005 | Pilgrim | 04/10/2017 | 06/07/2017 | ML17171A27 | <strong>10 CFR 50, Appendix J, Option B, Leak Rate Criteria Exceeded</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2017, the Personnel Airlock, X-2, failed to meet local leak rate test acceptance criteria. This failure is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. <br /><br /> On April 22, 2017, the High Pressure Coolant Injection System turbine exhaust line check valves both failed to meet local leak rate test acceptance criteria. The test volume for each valve could not be pressurized when flow was greater than 100 Standard Liters per Minute. Significant air flow was coming out of the test vent, indicating that each check valve was either degraded or not seated. <br /><br /> This failure resulted in the current Refueling Outage summation of Type B and Type C testing results exceeding the 10 CFR 50, Appendix J local leak rate test criteria limit of 0.6 La and the primary containment total leakage criteria limit of 1.0 La. This created an event that is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications,10 CFR 50.73(a)(2)(ii)(A), any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded, 10 CFR 50.73(a)(2)(v)(C), any condition that could have prevented the fulfillment of a safety function of a system needed to control the release of radioactive material, and 10 CFR 50.73(a)(2)(v)(D), any condition that could have prevented the fulfillment of a safety function of a system needed to mitigate the consequences of an accident. <br /><br /> There was no impact to public health and safety from this condition.
2932017006 | Pilgrim | 04/14/2017 | 06/13/2017 | ML17171A23 | <strong>Source Range Monitor Inoperable During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2017, with the reactor at 0 percent core thermal power in a refueling outage, Pilgrim Nuclear Power Station discovered that during fuel movements (core alterations) conducted on April 14th and April 15th in reactor quadrant 'B', source range monitor channel B (SRM B) was inoperable due to not meeting the signal to noise ratio of no less than 2 to 1 required by FSAR section 7.5.4.1. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. <br /><br /> There was no impact to public health and safety from this condition.
2932017007 | Pilgrim | 04/24/2017 | 12/20/2017 | ML18004A06 | <strong>Supplement to Potential Inoperability of Safety Relief Valve 3A</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2017, during Refueling Outage 21 while performing testing on the Pilgrim Nuclear Power Station (PNPS) Safety/Relief Valves, a high resistance was measured across the solenoid pilot valve coil of SV203-3A. This solenoid pilot valve was replaced during Refueling Outage 21. After the solenoid pilot valve was removed it was transported to an offsite vendor for additional testing. <br /><br /> This LER supplement is being submitted to provide the NRC with additional information. PNPS continued to follow the testing performed by our offsite vendor and now has additional information to provide the NRC. <br /><br /> PNPS stated at the time that this event was reportable under 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications and also, potentially reportable under 50.73(a)(2)(v)(B) and 50.73(a)(2)(v)(D), a condition that could have prevented fulfillment of a safety function needed to remove residual heat and mitigate the consequences of an accident. However, additional information provided by our offsite vendor and an engineering evaluation, support the conclusion that there was never a loss of safety function regarding SV203-3A. Therefore, this event was not reportable under 10 CFR 50.73(a)(2)(i)(B) nor under 10 CFR 50.73 (a)(2)(v)(B) or (D). <br /><br /> This event posed no threat to public health and safety.
2932017008 | Pilgrim | 05/03/2017 | 11/02/2017 | ML17312A27 | <strong>Supplement to 480V Bus B6 Auto Transfer Function Degraded due to Time Delay Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2017 with the unit shutdown for refueling outage, while performing plant procedure 3.M.3-27, "480V Bus B6 Transfer Test, UV, Degraded Voltage and Timing Relays Calibration and Annunciator Verification," the time delay Agastat relay 27A-B1X/TDDO opened instantaneously, instead of with a time delay. This relay is set to drop out after a 1.25 second time delay after being de-energized. This condition was discovered during the plant's refueling outage when conditions were such that the equipment normally energized/activated by this time delay relay was not required to be operable.<br /><br /> Pilgrim Nuclear Power Station is submitting this Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(i)(B) - Operation or condition prohibited by Technical Specifications; and in accordance with10 CFR 50.73(a)(2)(v)(B), (C) and (D) - Any condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat, control the release of radioactive material and mitigate the consequences of an accident. <br /><br /> This event was not risk significant. There was no threat to public health and safety from this condition.
2932017009 | Pilgrim | 05/17/2017 | 12/28/2017 | ML18009A43 | <strong>Supplement to Potential Primary Containment System Inoperability due to Relay Concerns</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2017, during Refueling Outage (RFO)-21 while performing an extent of condition review it was discovered that the contact indicating tabs of relays 16A-K30 and 16A-K54 of the Pilgrim Nuclear Power Station (PNPS) Primary Containment System, were visually hanging in the mid-position (partial travel). <br /><br /> The relays were replaced during RFO-21 along with 16A-K29 and 16A-K53, and all four relays were sent to an offsite vendor for further testing and analysis. Other relays were reviewed but were determined to be outside the scope of this extent of condition review. <br /><br /> PNPS stated at the time that this event was reportable under 10 CFR 50.73(a)(2)(i)(B) - Operation or condition prohibited by Technical Specifications; and potentially reportable in accordance with 10 CFR 50.73(a)(2)(v)(B), (C) and (D) - Any condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat, control the release of radioactive material and mitigate the consequences of an accident. However, additional information provided by our offsite vendor and an engineering evaluation, support the conclusion that there was never a loss of safety function regarding any of the four relays (16A-K29, 16AK30, 16A-K53 and 16A-K54). Therefore, this event was not reportable under 10 CFR 50.73(a)(2)(i)(B) nor under 10 CFR 50.73(a)(2)(v)(B), (C) or (D).<br /><br /> This event posed no threat to public health and safety.
2932017010 | Pilgrim | 06/07/2017 | 08/07/2017 | ML17227A13 | <strong>Air Accumulation Creates Small Void in Core Spray Discharge Piping</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2017, at 1357 [EDT] with the reactor at 100% core thermal power and steady state conditions, plant personnel were performing Ultrasonic testing (UT) examination on Core Spray A high point piping in the A Residual Heat Removal Quad to ensure this piping was water solid, when they identified that the top of this horizontal pipe had an air void internally. A high point vent line with valves is located in the area of the UT exam. It was found that the top 2 inches of the 10 inch core spray pump discharge line had accumulated an air void within the known inverted loop in Core Spray Loop-A discharge line. The system had been drained for maintenance during the Refueling Outage. <br /><br /> Pilgrim Nuclear Power Station is reporting this event pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications. Although upon discovery the proper Limiting Condition for Operation Action Statement was entered and the void was filled immediately to correct the issue, it is believed that this condition existed before the time of discovery for a period of time longer than that allowed by Technical Specifications. <br /><br /> This event posed no threat to public health and safety.
2932017011 | Pilgrim | 06/20/2017 | 08/15/2017 | ML17234A31 | <strong>Simultaneously Opened Reactor Building Airlock Doors Caused Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2017, at 1444 hours [EDT], with the reactor at 100% core thermal power and steady state conditions, plant personnel notified the Main Control Room that both doors in the secondary containment airlock at the 23 foot elevation on the East Side Reactor Building (RB) Entrance were opened simultaneously. The failure of this interlock (to prevent both doors from being opened) caused a loss of secondary containment per Technical Specification (TS) 3.7.C.1. The doors were immediately closed, and the secondary containment boundary was reestablished.<br /><br /> An 8-hour non-emergency notification was made in accordance with 10 CFR 50.72(b)(3)(v)(C), any event or condition that at the time discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The safety significance of this event was minimal given the impact on the secondary containment. <br /><br /> Secondary containment remained available and functional during the event since secondary containment was immediately restored by closing the doors.
2932017012 | Pilgrim | 09/13/2017 | 10/25/2018 | ML18304A33 | <strong>Supplement to Start-Up Transformer Degraded Voltage Relay Found Outside Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2017 with the unit at 100 percent power, Pilgrim Nuclear Power Station discovered during calibration of four Start-Up Transformer Degraded Voltage Relays (ABB model number ITE- 27N) after the relays had been removed from the plant, relay 127A-604/1 had an as-found setpoint value outside the Technical Specifications Table 3.2.B limit of 110.6 plus or minus 0.56 Volts ac (Vac) (110.04 - 111.16); the as-found value was 109.90 Vac. This relay was replaced with a spare relay that was calibrated prior to its installation. <br /><br /> Pilgrim Nuclear Power Station is submitting this Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(i)(B) - Any operation or condition that was prohibited by the plant's Technical Specifications. <br /><br /> This event was not risk significant. There was no threat to public health and safety from this condition.
2932017013 | Pilgrim | 11/26/2017 | 05/01/2018 | ML18128A18 | <strong>Supplement to Reportable Conditions Involving Standby Gas Treatment System and Secondary Containment Inoperability Not Reported During the Previous Three Years</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2017, with the Reactor in the Run Mode at 100 percent power, while reviewing a procedure to be performed during scheduled testing, it was determined that the test as written would cause both trains of the Standby Gas Treatment System (SGTS) to be made inoperable during the test. This also would make secondary containment inoperable. This LER is submitted to acknowledge that Pilgrim Nuclear Power Station missed providing Event Notifications and LERs for past occurrences. With both trains of SGTS and secondary containment inoperable while in Run, the occurrences would have been reportable if identified at the time in accordance with 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) as conditions that could have prevented the fulfillment of the safety function of a structure or system needed to control the release of radioactive material and mitigate the consequences of an accident. This has been determined to be a reportable condition involving SGTS and secondary containment inoperability in accordance with 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) which has not been reported during the past three years. <br /><br /> This event had no impact on the health and/or safety of the public.
2962017001 | Browns Ferry 3 | 09/01/2017 | 10/31/2017 | ML17304B08 | <strong>Inoperable Residual Heat Removal Pump Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2017, at approximately 1006 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) Unit 3 3A Residual Heat Removal (RHR) system pump failed to start during performance of Surveillance 3-SR-3.5.1.6 (RHR I), Quarterly RHR System Rated Flow Test Loop I. The apparent cause was the Electrical Preventive Maintenance Instruction for 4kV Wyle/Siemens Horizontal Vacuum Circuit Breaker (Type-3AF) and Compartment Maintenance was revised to include steps to secure the breaker’s mounting hardware which caused internal binding of the indication flag. Binding of the indication flag prevented the closing spring of the breaker from charging and the breaker from closing on demand. As a result, automatic start of the 3A RHR pump was prevented. On September 1, 2017, at approximately 1633 CDT, the 3A RHR Pump was declared operable following lubrication and testing of the breaker’s indication flag mounting bolt. <br /><br /> A Past Operability Evaluation concluded that the 3A RHR Pump was inoperable from July 26, 2017 to September 1, 2017, which exceeded the Technical Specification allowed outage time. During this time, the 3B, 3C, and 3D RHR pumps would have started automatically upon receipt of an Emergency Core Cooling System (ECCS) initiation signal or from an Operator manual start demand from the Control Room. Based on results from the Probability Risk Assessment and Engineering inspections, there was no significant risk to the health and safety of the public or plant personnel for this event. The Corrective Action to reduce the probability of similar events occurring in the future will be addressed by revising the Electrical Preventive Maintenance Instruction for 4kV Wyle/Siemens breakers to ensure freedom of movement of the indication flag is present during the breaker inspection.
2962017002 | Browns Ferry 3 | 11/01/2017 | 12/29/2017 | ML17363A29 | <strong>4kV Shutdown Board Potential Transformer Primary Fuses Do Not Coordinate with Secondary Fuses</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2017, at approximately 1425 Central Daylight Time, during an extent of condition review, a fuse coordination issue was discovered. Four Potential Transformer (PT) 10 amp secondary fuses on Unit 3 4kV Shutdown Boards (SD BD) do not selectively coordinate with upstream 0.5 amp primary fuses for fault currents greater than 30 amps on the 120 V secondary. Cable fire damage could cause an affected SD BD to spuriously disconnect from off-site power, and could cause a spurious, maintained under-voltage trip signal. The under-voltage trip signal would prevent motor load operation on the board whether on off-site power or Emergency Diesel Generator power. If a fire were to occur in fire areas 03-03 or 16, all four Unit 3 4kV SD BDs could be affected. In fire area 21, 4kV SD BDs 3EA and 3EB could be affected. <br /><br /> This condition was determined to be a legacy issue dating to the original design of the plant. The most likely cause is lack of rigorous oversight of the vendor during the preparation and subsequent issuance of the fuse evaluation for the four Unit 3 4kV SD BDs. The required coordination studies have since been performed and a vendor oversight process has been added to TVA procedures. Compensatory measures (hourly fire watches) have been put in place for affected fire areas. Additional corrective actions include issuing an Engineering Change Package to replace the Unit 3 4kV SD BDs primary 0.5 amp PT fuses with 1 amp fuses of the same type.
2982017001 | Cooper Station | 02/05/2017 | 12/15/2017 | ML17354A15 | <strong>Residual Heat Removal Minimum Flow Valves Out of Position Results in Loss of Safety Function and Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2017, during a quarterly sealed valve log audit, Residual Heat Removal (RHR) Valves RHR-V-58 and RHR-V-60 were discovered sealed closed. Normal configuration for these valves is sealed opened. Consequently, Operations declared RHR pumps A and C Inoperable at 0756 hours and entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.5.1 Condition A, LCO 3.6.1.9 Condition A, and LCO 3.6.2.3 Condition A. <br /><br /> Subsequently, the operating crew opened RHR-V-58 and RHR-V-60, independently verified the position of the valves and applied seals to the valves. As such, RHR pumps A and C were declared Operable at 1041 hours on February 5, 2017, and TS LCO 3.5.1 Condition A, LCO 3.6.1.9 Condition A, and LCO 3.6.2.3 Condition A were exited. <br /><br /> The root cause is Operations Department standards related to Operator Human Performance and Configuration Control are inadequate and do not meet industry expectations. Licensed and Non-Licensed Operators completed training focused on Standards and Expectations related to attention to detail and configuration control. To prevent recurrence, expectations will be established and institutionalized for Operations Leadership to reinforce consistent application of operator fundamentals and to identify and correct performance gaps for the operating crews.<br /><br /> This is a Safety System Functional Failure.
2982017002 | Cooper Station | 02/28/2017 | 04/27/2017 | ML17139D35 | <strong>Valve Test Failures Result in Condition Prohibited by Technical Specifications and a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>In February and March 2017, three Main Steam Safety Relief Valve (SRV) body assemblies (main body and pilot assembly) and the remaining five SRV pilot assemblies were tested at National Technical Systems Laboratories (formerly Wyle Laboratories). These SRVs had been removed from Cooper Nuclear Station during Refueling Outage 29 in the Fall of 2016. One SRV pilot assembly failed the as-found lift pressure testing; another SRV pilot assembly was conservatively considered a failure due to lack of as-found lift pressure test data since it was inadvertently disassembled prior to performing the as-found lift pressure test. <br /><br /> There were two causes for the failures. One of the SRV pilot assemblies failed due to corrosion bonding; the other SRV pilot assembly failed due to a lack of a barrier to prevent inadvertent disassembly of the SRV pilot prior to testing. <br /><br /> Although the Technical Specifications limits related to the set point lift pressures of the SRV pilot valve assemblies were exceeded, an analysis indicates that the design basis pressures to ensure safety of the reactor vessel and its pressure related appurtenances were not challenged. Public safety was not at risk. Safety to plant personnel and plant equipment was not at risk.
2982017003 | Cooper Station | 05/26/2017 | 04/20/2018 | ML18116A44 | <strong>Mispositioned Control Room Emergency Filter System Supply Fan Damper Causes Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2017, a Control Room Emergency Filter System (CREFS) supply fan damper was discovered to be partially open, limiting air flow to less than the Technical Specifications (TS) required flow. The configuration of the supply fan damper is to be fully open when the corresponding supply fan is in service. Cooper Nuclear Station (CNS) Operations personnel declared CREFS inoperable at 1105 and entered TS Limiting Condition for Operation 3.7.4, Condition A. <br /><br /> Subsequent investigation revealed that the damper control arm was correctly positioned, however the T-handle for the control arm was overtightened causing the control arm to bend upward which mispositioned the damper from full open to partially open. The control arm for HV-AD-AD1021B was replaced and post work testing performed to ensure the correct position of the damper. CREFS was declared operable at 0432 on May 27, 2017. <br /><br /> To prevent recurrence, CNS will modify the design of the both CREFS damper control arms and the means of securing in position to prevent control arm bending. <br /><br /> There were no safety consequences associated with this condition.
2982017004 | Cooper Station | 06/19/2017 | 01/24/2019 | ML19031B33 | <strong>Torus to Drywell Vacuum Breaker Failure to Indicate Full Closed Causes Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2017, during performance of surveillance 6.PC.207, the control switch for vacuum breaker PC-AOV-NRV21 was cycled open then closed. When the control switch was taken to close, the vacuum breaker failed to indicate closed. Operations declared Primary Containment (PC) and PC-AOV-NRV21 inoperable and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.1 Condition A and LCO 3.6.1.8 Condition B at 21:15 hours. In addition, TS LCO 3.6.1.1 Condition B was entered at 22:15 hours due to PC-AOV-NRV21 still indicating intermediate. The control switch for PC-AOV-NRV21 was cycled open, and then closed a second time. At this time, PC-AOV-NRV21 indicated closed. Operations declared PC and PC-AOV-NRV21 operable at 23:11 hours and exited TS LCO 3.6.1.1, Condition A and Condition B, and TS LCO 3.6.1.8, Condition B.<br /><br /> Two potential causes were identified during troubleshooting activities. The first is increased internal friction in the valve air operator of the vacuum breaker could cause the operator to close too slowly and limit the ability to fully close. The second is the solenoid operated valve (SOV) could bleed vented air off slowly causing the vacuum breaker to not fully close. Both the valve air operator and the SOV were replaced during troubleshooting activities. <br /><br /> There were no safety consequences associated with this condition.
2982017005 | Cooper Station | 06/22/2017 | 08/17/2017 | ML17236A16 | <strong>Traversing In-core Probe In-shield Limit Switch Mounting Failure Results in Common Cause Inoperability of Independent Trains or Channels and Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2017, Traversing In-core Probe (TIP) C failed to stop at its in-shield position when being withdrawn from the core. Cooper Nuclear Station (CNS) Operations personnel declared the associated TIP C ball valve inoperable as a Primary Containment Isolation Valve (PCIV) at 0524 and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.3, Condition A. On June 22, 2017, TIP D failed to stop at its in-shield position when being withdrawn from the core. CNS Operations personnel declared the associated TIP D ball valve inoperable as a PCIV at 0445 and entered TS LCO 3.6.1.3, Condition A. <br /><br /> Subsequent investigation determined the cause of the failures was inadequate mounting and securing of the in-shield limit switch to the chamber shield. Corrective actions included repair of the mounting of the in-shield limit switches for all TIP channels, and improved procedure guidance for properly mounting the in-shield limit switches.<br /><br /> Both valves were declared operable on July 13, 2017, at 1133. <br /><br /> There were no safety consequences associated with this condition.
3062017001 | Prairie Island 2 | 05/02/2016 | 11/29/2017 | ML17334A04 | <strong>23 Containment Fan Coil Unit Operability</strong><br /><i>Abstract:&nbsp;</i>From May 2, 2016 to May 6, 2016, when B Train 122 Control Room Chiller (CRC) was out-of-service (OOS) per Technical Specifications (Tech Specs) 3.7.11 Condition A, Unit 2 A Train 23 Containment Fan Coil Unit (FCU) was OOS. According to revision 41 of site procedure C18.1, "Engineered Safeguards Equipment Support Systems," Bus 16 load sequencer and Bus 121 were inoperable when 122 CRC was OOS. Bus 121 supports B Train Diesel Driven Cooling Water Pump and Unit 2 B Train containment cooling (22/24 FCUs). So both trains of containment FCUs were OOS at the same time for approximately 35.6 hours. This would have required entry into LCO 3.0.3 putting Unit 2 in MODE 3 within 7 hours, this did not occur. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Tech Specs. <br /><br /> The cause was that the Senior Reactor operators failed to utilize Human Performance Tools (Verification/Validation and Procedure Use/Adherence) when assessing the Tech Specs impact to Unit 2 for applying LCO 3.0.6 when 122 CRC was taken OOS. <br /><br /> Corrective actions include independent assessment of shared system LCO's for each unit, revising the LCO database, established a standard for LCO 3.0.6 log entries, and revising the safety function determination program to be more user friendly.
3062017002 | Prairie Island 2 | 10/16/2017 | 12/11/2017 | ML17346A07 | <strong>Reactor Coolant System Shutdown Communication Live Vent Through Wall Defect</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2017, with Unit 2 shutdown for a refueling outage, investigation into a boric acid indication identified a through wall leak at the socket weld that joins a 3/4 inch line to Loop A Reactor Coolant System (RCS)[AB] shutdown communication line valve 2RC-8-37 [VTV]. The leak was isolated by closed valves that would have limited primary coolant leakage to within the capacity of the charging system when the reactor coolant system was pressurized. The quantity of dry boric acid at the location was small (estimated at 1/2 teaspoon in volume). This failure constituted a welding or material defect in the primary coolant system that was not found acceptable under ASME Section Xl and an event or condition prohibited by Technical Specifications. <br /><br /> The cause of the leakage was determined to be stress corrosion cracking. Valve 2RC-8-37 was replaced. In addition, Prairie Island Nuclear Generating Plant intends to perform phased array ultrasonic inspections of socket welds on similar Class 1 piping containing stagnant water during future refueling outages.
3062017003 | Prairie Island 2 | 11/12/2017 | 01/11/2018 | ML18011A04 | <strong>Both Containment Spray Pump Control Switches in Pull-out in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2017 at 2119, a Control Room board walkdown discovered that both of the Unit 2 Containment Spray Pump control switches had been left in pull-out, when operators transitioned Unit 2 from Mode 5 to Mode 4. With the control switches in pull-out, the pumps would not automatically start as required. Technical Specification (Tech Specs) 3.0.3 was entered as a result of not complying with Technical Specification 3.6.5, Containment Spray and Cooling systems, which required both trains of Containment Spray to be Operable while in Mode 4. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), Condition Prohibited by Technical Specification and 10 CFR 50.73(a)(2)(v)(D), Event or Condition that Could Have Prevented Fulfillment of a Safety Function. <br /><br /> The root cause determined that Surveillance Procedure SP 2099, Unit 2 Main Steam Isolation Valve Logic Test, was not adequately designed to account for outage schedule variation. Contributing causes included that the Unit 2 Startup to Mode 4 procedure does not contain adequate process barriers such that plant configuration meets Technical Specification requirements for Mode 4 entry. Operations personnel failed to uphold standards for panel walkdown requirements. <br /><br /> Corrective actions include revising SP 2099, Unit 2 Main Steam Isolation Valve Logic Test to include steps to reposition Containment Spray Switches to the "as found" configuration and revise Unit 2 start-up procedure to add additional HOLD to have the Shift Manager perform Control Board Walkdown to verify equipment required in Mode 4 is aligned and Operable. Develop and implement an operations improvement plan specifically targeted to improve Operator standards in the performance of Control Board Walkdowns.
3112017001 | Salem 2 | 04/14/2017 | 06/13/2017 | ML17164A30 | <strong>Emergency Diesel Generator Start due to a Loss of Power to the 2C 4160 Volt Vital Bus</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2017 at 13:57 while attempting to transfer the 2C 4 Kilovolt (kV) vital bus from 24 Station Power Transformer (SPT) to 23 SPT, the 24 SPT infeed breaker opened properly but 23 SPT infeed breaker failed to close. The 23 SPT infeed breaker failing to close as expected resulted in de-energization of the 2C 4kV vital bus and subsequent start and loading of the 2C Emergency Diesel Generator (EDG) to power the bus.<br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the 2C EDG. Notification of this event was provided via ENS report 52681.
3132017001 | Arkansas 1, Arkansas 2 | 04/26/2017 | 06/26/2017 | ML17177A31 | <strong>Automatic Start of an Emergency Diesel Generator due to the Loss of Offsite Power due to Severe Weather</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2017, Arkansas Nuclear One, Unit 1 (ANO-1), was operating normally at 100% rated thermal power. The 500kV transmission line to the substation at Pleasant Hill, Arkansas was out of service for planned maintenance. The area around the plant was experiencing severe weather from thunderstorms and tornado warnings had been issued from the National Weather Service for the four county area. <br /><br /> At approximately 1002 CST switchyard breakers for 500kV lines opened on fault current. High winds had damaged the transmission towers approximately 16 miles away from ANO and caused phase to ground faults. This resulted in a loss of all offsite power lines to the 500kV bus. The autotransformer also locked out as designed when the 500kV transmission lines faulted. <br /><br /> The Reactor Operator initiated a manual reactor trip about 8 seconds after the 500kV lines tripped and prior to the reactor protection system initiating an automatic trip. During this time both emergency diesel generators (EDGs) [EK] started as expected. EDG #2 re-energized one Engineered Safeguards bus. EDG #1 ran unloaded until shutdown. <br /><br /> The plant was stabilized in Mode 3 with Emergency Feedwater (EFW) pumps supplying the steam generators, maintaining the water level at the natural circulation setpoint.
3132017002 | Arkansas 1 | 05/27/2017 | 11/13/2017 | ML17317A44 | <strong>High Pressure Injection Pump Inoperable for Greater Than Technical Specification Completion Time</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2017, an attempt to start the red train High Pressure Injection (HPI) pump [BJ] in accordance with normal operating procedures was initiated. Control Room operators received an annunciator, HPI PUMP TRIP, and observed no indication of the pump starting. <br /><br /> During investigative walk downs with the relay department, personnel discovered the HPI breaker was not fully racked up (trip pedal still in a tripped (down) condition and roller not free to roll). Operations personnel performed manual breaker operations to rack the 4160 V breaker [EB] further in the up direction. The pump was successfully started and declared operable. <br /><br /> The condition was the result of an inadequate risk evaluation.<br /><br /> The associated Operations Directive has been revised to require Operations management approval when waiving start-checks of vital 4160 VAC components following racking up of the respective breaker. The revision is expected to ensure appropriate personnel are involved when determining the risk associated with not testing components for functionality/operability following racking up evolutions of an associated breaker.
3152017001 | Cook 1 | 12/21/2017 | 02/19/2018 | ML18053A13 | <strong>Unit 1 Turbine Driven Auxiliary Feedwater Pump Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2017, with Unit 1 operating in Mode 1 at 100 percent power, the Unit 1 Turbine Driven Auxiliary Feedwater Pump (TDAFP) failed a surveillance test by not achieving the required operating speed and was declared inoperable. An investigation followed that discovered an incorrect governor valve linkage setup. Following corrective maintenance, surveillance testing requirements were met and the TDAFP was restored to operable status on December 23, 2017. An evaluation was completed and determined that the incorrect governor valve linkage setup condition that affected pump operating speed was introduced during a previous maintenance activity. As a result, the TDAFP was considered inoperable longer than allowed by Technical Specifications (TS) during a period from November 25, 2017, until December 23, 2017. <br /><br /> The cause of the incorrect governor valve linkage setup that prevented the TDAFP from reaching the required operating speed was due to insufficient guidance within applicable maintenance procedures. Corrective actions include revising the applicable maintenance procedures to ensure that future governor linkage maintenance activities result in the pump meeting all required acceptance criteria.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), as an Operation or Condition Prohibited by Technical. Specifications.
3162017001 | Cook 2 | 03/23/2017 | 05/19/2017 | ML17143A23 | <strong>Unit 2 Containment Hydrogen Skimmer Ventilation Fan #1 Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2017, at 0941, Eastern Daylight Time (EDT), with Unit 2 in Mode 1 at 100% power, the Unit 2 Containment Hydrogen Skimmer Ventilation (CEQ) Fan #1 was declared inoperable to perform surveillance testing. During the test, the Unit 2 CEQ Fan #1 Backdraft Damper opening force exceeded the Technical Specification (TS) Surveillance Requirement (SR) limit. Maintenance was performed on the damper and operability of the Unit 2 CEQ Fan #1 was restored at 1724 EDT. A past operability evaluation was performed and determined that the condition likely existed since maintenance was performed to lubricate the damper on February 24, 2017. As a result, the Unit 2 CEQ Fan #1 was inoperable longer than allowed by TS. During this time, the Unit 2 CEQ Fan #2 was declared inoperable to perform surveillance testing on March 2, 2017, from 0938 Eastern Standard Time (EST) until 1326 EST. This resulted in both trains being inoperable simultaneously for a short period of time. <br /><br /> The cause of the elevated force required to open the Unit 2 CEQ Fan #1 Backdraft Damper was determined to be that the lubrication Preventive Maintenance (PM) work order instructions were not adequate and did not provide adequate Post-Maintenance Testing (PMT) instruction. Corrective action is to revise model work order tasks to provide additional details and appropriate PMT. The risk significance of this condition has been determined to not constitute a significant increase in risk. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(v)(D).
3182017001 | Calvert Cliffs 2 | 02/20/2017 | 04/19/2017 | ML17111A97 | <strong>Pressurizer Safety Valve As-Found Settings Outside Technical Specification Limits due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During scheduled testing at the offsite testing facility, the as-found lift setting for the pressurizer safety valve previously installed in Unit 2 at the 2RV200 location was measured outside the Technical Specification allowable values (valve lifted low). The valve had been installed during the 2015 Unit 2 refueling outage and was removed during the 2017 Unit 2 refueling outage for scheduled testing and maintenance. As scheduled, a spare valve was installed during the 2017 refueling outage. The failed valve was disassembled and inspected at the offsite facility. The apparent cause of the pressurizer safety valve failure is due to setpoint drift. The valve was successfully re-certified for use at the plant in a future installation. Setpoint setting criteria were adjusted based on more recent operating experience (setpoint drifting low).
3212017001 | Hatch 1, Hatch 2 | 02/03/2017 | 04/03/2017 | ML17093A89 | <strong>Unanalyzed Conditions for a Postulated Fire Discovered During NFPA 805 Transition</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2017, in preparation for transitioning the Plant Hatch Fire Protection Licensing Basis from 10 CFR 50.48(b) (Appendix R) to 10 CFR 50.48(c) (NFPA 8051 a weak-link and operator manual action (OMA) analysis was completed for Information Notice (IN) 92-18 type hot shorts on motor operated valves (MOVs). Examination of the current Plant Hatch Appendix R Safe Shutdown Analysis identified circuit configurations in multiple Fire Areas where an Appendix R postulated fire could impact the ability to achieve safe shutdown conditions. The cable impacts can bypass the limit and torque switches and could result in physical damage to the valves, preventing the valves from being operated from the main control room, remote shutdown panel, or locally. Hourly fire watches had already been established for the affected fire areas and Fire Action Statements were initiated to address the postulated condition for the identified MOVs. <br /><br /> While these impairments represent unanalyzed conditions for Appendix R, the described scenarios are only possible given a fire has occurred in the associated Fire Areas. Plant Hatch issued a letter of intent to the NRC on October 4, 2013 to begin transition to NFPA 805 with a license amendment request (LAR) submittal date of April 4, 2018. Any identified noncompliances will be resolved during the transition process.
3212017002 | Hatch 1 | 02/08/2017 | 04/07/2017 | ML17097A33 | <strong>High Pressure Coolant Injection System Declared Inoperable due to Degraded Inverter</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2017, at 1151 EST with Unit 1 at approximately 100 percent rated thermal power, the High Pressure Coolant Injection (HPCI) suction and discharge pressure indicators were noted to be downscale during a main control room panel walk down. Upon further investigation, it was discovered that the output voltage of the DC to AC inverter was degraded. The HPCI DC to AC inverter supplies power to the HPCI flow controller and power supply. HPCI was therefore declared inoperable due to the degraded voltage condition. <br /><br /> The inoperable as found condition of the HPCI pressure indicators was due to degraded output voltage from the DC to AC HPCI inverter. The degraded inverter was removed and replaced and HPCI was returned to operable status. As part of an extent of condition review, the internals of the degraded inverter were inspected to determine what caused premature failure of the inverter. Based on the findings of this inspection, the preventative maintenance frequency for inverter replacement and calibration will be adjusted as necessary.
3212017003 | Hatch 1, Hatch 2 | 02/17/2017 | 04/13/2017 | ML17103A23 | <strong>Inoperable Secondary Containment due to Incorrect Penetration Flange Installation</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2017 at 1414 EST, with Unit 1 at 100 percent rated thermal power and Unit 2 at 0 percent rated thermal power due to a scheduled refueling outage, it was identified during an operations walkdown that a temporary blind flange was installed incorrectly, rendering secondary containment inoperable. In support of the Unit 2 Hardened Containment Vent System Wetwell Project, a temporary blind flange was to be installed downstream of the Standby Gas Treatment (SBGT) inlet isolation valve to prevent a breach of secondary containment. It was subsequently identified that upon removal of the SBGT isolation valve, the blind flange was installed on the wrong side of the piping. At 1503 EST on February 17, 2017, the blind flange was moved to the correct side of the piping and secondary containment was declared operable. <br /><br /> The cause of the event is due to having a lack of oversight, a lack of intrusiveness, and an inadequate challenge of the work instructions provided to the supplemental workers performing the work. Workers assumed that the work instructions meant for the blind flange to be installed downstream of primary containment rather than downstream of the SBGT inlet isolation valve. The work order planning procedure will be updated to require Southern Nuclear Operating Company (SNC) verification and signature for the installation of flanges and similar equipment.
3212017004 | Hatch 1, Hatch 2 | 03/30/2017 | 05/25/2017 | ML17145A39 | <strong>Tornado Missile Vulnerabilities Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2017 at approximately 0922 EST, with Unit 1 at 97 percent rated thermal power and Unit 2 at 100 percent rated thermal power, it was identified that based on the revised Enforcement Guidance Memorandum (EGM) 15-002, Revision 1, the Emergency Diesel Generator (EDG) fuel oil storage ventilation pipe extending approximately 5 feet above grade was reportable due to its nonconformance with tornado generated missile protection requirements. This condition caused the EDGs and their associated fuel oil storage system to be considered inoperable. However, due to implementing compensatory measures as required by EGM 15-002, the affected equipment was declared operable but non-conforming. <br /><br /> These tornado missile vulnerabilities have existed since original plant construction and is a design legacy issue. Upon identification of the noncompliance, compensatory measures were taken to revise the abnormal procedure for natural occurring phenomena to include actions that must be taken for the diesel generator fuel oil storage tank vent lines following a tornado or high winds event. A design change is also being processed to prevent the vent lines from being impacted due to a tornado missile.
3212017006 | Hatch 1 | 04/20/2017 | 06/19/2017 | ML17170A07 | <strong>Manual Scram Initiated ue to Inoperable Intermediate Range Monitors</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2017 at 2345 EST with Unit 1 in Mode 4 at 0 percent rated thermal power, the Unit 1 Reactor Mode Switch was taken from the REFUEL to the SHUTDOWN position per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.10 4 Required Action A.2.2, due to having no operable intermediate range monitors (IRMs) in one quadrant of the reactor vessel because of maintenance activities. All control rods had been previously inserted, therefore no control rod motion occurred when the mode switch was positioned to SHUTDOWN. <br /><br /> The cause of this event was due to flawed technical decision making surrounding maintenance activities related to inoperable IRMs. An inadequate review of TS LCO 3.10.4, in part due to the emergent nature of the maintenance activities to restore IRMs to operable status, resulted in Operations' incorrect determination that one of the requirements of TS LCO 3.10.4, "Single Control Rod Withdrawal - Cold Shutdown" was not met. The Unit 1 Reactor Mode Switch was therefore placed to the SHUTDOWN position per TS 3.10.4, Condition A.2.2. <br /><br /> Corrective actions included ensuring TS Bases 3.10.4 language is not ambiguous, issuing an order that requires the shift manager to approve the removal of TS equipment from service for maintenance, and inclusion of this event in licensed operator continuing training.
3232017001 | Diablo Canyon 2 | 07/29/2017 | 10/03/2017 | ML17276B86 | <strong>Relief Valve Leakage Resulting in Inoperable Pressurizer Power Operated Relief Valve</strong><br /><i>Abstract:&nbsp;</i>During an investigation of a nitrogen leak inside the Unit 2 containment, Nitrogen Accumulator Relief Valve (RV) RV-355 was found to be leaking. The leak caused the pressure in the back up nitrogen accumulator supply to Power Operated Relief Valve (PORV) PCV-455C to decrease to a level that made the PORV inoperable. Based on a review of the trend data for nitrogen usage in the containment, it is conservatively assumed that RV-355 had been degraded since December 1, 2016, rendering the PORV inoperable for longer than permitted by Technical Specifications. <br /><br /> The presumptive cause was inadequate instructions provided in plant procedures for placing a new nitrogen bottle in service. These instructions did not provide a sequence that assures system pressure transients are mitigated. This may have caused excessive pressure excursions resulting in multiple lifts of RV-355 which resulted in damage to the RV O-ring seat and a nitrogen leak path. <br /><br /> Corrective actions include replacing RV-355 and revising procedures to provide instructions on placing nitrogen supply bottles in service to maintain back pressure and minimize pressure transients on the nitrogen system. <br /><br /> This event did not affect the health and safety of the public.
3242017001 | Brunswick 2 | 03/22/2017 | 05/18/2017 | ML17142A16 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2017, Unit 2 implemented the guidance of EGM 11-003, Revision 3, "Enforcement Guidance Memorandum 11-003, Revision 3, Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements during Operations with a Potential for Draining the Reactor Vessel," dated January 15, 2016. Consistent with EGM 11-003, Revision 3, secondary containment operability was not maintained during Operations with a Potential for Draining the Reactor Vessel (OPDRV) activities, and Required Actions C.1 and C.2 of Technical Specifications (TS) 3.6.4.1, "Secondary Containment," were not completed. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by the plant's TS. <br /><br /> Implementation of EGM 11-003, Revision 3, during the Unit 2 refueling outage was a planned activity. As such, there was no causal evaluation of the event. Consistent with the guidance provided in EGM 11-003, Revision 3, BSEP will submit a license amendment request to adopt Technical Specification Task Force (TSTF)-542 associated with generic resolution to this issue within 12 months from its approval (i.e., from December 20, 2016).
3242017002 | Brunswick 2 | 04/13/2017 | 06/09/2017 | ML17163A36 | <strong>Plant Mode Change with Primary Containment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2017, Unit 2 was in Mode 4 preparing to exit a refueling outage. The primary containment was being vented to ensure habitability of the Drywell. The valve alignment for Drywell ventilation makes the primary containment inoperable due to the Drywell and Suppression Chamber airspaces being in communication with each other. At 23:47 Eastern Daylight Time (EDT), the reactor mode was changed from Mode 4 to Mode 2 with ventilation still in progress. In Mode 2, the Primary Containment is required to be operable. Therefore, the plant entered a condition prohibited by the Technical Specifications, and the event is reportable per 10 CFR 50.73(a)(2)(i)(B). It is also reportable per 10 CFR 50.73(a)(2)(v)(D) because the primary containment safety function was lost. The condition was discovered 28 minutes later on April 14, 2017, at 00:15 EDT and was corrected by closing the ventilation flowpaths at 00:30 EDT on April 14, 2017. This event resulted from Control Room personnel not initiating a tracking document while in Mode 4 with the primary containment inoperable. When preparing to change the plant mode from Mode 4 to Mode 2, the primary containment ventilation status was overlooked. Corrective actions for this event included closing the containment ventilation paths and remediating the Shift Manager and Control Room Supervisor.
3242017003 | Brunswick 2 | 06/05/2017 | 08/03/2017 | ML17215A99 | <strong>Setpoint Drift in Main Steam Line Safety/Relief Valves Results in Three Valves Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2017, BSEP received the results of testing of eleven main steam line safety relief valves (SRVs) removed from Unit 2 during the spring refueling outage. Three of the eleven valves were found to have as-found lift setpoints of their pilot valves outside the +/-3 percent tolerance required by Technical Specification (TS) 3.4.3. One SRV was 9.1 percent high. One SRV was 8.6 percent high, and one SRV was 5.0 percent high. Evaluation determined that the elevated lift pressures in two valves resulted from corrosion bonding of the SRV pilot valves which raised the breakaway force needed to open the pilot. The third valve experienced steam erosion. This event had no adverse impact on nuclear safety. Although the SRV setpoint limits required by the TS were exceeded, the plant condition was bounded by the Brunswick Unit 2 Cycle 22 Reload Safety Analysis, demonstrating that the SRVs could have performed their safety function of limiting reactor vessel overpressure. TS 3.4.3 requires ten of the eleven installed SRVs to be operable. Since less than ten SRVs were operable, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation prohibited by the plant’s TS. The SRV pilot valves were replaced with certified spares before the startup of Unit 2. A procedure was revised to reduce corrosion bonding by improving surface preparation of SRV pilot valve discs.
3252017001 | Brunswick 1, Brunswick 2 | 02/07/2016 | 03/22/2017 | ML17081A23 | <strong>Speed and Frequency Oscillations Result in Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2016, at 1312 Eastern Standard Time (EST), Unit 1 was in Mode 1 (i.e., Run) at 88 percent of rated power in end-of-cycle coastdown. At that time, an event occurred which resulted in a loss of offsite power (LOOP) on Unit 1. Emergency diesel generators EDG-1 and EDG-2 started and tied to their respective Unit 1 emergency buses. During diesel operation, EDG-1 exhibited oscillations in engine speed and bus frequency. These oscillations had no adverse effect on equipment supplied by the bus, and all supplied loads continued to perform their safety functions without interruption and without need for operator intervention. However, due to the speed and frequency oscillations, EDG-1 was deemed after the fact to have been inoperable. Following extensive testing and evaluation, the cause of the oscillations has not been determined. The governor system for EDG-1 was replaced on March 6, 2016, as part of a planned upgrade to EDG-1. Since that time, the oscillations have not recurred. Based on the fact that the governor replacement eliminated the oscillations, it's concluded that the oscillations resulted from a deficiency in the governor system. Since the cause of the inoperability has been eliminated, no further corrective actions are planned.
3252017002 | Brunswick 1, Brunswick 2 | 04/17/2017 | 06/12/2017 | ML17163A36 | <strong>Foreign Material in Switch Results in Unplanned Automatic Start of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2017, at 0004 Eastern Daylight Time, Unit 1 was in Mode 1 at approximately 100 percent of rated power, and Unit 2 was in Mode 1 at approximately 22 percent of rated power and was starting up from a refueling outage. Operators manually tripped the Unit 2 main turbine to halt increasing bearing vibration. The power circuit breakers (PCBs) for the Unit 2 main generator did not open as expected on the turbine trip, but subsequently opened when main generator reverse power relays actuated. This resulted in the automatic start of all four emergency diesel generators (EDGs). The EDGs did not tie to emergency busses because offsite power was still available. This event resulted from a component which failed due to foreign material intrusion. A limit switch associated with a main turbine stop valve failed to change states when the turbine was tripped. The limit switch configuration, together with other logic, satisfied the conditions to start the EDGs. The limit switch failure resulted from foreign material in the switch. The failed limit switch was replaced. Planned corrective actions include inspecting similar switches on both units, and sealing the wire entrances of the switch bodies to improve foreign material exclusion.
3252017003 | Brunswick 1, Brunswick 2 | 06/05/2017 | 08/02/2017 | ML17215A76 | <strong>Control Room Air Conditioning and Emergency Ventilation Systems Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2017, at 0930 Eastern Daylight Time (EDT), Unit 1 was in Mode 1 at 100 percent power, and Unit 2 was in Mode 1 at 87 percent power and was increasing power after a preplanned control rod improvement evolution. Maintenance personnel were inspecting dampers in the Control Room Air Conditioning (AC) system and Control Room Emergency Ventilation (CREV) system and disconnected an air supply to a damper. This resulted in the CREV system being inoperable due to interruption of the pneumatic supply. The CREV system was restored to operable status by 1009 EDT. At 1352 EDT, a second damper was inspected, and its pneumatic supply was disconnected. During the second occurrence, the Control Room AC system also tripped and was made inoperable. Affected systems were restored by 1407 EDT. The event is reportable as a loss of safety function per 10 CFR 50.73(a)(2)(v)(D). The event resulted from inadequate use of human performance tools and inadequate work instructions. Corrective actions for this event include restoring the affected pneumatic supply, revising work orders, and taking steps to emphasize proper use of human performance tools.
3252017004 | Brunswick 1, Brunswick 2 | 09/17/2017 | 11/15/2017 | ML17319A43 | <strong>Emergency Diesel Generator and Primary Containment Isolation System Actuations</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2017, at 0938 Eastern Daylight Time (EDT), a momentary power interruption to Emergency Bus E4 occurred during planned surveillance activities involving Emergency Diesel Generator (EDG) 4. This occurred when EDG 4 was disconnected from Emergency Bus E4 and offsite power was not supplying the bus. EDG 4 automatically transferred from manual mode to automatic control and reconnected to Emergency Bus E4. Normal frequency and voltage were restored with EDG 4 in automatic control. The momentary power interruption to Emergency Bus E4 resulted in various Unit 2 Primary Containment Isolation System (PCIS) actuations. The affected equipment responded as designed. <br /><br /> The direct cause of this event was that Operators were not aware that, at the time of the event, Emergency Bus E4 was being supplied solely by EDG 4. As a result of a failed under-frequency relay, the incoming line and feeder breakers from Balance of Plant (BOP) Bus 2C to Emergency Bus E4 had opened during the performance of the EDG 4 surveillance, leaving only EDG 4 to power Emergency Bus E4 in the manual mode of operation.
3272017001 | Sequoyah 1, Sequoyah 2 | 03/03/2017 | 04/26/2017 | ML17117A49 | <strong>Breached Door Renders Both Trains of the Auxiliary Building Gas Treatment System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2017, at 2232 eastern standard time (EST), Door A212 was improperly breached to facilitate a continuous fire watch. On March 7, 2017, at 0830 EST, a senior reactor operator discovered Door A212 blocked open during a walk down of the Auxiliary Building. The open door created a breach of the auxiliary building secondary containment enclosure (ABSCE) boundary. The identified breach exceeded the allowed ABSCE breach margin. As a result, both units entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12, Condition B for two trains of the Auxiliary Building Gas Treatment System (ABGTS) inoperable due to an inoperable ABSCE boundary in Mode 1, 2, 3, or 4. At 0949 EST, on March 7, the door was closed and both units exited LCO 3.7.12, Condition B. Both trains of ABGTS were inoperable longer than allowed by TS. There were no actual safety consequences as a result of this event. <br /><br /> An evaluation determined the cause to be a less than adequate single barrier breaching standard exists at Sequoyah Nuclear Plant. A contributing cause was an inconsistent approach to entry into the barrier breaching process. Corrective actions include revising the breaching procedure to address all possible breaches and include a matrix for doors and their associated impacts, and addressing potential knowledge deficiencies.
3272017002 | Sequoyah 1, Sequoyah 2 | 05/23/2017 | 07/14/2017 | ML17195A41 | <strong>Automatic Actuation of Emergency Diesel Generators Due to Loss of Power to 6.9kV Shutdown Board</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2017, at 2330 eastern daylight time (EDT), while transferring the 2A-A 6.9 kilovolt (kV) Shutdown Board (SDBD) from its alternate power source to its normal power source, in support of outage testing for Unit 2, a loss of power to the 2A-A 6.9kV SDBD resulted in the automatic actuation of all four emergency diesel generators. The power was restored to the SDBD on May 24, at 0027 EDT. <br /><br /> At the time of the event, Unit 1 was in Mode 1 at 100 percent power and Unit 2 was in Mode 5 for a refueling outage. There were no actual safety consequences as a result of this event. <br /><br /> The cause of the event was indeterminate. The direct cause of the event was an upstream unit board overcurrent relay actuation associated with the A phase. The corrective action was to obtain acceptable test results from all equipment in the zone of protection. This included all the cables, current transformers, relays and breakers that were in contact with the associated relay. There was no evidence of equipment degradation. Transient monitoring will be performed for 6.9kV SDBD normal and alternate feeder breakers. Data will be captured for each initial transfer. Any identified anomalies will be addressed via the corrective action program.
3312017001 | Duane Arnold | 01/26/2017 | 03/27/2017 | ML17089A38 | <strong>Condition Prohibited by Technical Specification - Containment Vent and Purge Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2017, at 1800 CST, while operating at 100% power, during planned surveillance testing, Drywell Vent Inboard Isolation Valve, CV4302 (System Code JM), was found to exceed its Leakage Integrity Test limits and was declared inoperable. The initial observed conditions indicated that CV4302 was the likely source of leakage and was the focus of repair efforts. After completion of repairs to CV4302, post maintenance testing showed that the Drywell Vent Line Outboard Isolation valve, CV4303, was exceeding its valve leakage limits, and therefore, was declared inoperable at 0300 CST on January 26, 2017. This resulted in a containment penetration flow path not within purge valve leakage limits and was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) (reference EN#52511). Repairs were completed on CV4303 and both primary containment valves were declared operable at 1007 CST on January 26, 2017. The cause of this event was determined to be inadequate work instructions and maintenance procedures. This event was of low safety significance and had no impact on public health or safety. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3332017001 | FitzPatrick | 01/14/2017 | 03/13/2017 | ML17072A04 | <strong>Vent Line Socket Weld Failure</strong><br /><i>Abstract:&nbsp;</i>Refueling Outage 22 commenced on January 14, 2017 at James A. FitzPatrick Nuclear Power Plant (JAF). With the plant in Mode 2 at 0613, the initial Drywell inspection identified a through wall leak on the 3/4 inch vent line off of the bonnet of the motor operated gate valve on the suction side of Reactor Water Recirculation Pump 'A'. This condition was determined to constitute Reactor Coolant Pressure Boundary (RCPB) leakage, which is prohibited by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.4. The average reactor coolant temperature decreased to less than 212 degrees F and the plant was in Mode 4 at 1530 of the same day, which is within the applicable TS LCO 3.4.4 required completion time. <br /><br /> The condition of a through wall leak on the RCPB is reportable pursuant to 10 CFR 50.73(a)(2)(ii), as a condition of the nuclear plant, including its principle safety barriers, being seriously degraded.
3332017003 | FitzPatrick | 04/04/2017 | 06/05/2017 | ML17156A29 | <strong>Inadvertent Isolation of the High Pressure Coolant Injection System</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2017 at 0735, with the James A. FitzPatrick Nuclear Power Plant operating in Mode 1 at 100 percent power the High Pressure Coolant Injection System (HPCI) was inadvertently isolated during the performance of l&C testing. Technicians were in the process of performing instrument surveillance tests for low pressure emergency core cooling systems when a trip signal was applied to the incorrect instrument. This caused a HPCI System isolation signal on High Area Temperature, resulting in the closure of the HPCI steam isolation valves. The surveillance testing was aborted and the HPCI system was restored. <br /><br /> HPCI is a single-train system; therefore, the inadvertent isolation is being reported as an event or condition that could have prevented fulfillment of the safety function of a system needed to mitigate the consequences of an accident per 10 CFR 50.73(a)(2)(v)(D).
3332017004 | FitzPatrick | 11/21/2017 | 03/30/2018 | ML18089A04 | <strong>Safety Relief Valves Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>The As-Found test results for the eleven Safety/Relief Valve (S/RV) pilot assemblies removed and replaced during the 2017 Refueling Outage at James A. FitzPatrick Nuclear Power Plant (JAF) identified ten (10) S/RV pilot assemblies that lifted outside of the allowable tolerance required by Technical Specification Surveillance Requirement 3.4.3.1. Nine (9) two-stage S/RV's were found out of tolerance high, and one three-stage was found out of tolerance low. The ten S/RV pilot assemblies are assumed to have been inoperable at some point in the operating cycle that preceded the 2017 Refueling Outage resulting in a condition reportable pursuant to 10 CFR 50.73(a)(2)(i)(B).<br /><br /> The S/RV design features an electric actuation capability that provides a diversified means of opening the S/RV's despite the out of tolerance condition. However, the electric lift function is considered a backup to the mechanical S/RV's and is not credited in the accident analysis. Therefore, the TS inoperability of the ten (10) S/RV's also resulted in a condition reportable pursuant to 10 CFR50.73(a)(2)(v)(D). <br /><br /> The cause of the two-stage failures has been identified as corrosion bonding; the cause of the three-stage failure is attributed to calibration and subsequent setpoint drift. The safety consequences associated with this event are considered low due to the electric actuation capability.
3342017001 | Beaver Valley 1, Beaver Valley 2 | 02/23/2017 | 04/18/2017 | ML17110A19 | <strong>Inadequate Tornado Missile Protection Identified due to Non-Conforming Design Conditions</strong><br /><i>Abstract:&nbsp;</i>In order to address the concerns outlined in NRC Regulatory Issue Summary (RIS) 2015-06 "TORNADO MISSILE PROTECTION", an evaluation of tornado missile vulnerabilities and their potential impact on Technical Specification (TS) plant equipment was conducted. This evaluation concluded that the following Structures, Systems, and Components (SSCs) are potentially vulnerable to tornado generated missiles:<br /> The steam discharge flow paths to atmosphere of the Beaver Valley Power Station Unit 1 (BV-1) and Unit 2 (BV-2) Main Steam Safety Valves (MSSVs) (reference TS 3.7.1) are potentially vulnerable to tornado generated missiles.<br /> The steam discharge flow paths to atmosphere of the BV-1 and BV-2 Atmospheric Dump Valves (ADVs) (reference TS 3.7.4) are potentially vulnerable to tornado generated missiles.<br /> On February 23, 2017, the BV-1 and BV-2 TS required MSSVs and ADVs were declared inoperable and Enforcement Guidance Memorandum (EGM) 15-002 Rev 1 "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," was applied. Compensatory measures were implemented within the time allowed by the applicable Limiting Condition(s) for Operation and the associated systems were then declared Operable but nonconforming. <br /> The apparent cause of this issue was a lack of clarity during the original design and licensing of the plants that led to inadequate understanding of the tornado missile protection regulatory requirements. <br /> In addition, as part of the evaluation of tornado missile vulnerabilities, two BV-2 tornado missile barrier doors were found to be open. Specifically, Auxiliary Building door (A-35-5A) was found open and Fuel Building door (F-66-3), was found to be partially open. These doors were then closed and latched.<br /> Actions will be taken to establish compliance for the MSSVs and ADVs either by plant modification or by employing a methodology for addressing tornado missile noncompliance for the MSSVs and the ADVs. <br /><br /> These conditions (as applicable) were reported to the NRC on February 23, 2017 in Event Notification (EN) number 52571 under 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(A).
3342017002 | Beaver Valley 1 | 07/19/2017 | 09/13/2017 | ML17261A19 | <strong>Beaver Valley Power Station Unit 1 Inadequate Emergency Diesel Generator (EDG) Tornado Missile Protection Identified due to Non-conforming Design Conditions</strong><br /><i>Abstract:&nbsp;</i>In order to address the concerns outlined in NRC Regulatory Issue Summary (RIS) 2015-06 "TORNADO MISSILE PROTECTION", evaluations of tornado missile vulnerabilities and their potential impact on Technical Specification (TS) plant equipment were conducted. This particular evaluation concluded that the following Structures, Systems, and Components (SSCs) are potentially vulnerable to tornado generated missiles: <br /><br /> The Beaver Valley Power Station Unit 1 (BV-1) Emergency Diesel Generators (EDGs) engine exhaust piping is potentially vulnerable as a result of tornado generated missiles striking and subsequently crimping or crushing this piping rendering the EDGs inoperable. <br /><br /> On July 19, 2017, both of the BV-1 TS required EDGs were declared inoperable and Enforcement Guidance Memorandum (EGM) 15-002 Rev 1 "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," was applied. Compensatory measures were implemented within the time allowed by the applicable Limiting Condition(s) for Operation and both EDGs were then declared operable but nonconforming. <br /><br /> The apparent cause of this issue was a lack of clarity during the original design and licensing of the plant that led to inadequate understanding of the tornado missile protection regulatory requirements.<br /><br /> Actions will be taken to establish compliance for BV-1 EDGs either by a plant modification or employing a methodology for addressing tornado missile nonconformances for the EDG exhaust piping. <br /><br /> This issue is reportable under 10 CFR 50.72 for a loss of safety function. However, enforcement discretion is being applied. As stated in EGM 15-002, Rev. 1, the NRC will exercise enforcement discretion for subsequent tornado missile 10 CFR 50.72 notifications. On February 23, 2017, FENOC provided the NRC the initial 10 CFR 50.72 notification in Event Notification (EN) number 52571 concerning tornado missile protection issues known at that time.
3342017003 | Beaver Valley 1 | 11/07/2017 | 01/04/2018 | ML18008A06 | <strong>Beaver Valley Power Station Unit 1 Reactor Trip due to Turbine Trip and Automatic Initiation of the Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2017 at 05:04 EST Beaver Valley Power Station (BVPS) Unit 1 experienced an automatic Reactor Trip from 100 percent power due to an automatic Turbine Trip. The Turbine Trip was initiated by a Main Unit Generator Overcurrent Protection Trip. The Reactor Trip was without complications. All control rods fully inserted into the core. The Auxiliary Feedwater System automatically actuated as expected and performed as designed. The plant was stabilized in Mode 3 with the normal Main Feedwater System in service and the Auxiliary Feedwater System properly secured. <br /><br /> The Main Unit Generator trip was caused by foreign material in the isophase bus duct. The isophase bus ducts have been properly inspected and cleared of all foreign material. <br /><br /> This event was reported (EN 53056) as an actuation of the Reactor Protection system 10 CFR 50.72(b)(2)(iv)(B) and a Specified System Actuation (Auxiliary Feedwater System) 10 CFR 50.72(b)(3)(iv)(A). <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the automatic actuation of the Reactor Protection System (RPS) and the expected automatic actuation of the Auxiliary Feedwater System.
3352017001 | St. Lucie 1 | 01/31/2017 | 05/02/2017 | ML17122A24 | <strong>Reactor Coolant Pressure Boundary Leak on the 1B2 Reactor Coolant Pump Lower Seal Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2017, while St. Lucie Unit 1 was shut down in Mode 3, technicians identified reactor coolant pressure boundary leakage within the 1B2 reactor coolant pump (RCP) lower seal heat exchanger. At 1200 hours, St. Lucie Unit 1 entered Technical Specification 3.4.6.2 Action a. and the plant was maneuvered to Mode 5 to affect repairs. <br /><br /> The most probable cause was determined to be a deficiency in the lower seal heat exchanger design which permitted stresses that approached or exceeded the yield strength of the assembly tubing during torqueing of the CCW flanges. The resultant plastic deformation and associated flaw formation caused low stress high cycle fatigue failure of the weld joint. <br /><br /> The flaw was removed and the weld repair was completed. St. Lucie Unit 1 was subsequently returned to service on February 7, 2017. <br /><br /> All remaining in-service and a spare RCP lower seal heat exchangers have since been inspected and no defects have been found. This event had no impact on the health and safety of the public.
3352017002 | St. Lucie 1 | 07/31/2017 | 09/28/2017 | ML17271A18 | <strong>Inadequate Hot Leg Injection Procedure Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On July 31, 2017, FPL determined that the proceduralized manual actions to mitigate postulated electrical single failures in the St. Lucie Unit 1 hot leg injection (HLI) flow path were inadequate. Manual actions previously developed based on failure modes and effect analysis (FMEA) failed to identify the need to override open permissive interlocks in the HLI flowpath. The procedures were revised to account for the oversight, and a detailed FMEA was performed and enhancement opportunities were identified to be evaluated under the site corrective action program. <br /><br /> The safety significance for the additional jumper scope was bounded by previous evaluations. Therefore, this event had no significant impact on the health and safety of the public.
3352017003 | St. Lucie 1 | 09/12/2017 | 11/13/2017 | ML17317A61 | <strong>Inadequate Reactor Protection System Trip Process for Inoperable Channel Results in Operation in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During a reactor startup performed on September 12, 2017, the operators noted that the inoperable ‘B’ channel reactor protection system (RPS) high startup rate (HSUR) trip did not occur as expected when reactor power exceeded the HSUR bypass removal setpoint. The ‘B’ RPS HSUR channel was then manually tripped via the bistable removal method and plant startup continued.<br /><br /> Investigation revealed that the setpoint reduction method process used to implement the RPS HSUR channel trip did not account for subsequent nuclear instrumentation (NI) detector failures. Therefore the ‘B’ RPS HSUR channel was not in the required tripped condition since the February 2017 failure of its wide range NI detector. <br /><br /> The setpoint reduction method was subsequently revised to ensure inoperable RPS HSUR channels tripped by the setpoint reduction method generate a trip with reactor power less than 15 percent reactor power. A procedure revision is in progress to implement these new rule-based instructions. <br /><br /> This event had no significant impact on the health and safety of the public based on system channel redundancy and procedural controls.
3412017001 | Fermi 2 | 01/06/2017 | 03/06/2017 | ML17065A22 | <strong>Loss of Reactor Protection System Scram Function During Main Steam Isolation Valve and Turbine Stop Valve Channel Functional Tests due to Use of a Test Box</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2017 an Operations Shift Engineer determined that use of the Reactor Protection System (RPS) test box described in station procedures would result in the loss of two RPS reactor scram functions. Technical Specification (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1-1 Function 5 for Main Steam Isolation Valves (MSIVs) and Table 3.3.1.1-1 Function 9 for Turbine Stop Valves (TSV) remain OPERABLE. Operations procedures were revised to incorporate the use of the test box in August of 2016. Between September 22 and 23, 2016 the MSIV and TSV procedures were each performed one time using the test box. The failure to recognize the impact of the procedure revisions is considered a human performance error by engineering and operations personnel. <br /><br /> The procedures were corrected in January 2017 to remove the use of the RPS test box. Subsequently, on January 7 and 9, 2017, respectively, the procedures for the TSVs and the MSIVs were performed successfully.
3412017002 | Fermi 2 | 01/19/2017 | 03/16/2017 | ML17076A43 | <strong>High Water Level Indications at Low Reactor Pressures Causes Some Functions of High Pressure Coolant Injection System and Reactor Core Isolation Cooling System to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2017, a condition was identified that impacted the operability of certain functions associated with the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems under low reactor pressure conditions. HPCI and RCIC both have automatic and manual actuation functions to inject water into the reactor vessel. HPCI and RCIC also both have an automatic function (i.e. Level 8 trip signal) to prevent injection to the reactor vessel so that water does not reach the steam lines. This Level 8 trip signal comes from instrumentation that is calibrated to be most accurate at normal operating conditions. Under low reactor pressure conditions (i.e. below 600 psig), the high drywell pressure automatic actuation of HPCI and the manual initiation of both HPCI and RCIC are prevented by a Level 8 trip signal such that the affected HPCI and RCIC functions should be considered inoperable per Technical Specifications (TS). This can cause HPCI to also be considered inoperable, which could prevent the fulfillment of a safety function since HPCI is a single train system. Fermi 2 was at a pressure above 600 psig at the time of discovery and, therefore, the condition did not exist. However, a review of past operating conditions identified twelve instances in the past three years where the condition did exist. Based on an engineering analysis, the affected HPCI and RCIC functions are not required to perform a safety function at low reactor pressures; therefore, there was no adverse impact to public health and safety or to plant employees. There were no radiological releases. The cause of the event was an inconsistency between the Fermi 2 TS and the original design and licensing basis of the HPCI and RCIC systems. For corrective actions, Fermi 2 has submitted a license amendment request to clarify the TS.
3412017003 | Fermi 2 | 05/22/2017 | 07/21/2017 | ML17202G75 | <strong>Division 2 Residual Heat Removal Service Water System (RHRSW) Inoperable due to an Inoperable RHRSW Flow Control Valve</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2017 at 05:10 am (EST), while placing Division 2 Residual Heat Removal Service Water (RHRSW) in service for biocide treatment of the Division 2 Residual Heat Removal (RHR) Reservoir, the Division 2 RHRSW Flow Control Valve (FCV) (E1150F068B) failed to fully open. Troubleshooting discovered the direct cause was failure of the anti-rotation bushing stem key. The apparent cause was system operating conditions (high vibration) resulting in the failed tack welds. Previous troubleshooting on an indication issue on May 5, 2017 for the RHRSW FCV was inadequate, and did not identify the failure of the anti-rotation key. As a result, the RHRSW FCV was returned to service at 2:50 pm on May 7, 2017, and subsequently failed on the next on-demand stroke at 5:10 am on May 22, 2017. Seventeen similar Motor Operated Valves (MOVs) were inspected and no MOVs exhibiting the symptoms observed on the E1150F068B prior to the failure of the anti-rotation key were found, and all anti-rotation devices were found to be intact. The Past Operability determination for E1150E068B found that the MOV was unable to perform its design basis functions from May 3, 2017 at 5:48 am, when the RHRSW FCV was last successfully stroked under dynamic conditions, through May 24, 2017 at 4:04 pm, when the RHRSW FCV was returned to service. The Division 1 RHRSW was available throughout the event except on two occasions. Division 1 of RHRSW was declared inoperable for Mechanical Draft Cooling Tower (MDCT) Nozzle Cleaning activities on May 9, 2017 from 8:41 am to May 9, 2017 at 11:18 pm. Division 1 of RHRSW was again declared inoperable for MDCT Nozzle Cleaning activities on May 11, 2017 at 8:35 am through May 11, 2017 at 10:01 pm. The as found condition of the Division 2 RHRSW FCV is a condition prohibited by Technical Specification 3.7.1 and reportable under 10 CFR 50.73 (a)(2)(i)(B) "Operation or Condition Prohibited by Technical Specifications," and 10 CFR 50.73(a)(2)(v)(B) "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: Remove Residual Heat."
3412017004 | Fermi 2 | 08/10/2017 | 10/09/2017 | ML17282A00 | <strong>Inadequate Procedural Guidance for Residual Heat Removal Complex Ventilation Systems Leads to Condition Prohibited by Technical Specifications and Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2017, it was determined that inadequate procedural guidance for determining operability for ventilation support systems was being utilized. The Residual Heat Removal (RHR) switchgear and pump rooms have ventilation systems to maintain operability of the equipment in the rooms. Fermi 2 procedures had directed personnel to declare the supported equipment in the rooms inoperable due to nonfunctionality of the ventilation systems only if the room temperature exceeded the operability limit. Following discovery, a review of the RHR switchgear and pump room ventilation systems for the past three years was performed. The review identified multiple instances where the ventilation systems were nonfunctional and should have resulted in entry into applicable Technical Specifications (TS). Many of these instances resulted in operations or conditions prohibited by TS, since TS Required Actions were not completed within the Completion Times for restoration of affected equipment and plant shutdown. In addition, one instance was identified where the plant configuration was such that it could have prevented the fulfillment of the safety function to remove residual heat following a design basis accident. An engineering evaluation of this specific instance was performed and verified that the plant remained within its analyzed design basis. All other instances maintained one fully operable division of heat removal equipment such that no loss of safety function existed. There were no radiological releases associated with this event. The safety significance was determined to be very low. The cause of the event was inadequate procedural guidance. Immediate actions were taken to provide interim guidance related to the procedure. Corrective actions to revise the affected procedure have been completed.
3412017005 | Fermi 2 | 09/09/2017 | 11/03/2017 | ML17310A16 | <strong>Non-Functional Mechanical Draft Cooling Tower Fan Brakes Leads to HPCI Being Declared Inoperable and Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>At 1000 EDT on September 9, 2017, the Division 2 Mechanical Draft Cooling Tower (MDCT) fans were declared inoperable due to loss of output from the over speed fan brake inverter. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) and the Emergency Equipment Cooling Water (EECW) system. The Division 2 EECW system cools the High Pressure Coolant Injection (HPCI) system room cooler. As a result, the non-functionality of the fan brakes lead to an unplanned HPCI inoperability. Since HPCI is a single train system designed to mitigate the consequences of a loss of coolant accident (LOCA), this event could have prevented the fulfillment of a safety function. The cause of the event was the failure of the Division 2 fan brake inverter.<br /><br /> Corrective Actions were taken to replace the inverter and returning the MDCT fans, the UHS, EECW and HPCI to service on September 9, 2017 at 2351 EDT. A failure modes evaluation was performed by the vendor with no direct cause of the failed output determined. The fan brake system is only required for a design basis tornado and there was no credible tornado threat during this event. The HPCI system is not required to mitigate a design basis tornado. The safety significance of this event is very low and there were no radiological releases associated with this event.
3462017001 | Davis-Besse | 07/20/2017 | 09/18/2017 | ML17268A13 | <strong>Emergency Diesel Generator Fuel Oil Storage Tank Vents Not Adequately Protected from Tornado-Generated Missiles</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2017, with the Davis-Besse Nuclear Power Station (DBNPS) operating at approximately 100 percent power, it was identified that the Emergency Diesel Generator (EDG) fuel oil storage tank vents were not adequately protected from potential tornado-generated missiles. If a missile crimped the vent it could disable the transfer pump or tank, potentially impacting the seven-day fuel supply for the affected train(s) of EDG. While the storage tanks were protected from tornado missiles when installed, the vents were not provided with any such protection. Compensatory measures were established to ensure a vent path remained following a tornado event, and actions will be taken to ensure the vents for each EDG fuel oil storage tank are adequately protected from tornado missiles. <br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety, in accordance with 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of the safety function, in accordance with 10 CFR 50.73(a)(2)(vii) as an event where a single cause or condition caused two independent trains to become inoperable in a single system, and in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3462017002 | Davis-Besse | 09/13/2017 | 06/29/2018 | ML18184A34 | <strong>Auxiliary Feed Water Pump Turbine Bearing Damaged due to Improperly Marked Lubricating Oil Sight Glass</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2017, with the Davis-Besse Nuclear Power Station operating at approximately 100 percent power, Auxiliary Feed Water (AFW) Pump Turbine 1 experienced high inboard bearing temperature during performance of quarterly Surveillance Testing. The turbine was tripped, and disassembly revealed damage to the journal bearing. The bearing was replaced, and following successful post maintenance testing, AFW Train 1 was declared Operable on September 16. The cause of the bearing damage was an improperly marked oil sight glass, which allowed operation with improper bearing lubrication. The improper markings were due to the maintenance work instruction for replacing the sight glass not including dimensions or guidance for setting required operational bands. <br /><br /> On September 26, 2017, it was identified that low inboard bearing oil level had likely existed since completion of the previous quarterly surveillance test on June 21, when an oil sample was taken following testing but the bearing was not refilled due to the improperly marked sight glass. This issue is being reported in accordance with 10 CFR 50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of the safety function, and in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3482017001 | Farley 1 | 10/01/2016 | 09/29/2017 | ML17272A66 | <strong>Entry Into Mode of Applicability with Component Cooling Water Isolation Valve Inoperable due to Configuration Error</strong><br /><i>Abstract:&nbsp;</i>On July 31, 2017 with Unit 1 at 100% Rated Thermal Power it was identified that Q1P17HV2229-Norm/Block Switch (Norm/Block Switch) was out of position (aligned to the "SI BLOCK" position). This is a key operated switch which controls the operation of valve Q1P17HV2229 (HV-2229), Component Cooling Water (CCW) Supply to Sample Coolers. HV-2229 functions to automatically isolate the non-seismic portion of the CCW system which includes the Reactor Coolant System (RCS) Sample Coolers. The Norm/Block switch allows a Safety Injection (SI) signal to be blocked to allow alignment of CCW to the RCS Sample Coolers for post-accident sampling. The Norm/Block Switch was returned to normal position on August 1, 2017 at 0415. <br /><br /> HV-2229 also receives a closed signal on low level CCW Surge Tank which will override the Norm/Block switch regardless of position. Thus, in the event of an SI concurrent with a CCW leak, the safety function of CCW would have still been met. Since HV-2229 was blocked from closing and would not have met Surveillance Requirement (SR) 3.7.7.2 from October 29, 2016 (entry to MODE 4) to August 1, 2017, the station unknowingly operated in a condition prohibited by Technical Specifications which is reportable under 50.73(a)(2)(i)(B). <br /><br /> Corrective actions include procedure changes, communications and training to close knowledge gaps associated with system operation.
3522017001 | Limerick 1, Limerick 2 | 11/29/2016 | 01/27/2017 | ML17027A10 | <strong>Condition Prohibited by TS due to Parts Quality Issue</strong><br /><i>Abstract:&nbsp;</i>Over a period of approximately one month, the 0B Main Control Room (MCR) Heating, Ventilating and Air Conditioning (HVAC) system experienced four failures. Troubleshooting was completed for each of the failures and for three of the failures the cause was determined to be an intermittent dropout or chattering of the Loss of Offsite Power (LOOP) start relay for two fans (0B-V116 MCR Supply and 0B-V121 MCR Return Fans). The fourth failure was due to a contactor in the Motor Control Center (MCC) for the 0B-V116 MCR Supply Fan. On 11/29/16 the second failure occurred on the LOOP start relay for the 0B-V116 MCR Supply fan. The investigation identified a manufacturing defect of the Agastat/Tyco ETR Relays in the lot of relays used for the recent preventative maintenance (PM) relay replacements. The relays were determined to be unreliable since the initial PM replacement on 10/19/16 until 12/5/16, when the quality issue was identified and relays from a different lot were installed. The B train of MCR HVAC was determined to be inoperable due to the relay issue for a period of 47 days, which is greater than the allowable Limiting Condition for Operation (LCO) action window of 7 days (per TS 3.7.2.a.1) for an inoperable Control Room Emergency Fresh Air System (CREFAS) train. Therefore, this was a condition prohibited by Technical Specifications (TS).
3522017003 | Limerick 1 | 03/22/2017 | 05/22/2017 | ML17142A14 | <strong>Condition Prohibited by TS due to Inoperable RPIS</strong><br /><i>Abstract:&nbsp;</i>A power supply in the Rod Position Indication System (RPIS) failed causing a Main Control Room (MCR) alarm and loss of several control rod position indications. Using the Four Rod Display, the control room operators determined the affected control rods and found approximately half of the control rods had no indication. Although the Four Rod Display did not show control rod position for these rods, the staff concluded that the Full Core Display indication satisfied control rod position indication requirements for a majority of the control rods that were either full-in or full-out. It was later determined that the Full Core Display indicates the last known position in memory which is not replaced until new data is received. In this case, no data would have been received for the control rods due to the power supply failure. The failure to identify loss of control rod position indication for the control rods caused a failure to meet the plant's Technical Specifications (TS) and is reportable under 10 CFR 50.73(a)(2)(i)(B). This condition existed for approximately 19.5 hours prior to the power supply replacement, which was greater than the TS required actions to determine rod position within 1 hour or be in hot shutdown within the following 12 hours.
3522017004 | Limerick 1 | 10/05/2017 | 03/13/2018 | ML18072A02 | <strong>Core Spray Failed to Start Resulting in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2017, when the 1C Core Spray pump breaker hand switch was placed in start, the breaker failed to close. The 1C Core Spray Pump was declared inoperable and Limiting Condition for Operation (LCO) Action 3.5.1.a.1 was entered. An initial investigation identified that the breaker limit switch which energizes the closing springs charging motor became dislodged inside the control device. With the contact unable to complete the circuit, the charging motor could not energize to charge the closing springs. An Exelon Power Labs analysis identified the cause of the failure to be associated with welding of the limit switch contacts eventually resulting in displacement of the limit switch. This condition existed since the last time the 1C Core Spray Pump was in service, July 17, 2017, until the discovery on October 5, 2017. Although this event was not considered to be within the Station's ability to foresee and correct, the LCO Actions were not completed in the required time frames provided in Technical Specification (TS). Therefore, an Operation or Condition Prohibited by TS existed and is reportable under 10 CFR 50.73(a)(2)(i)(B).
3532017004 | Limerick 2 | 05/08/2017 | 08/09/2018 | ML18221A25 | <strong>Degraded Condition due to RPV Instrument Nozzle Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2017, while Unit 2 was shut down for refueling outage 2R14, leakage was identified from a 2-inch Reactor Pressure Vessel (RPV) instrumentation nozzle (N-16D) during a RPV pressure test. The leakage amount was approximately one pint per minute. The leakage originated from the area where the nozzle penetrates the vessel wall. Prior to de-pressurizing, an extent of condition bare metal examination was conducted. No leakage was identified from any other instrument nozzles. A half nozzle repair was completed, consisting of replacing the outer portion of the existing nozzle with a new nozzle that was welded to the outside of the RPV. The safety significance of this event was minimal given the leakage was small, was found while the reactor was shut down, and would not have exceeded Technical Specification (TS) leakage limits for unidentified drywell leakage if it occurred during plant operation. Given the impact on the RPV boundary, this report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(ii)(A), which requires the reporting of any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
3532017006 | Limerick 2 | 07/27/2017 | 09/25/2017 | ML17268A27 | <strong>HPCI Inoperability During Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2017, during Post Maintenance Testing (PMT) following a relay replacement activity, the Unit 2 High Pressure Coolant Injection (HPCI) system was inoperable when an undesirable valve alignment was established as per the PMT instructions resulting in a loss of suction path for the HPCI pump. Work was stopped and Operations and Instrument & Controls (I&C) supervision were notified. HPCI was inoperable for approximately 20 minutes until Operations restored a HPCI suction path to the Unit 2 Suppression Pool. This event is significant because it resulted in an unplanned inoperability of a single train safety system. An eight (8) hour ENS notification to the NRC was completed on July 27, 2017 at 1854 hours.
3532017007 | Limerick 2 | 05/26/2017 | 11/28/2017 | ML17332A07 | <strong>Reactor Mode Switch Change During RCIC Testing</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2017, during the Limerick Unit 2 reactor startup from a refueling outage, the reactor mode switch was placed in the RUN position (OPCON 1) with Reactor Core Isolation Cooling (RCIC) inoperable for required surveillance testing due to the Control Room Supervisor (CRS) failing to maintain adequate control of plant evolutions prior to placing the Mode switch to RUN. The station initially determined this operation was permitted based on TS 3.0.4.c. On September 29, 2017, it was subsequently determined TS 3.0.4.c was inappropriately used for this evolution. Therefore, changing the Reactor Mode Switch from Startup to Run while RCIC was inoperable for testing was a TS violation and therefore reportable as an Operation or Condition Prohibited by TS under 10 CFR 50.73(a)(2)(i)(B). Operations will revise the 'Normal Plant Startup' procedure to incorporate lessons learned from this event. Additionally, a Shift Training Notification will be developed and distributed to ensure gaps and lessons learned are shared with the Operations organization.
3532017008 | Limerick 2 | 10/11/2017 | 02/22/2018 | ML18053A01 | <strong>EDG Inoperable for Greater than 30 Days Resulting in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2017, during the performance of the D22 Emergency Diesel Generator (EDG) monthly slow start test, a previously identified lube oil leak was identified to have increased to 0.5 cups per minute. The D22 EDG was declared inoperable due to the increased leak rate. A past operability review determined that the identified lube oil leak would have prevented the D22 EDG from operating for its design basis mission time from the time when the leak was first identified (September 7, 2017) to the time when the leak was repaired and the EDG declared available (October 15, 2017). The apparent cause was identified to be age related cyclic fatigue induced by engine vibration.<br /><br /> The D22 EDG was determined to be inoperable for a period of greater than 30 days and the Limiting Condition for Operation (LCO) 3.8.1.1.a actions were not completed in the required time frames provided in Technical Specifications (TS). Therefore, an Operation or Condition Prohibited by TS occurred, which is reportable under 10 CFR 50.73(a)(2)(i)(B).
3542017001 | Hope Creek | 05/08/2017 | 07/07/2017 | ML17188A31 | <strong>Secondary Containment Door Not Latched in Closed Position</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2017, a Hope Creek secondary containment door was observed to be unlatched in the closed position. The door was being held closed by the negative pressure within the reactor building (secondary containment). The door was determined to have been opened for equipment passage on, May 8, 2017, at 1323. It was concluded that the door was most likely unlatched for passage at that time and not re-latched following the passage. A review of Hope Creek design basis accident (DBA) conditions determined that the secondary containment pressure would become slightly positive for a short period of time, under certain DBA events. Based on the area of the door, and the expected pressure rise within secondary containment, the door could not be assured to remain closed. Hope Creek Technical Specifications require that secondary containment integrity be maintained while in Operational Condition 1. Secondary Containment Integrity is defined as having all doors in the closed position except for normal passage. Since the closed door position could not be assured under all postulated accident conditions, the event is being reported under 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications, and under 10 CFR 50.73 (a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material.
3642017001 | Farley 2 | 06/23/2017 | 08/21/2017 | ML17233A35 | <strong>2B Emergency Diesel Generator Rendered Inoperable due to a Jacket Water Leak Without Makeup Capability</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2017, during continued troubleshooting of a jacket water (JW) leak on the 2B Emergency Diesel Generator (EDG), it was determined that the backup service water (SW) makeup flow path to the JW expansion tank would not pass flow. This troubleshooting was conducted to validate operability assumptions made on April 21, 2017, after recurrence of a leak from the JW keep warm pump. <br /><br /> Based upon the measured leak rate from the April 21st event, the 2B EDG would have been unable to meet its 7 day mission time without the use of makeup water to the JW expansion tank. Had the 2B EDG received a demand signal after March 3rd, the EDG may not have been able to perform its safety function during a design basis accident due to the JW leak rate and inability to makeup to the JW expansion tank. <br /><br /> Since the 2B EDG may not have met its mission time from March 3, 2017 to April 21, 2017, the station unknowingly operated in a condition prohibited by Technical Specifications which is reportable under 50.73(a)(2)(i)(B).
3642017002 | Farley 2 | 11/01/2017 | 12/19/2017 | ML17353A93 | <strong>Main Steam Safety Valve Lift Pressure Outside of Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2017, while in Mode 6 and at 0% power level, one of the C Loop Main Steam Safety Valves (MSSV) as-found lift pressure did not meet the acceptance criteria of +/- 3% of the setpoint (1129 psig) as required by Technical Specifications (TS) Surveillance Requirement (SR) 3.7.1.1. The MSSV lifted at 1171 psig which is 9 psig outside of its acceptance range of 1096 to 1162 psig and 3.72% above its setpoint. The apparent cause of exceeding the MSSV upper acceptance limit is degradation of the valve spring and/or valve spindle compression screw. The as-found settings remained within analytical bounds; therefore, operation of the facility in this condition had no impact on the health and safety of the public. <br /><br /> TS Limiting Condition for Operation (LCO) 3.7.1, MSSVs, requires five MSSVs per steam generator to be operable in Modes 1, 2, and 3. Since the failure affected the lift pressure over a period of time, it is assumed that the C Loop MSSV was inoperable for a time greater than allowed by TS. Therefore, this occurrence is considered reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. <br /><br /> The C Loop MSSV was replaced on November 5, 2017, while in Mode 5.
3642017003 | Farley 2 | 10/31/2017 | 12/20/2017 | ML17354A39 | <strong>Pressurizer Safety Valve Lift Pressure Outside of Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2017, while in Mode 6 at 0% power level, it was discovered that a Unit 2 pressurizer safety valve (PSV), which had been removed during the October 2017 refueling outage (2R25) and shipped offsite for testing, failed its as-found lift pressure test. The PSV lifted below the Technical Specification (TS) 3.4.10 allowable lift setting value. Setpoint drift of the PSV is the most likely cause of the failure. <br /><br /> It is likely that the PSV was outside of the TS limits longer than allowed by the Required Action Statement (15 minutes) during the previous operating cycle in all applicable modes of operation. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. <br /><br /> The PSV was replaced during the October 2017 refueling outage.
3642017004 | Farley 2 | 10/31/2017 | 12/22/2017 | ML17362A03 | <strong>Turbine-Driven Auxiliary Feedwater Pump Steam Admission Valve Air Leak Resulted in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2017, while in Mode 6 and at 0% power level, the Turbine-Driven Auxiliary Feedwater (TDAFW) pump B-Train steam admission valve from the 2C Steam Generator failed to meet Technical Specification (TS) Surveillance Requirement (SR) 3.7.5.5. This SR requires that the valve's associated air accumulator provide sufficient air to ensure operation of the TDAFW pump during a loss of power or other failure of the normal air supply.<br /><br /> During the performance of a flow scan analysis it was identified that the air-operated actuator piston was leaking by the actuator o-ring. Although the steam admission valve would stroke open, the 2-hour acceptance criteria could not be met. It is likely that the steam admission valve was inoperable longer than allowed by the Required Action Statement (7 days) following the spring 2016 refueling outage when it passed its last associated surveillance. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.<br /><br /> Corrective actions included actuator repair during the outage and further evaluating the preventive maintenance frequency.
3642017005 | Farley 2 | 11/13/2017 | 01/11/2018 | ML18011A70 | <strong>Power Range Nuclear Instrument Inoperable due to Poor Connection of High Voltage Cable Connector</strong><br /><i>Abstract:&nbsp;</i>During a reactor startup on November 13, 2017 at 0136, while at approximately 1.5% power (MODE 2), an Excore Power Range Nuclear Instrument (N-42) was declared inoperable due to lower than expected detector amps and indicated power. N-42 was reading approximately 0.4% lower power than the other three Power Range instruments. The malfunction was determined to be the result of a failed High Voltage (HV) cable center pin connector to N-42. The HV cable connector was installed during N-42 rescaling on November 10, 2017 in preparation for startup physics testing. N-42 provides an input signal to Channel 2 of the Over Temperature Delta Temperature (OTDT) Reactor Trip Signal. Prior to the discovery of the N-42 failure, Channel 3 of OTDT had also been declared inoperable and associated bistables tripped due to a failed Pressurizer Pressure transmitter. Therefore, it was determined that two channels of OTDT were inoperable longer than allowed by Technical Specification (TS) 3.0.3. This condition is reportable per 10CFR50.73(a)(2)(i)(B). <br /><br /> The HV cable connector was repaired and all channels were OPERABLE on November 14, 2017 at 1000. The installation of the HV cable connector with the faulty center pin was attributed to human error. Corrective actions include procedure changes, training, and departmental communications related to maintenance fundamentals.
3662017001 | Hatch 2 | 02/10/2017 | 04/03/2017 | ML17093A88 | <strong>Performance of Operations with the Potential to Drain the Reactor Vessel (OPDRV) Without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On February 10 through February 13, 2017, planned operations with the potential to drain the reactor vessel (OPDRV) activities were performed while Unit 2 remained in Refueling Mode (Mode 5) without an operable secondary containment. These activities are prohibited by Technical Specifications (TS) 3.6.4.1. However, recent NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 and in Regulatory Issue Summary (RIS) 2012-11 allowed the implementation of interim actions as an alternative to full compliance. These actions are contained in the operating procedure for the OPDRV activities performed during the 2017 Hatch Unit 2 Refueling Outage in February.<br /><br /> The performance of OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request (LAR) will be submitted for the associated NRC-approved Technical Specifications Task Force (TSTF) Traveler 542, "Reactor Pressure Vessel Water Inventory Control."
3662017002 | Hatch 2 | 02/16/2017 | 04/13/2017 | ML17103A41 | <strong>Emergency Diesel Generator Start due to Inadvertent Electrical Bus De-Energization</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2017, at 1320 EST with Unit 2 at 0 percent rated thermal power due to being in a refueling outage, maintenance electricians were sent to the field to perform a protective relay trip test for the 2D start-up transformer (SAT). During the test setup, the 2E 4160 VAC Emergency Bus was inadvertently and momentarily de-energized, causing the 2A Emergency Diesel Generator (EDG) to autostart, secondary containment to isolate, and start of the standby gas treatment system. Subsequent investigations revealed that the cause of the event was due to a movement operated contact (MOC) switch adapter was not required to be installed on the 2D normal supply breaker in the 2E 4160 VAC bus. All systems responded appropriately. <br /><br /> A review of the event determined that the MOC switch adapter was not required to be installed by the procedure, but was instructed to be installed by supervision. Corrective actions were taken to cover supervisor roles and responsibilities and the need for all workers to follow plant standards for procedure use and adherence. All breaker procedures and protective relay test procedures were reviewed to determine if a MOC switch adapter needs to be installed. Continuing training will also be held to cover this event and its lessons learned.
3662017003 | Hatch 2 | 02/19/2017 | 04/13/2017 | ML17104A29 | <strong>Primary Containment Isolation Penetration Exceeded Overall Allowable Technical Specification Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2017 at 2323 EST, with Unit 2 at 0 percent rated thermal power due to a refueling outage, the Unit 2 outboard drywell ventilation penetration isolation valve 2T48F320 (EIIS Code: ISV) failed local leak rate testing (LLRT). Previously on February 7, 2017 at 1427 EST, the inboard drywell ventilation penetration isolation valve 2T48F319 had also failed LLRT. Therefore, due to both primary containment isolation valves (PCIVs) in this penetration flow path exceeding the maximum allowable leakage rate (La), this event represents a failure of the associated penetration (2T23X26) to maintain primary containment integrity per Technical Specifications (TS). <br /><br /> Actions were taken to repair both of the PCIVs and on February 21, 2017, the valves were successfully retested. During the next scheduled Unit 2 refueling outage, the 2T48F320 isolation valve will be completely rebuilt. Also a corrective maintenance rebuild procedure will be developed for Fisher Series 9200 butterfly valves.
3662017004 | Hatch 2 | 06/30/2017 | 08/24/2017 | ML17236A29 | <strong>Safety Relief Valves' As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2017, Unit 2 was at 100 percent rated thermal power (RTP) when "as-found" testing results of the 3-stage main steam safety relief valves (SRVs) indicated two of the eleven Unit 2 SRVs experienced a setpoint drift during the previous operating cycle which resulted in their failure to meet the Technical Specification (TS) opening setpoint pressure of 1150 +/- 34.5 psig as required by TS Surveillance Requirement (SR) 3.4.3.1. The test results showed that two SRVs were slightly out of specification low due to setpoint drift.<br /><br /> The SRV pilots were disassembled and inspected while investigating the reason for the drift. SNC has determined that the abutment gap closed pre-maturely. The pre-mature abutment gap closure is most likely due to loose manufacturing tolerances leading to SRV setpoint drift.
3682017001 | Arkansas 2 | 04/06/2017 | 05/30/2017 | ML17150A48 | <strong>Inadequate Protection from Tornado Missiles Identified due to Nonconforming Design Conditions</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2017, as part of the closure of an Arkansas Nuclear One, Units 1 and 2 (ANO-1 & 2) Tornado Protection Study, a nonconforming condition in the plant design for a conduit that contains safety related cables for the ANO-2 #1 Emergency Diesel Generator (EDG) meter and relay cabinets, was identified. The conduit did not meet current design basis for protection against a potential tornado missile impact. This vulnerability is similar to those previously reported in LERs associated with ANO-1. <br /><br /> On April 6, 2017, Operations declared the #1 EDG inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, “Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,” along with necessary compensatory measures, and subsequently declared the affected equipment operable but nonconforming. Interim corrections include implementation of compensatory strategies. Plant modifications and license basis changes are being evaluated to resolve outstanding issues.<br /><br /> The cause of this issue was unclear and changing regulatory requirements during original plant licensing that led to an inadequate understanding of the regulatory guidance with respect to tornado missile protection design requirements.
3682017002 | Arkansas 2, Arkansas 1 | 04/26/2017 | 06/26/2017 | ML17177A34 | <strong>Automatic Start of an Emergency Diesel Generator due to the Momentary Loss of Offsite Power due to Severe Weather</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2017, ANO-2 was in day 28 of a refueling outage with the core completely off loaded to the spent fuel pool (SFP). Power to ANO-2 plant equipment was supplied from Start Up Transformer 2 (SU2) while SU3 was out of service for planned maintenance. 500kV and 161kV offsite power lines were in service. The area around the plant was experiencing severe weather from thunderstorms and tornado warnings had been issued from the National Weather Service for the four county area. Switchyard work was ceased.<br /><br /> At approximately 1002 CST switchyard breakers for 500kV lines opened on fault current. High winds had damaged the transmission towers approximately 16 miles away from ANO and caused phase to ground faults. This resulted in a loss of all offsite power lines to the 500 kV bus. The autotransformer also locked out, as designed, when the 500 kV transmission lines faulted. <br /><br /> When the 500kV bus tripped, the 4.16kV bus that feeds a vital 480 volt bus was subjected to a voltage transient; subsequently; the #1 emergency diesel generator (EDG) auto started. The EDG output breaker never closed due to the fact that voltage was restored to normal almost immediately. This EDG was secured due to running unloaded. Both SFP cooling pumps were out of service after the transient. A SFP cooling pump was restarted at 1020 CST. The temperature of the SFP did not change during this event.
3702017001 | McGuire 2 | 02/23/2017 | 06/26/2017 | ML17184A14 | <strong>Technical Specification Required Shutdown due to Reactor Coolant System Leakage</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2017, at 19:22 hours, with Unit 1 and Unit 2 operating at approximately 100 percent power, operators commenced a Unit 2 shutdown upon discovery of pressure boundary leakage on Unit 2 Safety Injection (NI) pipe upstream of the connection to "D" Reactor Coolant System (NC) Cold Leg. During a containment walk down inspection in Mode 3 on the next day, a pinhole pressure boundary leak was observed in the body of 2NC-30, Pressurizer Spray Bypass Valve. <br /><br /> The cause of the NI pipe leak is thermal fatigue damage caused by NC cross-loop flows. The cause of the 2NC-30 valve leak is a casting flaw attributed to a combination of defects during the manufacturing process that resulted in a through wall pinhole leak in the valve body. The NI pipe with the flaw and the valve with the pinhole leak could have structurally performed their design functions. Therefore, the health and safety of the public were not affected by these events.<br /><br /> Valve 2NC-30, the NI pipe, and leaking B-Loop NI check valves were replaced. Thermal cycling monitoring and mitigation devices were installed on Unit 2 and will be installed on Unit 1 during the next refueling outage.
3732017001 | LaSalle 1 | 12/16/2016 | 02/08/2017 | ML17039A74 | <strong>Reactor Core Isolation Cooling System Inoperable Longer than Allowed by the Technical Specifications due to Low Suction Pressure Trips</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2016, the Unit 1 Reactor Core Isolation Cooling (RCIC) system tripped on low suction pressure during a normal system start following completion of scheduled maintenance activities. The system was restored to operable on October 20, 2016. A second event involving a Unit 1 RCIC system trip on low pressure suction pressure occurred on November 17, 2016, during the system's quarterly operability surveillance. The system was restored to operable on November 20, 2016. The component failure analysis completed on December 16, 2016, determined the cause of both Unit 1 RCIC system trips was a failure of the electronic governor-remote (EG-R) hydraulic actuator. <br /><br /> The Unit 1 RCIC inoperable period was from the first system trip on October 18, 2016, to when full restoration was completed on November 20, 2016. This time was greater than allowed by Technical Specifications (TS) 3.5.3, "RCIC System," Condition A Completion Time of 14 days. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. The root cause for the low suction pressure trips was inadequate management of the EG-R preventative maintenance (PM) strategy. Corrective actions included replacement of the EG-R and a plan to implement an appropriate PM strategy for the RCIC EG-R. The safety consequences were minimal since the RCIC system is not credited in the safety analysis, and the credited High Pressure Core Spray (HPCS) system remained available to provide its safety function.
3732017002 | LaSalle 1, LaSalle 2 | 01/18/2017 | 03/17/2017 | ML17076A18 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2017, LaSalle County Station, Unit 1 was in Mode 1 at 100 percent power, and Unit 2 was in Mode 1 at 100 percent power with movement of irradiated fuel (MIF) in progress. At 2056 hours CST, both air-lock doors of the Unit 2 reactor building 710-foot elevation three-way air-lock opened simultaneously for approximately five seconds during personnel ingress. Both doors were immediately secured in the interlock, and MIF activities were immediately suspended. While both interlock doors were open, Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.2 to verify one secondary containment access door in each access opening is closed was not met. Secondary containment was declared inoperable for the period of time that both interlock doors were open. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to OPERABLE status within four hours was entered and exited. TS 3.6.4.1 RA C.1 to immediately suspend MIF in secondary containment was entered and exited.<br /><br /> The most probable cause of the interlock failure was the intermittent failure of the relays on the door controller circuit card based on previous history with these circuit boards. Previous events and prior causal investigations have indicated degradations in the relays for these circuit cards, and the corrective actions to replace interlock door circuit cards was ongoing at the time this event occurred. The controller circuit card was replaced, which restored the interlock functionality on January 19, 2017.
3732017003 | LaSalle 1 | 02/13/2017 | 04/14/2017 | ML17104A08 | <strong>Automatic Reactor Scram due to Main Generator Trip on Differential Current During Back-Feed Operations</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2017, LaSalle County Station Unit 1 was in Mode 1 at 100 percent power and Unit 2 shut down for a planned refueling outage. At 2309 CST, a reactor scram signal was received on Unit 1 due to turbine control valves fast closure while the station was aligning back-feed operation to the Unit 2 main power transformer (MPT). The Unit 1 turbine trip was due to the main generator trip on differential current. The plant was placed in a stable condition with reactor pressure maintained by the turbine bypass valves and reactor water level controlled using feedwater. Unit 2 was unaffected by the event. <br /><br /> The root cause of the Unit 1 trip on differential current was a marginal generator differential relay design that was prone to responding to faults outside its zone of protection. Both units' 345 kV ring buses were connected together through the cross-tie bus, which allowed the Unit 1 generator to supply some of the electrical current that resulted in its differential circuit to create an unbalanced current that actuated the differential relay. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram. There were no safety consequences associated with the event since RPS and other emergency safety systems functioned as designed.
3732017004 | LaSalle 1, LaSalle 2 | 02/16/2017 | 04/17/2017 | ML17107A08 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2017, Unit 1 was in Mode 2 for startup at five percent power, and Unit 2 was defueled for a planned refueling outage with movement of irradiated fuel (MIF) in progress. At 0835 CST, both air-lock doors of the Unit 1 reactor building to the chemistry corridor were opened simultaneously for approximately five seconds during personnel ingress. The employee immediately secured both doors in the interlock and notified the Main Control Room. While both interlock doors were open, Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.2 to verify one secondary containment access door in each access opening is closed was not met. Secondary containment was declared inoperable for the period of time that both interlock doors were open. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to operable status within four hours was entered and exited. TS 3.6.4.1 RA C.1 to immediately suspend MIF in secondary containment was entered and exited. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. The most probable cause of the interlock failure was the intermittent failure of a circuit board which is designed to prevent more than one door to be open at a time. Previous events and prior causal investigations have indicated degradations in the relays for these circuit cards, and the corrective actions to replace interlock door circuit cards was ongoing at the time this event occurred. The door interlock was satisfactorily tested by maintenance technicians, and the door interlock was returned to service on February 18, 2017.
3732017005 | LaSalle 1 | 02/17/2017 | 04/18/2017 | ML17108A43 | <strong>Manual Reactor Scram Resulting from Feedwater Regulating Valve Failure Causing High Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2017, at 2353 CST, during Unit 1 power ascension from a previous forced shutdown, operators inserted a manual scram as a result of a high reactor water level condition caused by a rapid change in feedwater flow. The high reactor water level trip occurred due to a failure of the feedwater regulating valve (FRV) 1FW005 positioner arm, which caused the regulating valve to be driven to the full open position. This resulted in a rapid increase of reactor water level that required operators to perform a manual reactor scram. The plant was placed in a stable condition, with no complications in achieving shutdown. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS). The safety significance of this condition was minimal, as plant equipment responded as expected for the event. The feedback drive arm and new positioner were installed on the Unit 1 FRV, which allowed the unit to restart following repairs. The FRV positioner feedback assembly had been installed in 2002, during a modification to upgrade of the air-operated valve assembly. This design has proven not to be robust enough for the FRV application.
3732017006 | LaSalle 1 | 05/17/2017 | 07/17/2017 | ML17195A35 | <strong>Low Pressure Core Spray Inoperable due to Minimum Flow Valve Failure in Closed Position</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2017 at 0908 CDT, during Unit 1 full-power operations, operators received an unexpected alarm for the Low Pressure Core Spray (LPCS) pump injection high flow and automatic closure of the LPCS minimum flow valve (1E21-F011). Inspections indicated the flow switch that actively controls the LPCS minimum flow valve had a faulty diaphragm which allowed for water intrusion into the device. There were no impacts on plant operations. The required actions of Technical Specifications 3.5.1, "ECCS - Operating" and TS 3.3.5.1, "Emergency Core Cooling System (ECCS) Instrumentation" were entered. The switch was replaced and LPCS system tested, which allowed full restoration of the system on May 17, 2017 at 18:45 CDT. <br /><br /> This condition could have prevented the LPCS system from performing its design function. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. There was minimal safety consequences associated with the condition since other emergency safety systems remained operable.
3732017007 | LaSalle 1 | 06/22/2017 | 08/18/2017 | ML17230A28 | <strong>Low Pressure Core Spray System Inoperable due to Loss of Cooling</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2017, the Unit 1 Low Pressure Core Spray (LPCS) system was declared inoperable due to loss of corner room area cooling and loss of motor cooling. The common diesel generator cooling water pump received an automatic trip signal while being secured. The LPCS pump remained in standby during the event. Troubleshooting identified the most likely cause for the trip of the emergency cooling water pump breaker was a malfunction of the cooling water pump control switch or the cooling water supply fan control relay. Both suspected components were replaced. The causal investigation did not identify a specific cause; however, there is a high level of confidence that the failure modes were eliminated by the corrective actions taken during troubleshooting. <br /><br /> This component inoperability is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident. This condition could have prevented the LPCS system, a single train safety system, from performing its design function. There was minimal safety consequences associated with the condition since other required emergency safety systems remained operable, there were no actual demands for Unit 1 LPCS, and safety margins were maintained.
3742017001 | LaSalle 2 | 01/23/2017 | 03/24/2017 | ML17083A12 | <strong>Manual Reactor Scram due to Turbine-Generator Run-Back Caused by Stem-Disc Separation in Stator Water Cooling Heat Exchanger Inlet Valve</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2017, operators initiated a manual scram of the LaSalle County Station Unit 2 reactor as a result of observing a generator run-back due to a generator stator winding cooling (GC) system malfunction. Initial troubleshooting identified the most likely cause was plugging in the 'A' GC heat exchanger, based on inspection of the GC system flow-path components. The GC system was realigned to the 'B' heat exchanger until inspections could be performed in the upcoming refueling outage, and the unit was re-started on January 24, 2017.<br /><br /> Further inspections of the GC components were performed while the unit was shut down for a planned refueling outage. These inspections determined the cause of the GC system failure was stem-disc separation in the 'A' GC heat exchanger inlet valve. The valve was repaired during the refueling outage. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the Reactor Protection System (RPS). There were no safety consequences associated with the event since there was no loss of safety function, and the RPS functioned as designed.
3742017002 | LaSalle 2 | 01/30/2017 | 03/31/2017 | ML17089A65 | <strong>High Pressure Core Spray System Declared Inoperable due to Cooling Water Strainer Backwash Valve Stem-Disc Separation</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2017, during routine surveillance testing of the Unit 2 Division 3 Diesel Generator Cooling Water (DGCW) system, the cooling water strainer backwash valve was unable to open. The Division 3 DGCW system was declared inoperable. Upon investigation, operators determined the cause of the valve malfunction was due to stem-disc separation. Division 3 DGCW is a support system for the Division 3 Emergency Diesel Generator and the High Pressure Core Spray (HPCS) system. The required actions of Technical Specifications (TS) 3.7.2 and 3.5.1 were entered on January 30, 2017 when the DGCW and HPCS system, respectively, were determined to be inoperable. TS 3.7.2 Required Action (RA) A.1 requires the supported system to be immediately declared inoperable. TS 3.5.1 RA B.2 requires restoration of the HPCS system to operable within 14 days. TS 3.8.1 was not applicable since a note provides that Division 3 AC electrical power sources are not required to be operable when HPCS is inoperable. The valve was replaced, and the HPCS system was returned to operable on February 2, 2017. <br /><br /> This condition could have prevented the HPCS system, a single train safety system, from performing its design function. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident. There were minimal safety consequences associated with the event since the other emergency safety systems remained operable, and the Division 3 DGCW system remained functional as it retained the ability to provide the required flow through the system. The apparent cause of the stem-disc separation was erosion due to the carbon-steel valve internals in a raw water system environment.
3742017003 | LaSalle 2 | 02/11/2017 | 08/09/2017 | ML17236A16 | <strong>High Pressure Core Spray System Inoperable due to Injection Valve Stem-Disc Separation</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2017, Unit 2 was in Mode 5 for a planned refueling outage. While attempting to fill and vent the Unit 2 High Pressure Core Spray (HPCS) system, no flow was observed from the drywell vent valves or downstream of the HPCS injection valve. The HPCS system was already inoperable to support scheduled surveillances performed on February 8, 2017 in which the HPCS injection isolation valve had been cycled five times satisfactorily. Troubleshooting determined the cause of the valve malfunction was due to stem-disc separation. The valve internal components were replaced prior to restart of the unit from the refueling outage. The root cause of the valve failure was insufficient capacity of the shrink-fit stem collar, combined with multiple high-load cycles, which resulted in loosening and eventual shear failure of the wedge pin and threads.<br /><br /> This component failure is reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident. This condition could have prevented the HPCS system, a single train safety system, from performing its design function if the valve failure occurred during an actual demand. This component failure is also reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS) 3.5.1 "ECCS - Operating," since the HPCS system could have been inoperable for greater than the TS 3.5.1, Required Action B.2, Completion Time of 14 days to restore HPCS system to operable status. There were minimal safety consequences associated with the condition since HPCS was not required to be operable at the time of the failure, and other required emergency safety systems remained operable. There were no actual demands for Unit 2 HPCS, other ECCS systems, or the reactor core isolation cooling (RCIC) system during this period.
3742017004 | LaSalle 2 | 02/17/2017 | 06/28/2018 | ML18179A29 | <strong>Two Main Steam Safety Relief Valves Failed Inservice Lift Inspection Pressure Test</strong><br /><i>Abstract:&nbsp;</i>During the February 2017 Unit 2 refueling outage, two main steam safety relief valves (SRV) did not pass Technical Specification (TS) Surveillance Requirement 3.4.4.1 and Inservice Testing (IST) Program lift pressure requirements. Both SRVs (2B21-F013C and 2B21-F013L) lifted below their expected lift pressures. On February 16, 2017, SRV 21321-F013C was required to lift within plus or minus three percent of 1175 psi (i.e., 1175 psi plus or minus 35.2 psi), but actually lifted at 1131 psi. On February 17, 2017 SRV 2B21-F013L was required to lift within plus or minus three percent of 1195 psi (i.e., 1195 psi plus or minus 35.8 psi), but actually lifted at 1130 psi.<br /><br /> Multiple test failures are reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant's Technical Specifications. Both SRVs lifted prior to their expected lift pressures, which is conservative in regards to maintaining reactor pressure vessel over-pressure limits. Both SRVs were replaced during the outage. A failure analysis was conducted; however, it did not identify a cause for the valves lifting below their expected lift set-points.
3822017001 | Waterford 3 | 03/08/2017 | 05/04/2017 | ML17128A08 | <strong>Both Trains of Emergency Core Cooling System Inoperable due to Inadvertently Performing Maintenance on Train ‘B’ Resulting in Event or Condition That Could Have Prevented Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2017, at 1627 CST, it was identified that Low Pressure Safety Injection (LPSI) train ‘B’ was inoperable due to SI-135B, Reactor Coolant Loop 1 Shutdown Cooling Warmup Valve, being found open, which is not the required position. At the time of discovery, LPSI train ‘A’ was inoperable for maintenance and the station was in compliance with Technical Specification (TS) 3.5.2 action ‘a’ which requires that an inoperable LPSI train be restored within 7 days. The shift operating crew entered TS 3.5.2 action ‘c’ due to both trains of the Emergency Core Cooling System being inoperable. Action ‘c’ requires that with both LPSI trains inoperable, at least one train must be restored within one hour. SI-135B was subsequently closed and tested to verify operability. TS 3.5.2 action ’c’ was exited at 1705. The station remained in compliance with TS 3.5.2 action ‘a’. <br /><br /> It was determined that the SI-135B valve was opened inadvertently. It was planned to perform work on SI-135A, Reactor Coolant Loop 2 Shutdown Cooling Warmup Valve. The workers incorrectly began work on SI-135B and manually opened the valve. This was caused by personnel not performing proper component verification to validate that they were on the correct component, contrary to station procedures. Corrective actions are being performed to improve station work practices related to component verification.
3822017002 | Waterford 3 | 07/17/2017 | 06/27/2018 | ML18178A67 | <strong>Automatic Reactor Scram due to the Failure of Fast Dead Bus Transfer Relays to Automatically Transfer Station Loads to Off-Site Power on a Main Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2017, at 1606 CDT, Waterford 3 experienced an automatic reactor scram due to a loss of forced circulation, which was the result of a loss of off-site power to the safety and non-safety electrical busses. Prior to the scram, plant operators manually tripped the main turbine and generator due to overheating of the isophase bus duct due to the failure of a shunt assembly connection in the duct to Main Transformer 'B'. The automatic electrical bus transfer did not occur due to relay failures in the fast dead bus transfer system. Both 'A' and 'B' Emergency Diesel Generators started and loaded as designed to re-energize the 'A' and 'B' safety busses. The loss of off-site power caused a loss of both Main Feedwater pumps, resulting in an automatic actuation of the Emergency Feedwater system.<br /><br /> The Root Cause of this event was the design change procedure used for modifications to the fast dead bus transfer circuitry did not include guidance to detect the susceptibility of the relays to DC coil inductive kick. The faulty relays in the fast bus transfer circuit were replaced prior to plant startup. <br /><br /> An Unusual Event was declared at 1617 CDT due to loss of off-site power to safety buses for >15 minutes. <br /><br /> All required safety-related equipment responded as expected during this event.
3872017001 | Susquehanna 1, Susquehanna 2 | 01/17/2017 | 03/08/2017 | ML17067A47 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2017 at approximately 11:45, three employees with a group of visitors were exiting the Unit 1 Reactor Building Airlock on Elevation 676'. While processing through the card reader, an individual in the group opened the Turbine Building airlock door prior to the Reactor Building airlock door being completely closed. This resulted in not meeting Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3, which requires that one secondary containment access door in each access opening is closed. <br /><br /> The cause of this event was determined to be less than adequate use of Human Performance Tools, including Self-Checking/ Stop, Think, Act and Review (STAR). <br /><br /> This condition requires reporting in accordance with 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872017002 | Susquehanna 1, Susquehanna 2 | 02/17/2017 | 04/12/2017 | ML17102B40 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2017, three technicians were walking through the 818' Airlock doors. The lead (first) technician observed the green light, swiped their badge and entered into the airlock. The two additional technicians then swiped their badges and walked into the airlock. The lead technician observed the first door closing and turned to open the second airlock door. As the first technician opened the second door the Airlock Door alarm sounded briefly as the first door was not completely closed and latched. This caused an alarm for a momentary breach of Secondary Containment. When they heard the alarm, both workers shut the doors. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of the event was less than adequate situational awareness. <br /><br /> Corrective actions included documented coaching of the worker. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872017003 | Susquehanna 1, Susquehanna 2 | 03/08/2017 | 05/05/2017 | ML17125A01 | <strong>Loss of Secondary Containment Zone 3 due to Fan Trip</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2017 at approximately 0239 hours, Secondary Containment Zone III (Unit 1&2 Reactor Bui ding) differential pressure lowered to less than the Technical Specification (TS) limit of 0.25 in w.g. due to Load Center Breaker 2B240-021 (supply breaker to 2Y246) being returned to service without Motor Control Center (MCC) Breaker 2B246-023 (supply breaker to 2Y246) restored. As a result, TS 3.6.4.1 Surveillance Requirement (SR) 3.6.4.1.1 was not met due to the loss of vacuum. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. <br /><br /> The cause of the event was less than adequate procedure use and adherence.<br /><br /> Corrective actions included a communication to Operators and a revision to the Procedure and Work Instructions Use and Adherence procedure to perform a second check for non-conditional procedure steps. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872017004 | Susquehanna 1, Susquehanna 2 | 06/09/2017 | 08/04/2017 | ML17216A28 | <strong>Secondary Containment Declared Inoperable due to Failure of an Exhaust Fan Breaker</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2017 at approximately 0509 hours, Secondary Containment Zone 3 differential pressure was lost during a routine restoration due to the failure of the Unit 1 Zone 3 'A' Reactor Building Exhaust Fan. Technical Specification Surveillance Requirement (SR) 3.6.4.1.1 was not met. <br /><br /> Zone 3 differential pressure was recovered to > 0.25" WG (Water Gage) by placing Unit 1 Zone 3 Filtered Exhaust to STOP and allowing Unit 2 Zone 3 to recover differential pressure. Zones 1 and 2 were not affected. This event is being reported under 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function. <br /><br /> The cause was determined to be a broken ring terminal on the breaker which prevented the fan from starting. Maintenance replaced the ring terminal and re-terminated the wire. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872017005 | Susquehanna 1, Susquehanna 2 | 06/08/2017 | 10/04/2017 | ML17277A32 | <strong>Automatic Reactor Protection System Trip on High Neutron Flux</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2017 at 1527 hours, the reactor automatically scrammed due to a loss of Main Turbine-Electro-Hydraulic Control (EHC) logic power causing a high neutron flux, Reactor Protection System (RPS) trip. The safety systems operated as expected. Secondary Containment differential pressure lowered to 0" WG due to a trip of the normal operation of the Reactor Building Ventilation system. The differential pressure was restored by the initiation of Standby Gas Treatment System. <br /><br /> The scram was caused directly by a DC+ (direct current, positive) test lead (Maxi Grabber) that inadvertently contacted with the grounding screw, causing a short and momentary loss of EHC logic power. Immediate action was taken to validate that there was no damage to the +30 VDC (volts DC) EHC logic. The root cause for this event is an insufficient focus on the High Risk Activity of adjusting the EHC power supply, and inadequate risk mitigating actions for that activity. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the RPS, including reactor scram. Although no safety system functional failure occurred, this event is also reportable pursuant to 10CFR 50.73(a)(2)(v)(C) as a condition that could have prevented fulfillment of a safety function. There were no actual, or potential consequences to the health and safety of the public as a result of this event.
3872017006 | Susquehanna 1, Susquehanna 2 | 10/06/2017 | 02/15/2018 | ML18046A90 | <strong>Control Room Envelope In-leakage Exceeded the Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2017 at 1945 hours, a loss of Control Room Habitability Envelope (CRHE) was declared due to failing to meet Technical Specification (TS) 3.7.3, Surveillance Requirement (SR) 3.7.3.4 during surveillance testing. The CRHE is required to be maintained such that occupants can control the reactor safely under normal conditions and maintain it in a safe condition following a radiological event, hazardous chemical release, or a smoke challenge. Mitigating actions were identified and include the ability to issue potassium iodide (KI) to the control room staff and Emergency Plan responders. With implementation of the mitigating actions, the dose consequence to the control room operators and affected Emergency Plan personnel is substantially less than the regulatory limit of 5 Rem Total Effective Dose Equivalent (TEDE) for event duration. <br /><br /> On October 6, 2017, at 2146 hours, this condition was reported (ENS #53003) in accordance with 10 CFR 50.72(b)(3)(v)(D) and is also reportable in accordance with the corresponding criteria of 10 CFR 50.73(a)(2)(v)(D). Additional review resulted in an assumption that the gasket could have been out of position since installation in 2012; therefore, this condition is also being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The cause was out of position door gaskets on the "A" Control Room Emergency Outside Air Supply (CREOAS) filter train due to inadequate installation. Corrective actions include repairing the door gaskets, performing a successful retest, and adding a step in the preventive maintenance activity when replacing the door gaskets to ensure the gasket is entirely glued into the channel such that the gasket is in contact with the entire channel. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872017007 | Susquehanna 1, Susquehanna 2 | 11/30/2017 | 05/04/2018 | ML18124A01 | <strong>Secondary Containment Declared Inoperable due to the Opening of a Plenum</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2017 at approximately 1030 hours, Susquehanna control room received indication of a loss of Secondary Containment Zone 2 differential pressure, noting differential pressure less than 0.25 inches water gauge (WG) for several seconds. As a result, Technical Specification (TS) 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met and TS 3.6.4.1 action statement 'A' was entered. The alarm came during an entry into the Unit 2 Zone 3 Exhaust Plenum for fan maintenance. This event is similar to an event that occurred on February 11, 2018 (LER 50-388(387)/2018-001-00).<br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. The condition was previously reported on November 30, 2017 in accordance with 10 CFR 50.72(b)(3)(v)(C) in EN #53098. <br /><br /> This event was unable to be replicated under various scenarios and no obvious equipment issues were identified. A sign was installed on the Unit 2 Zone 3 exhaust plenum door that states: "Entry into the plenum may impact secondary containment, notify control room prior to entry to evaluate LCO requirements." <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872017008 | Susquehanna 1 | 12/03/2017 | 04/02/2018 | ML18092B51 | <strong>Core Spray Inoperable due to Not Meeting Seismic Requirements as a Result of a Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On December 3, 2017, at approximately 1030, Operations identified materials staged in the Susquehanna Steam Electric Station (SSES) Unit 1 Division 2 Core Spray Room near the "B" Core Spray Pump Room Unit Cooler. The replacement piping materials were located on pipe roller stands approximately 6 inches from the unit cooler and were not seismically restrained. At the time of this condition, the SSES Unit 1 Division 2 Residual Heat Removal (RHR) Low Pressure Core Spray (LPCI) Swing Bus MG voltage regulator was being replaced. As such, Unit 1 Technical Specification 3.5.1 condition A for the voltage regulator replacement had already been entered. With the U1 "B" Core Spray Unit Cooler inoperable due to the presence of the improperly stored materials, this would have required entry into TS 3.5.1 condition I which requires entry into TS LCO 3.0.3 immediately. <br /><br /> The cause of the condition was determined to be less than adequate procedure use and adherence. The staged piping was removed immediately and a communication was performed with site personnel on this issue. <br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. There were no actual consequences to the health and safety of the public as a result of this event.
3882017001 | Susquehanna 2, Susquehanna 1 | 03/06/2017 | 05/05/2017 | ML17125A03 | <strong>Secondary Containment Declared Inoperable due to Airlock Doors Open due to Sticking Door Latch</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2017 at approximately 1325 hours, both airlock doors of a secondary containment airlock were momentarily open at the same time causing an alarm. The event occurred at the Unit 2 airlock between the Turbine Building (TB) and Reactor Building (RB) on Elevation 676. Individuals on the TB side of the airlock verified a green light and opened the TB side door, causing the RB side door to pop open from differential pressure. The individual on the RB side, who was using the security card reader, saw the RB door pop open. The doors were immediately closed, reestablishing secondary containment. <br /><br /> With both airlock doors open simultaneously, Surveillance Requirement (SR) 3.6.4.1.3 was not met. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented fulfillment of a safety function. <br /><br /> The cause was determined to be sticking of the door latch inside the crash bar, which prevented the RB side airlock door from properly latching and staying latched when differential pressure was applied, such as when the TB side door was opened. Corrective action included replacing the crash bar on the RB side door. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017002 | Susquehanna 2 | 03/06/2017 | 05/05/2017 | ML17125A02 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 During Unit 2 Refueling</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this Licensee Event Report (LER) was an expected condition as a result of planned activities, with the exception of one activity, in support of a routine refueling outage. As described in the LER, the U. S. Nuclear Regulatory Commission (NRC) provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). <br /><br /> Between 3/6/2017 and 3/30/2017, Susquehanna Steam Electric Station (SSES) performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities on Unit 2 while in Mode 5 without an operable secondary containment, as expected and allowed by the enforcement guidance. Although NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 allows the implementation of interim actions as an alternative to full compliance, this condition is still considered a condition prohibited by Secondary Containment TS 3.6.4.1. The OPDRV activities were planned activities that were completed under the guidance of plant procedures, with the exception of one unplanned activity. Since the planned actions were deliberate, no cause determination was necessary. The unplanned activity was caused by a human performance error related to procedural use and adherence and peer checking. Corrective action included coaching and remediation of the individual involved in the event. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017003 | Susquehanna 2, Susquehanna 1 | 03/02/2017 | 04/13/2017 | ML17103A32 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2017, at approximately 0930, two employees were transporting a cart of scaffold materials from Reactor Building Elevation 818' to Elevation 779'. While maneuvering the cart through an airlock on Elevation 779', personnel failed to ensure that the Reactor Building-side airlock door was fully closed prior to opening the Turbine Building-side airlock door. This resulted in not meeting Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3, which requires that one secondary containment access door in each access opening is closed. <br /><br /> The cause of this event was determined to be less than adequate use of Human Performance Tools, specifically Verification Practices. <br /><br /> This condition requires reporting in accordance with 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017004 | Susquehanna 2, Susquehanna 1 | 03/02/2017 | 04/25/2017 | ML17115A32 | <strong>Secondary Containment Breach due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2017 at approximately 10:30, three employees were entering the Unit 2 Airlock on elevation 676' from the Reactor Building door. After entering the airlock, one employee opened the second airlock door prior to the first door being closed, resulting in an alarm. This resulted in not meeting Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3, which requires that one secondary containment access door in each access opening is closed. The cause of this event was determined to be less than adequate Situational Awareness. <br /><br /> This condition requires reporting in accordance with 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017005 | Susquehanna 2, Susquehanna 1 | 06/24/2017 | 08/18/2017 | ML17230A24 | <strong>Secondary Containment Declared Inoperable due to Trip of Zone Ill Filtered Exhaust Fan</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2017, at approximately 1028 hours, Unit 2 secondary containment Zone Ill differential pressure was not maintained above the Technical Specification (TS) limit of 0.25 in w.g. due to the trip of a Reactor Building (RB) Zone III Filtered Exhaust Fan. As a result, TS 3.6.4.1 Surveillance Requirement (SR) 3.6.4.1.1 was not met due to the loss of differential pressure. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. <br /><br /> The cause of the event was the failure of the ASCO solenoid valve. Based on further review, the ASCO solenoid valve has been determined to be less than adequate for its application in Reactor Building HVAC. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017006 | Susquehanna 2, Susquehanna 1 | 07/10/2017 | 09/06/2017 | ML17249A53 | <strong>Secondary Containment Declared Inoperable due to Trip of Zone II Exhaust Fan</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2017, at approximately 0250 hours, Reactor Building Zone II differential pressure was not maintained above the Technical Specification (TS) limit of 0.25 inch of vacuum water gauge (WG) due to Discharge Damper PDD27578B failing closed resulting in loss of the associated Reactor Building Zone II Exhaust Fan 2V205B. As a result, TS 3.6.4.1 Surveillance Requirement (SR) 3.6.4.1.1 was not met due to the loss of differential pressure. Reactor Building Zone ll Exhaust Fan 2V205A was manually started and Reactor Building Zone II differential pressure was restored to greater than 0.25 inches WG by approximately 0301 hours. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function.<br /><br /> The cause of the event was the failure of the ASCO solenoid valve. Based on further review, the ASCO solenoid valve has been determined to be less than adequate for its application in Reactor Building HVAC. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017007 | Susquehanna 2, Susquehanna 1 | 08/08/2017 | 10/09/2017 | ML17282A01 | <strong>Secondary Containment Declared Inoperable due to Supply Air Flow</strong><br /><i>Abstract:&nbsp;</i>On August 8, 2017 at approximately 2043 hours, Secondary Containment Zone 2 experienced a loss of differential pressure following the replacement of the Zone 2 ventilation supply side filters. <br /><br /> Technical Specification Surveillance Requirement (SR) 3.6.4.1.1 was not met. Zone 2 differential pressure was recovered following the slight adjustment of the Reactor Building Zone 2 inlet dampers at approximately 2052 hours. Zones 1 and 3 were not affected. This event is being reported under 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented fulfillment of a safety function. <br /><br /> The cause was determined to be increased supply air flow following the replacement of the supply side filters. An action to revise future work instructions to ensure operations support is available to adjust Zone 2 differential pressure control following Zone 2 Supply side filter replacement. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017008 | Susquehanna 2 | 04/21/2013 | 01/19/2018 | ML18019A35 | <strong>Condition Prohibited by Technical Specifications due to a Loose Terminal Block Associated with Primary Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On July 19, 2017 at approximately 02:25, while performing a control room panel walk down, Operations observed indication for Primary Containment Isolation Valves HV21313 and HV21314 extinguished. Troubleshooting commenced and Technical Specification (TS) 3.3.3.1, Condition A was entered for loss of remote position indication for HV21313 and HV21314. On July 19, 2017 at approximately 10:49, investigation of the condition concluded that the isolation circuit for HV21314 was affected and the valve would not close if called upon to do so, and TS 3.6.1.3, Condition A was entered. The investigation identified a loose terminal block. The block was securely snapped back into the seat and the mounting screw was tightened. On July 19, 2017 at approximately 13:56, TS 3.3.3.1, Condition A and TS 3.6.1.3, Condition A were exited.<br /><br /> The loose terminal block was caused by improper seating during installation on April 21, 2013. Seismic evaluation concluded that the installed configuration (i.e., not properly seated) is not a dynamically qualified configuration and that operability in this condition is therefore indeterminate. Based on this information, the affected components are considered to have been inoperable since installation in April 2013. Since the amount of time between the installation and restoration of operability was greater than allowed by Technical Specifications, this is a condition prohibited by Technical Specifications. <br /><br /> The cause was determined to be a loose terminal block due to a human performance error during installation in 2013. Planned corrective actions include a read and sign for applicable electricians and procedure changes regarding how to verify proper seating of terminal blocks. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017009 | Susquehanna 2, Susquehanna 1 | 09/16/2017 | 02/15/2018 | ML18046A86 | <strong>Secondary Containment Declared Inoperable due to Trip of Zone II Equipment Exhaust Fan</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2017 at approximately 13:30, when performing a swap to place the Unit 2 "A" Reactor Building Equipment Compartment Exhaust fan (2V206A) in service, the fan tripped unexpectedly after being placed in service. Reactor Building differential pressure lowered to < 0.25 inches water gauge (WG) due to the unexpected trip of 2V206A. As a result, Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met due to loss of Secondary Containment differential pressure. The 2V206B fan was placed back in service and Reactor Building differential pressure was restored to above 0.25 inches WG. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. <br /><br /> The failure was not able to be replicated during investigation. The direct cause is inconclusive. A failure modes analysis was completed to identify the likely cause of the fan trip. Potential causes include one of the following: the flow control damper linkages binding, the low flow switch failing to reset, or the "A" and "B" fans running in parallel long enough to result in a low flow trip. A corrective action was identified to address each of these potential causes including greasing the linkages, testing the low flow switch reset and replacing the switch if necessary, and enhancing the affected procedures. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882017010 | Susquehanna 2 | 12/05/2017 | 12/16/2019 | ML19350A28 | <strong>Condition Prohibited by Technical Specifications due to Drift of Reactor Pressure Switches</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2017, the Unit 2 "C" and Unit 2 "D" Reactor Steam Dome Pressure - Low permissive pressure switches, Microswitch 2 (SW2), were found outside of the Technical Specification (TS) 3.3.5.1 allowable value. Both drifted outside of the upper allowable value which is intended to ensure that the reactor dome pressure has fallen to a value below the Core Spray and Residual Heat Removal (RHR)/Low Pressure Coolant Injection (LPCI) maximum design pressures to preclude over-pressurization of the low pressure systems prior to low pressure injection initiation. Based on the information available, the condition existed for longer than allowed by TS 3.3.5.1 and TS 3.5.1. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). This is also considered a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)), a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)), and a single cause that could have prevented fulfillment of safety functions of trains or channels in different systems (10 CFR 50.73(a)(2)(ix)(A)). <br /><br /> The direct cause was determined to be instrument setpoint drift resulting from an over-ranged condition and the effects of the movement assembly on the torque tube. Interim compensatory actions include performing calibration using the quarterly calibration procedures every 45 days on Unit 1 and every 30 days on Unit 2. Final corrective actions will include installing Cameron-Barton 288A instruments that have been modified to remove the over-range condition and the movement assembly/associated linkages that were determined to be affecting instrument drift.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3892017001 | St. Lucie 2 | 03/01/2017 | 04/27/2017 | ML17143A22 | <strong>Delay in Initiating Immediate Technical Specification Required Action During Fuel Movements</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2017, Unit 2 was in a defueled condition during a refueling outage and transitioned to a single operable train of the control room emergency air cleanup system. While in this condition, movement of irradiated fuel is prohibited by Technical Specifications. Approximately 100 minutes after transitioning to the single operable train of the control room emergency air cleanup system, control room operators were informed that irradiated fuel inspections in the Fuel Handling Building were in progress. Operators immediately placed the control room emergency air cleanup system on recirculation to comply with Technical Specifications. <br /><br /> The cause of this event was inadequate procedure instructions for the coordination of fuel handling activities in the spent fuel pool. Corrective actions included revising procedure instructions for the coordination of fuel handling activities. <br /><br /> This licensee event report is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. This event had no impact on the environment or onsite personnel. <br /><br /> This event had no effect on the health and safety of the public.
3892017002 | St. Lucie 2 | 05/15/2017 | 07/14/2017 | ML17195A18 | <strong>2A3 4.16 KV Bus De-Energization due to Voltage Meter Failure</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2017, at 1800 hours, the St. Lucie Unit 2 2A3 4.16 KV Bus undervoltage protection relays actuated resulting in a loss of power to the bus. The 2A emergency diesel generator (EDG) did not respond to this event as this EDG had been properly removed from service for pre-planned maintenance. The 2A3 4.16 KV Bus was restored to service at 2340 hours. <br /><br /> The 2A3 4.16 KV Bus was de-energized when an internal fault within the 2A EDG local voltmeter blew fuses that removed power from the undervoltage relays that resulted in the loads powered from this bus being stripped. Corrective actions included replacing the fuses and replacing the susceptible local EDG voltmeter, as well as the interim use of caution tags on the susceptible voltmeter selection switches until modifications to remove the vulnerability are complete. <br /><br /> During this event the B train safety related electrical busses remained operable and energized. All other equipment responded to the event per the existing plant conditions and the unit remained at 100% power. The A train safety related electrical bus was restored to service well within the Technical Specification allowed outage time. Therefore, this event had no significant impact on the health and safety of the public.
3892017003 | St. Lucie 2 | 10/25/2017 | 12/18/2017 | ML17352A63 | <strong>Improper System Realignment Resulted in Loss of Steam Driven Auxiliary Feedwater Pump Flow Indication</strong><br /><i>Abstract:&nbsp;</i>On October 25, 2017, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power when the station discovered that both of the required flow transmitters (indication only) for the 2C steam driven auxiliary feedwater (AFW) pumps had been isolated since October 17, 2017. The transmitters were returned to service and extent of condition walkdowns were completed on the AFW pump flow transmitters for both St. Lucie Units 1 and 2; no other anomalies were noted. <br /><br /> This event was caused by human error because the personnel involved in the AFW flow calibration activities on October 17, 2017 did not adequately perform the system restorative steps in accordance with the governing procedure. <br /><br /> Based on the availability of diverse methods to verify AFW flow delivery to the steam generators, this condition had no effect on the health and safety of the public.
3892017004 | St. Lucie 2 | 10/26/2017 | 12/18/2017 | ML17353A01 | <strong>Automatic Reactor Trip due to Turbine Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2017, at 0212 hours with St. Lucie Unit 2 in Mode 1 at 100% power, the reactor automatically tripped due to a loss of load following a failure within the turbine control system. The reactor trip was uncomplicated and all control rod assemblies fully inserted. Following the trip, one of the low power feedwater valves LCV-9005, did not properly maintain steam generator level which resulted in an actuation of the A-train auxiliary feedwater system. During the auxiliary feedwater actuation, one main feedwater isolation valve did not reposition closed as expected, but this did not impact heat removal. The main feedwater system remained available. <br /><br /> The failure within the turbine control system was caused by design deficiencies. Planned corrective actions include modifications to improve protective circuits, the addition of coolers and use of conformal coatings on printed circuit boards in the modules.<br /><br /> The problem with LCV-9005 was due to a latent design error that resulted in the setting of an incorrect stroke length for the control valve. This was corrected by adjusting the stroke length of the valve. <br /><br /> This report is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for system actuations of the reactor protection system and the auxiliary feedwater system. <br /><br /> During this event offsite power remained operable and energized. All other equipment responded to the event as expected per the existing plant conditions; therefore, this event had no impact on the health and safety of the public.
3902017001 | Watts Bar 1, Watts Bar 2 | 11/10/2016 | 01/09/2017 | ML17009A28 | <strong>Failure of Emergency Raw Cooling Water Pump Reverse Rotation Keys Represents Potential Common Cause Inoperability</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2016, Watts Bar Nuclear Plant personnel identified a failure of the non-reverse clutch key on Emergency Raw Cooling Water (ERCW) motor B-A. While performing a lubrication work order, it was discovered that the clutch key was sheared. Subsequent investigation identified that other clutch key failures had occurred in the recent past. The non-reverse clutch prevents the ERCW pump from rotating in the reverse direction after pump trip, which could cause the motor to develop a higher than normal in-rush current if the motor was subsequently started, such as following an accident. <br /><br /> Based on the potential common mode failure of the non-reverse clutch, immediate corrective actions were put in place to ensure that the safety function of the ERCW pumps to start following an accident would not be impaired. The cause of the failure is under investigation.
3902017002 | Watts Bar 1 | 12/24/2016 | 02/22/2017 | ML17053A88 | <strong>Incorrectly Hung Clearance Leads to a Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 24, 2016, Watts Bar Nuclear Plant (WBN) personnel identified that a clearance associated with a containment purge valve, 1-FCV-30-17, had been incorrectly hung. The clearance was intended to pull fuses to close and de-energize this valve in support of local leak rate testing. The incorrect fuses were removed, and the valve remained energized for about 24 hours while local leak rate testing was performed on the associated containment penetration. The clearance error was discovered when operations personnel attempted to replace the fuses for valve 1-FCV-30-17. The cause of the error was determined to be a human performance error. This has been determined to be a condition prohibited by Technical Specification 3.6.3, Limiting Condition for Operation, Condition A, because the penetration was inoperable for longer than the four hour required action time.
3902017003 | Watts Bar 1, Watts Bar 2 | 01/04/2017 | 03/03/2017 | ML17065A01 | <strong>Inadequate Operability Determination Leads to a Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2017 at 1010 Eastern Standard Time (EST), Watts Bar Nuclear Plant Operations personnel declared Essential Raw Cooling Water (ERCW) strainer flush valve 2-FCV-67-9B inoperable due to having a through-wall leak. The valve was replaced and the ERCW strainer was returned to service on January 5, 2017 at 0952 EST. This event is reportable because the valve had had a through-wall leak since January 31, 2016 and had not been declared inoperable. With a through-wall leak, a flaw evaluation is required to be performed to demonstrate the through-wall leak was stable. The failure to perform an adequate operability evaluation allowed the valve to remain in service for a period of time longer than allowed by Technical Specification (TS) 3.7.8, Essential Raw Cooling Water, Limiting Condition for Operation (LCO) Condition A. This represents a condition prohibited by the TS. Subsequent analysis of the valve demonstrated that it remained structurally sound with the leak, and would not have impacted the operability of the ERCW system.<br /><br /> The cause of the failure to perform an adequate operability evaluation has been determined to be human performance errors on the part of both operations and engineering personnel. Additional training of operations and engineering personnel is planned as corrective action to address the potential for recurrence of this issue.
3902017004 | Watts Bar 1 | 05/02/2017 | 08/31/2017 | ML17243A25 | <strong>Manual Reactor Trips due to Failed Reactor Coolant Pump Power Transfer During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2017, at 1945 Eastern Daylight Time (EDT) and on May 4, 2017 at 1710 EDT, Watts Bar Nuclear (WBN) Plant Unit 1 reactor was manually tripped due to a failure of the Reactor Coolant Pump (RCP) Board 1C normal feeder breaker to close during the planned power transfer to unit power following plant startup. Concurrent with each reactor trip, the Auxiliary Feedwater system actuated as designed. All control and shutdown rods fully inserted. All safety systems responded as designed for both events. <br /><br /> For the first event, the cause was incorrectly attributed to a high resistance contact resulting in the normal feeder breaker failing to close. In the investigation following the second event, a relay associated with the RCP Board 1C control circuit was found incorrectly configured due to a human performance issue, which resulted in a standing trip signal on the RCP normal feeder breaker. To prevent recurrence, procedures will be revised to address material control of pretested components.
3902017005 | Watts Bar 1 | 05/10/2017 | 07/10/2017 | ML17191A43 | <strong>Isolation of the 1B-B Safety Injection Pump Leads to Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2017, at 0907 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) Unit 1 operations personnel discovered the 1B-B Safety Injection pump discharge isolation valve (1-ISV-63-527) closed. Technical Specification (TS) 3.5.2, ECCS - Operating, Condition A was immediately entered for one or more trains of the Emergency Core Cooling System (ECCS) inoperable. TS 3.5.2 Condition A was exited at 0913 EDT when 1-ISV-63-527 was opened. Investigation determined that the 1B-B SI pump discharge isolation valve had been closed prior to Unit 1 entering Mode 3 on April 26, 2017, representing a condition prohibited by TS. During this time period, the 1A-A SI pump was inoperable for 21 minutes, representing a condition that could have prevented fulfillment of a safety function.<br /><br /> The cause of the mispositioned valve was the result of an individual failing to follow procedure use and adherence requirements during the performance of Emergency Diesel Generator (EDG) Blackout testing. The safety injection pump discharge valve was closed to support the test but was not reopened following the testing. Corrective actions for this event include personal accountability actions, revision of the EDG blackout procedures to ensure the SI pump discharge valves are reopened, and additional station focus on procedure use, particularly use of Not Applicable (N/A) in performing procedures.
3902017006 | Watts Bar 1 | 06/01/2017 | 07/31/2017 | ML17212A37 | <strong>Structural Degradation of 161 kV Line Pole Leads to a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2017, at 1550 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) Unit 1 operations personnel declared one of its two required offsite power sources to be inoperable in accordance with Technical Specification (TS) 3.8.1, Condition A. One of the poles for this power source was found cracked and not able to meet its structural load requirements for wind or icing. The pole was replaced and the line returned to service on June 2, 2017. <br /><br /> This crack was determined to have been caused by an earlier line failure on May 27, 2017 when adjacent poles fell during a thunder storm, which also caused the plant to enter TS 3.8.1, Condition A. Based on evidence demonstrating that the pole with the crack had not met requirements from May 27, 2017 until replaced on June 2, 2017, a condition prohibited by Technical Specification 3.8.1 occurred because the line was not functional for a period longer than the allowed outage time. <br /><br /> The cause for failure to repair the pole with the crack following the May 27, 2017 event was that it was covered by vegetation, and was not discovered until June 1, 2017. Corrective actions to address this issue included investigation of the offsite power source support structures and replacement of degraded offsite power line poles to maintain high reliability of offsite power.
3902017007 | Watts Bar 1, Watts Bar 2 | 06/09/2017 | 11/03/2017 | ML17310A10 | <strong>Multiple Unreported Potential Loss of Safety Function Events Associated with Inoperable Single Train Systems due to Misinterpretation of Reporting Guidance</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2017. Watts Bar Nuclear Plant (WBN) personnel determined that the reporting requirements of 10 CFR 50.72(b)(3)(v) and 10 CFR 50.73(a)(2)(v), as clarified by guidance in NUREG-1022, Revision 3. were being incorrectly applied for certain events associated with single train safety systems. When events occurred that resulted in these systems not meeting Technical Specification (TS) Limiting Conditions for Operation (LCO), the short duration of these events relative to their required action completion time, coupled with prompt return to allowable values, were not considered a loss of safety function by Operations and Licensing personnel. As a result, multiple potential loss of safety function events were not reported as required. These events were related to Refueling Water Storage Tank (RWST) level, Containment and Shield Building pressure, and Control Room Envelope integrity.<br /><br /> A review of these events indicate, when considering the actual system capability and the response of equipment and personnel, a loss of safety function capability impacting public health and safety did not occur for events associated with the RWST, Containment. Shield Building, or Control Room. Corrective actions include briefing personnel on the regulatory impact of these events, and the importance of the control room boundary.
3902017008 | Watts Bar 1 | 06/15/2017 | 08/14/2017 | ML17226A29 | <strong>Shield Building Inoperability and Potential Loss of Safety Function Resulting from Spurious Equipment Operation</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2017, at 1219 Eastern Daylight Time (EDT), Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.15 Condition B was entered for Watts Bar Nuclear Plant (WBN) Unit 1 annulus pressure not within limits, resulting in Shield Building inoperability. At 1221 EDT, the WBN Unit 1 annulus pressure returned to normal, the Shield Building was declared operable, and LCO 3.6.15 Condition B was exited. Because the shield building is a non-redundant safety system, operation outside of TS allowable limits represents an event that could have prevented fulfillment of a safety function. <br /><br /> The temporary loss of the Shield Building resulted from a loss of pressure control in the Auxiliary Building caused by a loss of Auxiliary Building General Ventilation due to a spurious cross zone fire alarm. The Auxiliary Building Gas Treatment System was started to maintain Auxiliary Building pressure within limits and the non-safety related Annulus Vacuum system automatically restored annulus pressure. The fire detectors that resulted in the loss of the WBN Unit 2 Auxiliary Building ventilation supply fans were replaced.
3902017009 | Watts Bar 1, Watts Bar 2 | 07/12/2017 | 09/11/2017 | ML17254A76 | <strong>Unanalyzed Condition Related to Dual Unit Operation of the Essential Raw Cooling Water System During a Design Basis Accident</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2017, at 1238 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) determined that a preliminary analysis shows adequate Essential Raw Cooling Water (ERCW) flow may not be available during dual unit limiting design basis conditions of one unit in Hot Shutdown on Residual Heat Removal (RHR) cooling when the other unit experiences a Loss of Coolant Accident (LOCA). Based on preliminary analysis, during a Unit 1 LOCA, Unit 1 receives adequate flow when following existing procedural guidance. However, Unit 2 may not receive adequate flow to meet cool-down requirements with design basis maximum temperatures. During a Unit 2 LOCA, however, current procedural guidance is not adequate to ensure the proper system alignment to establish correct ERCW Component Cooling Water (CCS) Heat Exchanger A and B flow rates for either unit's cool down requirements. <br /><br /> At the time of the event, Unit 2 had been shutdown for an extended period of time such that the flow delivered by ERCW was adequate to serve both Unit 1 in a LOCA and Unit 2 in Mode 4 or 5. Immediate corrective actions included procedure changes to ensure adequate ERCW flow for all possible plant situations in both units. The causes of this issue are a failure to address cross train elements of the ERCW system in the design analysis and a failure to address procedural impacts when the plant transitioned to dual unit operation. The procedure errors were corrected.
3902017010 | Watts Bar 1 | 08/17/2017 | 10/16/2017 | ML17289B08 | <strong>Actuation of Turbine Driven Auxiliary Feedwater Pump due to Loss of 6.9kV Shutdown Board</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2017, at 1205 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) lost power to the 1B-B 6.9kV Shutdown Board. The loss of power to this safety related bus resulted in an automatic start of the Unit 1 Turbine Driven Auxiliary Feedwater Pump (TDAFWP). Power to the 1B-B Shutdown Board (SDBD) was restored at 1505 EDT on August 17, 2017.<br /><br /> During the loss of power to the 1B-B SDBD, a reduction in containment and control rod drive mechanism cooling occurred. At 1233 EDT, lower containment average temperature exceeded Technical Specification (TS) limits, and TS 3.6.5 Condition A was entered for containment average air temperature not within limits. Lower containment average temperature was restored to within limits at 1525 EDT on August 17, 2017. This is reportable as a potential loss of safety function. <br /><br /> The cause of this event is mechanical vibration while closing a panel drawer resulting in actuation of protective relays that led to a loss of power. Clearances will require the relays involved in this event to be isolated during drawer movement to prevent a similar occurrence.
3902017011 | Watts Bar 1 | 08/23/2017 | 10/23/2017 | ML17296A32 | <strong>Failure to Enter Technical Specification 3.6.3 for Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2017, Watts Bar Nuclear Plant (WBN) personnel identified Technical Specification (TS) 3.6.3, Containment Isolation Valves, was not entered for on-going work related to 1-FCV-31-330, Incore Instrument Room Air Handler Unit 1B Chilled Water System Isolation Valve. A clearance was placed on 1-FCV-31-330 by Operations Work Control for scheduled work on May 17, 2017 rendering the valve inoperable. Work was completed May 19, 2017, however, the clearance remained in place pending post maintenance testing after other related system work was complete. Due to a human performance error, the appropriate TS tracking program was not activated and no narrative log entry was made to signify entry into the TS as required by procedure. The in-place clearance satisfactorily met the required actions of TS 3.6.3 condition A.1. to isolate the affected containment penetration flow path by use of at least one closed and de-activated automatic valve. However, without the required TS tracking program activated, personnel failed to comply with TS 3.6.3 condition A.2. to verify the affected penetration flow path is isolated every 31 days. <br /><br /> Failure to enter the TS tracking program in accordance with procedure was a human performance error. Corrective actions included coaching and department operating experience communication.
3902017012 | Watts Bar 1, Watts Bar 2 | 08/23/2017 | 01/30/2018 | ML18030A58 | <strong>Error in Plant Emergency Procedures Leads to a Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2017, Watts Bar Nuclear Plant (WBN) identified that procedures 1-E-1 and 2-E-1, Loss of Reactor or Secondary Coolant, contained steps to manually open 1-FCV-67-458 in the event of a Train A or B power failure. Opening 1-FCV-67-458 would result in the crosstie of Essential Raw Cooling Water (ERCW) Headers 2A and 1B, which would lead to providing flow to equipment not operating due to the loss of a train of power. On October 6, 2017, it was determined that for certain time periods, if a design basis accident had occurred on Unit 2 with a loss of offsite power concurrent with a train failure and with 1-FCV-67-458 opened, inadequate ERCW flow would have been available to remove decay heat after transfer to cold leg recirculation. This condition only affected operability of ERCW Train A. This is reportable as a condition prohibited by Technical Specification 3.7.8. <br /><br /> The issue associated with this incorrect procedural step to cross-tie the ERCW trains in 1-E-1 and 2-E-1 was addressed as part of actions to resolve an ERCW design and procedure issue documented in Licensee Event Report (LER) 390-2017-009. This report, while related, identifies an issue that was not addressed in the prior LER. The cause was determined to be the incorrect application of a cross tie requirement associated with 10 CFR 50 Appendix R. Corrective action will be to include engineering in the review of procedures affected by complex design changes.
3902017013 | Watts Bar 1, Watts Bar 2 | 09/06/2017 | 01/24/2018 | ML18024A36 | <strong>Incorrectly Adjusted Auxiliary Building Gas Treatment System Damper Leads to a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2017, Watts Bar Nuclear Plant (WBN) identified that the vacuum relief line airflows did not meet acceptance criteria for the Auxiliary Building Gas Treatment System (ABGTS) for Train A during the performance of 0-SI-30-7-A, ABGTS Pressure Test. Troubleshooting of the low airflows identified an Auxiliary Building Secondary Containment Enclosure (ABSCE) Unit 2 General Ventilation intake damper 2-FCO-30-108 with approximately one inch gaps in the blade seals with the damper in the closed position. Preliminary investigation found that the damper linkage appeared to not be adjusted correctly to allow full closure of the damper blades following maintenance in May of 2017. The low vacuum relief line airflows resulted in the Train A ABGTS being inoperable, based on identified open ABSCE breaches, from July 7, 2017 to September 5, 2017. This time period is longer than that allowed by Technical Specification (TS) 3 7 12 for ABGTS, and is therefore a condition prohibited by TS.<br /><br /> The cause of this event was an incorrectly adjusted damper linkage after replacement of the damper actuator. A training needs analysis will be performed to evaluate training solutions for damper linkage adjustments. Damper preventative maintenance activities will be revised to address smooth operation and absence of mechanical binding.
3902017014 | Watts Bar 1, Watts Bar 2 | 10/30/2017 | 12/20/2017 | ML17354A23 | <strong>Main Control Room Boundary Door Left Open Leading to a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 30. 2017, at 0942 Eastern Daylight Time (EDT) Watts Bar Nuclear Plant (WBN) operations personnel received a Main Control Room (MCR) alarm for low control room positive pressure. At 0943 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10 Control Room Emergency Ventilation System (CREVS) was declared not met for both trains, and Limiting Conditions for Operation (LCO) Condition B was entered for Unit 1 (Mode 1) and Condition G was entered for Unit 2 (Mode 5). At 0945 EDT the alarm cleared, CREVS was declared operable and LCO 3.7.10, Conditions B and G were exited. The loss of the control room envelope is being reported as a loss of safety function needed to mitigate the consequences of an accident.<br /><br /> The cause of this issue is a human performance error in that an individual leaving the control building complex failed to confirm closure of the MCR envelope boundary door. Corrective actions have been generated to develop and install an engineering feature to inform personnel closing the door that it is fully shut and latched.
3902017015 | Watts Bar 1, Watts Bar 2 | 11/09/2017 | 01/08/2018 | ML18008A21 | <strong>Failure to Enter Limiting Condition of Operation Action Statement Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2017, an issue was identified where Technical Specification (TS) Limiting Conditions of Operation (LCOs) were not entered when non-TS Engineered Safety Feature (ESF) area coolers were removed from service for maintenance. The Watts Bar Nuclear Plant (WBN) had been performing maintenance on ESF coolers serving Auxiliary Building areas without entering the TS LCO Action Statements associated with equipment present in those areas. Specific areas of concern identified were the general areas of the 713 foot and 737 foot elevations of the Auxiliary Building. These coolers were taken out of service for time periods longer than allowed for ESF equipment (typically 72 hours), which would represent a condition prohibited by the TS.<br /><br /> At this time, WBN has not confirmed that for those cases where a cooler was taken out of service without entering a TS LCO if an actual adverse impact on safety function would have occurred if an accident with a single failure had occurred during those time periods. Those details, and the cause and corrective actions related to a 2010 guidance change, will be provided in a supplement to this report.
3902017016 | Watts Bar 1 | 12/20/2017 | 02/20/2018 | ML18051B08 | <strong>System Actuations due to Opening of Feeder Breaker to the 1B-B 6.9 kV Shutdown Board</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2017, at 1040 Eastern Standard Time (EST), the Watts Bar Nuclear Plant (WBN) 1B-B 6.9kV Shutdown Board (SDBD) normal feeder breaker opened. The loss of voltage to the 1B-B SDBD resulted in the start of the 1B-B Motor Driven Auxiliary Feedwater (MDAFW) pump, the Unit 1 Turbine Driven Auxiliary Feedwater (TDAFW) pump, and the start of all four Emergency Diesel Generators (EDGs). Power was restored to the 1B-B SDBD when it loaded on to its associated EDG. Following initial investigation, the 1B-B SDBD was transferred to its alternate offsite power source at 1217 EST. At 1230 EST, the 1B-B SDBD alternate feeder breaker opened, with a plant response that was similar to the first loss of power. Restoration of normal offsite power to the 1B-B SDBD was completed at 1654 EST. This event is being reported as a safety system actuation and as an event or condition that could have prevented fulfillment of a safety function related to containment temperature being outside Technical Specification limits. <br /><br /> Both loss of voltage events to the 1B-B SDBD were caused by poor contact of the B and C phases of the protective relay potential transformer drawer secondary connections which supplies the degraded and loss of voltage relays. The mounting block that houses the secondary pins was able to be trimmed, resulting in an improvement of the secondary connection. The mounting blocks for the secondary connections on SDBDs 1A-A, 2A-A, and 2B-B will be inspected and modified, if required, during future equipment outages. The procedure associated with inspection of the secondary connections will be revised.
3912017001 | Watts Bar 2 | 03/09/2017 | 05/03/2017 | ML17123A36 | <strong>Containment Airlock Function Lost due to Equalizing Valve Not Closing</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2017 at 0120 Eastern Standard Time, the equalizing valve for the Watts Bar Nuclear Plant (WBN) Unit 2 upper containment airlock inboard door was found not closed while the outboard airlock door was open. This created a containment bypass with leakage potentially greater than allowed by the Technical Specifications. The operator immediately identified that the pressure equalizing valve for the inner door was not fully closed when the outer door of the airlock was opened. The outer door was promptly shut to isolate the airlock. The inner door was then cycled which closed the equalizing valve. The total time that a containment bypass was present is estimated to be five minutes. <br /><br /> The equalizing valve did not seat properly due to a damaged part in the valve closing mechanism. The airlock remains functional, and an operations caution order was put in place related to use of this air lock. The airlock will be repaired prior to Unit 2 returning to Mode 4.
3912017002 | Watts Bar 2 | 03/20/2017 | 05/12/2017 | ML17132A26 | <strong>Manual Reactor Trip as a Result of a Secondary Plant Transient</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2017 at 0813 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) Unit 2 operations personnel manually tripped the plant from approximately 91 percent power based on lowering steam generator levels. Prior to the plant trip, the 2A Hotwell pump tripped at 0759 EDT and the 2C Condensate Booster Pump subsequently tripped at 0803 EDT. Operations personnel commenced to lower plant power after the 2A Hotwell pump trip in an attempt to maintain steam generator levels, but were unable to recover level and manually tripped the unit. <br /><br /> All control rods fully inserted and all automatically actuated safety related equipment operated as designed. At 0905 EDT, operations personnel exited the emergency operating instructions after the plant was stabilized. <br /><br /> This event resulted when scaffold crews inadvertently depressed the local trip button for the 2A Hotwell pump, which resulted in the secondary system transient. Bump guard covers were subsequently installed on local pushbuttons for selected pumps in the turbine building.
3912017003 | Watts Bar 2 | 03/23/2017 | 05/22/2017 | ML17142A10 | <strong>Automatic Start of Auxiliary Feedwater System due to Main Condenser Failure</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2017, at 0014 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant Unit 2 experienced an unplanned trip condition of both Turbine Driven Main Feed Pumps (TDMFPs) following a loss of Main Condenser Vacuum. The trip of both TDMFPs caused an automatic start of both Motor Driven Auxiliary Feed Water Pumps and the Turbine Driven Auxiliary Feed Water Pump as designed.<br /><br /> The plant was performing a normal startup, and had just synchronized the main generator to the grid. Subsequent to the event, the plant was transitioned to Mode 3 by inserting all control rods with a manual trip. All plant safety systems operated as expected.<br /><br /> The loss of condenser vacuum was the result of a significant breach of the Unit 2 main condenser - B zone. This failure is attributed to the main condenser neck support structural design being inadequate to maintain integrity within specification. Repairs to the condenser will be completed prior to Unit 2 returning to service.
3912017004 | Watts Bar 2 | 07/25/2017 | 09/25/2017 | ML17268A21 | <strong>Manual Reactor Trip due to Inoperable Rod Position Indication</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2017, at 0428 Eastern Daylight Time (EDT) Watts Bar Nuclear Plant (WBN) Unit 2 was in Mode 3, commencing a Reactor Startup. While in the initial phase of withdrawing the first of four Control Banks, the two associated group demand position indicators deviated greater than 2 steps from each other. In accordance with Technical Requirement 3.1.7, Position Indication System, Shutdown, with one or more group demand position indicators inoperable, the reactor trip breakers are to be opened immediately. Operations personnel opened the reactor trip breakers immediately by initiating a manual trip of the Reactor Protection System. The Auxiliary Feedwater system was in service and controlling Steam Generator water levels at the time of the event and did not receive any valid actuation signals. No other system actuations occurred as a result of this reactor trip and all systems operated as designed. <br /><br /> The rod demand indication deviation was determined to be caused by a failed logic card, which was replaced.
3912017005 | Watts Bar 2 | 11/26/2017 | 01/25/2018 | ML18025B34 | <strong>Unplanned Emergency Core Cooling System Injection Into the Reactor Coolant System due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2017. at 1225 Eastern Standard Time (EST), the Watts Bar Nuclear Plant (WBN) Unit 2 experienced an unplanned Emergency Core Cooling System (ECCS) discharge to the Unit 2 Reactor Coolant System (RCS) while de-pressurized, in Mode 5, with the Pressurizer vented to the Pressurizer Relief Tank. ECCS injection via the Boron Injection flow path occurred during planned Safety Injection system Engineered Safety Features Actuation System (ESFAS) testing. The Boron Injection flow path should have been isolated and should not have resulted in any injection flow to the Unit 2 RCS. The condition was promptly corrected by operator actions based on observed plant conditions. <br /><br /> The cause of this event is that an Operator improperly used a Caution Order to determine the configuration of the breaker for the Boron Injection Tank outlet valve. Correct Component Verification was not utilized as required and the current position of the breaker in the field was not validated to support testing. Corrective actions for this event include revising procedures to ensure the breakers associated with the boron injection flow path will be tagged open during ESFAS testing and that lessons learned related to this event are communicated to operating crews. An evaluation on the use of Caution Orders for off normal equipment positions will be performed.
3912017006 | Watts Bar 2 | 12/11/2017 | 02/09/2018 | ML18040A62 | <strong>Manual Reactor Trip in Response to Indication of Multiple Dropped Control Rods</strong><br /><i>Abstract:&nbsp;</i>On December 11, 2017 at 0857 Eastern Standard Time (EST), the Watts Bar Nuclear Plant Unit 2 reactor was manually tripped after Operators observed multiple dropped control rods. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant was stabilized with decay heat removal through Auxiliary Feedwater and the Steam Dump System. <br /><br /> An intermittent electrical connection between a rod control power cabinet card and the power cabinet backplane power supply caused a rod control malfunction with control bank A group 2 control rods. The malfunction resulted in four control rods dropping into the reactor core. As a corrective action, all five control rod power cabinets had a 100 percent inspection of backplane connectors on the card cages. Backplane connectors were reformed and aligned as necessary to attain suitable electrical and mechanical connection. Additionally, all associated circuit cards for the power cabinets had their connectors re-formed with a precision tool. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as safety system actuations of the Reactor Protection System and Auxiliary Feed Water System.
3952017001 | Summer 1 | 04/07/2017 | 08/03/2018 | ML18215A18 | <strong>C Main Feedvvater Pump Failure to Trip Results In Loss of Emergency Feedvvater Autostart Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2017, the station completed a past operability review and determined that an Emergency Feedwater Auto Start Actuation Signal was inoperable from November 12, 2016 until April 7, 2017. Technical Specification (TS) 3.3.2 Limiting Conditions for Operation (LCO) was entered due to having less than the minimum number of channels operable for Motor Driven Emergency Feedwater Pump (MDEFWP) actuation per TS Table 3.3-3 Functional Unit 6.g. <br /><br /> This event was a result of TPP0022C, MAIN FEEDWATER PUMP TURBINE C, remote trip actuating device not operating as designed. The remote trip actuating device not operating as designed was a result of oil contamination due to a gland seal steam leak near the Low Pressure (LP) bearing. <br /><br /> This condition is reportable under 10CFR50.73(a)(2)(i)(B), an operation or condition which was prohibited by the plant's Technical Specifications.
3952017002 | Summer 1 | 06/29/2017 | 01/31/2018 | ML18031B18 | <strong>Low Feedwater Flow to the 'B' Steam Generator Causes Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2017 at 0857, VCSNS Unit 1 automatically tripped due to low Feedwater (FW) flow to the 'B' Steam Generator (SG). The trip was the result of a spurious closure of the Main FW to 'B' Steam Generator Flow Control Valve, IFV00488-FW. The Flow Control Valve's closure resulted in low SG level coincident with the low FW flow, which caused an automatic reactor trip. The plant trip response was normal.<br /><br /> The cause of this event was determined to be the inadvertent closure of IFV00488-FW due to solenoid valve failure. The solenoid valve failure appears to be a result of an inadequate solder applied to the solenoid coil during the manufacturing process.
3952017003 | Summer 1 | 08/28/2017 | 12/12/2017 | ML17347A21 | <strong>Failed Lightning Arrester on Main Transformer Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2017, at 0837, VCSNS Unit 1 automatically tripped due to a turbine trip. The turbine trip was caused by the Main Generator Differential Lockout due to a fault on the center phase, 230 kV lightning arrester, on the Main Transformer (XTF-1). <br /><br /> The plant trip response was normal. All control rods fully inserted. Balance of Plant (BOP) buses automatically transferred to their alternate power source, Emergency Auxiliary Transformers (XTF-31/32). Both Motor Driven (MD) Emergency Feedwater (EF) pumps and the Turbine Driven EF Pump started as designed.<br /><br /> The cause of this event was the failure of the center phase lightning arrester on XTF-1. The failed arrester, along with the other two lightning arresters that were in service on XTF-1 during the reactor trip, was replaced. The lightning arresters were sent to an independent lab, NEETRAC - Georgia Tech, for testing and evaluation. <br /><br /> The examination results indicate that the most probable cause of the arrester failure was an internal flashover of the metal oxide varistor blocks. The cause of the internal flashover is likely moisture ingress from the upper end seal.
3952017004 | Summer 1 | 09/11/2017 | 11/09/2017 | ML17313B09 | <strong>Actuation of 'A' Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2017 at 1648. the VCSNS Unit 1 'A' emergency diesel generator (EDG) was actuated. VCSNS Unit 1 was and continued to operate in Mode 1 at 100% reactor power. The EDG actuation was caused by a storm induced perturbation on the off-site power system. The duration of the fault was longer than it should have been due to a malfunction of a transmission system relay. The perturbation cleared and off-site voltage was returned to normal within the designed recovery time limit. The bus continued to be carried by the off-site source and the EDG output breaker remained open.<br /><br /> The station review of this event has shown that plant response was as designed and that no safety consequences occurred.
3952017005 | Summer 1 | 11/07/2017 | 12/22/2017 | ML17356A21 | <strong>Automatic Reactor Trip due to Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At 1957 on November 07, 2017, VCSNS Unit 1 was operating. in Mode 1 at 100% reactor power when a turbine trip caused an automatic reactor trip. All systems responded as expected, with the exception of 'B' Steam Generator Feedwater Isolation Valve (FWIV) XVG1611B-FW. This valve did not appear to automatically close and was slow to indicate closed from the Main Control Board, however this did not complicate the response. All Control Rods fully inserted and all Emergency Feedwater (EFW) pumps started as required. The Operating crew stabilized the plant, which remained in Mode 3 with decay heat removal via the Steam Dump system to the Main Condenser. <br /><br /> The cause of the turbine trip has been determined to be a loss of Digital Control System (DCS) power to all three Main Feedwater Pumps (FWP), which was caused by the failure of Non-Safety Related Inverter XIT5905.
3952017006 | Summer 1 | 10/31/2017 | 12/15/2017 | ML17349A66 | <strong>Technical Specification Action Not Met for Inoperable Oxygen Monitor</strong><br /><i>Abstract:&nbsp;</i>At 0230 on October 30, 2017, VCSNS Unit 1 entered Technical Specification (TS) 3.3.3.9, Explosive Gas Monitoring Instrumentation, Action b. Entry into the TS action was a result of having one less than the minimum number of operable oxygen monitoring channels on the Waste Gas Holdup System Explosive Gas Monitoring System. TS Table 3.3-13, Line Item 1a requires a minimum of two operable channels for oxygen monitoring. When the number of operable monitoring channels is one less than required, the system can remain in operation, provided that grab samples are taken and analyzed at least once per 24 hours. <br /><br /> Upon entry into the TS action statement, the Control Room initiated station procedure GTP 702, General Test Procedure for Surveillance Activity Tracking and Triggering, and notified Chemistry of the grab sample requirements. The TS requirements were not adequately communicated to the oncoming personnel the following shift. As a result, the grab sample and analysis was not performed until 0405 on October 31, 2017 (after the 0230 requirement). The analysis was found to be satisfactory.<br /><br /> At the time of the event, Virgil C. Summer Nuclear Station (VCSNS) Unit 1 was operating in Mode 1 at 100% rated thermal power.
3972017001 | Columbia | 01/25/2017 | 03/20/2017 | ML17079A54 | <strong>Contactor Coil Failure Results in Tripping of HPCS Diesel Mixed Air Fan</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2017 at 1836 PST, smoke was detected in the High Pressure Core Spray (HPCS) System diesel room with no indication of a fire. Immediate recovery actions by Operations personnel included opening the disconnect for the affected motor starter, at which point the smoke dissipated, Investigation of the condition found the motor starter for the Diesel Mixed Air Fan had failed. Prior to the start of the event, the HPCS system had been declared inoperable in accordance with plant Technical Specifications for planned maintenance. <br /><br /> The apparent cause of the motor starter failure was overheating of the contactor coil due to elevated system voltages. Corrective actions for this event include replacement of the contactor coil, increased frequency of preventative maintenance, and procedure revision. There were no other event-related equipment malfunctions.
3972017002 | Columbia | 05/16/2017 | 07/10/2017 | ML17191B13 | <strong>Implementation of Enforcement Guidance Memorandum 11-003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this Licensee Event Report (LER) was an expected condition as a result of planned activities in support of a routine refueling outage. As described in the LER, the Nuclear Regulatory Commission (NRC) has provided enforcement guidance, applicable to boiling water reactors, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, this condition is considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> Between May 16, 2017 and June 15, 2017, Energy Northwest performed operations with the potential for draining the reactor vessel (OPDRV) activities while in Mode 5 without an operable secondary containment. Although this was an expected condition, and is allowed by Enforcement Guidance Memorandum 11-003, Revision 3, these activities resulted in a condition prohibited by Technical Specification 3.6.4.1. The OPDRV activities were planned and completed under the guidance of plant procedures and work instructions, and are considered to have low safety significance based on the interim actions taken. Since this condition was an expected result of these actions, cause determination is not necessary. Energy Northwest will submit a license amendment request to adopt Technical Specification Task Force Traveler 542 associated with generic resolution of this issue.
3972017003 | Columbia | 06/26/2017 | 08/24/2017 | ML17236A45 | <strong>Momentary Loss of Secondary Containment due to Weather</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2017 at 1756 PDT hours Secondary Containment pressure exceeded the Technical Specification (TS) limit during a period of inclement weather. At 1756 PDT Secondary Containment was declared inoperable and operations personnel entered TS Action Statement 3.6.4.1.A and subsequently exited at 1800 PDT. Secondary Containment pressure was restored automatically by system response and operator action was not required. <br /><br /> The direct cause of the momentary loss of Secondary Containment was due to slow system response to maintain a vacuum in Secondary Containment during a period of inclement weather. The interim planned corrective action is to verify proper operation and tuning of the Secondary Containment instrumentation. Additionally Columbia Generating Station is pursuing the change to TS requirements by adopting TSTF-551, Revise Secondary Containment Surveillance Requirements. <br /><br /> This condition is being reported under 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and to mitigate the consequences of an accident.
3972017004 | Columbia | 08/20/2017 | 10/17/2017 | ML17291A39 | <strong>Manual Reactor Scram due to High Main Condenser Back Pressure</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2017 at 1605 PDT, Columbia Generating Station was manually scrammed due to a rise in Main Condenser back pressure. The rise in back pressure was due to the spurious closure of the Main Condenser Air Removal Suction Valve (AR-V-1) as a result of the failure of it's associated solenoid pilot valve. Following the reactor scram and depressurization of the reactor a Level 3 actuation occurred. In addition a startup flow control valve failed which necessitated throttling of the Feedwater start-up level control isolation valve to control Reactor Pressure Vessel level. All other safety systems functioned as expected and all control rods were fully inserted. Reactor decay heat was removed via bypass valves to the main condenser.<br /><br /> The apparent cause was the plant modification to address the single point vulnerability of the closure of AR-V-1 was not implemented in time to prevent a plant shutdown. A temporary modification has been installed to maintain AR-V-1 open for the remainder of the operating cycle. <br /><br /> These events are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3972017005 | Columbia | 09/12/2017 | 11/09/2017 | ML17313A74 | <strong>Valve Closure Results in Momentary Increase in Secondary Containment Pressure</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2017 at 1227 PDT, Secondary Containment became inoperable due to pressure increasing above the Technical Specification limit of -0.25 inches of water gauge. While the plant was at 100% power, a Reactor Building exhaust valve and supply valve unexpectedly lost power and closed, resulting in a loss of Secondary Containment for approximately one minute. While Technical Specification limits were exceeded for this short time period, the resulting pressure excursion was bounded by analytical results; and thus, there were no safety consequences for this condition. This event was reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) as Event Notification #52966. <br /><br /> The apparent cause of the event was that station personnel did not deliberately and conservatively perform work tasks. Workers failed to update work instructions when work was rescheduled, and did not verify power sources at the work site. Corrective actions for this event include conducting a workshop on management expectations of Maintenance, increased management oversight, and addressing human performance issues.
3972017006 | Columbia | 09/21/2017 | 11/09/2017 | ML17313A93 | <strong>Condition Prohibited by Technical Specifications due to Incomplete Action Statement</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2017 at 0800 PDT, Columbia Generating Station declared number 2 Diesel Generator inoperable for maintenance and entered Technical Specification Action Statement (TSAS) 3.8.1, Condition B for One Required Diesel Generator inoperable. At 0821 PDT and again at 1537 PDT Surveillance Requirement 3.8.1.1 was performed per action statement B.1. At 2315 PDT it was noted by operations that a page was missing from the surveillance procedure for both occurrences and determined that the action statement was not met within the required action time. Operations entered TSAS 3.8.1, Condition F for Required Action and associated Completion Time of Condition B not being met. At 2321 PDT SR 3.8.1.1 was performed satisfactorily and Condition F was exited.<br /><br /> The apparent cause was a failure to page check the surveillance procedure prior to use. Initiatives have been developed to reinforce existing standards and improve human performance. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) Operation or Condition Prohibited by Technical Specifications.
3972017007 | Columbia | 10/03/2017 | 11/30/2017 | ML17334B44 | <strong>Valve Closure Results in Momentary Increase in Secondary Containment Pressure</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2017 at 0800 PDT, Secondary Containment (Reactor Building) became inoperable due to pressure increasing above the Technical Specification (TS) limit of -0.25 inches of water gauge (inwg). While the plant was at 100% power, a Reactor Building exhaust valve unexpectedly closed, resulting in a loss of Secondary Containment for approximately two minutes. Secondary Containment was declared inoperable and TS Action Statement 3.6.4.1.A was entered. The Control Room operators reopened the Reactor Building exhaust valve and pressure returned to within limits automatically. Secondary Containment was declared operable at 0810 PDT and TS Action Statement 3.6.4.1.A was exited. The event was reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72 (b)(3)(v)(D) as Event Notification #52999.<br /><br /> The apparent cause of the event is a surface degradation on the lower stab of an electrical disconnect causing a momentary high resistance when the cubicle door is opened. This event occurred during performance of thermography in the cubicle.
4102017001 | Nine Mile Point 2 | 08/05/2017 | 10/04/2017 | ML17296A15 | <strong>Automatic Reactor Scram due to High Reactor Pressure</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2017, at approximately 2235, the Nine Mile Point Unit 2 (NMP2) reactor scrammed on an automatic scram signal during performance of quarterly turbine stop valve surveillance testing. The automatic Reactor Protection System (RPS) actuation and reactor scram is reportable per 10 CFR 50.73(a)(2)(iv)(A). The definitive root cause of the equipment failure was not located but was bound to spurious actuation of load limit relays KL186 and KL187. The spurious action was caused by an intermittent ground and/or an induced voltage within the load limit circuit. This is a result of the non-fault tolerant original design of the Electro-hydraulic Control (EHC) system. The corrective action planned is replacement of the current single point vulnerable NMP2 Turbine EHC system with a fault tolerant Digital EHC system. Interim actions have also been developed to mitigate risk associated with testing of the current system until replacement can be accomplished during the 2018 refueling outage.
4102017002 | Nine Mile Point 2 | 09/30/2017 | 11/28/2017 | ML17346A74 | <strong>Secondary Containment Inoperable due to Wind Conditions</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2017 at 0134, Nine Mile Point Unit 2 declared Secondary Containment inoperable due to Secondary Containment vacuum decreasing below the technical specification limit. The condition is reportable under 10 CFR 50.72 (b)(3)(v)(C) and 10 CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The change in Secondary Containment vacuum was the result of changing wind conditions.<br /><br /> Secondary Containment was declared operable at 0135 when Secondary Containment vacuum was restored to greater than 0.25 inches of vacuum water gauge. <br /><br /> The event described in this LER is documented in the plant's corrective action program as IR# 04057558.
4122017001 | Beaver Valley 2 | 03/03/2017 | 05/02/2017 | ML17124A38 | <strong>Surveillance Testing Rendered Service Water System Inoperable due to the Coupling of Seismic Category 1 Piping to Not Seismic Category 1 Piping</strong><br /><i>Abstract:&nbsp;</i>A review of the current licensing basis revealed that intentionally coupling the Seismic Category I Service Water System (SWS) with the not Seismic CAT I Standby Service Water System (SWE)(KG) is a non-conformance with the current licensing basis, and renders the SWS inoperable. As a result, a review of the SWS Design Basis Accident (DBA) full flow surveillance test revealed that during the past three years performance, there were two trains of SWS concurrently inoperable for a time period, as logged, greater than the seven hour shutdown completion time required by Technical Specification 3.0.3. <br /><br /> This condition is reportable as an operation or condition which was prohibited by the plant's Technical Specifications under 10 CFR 50.73 (a)(2)(i)(B), and could have prevented the fulfillment of a safety function under 10 CFR 50.73(a)(2)(v)(B) for the SWS along with the systems that it supports of Emergency Core Cooling (ECCS), Primary Component Cooling Water System (CCP), and the Recirculation Spray System (RSS) . <br /><br /> The plant was not aligned to this configuration at the time of discovery, and all procedures have been revised to eliminate this condition.
4162017001 | Grand Gulf 1 | 01/27/2017 | 03/28/2017 | ML17087A13 | <strong>High Pressure Core Spray (HPCS) Jockey Pump Trip</strong><br /><i>Abstract:&nbsp;</i>At 1808 hours on 1/27/17, Grand Gulf Nuclear Station entered into LCO 3.5.1.6 when the High Pressure Core Spray (HPCS) Jockey Pump (Component Function Identifier- P) failed and the HPCS System was declared inoperable. The Reactor Core Isolation Cooling (RCIC) System was verified operable and investigation into the cause was initiated. Under those plant conditions the Plant Technical Specifications action to restore the HPCS System to operable status allows a 14 day completion time. <br /><br /> No other safety systems were inoperable at the time of this event. <br /><br /> The decision was made to disassemble the HPCS Jockey Pump and rebuild the pump using parts from the warehouse which was completed on 1/29/17. The pump was tested to demonstrate functionality of the pump on 1/29/17 and the system was returned to service.
4162017002 | Grand Gulf 1 | 02/28/2017 | 03/22/2018 | ML18081B21 | <strong>Loss of Secondary Containment and Inoperability of the Standby Gas Treatment Systems as a Result of a Damages Power Supply</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2017 the A Standby Gas Treatment System (SGTS) was not operating as expected. The investigation revealed the Single Nest Power Supply was damaged, resulting in loss of flow control. The power supply had been replaced on February 23, 2017. SGTS A was not run between replacement of the power supply and the time of discovery condition on March 24, 2017. Additionally, SGTS B was removed from service for planned maintenance on February 28, 2017, and returned to service on March 3, 2017. The cause of this event has been determined to be an inadequate design that allowed the standby gas treatment system filter train to not provide annunciation and indication upon power loss to the control room. The power supply was replaced and tested satisfactorily. Implementation of a design modification to ensure the standby gas treatment system filter train will provide annunciators/indication upon power loss to the control room. There were no actual nuclear safety consequences or radiological consequences.
4162017003 | Grand Gulf 1 | 04/04/2017 | 10/02/2018 | ML18275A41 | <strong>Reactor Shutdown Because of Condensate System Inventory Depletion and a Manual Reactor Core Isolation Cooling (RCIC) Initiation Because of Feedwater System Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 00:10 on, April 4, 2017, the reactor was manually shutdown from approximately 75 percent core thermal power due to condensate storage tank level lowering to 24 feet. All control rods fully inserted and all systems actuated and operated as designed. No safety relief valves actuated. Reactor level and pressure were controlled within normal bands. Reactor core isolation cooling (RCIC) was manually initiated for level control. Decay heat was removed via steam discharge to the condenser, and to the suppression pool via RCIC. The electrical grid was stable and supplying plant loads. The cause of the condensate depletion was a condensate system leak. <br /><br /> The condensate system leak was a failed pipe connection caused by cycling water injection valves that induced excessive vibration on the pipe flange. A failing Turbine Control Card caused the faulty signals; which led to the water injection valves cycling. The piping and flange connection were repaired, and the Turbine Control Card was replaced. In addition, the Turbine Control System is planned to be replaced in Refueling Outage 22 in 2020. <br /><br /> All other systems operated as designed, and there were no actual nuclear safety or radiological consequences during the event.
4162017004 | Grand Gulf 1 | 05/26/2017 | 12/18/2017 | ML17360A15 | <strong>Outside-of-Tech-Spec-Allowable-Value Automatic Depressurization System Initiation Timer Relay due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2017, while performing the Automatic Depressurization System (ADS) quarterly surveillance, the time delay on the Trip System A (Division 1) ADS initiation timer relay was found outside of its Technical Specification (TS) Allowable Value of </= to 115 seconds. Specifically, the ADS timer requirements in TS 3.3.5.1, Emergency Core Cooling System Instrumentation, Table 3.3.5.1-1, Emergency Core Cooling System Instrumentation, Function 4, Sub-function c. ADS Initiation Timer, Allowable Value was not met. The cause was determined to be inadequate preventive maintenance and review of the previous test results. This event is reportable as a license event report (LER) in accordance with 10CFR50.73(a)(2)(i)(B), as a "condition prohibited by Technical Specifications" because the same relay failed its previous test and could not be considered as OPERABLE during the full interval between tests. Corrective actions included replacement of the defective timer relay and planned actions to replace the corresponding timer relays in ADS and the Feedwater Control System. In addition, the applicable preventive maintenance procedures were revised. The event posed no threat to the health and safety of the general public or to nuclear safety as ADS would have performed as designed. No Technical Specification safety limits were challenged or violated.
4162017005 | Grand Gulf 1 | 07/09/2017 | 09/07/2017 | ML17250A20 | <strong>Loss of Safety Function and Control Room Envelope due to an Open Boundary Door</strong><br /><i>Abstract:&nbsp;</i>On July 9, 2017, at approximately 2158 hours central daylight time a pressure boundary door to the Control Room Envelope was left unsecure. The Control Room Envelope was inoperable for approximately one minute, at which time the door was closed. Grand Gulf Nuclear Station personnel identified that a loss of Safety Function occurred due to a breach in the Control Room Envelope resulting in inoperability of both divisions of Standby Fresh Air. This event is being reported under 10CFR 50.72(a)(2)(v)(D), as any event or condition that, at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The cause was determined to be that the organization failed to understand the nuclear safety consequence associated with a degraded condition of door SZ100C516 and failed to implement a mitigating strategy. Corrective actions included restoration of the door to operable status and coaching of the responsible individual. Future corrective action will include implementation of a maintenance strategy for control room pressure boundary doors to ensure reliable operation. There were no nuclear safety consequences or radiological consequences as a result of this event.
4162017006 | Grand Gulf 1 | 08/29/2017 | 11/16/2018 | ML18320A19 | <strong>Completion of Grand Gulf Nuclear Station Shutdown Required By Technical Specifications Because of an Inoperable A Residual Heat Removal Pump</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2017 at 2321 hours central daylight time, Grand Gulf Nuclear Station (GGNS) entered Technical Specification (TS) conditions for three Limiting Condition for Operations (LCOs) not met due to Residual Heat Removal 'A' system (RHR A) being declared inoperable. Entergy Operations Inc. (Entergy) made the decision to shut down the plant based on the results of troubleshooting performed on the RHR A pump. The A RHR pump TS differential pressure was out of specification (low) and could not be returned to acceptable limits. GGNS initiated plant shutdown as required by Technical Specifications 3.5.1, 3.6.1.7, and 3.6.2.3 at 1200 hours CDT on August 29, 2017, due to expected restoration of RHR A exceeding the completion time of 7 days prior to restoring Operability. The shutdown was completed and entry into MODE 3 occurred at 2217 hours CDT on August 29, 2017. <br /><br /> The direct cause of the event was increased surface roughness from corrosion in the Division I Residual Heat Removal Pump due to suppression pool water quality and lack of pump passivation. Corrective actions include replacement and successful testing of the pump, reanalysis of calculation limits, procedural upgrades, and the enhancement of pump management controls. This condition is reportable as a completion of a plant shutdown required by the TS.
4162017007 | Grand Gulf 1 | 12/12/2017 | 12/12/2018 | ML18346A39 | <strong>Engineered Safety Features System Actuations due to the Loss of Engineered Safety Features Transformer 11</strong><br /><i>Abstract:&nbsp;</i>At approximately 0918 hours on Tuesday, December 12, 2017, while operating in MODE 1 at approximately 18 percent power, the Grand Gulf Nuclear Station (GGNS) experienced a loss of the Engineered Safety Features (ESF) Transformer 11 which was powering the Division 1 ESF bus. Subsequently, the station experienced an automatic start of the Division 1 Emergency Diesel Generator and the partial isolation of the primary and secondary containment buildings. Both of these events were expected and as designed. The direct cause of ESF actuations was the loss of ESF Transformer 11. The cause of the transformer loss was due to a degraded cable with a zinc shield coming in contact with moisture. <br /><br /> Additionally, GGNS experienced an unrelated isolation of the Reactor Core Isolation Cooling System upon restoration of power. The isolation of the Reactor Core Isolation Cooling System did not result in a safety system functional failure.<br /><br /> This event is reportable to the NRC in accordance with 10 CFR 50.72(b)(3)(iv) and 10 CFR 50.73(a)(2)(iv)(A) as an event or condition resulting in a valid actuation of a ESF system.
4162017008 | Grand Gulf 1 | 03/06/2017 | 04/10/2018 | ML18100B30 | <strong>Inadequate Diesel Generator Common Mode Failure Evaluations Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2017 at 1216 hours CST, the Diesel Generator (DG) Jacket Water Cooler Shell-Side Vent Valve was found with a broken stem, and could not be operated. The Condition Report (CR) screened the Division II DG as Inoperable. However, Grand Gulf Nuclear Station (GGNS) personnel failed to add the CR to the Limited Condition of Operation (LCO) tracker and no extent of condition for common cause failure for the other DGs is evident. Since the common cause evaluation was not adequately completed and Surveillance 3.8.1.2 was not performed within 24 hours, the unit should have been placed in Mode 3 within 12 hours, as required by Technical Specification 3.8.1. Therefore, Grand Gulf Nuclear Station was in a condition prohibited by Technical Specifications. No other component or system failures contributed to the event. <br /><br /> The cause of the failure to document the common cause evaluation resulted from a lack of reinforcement of documentation standards, and training will be performed to close this gap in Senior Reactor Operator formality. <br /><br /> The safety significance of this event is very low, since the condition did not represent an actual loss of function of either Division I or Division II emergency diesel generators for greater than its Technical Specifications completion time and the Division II diesel generator was successfully performed during its subsequent monthly surveillance run.
4162017009 | Grand Gulf 1 | 12/12/2017 | 03/26/2018 | ML18085A07 | <strong>Reactor Core Isolation Cooling System Inoperability due to Lockout Circuit Settings</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2017, at approximately 0918 hours, Grand Gulf Nuclear Station (GGNS) was in MODE 1 and increasing power when the unit experienced an essential transformer (ESF-11) lockout. Concurrent with the lockout the Reactor Core Isolation Cooling (RCIC) system received a Division I isolation signal. <br /><br /> The cause of the RCIC isolation is determined to be installation of temperature switches in the RCIC isolation initiation circuits with unrecognized response times. <br /><br /> The power bus monitor time delay relays were adjusted from a one second delay to a 10-second delay to account for the response of the temperature switches. Additionally, a review of engineering change testing involving applicable temperature switch installations was performed to verify the post modification testing requirements of the Entergy testing philosophies are met. <br /><br /> There was no increase to any accident consequences, and no impact on plant safety or the safety of the public
4232017001 | Millstone 3 | 01/20/2017 | 03/20/2017 | ML17087A26 | <strong>Loss of Safety Function - Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>At 0835 on January 20, 2017 while operating in MODE 1 at 100% power, a door in the auxiliary building at Millstone Power Station Unit 3 failed to fully close following personnel passage due to the failure of the mechanical door closer mechanism. This door is part of the secondary containment boundary which must be intact for the supplemental leak collection release system to perform its safety function. Operators determined that the condition of the door rendered secondary containment inoperable and resulted in a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material and mitigate the consequences of an accident. The door was repaired and the door completely closed at 1256 on January 20, 2017. This condition is being reported under 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D).
4242017001 | Vogtle 1 | 02/03/2017 | 04/03/2017 | ML17093A60 | <strong>Manual Reactor Trip due to Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On February 03, 2017 at 1545 EST, Vogtle Unit 1 was operating in Mode 1 at 100 percent power when the Loop 1 Outboard Main Steam Isolation Valve (MSIV)[ISV], 1HV30066, began drifting closed due to hydraulic oil leak. Operating crew identified the issue and initiated a manual reactor trip due to the MSIV[ISV] drifting closed. All control rods fully inserted and all equipment actuated as designed. <br /><br /> Unit 1 was stabilized in Mode 3 with the heat sink being maintained by Auxiliary Feedwater (AFW)[BA] and through the Atmospheric Relief Valves (ARVs)[RV]. The Loop 1 MSIV[ISV] closing was caused by an o-ring failure that led to a loss of hydraulic oil used to maintain the MSIV[ISV] in the open position. This event had no adverse effect on the health and safety of the public, and is of very low safety significance. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv)(A) due to manual and automatic actuation of a systems listed in 10CFR50.739(a)(2)(iv)(B). Unit 2 was unaffected.
4242017002 | Vogtle 1 | 03/17/2017 | 06/29/2017 | ML17180A19 | <strong>Wiring Error Results in Automatic Actuation of a Safety System</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2017, at approximately 1517 EDT, during refueling operations on Unit 1, power was being restored to the Open Phase system for the 1-B Reserve Auxiliary Transformer (RAT). During restoration, a valid undervoltage actuation signal was sent to the 1-B Emergency Diesel Generator (EDG). The EDG automatically started and tied to the safety bus. This undervoltage condition was caused by a wiring error in the Open Phase system to the 1-B RAT. <br /><br /> Unit 1 was in Mode 6 at the time and remained so throughout the event. There was no change in the decay heat removal for the plant. <br /><br /> Because this event resulted in the automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B), this event is reportable under 10 CFR 50.73(a)(2)(iv)(A). This event had no adverse effect on the health and safety of the public, and is of very low safety significance.<br /><br /> Unit 2 was unaffected.
4252017001 | Vogtle 2 | 03/09/2017 | 06/29/2017 | ML17180A52 | <strong>Power Supply Failure Resulted in Operation in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Between January 16 and February 13, 2017, a power supply that supports operation of one of two ventilation supply fans for the 2A Emergency Diesel Generator (EDG) failed. Vogtle Electric Generating Plant (VEGP) Technical Specifications (TS), 3.8.3 Condition F requires restoration of the fan within 14 days or the EDG must be declared inoperable. This condition was not identified by operators because there is no failure indication. Therefore, the power supply was not repaired within the required time. The EDG should have been declared inoperable and TS 3.8.1. Condition B entered. Subsequently the completion time for TS 3.8.1 Condition B expired and the unit should have been shut down. This action was not taken and Unit 2 operated in a condition prohibited by TS. <br /><br /> Between February 13 and February 22, 2017, the second power supply failed on this EDG resulting in the second ventilation supply fan being inoperable. Since no failure indication is available, this condition was not identified by the operators. The TS 3.8.3 action for two power supplies inoperable is to immediately declare the EDG inoperable. Subsequently, the completion time expired and the unit operated in a condition prohibited by TS. During a monthly surveillance run on March 8, both power supplies were discovered failed. Both power supplies were replaced on March 9, 2017 and the EDG was declared operable.
4252017002 | Vogtle 2 | 09/26/2017 | 11/17/2017 | ML17321B05 | <strong>Valid Undervottage Condition Results in Automatic Actuation of a Safety System</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2017, at approximately 0543 EDT, while performing 2B Emergency Diesel Generator (EDG) and Emergency Safety Function Actuation System (ESFAS) testing, a valid undervoltage actuation signal was sent to the Unit 2 B-Train Emergency Diesel Generator. The 2B AC emergency bus (2BA03) was load shed, the 2B EDG automatically started, and tied to 2BA03. The 2BA03 bus was loaded by the automatic load sequencer. The actuation was identified by the Control Room operators and the 2B EDG was locally monitored while in service. An air leak on the shutdown logic board caused a non-emergency trip to actuate when the non-emergency trips were unblocked.<br /><br /> The reactor was in Mode 6 at the time of the event and not challenged throughout the event. <br /><br /> Decay heat removal and spent fuel pool cooling were not challenged throughout the event. <br /><br /> Because this event resulted in the automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B), this event is reportable under 10 CFR 50.73(a)(2)(iv)(A). This event had no adverse effect on the health and safety of the public, and is of very low safety significance. <br /><br /> Unit 1 was unaffected.
4402017001 | Perry | 03/17/2017 | 05/01/2017 | ML17123A04 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this LER is the result of planned activities in support of Refueling Outage 1R16 at the Perry Nuclear Power Plant (PNPP) In Enforcement Guidance Memorandum (EGM) 11-003 Revision 3, the NRC provided enforcement guidance, applicable to boiling water reactor licensees, that addresses the reported condition Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10CFR50 73(a)(2)(1)(B) as a condition prohibited by Technical Specifications From March 17, to March 24, 2017, PNPP conducted Operations with the Potential for Draining the Reactor Vessel (OPDRV) while in Mode 5 at zero percent power, without an operable Primary and Secondary Containment These activities were performed in accordance with the EGM 11-003, Revision 3, which allows the implementation of interim actions as an alternative to full compliance with Technical Specifications provided several conditions are met <br /><br /> The OPDRV activities were planned activities that were completed following the guidance of the EGM and are considered to have low safety significance based on the interim actions taken Since these actions were preplanned, no cause determination was necessary As required by the EGM, a license amendment request will be submitted, based on the Technical Specifications Task Force traveler associated with generic resolution of this issue, by December 20, 2017.
4402017002 | Perry | 04/30/2017 | 06/27/2017 | ML17179A20 | <strong>Loss of Safety Function due to Main Turbine Bypass Valve Opening</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2017, at 1818 hours, while the plant was at 100 percent rated thermal power, main turbine steam bypass valve number 1 partially opened. Power was subsequently lowered in an attempt to close the bypass valve. While lowering power the bypass valve would shut and then reopen and power would again be lowered. When power was lowered to approximately 74 percent the bypass valve remained closed. During the transient the reactor protection system (RPS) trip functions for the main turbine stop valve closure and turbine control valve fast closure scram were declared inoperable due to the opening of the bypass valve, which changes the bypass setpoint for those RPS trips. With the loss of RPS trip capability, a loss of safety function existed intermittently for approximately 37 minutes. The manual reactor trip function and other RPS functions remained operable. <br /><br /> Both channels of the rod withdrawal limiter (RWL) and the end of cycle reactor recirculation pump trip (EOC-RPT) function were also declared inoperable. These functions are credited in accident analysis and this also resulted in a loss of safety function in accordance with the plants Technical Specification bases. <br /><br /> The direct cause of the bypass valve opening was degradation of the Primary Low Value Gate (PLVG) card in the main turbine speed control circuit. <br /><br /> The safety significance of this event is considered to be small. This event is not considered a safety system functional failure as the specific functions were maintained and never bypassed during the event. This event is being reported under 50.73(a)(2)(v)(A) and 50.73(a)(2)(v)(D) for a loss of safety function.
4402017003 | Perry | 04/27/2017 | 06/26/2017 | ML17177A35 | <strong>Annulus Exhaust Gas Treatment System Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On April 27. 2017, at 0545 hours, with the plant in Mode 1 at 100 percent rated thermal power, while shifting Annulus Exhaust Gas Treatment System (AEGTS) from sub-system B to sub-system A, annulus differential pressure could not be maintained within the required system operating band, which caused an unplanned entry into technical specification limiting conditions of operation and a momentary loss of safety function. Sub-system B was inoperable while being shutdown to standby readiness in accordance with plant operating procedures and would not have automatically started in response to an actuation signal. Investigation determined that subsystem A was inoperable due to failed recirculation damper. Sub-system B was restarted at 0550 hours, to maintain annulus differential pressure. Annulus differential pressure was maintained above the minimum differential pressure throughout the event and the technical specification limiting conditions for operation were not exceeded. <br /><br /> The cause for the AEGTS sub-system A recirculation damper failure was a failure to follow procedure which resulted in the split coupling that connects the actuator to the damper not being properly tightened. The recirculation damper was repaired and AEGTS sub-system A was restored to operable status on April 28, 2017, at 2208 hours. The failure to follow procedure was addressed by the FENOC performance management process. <br /><br /> Since AEGTS is not a core damage mitigation system and does not mitigate large and early containment releases, the inoperability of the AEGTS is determined to be of small safety significance. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(C) and 10CFR50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function.
4402017004 | Perry | 08/08/2017 | 10/04/2017 | ML17278A06 | <strong>Loss of Safety Function for High Pressure Core Spray Suppression Pool Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On August 8, 2017, at 1554 hours, while the plant was at 100 percent rated thermal power, during restoration from testing of the High Pressure Core Spray (HPCS) Suppression Pool (SP) Level High Instrumentation, unexpected as-left indications were found that impacted both of the required channels of instrumentation. With both SP level instruments inoperable, a loss of safety function existed. <br /><br /> While venting the sensing line, the HPCS system was aligned to the suppression pool water source. This source of water is HPCS's safety-related source of water. The automatic suction swap on high suppression pool level is implicitly assumed in the accident and transient analysis since it assumes that the HPCS suction source is the suppression pool. Since the HPCS system was aligned to the suppression pool when the failure occurred, the assumptions of the accident analysis are met, and no safety system functional failure occurred. <br /><br /> The cause for the unexpected as-left indications is due to air entrained in the sensing line which came out of solution. <br /><br /> The safety significance of this event is considered to be small. This event is being reported under 50.73(a)(2)(v)(D) for a loss of safety function.
4402017005 | Perry | 08/14/2017 | 10/04/2017 | ML17278A07 | <strong>Controller Malfunction Results in Momentary Degradation of Secondary Containment Pressure</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2017 at 2257, with both trains of the Annulus Exhaust Gas Treatment System (AEGTS) running in parallel, Secondary Containment vacuum momentarily degraded to 0.52" water gauge when AEGTS B was shutdown to Standby Readiness. After an approximately 15 second delay, AEGTS A responded to maintain the proper vacuum. Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.1 requires a minimum of 0.66" water gauge differential pressure to be maintained between ambient and annulus pressure. The failure to comply with SR 3.6.4.1.1 caused Secondary Containment to be inoperable resulting in Technical Specification 3.6.4.1 not being met. <br /><br /> The cause was determined to be equipment age-related degradation of the AEGIS A controller circuit card, which was subsequently replaced. There were no other event-related equipment malfunctions. <br /><br /> Since AEGTS is not a core damage mitigation system and is not credited in the PRA model to mitigate large and early containment releases, the inoperability of the AEGTS is determined to be of small safety significance. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(C) and 10CFR50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function.
4402017006 | Perry | 10/04/2017 | 12/01/2017 | ML17335A06 | <strong>Loss of Safety Function due to the Inoperability of Both Trains of Motor Control Center Ventilation</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2017 at 0155 hours, while in Mode 1 at 100 percent rated thermal power, inoperability of both A and B trains of Motor Control Center, Switchgear, and Miscellaneous Electrical Equipment Areas Heating, Ventilation, and Air Conditioning System and Battery Rooms Exhaust System (M23/24) occurred. Train A was shutdown and declared inoperable based on excessive drive belt noise and belt malfunction. Train B was inoperable due to ongoing maintenance on its associated chilled water system. The combination of inoperability resulted in a loss of safety function. Technical Specification (TS) 3.0.3 was entered per plant procedures, and at 0250 hours a plant shutdown was commenced. At 0620 hours, the A train of M23/24 was declared operable following belt replacement and TS 3.0.3 was exited. The plant was restored to 100 percent rated thermal power at 0804 hours. <br /><br /> The cause was determined to be inadequate procedural guidance in that the "general tensioning" method described in plant maintenance procedure, V-belt and Sheave Maintenance, is insufficient for restoring components to a reliable condition. Corrective action includes revising the procedure for correct tensioning guidance.<br /><br /> The safety significance of this event is considered to be very small. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(B), 10CFR50.73(a)(2)(v)(C), and 10CFR50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function.
4402017007 | Perry | 12/22/2017 | 02/13/2018 | ML18045A05 | <strong>High Pressure Core Spray Inoperability due to System Leak</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2017 at 2348 hours, the High Pressure Core Spray (HPCS) system was declared inoperable due to a through-wall leak on the minimum flow line piping. The leak was on the outside bend of the first elbow downstream of the minimum flow restricting orifice and was leaking approximately 60 drops per minute. Technical Specification (TS) Limiting Condition of Operation (LCO) 3.5.1 Condition B was entered. The piping was repaired, the TS LCO exited, and HPCS was declared operable on December 25, 2017 at 2213 hours. <br /><br /> The cause was pipe wall loss due to a combination of cavitation and mechanical erosion wear. <br /><br /> The safety significance of this event is considered to be very small. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function.
4432017001 | Seabrook | 04/29/2017 | 06/28/2017 | ML17178A35 | <strong>Manual Reactor Trip in Response to a Feedwater Isolation due to High Level in Steam Generator 'B'</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2017 at 18:44, the Reactor was manually tripped by the operators at approximately 12% power in response to a feedwater isolation caused by High Steam Generator (SG) Level on the 'B' SG. The feedwater isolation signal P-14 was automatically actuated at 18:43 when the 'B' SG level reached the setpoint of 90.8% narrow range level. The plant was being started up following the major work performed for Refueling Outage 18. No adverse consequences resulted from this event. <br /><br /> Post-trip investigation revealed that FW-LT-502-V1L (the Variable leg pressure isolation for FW-LT-502) had not been restored to the required open position during routine instrument line filling and venting. On April 26, 2017, l&C performed backfilling of the reference legs on multiple steam generator level channels, including FW-LT-502, the 'B' SG wide range level instrument. FW-LT-502-V1L not being restored to the open position caused the 'B' SG wide range indication to respond slowly to level changes resulting in overfeeding the 'B' steam generator. The cause of the event was determined to be failure of the l&C technician to properly implement maintenance fundamentals during the performance of restoration of FW-LT-502. Individual performance was corrected. A contributing cause was determined to be improper characterization or SG level backfill activity as skill-of-the-craft. Planned corrective actions include development of a maintenance procedure to provide specific step-by-step instructions.
4462017001 | Comanche Peak 2 | 08/11/2017 | 03/22/2018 | ML18092A07 | <strong>Auxiliary Feedwater System Actuation During Unit 2 Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At 1124 Central Daylight Time on August 11, 2017, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 experienced an automatic Auxiliary Feedwater System actuation during a Turbine trip. The plant was stabilized at 3 percent reactor power with the Auxiliary Feedwater System feeding all Steam Generators with all levels within their normal bands. The cause of the Turbine trip was high water level in Steam Generator 2-02 related to the mechanical malfunction of a Steam Generator 2-02 flow control bypass valve. The valve malfunctioned due to a loose locknut on the valve hand wheel. Corrective actions included repair of the Steam Generator 2-02 flow control bypass valve. All times in this report are approximate and Central Daylight Time unless noted otherwise.
4462017002 | Comanche Peak 2 | 09/01/2017 | 10/27/2017 | ML17313A45 | <strong>Manual Reactor Trip due to Dropped Rods</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2017 CPNPP Unit 2 was manually tripped by Control Room Operators due to two dropped rods. All safety systems responded as designed including the automatic start of the Auxiliary Feedwater System. The proximate cause of the dropped rods was a high resistance condition on a single phase of a three phase fusible knife switch in a Rod Control System Power cabinet. Subsequent third party cause analysis was unable to determine the root cause of the high resistance condition. The defective switch was replaced. Additional corrective actions to avoid recurrence have been entered into the CPNPP Corrective Action Program. <br /><br /> All times below are in Central Standard Time (CDT). <br /><br /> I. DESCRIPTION OF THE REPORTABLE EVENT<br /><br /> At time 2140 [CDT] on September 1, 2017, CPNPP Unit 2 experienced two (2) dropped rods, one control, one shutdown. The reactor was then manually tripped. The Auxiliary Feedwater system automatically started as expected.
4462017003 | Comanche Peak 2 | 11/25/2017 | 01/22/2018 | ML18033A32 | <strong>Manual Reactor Trip due to Trip of Both Main Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2017 Comanche Peak, Unit 2 received alarms indicating a trip of both main feedwater pumps. After confirming a decreasing water level in all four steam generators, the control room initiated a manual reactor trip. All safety systems responded as designed including the automatic start of the auxiliary feedwater system. The cause of the trip of both main feedwater pumps could not be positively identified. Causal analysis indicates that a prior plant modification maintained power to abandoned relays in the Solid State Protection System that may have caused both main feedwater pumps to trip. Subsequent actions were taken to remove the fuses that provided power to the abandoned relays on both Unit 1 and Unit 2 to eliminate recurrence from this possible source. Additional corrective actions have been entered into the Comanche Peak Corrective Action Program. <br /><br /> All times below are in Central Standard Time (CST).
4542017001 | Byron 1 | 03/03/2017 | 04/25/2017 | ML17115A06 | <strong>Byron Station Unit 1 Volumetric and Surface Examinations of Reactor Pressure Vessel Head Penetration Nozzles Identify Indications Attributed to Primary Water Stress Corrosion Cracking and Minor Subsurface Void Enlargement from Operating Stresses</strong><br /><i>Abstract:&nbsp;</i>During the Byron Station, Unit 1, spring 2017, refueling outage, volumetric and surface examinations of the Reactor Vessel Head Penetration (VHP) nozzles identified recordable indications for VHP nozzles 31, 74, 76, and 77 that did not meet the applicable acceptance criteria. The unacceptable indications were identified and repaired prior to returning the reactor head to service. None of the indications were located in the Reactor Coolant System pressure boundary region. <br /><br /> The cause of the P-31 unacceptable indication is attributed to existing welding discontinuities/minor subsurface voids opening to the surface or enlarging due to thermal and/or pressure stresses during plant operation. The cause of the P-74, P-76 and P-77 unacceptable indications is attributed to Primary Water Stress Corrosion Cracking. The indication in penetration 31 was removed by manual buffing. <br /><br /> The indications in P-74, P-76 and P-77 were repaired by manual grinding with no welding required.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A) for any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
4582017001 | River Bend | 01/31/2017 | 04/03/2017 | ML17101A61 | <strong>Operations Prohibited by Technical Specifications (Conduct of Operations with a Potential to Drain the Reactor Vessel with Primary Containment Open)</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage that commenced on January 28, 2017, there were occasions during which maintenance was performed without taking the required actions to comply with the applicable Technical Specifications. Specifically, operations with a potential to drain the reactor vessel (OPDRVs) were conducted without establishing primary containment integrity, and the provisions of NRC Enforcement Guidance Memorandum (EGM) 11-003, Rev. 3, were invoked instead. The first such operation was commenced on January 31, and the final OPDRV was completed on March 4. This condition is being reported in accordance with 10 CFR 50.73(a)(2) (i)(B) as operations prohibited by Technical Specifications. During all OPDRVs, the prerequisites specified by the EGM were enforced. All activities were completed with no transients in reactor cavity water level having occurred. This event was, thus, of minimal safety significance with regard to the health and safety of the public. On December 20, 2016, NRC approved a generic Technical Specification amendment that can be used by licensees to reconcile this condition. It is required by the EGM that applicable licensees (including River Bend Station) must submit a request for this amendment by December 20, 2017.
4582017002 | River Bend | 02/18/2017 | 04/18/2017 | ML17116A29 | <strong>Loss of Safety Function of Onsite Electrical Distribution due to Malfunction of Control Building HVAC System</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2017, at 3:37 p.m. CST, while a refueling outage was in progress, the operators were shifting subsystems of the main control building ventilation system. The Division 2 "B" chiller had been in service, and it was intended to start the Division 1 "C" chiller to facilitate the outage work schedule. After the swap, operators noted that the air flow was abnormally low, and within approximately four minutes, the "C" chiller tripped. The operators were unsuccessful in attempts to restore the Division 2 subsystem to service and the abnormal operating procedures for the loss of control building ventilation were then implemented. The electrical distribution subsystems in the control building were declared inoperable due to the loss of the ventilation system. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(A). As described in the causal analysis, a circuit breaker manufacturing defect that violated the single failure requirements of 10 CFR 50 Appendix A, General Design Criteria, was discovered. This is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition. During the restoration of the ventilation system, main control room temperature increased from approximately 73F to 81F as recorded in the operator's logs. No high temperature alarms from the electrical equipment rooms actuated. Thus, this event was of minimal significance to the health and safety of the public.
4582017003 | River Bend | 03/10/2017 | 05/09/2017 | ML17136A27 | <strong>Manual Reactor Scram Initiated in Response to Increase in Steam Pressure During Steam Leak Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2017, at approximately 7:14 a.m. CST, the reactor operator manually actuated a reactor scram in response to an abnormal increase in steam pressure. Reactor power was approximately 15 percent at the time. The turbine generator had been synchronized to the grid at 5:13 a.m. on March 10, and was being closely monitored by engineers and operators since a major modification to the turbine electro-hydraulic control (EHC) system had been installed during the recent refueling outage. Approximately 45 minutes prior to the manual scram, a main control room alarm actuated indicating a problem with the EHC system. A few minutes later, it was reported from the turbine building that there was a steam leak in the area of the EHC steam pressure transmitters. Shortly thereafter, reactor pressure began to increase with no demand signal present, at which time the reactor operator initiated the scram. The main feedwater system remained in service, and reactor water level control performed normally as designed. No reactor safety-relief valves actuated. The main turbine bypass valves did not open following the shutdown, and engineering review determined this condition was consistent with the response to the abnormal configuration of the EHC system pressure transmitters created by efforts to isolate the leak locally. Approximately five minutes after the scram, the outboard main steam isolation valves were manually closed to limit the reactor cooldown rate. This event resulted from the incorrect installation of a new compression fitting in the steam pressure instrumentation tubing for the main turbine control system. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of the reactor protection system.
4582017004 | River Bend | 03/23/2017 | 03/15/2018 | ML18081A02 | <strong>Loss of High Pressure Core Spray Safety Function During Surveillance due to Malfunction of Test Return Valve</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2017, at 0028 CDT, with the plant operating at 100 percent power, the high pressure core spray system (HPCS) was declared inoperable due to a malfunction of a motor-operated valve (MOV) in the system. During a scheduled test, the HPCS pump test return valve to the suppression pool was given a "close" signal after having been opened for the test. The valve position lights indicated that it fully closed, but system flow parameters did not respond as expected. An operator went to the valve and reported that it appeared that the anti-rotation device on the valve actuator had failed, and that the valve was not fully closed. This valve is a primary containment isolation valve. An examination of the MOV found that a set screw on the actuator had loosened, allowing the anti-rotation device to slip down the valve stem. When the anti-rotation device slipped far enough, the retainer keys fell out, allowing the valve stem to disengage from the anti-rotation device. The maintenance history of the valve was investigated, and it was found that in 1996, the anti-rotation device was loosened during a scheduled maintenance task. A review of the work documentation package and the vendor manual found that no torque value was specified for the set screw. The Flowserve Vendor was contacted and recommended the set screw be torqued to 60 ft.-lbs. IAW Entergy procedure EN-MA-145, MAINTENANCE STANDARD FOR TORQUE APPLICATIONS. This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v) as a potential loss of safety function of the HPCS system and the primary containment isolation function. An evaluation of the as-found condition has concluded that the HPCS system and primary containment isolation would have been able to perform their design safety function had an actual design basis event occurred during the test.
4582017005 | River Bend | 04/05/2017 | 06/05/2017 | ML17156A61 | <strong>Operations Prohibited by Technical Specifications due to Inoperable Main Control Room Filter Train</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2017, during a scheduled surveillance test, it was discovered that the Division 1 main control room ventilation filter train was inoperable due to the flow rate being below the lower limit. The initial investigation found that a manually-operated damper in the flow path for that filter train was not correctly positioned. Work documents from the recent refueling outage that started on January 28 were reviewed, and it was found that the damper had been closed as part of establishing a system configuration needed for repairs to other dampers. It was concluded that the as-left condition of the damper after restoration from the maintenance was such that it vibrated in the closed direction upon the first start of the filter train fan, and that the filter train had thus been inoperable since the return to service on February 26, 2017. The plant was restarted at the end of the refueling outage on March 8. On March 10, an unplanned manual reactor scram was initiated due to a steam leak in the turbine building. The leak was repaired and the plant was restarted on March 11. Since the filter train was inoperable on both occasions, those mode changes were made in violation of Technical Specifications. The investigation of this event also found that during one 8-minute period when the Division 1 filter train was inoperable, the Division 2 main control room fresh air system was inoperable for planned testing. This event was caused by the lack of any instructions provided for the restoration of the Division 1 subsystem that directed the torqueing of the damper locking mechanism.
4582017006 | River Bend | 05/15/2017 | 07/13/2017 | ML17200C93 | <strong>Potential Loss of Safety Function of Onsite Power Sources due to Inadvertent Inoperability of Control Building Chiller</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2017, an engineering investigation determined that a modification installed in 2014 on two of the four safety-related main control building chillers had a design error. The nature of that error was such that the performance of a regularly scheduled preventative maintenance (PM) task to draw an oil sample from the chiller gearbox inadvertently caused the chiller to be incapable of responding to an automatic start signal. A review of the history of the PM found that, on three occasions since the modification was installed, the task was performed on the operable chiller that was in the standby condition. The inadvertent inoperability of the standby division of the main control building chillers causes the loss of safety function of the supported electrical distribution systems in the building. The control building chilled water system provides cooling to the equipment rooms housing the battery chargers and inverters for the safety-related onsite electrical distribution systems. The loss of cooling to the various equipment rooms in the control building requires that the supported equipment in those areas be declared inoperable. The Technical Specifications for the Division 3 DC distribution system requires that the high pressure core spray (HPCS) system be immediately declared inoperable. This condition potentially causes the HPCS system to be incapable of performing its safety function, and is, thus, reportable in accordance with 10 CFR 50.73(a)(2)(v)(D). The error in the subject modification is considered a legacy issue since its design was completed and approved in July 2012. The PM task will be revised to preclude its performance on chillers in the standby configuration. At no time during the three performances of the PM on the operable standby chiller was there an actual demand for its automatic start. This condition was, thus, of minimal significance with respect to the health and safety of the public.
4582017007 | River Bend | 06/23/2017 | 08/21/2017 | ML17234A33 | <strong>Automatic Reactor Scram due to Failure of Main Generator Voltage Regulator Mode Transfer Relay</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2017, at 10:18 PM CDT, an unanticipated reactor scram occurred during scheduled testing of the main turbine generator. The plant was operating at 100 percent power at the time, and no safety-related equipment was out of service. A reactor recirculation system flow control valve runback occurred as designed, and the recirculation pumps properly downshifted to slow speed. The main feedwater system responded properly to control reactor water level. The scram signal was initiated by the closure of the main turbine control valves, which was an automatic response to a trip of the main generator. The associated steam pressure increase following turbine valve closure resulted in the actuation of 12 main steam safety-relief valves. A reactor water level 3 signal was received, as expected, following the turbine trip and reactor scram and was promptly restored to the normal reactor water level band. The non-safety related turbine building chillers tripped as a result of the electrical transient caused by the generator trip. One area served by that cooling system is the reactor water cleanup (RWCU) system heat exchanger room. Approximately 20 minutes after the scram, the temperature in that room exceeded the trip setpoint of the area temperature monitors, resulting in the automatic closure of the primary containment isolation valves for the RWCU system.
4582017008 | River Bend | 08/18/2017 | 10/12/2017 | ML18039A10 | <strong>Automatic Reactor Scram due to Failure of Main Feedwater Regulator Transfer Relay</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2017, at 8:55 p.m. CDT, an automatic reactor scram occurred while the plant was operating at 100 percent power. The operators promptly established control of reactor water level and pressure, and a controlled plant cooldown was commenced. The initial scram signal was a flow-biased thermal power trip on the average power range monitors. This action closely followed a planned shift of the master feedwater controller from channel "B" to channel "A." Troubleshooting discovered that the feedwater level channel select relay had failed such that no signal was present on the "A" channel. When that channel was selected, the feedwater system erroneously sensed that reactor water level was low, and caused all three feedwater regulating valves to move fully open. At the same time, the false low water level signal was sensed in the control circuitry for the reactor recirculation system, resulting in an automatic shift of the recirculation pumps to slow speed. The resultant decrease in core flow caused the flow-biased thermal power trip in the average power range monitors, actuating the reactor scram. The failed feedwater system relay was replaced with an updated model with gold contacts. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an event resulting in the automatic actuation of the reactor protection system.
4582017009 | River Bend | 09/27/2017 | 11/13/2017 | ML17325A99 | <strong>Potential Loss of Safety Function of Secondary Containment due to Unsecured Personnel Door</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2017, at approximately 10:00 a.m. CDT, with the plant operating at 85 percent power, a door in the auxiliary building pressure boundary was left unsecured by an employee entering the building. The employee failed to fully close the door, and then did not properly challenge the door to confirm its security prior to leaving the area. A security officer responded to the resulting alarm, and fully closed the door approximately four minutes later. Since the worker had sufficient experience with watertight doors to know their proper operation, this event is considered a skill-based error caused by over-confidence and improper assumptions. Having successfully used such doors numerous times, the worker was confident in the ability to do so. The effort to check the door's security by pushing it failed, likely due to its heavy mass. A briefing memorandum was issued from the general manager to site personnel. Tamper alarms were installed on all watertight doors in the secondary containment boundary to provide an audible indication that the door is open. Administrative controls have been instituted to schedule routine battery replacements.
4612017001 | Clinton 1 | 02/24/2017 | 04/21/2017 | ML17114A47 | <strong>Failure of the 138 kV Offsite Power Source Results in a Loss of Secondary Containment Vacuum</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2017 at approximately 2239 hours (CDT), the Main Control Room (MCR) received numerous annunciators which indicated a loss of the 138 kV off-site supply to the Emergency Reserve Auxiliary Transformer (ERAT). The MCR entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Actions A.1 and A.2. The Division 1 Fuel Building ventilation (VF) system isolation dampers closed due to the voltage transient causing a trip of the VF supply and exhaust fans and Secondary Containment (SC) vacuum to rise to slightly greater than 0 inches water gauge (WG), exceeding the TS requirement of greater than 0.25 inches vacuum WG. The MCR entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control, and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. SC vacuum was restored within TS requirements at approximately 2242 hours by starting the Standby Gas Treatment (VG) system. The Transmission System Operator confirmed that the loss of the 138 kV line was due to a line fault external to the Station. The 138 kV line was successfully re-energized at 0053 hours on February 25, 2017 and the ERAT off-site source was restored and declared OPERABLE at 0300 hours. This event is reportable per 10CFR50.73(a)(2)(v)(C).
4612017002 | Clinton 1 | 03/09/2017 | 07/16/2018 | ML18199A10 | <strong>Failure of the Division 1 Diesel Generator Ventilation Fan Load Sequence Relay Circuit During Concurrent Maintenance of RHR Division 2 Results in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, March 7, 2017 at 2258 CDT, an Equipment Operator detected a relay cycling every 10 seconds from the Division (Div.) 1 480V Unit Substation (Sub) 1A. Agastat Time Delay Relay (TDR) 427X2-41A (X2 relay) was determined to be the source of the clicking sound. The X2 relay supports the undervoltage load shed and restoration of the Div. 1 Emergency Diesel Generator (EDG) ventilation room fan 1VD01CA. The logic is designed to shed 1VD01CA on undervoltage, prevent it from restarting, then allow it to be restored 10 seconds after voltage is restored either by the EDG or return of the safety bus. An investigation of the relay cycling condition determined that 1VD01CA was unable to respond to a demand signal and the cycling was the effect of interaction between the X2 and 427X3-41A (X3) relays. As a result, Div. 1 EDG was declared inoperable on March 9. With the Div. 2 Residual Heat Removal (RHR) System already inoperable due to scheduled maintenance, the plant was determined to be in an unanalyzed condition. A causal analysis determined that the original design of the EDG ventilation fan relay logic relied on executing parallel sequencing logic to perform the control function, which was vulnerable to differences in relay model drop out voltages. Corrective actions included the replacement of the X3 relay with the original design relay and subsequent circuit modifications to eliminate the vulnerability to lower drop out voltage settings. Div. 2 RHR was returned to service on March 8. Subsequently, Div. 1 EDG was restored to OPERABLE on March 11. This is reportable as an unanalyzed condition, operation prohibited by the Technical Specifications and a loss of safety function.
4612017003 | Clinton 1 | 05/09/2017 | 07/03/2017 | ML17188A38 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11 - 003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this LER is the result of planned activities in support of Refueling Outage C1 R17 at Clinton Power Station (CPS). As described in the LER, the NRC provided enforcement guidance, applicable to boiling water reactor licensees, that addresses the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). On May 9 through May 28, 2017 CPS performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities while in Mode 5 without an operable Secondary Containment. These activities were performed within the guidelines of NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 which allows the implementation of interim actions as an alternative to full compliance, provided several conditions are met. The OPDRV activities were planned activities that were completed following the guidance of the EGM and are considered to have low safety significance based on interim actions taken. Since these actions were preplanned, no cause determination was necessary. As required by the EGM, a license amendment request was submitted on May 1, 2017 which follows the guidance in Technical Specifications Task Force traveler TSTF-542 which is the agreed-upon generic resolution of this issue.
4612017004 | Clinton 1 | 05/12/2017 | 11/22/2017 | ML17331A47 | <strong>Main Steam Isolation Valve Local Leak Rate Test Limit Exceeded During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>During the Clinton Power Station (CPS) Refueling Outage (C1 R17) on May 12, 2017 at 0045 [CDT], CPS tested its Main Steam Isolation Valves (MSIV) and discovered the as-found leakage for main steam line (MSL) 'D' exceeded the Technical Specifications (TS) 3.6.1.3, Primary Containment Isolation Valves, Surveillance Requirement (SR) 3.6.1.3.9 limit placed on an individual MSL and total leakage from all four MSLs. During Modes 1, 2, and 3, TS SR 3.6.1.3.9 requires MSIV leakage for a single MSL to be less than or equal to 100 standard cubic feet per hour (scfh) (47,195 standard cubic centimeters per minute (sccm)) and requires the combined leakage rate for all MSLs to be less than or equal to 200 scfh (94,390 sccm) when tested at 9 psig. The as-found leakage for the 'D' MSL was 53,921.61 sccm for the 'D' inboard MSIV (1B21F022D) and 59,698.8 sccm for the 'D' outboard MSIV (1B21F028D). The as-found combined min-path leakage for all four MSLs was 102,463 sccm. An event investigation determined the as found condition of MSIVs 1B21F022D and 1B21F028D did not reveal any damage, only normal wear indications. Thus, the apparent cause for the excessive leakage past all affected MSIVs is expected wear. Valves 1621F028A, 1B21F022D, and 1B21F028D were repaired so that as-left leakage values complied with limits established by TS SR 3.6.1.3.9. This event is reportable due to principle plant safety barriers being seriously degraded, under the provisions of 10 CFR 50.73(a)(2)(ii)(A) and a condition prohibited by TS under 10CFR50.73(a)(2)(i)(B).
4612017005 | Clinton 1 | 05/30/2017 | 09/28/2017 | ML17275A17 | <strong>Automatic Reactor Scram During the Performance of Scram Time Testing as a Result of an Invalid Oscillation Power Range Monitor Growth Rate Trip</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2017 at 2038 CDT, with the reactor at approximately 28% thermal power Clinton Power Station (CPS) experienced an automatic reactor scram while conducting scram time testing (STT). Plant systems responded as expected and functioned properly following the automatic scram. The automatic scram signal was generated by the Oscillation Power Range Monitor (OPRM) Growth Rate Algorithm (GRA). An evaluation confirmed that the reactor was operating in a very stable core condition and that the event did not occur due to an actual core thermal hydraulic instability. The cause of the event was that the OPRM GRA trip function design is unable to distinguish between plant response to system perturbations and onset of thermal-hydraulic instabilities. Interim actions were implemented to increase operating margin to trip setpoints to support reactor startup and completion of STT. They included a revision to a plant procedure to establish an operating strategy when performing STT in the OPRM enabled region, implementing a monitoring strategy to assess the effectiveness of the operating strategy and monitoring for expected plant response, and raising OPRM Amplitude and GRA set points. Planned corrective actions include working with the industry, as needed, to develop and implement an industry solution for the design of the OPRM GRA to prevent false, spurious trip signals. The automatic scram is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system.
4612017006 | Clinton 1 | 06/02/2017 | 08/01/2017 | ML17215A23 | <strong>Secondary Containment Inoperable During Mode Change due to Doors Propped Open</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2017, plant personnel were performing welding activities on the 'B' Reactor Water Cleanup System (RT) pump while the plant was in operating Mode 4. The Operations Work Control Supervisor (WCS) had given maintenance personnel authorization to prop both 'B' RT pump room doors open so that welding cables could extend through both doors in support of maintenance activities. The doors are part of the plant secondary containment boundary. Authorization granted by the WCS was executed without utilizing the plant barrier impairment process (PBI) per plant procedures. Prior to the plant's transition to operating Mode 2, Operations personnel made a plant announcement requiring the establishment of primary and secondary containment. The plant then transitioned to operating Mode 2 at 0241. However, both RT Pump 'B' doors remained propped open during the plant mode change. This condition was discovered by shift personnel at 0300 (CDT) and secondary containment was declared inoperable. The loss of secondary containment was caused by personnel not following the PBI per plant procedure. Secondary containment was subsequently restored twenty four minutes after discovery of the open 'B' RT doors. Corrective actions taken and planned include implementing management action response checklist (MARC) principles for the responsible supervisor and completing a read and sign for planners and schedulers associated with the PBI process.
4612017007 | Clinton 1 | 06/10/2017 | 04/05/2018 | ML18099A06 | <strong>Manual Reactor SCRAM due to Loss of Feedwater Heating</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2017, at 2256 CDT, Clinton Power Station (CPS) experienced a complete loss of the 'A' feedwater (FW) heater string. The operators received numerous FW trouble alarms on FW string 'A' and low pressure heater 1A/1B bypass opened (1CB004). The operators entered procedure CPS 4005.01, "Loss of FW Heating," which directs the operators to restore and maintain power at or below the original power level. The operators lowered core flow and inserted all CRAM rods, and then observed that FW temperature had dropped greater than 100°F. As directed by CPS 4005.01, at 2306 hours the reactor mode switch was placed into the shutdown position and Procedure 4100.01, "Reactor Scram," was entered. All systems operated as expected following the scram. At 0100 EDT on June 11, 2017, Event Notification 52800 was made. The loss of FW heating transient was caused by a loss of power to Moore trip units caused by a shorted condition on the Moore trip unit associated with the Hi-Hi level in the 4A FW heater. The root cause is that the design of the FW heater level control trip circuitry was not adequate to prevent scrams due to an unevaluated single point vulnerability. Prior to startup, CPS modified the circuit card locations and thereby diversified the power supplies so that the trip units have less dependency on common fuses. Additional corrective actions include performing an engineering evaluation to determine if there are additional single component failures, operator errors, or events for the FW heating system that could result in a drop in FW temperature of greater than 100°F.
4612017008 | Clinton 1 | 06/15/2017 | 12/18/2018 | ML18354A73 | <strong>Division 3 Shutdown Service Water Pump Start Failure</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2017, Clinton Power Station (CPS) commenced procedure CPS 9069.01, Shutdown Service Water Operability Test. The purpose of this procedure is to verify operability of the Division 3 Shutdown Service Water (SX) System Pump 1SX01PC and selected valves per the Inservice Testing program on a quarterly basis. At 0958, SX pump 1SX01PC was started and after approximately 30 seconds, it tripped due to thermal overload. The pump was declared inoperable and Operations entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.7.2, Condition A which requires the High Pressure Core Spray (HPCS) system to be declared inoperable and enter TS LCO 3.5.1 Condition B which requires verification by administrative means that the Reactor Core Isolation Cooling (RCIC) system is operable and within 14 days restore the HPCS system to operable status. The cause of the event was an incremental increase in internal pump resistance that could not be overcome by the developed torque of the motor starting from standby conditions. This increased pump resistance was due to unidentified impacts during a design modification (i.e., dry packing at pump start, unidentified corrosion effects on packing shaft sleeve, and inadequate hard-face material). Another root cause was the untimely implementation of a corrective action that resulted from a 2014 causal evaluation due to inadequate procedure guidance. Corrective actions have been completed to restore operability of 1SX01PC and ensure failure mechanisms introduced by design changes have been assessed. This event is reportable under 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfilment of a safety function and 10 CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
4612017009 | Clinton 1 | 11/05/2017 | 01/04/2018 | ML18008A06 | <strong>Trip of Emergency Reserve Auxiliary Transformer Static VAR Compensator Causes Positive Secondary Containment Pressure Following Voltage Transient on 138 kV Offsite Source</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2017, at approximately 1240 CDT, the Main Control Room (MCR) received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) caused by a voltage transient on the 138 kV offsite supply. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Action A.1 and A.2 were entered. As a result of the voltage transient, the Division 1 Fuel Building ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no operating VF fans, Secondary Containment (SC) vacuum rose to slightly greater than 0 inches water gauge (WG) at 1241 CDT which exceeded the TS requirement of greater than 0.25 inches vacuum WG. The MCR entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. The cause of the SC differential pressure becoming positive is that the circuit design of VF is not adequately robust to withstand loss of the 138 kV feed. At the time, the Division 1 safety bus was being fed from the ERAT. Secondary Containment vacuum was restored within TS requirements at 1242 CDT by starting the Standby Gas Treatment System. A modification will be installed to prevent tripping VF during a momentary loss of power. Installation of a 138 kV Ring Bus is scheduled that is intended to improve the reliability of the radial feed of the 138 kV line. This event is being reported as a condition that could have prevented fulfillment of a safety function under 10 CFR 50.73(a)(2)(v)(C).
4612017010 | Clinton 1 | 12/09/2017 | 01/17/2019 | ML19022A26 | <strong>Division 1 Transformer Failure Leads to Instrument Air Isolation to Containment Requiring a Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2017 at 1347 CDT the Main Control Room received annunciators that indicated a trip of a 4160V 1A1 Breaker (1AP07EJ), 480V transformer 1A and A1 feed breaker. The loss of Division 1 480V power caused the Instrument Air (IA) containment isolation valves to fail close as designed. The loss of IA affected various containment loads, including the scram pilot air header and containment isolation valves. Another consequence of this event was that secondary containment (SC) vacuum was not maintained within Technical Specification (TS) limits due to Fuel Building ventilation dampers failing closed by design due to the loss of power. In addition, this event resulted in the inoperability of the Low Pressure Core Spray System (a single train safety system) and inoperability of primary containment due to primary to secondary containment differential pressure being outside TS limits. Operations entered Emergency Operating Procedure (EOP) -08, Secondary Containment Control. Division 2 Standby Gas Treatment System was activated at 1350 and restored SC vacuum within allowable TS values at 1351 and the EOP was exited. Due to the loss of IA, a manual reactor scram was inserted at 1353 when two control rods began drifting in as expected. A phase to ground fault was identified on 480V transformer 1A (1AP11E). On December 14, 2017, the 480V transformer was replaced and the plant returned to Mode 1 operations on December 15, 2017. The condition described in this report was determined to be reportable under 10 CFR50.73(a)(2)(iv)(A), 10 CFR 50.73(a)(2)(v)(C), 10 CFR 50.73 (a)(2)(ii)(B) and 10 CFR 50.73 (a)(2)(v)(D). Based on analyses performed at vendor test facilities following the event, the cause of the transformer failure was determined to be excessive layer to layer design stress within the 4160V winding. The identification of a pre-existing design defect during the cause analysis also resulted in the issuance a 10 CFR Part 21 notification to the NRC. This event is classified as an unplanned scram with complications due to the loss of Div. 1 480 power.
4822017001 | Wolf Creek | 03/22/2017 | 05/17/2017 | ML17143A23 | <strong>Condition Prohibited by Technical Specifications due to One Train of Component Cooling Water Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2017, with the plant in Mode 1, a work activity isolated the emergency makeup from the Essential Service Water (ESW) to the "A" Train Component Cooling Water (CCW). An individual questioned whether the "A" Train CCW was operable in this configuration. Technical Specification (TS) 3.7.7 requires two CCW trains to be operable in Modes 1 through 4. <br /><br /> It was determined that the "A" train CCW was inoperable when emergency makeup from ESW was isolated and that the allowed outage time was exceeded. The cause of the event was that adequate information was not incorporated into TS Bases 3.7.7, stating that emergency makeup from ESW is required to maintain a CCW train operable.
4822017002 | Wolf Creek | 04/05/2017 | 05/31/2017 | ML17158B34 | <strong>Tornado Missile Vulnerabilities Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2017, Wolf Creek Generating Station (WCGS) was in Mode 1 at 100 percent power. During evaluation of protection for safety-related equipment from the damaging effects of tornados, WCGS personnel determined that safety-related fuel oil transfer lines inside the Diesel Generator Building could be damaged if tornado generated missiles struck the non-safety related truck connections to these transfer lines. As these safety-related transfer lines are required to supply fuel to the Emergency Diesel Generators (EDGs) from the fuel oil storage tank, Operations declared both of the EDGs inoperable. On April 5, 2017, at 1632 Central Daylight Time, an 8- hour, non-emergency report to the Nuclear Regulatory Commission (NRC) (reference NRC Event Notification Number 52666) was made in accordance with 10 CFR 50.72. Compensatory measures were implemented consistent with Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance." The EDGs were then declared operable but non-conforming.<br /><br /> These tornado missile vulnerabilities existed since the original plant construction. Immediate compensatory measures included verification that the severe weather procedures were up-to-date, ensuring that Operations personnel were current on their training to these procedures, and implementing measures to heighten station awareness until the vulnerabilities had been corrected. These vulnerabilities have now been permanently eliminated.
4822017003 | Wolf Creek | 09/07/2017 | 11/02/2017 | ML17317A46 | <strong>ARV and MSSV Tornado Missile Vulnerabilities Result in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2017, Wolf Creek Generating Station (WCGS) was in Mode 1 at 100 percent power. During evaluation of protection for safety-related equipment from the damaging effects of tornados, WCGS personnel determined that the non safety-related exhaust lines from safety-related atmospheric relief valves (ARVs) and main steam safety valves (MSSVs) could be crimped by tornado generated missiles. If these are crimped completely, these components may be unable to perform their safety functions. The ARVs and MSSVs were declared inoperable and Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," Revision 1 was applied. Immediate compensatory measures consistent with EGM 15-002 were implemented within the time allowed by the applicable Technical Specification Limiting Condition(s) for Operation. The ARVs and MSSVs were subsequently declared operable but nonconforming. These tornado missile vulnerabilities existed since the original plant construction. Actions will be taken to establish compliance for these components either by a plant modification or employing a methodology for addressing tornado missile non-conformances. <br /><br /> On April 5, 2017, WCGS personnel provided a 10 CFR 50.72 notification in Event Notification (EN) 52666 concerning tornado missile protection issues known at that time. As stated in EGM 15-002, the NRC will exercise enforcement discretion for subsequent tornado missile 10 CFR 50.72 notifications. Therefore, no 10 CFR 50.72 notification was made for this condition.
4832017001 | Callaway | 06/16/2017 | 03/01/2018 | ML18060A40 | <strong>Violation of Technical Specification 3.7.9 due to Ultimate Heat Sink (UHS) Cooling Tower Train Inoperability</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2 017, with the plant in Mode 1 and 100% reactor power, the 'A' Ultimate Heat Sink (UHS) Cooling Tower Fan was operating in fast-speed to cool the UHS retention pond. The fan spuriously tripped after 44 minutes of operation. The most probable cause of the spurious trip was a defective fast-speed thermal overload relay that had been installed as a replacement during recent preventative maintenance activities. <br /><br /> In Mode 1, Technical Specifications require each of two redundant UHS cooling tower trains to be capable of dissipating the heat contained in the Essential Service Water (ESW) system. An inoperable UHS cooling tower fan renders its UHS cooling tower train inoperable. Review determined that the fan was inoperable from the start of the preventative maintenance task, and existed for a duration of 96 hours and 23 minutes while the plant was in Mode 1. Consequently , it was concluded that the 'A' UHS Cooling Tower Train had been inoperable for a period of time longer than allowed by the plant's Technical Specifications. <br /><br /> For corrective action, maintenance procedures have been revised to include additional pre-installation testing of similar thermal overload relays to ensure that defects similar to the one that caused the reported failure are detected prior to installation in the plant.
4832017002 | Callaway | 08/15/2017 | 03/01/2018 | ML18060A40 | <strong>Tornado Missile Vulnerabilities Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2017, Callaway Plant was in Mode 1 at 100 percent power. During evaluation of protection for safety-related equipment from the damaging effects of tornados, Callaway Plant personnel determined that safety-related minimum-flow recirculation lines for the turbine-driven auxiliary feedwater pump (TDAFP) and both motor-driven auxiliary feedwater pumps (MDAFPs) could be damaged in the event that a postulated tornado generated missile were to penetrate a structure that is not resistant to tornado missiles (i.e., the condensate storage tank (CST) valve house) and strike the lines. Operations declared all three auxiliary feedwater pumps inoperable . On August 15, 2017, at 1407 Eastern Daylight Time (EDT), an 8-hour, non-emergency report to the Nuclear Regulatory Commission (NRC) (reference NRC Event Notification Number 52905) was made in accordance with 10 CFR 50.72. Compensatory measures were implemented consistent with Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance." The TDAFP and MDAFPs were then declared Operable but non-conforming. <br /><br /> Subsequent to the condition identified on August 15, 2017, continued investigation of tornado missile vulnerabilities led to discovery that the exposed steam exhaust stacks for the main steam safety valves and atmospheric steam dump valves, the exposed vents for the diesel generator fuel oil storage and day tanks, and the electrical power cable trays and/or conduits for the ultimate heat sink cooling tower fan motors were also susceptible to tornado missile damage to the extent that compliance with General Design Criterion 2 is not ensured. Compensatory measures were then promptly implemented for these conditions, as well, in accordance with EGM 15-002 such that the affected systems have been evaluated to be nonconforming but Operable. <br /><br /> It has been determined that the identified nonconformances are an original plant design legacy issue. Long-term resolution for establishing compliance is under development and will be completed within the timeframe described in the EGM, subject to any extensions that may be requested for Callaway Plant and subsequently approved by the NRC.
4832017003 | Callaway | 10/31/2017 | 12/21/2017 | ML17355A56 | <strong>Violation of Technical Specification 3.6.3, Containment Isolation Check Valve Found in Open Position</strong><br /><i>Abstract:&nbsp;</i>Between 4/21/2016 and 11/2/2017, containment isolation valve KCV0478 was inoperable due to an improperly functioning check valve internal assembly (i.e. hanger/disc). This check valve serves as the inside containment isolation valve (CIV) for penetration P-67. The containment isolation integrity function was maintained by KCHV0253, the outer CIV for penetration P-67, during the time KCV0478 was inoperable.<br /><br /> The valve was found in the fully open position on 10/31/2017 (during Refuel 22) after the penetration failed to pressurize for the Local Leak Rate Test (LLRT). The valve appears to have been stuck in the open position from a fire protection system flow test conducted on 4/21/2016 during Refuel 21. Technical Specification (TS) 3.6.3 requires each CIV to be OPERABLE in Modes 1 through 4. In this case, it was not known that the valve was in full open position when the plant entered Mode 4 on 5/5/2016. Therefore, a condition prohibited by TS 3.6.3 subsequently occurred due to failure to comply with the Required Actions specified in the TS for an inoperable CIV. <br /><br /> The root cause of the valve inoperability was dimensional interferences due to inadequate design clearances in the vendor supplied internal assembly (i.e. hanger / disc) on KCV0478. For corrective action, the check valve will be replaced with a new design utilizing corrosion resistant materials.
4982017001 | South Texas 1 | 03/10/2017 | 05/11/2017 | ML17131A35 | <strong>Unit 1 Failure of a Timing Relay During a Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2017, during a Technical Specification surveillance, the as-found operating time of one of four undervoltage timing relays in a Safety related 4.16kV switchgear was greater than the Technical Specification allowable value. The relay was retested without making any changes to the relay timing or the test configuration. The second test resulted in a lower value that was within the Technical Specification allowable value but outside the acceptance criteria of the procedure. A third test (and subsequent follow-up testing) resulted in values that met Technical Specification limits. The associated channel was declared Operable. <br /><br /> On March 14, 2017, an engineer reviewed the surveillance results and questioned the reliability of the relay based on its behavior. The Control Room was contacted and the relay was replaced. Based on the engineer’s analysis, the Shift Manager determined that the relay should not have been declared Operable on March 10. The Technical Specification Action Statement required the inoperable channel to be placed in the tripped condition within 72 hours. This Action was not met and is reportable as a condition prohibited by Technical Specifications per 10 CFR 50.73(a)(2)(i)(B). The event was of very low risk significance and no radioactive release occurred; therefore, there was no adverse effect on the health and safety of the public.
4982017002 | South Texas 1 | 11/23/2017 | 01/22/2018 | ML18022A78 | <strong>Unit 1 Condition Prohibited by Technical Specifications due to Inoperable Control Room Envelope Makeup Filtration System Heating Coil</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2017, a routine surveillance on the South Texas Unit 1 Train "C" Control Room Makeup and Cleanup Filtration System failed due to the Train "C" control room makeup filtration system heater de-energizing approximately two minutes after actuation. The makeup filtration system heater de-energized due to an improperly configured jumper on a circuit board associated with the Train "C" control room makeup filtration unit outlet low flow switch. The circuit board had been installed with the improperly configured jumper on September 27, 2017. The circuit board was properly configured and returned to service on November 24, 2017. <br /><br /> This resulted in the Train "C" Control Room Makeup and Cleanup Filtration System being inoperable for 58 days; the associated Technical Specification allowed outage time for this condition is 7 days. The cause of the event is the maintenance work instructions did not include steps to: (1) ensure that the circuit board jumper is in the correct position, and (2) conduct a post-maintenance test to ensure proper operation of the heaters. As a corrective action, the applicable maintenance work instructions will be revised to (1) ensure that the circuit board jumper is in the correct position, and (2) conduct a post-maintenance test to ensure proper operation of the heaters.
5282017001 | Palo Verde 1 | 04/11/2017 | 06/14/2017 | ML17165A44 | <strong>Essential Chiller B Inoperable due to Refrigerant Leak Resulting in Safety System Functional Failure</strong><br /><i>Abstract:&nbsp;</i>On April 17. 2017, the staff identified a low refrigerant level in the Unit 1 train B essential chilled water (EC) system chiller during inspection. Operations personnel immediately declared EC chiller train B inoperable. On April 17, 2017, the leak was corrected and EC chiller train B was refilled with refrigerant to within the manufacturer's specifications. Operations personnel declared the system operable on April 18, 2017. The chiller had been inoperable since April 11, 2017, when the automatic purge system was placed into service. The direct cause of the low refrigerant level was leakage due to prior installation of a fitting on the automatic purge system filter without a plug.<br /><br /> During the 7-day period that EC chiller train B was inoperable, the supported low pressure safety injection (LPSI) system train B was inoperable. LPSI train A was also inoperable for approximately 17 minutes on April 13, 2017, during the performance of a routine surveillance test. This 17-minute period represented a condition that could have prevented the fulfillment of a safety function. <br /><br /> The cause of the leak was determined to be ineffective work instructions that did not identify the appropriate part number to be used during filter replacement. Corrective actions include revision of the work instructions. This change will ensure that the existing plug remains in place during filter element replacement. A leak test was also added to the work instructions to verify that no refrigerant leaks are present following maintenance.
5282017002 | Palo Verde 1, Palo Verde 3 | 11/13/2017 | 07/03/2019 | ML19184A62 | <strong>Emergency Diesel Generator Inoperable due to Fuel Oil Transfer Pump Testing</strong><br /><i>Abstract:&nbsp;</i>This LER addresses two events in which both emergency diesel generator (EDG) trains became INOPERABLE, once in Unit 1 on November 13, 2017, and once in Unit 3 on February 21, 2019. In each event, one EDG train became INOPERABLE due to a diesel fuel oil transfer pump (DFOTP) trip. A test was conducted on the opposite OPERABLE EDG train DFOTP to comply with the plant’s Technical Specification to determine the OPERABLE EDG was not INOPERABLE due to a common cause failure. <br /><br /> The diesel fuel oil transfer system (DF) operating procedure used for the common cause failure validation contained a test sequence which inadvertently rendered the affected EDG INOPERABLE. This resulted in both EDG trains being INOPERABLE concurrently, which corresponds to an event that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident (10 CFR 50.73(a)(2)(v)(D)).<br /><br /> The preliminary cause was a failure to adhere to procedural guidance for the creation of a procedure change when the test sequence was added to the operating procedure. Specifically the procedure change did not address the impacts of all steps that affect operability. The procedure has been revised to eliminate the common cause testing method.