## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0291991001 | Yankee-Rowe | 02/26/1991 | 03/28/1991 | 9104030139 | <strong>Inadequate Quality Controls Result in Defective Wire Crimps on Safety Related Systems</strong><br /><i>Abstract:&nbsp;</i>On 2/26/91, with the plant in Mode 1 at 100% power, an inspection of the three emergency diesel generators' (EDGs) wiring connections was started which resulted in discovery of deficient connections. The inspection was conducted as part of a nonconformance report that was initiated because a defective crimp was discovered on No. 1 EDG, on 1/2/91, which resulted in its failure to start during routine surveillance testing. Although an evaluation indicated that the EDGs would have functioned as designed the connectors were replaced. On 2/27 the inspection, connector replacement and operational tests were completed. <br /><br /> The root cause of this event was attributed to inadequate planning for and implementation of quality assurance controls during the installation of the EDGs. A 100% inspection of the electrical terminations on the EDGs and replacement of deficient connectors has been completed. All other safety-related jobs performed by the electrical contractor during the 1990 refueling were inspected with no defective connectors being identified. A sampling of other existing crimped connections will be inspected. A training program will be developed for anyone using calibrated crimpers. Plant procedures will be revised to include instructions on making crimped connections. A review of work and QC oversight of the work performed by contractors will be conducted. There was no adverse effect on the public health or safety as a result of this event. This is the first event of this nature at this facility.
0291991002 | Yankee-Rowe | 06/15/1991 | 07/16/1991 | 9107220232 | <strong>Reactor Scram/Turbine Trip and Loss of Offsite Power Due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1991, at 2350 hours, while in Mode 1 at 88% reactor power, a lightning strike resulted in destruction of a lightning arrestor on the No. 3 Station Service Transformer (SST) and flashover of an insulator on the Z-126 115 kV transmission line disconnect switch. As a result, all offsite AC power was lost, an automatic reactor scra and turbine trip occurred, and all three EDGs operated as designed. On June 16, 1991, at 0010 hours, an UNUSUAL EVENT (UE) was declared based on the loss of offsite power and a fire emergency (smoldering arrestor). At 0014 hours, one source of offsite power was restored. At 0130 hours, an ALERT was declared at the discretion of the Shift Supervisor. While attempting to normalize the emergency busses, an inadvertent SI actuation signal was initiated at 0155 hours. Following restoration of essential communication systems and plant equipment, the ALERT was de-escalated to an UE at 0450 hours. On June 17, 1991, the plant attained a cold shutdown condition at 0755 hours and the UE was terminated at 0925 hours. <br /><br /> The root cause of this event has been attributed to lightning-induced transients. Immediate corrective actions involved repairing and testing of affected electrical and mechanical equipment and plant instrumentation, and returning normal and emergency communication equipment back to service. A Yankee Investigation Team was assembled to evaluate the event and develop immediate and long-term corrective actions. There was no adverse effect to the public health or safety.
0291991003 | Yankee-Rowe | 08/01/1991 | 08/30/1991 | 9109040225 | <strong>Failure to Perform Surveillances Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1991, while in mode 1, a routine chemistry control audit team determined that the required Technical Specification (TS) surveillance of the radioactive liquid effluent continuous composite sampler for the Turbine Building Sump had not been satisfactorily performed between July 10, 1990 and August 20, 1990. T.S. 4.3.3.6, Table 4.3-6, Item 2.c requires a channel check be performed daily during releases via the pathway. The logs indicated that the surveillance was not performed on fourteen days during this period. <br /><br /> The root cause of this event has been attributed to personnel error. During the period of the missed surveillances the plant was shutdown for a refueling outage. Some of the operators mistakenly believed that the surveillance was no longer required because the equipment that normally discharges water into the sump was not in operation. The significance of the proper and timely performance of all TS surveillances was reviewed with the auxiliary operators. All Operations Department personnel will be reminded that no log readings shall be omitted without the Shift Supervisor's approval. <br /><br /> Although the surveillance was not performed the sampler was in operation and the effluent from the sump was continuously monitored. There was no adverse effect on the public health or safety as a result of this event. This is the first event of this nature at this facility.
0291991004 | Yankee-Rowe | 08/03/1991 | 09/02/1991 | 9109040086 | <strong>Reactor Scram Due To Loss Of Generator Field</strong><br /><i>Abstract:&nbsp;</i>On August 3, 1991, at 1647 hours, with the plant in Mode 1 at 78% power, the turbine generator static exciter input breaker opened, causing a loss of generator field with resultant turbine trip and reactor scram. There were no inoperable structures, components or systems that contributed to the event. <br /><br /> The root cause of the event is still under investigation. The plant is operating on the rotating exciter. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) which identifies actuation of a Reactor Protection System as a reportable event. At no time during the event was the plant in an unanalyzed condition or in a condition outside the plant design basis. All Engineered Safety Feature systems and equipment operated as designed. Therefore, the health and safety of the public was not adversely effected by this event.
0291991005 | Yankee-Rowe | 11/05/1991 | 12/04/1991 | 9112090331 | <strong>All Emergency Diesel Generators Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>The plant was in Mode 5, at 0% reactor power, with a main coolant system temperature of 103 degrees Fahrenheit. EDG No. 2 was out of service. During weekly surveillance testing of EDG Nos. 1 and 3, excessive arcing was observed across contacts in a control relay. The EDGs were removed from service for evaluation, and declared inoperable. At 1115 hours, an Unusual Event was declared due to the loss of all three EDGs. At 1300 hours, EDG No. 2 was returned to service and the Unusual Event was terminated.<br /><br /> The root cause of the control relay arcing was the installation of 240/480 VAC starting contactor coils in a system designed for 125 VDC. Short term corrective action includes replacement of the AC coils with Dc coils and replacement of the starter contactor with one rated for DC applications. Long term corrective action is to upgrade the EDG circuitry during the present refueling outage. Although EDGs Nos. 1 and 3 were declared inoperable, they remained capable of being started and loaded if needed. <br /><br /> There was no adverse impact on the health and safety of the public as a result of this event. No similar events of this nature have been reported in any previous LERs at the Yankee Nuclear Power Station.
0291991006 | Yankee-Rowe | 11/13/1991 | 12/13/1991 | 9112160140 | <strong>Missed Surveillance - Technical Specification 4.1.2.2.a.1</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1991, with the plant in Mode 5 at 0% power, a supervisory review of completed Technical Specification (TS) required surveillances determined the 7 day valve operability test for the reactivity control system flow path (Surveillance Requirement 4.1.2.2.a.1) was not performed on November 4, 1991. It was satisfactorily performed on November 11. <br /><br /> The root cause of this event is attributed to personnel error. A contributing factor was the inclusion of the 7 day valve operability surv illance as a step in the charging pump operability test procedure, a 31 day surveillance, with no information to direct the operator to the valve operability surveillance requirement. <br /><br /> The surveillance procedure will be revised to include additional detail to ensure that personnel responsible for its performance are aware of TS surveillance schedules. <br /><br /> Throughout the fourteen day period (October 28 through November 11) when the valves were not cycled, there was flow through the flow path from the purification system. There was no adverse impact on the health and safety of the public as a result of this event. <br /><br /> Previous missed surveillances have been reported in LERs 86-11, 87-01, 89-08, 90-09, and 91-03.
1331991001 | Humboldt Bay 3 | 01/23/1991 | 02/22/1991 | 9102280195 | <strong>Failure Of Remote Annunciator System Due To A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1991 at 1050 PST, while the Unit was in SAFSTOR, an Operator found that although the Unit 3 annunciator was both audibly and visibly annunciating an alarm, the remote annunciator for Unit 3, which is in the continuously manned control station for the nonnuclear Units 1 and 2, would not audibly annunciate. The Unit 3 Control Room is not and was not at the time of this incident continuously manned. The Administrative Controls section of the Technical Specifications (VII.C.1.c) requires that the Unit 3 control room be continuously manned, or as an alternative, audible and visual annunciation of all Unit 3 alarms be provided at the control station for Units 1 and 2. Subsequent to the discovery that the Unit 3 remote annunciator was inoperable, the Unit 3 control room was continuously manned until the root cause of the problem was diagnosed and an administrative solution was implemented. <br /><br /> The root cause of this event was a design deficiency of the Unit 3 remote annunciator. <br /><br /> Corrective action to prevent recurrence was the establishment of administrative controls to overcome the design deficiency.
1551991001 | Big Rock Point | 01/10/1991 | 03/15/1991 | 9103260311 | <strong>Incomplete Filling Of Fire Barrier Foam Penetration Seal - Revision 1</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 12.3.7.12 requires that "All penetration fire barriers including fire doors and fire dampers protecting safety-related areas be functional at all times". <br /><br /> Contrary to the above, on January 10, 1991 inspection on three silicone foam fire barrier penetrations were initiated in response to a NRC Information Notice 88-56. Following removal of the damming material on both sides of the foam seal, the seals were inspected for such defects as voids in the foam, gaps along the wall/seal border and cracking within the seal material. Small voids in the foam material were found in two of the three seals. The Shift Supervisor was immediately notified and established a fire patrol to inspect the affected areas once every hour as directed by Technical Specifications. These seals were subsequently repaired on January 11, 1991 and January 16, 1991 and declared operable. In addition, on January 29, 1991 two seals of a somewhat larger size were inspected. One of the two seals has been declared inoperable for the same reasons stated above. Fire patrols once every hour have been established. Repairs are in progress. <br /><br /> The cause of the void defects has been attributed to incomplete filling of the seal cavity during the installation process. Big Rock Point concluded that foam defects in additional seals may exist. Additional inspections and repairs are ongoing and fire patrols will remain in effect until all inspections and required repairs are complete.
1551991002 | Big Rock Point | 08/30/1990 | 03/15/1991 | 9103260220 | <strong>Informational LER - Oversized Holes In Channel/Support Tube Orifice Plate</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1990, 13 channel/support tubes arrived at Big Rock Point. During routine receipt inspection on August 30, 1990 four out of the five flow holes in channel/support tube serial number 8194E, orifice plate serial number 226 were found to be out of specification by five to seven mils. The assembly was returned to the vendor for repair/rework. <br /><br /> Cause of the out of specification condition was attributed to the manufacturing and inspection process by the vendor.<br /><br /> To prevent recurrence, the vendor has counseled and recommended additional training for the inspectors involved. The manufacturing process has been reviewed and no changes are planned.
1551991003 | Big Rock Point | 05/17/1991 | 06/10/1991 | 9106190016 | <strong>Damaged O-Ring Seal Discovered During Rotork Actuator Refurbishment</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1991 a damaged O-Ring seal for Rotork Valve Operator Model 14NA-1 was discovered during refurbishment at the vendor. The operator had been removed from Core Spray Valve MOV MO-7071 during the 1990 Refueling Outage. This damaged seal placed the operator in an untested LOCA environmental configuration for Cycle 24, which lasted about 13 months. A new seal was required to complete the refurbishment.<br /><br /> The cause of the damage to the seal has been attributed to the replacement of the terminal block (because of a broken lug) into its housing during a previous repair. Apparently the individual performing the task lacked the proper knowledge or instruction, causing the seal to be pinched during installation. <br /><br /> To prevent recurrence, the maintenance orders and activities associated with the 1989 refurbishment were evaluated. Personnel associated with these maintenance activities were interviewed and made aware of the deficiency.
1551991004 | Big Rock Point | 05/29/1991 | 06/26/1991 | 9107030018 | <strong>Plant Shutdown Due To Inoperable Redundant Core Spray Valve</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1991 at 2011 hours Surveillance Test T30-22 (Emergency Core Cooling System Valve Tests) was being performed. The Primary Core Spray System Valves were tested first and met the acceptance criteria required by the procedure. The procedure then directs the testing of the Secondary Backup Core Spray Valve, MO-7070. After MO-7070 was successfully stroked, the Primary Backup Core Spray Valve, MO-7071 was tested next. As MO-7071 was being opened, the AO heard a loud "bang" and observed the Backup Core Spray piping move in a north-to-south direction for about 2 seconds and then in a vertical direction for about 8 seconds. In the control room, the CO halted the opening of MO-7071 (10 second stroke time), observed both green and red position limits illuminated and initiated closure (2 second stroke time). After MO-7071 was run closed, the Backup Core Spray pipe movement terminated. MO-7071 was then declared inoperable and in accordance with Technical Specifications 11.3.1.4 a. and e., the plant entered a Limiting Condition of Operation, which was terminated by bringing the plant to a cold shutdown condition. <br /><br /> The cause of the event has been attributed to water-hammer. A water-slug formed on the reactor side of MO-7071 was accelerated towards MO-7071, impacting the valve disc as it opened. <br /><br /> To eliminate the formation of a water-slug in the future, the Backup Core Spray Line was cut and sloped towards the reactor. <br /><br /> The telltale has also been modified to preclude blockage and controls have been established by the Operations Department to insure the telltale will be free of debris.
1551991005 | Big Rock Point | 06/15/1991 | 07/15/1991 | 9107240015 | <strong>Unplanned Actuation Of The Diesel Fire Pump (ESF Feature)</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1991 the reactor was in the cold shutdown condition and the reactor water level had been lowered to the vessel flange. This action drains the steam drum and generates a fire pump start signal which is inhibited by a key switch at the Reactor Depressurization System panel in the control room. At 0330 hours a control room operator sat down in a chair moved near the RDS panel, bumping the Diesel Fire Pump key switch to the AUTO position, starting the pump. The pump was shutdown after 30 minutes run time and the key switch was placed back to the inhibit position. A memo will be issued to the Operations staff reminding them of the potential for more serious consequences due to inadvertent switch or controls actuation. Further review concludes this to be an isolated occurrence.
1551991006 | Big Rock Point | 08/22/1991 | 09/09/1991 | 9109170101 | <strong>Inoperable Fire Barrier (Fusable-Link Auto Closing Fire Door)</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 12.3.7.12 requires that "All penetration fire barriers including fire doors and fire dampers protecting safety-related areas be functional at all time". <br /><br /> Contrary to the above, on August 22, 1991, an audit inspection team discovered that the fusable-link on a fire door auto closing mechanism was missing, rendering the fire barrier inoperable. The Shift Supervisor was notified and the door was closed and tagged indicating that the door must remain closed for the fire barrier to be operable. The fusable-link was found lodged between the door and closure. It appears that the link was struck and dislodged causing the door to close. The door was re-opened and only the spring was installed by an individual(s) unfamiliar with the fusable - link/spring auto-closing mechanism and fire barrier requirements. It has been concluded that this event was caused by a personnel error, and is an isolated occurrence. <br /><br /> All fusable-links on other plant fire doors have been verified to be properly installed. Upon installation of the new fusable-link in the offending fire door closure, the door will be tested in accordance with plant procedures. <br /><br /> To prevent recurrence, a memorandum will be distributed to Department Heads, describing this incident and outline fire door requirements for their personnel to review.
1551991007 | Big Rock Point | 11/23/1991 | 12/18/1991 | 9112300049 | <strong>Failure Of Solenoid To Close Containment Isolation Valve On Loss Of Power</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3.4.3(b) requires that "Normally open lines, carrying fluids into the containment sphere, shall be equipped with check valves to prevent backflow upon loss of inward propellent force. In addition, these lines shall be capable of being secured by manually-operated gate valves or by air-operated control valves. The later shall close upon air or power failure....". <br /><br /> Contrary to the above, at 0415 on November 23, 1991, Demineralized Water Valve CV-4105 failed to close via a hand switch in the control room during the routine performance of a 90 day surveillance procedure. The Shift Supervisor was notified, and verified by visual inspection that the valve was still open. Air pressure on the valve operator was also observed, suggesting a lack of response at the solenoid valve, SV-4897, when the control room switch was actuated. CV-4105 was closed by venting the air pressure from the CV-4105 operator. <br /><br /> The cause of the failure has been attributed to the solenoid valve, SV-4897. SV-4897 was repaired, tested and declared operable on November 27, 1991. <br /><br /> To prevent recurrence, an engineering project will be initiated that includes testing, inspection and/or the replacement of all similar solenoid valves in use at Big Rock Point.
1551991008 | Big Rock Point | 12/10/1991 | 12/18/1991 | 9112300074 | <strong>Control Rod Drive Replacement Delay</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 7.5.7 requires that "....The control rod drive that was removed shall without delay be replaced by a spare control rod drive or the original control rod drive shall be reinstalled.....".<br /><br /> Contrary to the above, on December 10, 1991 at 0330, a control rod drive was removed from the reactor, and a spare drive nor the original drive could be reinstalled. Problems with alignment of the drives caused the delay to occur. Since the alignment problem required additional time to investigate, a blank flange was installed as a temporary safeguard to prevent a path for possible drainage of the reactor. Later, on December 10, 1991, following review of the installation difficulties, personnel re-installed the spare drive. The facility is presently in a major refueling outage, and the reactor was defueled at the time of occurrence.<br /><br /> The cause of the alignment trouble was with the hoist and pulley assembly used to install the control rod drive to the reactor vessel. The location of the work and first time experience for some of the personnel performing the installation also contributed to the delay.<br /><br /> To prevent recurrence, the event was reviewed with CRD crew personnel stressing proper installation technique, prior to resuming further drive change-outs. Procedure improvements are also being investigated.
1551991009 | Big Rock Point | 11/30/1991 | 01/13/1992 | 9201210253 | <strong>Informational LER - Return To Criticality During A Reactor Shutdown Evolution</strong><br /><i>Abstract:&nbsp;</i>In preparation for the upcoming refueling outage, an orderly reactor shutdown commenced at 2157 on November 29, 1991. Power was reduced by inserting control rods, and at 2333 the turbine generator was removed from service. Around midnight, a shift turnover was conducted between the control room operators. During this period of time, the control rods were not being inserted. The reactor power began to turn at 0011, and at 0013 the operator responsible for reactivity control responded by inserting control rods. Power was reduced, and all-rods-all-in was reached at 0330, November 30, 1991.<br /><br /> To prevent recurrence, a Reactivity Management Program has been formed. Management will also undertake new initiatives that will provide their expectations to the operating crews.
1551991010 | Big Rock Point | 12/15/1991 | 04/01/1993 | 9304060027 | <strong>Reactor Protection System Pressure Switches Experiencing Setpoint Drift; Revision 1</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1991 @ 1100 hours, two out of four Reactor Pressure Switches were found to be out-of-tolerance high. <br /><br /> The switches were recalibrated in accordance with plant procedure and the setpoint adjustment was sealed and documented per a Plant Maintenance Order. <br /><br /> The cause of the instrument drift is being attributed to the aging and corrosion experienced by the instrumentation. This event is being reported because it is indicative of a repetitive problem with this type of switch which is used only in the Reactor Protection System. <br /><br /> To prevent recurrence, a calibration check of the four switches was performed on August 14, 1992, when the reactor was taken to the cold shutdown condition to perform maintenance on the turbine. <br /><br /> In addition, a modification to upgrade the instruments' design has been cancelled after research concluded that accuracy could not be improved;
1551991011 | Big Rock Point | 12/23/1991 | 01/20/1992 | 9201270322 | <strong>Failure To Establish Air Lock Interlock Required For Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3.4.2(a) requires that: "(Containment) Access air locks shall have two in-series gasketed doors, which shall be interlocked to insure that at least one door is locked closed at all times when containment integrity is required".<br /><br /> On December 22, 1991 at 2255, the inner and outer doors of the escape lock were closed after instrument cables used for reactor vessel examinations were removed. On December 23, 1991 at 0925 the operations department restored containment integrity after a visual inspection that both doors were closed. <br /><br /> Contrary to the Technical Specification, on December 25, 1991 at 0910 during a daily check performed by operations, the interlock was discovered to be disabled. The interlock was immediately enabled and reported to the shift supervisor. There were no open door alarms (except routine testing) reported by security during the time the interlock was disabled. <br /><br /> The cause of the interlock not being reestablished is personnel error. This is considered to be an isolated incident. To prevent recurrence, procedures and shift routines are being evaluated.
1551991012 | Big Rock Point | 10/22/1991 | 03/05/1992 | 9203120149 | <strong>Spent Fuel Bundle Drop In The Big Rock Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1991 @ approximately 1830, spent fuel bundle I118 was being shuffled in the Spent Fuel Pool from fuel storage rack location G-A6 to G-I6. In the process of lowering the bundle into the fuel cell, it de-grappled from the fuel handling equipment and fell over, settling in a horizontal position on the top of the G fuel rack. No other fuel bundles were involved. The operation of the plant was not affected. <br /><br /> The operators could not detect any signs of physical damage to the bundle or rack. Radiation levels in the area of the spent fuel pool did not change. <br /><br /> The fuel bundle was retrieved and placed in position G-I6 in the fuel rack. No further spent fuel moves were made.<br /><br /> The following reasons were identified as acting together to cause the degrappling: <br /> a. A bent grapple hook. <br /> b. The assembly was leaning when it contacted the fuel rack, causing slack in the fuel handling cable. <br /> c. The bail was above the hooks. <br /> d. The spring force of the new grapple was weaker than the original grapple. <br /> e. The experience level of the auxiliary operator(s). <br /><br /> Several recommendations are being evaluated by the Big Rock Staff to prevent recurrence.
1551991013 | Big Rock Point | 11/30/1991 | 05/22/1992 | 9205290268 | <strong>Voluntary LER - Check Valve Failure Resulting In Degraded Shutdown Cooling Loop</strong><br /><i>Abstract:&nbsp;</i>During a planned reactor shutdown for the 1991/92 Refueling Outage the #1 Shutdown Cooling Loop was inservice providing decay heat removal. Reactor System temperature was approximately 134 degrees F and the plant was in a cold shutdown condition with all control rods inserted. On November 30, 1991 (1735 hours) the #2 shutdown cooling loop was placed inservice to flush the piping to reduce radiation levels in the area. About an hour later, reactor temperature increased about 6 degree indicating inadequate cooling. At that time the #1 loop-was returned to service and reactor cooldown was re-established. <br /><br /> Following inspection of the #2 shutdown cooling loop, the discharge check valve was found restricted and difficult to open beyond the 30, open position. Upon disassembly, the pivot pins were found bent causing disc binding. The probable cause of the bent pins was improper valve assembly following an ISI examination on July 7, 1989. <br /><br /> On January 22, 1992, the check valve was repaired and returned to service.
2061991001 | San Onofre 1 | 01/07/1991 | 05/13/1991 | 9105210149 | <strong>Containment Spray Flow Limiter Valve Actuator Incorrectly Coupled</strong><br /><i>Abstract:&nbsp;</i>On 12/23/90, with Unit 1 in Mode 6, an evaluation of the performance of a Refueling Water Pump (RWP) (which provides containment spray) full flow Inservice Test (IST) revealed that position indication for flow restricting ball valve CV-518 was reversed (i.e., the valve indicated open when in the closed position and vice versa). This dual function valve is designed to open to increase flow to the containment spray header during Loss of Coolant (LOCA) and Main Steam Line Break (MSLB) accidents, and close to reduce flow during recirculation. On 1/7/91, following investigation and analysis, it was determined that this condition existed during plant operation, and would have affected the response of the Containment Spray System (CSS) and the Containment Recirculation System (CRS) to a LOCA or MSLB inside containment. <br /><br /> During a February 1989 maintenance activity in which the actuator was removed from the valve, the position of the valve was improperly changed resulting in improper alignment between the valve and actuator when the actuator was reinstalled. The cause of this event included procedural deficiencies, maintenance implementation deficiencies, deficient design characteristics, and a missed opportunity to identify the misaligned valve. Corrective actions to prevent recurrence include: procedural reviews and changes, training, and design changes. Although this event had minimal direct safety significance, SCE recognizes the programmatic significance of this event and is taking necessary corrective actions.
2061991002 | San Onofre 1 | 02/05/1991 | 03/07/1991 | 9103110319 | <strong>Calculational Error Associated With The Minimum Quantity Of Trisodium Phosphate (TSP) Used For Controlling PH Of Containment Sump Water Following A LOCA</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1991, with Unit 1 in Mode 5, while revising the calculation which specifies the minimum quantity of Trisodium Phosphate (TSP) required for controlling containment sump water pH following a Loss Of Coolant Accident (LOCA), it was determined that the post LOCA pH could have ranged between 6.74 e and 7.33. This range was determined based upon current Technical Specifications (TS) governing TSP and boric acid sources to the Reactor Coolant System (RCS). The basis for the TS governing TSP specifies a minimum pH of 7.0 within four hours following a design basis LOCA. Therefore, there has existed the potential for Unit 1 to be operated in a condition outside of its design basis with respect to post LOCA containment sump water pH. <br /><br /> The calculation revision had been initiated after it was identified that the original calculation had not included the Boric Acid Storage Tank (BAST) as a potential source of boric acid into the containment sump. Given the length of time since the original calculation was performed, SCE has been unable to definitively conclude the reason for the omission. However, it is our belief that the original calculation only considered sources of boron that were introduced into the containment sump in accordance with procedure or were credited in the LOCA analysis. Since this is not the case for the BAST, its contents were not incorporated in the calculation. <br /><br /> The amount of TSP located in racks in the lowest elevation of containment has been increased. Appropriate administrative controls have been implemented to limit boron in the Refueling Water Storage Tank (RWST) and BAST. A proposed TS change reflecting these limits and the increase in the minimum TSP required will be submitted within three months after restart from the current outage. <br /><br /> This condition would have had minimal safety significance.
2061991003 | San Onofre 1 | 02/25/1991 | 03/27/1991 | 9104010303 | <strong>Diesel Generator No. 2 Automatic Start During System Restoration</strong><br /><i>Abstract:&nbsp;</i>At 2023 on February 25, 1991, with Unit 1 in Mode 5, Diesel Generator (DG) No. 2 was removed from service by placing the DG in maintenance lock-off to prevent the DG from automatically starting on a Loss Of Power (LOP) signal when the 125 VDC power to 4KV Bus 2C undervoltage (UV) relays were de-energized for maintenance. At 2229 during system restoration, Operations removed DG No. 2 from maintenance lock-off without first manually resetting the LOP signal latched into the No. 2 Sequencer. As a result, DG No. 2 automatically started by the Sequencer on the latched-in Bus 2C LOP signal. Bus 2C remained energized from off-site sources throughout the event. DG No. 2 and all support systems were verified to have operated properly. At 2236, the Sequencer No. 2 LOP was manually reset and DG No. 2 was secured per procedure. <br /><br /> The Work Authorization Record (WAR) which was prepared for the work did not adequately address system restoration by either; 1) referencing the Diesel Generator Operations Procedure, which would have ensured that a DG start signal was not latched-in at the sequencer; or 2) specifying that the LOP signal at Sequencer No. 2 must be manually reset prior to removing DG No. 2 from maintenance lock-off. This deficiency resulted from inadequacies in the WAR process. Specifically: 1) the Equipment Status Control Procedure does not provide adequate direction for establishing system restoration requirements, and 2) the WAR form does not provide a means by which system restoration steps/information can be specified. <br /><br /> Corrective actions include reviewing this event with appropriate Operations personnel and procedural enhancements.
2061991004 | San Onofre 1 | 02/14/1991 | 03/18/1991 | 9103260038 | <strong>Calculational Error Affecting the Time Interval for Initiation of Hot Leg Recirculation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. ON 2/14/91 WITH UNIT 1 IN MODE 5, SCE'S DESIGN BASIS DOCUMENTATION (DBD) PROGRAM DETERMINED THAT THE CALCULATED POST-LOSS OF COOLANT ACCIDENT (LOCA) TIME TO INITIATION OF HOT LEG RECIRCULATION (HLR) WAS NON-CONSERVATIVE. HLR IS UTILIZED TO PREVENT BORON PRECIPITATION IN THE CORE DURING LONG TERM COOLING FOLLOWING CERTAIN LOCAS. UNDER CONSERVATIVE CALCULATIONAL ASSUMPTIONS (E.G., RCS TEMPERATURE IS ASSUMED TO BE 212F, THE TEMPERATURE AT WHICH THE BORON PRECIPITAT ION DESIGN LIMIT IS BASED) FOLLOWING A LARGE COLD LEG BREAK LOCA, PRECIPITATION OF BORIC ACID IS PREDICTED TO OCCUR IN THE REACTOR VESSEL PRIOR TO HLR BEING ESTABLISHED IN ACCORDANCE WITH EMERGENCY OPERATING INSTRUCTIONS (EOIS). THE TIME TO INITIATION OF HLR WAS ESTABLISHED BASED UPON CALCULATIONS PERFORMED FROM 1976 TO 1978. THESE CALCULATIONS CONTAINED ERRORS AND ASSUMPTIONS WHICH RESULTED IN A NON-CONSERVATIVE TIME TO HLR INITIATION IN THE EOIS. HOWEVER, UNDER MORE REALISTIC POST-ACCIDENT CONDITIONS, HLR WOULD HAVE BEEN ESTABLISHED PRIOR TO A DEGRADATION IN CORE COOLING DUE TO BORON PRECIPITATION. GIVEN THE LENGTH OF TIME SINCE THE ORIGINAL CALCULATIONS WERE PERFORMED, SCE HAS BEEN UNABLE TO DEFINITIVELY DETERMINE THE CAUSE OF THE ERRORS. A COMPLETE REVISION TO THE CALCULATIONS WAS PERFORMED, AND EOIS HAVE BEEN REVISED TO ALIGN HLR AT A TIME CONSISTENT WITH CORRECTED DESIGN ASSUMPTIONS.
2061991005 | San Onofre 1 | 03/21/1991 | 04/22/1991 | 9104260112 | <strong>Technical Specification Required Effluent Samples Discarded Due To Inadequate Labeling</strong><br /><i>Abstract:&nbsp;</i>On 3/21/91 during the midnight shift, a chemistry technician inadvertently discarded the weekly continuous release pathway liquid composite samples for the week of March 11 - 17, 1991. Thus, the March 1991 monthly gross alpha and first quarter 1991 Fe-55/Sr-89/Sr-90 composite samples will not accurately reflect Unit releases as required by Technical Specification (TS) 4.5.1, "Radioactive Liquid Effluents - Liquid Effluent Concentration." <br /><br /> The root cause was attributed to personnel error since a chemistry technician had deviated from procedural requirements governing chemistry sample labeling. The sample containers were not labeled such that the requirement for retention was apparent. The chemistry technician responsible for the labeling deficiency received appropriate disciplinary action, and this event was reviewed with other appropriate chemistry personnel. <br /><br /> Since there is typically little deviation in the sample's isotopic concentration from week to week, a composite consisting of samples obtained in the first, third, and fourth weeks is considered to be representative of the entire month. As such, this will be reported in the next semi-annual effluent report. <br /><br /> There was no safety significance to this event since the contributions of gross alpha, Sr-89, Sr-90, and Fe-55 isotopes to the annual projected dose are typically insignificant.
2061991006 | San Onofre 1 | 02/19/1991 | 04/15/1991 | 9104220128 | <strong>Failure To Perform Radioactive Gaseous Effluent Technical Specification Required Sample</strong><br /><i>Abstract:&nbsp;</i>On 3/14/91, with Unit 1 in Mode 3, it was discovered during the calculation of gaseous discharges for the February monthly effluent report that particulate and iodine data for a two day time period was not available. Technical Specification (TS) 4.6.1, "Radioactive Gaseous Effluents", requires continuous sampling for iodine and particulate activity for the plant vent stack flowpath. <br /><br /> On 2/21/91, while in Mode 5 and with the normal plant vent stack monitors out of service, auxiliary sampling equipment was connected as required compensation for the out of service monitors. Following a shift change, the permanent monitors were returned to service, the auxiliary equipment was removed and the filters which collect the particulate and iodine samples were removed and analyzed. The filters on the permanent radiation monitors were also removed and discarded at this time. As a result, the contribution of the particulate and iodine activity from the plant vent stack from 2/19/91 to 2/21/91 can not be positively determined. The root cause of this event is inadequate communication during the shift change turn-over process. The turn-over instructions, documented in the turn-over log by swing shift chemistry technicians, were inadequate in that they directed the grave yard shift chemistry technicians to remove the auxiliary sample equipment and replace the filters in the permanent monitors, but it did not include saving and analyzing the permanent monitor filters.
2061991007 | San Onofre 1 | 03/28/1991 | 06/14/1991 | 9106210240 | <strong>Large Break Loss Of Coolant Accident Analyses Non-Conservatisms Due To Incorrect Reactor Coolant System Volumes Utilized In The Analyses</strong><br /><i>Abstract:&nbsp;</i>On 3/28/91, with Unit 1 operating at 20% reactor power, it was determined that the value for the reactor vessel refill volume used in the Large Break Loss of Coolant Accident (LBLOCA) analysis performed by Westinghouse was underestimated by approximately 182 cubic feet. An initial evaluation of the effects of this volume discrepancy using actual plant operating parameters in the event of LBLOCA indicate that the Peak Clad Temperature (PCT) would not have exceeded the SONGS 1 acceptance criteria of 2300 degrees F. Although actual operation could not have resulted in exceeding the LOCA/PCT limit, under hypothetical operating conditions assumed in the design basis accident analysis, it is possible that LOCA/PCT limit exceedence could be predicted to occur. <br /><br /> Corrective actions included: 1) immediately restricting reactor power level to 75% (this reduced power level ensured that the SONGS 1 PCT acceptance criteria following a LBLOCA would have been satisfied), and 2) administratively restricting Incore Axial Offset (IAO) to allow for full power operation. <br /><br /> Subsequently, additional volume differences were identified in other analyses performed by Westinghouse. These additional differences could affect the LBLOCA/PCT and the LBLOCA Containment Mass and Energy Analyses, conservatively assuming these differences to be errors. Our evaluation has concluded that the controls restricting IAO, and operation within the currently allowed T sub avg provide sufficient margin to compensate for all of the identified volume differences, conservatively assuming these differences are non-conservative modeling errors. <br /><br /> Westinghouse was unable to determine the basis for the original calculation of the refill volume in the LBLOCA analysis. The additional volume differences are largely attributable to differences in calculational approach as compared to current analysis methods and standards. <br /><br /> The volume differences described in this LER have been documented in SCE letters to the NRC dated 3/29/91, 5/10/91, and 5/17/91.
2061991008 | San Onofre 1 | 04/16/1991 | 05/16/1991 | 9105240135 | <strong>Rod Control System Inoperable</strong><br /><i>Abstract:&nbsp;</i>At about 0430 on 4/16/91, with Unit 1 at about 90% power and after successful completion of routine Technical Specification (TS) surveillance testing to determine control rod operability, a Rod Control (RC) system interlock relay (which prevents simultaneous control signals for insertion and withdrawal of control rod banks 1 and 2) failed. The failure mode of the relay effectively caused the RC System logic to be in the withdraw mode, thereby precluding RC System control rod bank insertion. At the time of the failure, the position of all rods and banks were within the limits of applicable TSs. Furthermore, reactor power and power distribution were within the limits of applicable TSs. The unit remained fully capable of being automatically or manually tripped by the Reactor Protection System. <br /><br /> Continued operation in the existing configuration was considered to be safer during the brief period required to effect repairs than to place the unit in a shutdown transient which would normally be performed with control rod insertion. Accordingly, a temporary waiver of compliance was requested and approved for a period of 36 hours, commencing at 0430 on 4/16/91 and ending at 1630 on 4/17/91. This provided sufficient time to replace the faulty relay and to demonstrate that the RC System functions as designed. In this regard, the failed relay was replaced and the RC System determined to be functioning correctly at 1940 on 4/16/91. Reliance on the temporary waiver of compliance for continued operation beyond the time allowed by TS action requirements is a violation of TS 3.5.3, "Control and Shutdown Rod Misalignment," and is therefore being reported.<br /><br /> Preliminary investigation into the cause of the relay failure indicates that relay contacts stuck with the normally open contacts closed thereby inhibiting control bank insertion. The failed relay has been replaced and sent to the manufacturer for failure analysis. A supplement to this LER will be provided if the failure analysis provides unique information concerning the relay failure or causes us to revise our corrective action.
2061991009 | San Onofre 1 | 04/29/1991 | 05/24/1991 | 9105300324 | <strong>Test Interval Exceeded On Containment Air Lock Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On 4/25/91, a Quality Assurance (QA) audit of the Local Leakage Rate Tests (LLRTs) performed on the Unit 1 emergency escape and personnel air locks per Technical Specification (TS) 4.3.1.II, "Containment Penetration Leakage Rate Tests (Type B)," Section C identified that the 6-month surveillance interval for performing a leak test with an initial pressure of at least 49.4 psig was exceeded. On 4/29/91, with Unit 1 in Mode 5, it was determined that in 1990 the TS testing interval had been exceeded once each for the emergency escape and personnel air locks.<br /><br /> The root cause was attributed to mis-communication and lack of formality in the scheduling process. The group performing the LLRTs had provided the test completion dates for the 49.4 psig tests, as well as for lower pressure tests (performed at 10 psig within 72 hours following each air lock closing in accordance with TS 4.3.1.II.C (2)), to the group which maintains the test schedule. The scheduling group incorrectly identified a low pressure test as a full pressure test, resulting in an incorrect determination of the required next inspection date (scheduling performance of subsequent 49.4 psig tests 6 months from the completion of a 10 psig test, rather than from the completion of the previous 49.4 psig test).<br /><br /> Corrective actions included a review of the air lock LLRT records since 1/1/88 to ensure that all similar instances had been identified. Also, a more formal method has now been established for updating the surveillance schedule. Actual test documentation, which clearly identifies the test type, will be utilized in the scheduling process. <br /><br /> This event has been reviewed in detail with the personnel involved by their supervision.
2061991010 | San Onofre 1 | 05/28/1991 | 06/27/1991 | 9107050020 | <strong>Manual Reactor Trip Following Dropped Control Rods Due To An Open Circuit In The Control Rod Drive Circuitry</strong><br /><i>Abstract:&nbsp;</i>At 2343 on 5/28/91, with Unit 1 in Mode 1 at 91% power, two of the 12 Control Bank 1 control rods (CRs) (H-6 and H-10) dropped into the core. Appropriate control room alarms were received and operators confirmed negative reactivity insertion per procedures. Operators properly responded (within 20 seconds) by manually tripping the reactor. At 2344, the auxiliary feedwater (AFW) system actuated on low steam generator (SG) water level which occurred due to expected SG water level shrinkage. At 0044 on 5/29/91, the reactor trip response procedure was exited with the plant stabilized in Mode 3. <br /><br /> The CRs dropped as a result of an open connection in the "half-voltage" resistor network associated with this rod subgroup. The open connection de-energized the moveable gripper coils associated with the affected rods, thus permitting them to drop into the core. The open connection was caused by a conductor/lug (jumper) connection failure at one termination point. Destructive physical analysis has revealed that the open connection resulted from long-term localized heating resulting in oxidation of the copper wire in the vicinity of the failure site. Continued heating led to arcing, melting, and eventual failure.<br /><br /> The failed jumper was replaced with in-kind parts. In addition, other jumper wires/lugs within the CR "half power" resistor bank were replaced in-kind. A continuity check and thermographic inspection were performed and no anomalous conditions were identified. Rod position indication and control rod drive operability tests were completed satisfactorily prior to startup.
2061991011 | San Onofre 1 | 03/09/1991 | 07/05/1991 | 9107100217 | <strong>480 Volt Motor Control Center Breaker Handle Found Improperly Locked Open</strong><br /><i>Abstract:&nbsp;</i>At approximately 1600 on 6/4/91, with Unit 1 in Mode 1 at 91% power, the locking device for circuit breaker S1-8-1122 (provides alternate power to manual transfer switch MTS-8) was discovered improperly installed. Although the locking device was improperly installed, the breaker remained open at all times as required by the plant design. MTS-8 provides power to several safety injection system and containment spray system motor-operated valves. Improper installation of the locking device represents a condition prohibited by Technical Specification (TS) 4.4, "Emergency Power System Periodic Testing," Section G, "Manual Transfer Switches," which requires that breaker S1-8-1122 be locked open while operating in Modes 1 through 4. Unit 1 operated in Modes 1 through 4 fr m 0827 on 3/9/91 through 1452 on 4/22/91 (at which time the Unit entered Mode 5 for a steam generator tube inspection outage), and again upon recovery from the outage at 1435 on 5/18/91, until the breaker was properly locked at approximately 1615 on 6/4/91.<br /><br /> The root cause was attributed to a lack of appropriate training for this particular breaker locking mechanism. A contributing cause included inadequate procedural guidance addressing verification of proper locking device configuration. <br /><br /> The information outlined in this event and the proper locking methodology for this type breaker was assigned as required priority reading for Unit 1 Operators. In addition, appropriate breaker locking guidance has been incorporated into those procedures that require breaker S1-8-1122 to be verified locked open.
2061991012 | San Onofre 1 | 03/12/1991 | 03/03/1992 | 9203090395 | <strong>Inoperable Air Operated Valves Due To Backup Nitrogen System Leakage</strong><br /><i>Abstract:&nbsp;</i>At approximately 0919 on 6/25/91, with Unit 1 in Mode 3 at 0% power, it was determined that the air operated actuator associated with one of the two power operated relief valve (PORV) block valves, CV-531, was leaking instrument air. In addition to instrument air, CV-531 is supplied with backup nitrogen (in the event of a loss of instrument air) from a header which is common to several components inside containment. Since this leakage was greater than that assumed in the backup nitrogen system (BNS) design basis, CV-531, as well as the other valves supplied with backup nitrogen from the common nitrogen header, did not satisfy all of the conditions required for operability. This condition had existed during periods of operation when Technical Specifications required the valves to be operable. This event was determined to have no safety significance.<br /><br /> The excessive air leakage from the CV-531 actuator was due to loose actuator diaphragm casing bolts. An assessment of the actuator diaphragm as-found condition concluded that replacement was not required. The actuator diaphragm casing bolts were subsequently torqued to the required value. Post-maintenance testing demonstrated valve operability with no air leakage. The root cause was attributed to improper torquing of the CV-531 diaphragm housing fasteners during maintenance which had been conducted to replace the diaphragm on 7/18/90.
2061991013 | San Onofre 1 | 07/01/1991 | 03/05/1992 | 9203110117 | <strong>Mis-Assembly Of The 4160 Volt Room Halon System Actuation Lines</strong><br /><i>Abstract:&nbsp;</i>At 0524 on 7/1/91, an inadvertent actuation of the halon fire suppression system in the Unit 1 4160 volt (4 kv) switchgear room occurred. Moisture intrusion into the halon control panel actuation circuitry caused the inadvertent actuation. Contrary to design, the discharge was limited solely to the main bank master bottle. The main bank slave bottles failed to properly actuate as designed due to an incorrectly connected actuation line between the master bottle and the slave bottles. The reserve bank (redundant) halon system was similarly incorrectly configured and was therefore also incapable of complete discharge. As a result, both banks of the 4 kv room halon system were inoperable. <br /><br /> Our investigation has concluded that the actuation lines were incorrectly connected during maintenance activities that occurred either in June 1988 or in April/ May 1989, when the main and reserve bank master bottles were disconnected and transported to an off-site vendor for servicing, and subsequently reinstalled by SCE. This event represents a condition prohibited by Technical Specification 3.14.4, "Halon Systems," Part B, since the operability requirements of the halon system had not been satisfied during the period of time that the system was not properly configured. <br /><br /> SCE's investigation has identified deficiencies in: 1) maintenance procedures, 2) post-maintenance verification, 3) practices related to marking of parts for correct reassembly, and 4) halon system knowledge. These deficiencies collectively contributed to the incorrect reassembly of the halon system and the failure to detect this condition. Corrective actions underway include procedural changes, post-maintenance retesting/verification improvements, and training. <br /><br /> SCE has concluded that due to the fire protection and safe shutdown features available, the likelihood of a fire in the 4 kv room preventing the Unit from achieving and maintaining safe shutdown during the period of halon system inoperability is considered to be remote.
2061991014 | San Onofre 1 | 08/07/1991 | 03/30/1992 | 9204030127 | <strong>ENTRY INTO TECHNICAL SPECIFICATION 3.0.3 DUE TO INOPERABLE VOLUME CONTROL TANK LEVEL TRANSMITTERS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 090%. ON 8/7/91 AT 1135, WITH UNIT 1 IN MODE 1 AT APPROX. 90% POWER, VOLUME CONTROL TANK (VCT) LEVEL TRANSMITTER LT-11OO WAS EXHIBITING ERRATIC INDICATION AS COMPARED TO THE OPPOSITE TRAIN LEVEL TRANSMITTER (LT-2550). THESE LEVEL TRANSMITTERS FUNCTION TO REALIGN THE CHARGING PUMPS FROM THE VCT TO THE REFUELING WATER STORAGE TANK WHEN THE VCT LEVEL BECOMES LOW, AND PROVIDE A PROTECTIVE TRIP TO THE CHARGING PUMPS TO AVOID THE INTRODUCTION OF VCT HYDROGEN GAS TO THE PUMP SUCTION. TO AVOID INADVERTENT ACTUATION DURING CORRECTIVE MAINTENANCE ON LT-11OO, THE AUTOMATIC ACTUATION FUNCTIONS OF BOTH TRANSMITTERS WERE BYPASSED. AT 0440 ON AUGUST 8TH, THE AUTOMATIC PROTECTION AFFORDED BY LT-2550 WAS RESTORED SINCE MAINTENANCE WHICH COULD AFFECT BOTH TRANSMITTERS HAD BEEN COMPLETED. AT ABOUT 1700 ON AUGUST 8TH, IT WAS RECOGNIZED THAT REMOVAL OF THE AUTOMATIC ACTUATION FEATURE WAS CONTRARY TO THE REQUIREMENTS OF TS 3.3.1, 'SAFETY INJECTION SYSTEM ... OPERATING STATUS,' SECTION A(3) SINCE AN APPLICABLE ACTION STATEMENT GOVERNING THESE COMPONENTS IS NOT PROVIDED. AS SUCH, SHUTDOWN OF UNIT 1 WAS INITIATED AT 1800 PER TS 3.0.3. SCE REQUESTED A TEMPORARY 72-HOUR WAIVER OF COMPLIANCE FROM THE ABOVE TS REQUIREMENTS SINCE A PREVIOUSLY SUBMITTED TS CHANGE PROVIDED A 72-HOUR ACTION STATEMENT FOR THIS SITUATION. THE NRC VERBALLY APPROVED THE WAIVER AT APPROXIMATELY 2000.
2061991015 | San Onofre 1 | 08/16/1991 | 09/16/1991 | 9109200211 | <strong>Failure To Satisfy The Technical Specification Surveillance Requirements Associated With The Fire Protection System Foam Tank Level Measurements</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1991, with Unit 1 at 91% power, while performing the Technical Specification (TS) 4.15.3.a.1, "Foam Suppression Systems," surveillance to verify an acceptable level in the fire protection system foam tank associated with the lube oil conditioner and reservoir, the tank sight glass isolation valves were observed to be closed, contrary to the system drawing. The valves were opened and the tank level verified to be satisfactory. <br /><br /> On August 16, 1991, following an investigation of the correct position of the valves, it was determined that the procedure used to perform previous TS surveillances did not prescribe a system alignment which would properly equate the sight glass level with that of the tank. This condition represents a failure to satisfy the surveillance requirements of TS 4.15.3.a.1. Notwithstanding the improperly performed surveillance, the content of the tank was determined to be satisfactory. <br /><br /> The proper valve line up for determining foam tank level, as provided for in the vendor manual, was not incorporated into appropriate Operations procedures at the time the foam system was installed in 1980. The methodology for incorporation of design change information was not sufficiently rigorous at the time of the installation. This methodology has since been strengthened. <br /><br /> Corrective actions include revising the surveillance procedure to specify the proper valve line up for verifying foam tank level.
2061991016 | San Onofre 1 | 09/06/1991 | 09/30/1991 | 9110090190 | <strong>Voluntary Entry Into Technical Specification 3.0.3 Due To A Pressure Gauge Failure In The Safety Injection System</strong><br /><i>Abstract:&nbsp;</i>At 1307 on 9/6/91, with Unit 1 at 91% power, main feedwater pump (which also provides safety injection flow) mini flow isolation valve (CV-875B) ISV! was removed from service in order to replace a failed pressure indicating gauge PI! in the air supply to its actuator. With CV-875B removed from service, one train of safety injection (SI) BP! was considered inoperable since the mini-flow valve must function (i.e. open) in response to a SI signal to ensure pump protection. Since the Technical Specification (TS) governing safety injection (TS 3.3.1.A) does not contain an Action Statement that allows for the removal of one SI train, TS 3.0.3 was applied. The failed pressure gauge was replaced and the SIS train was returned to service at 1312 on 9/6/91. <br /><br /> The pressure gauge is used to verify that sufficient air pressure or backup nitrogen LK! is available from the instrument air system LD! or its backup nitrogen system to provide the motive power necessary to open the normally closed CV-875B upon receipt of a SI signal. <br /><br /> Following gauge replacement, sufficient air pressure was verified to have been available to open CV-875B; thus CV-875B continued to be operable except for the five minutes required to replace the gauge. The gauge failed due to normal system vibration.<br /><br /> SCE has previously recognized the potential for entering TS 3.0.3 due to a lack of Action Statements for the SI system and the requirements of TS 3.3.1.A. A proposed change to TS 3.3.1 to correct these deficiencies has been submitted. <br /><br /> This event had no safety significance, since the redundant SI train was always operable throughout the event. Additionally, the inoperable train of SI would have been capable of injecting borated water into the Reactor Coolant System AB!, if required, during the time CV-875B was inoperable during the pressure gauge replacement.
2061991017 | San Onofre 1 | 10/17/1991 | 11/18/1991 | 9111250168 | <strong>Unit 1 Automatic Reactor Trip Upon Transfer Of Vital Bus #1 With Pre-Existing Failure Of High Startup Rate Block Relay</strong><br /><i>Abstract:&nbsp;</i>At 1314 on 10/17/91, during the performance of corrective maintenance on an alarm module powered from Vital Bus No. 1 (VB1), and with a pre-existing failure of the high startup rate (SUR) block relay (AP4D), Unit 1 automatically tripped from 91% power on a spurious high SUR signal. The spurious SUR signal was generated when a momentary power interruption to VB1 occurred during an automatic transfer of VB1 to its alternate power source, which was initiated due to a momentary ground fault on the bus. As a taped alarm module power lead was being routed through a grooming hole in the module chassis, the lead arced apparently through the tape to the module chassis, causing the ground. The reactor protection system (RPS) and automatic control systems functioned as designed, and the plant was stabilized in Mode 3 at 1342. An auxiliary feedwater (AFW) actuation occurred due to the expected decrease in steam generator levels following the trip. All AFW components responded in accordance with design, and the AFW actuation was reset at 1401. <br /><br /> Laboratory analysis of the taped lead revealed that the insulating capability of the tape had apparently been degraded during handling. This is postulated to have occurred when the taped lead contacted a sharp edge of the grooming hole on the alarm module chassis when the lead was inserted through the hole. <br /><br /> The methodology used to route insulated live leads will be reviewed. Any methodology enhancements identified by this review will be implemented as appropriate. <br /><br /> There is no safety significance to this event since all RPS and AFW components actuated in accordance with design.
2061991018 | San Onofre 1 | 10/21/1991 | 11/20/1991 | 9111260218 | <strong>Delinquent Technical Specification Surveillances Due To Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On 10/21/91 with Unit 1 in Mode 3 following a reactor trip on 10/17/91, it was determined that both Power Operated Relief Valve (PORV) block valves had exceeded their quarterly inservice testing (IST) interval plus the allowable extension permitted by Technical Specifications (TS) on 10/19/91 and 10/20/91, respectively. The valves were declared inoperable and the TS 3.1.5, "Pressurizer Relief Valves," action statement was entered. Upon satisfactory completion of the IST on 10/21/91, both valves were declared operable and the TS 3.1.5 action statement was exited. <br /><br /> The cause of this event was a weakness in the administrative controls for the Operations IST surveillance program which resulted in the failure to provide the control room with a list of valves requiring ISTs on 10/18/91. The administrative controls were not sufficient to ensure that the IST valve list would be delivered to the control room in a timely fashion. Additionally, these administrative controls did not include provisions to alert control room operators when IST surveillance interval extensions are used, therefore requiring more attention than that given to normally scheduled ISTs. Since surveillance interval extensions were used in this case, there was little margin in the test schedule to account for unforseen events such as the 10/17/91 reactor trip. <br /><br /> The planned corrective actions include the enhancement of operations instructions to: 1) provide a more formal methodology for assuring that the control room is provided with the required IST valve list, and 2) require that extensions of IST surveillances be administratively controlled and documented.
2061991019 | San Onofre 1 | 10/30/1991 | 12/02/1991 | 9112060182 | <strong>Emergency Light Inoperable Contrary To Technical Specifications Due To Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1991, with Unit 1 in Mode 1, during the review of routine preventative maintenance inspection data for 8-hour emergency lights, it was determined that Emergency Light L2-25-1-R had been inoperable since October 23, 1991, when a battery lead became disconnected from a severely corroded battery terminal as it was being cleaned. On November 1, 1991, the emergency light was repaired. The light was satisfactorily tested and demonstrated to be operable on November 3, 1991. Contrary to Technical Specification (TS) 3.14.9, "8-hour Emergency Lighting Units," the repair of the light was not completed within the 7 days permitted, which ended on October 30, 1991. <br /><br /> The incident resulted from an inadequate inspection procedure that failed to provide appropriate guidance relative to observed 10 CFR 50, Appendix R, emergency light deficiencies requiring prompt action and notification. As a result, initiation of corrective action for the identified deficiency was incorrectly deferred from the time of discovery to October 30, 1991, when the other emergency light inspections were completed. As corrective action, a Maintenance surveillance test procedure will be developed exclusively for Unit 1 TS related 10 CFR 50, Appendix R, lighting units. <br /><br /> This event is of no safety significance, since even without the use of the inoperable emergency light, adequate lighting was available for operators to perform necessary functions.
2061991020 | San Onofre 1, San Onofre 3 | 10/24/1991 | 11/25/1991 | 9112060380 | <strong>Delinquent Reactor Coolant Pump Flywheel Inspections</strong><br /><i>Abstract:&nbsp;</i>On 10/24/91, with Unit 3 in Mode 1 at 100% power, the Reactor Coolant Pump (RCP) motor flywheel inspection interval, as specified by Technical Specification (TS) surveillance 4.4.9, "Reactor Coolant System - Structural Integrity," and Regulatory Guide (RG) 1.14, was identified to have been exceeded. It was subsequently discovered on 10/25/91, with Unit 1 in Mode 1 at 90% power, that the flywheel inspection interval, as specified by TS 4.7, "Inservice Inspection Requirements," and RG 1.14, for Unit 1 RCPs "B" and "C" had also been exceeded. Since the surveillance intervals had been exceeded, the four Unit 3 RCPs and Unit 1 RCPs "B" and "C" were considered inoperable. As Units 1 and 3 TSs do not address operability requirements for RCP motor flywheels, TS 3.0.3 was also applicable. Plant shutdown was delayed, as allowed by TS 4.0.3, while SCE sought a temporary waiver of compliance for Units 1 and 3 to defer shutdown of the Units to inspect the RCP motor flywheels until 12/1/91. Verbal approval was obtained on 10/25/91, and on 10/30/91, the waiver request was formally granted. <br /><br /> The cause of the delinquent Unit 1 flywheel inspection has been attributed to a weakness in the tracking of the flywheel surveillance. The cause of the Unit 3 inspection interval being exceeded was a scheduling oversight by SCE personnel due to weaknesses in administrative controls. <br /><br /> Corrective actions include the following: 1) monitoring of the RCPs for changes in the vibration levels until the inspection could be completed, 2) the Unit 1 RCP flywheels were inspected and found satisfactory, 3) the personnel responsible for this failure have received appropriate disciplinary action, and 4) the Units 1, 2 and 3 RCP motor flywheels were added to the San Onofre repetitive maintenance tracking program. In addition, administrative controls and tools utilized for the RCP motor flywheel surveillance scheduling will be reviewed and appropriately modified.
2061991021 | San Onofre 1 | 11/07/1991 | 12/06/1991 | 9112120222 | <strong>Voluntary Entry Into Technical Specification 3.0.3 Due To Inadequate Technical Specification In Order To Perform A Surveillance Of A Containment Spray System Pump</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1991, between 1724 and 1752, while Unit 1 was in Mode 1 at approximately 90% power and with the North Refueling Water Pump (RWP) BE, P! (G27N) inoperable with maintenance required on its Circuit Breaker 52!, Technical Specification (TS) 3.0.3 was entered in order to demonstrate the operability of the South RWP (G27S). <br /><br /> In order to initiate maintenance on G27N, TS 3.3.1.C. requires that G27S be tested to demonstrate its availability. In order to perform the test without initiating containment spray, the pump's manual discharge isolation valve ISV! must be closed rendering the South train inoperable. Since there are no action statements which address the inoperability of both Containment Spray System (CSS) BE! trains, performance of the G27S surveillance test would constitute an entry into TS 3.0.3. The G27S discharge isolation valve was closed between 1724 and 1752 while the pump surveillance was being performed. The surveillance test verified that pump G27S continued to be operable.<br /><br /> The cause of the TS 3.0.3 entry is the absence of appropriate action statements. A TS amendment application has been submitted which will revise TS 3.3.1 to preclude TS 3.0.3 entries for conditions similar to this event. This TS amendment application is being reviewed by the NRC and SCE. <br /><br /> The entry into TS 3.0.3 is of no safety significance since: (1) There was a low probability of a plant condition which would require operation of the containment spray system during the 28 minute period during which the CSS was unavailable, and (2) there was a reactor operator (utility, licensed) standing by to open the RWP G27S discharge isolation valve.
2131991001 | Haddam Neck | 01/11/1991 | 02/08/1991 | 9102130342 | <strong>Apparent Failure of Main Steam Line Trip Valves to Stroke</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1991, at 1230 hours, with the plant in Mode 1 at 100 percent power, all four main steam line isolation trip valves were declared inoperable following the failure of the valves to move during quarterly surveillance testing. A load reduction was initiated at 1325 in accordance with Technical Specification 3.0.3. Subsequent trouble shooting determined that the valves were operable and the problem was that the test switch has to be held in the test position much longer than it used to due to a recent design change which replaced the solenoid valves and pneumatic tubing in the trip valves' testing system. The new tubing has a smaller inside diameter which restricts air flow to the top of the valve's operating piston thus delaying valve movement in the test mode only. The valves were tested satisfactorily and the load reduction was terminated at approximately 1345 hours at 98 percent power. The root cause of the event was that the increased valve response times were not anticipated by the operators. Corrective action consisted of revising the surveillance test procedure to indicate how long the test switch must be held in.
2131991002 | Haddam Neck | 02/27/1991 | 03/27/1991 | 9104010242 | <strong>Failure to Perform Reactor Trip Breaker Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1991, at 1000 hours, with the plant in Mode 1 at 100 percent power, Maintenance Department personnel, during an administrative review of Technical Specification surveillance performance, determined that a reactor trip breaker surveillance test was not performed prior to the September 3 and 25 and November 15, 1990 startups as required by the plant's Technical Specifications. The surveillance was last performed in July 23, 1990. The root cause was personnel error in that the new surveillance frequency for this test was not incorporated into the surveillance scheduling system. A plant load reduction was initiated at approximately 1000 on February 28, 1991 in accordance with plant Technical Specifications. The load reduction was terminated at 1200 hours upon receipt of an NRC waiver of the surveillance, and 100 percent power was achieved at 1616 hours. Corrective action consisted of adding the surveillance to the scheduling system and initiating a review of other Maintenance Department surveillances for similar problems. The reactor trip breakers were successfully tested during a subsequent shutdown on March 3, 1991. This event is reportable under 10CFR30.73 (a) (2) (i) (B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991003 | Haddam Neck | 03/01/1991 | 03/28/1991 | 9104020269 | <strong>Appendix R Design Deficiency Identified In Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1991, at approximately 0920 hours, with the plant in Mode 1 at 100 percent power, an engineering analysis concluded that the operability of the auxiliary feedwater system could be compromised during certain plant fires. A hot short on the control circuitry for either the motor operated valve CD-MOV-10 (condensate makeup line) or CD-MOV-17 (condensate dump line) could cause the valve(s) to open resulting in the demineralized water storage tank inventory draining to the condenser hotwell. The root cause was personnel error in that a previous modification to the control circuit for CD-MOV-10 was inadequate and the failure mode for CD-MOV-17 was not identified during the original Appendix R analysis. Immediate corrective action was to deenergize both MOV's in the closed position. Long term corrective action consists of maintaining the valves closed in Modes 1, 2 and 3 and allowing operation under certain conditions for up to seven days. This event is reportable under 10CFR50.73 (a) (2) (v) (B) as a condition that alone could have prevented the fulfillment of the safety function of a system needed to remove residual heat.
2131991004 | Haddam Neck | 03/01/1991 | 04/24/1991 | 9104290089 | <strong>Plant Shutdown Due to Inadequate CAR Fan Air Flow</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1991, at 1635 hours, with the plant in Mode 1 at 100 percent power, all four containment air recirculation (CAR) fans were declared inoperable following an engineering review of the surveillance testing techniques used to measure CAR fan air flow. The review indicated a potential for the air flow measurements being nonconservatively high and the actual air flows nonconservatively low. A plant shutdown was immediately initiated in accordance with Technical Specification 3.0.3 and the plant entered Mode 5 (cold shutdown) on March 2, 1991, at 1343 hours. Subsequent testing by a different method confirmed that the air flow for all four CAR fans was below the amount required by the Technical Specifications. The root cause of the event was application of an inadequate test method. Corrective action consisted of adjusting the fans' flow vanes and satisfactorily reperforming the test with a revised and validated test method. This event is reportable under 10CFR50.73(a)(2)(i)(A) and 10CFR50.73(a)(2)(i)(B). This supplemental report has been issued to provide additional information on the safety assessment of the event.
2131991005 | Haddam Neck | 03/04/1991 | 03/28/1991 | 9104020198 | <strong>Feedwater Regulator Bypass Check Valves Fail Leakage Test</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1991, at approximately 0830 hours, with the plant in Mode 5 (cold shutdown) the failure of the feedwater (FW) regulator bypass line check valves (FW-CV-135-1, 2, 3, 4) to meet leakage criteria during a surveillance test conducted on March 4, 1991, was determined to be reportable. The root cause is attributed to valve chatter which accelerated the wear of the valve seat. It is believed that the valve chatter was due to leakage flow through the normally closed feedwater bypass valves. Corrective action consisted of replacing the check valves with more durable valves. The valves were successfully retested following replacement. The adequacy of this corrective action will be confirmed by performing a seat leakage test during the next cold shutdown. This event is reportable under 10CFR50.73 (a) (2) (v) (D) since this condition alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
2131991006 | Haddam Neck | 03/05/1991 | 04/02/1991 | 9104080030 | <strong>Calibration of Containment Pressure Transmitters Violated Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1991, at 1430 hours, with the plant in Mode 5 (cold shutdown) Instrumentation and Control Department personnel, during a review of an Engineering evaluation of containment instrument penetrations, determined that the calibration of two containment pressure transmitters on August 22, 1990, resulted in a violation of containment integrity. At the time of the event the plant was in Mode 1 at 9 percent power. The root cause of the event was misapplication of the Technical Specification definition of containment integrity as it relates to the manipulation of process connections during instrument calibrations. Corrective action consisted of revising the affected surveillance procedures in addition to other procedures to preclude performance of the tests during periods in which containment integrity is required. This event is reportable under 10CFR50.73(a)(2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991007 | Haddam Neck | 03/08/1991 | 04/05/1991 | 9104080317 | <strong>Surveillance Procedure for Manual Reactor Trip Buttons Determined Inadequate</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1991, at 1500 hours, with the plant in Mode 5 (cold shutdown), Operations Department personnel, during an administrative review of Technical Specification surveillance performance, determined that both manual reactor trip pushbuttons on the main control board were not being tested prior to each reactor criticality as required by the plant's Technical Specifications. The reactor startup procedure only required the testing of one of the two pushbuttons. The root cause of the event was the failure to adequately incorporate Technical Specification surveillance requirements into appropriate implementing procedures. Corrective action consisted of revising the reactor startup procedure to require testing of both reactor trip pushbuttons. Both pushbuttons were satisfactorily tested on March 13, 1991. The review of all Operations Department Technical Specification surveillance requirements is continuing to ensure there are no other similar problems. This event is reportable under 10CFR50.73(a)(2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991008 | Haddam Neck | 03/08/1991 | 04/05/1991 | 9104080352 | <strong>Automatic Reactor Trip Signal Initiated While Filling Pressurizer</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1991, at 2313 hours, with the plant in Mode 5 (cold shutdown) an automatic actuation of the reactor protection system occurred due to a control room operator overfilling the reactor coolant system (RCS). The root cause of the event was personnel error in that a control room operator failed to close a motor operated valve (MOV) that supplies makeup water to the RCS prior to pressurizer level reaching the high level trip setpoint. Corrective action consisted of counseling the operator, revising the operator training program to address the lessons learned and evaluating the adequacy of the location of the MOV's control switch. This event is reportable under 10CFR50.73(a)(2)(iv) since an automatic actuation of the reactor protection system occurred which was not part of a preplanned sequence during testing or normal operation.
2131991009 | Haddam Neck | 03/13/1991 | 04/12/1991 | 9104180140 | <strong>Core Deluge Motor Operated Valve Discovered Closed in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1991, at 1600 hours, with the plant in Mode 3 (hot standby) an auxiliary operator conducting plant rounds discovered that the circuit breaker for core deluge isolation valve SI-MOV-873 was in the closed position contrary to the requirements of the plant's Technical Specifications. Technical Specification 4.5.1.b requires both SI-MOV-873 and its circuit breaker to be locked open prior to entering Mode 4. The operator immediately contacted the control room and was instructed to open and lock the circuit breaker for SI-MOV-873. Further investigation revealed that SI-MOV-873 itself was closed when the plant entered Mode 4 in violation of the same Technical Specification. It was also determined that this condition existed when the plant was in Mode 4 on March 2, 1991. The root cause of the event was the failure to incorporate Technical Specification surveillance requirements into appropriate implementing procedures. Corrective action consisted of revising those procedures that required the valve and/or the breaker to be closed in Mode 4. In addition, plant heatup procedures were revised to verify that the valve and its breaker are locked open prior to entering Mode 4. Long term corrective action consists of reviewing all Operations Department Technical Specification surveillance requirements to insure there are no other similar problems.
2131991010 | Haddam Neck | 03/13/1991 | 04/12/1991 | 9104180124 | <strong>Manual Containment Isolation Valve Opened in Mode 3</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1991, at approximately 0020 hours, with the plant in Mode 3 (hot standby) a control room operator reviewing the locked valve checklist noted that a manual containment isolation valve had been opened on March 13, 1991, to add nitrogen to the pressurizer relief tank (PRT). Since the plant was in Mode 3 at the time the valve was opened this event constituted a breach of containment integrity and a violation of the plant's Technical Specifications. The root cause of this event was personnel error in that a control room operator incorrectly determined that it was permissible to open this valve as long as a dedicated operator was standing by the valve in direct communication with the control room. Corrective action consisted of counseling the operator involved and issuing a notice to all operators regarding the lessons learned. In addition, a license amendment is being requested to allow operation of the valve under appropriate restrictions. This event is reportable under 10CFR50.73 (a) (2) (i) (B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991011 | Haddam Neck | 03/25/1991 | 04/23/1991 | 9104250409 | <strong>Channel Check of Subcooling Margin Monitor Determined Inadequate</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1991, at 1800 hours, with the plant in Mode 1 at 100 percent power, Operations Department personnel, during an administrative review of Technical Specification surveillance performance, discovered that data for the monthly channel check of the subcooling margin monitor was being obtained from the safety parameter display system (SPDS) instead of the inadequate core cooling (ICC) system. It was determined that this did not constitute a valid channel check. The root cause of this event was the failure to adequately incorporate Technical Specification surveillance requirements into appropriate implementing procedures. Corrective action consisted of revising the surveillance procedure to require that data for the channel check be obtained from the ICC cabinets. The monitor was subsequently checked with satisfactory results. A review of all Operations Department Technical Specification requirements is continuing to ensure there are no other similar problems. This event is reportable under 10CFR50.73(a)(2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991012 | Haddam Neck | 04/11/1991 | 05/09/1991 | 9105160242 | <strong>Sampling Frequency Exceeded With Effluent Monitor Out of Service</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1991, at 1530 hours, with the plant in Mode 1 at 100 percent power, Chemistry Department supervisory personnel noted that grab samples of service water effluent were not being collected and analyzed once per 12 hours as required by the plant's Technical Specifications. Grab samples were required to be taken as a result of the radiation monitor for service water effluent being taken out of service at 1026 on April 10, 1991. Although samples were drawn at 1030 and 1830 on April 10, 1991, the next sample was not taken until approximately 20 hours later at 1455 on April 11, 1991. The root cause of this event was personnel error. Corrective action consisted of counseling the personnel involved, discussing the lessons learned with Chemistry Department personnel and revising the Chemistry shift turnover log book to identify any ongoing Technical Specification requirements that are required to be performed. This event is reportable under 10CFR50.73(a)(2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991013 | Haddam Neck | 06/20/1991 | 07/16/1991 | 9107190168 | <strong>Load Reduction Due To Erratic Steam Flow Indication</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1991, at 1500 hours, with the plant in Mode 1 at 100 percent power, control room operators noted that the no. 1 steam generator steam flow indication was erratic and transferred the no. 1 feedwater regulating valve from automatic to manual to maintain proper feedwater control. Placing the valve in manual control defeats both channels of the steam generator overfill protection circuitry, therefore, a load reduction was initiated at 1518 hours in accordance with Technical Specification 3.0.3. At 1705 hours the NRC granted a temporary waiver of compliance with the feedwater isolation Technical Specification and the load reduction was terminated. The root cause of this event was inadequate licensee review of the initial feedwater isolation Technical Specification submittal. The erratic steam flow indication was a contributing cause, however, subsequent troubleshooting of the steam flow instrumentation did not reveal any apparent reason for the fluctuations. Corrective action consists of revising the Technical Specifications and reinforcing the need for increased attention to detail during the technical review of proposed Technical Specification changes. This event is reportable under 10CFR50.73 (a) (2) (i) (B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991014 | Haddam Neck | 07/17/1991 | 08/14/1991 | 9108210244 | <strong>Spent Fuel Pool Cooling System Isolated for Preplanned Maintenance</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1991, at 1000 hours with the plant in Mode 1 at 100 percent power, Operations Department personnel isolated service water to the spent fuel pool heat exchangers to support preplanned maintenance on the service water system. The root cause of this event was the need to remove the spent fuel cooling system from service to replace several pipe nipples in the service water system. Corrective action consisted of returning the spent fuel pool cooling system to service at 1755 hours following completion of the maintenance activities. This event is reportable under 10CFR50.73(a)(2)(v)(B) as a condition that alone could have prevented the fulfillment of the safety function of a system needed to remove residual heat.
2131991015 | Haddam Neck | 07/30/1991 | 08/27/1991 | 9109030245 | <strong>Potential for Heating Steam Pipe Break in Cable Spreading Area</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1991, at 1600 hours, with the plant in Mode 1 at 100 percent power, an engineering evaluation determined that the rupture of a 10 inch heating steam line in the cable spreading area of the service building could adversely affect safety related equipment due to pipe whip or jet impingement. The root cause appears to be an installation error during original construction in that the pipe supports were not consistent with the original design drawings. Immediate corrective action was to isolate the steam to the affected portion of the system. Short term corrective action is to reroute the piping. Long term corrective action consists of evaluating other areas for similar problems. This event is reportable under 10CFR50.73(a)(2)(v)(A) and (B) since this condition alone could have prevented the fulfillment of the safety function of a system needed to (A) shut down the reactor and maintain it in a safe shutdown condition and (B) remove residual heat.
2131991016 | Haddam Neck | 08/14/1991 | 09/11/1991 | 9109170095 | <strong>Spent Fuel Pool Cooling System Isolated to Clean Service Water Piping</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1991, at 0900 hours with the plant in Mode 1 at 100 percent power, Operations Department personnel isolated service water to the spent fuel pool heat exchangers to support preplanned maintenance on the service water system. The root cause of this event was the need to remove the spent fuel cooling system from service to clean the supply and return service water piping to the spent fuel pool heat exchangers. Corrective action consisted of returning the spent fuel pool cooling system to service at 1930 hours following the installation of temporary hoses which are providing cooling water to the heat exchangers during the cleaning process. The cleaning is expected to last approximately 4 weeks. This event is reportable under 10CFR50.73 (a) (2) (v) (B) as a condition that alone could have prevented the fulfillment of the safety function of a system needed to remove residual heat.
2131991017 | Haddam Neck | 08/23/1991 | 09/20/1991 | 9109240430 | <strong>Service Water Pump Strainers Declared Inoperable Due to River Silt</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1991, at 0940 hours, with the plant in mode 1 at 99 percent power, both service water headers were declared inoperable after all four service water pump discharge strainers indicated differential pressures in excess of allowable limits. Immediate action was taken to clean the strainers and each header was restored to operable status. Shortly thereafter, at 2100 hours, it was noted that the differential pressure gauges across two strainers, one in each header, were not indicating a differential pressure and again both service water headers were declared inoperable. Action was taken to exchange two indicators such that one header was returned to operable status within one hour. The two inoperable indicators were cleaned of river silt and returned to service at 1011 hours on August 24. The root cause of the event is excessive debris and silt suspended in the Connecticut River as a result of Hurricane Bob which passed by the area four days earlier. This event is reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications since it was necessary to implement Technical Specification 3.0.3.
2131991018 | Haddam Neck | 09/20/1991 | 10/18/1991 | 9110280023 | <strong>Spent Fuel Pool Cooling System Insolated for Heat Exchanger Cleaning</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1991, at approximately 0900 hours with the plant in Mode 1 at 100 percent power, Operations Department personnel isolated service water to the spent fuel pool (SFP) heat exchangers to support preplanned maintenance on the service water system. The root cause of this event was the need to remove the spent fuel cooling system from service in order to swap the temporary hoses supplying the 'A' SFP heat exchanger to the 'B' SFP heat exchanger which will allow cleaning of the 'A' heat exchanger. Corrective action consisted of returning the 'B' spent fuel pool heat exchanger to service at 1500 hours following the re-installation of the temporary hoses. The cleaning is expected to last approximately 2 weeks. This event is reportable under 10CFR50.73 (a) (2) (v) (B) as a condition that alone could have prevented the fulfillment of the safety function of a system needed to remove residual heat.
2131991019 | Haddam Neck | 10/04/1991 | 11/01/1991 | 9111120142 | <strong>Fire Protection Sprinklers Declared Inoperable Due to Erection of Staging</strong><br /><i>Abstract:&nbsp;</i>A 0230 hours on October 4, 1991, with the plant in Mode 1 at 100 percent power a plant operator reported that staging erected under the High Pressure Turbine was partially obstructing the flow pattern of 3 fire protection piping sprinkler heads. The area involved has a total of 6 sprinkler heads for fire protection. The staging was installed at approximately 1500 hours on October 3, 1991. Operators determined that the sprinkler heads were unable to perform their design function and declared them inoperable. This condition is a violation of Technical Specification 3.7.6.2a.4. The required action was taken by posting an hourly fire watch patrol. The root cause of this event was the unfamiliarity of the requirement for a fire sprinkler head to be capable of achieving 100 percent of its flow pattern. Corrective actions taken included the removal of staging that blocked the flow pattern of the sprinkler heads. In addition, a meeting with job supervisors and workers was held in which the lessons learned from this event were discussed. <br /><br /> This event is reportable per 10CFR50.73 (a)(2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2131991020 | Haddam Neck | 10/18/1991 | 11/15/1991 | 9111190449 | <strong>Inappropriate Removal of a Reactor Protection System Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1991, at 1525 hours, with the plant in Mode 1 (power operation) at 35% power, plant operators declared the channel 4 steam flow-feed flow mismatch trip to be out of service. In accordance with Technical Specification Table 3.3-1, action statement 5, a trip signal was inserted for the inoperable channel within one hour at 1601 hours. At 2034 hours, with the plant in Mode 2 (startup) at less than 1% power, the trip was removed prior to returning the steam flow-feed flow signal to operable status. On October 18, 1991, at 1006 hours, it was recognized that it was inappropriate to have removed the trip and it was reinserted. The root cause of the event is failure of the Control Room operators to consult the Technical Specifications prior to having an inserted trip signal removed. Corrective action includes counseling the operators involved, reviewing the event with all Operations Department personnel, and the incorporation of lessons learned into the licensed operator training program. This event is reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131991021 | Haddam Neck | 10/19/1991 | 03/12/1992 | 9203190110 | <strong>Reduction in Residual Heat Removal Capability Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1991, with the plant in Mode 4 (hot shutdown) and forced Reactor Coolant System (RCS) flow being maintained only in loop 3, a failure of the RCS loop 3 hot leg loop isolation valve caused a major reduction in forced reactor coolant flow. The valve stem broke allowing the disc assembly to fall. The cause of the event was stress corrosion cracking of the valve stem. Corrective action consisted of installing a new stem. The stems of the other seven loop isolation valves were ultrasonically examined for damage. No other damaged stems were discovered. This event is reportable under 10CFR50.73(a)(2)(v)(B) since the valve failure impeded the loop's function of removing residual heat. Forced RCS flow was reestablished in 17 minutes by starting the loop 4 Reactor Coolant Pump (RCP). During the starting of the loop 4 RCP, the provision of the idled loop startup Technical Specification (3.4.1.11) were not fulfilled in order to expedite the reestablishment of forced flow in the RCS and limit RCS heatup. This event is reportable under 10CFR50.73(a)(2)(i)(B) since it is a condition prohibited by the plant's Technical Specifications.
2131991022 | Haddam Neck | 11/04/1991 | 12/04/1991 | 9112100218 | <strong>Leaking Flange on Residual Heat Removal to Charging System Crosstie Piping</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991, at 0015, with the plant in Mode 6 (Refueling), a blank flange on a line which connects the discharge of the Residual Heat Removal (RHR) system to the Chemical and Volume Control system (CVCS) was found to be leaking. Leakage was estimated to be approximately 1 gallon per minute. At the time of the event, the RHR system was in operation and seal water to the Reactor Coolant Pumps (RCP's) was being supplied by the RHR pumps via the cross-tie line to the CVCS. Initial corrective action involved starting a charging pump to supply RCP seal water from the Volume Control Tank and then isolating and depressurizing the RHR to CVCS cross-tie line to stop the leakage from the flange. A prompt report of this event was made under 10 CFR 50.72(b)(2)(i). This event is reportable under 10 CFR 50.73(a)(2)(ii) as a condition that could have resulted in the plant being in an unanalyzed condition, since the RHR to CVCS cross-tie line is one of the pathways for containment sump recirculation flow following a loss of coolant accident. Leakage from this flange during sump recirculation operation after an accident could have resulted in adverse radiological consequences. Corrective action will involve a plant modification to replace the blank flange with a welded cap.
2131991023 | Haddam Neck | 11/10/1991 | 05/14/1992 | 9205190307 | <strong>Steam Generator Eddy Current Testing Results Classified as Category C-3</strong><br /><i>Abstract:&nbsp;</i>Scheduled Steam Generator (SG) Eddy Current Testing (ECT) has been conducted during the 1991/1992 refueling outage in accordance with ASME Section XI and Technical Specification 4.4.5. On November 9 at approximately 1600 hours, with the plant in Mode 6 (Refueling), it was determined that analyzed ECT data placed SG No. 2 into the C-3 Category. A prompt report of this event was made under 10CFR50.72 (b)(2)(i). Subsequently, on November 10, 1991, analyzed ECT results for SG No. 1 placed it in Category C-3, thus requiring expansion of the ECT program to 100 percent of the tubes in all four SG's. The major cause of the tube defects was attributed to primary water stress corrosion cracking and, to a lesser extent, pitting. As a result of the inspections, a total of 130 tubes were plugged. This supplemental report is being issued to provide additional information on the identified causes and corrective action taken. This event is reportable per 10CFR50.73(a)(2)(i)(B) since it involves a condition prohibited by the plant's Technical Specifications.
2131991024 | Haddam Neck | 11/14/1991 | 02/07/1992 | 9202100306 | <strong>Inoperable Containment Isolation Valve Due to a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1991, at 1600, with the plant in Mode 1 at 100% power, a design deficiency was identified that could possibly prevent the containment isolation valve inside of containment for the reactor coolant letdown line (LD-TV-230) from closing following receipt of a containment isolation signal. Immediate corrective actions consisted of declaring LD-TV-230 inoperable and isolating the letdown line containment penetration with a closed manual valve in accordance with Technical Specification 3.6.3.c. An alternate path for reactor coolant letdown was established via the reactor coolant system drain line back to the chemical and volume control system. The normal letdown flowpath through LD-TV-230 was reestablished after approximately 14 hours, following implementation of a design change. At the time of the event, a detailed operability evaluation had been initiated. On November 14, 1991, the detailed operability evaluation concluded that LD-TV-230 was inoperable with this condition existing. This event is reportable under 10CFR50.73 (a)(2)(i)(B), since the plant was in operation with a condition prohibited by the Technical Specifications.
2131991025 | Haddam Neck | 11/14/1991 | 12/11/1991 | 9112170340 | <strong>Failure to Maintain Containment Penetration Alignment During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1991, with the plant in Mode 6 and core alterations in progress, operators discovered that all containment penetrations had not been properly aligned as required by plant Technical Specification 3.9.4. Core alterations were immediately halted and containment penetrations were verified to be properly aligned. A prompt report of this event was made under 10CFR50.72 (b) (2) (iii). The cause of this event was procedural inadequacy. Corrective actions involve revision of procedures to provide a separate clearance for containment penetrations, walkdown verification of containment penetrations, and enhanced measures for controlling the containment boundary once it is established. Lessons learned will be incorporated into operator training programs. This event is reportable under 10CFR50.73 (a) (2) (v) (C) as a condition that alone could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material.
2131991026 | Haddam Neck | 11/19/1991 | 12/18/1991 | 9112270264 | <strong>Missed Surveillance on Emergency Diesel Generator EG-2B Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991, at 0800 hours, with the plant in a refueling outage and the core offloaded to the spent fuel pool, Operations personnel discovered the 31 day surveillance for emergency diesel generator EG-2B had not been performed as required for the month of October. The redundant diesel generator (EG-2A) was inoperable having been removed from service on October 21 for maintenance purposes. Upon discovery, the surveillance was immediately and successfully performed. The root cause of the event was a personnel error in updating the status board utilized for tracking and scheduling Operations Department surveillances. The erroneous information from the status board was then transferred to the Control Room surveillance tracking procedure. Corrective actions to assure the two tracking systems remain independent of each other include requiring independent verification of all status board entries and requiring Control Room personnel to personally review each completed surveillance procedure prior to updating the Control Room surveillance tracking procedure. This event is reportable under 10CFR50.73 (a)(2)(i)(B) since it is a condition prohibited by the plant's Technical Specifications.
2131991027 | Haddam Neck | 11/21/1991 | 12/20/1991 | 9112270021 | <strong>Missed Surveillance on Main Stack Gas Sampler Flow Rate Monitor Due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1991, with the plant in a refueling outage and the core offloaded to the spent fuel pool, it was determined that the required test interval for surveillance procedure SUR 5.2-84, "Replacement of the Containment Gas and Main Stack Gas Sampler Flow Rate Monitor", had been exceeded by approximately ten weeks. The Haddam Neck Technical Specifications require that the main stack gas sampler flow rate monitor be calibrated once every eighteen months. The root cause of this event was personnel error in misinterpretation of the plant Technical Specification surveillance frequency requirements. The surveillance was subsequently performed on November 21, 1991 with satisfactory results. This event is reportable under 10CFR50.73(a)(2)(i)(B) since it involves a condition prohibited by the plant's Technical Specifications.
2131991028 | Haddam Neck | 11/25/1991 | 12/24/1991 | 9112300226 | <strong>Residual Heat Removal System Piping Design Analysis Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1991, at 1040, with the plant in a refueling outage and the core offloaded to the spent fuel pool, an engineering review of a previously performed pipe stress analysis on the Residual Heat Removal (RHR) system determined that the seismic piping analysis had incorrectly assumed that the RHR system boundary terminated at valve RH-V-783. This error resulted in a section of RHR system piping downstream of RH-V-783 having not been adequately analyzed. A prompt report of this event was made under 10CFR50.72(b)(2)(i). The cause of this event was an engineering design deficiency. The corrective action involved a re-analysis of the omitted section of piping. Based on the re-analysis of this pipe section, an additional pipe restraint is required. This restraint will be added prior to plant startup from the current refueling outage. This event is reportable under 10CFR50.73(a)(2)(v)(D) as a condition that alone could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident.
2131991029 | Haddam Neck | 12/05/1991 | 01/03/1992 | 9201070350 | <strong>Potential Steam Line Break Protection System Inoperability Due to Postulated High Energy Line Breaks</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1991 at 1550 hours, with the plant in a refueling outage and the core off-loaded to the spent fuel pool, the results of an engineering analysis indicated that the maximum postulated temperature which could be expected in the Terry Turbine Building during a High Energy Line Break (HELB) would be approximately 320 degrees (F). The engineering analysis further concluded that the environmental conditions presented by the HELB would render the Steam Line Break (SLB) detection portion of the Reactor Protection System (RPS) inoperable. Based on these findings, a prompt report was issued per 10CFR50.72(b)(2)(iii)(B) and (D) on December 5, 1991. This event is being conservatively reported under 10CFR50.73(a)(2)(vii)(A) as the postulated environmental conditions in the Terry Turbine Building would have resulted in all four channels of SLB detection being inoperable. Corrective action will consist of relocating the SLB detection transmitters. This action will be complete prior to startup from the current refueling outage.
2131991030 | Haddam Neck | 12/23/1991 | 01/22/1992 | 9201290071 | <strong>Potential Valve Inoperability and Excessive Leakage Due to a Design Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1991 at 1130 hours, with the plant in a refueling outage and the core offloaded to the spent fuel pool, an engineering review determined that the teflon seat material in several ball valves in the containment sump recirculation flowpath could degrade during post LOCA containment sump recirculation, causing unacceptable system leakage. On January 13, 1992, further review determined that additional valves in the sump recirculation flow path and in isolation or containment boundary service were subject to the same phenomenon. This review resulted from followup to other ball valve problems as discussed in LERs 89-006 and 90- 024. The root cause of the event is a design inadequacy, in that, at the time these valves were specified and installed, the ability of teflon seat material to function under specified radiation and temperature environments was not well understood. Corrective action consists of blanking or replacing the affected valves. This event is reportable under 10CFR50.73 (a)(2)(v)(C) for those valves that could result in unacceptable post LOCA release of radioactive materials and under 10CFR50.73(a)(2)(i)(B) for those containment isolation or boundary valves that could become inoperable under post LOCA conditions.
2191991001 | Oyster Creek | 03/01/1991 | 07/26/1991 | 9108050239 | <strong>Technical Specification Violation Due to Missed Firewatch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1991 at 1755 hours deluge systems were taken out of service without establishing a continuous firewatch in accordance with Technical Specifications. The cause of this occurrence is attributed to a failure to adequately control firewatch activities. This event is considered to have minimal safety significance because all of the fire detection sensors and systems for the affected areas were operable and would have provided an alarm to the control room had a fire condition occurred. A fire condition therefore would have been detected early and the deluge systems could have been manually actuated or any one of eight hose stations utilized to extinguish a fire. Corrective action includes a lessons-learned lecture for fire watch personnel and a revision to the procedure controlling fire watches.
2191991002 | Oyster Creek | 02/21/1991 | 12/13/1991 | 9112270097 | <strong>Local Leak Rate Test Results in Excess of Limits Due to Valve Degradation</strong><br /><i>Abstract:&nbsp;</i>During the 13R Refueling Outage, local leak rate testing (in accordance with 10CFR50, Appendix J) identified a Main Steam Isolation Valve (MSIV) with a leak rate in excess of the acceptance criteria of 12.08 SCFH at 20 psig as specified in Technical Specifications 4.5.F.2. The safety significance of this discovery is considered minimal since the other MSIV in the same header met the local leak rate test requirements. <br /><br /> Subsequent local leak rate testing identified a pair of isolation valves (in series) with a potential leak rate in excess of the acceptance criteria of 6 0% of the maximum allowable limit (La) at 35 psig as specified in Technical Specifications 4.5.F.1. Leakage was caused by the age of a soft disc seat on one valve and by a deformed seat due to improper valve installation on the other. <br /><br /> These leaking valves were repaired and subsequent local leak rate testing verified that leakage rates were within the acceptance criteria. <br /><br /> Due to an improper interpretation of reporting requirements implemented by a recent Technical Specification Amendment, this condition was not reported within 30 days as required by 10CFR50.73.
2191991003 | Oyster Creek | 06/13/1991 | 08/01/1991 | 9108090126 | <strong>Tech Spec Violation Due to Unlocked High Radiation Area Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>An area designated as a locked high radiation area was found unlocked. This condition is prohibited by Plant Technical Specification 6.13.2 and is being reported voluntarily. A critique of this event was conducted and concluded that procedure controls, General Employee Training, and Radiation Control Technician Training with respect to High Radiation Areas are all adequate and did not contribute to this event. This event was caused by several personnel errors all of which were contrary to an approved plant procedure. During the past two years at least ten thousand entries have been made to locked high radiation areas without incident. The personnel directly responsible for this event were contractor personnel and were determined to be negligent in performing their duties.
2191991004 | Oyster Creek | 08/03/1991 | 08/27/1991 | 9109040326 | <strong>Failure to Set Continuous Fire Watch Due to Personnel Error & Inadequate Guidance</strong><br /><i>Abstract:&nbsp;</i>On August 3, 1991 a trouble alarm was received for a fire zone on the 51' elevation of the Reactor Building. The cause of the trouble alarm could not be determined, but failure of a detector circuit was recognized as a potential problem. An hourly fire watch was set, although a continuous watch is required for detector circuit failure which results in the inoperability of the associated fire suppression system. On August 5th, troubleshooting determined that detectors for the affected circuit were disabled and that the deluge system for this area would not have automatically initiated, rendering it inoperable. The failure to set the appropriate fire watch is attributed to personnel error, inadequate guidance, and the failure to take prompt action in evaluating the problem. This event is considered to have minimal safety significance because the other fire detection circuit in this area would have alarmed in the event of a fire and operators would still have been able to initiate the associated deluge system manually. Once it was recognized that the area deluge system was inoperable, a continuous fire watch was established. Guidance has been given to the operators via memo that a deluge system in a fire area is to be considered inoperable when a detection system trouble alarm is received, until it can be proven otherwise.
2191991005 | Oyster Creek | 08/22/1991 | 09/23/1991 | 9110080197 | <strong>Automatic Reactor Scram Due to Loss of Feedwater Flow Caused by a Grounded Condensate Pump Motor</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1991, at 0306 hours, a reactor scram occurred due to low reactor water level. The cause of the low reactor water level was a loss of feedwater flow due to a main feed pump trip on low suction pressure. The root cause of this event was a grounded condensate pump motor which led to a condensate pump trip while the plant was operating above 80% power. The motor was replaced. <br /><br /> The shrink in reactor water level caused by the scram and the reduction in feedwater flow caused reactor water level to reach the double low Reactor Protection System (RPS) setpoint which actuated appropriate Engineered Safety Features. <br /><br /> A second event being reported is a procedure violation which occurred at 1012 hours. While plant cooldown to cold shutdown conditions was in progress, all five reactor recirculation discharge valves were shut simultaneously with reactor temperature above 212 degrees F. The plant achieved cold shutdown at approximately 1800 hours.
2191991006 | Oyster Creek | 10/01/1991 | 10/31/1991 | 9111150047 | <strong>Degradation of Instrument Response Due to Inadequate Design Control of Instrument Snubber Use</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1991, a routine calibration of the pipe break sensors was performed on Isolation Condenser Systems 1 and 2. During the surveillance for each instrument, a check revealed a degradation in the flow dampening snubber performance for seven of the eight sensors when compared to the procedure criteria. The flow dampening snubbers were removed and tested. Based upon limited testing of the removed snubbers and an extrapolation of the test results, the pipe break sensors would have experienced a delay in response time such that the design basis isolation valve closure time of sixty seconds would not have been met for all postulated pipe break events. The cause of this occurrence has been attributed to inadequate design control. During the recent 13R refueling outage, the existing snubbers were replaced with a different manufacturer and type snubber without performing an evaluation to assess the impact on the sensor response time. Corrective action consisted of removing the snubbers from the eight pipe break sensors. Additional corrective action will consist of performing a review of other applications where snubber fittings are used on critical plant instrumentation to ensure appropriate use and proper design documentation.
2191991007 | Oyster Creek | 11/02/1991 | 11/27/1991 | 9112120221 | <strong>Air Ejector Off-Gas Isolation Time Delay Found Out of Specification High During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>During Surveillance testing performed on November 2, 1991, it was noted that the Off-Gas System isolation function exceeded the 15 minute delay limit specified by Technical Specifications. This condition is considered to have existed since August 24, 1991, when a faulty time delay relay was replaced as part of a modification. A technical evaluation of the replacement time delay was not adequately performed during the modification process. Vendor documentation on instrument setpoint accuracy and temperature effects on repeatability were not included in the surveillance test "as left" setpoint determination until after the November 2, 1991, surveillance. The surveillance procedure "as-left" setpoint was changed on November 4, 1991, to preclude exceeding a Technical Specification limit.
2191991008 | Oyster Creek | 11/12/1991 | 12/13/1991 | 9112270101 | <strong>Feedwater Nozzle Calibration Reveals Operation of Reactor in Excess of Licensed Limit</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1991 a difference between test measured and indicated feedwater flow was discovered as a result of a special lithium nitrate flow test. This difference was 1.19% in the non conservative direction with respect to the feedwater flow impact on the heat balance. <br /><br /> The exact cause of the 1.19% difference in feedwater flow cannot be determined. Existing plant instrumentation accuracy, calibration techniques, a change in nozzle discharge coefficient or feedwater piping errosion upstream of the feedwater nozzles may have contributed to the difference observed. <br /><br /> Oyster Creek thermal limits are based, in part, on a 1.76% standard deviation for the uncertainty in feedwater flow. Therefore, the error found in the feedwater flow was within the accepted uncertainty and the safety significance of this event is minimal. Indicated reactor power was reduced by 1.2% to account for the feedwater flow difference. The heat balance calculations were revised to account for the observed difference in feedwater flow.
2201991001 | Nine Mile Point 1 | 01/08/1991 | 04/25/1991 | 9104300420 | <strong>Reactor Scram Due To Spurious Non-Coincident Logic Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1991, at 0327 hours, Nine Mile Point Unit 1 (NMP1) experienced a full reactor scram and a Main Steam Isolation Valve (MSIV) isolation. The mode switch was in the REFUEL position, all control rods were at position 00, reactor coolant temperature was 163 degrees Fahrenheit, and reactor pressure was 0 Psig. Water level was being lowered following the performance of a reactor vessel inservice leak test. The inside MSIV's closed due to the isolation signal and the outside MSIV's were already closed due to the hydro. <br /><br /> The cause of the event was determined to be a spurious actuation of Reactor Protection System (RPS) non-coincident logic, specifically Condenser Low Vacuum and Main Steam Isolation Closed Bypass Logic. <br /><br /> Corrective actions taken were to perform checks, troubleshooting, and monitoring of components that make up the Condenser Low Vacuum and Main Steam Isolation Closed Bypass logic. The results of these corrective actions did not indicate any equipment malfunction or degradation that could have contributed to a spurious actuation.
2201991002 | Nine Mile Point 1 | 02/12/1991 | 03/12/1991 | 9103210060 | <strong>TURBINE CONTROL VALVE LINKAGE STICKING RESULTING IN A REACTOR SCRAM AND EMERGENCY VENTILATION SYSTEM INITIATION</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 078%. ON FEBRUARY 12, 1991, AT 0942 HOURS, WITH THE REACTOR MODE SWITCH IN THE 'RUN' POSITION, REACTOR POWER AT ABOUT 78%, NINE MILE POINT UNIT 1 (NMP1) EXPERIENCED A FULL REACTOR SCRAM ON HIGH NEUTRON FLUX. THE TURBINE CONTROL SYSTEM HAD BEEN EXPERIENCING SMALL CONTROL VALVE POSITION OSCILLATIONS (<4%) DUE TO SUSPECTED PRESSURE REGULATOR PROBLEMS. AT 0942 HOURS THE TURBINE CONTROL VALVES CLOSED FROM APPROX. 83% OPEN TO 54% OPEN. THIS CAUSED THE REACTOR PRESSURE TO INCREASE FROM 1005 PSIG TO 1043 PSIG CAUSING NEUTRON FLUX TO INCREASE TO ABOUT 100%, WHICH WAS ABOVE THE AVERAGE POWER RANGE MONITOR (APRM) FLOW BIASED SCRAM SETPOINT OF ABOUT 100%. HIGH PRESSURE COOLANT INJECTION (HPCI) WAS INITIATED. THE EMERGENCY VENTILATION SYSTEM WAS INITIATED. THE CAUSE OF THE CONTROL VALVE PARTIAL CLOSURE PROBLEM WAS DUE TO THE PRIMARY VALVE LIMIT STOP LINKAGE BUSHING STICKING. THE STICKING LINKAGE CAUSED A MISOPERATION OF THE CONTROL VALVES. THE IMMEDIATE CORRECTIVE ACTION WAS TO RESPOND TO THE SCRAM AND TO PERFORM A NORMAL COOLDOWN OF THE REACTOR. THE CAUSE OF THE CONTROL VALVE OSCILLATIONS WAS INVESTIGATED.
2201991003 | Nine Mile Point 1 | 02/23/1991 | 03/25/1991 | 9104010359 | <strong>Reactor Scrams Due To Spurious Trips Of Neutron Monitor Caused By Noise And Inadequate Procedural Controls</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1991, at 0047 hours, Nine Mile Point Unit 1 (NMP1) experienced a full reactor scram when a trip signal was received on Reactor Protection System (RPS) Channel 12 due to a spike on Intermediate Range Monitor (IRM) 16. At the time of the event, the unit was in a mid-cycle outage with the mode switch in "REFUEL" an all control rods at position 00. The cause of the event was a spurious upscale spike of IRM 16 in RPS Channel 12, coincident with a manual half scram inserted on RPS Channel 11 required by an ongoing surveillance procedure. <br /><br /> On March 8, 1991, at 2206 hours, NMP1 experienced a full reactor scram due to coincident spurious upscale spikes on IRM 11 and IRM 16. At the time of the event, the Unit was in a mid-cycle outage with the mode switch in "REFUEL", control rod power off, Control Rod Drive (CRD) pumps off, all CRD accumulators discharged, and all control rods at position 00. At 2207 hours, a second reactor scram occurred from a high level in the scram discharge volume. The cause of the second scram was inadequate procedural control.<br /><br /> Immediate corrective actions taken in these events was to reset the scram, bypass IRM 16, and perform NMP1 procedure N1-RAP-6, "Post Reactor Scram Analysis and Evaluation".
2201991004 | Nine Mile Point 1 | 03/15/1991 | 04/15/1991 | 9104230235 | <strong>Operation of NMP1 Above Maximum Lake Temperature of Containment Spray due to Inadequate Design Basis and Configuration Control</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1991, while Nine Mile Point Unit 1 (NMP1) was in Cold Shutdown it was determined that NMP1 has operated in the past with Lake Temperatures above the maximum allowable lake temperature. Also, the values for maximum lake temperature, flow rate and fouling factor used for calculating the heat removal capacity of the Containment Spray Heat Exchangers may have been non-conservative. <br /><br /> The cause of the events were Standards, Policies and Administrative Controls that in the past, were less than adequate to implementing Design Basis Information and Configuration Control.<br /><br /> Actions taken were to write and issue a Technical Specification Interpretation on Maximum Lake Temperature and the required action should that temperature limit be exceeded. Procedures and instructions were revised to reflect this limit. Shift briefings were used to inform Control Room Operators of the new maximum lake temperature. The long term corrective action will be to complete the Design Basis Reconstitution for the Containment Spray system and to incorporate that basis in the required documents. This will ensure that all of the required values for the Containment Spray System are known and are being met.
2201991005 | Nine Mile Point 1 | 02/24/1991 | 05/10/1991 | 9105210264 | <strong>Local Leak Rate Tests Exceed Regulatory Limit</strong><br /><i>Abstract:&nbsp;</i>During the Nine Mile Point Unit 1 (NMP1) midcycle outage (2/19/91 to 3/28/91) with primary containment not required, the sum of the "as found" Type B and C test results, based on Maximum Pathway Leakage Rate (MXPLR) exceeded the allowable limit (0.60 La) as defined in 10CFR50 Appendix J. Under this condition, the primary containment is considered inoperable with respect to providing a leakage boundary and represents a degradation of a principal safety barrier. <br /><br /> The root cause for this event was normal valve wear and small amount of impurities deposited on the valve seating surfaces. <br /><br /> The immediate corrective action was to declare the valves inoperable, write Occurrence Reports to document failures and issue Work Requests to inspect the valves and repair as necessary. The Local Leak Rate Test was again performed with satisfactory results that were within 10CFR50 Appendix J and Technical Specification limits.
2201991006 | Nine Mile Point 1 | 05/08/1991 | 11/14/1991 | 9111270152 | <strong>Containment H sub 2/O sub 2 Monitoring Inoperable due to Non- Safety Related Gas</strong><br /><i>Abstract:&nbsp;</i>During the performance of N1-ISP-201-M020, on December 11, 1990, at approximately 2025, #11 and #12 Containment Hydrogen and Oxygen monitors were found to contain non-safety related calibration gases. The mode switch was in the RUN position and reactor power was at 1811 MW. An evaluation was performed by Niagara Mohawk Licensing Department for past operability. It has determined that the calibration gas should have been safety related since December 10, 1987. <br /><br /> The cause of this condition was a programmatic deficiency. The specific cause resulted from a lack of guidelines or a program that addresses necessary actions and reviews which should take place when components or systems safety classifications are changed from non-safety to safety related. <br /><br /> Corrective actions taken were to initiate the pre-planned alternate sampling method, to install safety related calibration gas bottles and revise procurement requirements to ensure installation of safety related gases in the future. Special Report NMP73977 dated December 22, 1990, was written as required by Tech Specs.
2201991007 | Nine Mile Point 1 | 06/29/1991 | 07/23/1991 | 9107290246 | <strong>Engineered Safety Feature Actuation due to a Damaged Cable</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1991, at 1724 hours and July 1, 1991, at 1635 hours, Nine Mile Point Unit 1 (NMP1) experienced actuations of an Engineered Safety Feature (ESF). Specifically, initiation of Reactor Building Emergency Ventilation (RBEVS) and isolation of Reactor Building Normal Ventilation. At the time of both events, the plant was operating at 100 percent power with the mode switch in "RUN". <br /><br /> The cause of both events was determined to be a blown fuse. The root cause of both events was determined to be a damaged cable. <br /><br /> The corrective actions taken for both events were to verify that an actual high radiation condition did not exist, issue work requests to investigate and correct and to return the Ventilation System to normal operation. Other corrective actions to be taken include replacement of the cable, issue a Lessons Learned Transmittal, and to evaluate a modification of the RBEVS logic.
2201991008 | Nine Mile Point 1 | 07/18/1991 | 08/19/1991 | 9108230043 | <strong>Reactor Scram due to Neutron Monitoring Trip While Performing a Controlled Shutdown</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1991, at 0840 hours, Nine mile Point Unit 1 (NMP1) experienced an unplanned reactor scram on Intermediate Range Monitoring System (IRM) HI HI while in the process of a controlled plant shutdown. At the time of the event, the mode switch was in STARTUP with reactor coolant pressure and temperature at approximately 893 pounds per square inch gauge (psig) and 529 degrees Fahrenheit (degrees F), respectively. The reactor was operating at approximately 3% of rated thermal power. <br /><br /> The reactor scram occurred while attempting to terminate an unanticipated reactor pressure decrease. Possible causes are: neutron flux spike due to pressure perturbations resulting from isolating an auxiliary steam load, or spurious spiking of the IRM neutron monitors due to induced noise. <br /><br /> Corrective actions have been taken to address the equipment deficiencies that contributed to the reactor pressure decrease and to improve the Operations response in such situations (generation of a Lessons Learned Transmittal and revision of operating procedures for isolating steam loads at low power).
2201991009 | Nine Mile Point 1 | 08/12/1991 | 11/04/1991 | 9111180121 | <strong>Plant Operated Outside of Design Basis and in Violation of Technical Specification due to Personnel Error Caused by Poor Work Practices</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1991, at 0130 hours, it was determined that Nine Mile Point Unit 1 (NMP1) was in a condition outside the design basis of the plant. Specifically, the Battery Charger output breaker to Battery Board #12 trip open setpoint was at a value whereby the Battery Charger was prevented from performing its required safety function. At the time of this determination, the Mode Switch was in the "RUN" position with the reactor at 97 percent power. <br /><br /> The root cause of this event was a personnel error caused by poor work practices in that the design analysis and design review failed to identify the deficiency. <br /><br /> Corrective actions consisted of the completion of a Plant Change Request to increase trip open setpoint to an appropriate value, performing a Battery Charger Breaker coordination calculation, verifying Battery #11 operable and conducting an accountability meeting. To prevent recurrence, procedures will be revised and a Lessons Learned Transmittal will be issued. To assess potential impact to other electrical equipment/systems, a review of setpoint changes made via I&C Setpoint Program will be conducted.
2201991010 | Nine Mile Point 1 | 09/09/1991 | 10/02/1991 | 9110110240 | <strong>Engineering Safety Feature Actuation Due to Poor Man - Machine Interface</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1991, at 1716 hours, Nine Mile Point Unit 1 (NMP1) experienced an actuation of an Engineering Safety Feature (ESF). Specifically, an isolation of #12 Emergency Cooling Loop. At the time of the event, the plant was operating at approximately 97 percent power with the mode switch in the "RUN" position.<br /><br /> The primary cause of the event was the combination of poor human factors design of a calibration unit, poor environmental conditions, degraded hardware and the failure of the technicians to appreciate the consequences of these less than optimum conditions. <br /><br /> The immediate corrective actions were to inform Operations personnel as to the cause of the inadvertent isolation, returning the instrument loop to normal and opening the isolation valves. Other corrective actions include: assessed plant impact by verifying selector switches on other applications of this equipment were securely fastened, issuing a Lessons Learned Transmittal, and a Plant Change Request to modify the calibration unit selector knobs has been written.
2201991011 | Nine Mile Point 1 | 09/25/1991 | 10/18/1991 | 9111010018 | <strong>Breach Of Secondary Containment Due To Inadequate Air Lock Design</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1991 at 1316 hours, with the mode switch in the "RUN" position and Reactor Power level at approximately 97%, Secondary Containment Integrity was momentarily breached. This breach was the result of both Reactor Building Airlock doors providing access from the Turbine Building to the Reactor Building being open simultaneously. Nine Mile Point 1 (NMP 1) Technical Specifications (T.S.) Sections 1.12 and 3.4.3 which state that one door in each of the double door access ways shall be closed whenever Secondary Containment Integrity is required. <br /><br /> The cause of this event is man-machine interface. The combination of limited time, combined with seven process steps results in less than completely reliable task performance. The Reactor Building Airlock doors are not physically interlocked to prevent simultaneous opening. <br /><br /> Initial corrective actions taken were to close at least one Airlock door to restore Secondary Containment. Additional corrective actions include the installation of physical interlocks on the Reactor Building airlocks.
2201991012 | Nine Mile Point 1 | 09/26/1991 | 10/15/1991 | 9110280296 | <strong>Reactor Scram Caused by Main Generator Trip Due to Failed Current Transformer</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1991, at 1728 hours, Nine Mile Point Unit 1 experienced Engineered Safety Feature (ESF) and Reactor Protective System (RPS) actuations. Specifically, a full reactor scram and a High Pressure Coolant Injection (HPCI) automatic initiation caused by a Main Generator trip. At the time of the event, the reactor mode switch was in the "RUN" position and reactor power was at approximately 97 percent power. <br /><br /> The cause of the Main Generator trip was the failure of one of three Unit Overall Differential Trip Relay Current Transformers installed on phase two neutral side of the Main Generator. A root cause investigation of the failed Current Transformer determined the failure was caused by moderately high localized temperature over a significant period of time. <br /><br /> The immediate corrective action was to respond to the scram and ensure safe shutdown conditions. Other completed corrective actions include evaluation of all Current Transformers associated with the Main Generator Protective Relaying Circuitry and replacement of the failed transformer and the other two Current Transformers mounted on phase two neutral. Periodic thermographic surveillance of Current Transformers will be implemented to preclude Main Generator trips caused by a failed Current Transformer.
2201991013 | Nine Mile Point 1 | 12/02/1991 | 12/23/1991 | 9201060363 | <strong>Breach of Secondary Containment Integrity Due To Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1991, at 1100 hours, with the mode switch in the "RUN" position and the Reactor Power level at approximately 98% of rated, Secondary Containment Integrity was momentarily breached. This breach was the result of both Reactor Building Airlock doors, providing access from the Turbine Building to the Reactor Building, being open simultaneously. Nine Mile Point Unit 1 (NMP1) Technical Specifications (T.S.), Sections 1.12 and 3.4.3, state that at least one door in each of the double door access ways shall be closed whenever Secondary Containment Integrity is required. <br /><br /> The cause of this event is man-machine interface. The limited time combined with seven distinct actions the individual must perform to open the door, results in an increased probability that both doors could be opened at the same time. The Reactor Building Airlock doors are not physically interlocked to prevent simultaneous opening. <br /><br /> Initial corrective actions taken were to close at least one Airlock door to restore Secondary Containment. Additional corrective actions include the evaluation of the installation of physical interlocks and the processing of a Technical Specification amendment to incorporate a Limiting Condition of Operation (LCO) for a specific time period to allow for this event.
2201991014 | Nine Mile Point 1 | 12/04/1991 | 12/26/1991 | 9201090147 | <strong>Reactor Scram Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1991, at 0842 hours, with the mode switch in "RUN" and reactor power level at approximately 96.5% of rated, the Nine Mile Point Unit 1 (NMP1) Reactor experienced a reactor scram. The reactor scram was the result of a level transient that lowered reactor water level below the scram setpoint of greater than or equal to 53 inches. <br /><br /> The root causes were manufacturing defects and design inadequacies. The immediate cause of the event was equipment failure. A solder connection failed on the total steam flow meter in the Feedwater Level Control circuitry, causing an imbalance in the signals to the 3 element controller, which closed 13a and 13b Feedwater Flow Control Valves in response.<br /><br /> Initial corrective actions were to respond to the reactor scram and increase reactor water level to its normal range. The cause of the level transient was investigated, and the failed total steam flow meter was identified and replaced. The remaining meters in the Feedwater Control System were evaluated and those without electrical shunts were replaced. An evaluation will be performed of meters in other control circuits to prevent similar events.
2371991001 | Dresden 2 | 01/05/1991 | 01/28/1991 | 9102050101 | <strong>Partial Group I Isolation Due To Shorting of 1B MSIV Position Indicating Light Socket</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1991 while performing Dresden Operating Surveillance (DOS) 250-2, Full Closure Timing and Exercising of Main Steam Isolation Valves (MSIVs), the Unit 2 Nuclear Station Operator (NSO) noted that the open postion indication for the 1b MSIV was not illuminated. While the NSO was attempting to replace the bulb, the bulb socket shorted causing fuse 595-709-A in Control Room panel 902-3 to blow. The blown fuse, which powers half the Primary Containment Group I Isolation logic, initiated the closure of both the Recirculation Loop Sample Valve 2-220-44 and Main Steam Line Drain Valve 2-220-1. In addition, the blown fuse caused the loss of position indication and the de-energization of the DC pilot valve soleniod for each inboard MSIV. Unit 2 was in the Startup mode at 6 percent power when this event occurred. The cause of the shorted socket and subsequent partial Group I isolation was the introduction of foreign material into the light bulb socket. As corrective action, the light socket was replaced, affected circuitry was then energized, and the system was returned to normal. The safety significance of this event was considered minimal because none of the MSIVs experienced automatic closure, and closure of Recirculation Loop Sample Valve 2-220-44 and Main Steam Line Drain Valve 2-220-1 had minimal effect on plant operation. A previous occurrence of this type at Dresden Station was reported by LER 90-002/0500237.
2371991002 | Dresden 2, Dresden 3 | 01/16/1991 | 04/16/1993 | 9304230020 | <strong>Reactor Head Closure Stud 61-198-047 Outside FSAR allowable for Material Toughness Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1989, while Unit 2 was in a scheduled refuel outage, ultrasonic examination revealed cracks in the lower threaded portion of two reactor head closure studs. One stud was sectioned and sent out for chemical and metallurgical evaluation. The evaluation results received in January 1991, while Unit 2 was shutdown for a subsequent refuel outage, indicated that the material toughness of the stud did not meet FSAR requirements. <br /><br /> The cause of the cracking is stress-corrosion cracking (SCC) which initiated in the base of pits located in the thread roots. Exposure of the studs to oxygenated water during refueling outages is thought to be a contributing factor. The cause for the reduction in material toughness has been determined to be a mechanism known as 500 degrees F tempered martensite embrittlement. <br /><br /> Corrective actions for this event included replacement of the two cracked studs and the sectioning of both studs for chemical and metallurgical evaluation. Additionally, a sample of ten studs was examined during the D2R12 Refuel Outage using an enhanced ultrasonic technique. Future corrective actions will include an augmented inspection schedule for closure studs and exploring methods to protect the studs from exposure to water. A structural evaluation of the closure studs has shown that this condition would have minimal effect on proper head closure. This is the first occurrence of cracks being found in reactor head closure studs.
2371991003 | Dresden 2, Dresden 3 | 02/01/1991 | 02/25/1991 | 9103050382 | <strong>Omission of Liquid Radwaste Discharge Composite Analysis Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours on February 1, 1991 with Units 2 and 3 in cold shutdown, it was discovered that the composite Radwaste River Discharge sample for September 2 through October 3, 1990 was not submitted to the vendor for analysis of gross alpha activity, Fe55, Sr89 and Sr90. This composite sample is required by Technical Specification Table 4.8.3. The cause of this event was attributed to a management deficiency concerning implementation of sample preparation requirements. Procedure deficiency regarding sample shipment preparation was a contributing cause. This event was initially reviewed with the personnel involved and will be reviewed with all Chemistry Department personnel. The Chemistry Department has also implemented improved administrative controls regarding management tracking and review of these activities. <br /><br /> The safety significance of this event is minimal since all Radwaste tanks discharged during September, 1990 were sampled and analyzed for gross activity, and gamma isotopic Maximum Permissible Concentration (MPC) fractions were verified to be satisfactory. <br /><br /> A previous event involving a Chemistry surveillance was reported by LER 89-017-0 on Docket Number 050237.
2371991004 | Dresden 2 | 02/13/1991 | 03/08/1991 | 9205260173 | <strong>Unit 2 Reactor Scram and Containment Group I Isolation Due to Main Steam Line High Radiation Caused by Resin Intrusion</strong><br /><i>Abstract:&nbsp;</i>At 0232 hours on February 13, 1991 with Unit 2 at 63% power, a Primary Containment Group I Isolation and Reactor Scram occurred due to valid Main Steam Line High Radiation signals. Operations personnel were attempting to change resins from a Reactor Water Cleanup Demineralizer (2A) while a parallel demineralizer (2C) was in service and providing cleaning of the reactor coolant. Investigation revealed that two isolation valves, normally fully closed, were not closed despite remote handwheel indications to the contrary. Later, it was found that the remote operators were broken allowing remote indications to show the valve positions without actual manipulation of the valves. Corrective action included improved administrative controls restricting resin moves only upon system isolation and flushing of the system to the Main Condenser Hotwell prior to returning it to service, to prevent resins from entering the reactor. The safety significance was minimal since the main steam line radiation monitors properly initiated the isolation/scram logic, Operators promptly responded to the event, and the short duration coolant chemistry transient had minimal effects. A previous resin intrusion occurred on December 17, 1985 on Unit 2 from the condensate demineralizers but did not result in a reactor scram.
2371991005 | Dresden 2 | 03/04/1991 | 03/28/1991 | 9208240184 | <strong>Orderly Unit Shutdown Due to Leakage Through Primary Containment Isolation Valves AO 2-220-44 and AO 2-220-45</strong><br /><i>Abstract:&nbsp;</i>At 1740 hours on March 4, 1991, with Unit 2 at 73% power, a steam leak was discovered at a fitting downstream of the 2-1299-16 valve located in the 'A' Reactor Water Clean-Up Heat Exchanger Room. The leak was discovered during the performance of a modification test. Air operated Reactor Recirculation sample line Primary Containment isolation valves AO 2-220-44 and AO 2-220-45 were then closed in an attempt to isolate the leak. The leak continued, so downstream valve 2-1299-15 was closed by a Shift Supervisor. When this action stopped the leak, it was concluded that the AO 2-220-44 and AO 2-220-45 valves were leaking through. Both valves were then declared inoperable and a 24 hour LCO was entered per Technical Specification 3.7.D.3. An orderly shutdown was completed promptly. A primary containment drywell entry was also performed to close upstream manual valve 2-220-102 to assure primary containment integrity. Corrective actions included repacking, stem replacement, and machining of the valve seating surfaces. <br /><br /> The safety significance of this event was minimal because performance of Dresden Technical Surveillance (DTS) 1600-1, Local Leak Rate Testing of Primary Containment Isolation Valves, indicated that the through leakage of the AO 2-220-44 and AO 2-220-45 valves did not result in exceeding the allowable limits for total Primary Containment leakage. A previous non-reportable event involving leakage of these valves occurred on February 21, 1990.
2371991006 | Dresden 2 | 03/13/1991 | 04/05/1991 | 9104160346 | <strong>Unplanned Primary Containment Group V Isolation Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1991 at 0615 hours with Unit 2 in the refuel mode with all control rods fully inserted, an unplanned Primary Containment Group V Isolation occurred, causing spurious closure of the Isolation Condenser isolation valves. The Isolation signal was reset after verification that the signal was spurious. Operations personnel were also dispatched to the area of the differential pressure instrumentation which initiates the Isolation. No personnel were identified as having inadverently jarred the instruments in question. There was no affect on plant operation because Isolation Condenser operability was not required under the current plant conditions; the Primary Containment Group V circuitry functioned properly when challenged by the spurious signal. A previous similar event was reported by LER 90-007/050237.
2371991007 | Dresden 2 | 04/11/1991 | 05/06/1991 | 9105160207 | <strong>Violation of Core Thermal Power Limits Due to Unplanned 2B Reactor Recirculation Pump Speed Increase</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1991 at 1601 hours, with Unit 2 at 99% power, the Nuclear Station Operator (NSO) was attempting to reset the 2B recirculation pump motor-generator (MG) set scoop tube in accordance with approved procedures; however, the 2B recirculation pump speed increased from 94% to 100% speed, causing an unplanned increase in reactor power. The scoop tube was locked out again and an Operator was dispatched to manually reduce the speed of the 2B recirculation pump. Mechanical binding of the 2A feedwater regulating valve was also observed. During these evolutions, maximum core thermal power of 102.04% was approached, which exceeded DPR-19 License Condition 2.G. limits. A Qualified Nuclear Engineer instructed the NSO to insert a rod step in an attempt to reduce power. Reactor power was further reduced to less than 100% by manually reducing the speed of the 2B recirculation pump. There was no safety significance because all core thermal limits as governed by the Technical Specifications had a minimum margin of 17%, at no time did the 8 hour average thermal power exceed the licensed power level, and recirculation pump speed run-up is a previously analyzed non-limiting transient. Investigation revealed a faulty MG set speed error limiting network socket, which was replaced. A piece of a shaft split ring for the second-stage impeller of a reactor feed pump was found to be the cause of the 2A feedwater regulating valve binding. This is believed to be the first event involving violation of core thermal power limits caused by this type of failure.
2371991008 | Dresden 2 | 04/15/1991 | 05/08/1991 | 9105230082 | <strong>Violation of Core Thermal Power Limit Due to 2A Reactor Feed Pump Seal Failure</strong><br /><i>Abstract:&nbsp;</i>At 1043 hours on April 15, 1991, with Unit 2 at 99% power, an unplanned power increase above the Unit 2 License Condition 2.G limit occurred as the result of a minor reactor water level excursion which occurred while securing a reactor feed pump due to failure of an inboard seal. An approximate eight inch increase in reactor water level occurred, resulting in a core thermal power increase to a peak of 104%. This event was of minimal safety significance because this type of transient had been previously demonstrated by analysis to have no adverse affect on the core. Corrective actions will include evaluations of reactor feed pump seal maintenance activities, potential reactor feed pump minimum flow line capacity enhancements, and potential operating practice changes. A previous event involving violation of the core thermal power limit License Condition was reported by LER 91-007/050237.
2371991009 | Dresden 2, Dresden 3 | 05/17/1991 | 06/07/1991 | 9209250271 | <strong>Failure of Standby Gas Treatment System Charcoal Adsorber Leak Test Due to Seal Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1991 with Unit 2 at 88 percent power and Unit 3 at 56 percent power while performing Dresden Technical Surveillance (DTS) 7500-7, Standby Gas Treatment (SBGT) System Charcoal Leak Test, the leakage around the charcoal trays of the B Train of SBGT was found to be 1.15 percent, exceeding the Technical Specification requirement of less than 1 percent leakage. Post testing maintenance on the B Train revealed inadequate sealing between the charcoal trays and the B Train housing, slight settling of the charcoal in the trays, and broken sealing mechanisms. The B Train was repaired, successfully retested, and returned to service. An as-found test performed on the A Train revealed leakage around the charcoal trays of 2.32 percent. Maintenance on the A Train revealed failures on the A Train similar to the failures found on the B Train. The A Train was promptly repaired and returned to service. <br /><br /> The gaskets on all twelve trays in the A Train and on two of the trays in the B Train were replaced. Charcoal was also added to each tray to compensate for any settling that has occurred. The sealing mechanisms were also repaired on both trains. The A and B Trains of SBGT were tested at 0.71 and 0.57 percent leakage, respectively. An Engineering review of the safety significance of this event indicated that 10CFR100 site boundary exposure limits would not have been exceeded under design basis accident conditions. Two previous failures of this test were reported by LER 82-003/050237 and LER 75-021/050237.
2371991010 | Dresden 2, Dresden 3 | 05/30/1991 | 06/21/1991 | 9107030021 | <strong>Liquid Radwaste Discharge Composite Sample Discrepancy Due To Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>During an upgrade of Dresden Chemistry Procedures (DCP), it was determined that the method of preparing the monthly River Discharge composite sample per DCP 2000-28, River Discharge Card, failed to comply with Technical Specification 4.8.3. Notation 2. The composite sample had previously been prepared by saving a 100 milliliter sample aliquot from each tank discharged regardless of the volume of the discharge. Technical Specification 4.8.3. Notation 2 requires a proportionate sample for each tank discharged based on the volume of the discharge. In this way the monthly composite sample would be more representative of the total volume discharged during the month. The root cause of this discrepancy was attributed to procedure deficiency. No River Discharges were permitted until the Chemistry Department implemented the necessary procedure changes to ensure that a proportionate sample based on the volume of the discharge from each tank is used to prepare the monthly composite sample. The safety significance of this event is minimal in that review of composite sample analysis data indicates significant margin to the maximum allowable limits. This is the first occurrence of this type at Dresden Station.
2371991011 | Dresden 2 | 06/09/1991 | 07/03/1991 | 9107120071 | <strong>Unit 2 Reactor Scram Following Turbine Trip Due to Main Turbine Thrust Bearing Wear Detector Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 0302 hours on June 9, 1991 with Unit 2 at 42% power, a reactor scram occurred due to a high reactor pressure signal. At the time, operations personnel were testing the turbine thrust bearing wear detector when a turbine trip occurred. All turbine bypass valves fully opened. However, reactor pressure began to increase due to loss of feedwater heating. The reactor operators attempted to control reactor pressure by inserting control rods in reverse sequence. One control rod had been inserted before reactor pressure reached 1048 psig and initiated a reactor scram. Investigation revealed that foreign material in the turbine bearing oil had fouled the thrust bearing wear detector causing it to drift close to the trip setpoint. During testing, the wear detector reached its setpoint before the turbine trip bypass interlocks had actuated. Review of thrust bearing plate temperatures revealed no abnormalities, indicating that an actual turbine thrust was not present. Corrective actions included a change to the thrust bearing wear detector testing procedure which lowers the acceptance criteria for movement of the detector, evaluation of an improved wear detector design, and simulator training. The safety significance was minimal, in that safety systems performed as required and post-scram recovery was normal. Operations personnel promptly responded to the scram in accordance with procedures and training.
2371991012 | Dresden 2 | 06/27/1991 | 07/19/1991 | 9107290111 | <strong>HPCI Turbine Exhaust Line Outside FSAR Stress Allowables Due to Degraded Support</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1991, with Unit 2 at 52% power, the Technical Staff Inservice Inspection (ISI) Coordinator determined that a High Pressure Coolant Injection (HPCI) turbine exhaust line had been outside FSAR stress allowables during the previous operating cycle due to a degraded support. The degraded support had been found during refuel outage ISI inspections and had been repaired prior to startup. Corrective actions included application of a coating to prevent future support corrosion of this type and ISI program enhancement. Safety significance was minimal as engineering review concluded that the condition did not pose an operability concern. A previous event involving a degraded support found during the refuel outage was reported by LER 90-16/050237.
2371991013 | Dresden 2, Dresden 3 | 06/24/1991 | 02/22/1993 | 9303020526 | <strong>Potential Degradation of Secondary Containment Involving Reactor Building Trackway Doors Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1400 hours on June 24, 1991 with Unit 2 and Unit 3 at approximately 70% power, an NRC Inspector discovered the Unit 2 reactor building trackway inner door open with no monitor in attendence, contrary to an administrative procedure governing its use. The inner door had been left unattended since 0845 hours. The next day, June 25, 1991, the NRC Inspector noticed a seal on the lower portion of the outer door was not properly closed. Investigation revealed that this lack of proper sealing on the outer door had existed during the incident of the previous day. This constituted a potential degradation of secondary containment integrity. The cause of the event was attributed to personnel error on the part of a Mechanic who failed to read the posted procedure governing use of the trackway doors and a Work Analyst who changed the scope of a previous work request utilized to install the outer door sealing mechanism. The personnel involved in the event were counselled and a revision was made to the work request procedure. A secondary containment leak rate test was performed to determine if this condition would have violated reactor building differential pressure requirements under reactor building ventilation isolation conditions. The safety significance was minimal because proper reactor building differential pressure was maintained by the reactor building ventilation system and operator action could have been taken to close the inner door if required. A previous event involving inadequate control of secondary containment interlocks is reported by LER 88-018/050249.
2371991014 | Dresden 2 | 07/04/1991 | 07/25/1991 | 9108060256 | <strong>Primary Containment Isolation Valve Closure Due to Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 4, 1991 at 1645 hours with Unit 2 at 48% power, a Reactor Water Cleanup System (RWCU) isolation occurred with Primary Containment Isolation Motor Operated Valves (MOVs) 2-1201-1 and 2-1201-2 fully closing. Operations personnel were replacing a position indication light at a local control station for MOV 2-1201-7 when the RWCU isolation occurred. Investigation revealed that a momentary short circuit occurred when the bulb was being replaced which resulted in the deenergization of relay 2-595-133, as it is electrically in parallel with the bulb. The deenergization of this relay initiated a trip of the RWCU recirculation pump and causing the RWCU system to isolate on a high pressure signal. Corrective actions included successful replacement of the bulb and prompt return of the RWCU system to normal operation. This event had no safety significance because the RWCU system properly isolated on the high pressure signal and isolation of the RWCU system for short periods has no affect on power operation or coolant chemistry limits. A previous event involving a partial Primary Containment Group I Isolation while changing a position indication bulb was reported by LER 91-1/050237.
2371991015 | Dresden 2 | 07/09/1991 | 08/01/1991 | 9208240165 | <strong>Orderly Unit Shutdown Due to Leakage Through Primary Containment Isolation Valves AO 2-220-44 and AO 2-220-45</strong><br /><i>Abstract:&nbsp;</i>At approximately 1330 hours on July 9, 1991, with Unit 2 at 51% power, a water leak was discovered at a piping penetration from the 'A' Reactor Water Clean-Up Heat Exchanger Room. Air operated Reactor Recirculation sample line Primary Containment isolation valves AO 2-220-44 and AO 2-220-45 were closed in an attempt to isolate the leak. However, the leakage was not secured. At 1700 hours the AO 2-220-44 and AO 2-220-45 valves were declared inoperable as a conservative measure pending further investigation. An entry was then made into the 'A' Reactor Water Clean-Up Heat Exchanger Room to close manual valve 2-1299-15 to stop the leakage; the leakage source was identified as a non-safety related tubing fitting. A 24 hour Limiting Condition for Operation was entered per Technical Specification 3.7.D.3 because integrity of the AO 2-220-44 and AO 2-220-45 valves was in question. A unit shutdown was initiated. A primary containment drywell entry was made at 40 percent power to close manual valve 2-220-102 to assure primary containment integrity. Cold shutdown was reached at 2000 hours on July 10, 1991. The safety significance of this event was minimal because testing confirmed that the leakage did not exceed Technical Specification limits. Corrective actions included the machining of the valve seating surfaces and valve maintenance procedure improvement. A previous event involving these valves was reported by LER 91-05/050237.
2371991016 | Dresden 2 | 07/10/1991 | 08/01/1991 | 9108120232 | <strong>Spurious Closure of 2A SDC Pump Isolation Valve Due to Control Relay Contact Problem</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1991 at 1400 hours, following a Unit 2 shutdown, the Nuclear Station Operator (NSO) was attempting to place the 2A Shutdown Cooling (SDC) Loop in operation; however, the 2A SDC pump suction isolation motor-operated (MO) 2-1001-2A valve automatically cycled closed after the NSO placed it in the full open position. The NSO made several attempts to open the valve but it continued to close automatically after reaching its full open position. The Electrical Maintenance Department performed a continuity test across M02-1001-2A control logic relay contact 3/4, which required lifting of a connection wire off the contact's terminal. Upon verification that the contact was not short circuited, the connection wire was relanded and the isolation signal simultaneously cleared. The relay was replaced to allow for further bench testing and also as a preventative measure. Bench testing of the relay could not pin point the cause of the spurious signal. The safety significance for this event was minimal because the valve closed when given the spurious signal and a redundant isolation valve was operable. Review of system records indicates that this type of failure has not been a recurring problem.
2371991017 | Dresden 2 | 08/25/1991 | 09/13/1991 | 9109230056 | <strong>Unplanned Primary Containment Isolation Valve Movement During Auxiliary Power Transfer Due to Deficient Relays</strong><br /><i>Abstract:&nbsp;</i>At 2101 hours on August 25, 1991, while verifying post maintenance operability of the motor operated (MO) "B" Recirculation Pump Discharge Valve, MO2-202-5B, Unit 2 experienced a turbine trip from approximately 38% rated core thermal power. While throttling open valve MO2-202-5B at approximately 20% open, the Turbine Thrust Bearing Trip Device actuated causing the Main Turbine to trip and a subsequent Auxiliary Power Transfer. The turbine trip device reset itself within two seconds of actuation. During the Auxiliary Power Transfer, several Group I and Group II Primary Containment Isolation Valves experienced unplanned closure. The apparent cause of the unplanned valve isolations is attributed to the valve relays dropping out during the momentary power interruption required to transfer auxiliary power. Corrective actions include installation of a modification for the Group I relays, initiation of an Action Item Record to evaluate potential concerns and recommend a solution to address the Group II and Group III valve unplanned isolations.
2371991018 | Dresden 2 | 07/11/1991 | 08/01/1991 | 9108120060 | <strong>Reactor Scram on Intermediate Range Monitor Hi-Hi Due to System Noise</strong><br /><i>Abstract:&nbsp;</i>At 1043 hours on July 11, 1991 an automatic reactor scram occurred due to a spurious Hi-Hi neutron flux signal from Intermediate Range Monitor (IRM) 15. The spike occurred during performance of Dresden Technical Surveillance 500-2, Functional Testing of RPS MG Set and RPS Reserve Power Supply, as the RPS Channel A Bus was transferred from its normal to reserve power supply. Due to the transfer of the RPS Channel A power supply, Channel A was already in a tripped condition. The IRM 15 spike tripped RPS Channel B, causing a full reactor scram. It is believed that the transfer of the RPS A power supply to its reserve power supply, the , Reserve Instrument Bus, created an electrical disturbance which resulted in the spike of IRM 15. A work request (01217) has been written to reroute all SRM/IRM signal cable in the Unit 2 drywell inside conduit in the next Unit 2 refueling outage to alleviate the spiking problem. Similar events have been documented in Licensee Event Report (LER) 90-015/050237, Intermediate Range Monitor Full Scram Due to Inductive Noise Input to the IRM/SRM Power Supplies, and LER 90-017/050237, Reactor Scram on Intermediate Range Monitor Hi-Hi Due to Unknown Cause.
2371991019 | Dresden 2 | 07/14/1991 | 08/06/1991 | 9108120317 | <strong>Primary Containment Isolation Valve Closure Due to Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1991 at 1935 hours with Unit 2 at 20% power, a Reactor Water Cleanup (RWCU) system isolation occurred with Primary Containment isolation Motor Operated Valves (MOVs) 2-1201-1 and 2-1201-2 fully closing. Operations personnel were adjusting RWCU system flow when the RWCU system isolated. The 2B RWCU Recirculation Pump (RP) inlet pressure measured downstream from the pressure reducing station indicated a pressure spike from 100 psig to 155 psig on recorder 2-1290-12. The 2B RWCU RP automatically tripped and the RWCU system automatically isolated on a high pressure signal (nominal setpoint for these automatic actions is 150 psig). Although these automatic actions were not initiated by Primary Containment Isolation logic, the RWCU system isolation did result in closure of Primary Containment Isolation MOVs 2-1201-1 and 2-1201-2. The cause of the RWCU system isolation was attributed to control difficulties within the RWCU flow controller. The immediate corrective action was to reset and restart the RWCU system. This event had no safety significance because the trips occurred as required when challenged by the pressure spike to protect the RWCU piping and isolation of the RWCU system for short periods has no affect on reactor coolant chemistry limits. The Technical Staff will investigate potential improvements to the RWCU flow controller to facilitate smoother control under low power conditions. A previous RWCU valve closure event was reported by LER 91-14/050237.
2371991020 | Dresden 2, Dresden 3 | 07/23/1991 | 08/13/1991 | 9108220145 | <strong>Reactor Building Ventilation Isolation and Automatic Standby Gas Treatment Initiation Due to Radiation Monitor Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1991 at 1435 hours with Units 2 and 3 operating at 65% and 60% respectively, the power supply (2-1705-7A) for the Unit 2 Channel "A" Reactor Building Ventilation (RBV) and Channel "A" Fuel Pool Radiation Monitors failed. This caused these Radiation Monitors to initiate automatic isolation of the Unit 2 and 3 RBV systems and automatically initiated the Standby Gas Treatment (SBGT) system. Underlying causes of the Radiation Monitor signals were electronic in nature (power supply capacitor and Zener diode failures). The RBV systems remained isolated and SBGT was kept operating until 2220 hours when the power supply was replaced. The safety significance of this event is considered minimal because the automatic actuations that occurred were proper upon receipt of the Radiation Monitor signals and there was no affect on secondary containment integrity. A previous event involving automatic SBGT start due to a radiation monitor problem was reported by LER 88-019-0. Power supply problems of this type have not been an adverse trend.
2371991021 | Dresden 2, Dresden 3 | 07/31/1991 | 08/22/1991 | 9208180072 | <strong>Improper Setpoint of Second Level Undervoltage Relays Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1991 at 1530 hours with Unit 2 at 99% and Unit 3 at 59% rated core thermal power during Electrical Distribution System Functional Inspection (EDSFI), an NRC inspection team questioned whether the setting of the 4KV emergency bus Second Level Undervoltage relays (set at 3708 volts) would provide adequate protection to Class 1E equipment. An Emergency Notification System (ENS) notification was performed concerning preliminary calculations performed by the Nuclear Engineering Department (NED) which indicated that the existing Second Level Undervoltage setpoints for 4kV Emergency buses were too low to provide adequate protection to the most limiting Safety Related component. The most limiting component was determined to be the Unit 2 Diesel Generator Cooling Water Pump (DGCWP), which is fed from Unit 2 Division II AC Distribution System. Dresden Station was notified by NED on November 20, 1991, that further Unit 2 Division II calculations had identified additional loads more limiting than the DGCWP; this was reported via Emergency Notification System (ENS). Both Unit 2 and Unit 3 were in cold shutdown at the time. <br /><br /> On January 22, 1992, NED notified the Station that degraded voltage calculations had been completed for Unit 3 Divisions I and II. These calculations, which included credit for planned modifications to improve the available voltage to critical Safety Related components, indicated minimum required 4kV safety bus voltages for Buses 33-1 and 34-1 to be 3832 Volts and 3792 Volts, respectively. Additional information is being provided in Commonwealth Edison's letter to Dr. Thomas E. Murley dated March 3, 1992 (attached) and Commonwealth Edison's letter dated March 18, 1992 to Dave Butler (attached).
2371991022 | Dresden 2 | 08/05/1991 | 08/29/1991 | 9109110089 | <strong>Control Rod Dive F-3 Drift Due to Pilot Solenoid Failure</strong><br /><i>Abstract:&nbsp;</i>At 2147 hours on August 5, 1991, with Unit 2 at 98% rated power, during main turbine Electro Hydraulic Control (EHC) low pressure scram switch calibration per Dresden Instrument Surveillance (DIS) 500-8, EHC Low Pressure Scram Switch Calibration, Control Rod Drive (CRD) F-3 suddenly inserted from position "48" to position "34". Previous to the unplanned rod insertion, a Channel A 1/2 scram signal had been received and reset per DIS 500-8. Upon initiation of a Channel B 1/2 scram signal, CRD F-3 suddenly inserted. Shortly after rod insertion, Operations personnel reported chattering in one of the two scram pilot solenoids (305-117 or 305-118). DIS 500-8 was suspended and the control rod was manually inserted to position "00" and electrically disarmed. Troubleshooting indicated that the rod insertion was caused by air leakage past the scram pilot solenoid valves. The scram pilot solenoid valves were therefore replaced and CRD F-3 was placed back in service. Further inspection will be conducted on the pilot solenoid valves that were removed to confirm the failure mode. Safety significance was minimal because no core thermal and hydraulic limits were challenged and the scram function of CRD F-3 was not affected. Review of the system history records indicates that this type of event has not been an adverse trend.
2371991023 | Dresden 2 | 08/07/1991 | 09/04/1991 | 9202110297 | <strong>2A Recirculation Pump Discharge Motor-Operated Valve Failure to Close Due to Torque Switch Setting Problem</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1991 at 0215 hours, with Unit 2 at 37% power, while attempting to start the 2A Recirculation pump, the pump discharge motor-operated valve (MOV) 2-0202-5A would not close. Troubleshooting revealed that the closing power contactor for the motor was dropping out shortly after close signal initiation. The Low Pressure Coolant Injection (LPCI) System was declared inoperable because this MOV is included in LPCI initiation logic. The Electrical Maintenance Department analyzed strip chart recorder motor current traces of the MOV and determined that the close torque switch was causing the MOV to trip early. Maintenance personnel made a primary containment entry to temporarily bypass the open-to-close torque switch for 77% of valve closing stroke by installing jumpers at the limit switch assembly. Analysis by the Nuclear Engineering Department (NED) revealed an incorrect torque switch setting for MOV 2-0202-5A. This problem was attributed to incorrect determination of the force-axis zero coordinate due to invalid test data obtained during a previous valve diagnostic test. On August 10, 1991, the torque switch bypass limit switch was returned to normal and the torque switch setting was raised per NED instructions. The safety significance for this event was mitigated by the availability of the Core Spray Subsystems. The use of invalid data obtained during valve diagnostic testing is reportable per 10CFR21. Corrective actions included review of all other MOV VOTES tests performed during the recent refuel outage and enhancements to the diagnostic testing review process.
2371991024 | Dresden 2 | 08/26/1991 | 09/19/1991 | 9110010138 | <strong>Unit 2 Reactor Scrams Due to Spurious Main Steam Line Low Pressure Signals</strong><br /><i>Abstract:&nbsp;</i>At 1113 hours on August 26, 1991, with Unit 2 at 28% power, a main turbine trip occurred, followed by an unplanned Primary Containment Group I Isolation caused by spurious Main Steam Line (MSL) low pressure signals. The reactor scrammed as a result of the Group I Isolation closure of the Main Steam Isolation Valves (MSIVs). Investigation revealed that the root cause of the turbine trip was inadequate clearances within the thrust bearing assembly, which required disassembly and installation of proper shim material. In order to diagnose the cause of the unplanned scram, a test program was developed to duplicate the initial conditions while instrumenting the MSL low pressure logic; during performance of this test on August 30, 1991, a similar Primary Containment Group I Isolation / reactor scram occurred. Review of the test data concluded that the root cause was a combination of resonating pressure waves within the MSLs and the MSL low pressure switch instrument lines. Procedural actions were implemented pending review of design changes to correct this phenomenon. Safety significance of these events was minimal as the Group I Isolation logic responded as expected when challenged by the spurious signals. Previous related events are reported by LERs 91-17/050237 and 88-17/050249.
2371991025 | Dresden 2 | 08/12/1991 | 09/04/1991 | 9109170223 | <strong>SRM/IRM Functional Test Technical Specification Requirements Not Met Due to Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>In response to a verbal request for information regarding Intermediate Range Monitor (IRM) functional testing, the Technical Staff System Engineer, Instrument Maintenance, and Operations initiated a review of applicable procedures. In the course of this review it was determined that Technical Specification requirements for functional testing of the IRM inoperable (INOP) Reactor Protection System (RPS) trip were not fully met by current station procedures. In addition, it was discovered that the Technical Specification requirements for functional testing of the IRM Hi-Hi RPS trip function and the Source Range Monitor (SRM) Hi and IRM Hi rod block functions were not met in some cases in which the testing surveillances were performed in Run mode during Unit shutdowns. Performance of the tests in Run mode does not allow proper functional testing because these SRM/IRM rod block and RPS trips are bypassed in that mode of operation. The cause of this event has been determined to be procedural deficiency. The safety significance is minimal because the proper operation of these functions has been verified and there is no indication that their condition was degraded. Corrective actions included issuance of temporary procedure changes to ensure proper testing. Long term corrective actions will include permanent procedure changes.
2371991026 | Dresden 2 | 08/15/1991 | 09/06/1991 | 9109160268 | <strong>Unanticipated Valve Closures During 125 VDC Ground Checking Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1991 at 1215 hours, with the reactor at 84% power, Low Pressure Coolant InJection (LPCI) System I minimum flow valve M02-1501-13A closed during search for a ground on the 125 VDC Turbine Building Main Bus 2A-1. Although the circuit design causes this closure on de-energization of power circuit #22, Dresden Operating Procedure (DOP) 6900-06, 125 Volt DC Ground Detection - Unit 2, did not state this would occur. The valve was restored to its normal position and DOP 6900-06 was completed. <br /><br /> On August 15, 1991 at 1945 hours, with the reactor at 97% power, while continuing the ground checking activity on Turbine Building 125 VDC Reserve Bus 2B-1 per Work Request 02999, LPCI System II minimum flow valve M02-1501-13B closed. This was expected; however, High Pressure Coolant Injection (HPCI) Turbine Stop Valve above seat drain valves A02-2301-64 and A02-2301-65 also auto closed on interruption of power from Reserve Bus 2B-1. Logic diagram review indicated that this should have occurred; however, DOP 6900-06 had not adequately identified this concern. The valves were promptly restored to their normal position and the ground search was continued. Temporary Procedure Changes were implemented adding caution statements to DOP 6900-06 for Unit 2 and DOP 6900-07 (similar procedure for Dresden Unit 3); permanent changes will be implemented. Safety significance was minimal because the valves were promptly repositioned, redundant low pressure core cooling systems were unaffected, and the HPCI valves involved moved to their design positions for initiation. There has not been a previous adverse trend concerning events of this type.
2371991027 | Dresden 2 | 08/13/1991 | 09/06/1991 | 9109160267 | <strong>Inadvertent Closure of Core Spray Minimum Flow Valve 2-1402-38A Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1745 hours on August 13, 1991, with Unit 2 at 92% power, the Instrument Maintenance Department (IMD) was completing Dresden Instrument Surveillance (DIS) 1400-6, Core Spray Flow Transmitter (FT) 1461A(B) Calibration and Maintenance Inspection, when an inadvertent closure of the Core Spray minimum flow valve 2-1402-38A occurred. The valve was reopened manually by a Control Room Operator using the valve control switch in the Control Room. Further investigation showed that the 2-1402-38A valve closed when the 2-1461-A flow transmitter was valved back in. DIS 1400-6 states specifically to slowly open the differential pressure (dP) cell instrument isolation valves when the transmitter is valved back into the system. FT 2-1461-A has a common sensing line with FT 2-1464-A, which is the flow transmitter that causes movement of the Core Spray Minimum flow valve; however, a caution statement was not provided in the procedure to explain that operating the transmitter isolation valves too quickly, a change in common sensing line pressure could simulate flow greater than 750 gpm, the flow rate at which the 2-1402-38A valve automatically closes. As a result of this event, DIS 1400-6 will be changed to heighten awareness of this potential problem. This event had no safety significance because the valve was immediately repositioned and operability of the 2B Core Spray Subsystem and the Low Pressure Coolant Injection System were unaffected. Review of System records indicates no adverse trend of events of this type while performing Core Spray FT Calibration.
2371991028 | Dresden 2 | 09/01/1991 | 10/01/1991 | 9301250256 | <strong>Violation of Technical Specification Limit on Torus Water Bulk Temperature Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1959 hours on 9/1/91, with Unit 2 operating at 47% rated core thermal power, torus water bulk temperature exceeded 95 degrees F (without testing in progress) in violation of Technical Specification 3.7.A.1.c.(1). This requires entry into Technical Specification 3.0.A which requires that the unit be in hot shutdown within 12 hours. Shift supervision was aware of the rising torus water bulk temperature and was preparing to initiate torus cooling. Shift Supervision failed to identify and secure the source of heat addition to the torus until after the temperature reached a maximum value of approximately 97 degrees F. The root cause was personnel error by Shift Supervision in failing to initially recognize 95 degrees F as a Technical Specification limit, with contributing factors of procedural deficiency and miscommunication. This event was of minimal safety significance because of the low reactor power levels since startup earlier that day. Torus water bulk temperature was reduced below 95 degrees F at 0157 on 9/2/91, and the Limiting Condition for Operation (LCO) was terminated 0230 on 9/2/91 when the torus water bulk temperature was reduced to 92 degrees F. Corrective action initiated to prevent recurrence of this type of event included counseling the appropriate Shift Supervisors, continuing training of licensed operators on expectations for communications and on Technical Specifications and their interpretation, procedure revisions, and requesting a Technical Specification amendment to add an action statement to section 3.7.A.1.c.(1). A previous event in which the torus water bulk temperature exceeded 95 degrees F was reported by LER 90-006/050237.
2371991029 | Dresden 2 | 08/21/1991 | 09/12/1991 | 9304070044 | <strong>Main Steam Line Log Radiation Monitor Setpoints Non- Conservative Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1991, an Instrument Mechanic (IM) was performing Dresden Instrument Surveillance (DIS) 1700-1, 'Unit 2 Main Steam Line Log Radiation Monitoring System Calibration.' Due to an incorrect assumption and a need to respond to an Institute for Nuclear Power Operations (INPO) Evaluator, the IM transferred data from the previous month's surveillance to the data sheet for the current month. The IM that transferred the data to the data sheet could not complete the surveillance on his shift. The data sheets in the procedure are not indexed to the procedure steps and can be easily misinterpreted. <br /><br /> The IM that continued the surveillance following shift change was not aware that the data on the data sheet was from the previous quarter and hence made no changes in the calibration constants. The root cause of this event is procedure deficiency. DIS 1700-1 contains an unclear data sheet that resulted in the wrong data being transferred from a previous quarter's surveillance. Contributing to the event was a lack of administrative controls to prevent an error from being propagated through all instrument channels once an error has been made. The safety significance of this event is minimal because the shift in the Group I isolation setpoint would have been only approximately 600 mRem/hour. DIS 1700-1 will be revised by personnel knowledgeable in the performance of the procedure to enhance the user friendliness of the procedure. In addition, the IM Department will evaluate methods of instituting additional administrative controls to ensure that errors do not propagate between instrument channels during the performance of surveillances. ZDVR/828
2371991030 | Dresden 2 | 08/26/1991 | 09/17/1991 | 9110010128 | <strong>Spurious Closure of 2A Shutdown Cooling Pump Isolation Valve Due to Local Control Pushbutton Contact Failure</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1991 at 1821 hours, following a Unit 2 shutdown, the Nuclear Station Operator (NSO) was attempting to place the 2A Shutdown Cooling (SDC) Loop in operation; however, the 2A SDC pump suction isolation motor-operated (MO) 2-1001-2A valve automatically cycled closed after the NSO placed it in the full open position. The NSO made several attempts to open the valve but it continued to close automatically after reaching its full open position. The Electrical Maintenance Department (EMD) performed continuity tests of the MO2-1001-2A control logic circuitry. As a result, the EMD discovered a short circuit in the local control station circuit. Further investigation revealed a failed "close" pushbutton contact as the cause of the spurious signal. The local control "close" pushbutton was electrically disabled, since replacement parts were not available. The safety significance for this event was minimal because the valve closed when given the spurious signal and a redundant isolation valve was operable. A previous spurious closure of this valve was reported by LER 91-016 (050237).
2371991031 | Dresden 2 | 09/21/1991 | 10/08/1991 | 9207310051 | <strong>Control Rod Drive R-10 Failure to Latch Due to Collet Piston Binding</strong><br /><i>Abstract:&nbsp;</i>At 0327 hours on September 21, 1991 with Unit 2 at 85% power, Control Rod Drive (CRD) Exercising was being conducted on CRD R-10 per Dresden Operating Surveillance (DOS) 300-1, Daily/Weekly Control Rod Drive Exercise. While attempting to exercise CRD R-10 from position "48" (full out) to position "46", the CRD failed to latch at positions "46" and "44". With Qualified Nuclear Engineer (QNE) permission, an attempt to latch at position "42" was also made and failure to latch again occurred. <br /><br /> The CRD was fully inserted and maintained at position "00" by continuously applying an Emergency-In signal. At 0535 hours, CRD R-10 began to drift out; the CRD was scrammed to position "00" (full in) and held in position by charging water pressure.<br /><br /> Tests were conducted per Special Procedure (SP) 91-9-114 to relatch CRD R-10 and flush the CRD collet piston. During testing, CRD R-10 was successfully relatched. Testing indicated that there was no leakage in the directional control valves. The CRD collet housing was determined to be intact and latching failure was determined to be a result of collet piston binding. Upon completion of flushing, latching failure again occurred and CRD R-10 was scrammed to position "00" where it successfully latched. This event had minimal safety significance because shutdown margin was not exceeded with this rod and the highest worth rod postulated to fail and all other rods postulated at position "02". Inspection during disassembly on July 11, 1992 found significant corrosion on the mating surfaces between the collet piston and collet housing (see figure 2). The corrosion is determined to be the cause of the collect piston binding. A previous rod drift due to unrelated causes was reported by LER 91-22/050237.
2371991032 | Dresden 2 | 10/25/1991 | 11/22/1991 | 9112020018 | <strong>Actuation of Group I Isolation Valves Due to Personnel Error During Placement of Jumpers</strong><br /><i>Abstract:&nbsp;</i>On 10/25/91 at 1852 hours, with Unit 2 in cold shutdown, Dresden Operating Surveillance (DOS) 0250-3, Main Steam Isolation Valve (MSIV) Fail-Safe Closure Test, was being performed. This test requires jumpers to be placed across the control relays for the MSIVs to prevent their movement during the test. While installing the jumpers, two fuses opened, resulting in closure signals being sent to certain Primary Containment Group I Isolation valves. The personnel involved initially believed that the cause of the open fuses was inadvertent grounding of the jumpers during installation. At 2049 hours, in preparation for DOS 250-3, the NSO attempted to reset one side of the Group I isolation logic and one of the fuses opened again. It was then discovered that the jumpers had been incorrectly installed on the MSIV control switches, rather than the control relays as specified in DOS 0250-3, which resulted in a partial Group I isolation signal. The jumpers were removed and the circuit function was verified. Both of the Electricians involved have been counselled by the Master Electrician and appropriate disciplinary action was taken. Operability of the isolation logic was not required during cold shutdown. A previous event involving an unrelated surveillance error resulting in a unplanned start of the Standby Gas Treatment System was reported by LER 91-4/050249.
2371991033 | Dresden 2 | 10/14/1991 | 11/06/1991 | 9111140160 | <strong>Primary Containment Isolation Valve Closure Due to Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1991, at 1101 hours, with Unit 2 at 51% power, a Reactor Water Cleanup (RWCU) system isolation occurred resulting in Primary Containment Isolation Motor Operated Valves (MOVs) 2-1201-1 and 2-1201-2 fully closing. Operations personnel were returning the RWCU system to normal operation after it was isolated to support 250 VDC battery switching. While returning the RWCU system to normal operation, it isolated on a high pressure signal. The automatic isolation occurred, as expected, to protect the RWCU piping. This event had no safety significance because isolation of the RWCU system for short periods has no affect on power operation or coolant chemistry limits. When returning the RWCU system to operation with the reactor at operating pressure, RWCU system pressure oscillations are frequently generated due to control difficulty within the RWCU flow controller. Although this event was not initiated by Primary Containment Isolation logic, it did result in unplanned closure of Primary Containment Isolation valves. Immediate corrective actions were to reset/restart the RWCU system. Additional corrective actions include reviewing the pressure and flow control valve trim and pneumatic actuator configurations for possible improvement. Three previous events involving RWCU system isolations or unplanned isolation valve closures have been reported by LERs 91-014/0500237, 91-019/0500237, and 91-034/0500237.
2371991034 | Dresden 2 | 10/12/1991 | 11/06/1991 | 9111140172 | <strong>Primary Containment Isolation Valve Closure Due to Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1991, at 1643 hours, with Unit 2 at 95% power, a Reactor Water Cleanup (RWCU) system isolation occurred resulting in Primary Containment Isolation Motor Operated Valves (MOVs) 2-1201-1 and 2-1201-2 fully closing. Due to pressure oscillations in the RWCU system, Operations personnel were transferring the pressure control station from "Auto" to "Manual" when the RWCU system isolated on a high pressure signal. On investigation, it was found that the nitrogen gas blanket on the RWCU surge tank had been lost. Corrective actions were to drain the low pressure sensing line of the surge tank level transmitter, re-pressurize the RWCU surge tank with nitrogen, inspect RWCU pumps and piping, and reset/restart the RWCU system. This event had no adverse safety significance because the RWCU system properly isolated on the high pressure signal and isolation of the RWCU system for short periods has no effect on power operation or coolant chemistry limits. Two recent previous events involving closure of Primary Containment Isolation valves while adjusting pressure/flow on the RWCU system have been reported by LERs 91-014/0500237 and 91-019/0500237.
2371991035 | Dresden 2 | 11/26/1991 | 12/16/1991 | 9112300228 | <strong>Auto Closure of Reactor Building Ventilation Inlet Isolation Dampers Due to Setpoint Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1991 at 1916 hours, with Unit 2 shutdown, a Control Room Operator attempted to open the Reactor Building Ventilation System (RBVS) inlet isolation dampers 2A-5741 and 28-5741; however, the dampers opened and immediately closed. The root cause of the event was determined to be a setpoint deficiency such that a pressure switch setting on the damper operator had insufficient margin to the actual Instrument Air header pressure. The pressure switches for damper operators 2A-5741 and 28-5741 had been recently adjusted to 79.6 and 80.0 psig respectively. During operation of the damper, a reduction of the motive air pressure below the pressure switch setting resulted in the unplanned damper closure. The dampers closed as designed when the actuator setpoint was challenged and isolation of the RBVS dampers for the short time had minimal affect on plant status. The event was deemed of minimal safety significance. Engineering is currently reviewing the pressure switch setting. This is the first occurrence of this type.
2371991036 | Dresden 2 | 10/31/1991 | 11/24/1991 | 9112030110 | <strong>Primary Containment Isolation Valve Closure Due To Shutdown Cooling System Spurious Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1991, at 1418 hours, a Shutdown Cooling System isolation occurred resulting in Primary Containment Isolation Motor Operated Valves (MOVs) 1001-1A and 1B, 1001-2A and 2B, and 1001-5A and 5B fully closing. Unit 2 was in cold shutdown with the A and B Shutdown Cooling loops in service maintaining reactor water temperature between 110 and 130 degrees F. The B Reactor Recirculation loop temperature on Control Room Temperature Recorder 2-260-11 spiked high to approximately 350 degrees F (A loop remained normal). Control Room Panel 902-4 alarm H-8, Recic Loop 8 Water High Temp, was received and the Shutdown Cooling System automatically isolated. Approximately five minutes later the alarm cleared and SDC system was restarted. The cause of the system isolation was an unidentified spurious signal. Corrective actions were to restart the Shutdown Cooling System. This event had minimal safety significance because the Shutdown Cooling System was promptly restored to normal operation and reactor water temperature was maintained well below the 212F limit required for primary containment integrity. Spurious Shutdown Cooling System isolations of this type have not been a recurring adverse trend.
2371991037 | Dresden 2 | 11/13/1991 | 12/03/1991 | 9112130293 | <strong>Reactor Scram on Spurious Intermediate Range Monitor Hi-Hi Signals Due to Electromagnetic Interference</strong><br /><i>Abstract:&nbsp;</i>At 1541 hours on November 13, 1991, an automatic reactor scram occurred due to a spurious Hi-Hi neutron flux signal on the Intermediate Range Monitors (IRMs). A unit startup was in progress with reactor pressure at approximately 101 psig at the time of the scram. The scram functions that occurred were proper upon receipt of the spurious spikes. The spurious spikes occurred as a High Pressure Coolant Injection (HPCI) steam isolation valve was opened. An extensive investigation into the spiking determined the cause to be electromagnetic interference (EMI) produced by DC valve motor operation. The EMI was being picked up in the drywell by the IRM signal cables. During the last refueling outage, new stainless steel jacketed Whittaker signal cables were installed in the drywell outside of the IRM rigid conduit. Corrective actions involved rerouting the IRM signal cables in the drywell inside flexible conduit for additional shielding, and installation of varistors on HPCI 250 Vdc valve motor circuitry to reduce the amount of EMI produced by valve operation. In addition, the IRM signal cables will be routed inside permanent rigid conduit during the next refueling outage. Previous similar events are documented by LERs 90-15/050237, 90-17/050237, and 91-18/050237.
2371991038 | Dresden 2 | 11/13/1991 | 12/03/1991 | 9112130290 | <strong>Primary Containment Isolation Valve Closure Due to Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1991, at 1723 hours, with Unit 2 shutdown, a Reactor Water Cleanup (RWCU) System isolation occurred, resulting in Primary Containment Isolation Motor Operated Valves (MOVs) 2-1201-1 and 2-1201-3 fully closing. Operations personnel had just secured the RWCU 28 recirculating pump and were attempting to place the auxiliary pump in service. The RWCU System isolated on a high pressure signal. When turning RWCU pumps on, RWCU system pressure oscillations can be generated due to control difficulty within the RWCU flow controller. Although this event was not initiated by Primary Containment Isolation logic, it did result in unplanned closure of Primary Containment Isolation Valves. This event had minimal safety significance because the isolation of the RWCU System was promptly reset and there was no affect on reactor coolant chemistry. Immediate corrective actions were to reset/restart the RWCU System. Additional corrective actions include reviewing the pressure and flow control valve trim and pneumatic actuator configurations for possible improvement. The most recent similar occurrence was reported by LER 91-31/050237.
2371991039 | Dresden 2, Dresden 3 | 09/18/1991 | 11/25/1991 | 9112030404 | <strong>Vent and Purge System Exhaust Ductwork Seperation Due to Construction/Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 0515 hours on September 18, 1991, with Unit 2 at 95% power and Unit 3 in a refuel outage, a joint in the exhaust ductwork of the Unit 3 Drywell Vent and Purge System was found separated. The two pieces of exhaust ductwork were touching and slightly out of alignment. Repairs were completed by 0600 hours on September 18, 1991. The exhaust ductwork had been verified to be intact on September 17, 1991 at 1600 hours by a Technical Staff Engineer; this indicated that the failure occurred subsequent to that time. Initial review of the event focused on scaffolding erection work in the area as a potential cause of the damage. However, further investigation into the existing joint configuration concluded that it had not been fastened in accordance with its design requirements. Inspections of the other ductwork sections were also completed. Engineering review concluded on November 12, 1991 that the as-found configuration of the failed joint did not conform to design basis criteria; however, failure of this joint under design basis conditions would not have prevented the Standby Gas Treatment System from maintaining a significant vacuum in the Reactor Building.
2371991040 | Dresden 2 | 11/19/1991 | 12/09/1991 | 9112260051 | <strong>Isolation Condenser Group V Isolation Due to Spurious Flow Spikes</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991, at 2355 hours with Unit 2 in cold shutdown with all control rods inserted, an unplanned Primary Containment Group V Isolation occurred, causing closure of the Isolation Condenser isolation valves. The isolation signal was reset after verification that the signal was spurious. In addition, following the event, all of the Group V initiating instrumentation setpoints were verified to be within their specified tolerances. The probable cause is differential pressure flow spikes in the Isolation Condenser condensate return line while starting the 2B Shutdown Cooling pump. Isolation Condenser operability is not required whenever reactor pressure is less than 90 psig; also, had this event occurred under power operation, the High Pressure Coolant Injection or Automatic Depressurization systems could have been utilized for reactor pressure control. Therefore, the safety significance of this event is minimal. A previous unplanned Group V Isolation was reported by LER 91-006/050237.
2371991042 | Dresden 2, Dresden 3 | 11/27/1991 | 12/23/1991 | 9208030199 | <strong>Cable Separation Criteria Not Met Due to Original Construction Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>While performing a walkdown for a proposed modification to re-install feed cable to Unit 2 480V Motor Control Center (MCC) 29-2, it was discovered that the existing cabling crossed from Engineered Safeguards System (ESS) Division II to ESS Division I along its cable pan routing. This condition is contrary to system separation criteria. Upon further investigation, three other MCC feed cables were identified as being of concern. Corrective actions were to initiate modifications M12-2-91-027 and M12-3-91-027 to recable and divisionally reroute the feed cabling from Unit 2 480V Bus 29 to MCC 29-2, from Unit 2 480V Bus 28 to MCCs 28-3 and 28-2, and from Unit 3 480V Bus 38 to MCC 38-2. Both Units 2 and 3 were shutdown and depressurized at the time these discrepancies were discovered; the modifications were completed prior to restart on each unit. No previous events of this type have been identified. The Commonwealth Edison Co. Nuclear Engineering Department (NED) has performed a comprehensive investigation into this event. The NED Operability and Safety Assessment performed determined that no credible failure mechanisms existed for this issue which could reduce plant safety to an unacceptable level.
2441991001 | Ginna | 02/15/1991 | 03/18/1991 | 9103260186 | <strong>Loss of Safeguards Bus During Emergency Diesel Generator Monthly Load Test, Due To Supply Breakers Tripping, Causes A Condition Prohibited By The Plant Tech Specs.</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991 at 0845 EST with the reactor at approximately 97% full power, the emergency and normal feed breakers to Bus 18 tripped while the 1A Emergency Diesel Generator was being paralleled onto the bus. The loss of Bus 18 placed the plant in a condition prohibited by plant Technical specifications. <br /><br /> Immediate operator action consisted of starting an additional service water pump from Bus 17. Subsequently, the Control Room operators declared an Unusual Event and commenced a plant shutdown to comply with plant Technical Specifications.<br /><br /> The underlying cause of the event is undetermined at this time. Further testing and evaluation will be performed. <br /><br /> Corrective action was to inspect Bus 18, the 1A Emergency Diesel Generator output breaker and the 1A Emergency Diesel Generator. Components were found satisfactory and returned to service.
2441991002 | Ginna | 03/04/1991 | 04/02/1991 | 9104100183 | <strong>Loss of Offsite Power Circuit 751, Due To Ice Storm, Causes Automatic Actuation of the ESF and RPS, (i.e. Emergency Diesel Generator Operation and Turbine Runback)</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1991 at 0148 EST, with the reactor at approximately 97% full power and again on March 7, 1991 at 0248 EST, with the reactor at approximately 80% full power, a turbine runback occurred and the "A" Emergency Diesel Generator started and tied into safeguard buses 14 and 18. <br /><br /> The Control Room operators performed the appropriate actions of AP-TURB.2 (Automatic Turbine Runback) and verified that the "A" Emergency Diesel Generator was operating properly and that safeguards buses 14 and 18 were energized. The plant was subsequently stabilized at approximately 20% full power less than when the events started. <br /><br /> The cause of the events was the loss of power to safeguards buses 14 and 18 due to loss of offsite power 34.5 KV circuit 751. Circuit 751 was lost due to RG&E system disturbances caused by a major ice storm. <br /><br /> Corrective action was to restore normal power to safeguards buses 14 and 18 from offsite power and to stop the "A" Emergency Diesel Generator and realign it for auto standby.
2441991003 | Ginna | 03/14/1991 | 04/15/1991 | 9104240254 | <strong>Firewatch Not Posted During Fire System Isolation, Due To Inadequate Adherence To Procedures Causes A Condition Prohibited By Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1991 at 1045 EST, with the reactor at approximately 89% full power, fire sprinkler system S-04 was rendered inoperable without a firewatch with backup fire suppression equipment being established. This placed the plant in a condition prohibited by Plant Technical Specifications. This event was not discovered until approximately 1327 EST, March 14, 1991. <br /><br /> Immediate corrective action was to establish a firewatch with backup suppression equipment for fire sprinkler system S-04. Subsequently at 1510 EST the system was again declared operable. <br /><br /> The underlying cause of the event has been attributed to inadequate adherence to procedures. <br /><br /> Corrective actions will be to establish a formalized method to verify a firewatch is posted prior to holding the fire system. Other corrective action planned is outlined in section V B.
2441991004 | Ginna | 03/28/1991 | 04/26/1991 | 9105010167 | <strong>Manual Start and Loading of "B" Emergency Diesel Generator, Due To Potential Severe Weather Conditions While Operating at Reduced Inventory In The RCS</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1991 at 0211 EST, with the reactor in the cold shutdown condition and reactor coolant system temperature and pressure at 100 degrees F and zero (0) psig respectively, the "B" Emergency Diesel Generator was started due to the potential for severe weather in the area.<br /><br /> After the "B" Emergency Diesel Generator was started the Control Room operators tied it into Safeguards Bus #17. <br /><br /> Subsequently, after the threat of the severe weather had passed, the "B" Emergency Diesel Generator was removed from service and realigned for auto standby.<br /><br /> The underlying cause of the event was justifiable conservatism on the part, of the plant staff due to the sensitivity to loss of RHR while operating in the RCS reduced inventory condition. <br /><br /> Since the potential severe weather conditions were a natural phenomenon, no corrective actions to prevent recurrence are warranted.
2441991005 | Ginna | 04/14/1991 | 05/13/1991 | 9105210249 | <strong>Steam Generator Tube Degradation Due to IGA/SCC Causes Q.A. Manual Reportable Limits to be Reached</strong><br /><i>Abstract:&nbsp;</i>During the 1991 Annual Refueling and Maintenance Outage subsequent to the eddy current examination performed on both the "A" and "B" Westinghouse series 44 Steam Generator (S/G), 116 tubes in the "A" S/G and 117 tubes in the "B" S/G required corrective action due to tube degradation.<br /><br /> The immediate cause of the event was that the "A" and "B" S/Gs tube degradation was in excess of the Ginna Quality Assurance Manual reportability limits. <br /><br /> The underlying cause of the tube degradation is a common S/G problem of a partially rolled tube sheet crevice with recurring Intergranular Attack/Stress Corrosion cracking (IGA/SCC) and Primary Water Stress Corrosion Cracking (PWSCC) attack on S/G tubing. <br /><br /> Corrective action taken was to either sleeve or plug the affected tubes with accepted industry repair methods.
2441991006 | Ginna | 06/29/1991 | 07/29/1991 | 9108050066 | <strong>Apparent Voltage Drop On Safeguards 480 Volt Bus 14 Causes an Automatic Start of the "A" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1991 at 1754 EST with the reactor at approximately 98% full power, the "A" Emergency Diesel Generator started automatically due to an apparent undervoltage signal from the Bus 14 Undervoltage Monitoring System. <br /><br /> The "A" Emergency Diesel Generator, after starting, attained proper voltage and frequency. By design, it did not close into Bus 14 because Bus 14 was at its proper voltage and being fed from its normal power supply. <br /><br /> Immediate operator action was to verify that Bus 14 was energized and that the "A" Emergency Diesel Generator was operating normally. Subsequently, the "A" Emergency Diesel Generator was stopped and realigned for auto-standby. <br /><br /> The cause of the event has not been positively determined, although off-site electrical disturbance is postulated. <br /><br /> Since the cause of this event has not been positively determined at this time, we will continue to investigate for the underlying cause. Any further corrective action will depend on the results of this investigation.
2441991007 | Ginna | 07/31/1991 | 08/29/1991 | 9109130162 | <strong>Safeguards Buses Undervoltage Relay Actuations Due to Failed Solid State Switches Causes Automatic Starts of the "B" Emergency D/G</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1991 at 1746 EDST, with the reactor at approximately 98% full power and again on August 2, 1991 at 1049 EDST, with the reactor at approximately 98% full power, the "B" Emergency Diesel Generator started automatically due to an initiation signal from the Bus 16 and Bus 17 Undervoltage Monitoring/Protection Systems. <br /><br /> The "B" Emergency Diesel Generator started normal for both events and attained proper voltage and frequency. By design, it did not close into Bus 16 or Bus 17 because these buses were at their proper voltage fed from their normal power supply.<br /><br /> Immediate operator action was to verify that Bus 16 and Bus 17 were energized and that the "B" Emergency Diesel Generator was operating properly.<br /><br /> The cause of the event was determined to be a temperature related failure of a solid state switch printed circuit board. <br /><br /> Corrective action taken was to replace the solid state switch printed circuit board with a qualified spare, followed by a satisfactory test and return to service. Corrective actions to prevent recurrence are discussed in section (V) (B).
2441991008 | Ginna | 08/05/1991 | 09/04/1991 | 9109160127 | <strong>During Maintenance, A Failure Of One Of Two Trains Of Undervoltage Protection Was Discovered On Safeguards Bus 14</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1991 at approximately 1800 EDST, with the reactor at approximately 30% full power, the Maintenance Department observed that a solid state switch printed circuit card for Safeguards Bus 14 Undervoltage Monitoring/Protection System was damaged. Following inspection of the damaged card, it was determined that the damaged card would have prohibited certain protective functions. <br /><br /> No immediate operator action was necessary as the "A" Emergency Diesel Generator was running tied to Bus 14 during the maintenance activity to satisfy plant technical specifications.<br /><br /> The cause of the event was determined to be a temperature related failure of a solid state switch printed circuit card. <br /><br /> Corrective action taken was to replace the solid state switch printed circuit card with a qualified spare, followed by a satisfactory test and return to service. Corrective actions to prevent recurrence are discussed in section (V)(B) of this report.
2441991009 | Ginna | 11/11/1991 | 12/11/1991 | 9112170532 | <strong>Automatic Feedwater Control Perturbations, Due To Electromagnetic Noise Spikes From Unrelated Relay Actuation, Caused Steam Generator Feedwater Isolation on High Level</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1991 at approximately 1214 EST, with the reactor at approximately 98% full power, steam generator feedwater isolations occurred on both steam generators. These feedwater isolations were caused by perturbations of the advanced digital feedwater control system which increased feedwater flow to the steam generators. <br /><br /> Immediate operator action was to manually control the feedwater regulating valves to reduce steam generator levels and stabilize the plant. <br /><br /> The underlying cause of the event was determined to be electro-magnetic noise spikes affecting the advanced digital feedwater control system. <br /><br /> Corrective action taken was to modify specific relay circuits that were causing these spikes.
2441991010 | Ginna | 12/30/1991 | 01/29/1992 | 9202060130 | <strong>During Operator Review of Plant Process Computer Logs, It Was Discovered That Invalid Data Had Been Used For Calorimetric Calculation</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1991 at approximately 1830 EST, with the reactor at approximately 98% full power, the Control Room Foreman, while performing a review of the hourly Plant Process Computer System (PPCS) logs, determined that the Leading Edge Flow Meter (LEFM) data used by the PPCS to calculate calorimetrics, was invalid from 1800 EST, December 20, 1991 to approximately 1830 EST, December 30, 1991. This event is being voluntarily reported to alert other utilities which may have similar systems. <br /><br /> The Control Room operators notified the reactor engineer and reinitialized the LEFM computer. After reinitialization, the LEFM printout values and PPCS values returned to expected/normal indications.<br /><br /> Corrective actions include revisions to the affected procedures to require checking the operation of the LEFM prior to performing calorimetrics and the addition of a high alarm on PPCS indicating a failure may have occurred. <br /><br /> The immediate cause was identified as a failure of the LEFM HP-85B computer.
2451991002 | Millstone 1 | 02/08/1991 | 01/06/1992 | 9201150148 | <strong>Low Pressure Coolant Injection and Core Spray System Design Temperatures</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1991, at 1725 hours, with the plant at 100% power (530 degrees Fahrenheit and 1030 psig), an inconsistency between the design temperatures associated with the Low Pressure Coolant Injection (LPCI) and Core Spray piping, piping supports, and components was reported.<br /><br /> It was discovered that temperatures for portions of the LPCI and Core Spray system used to analyze piping that would be subjected to high water temperatures during a design basis Loss of Coolant Accident were not consistent with the accident analysis temperature profile. The original design basis temperature for the post accident peak torus temperatures was established at 203 degrees F and was based upon an initial service water temperature of 75 degrees F. Engineering evaluations were in progress to qualify the various components to temperatures above the existing design basis value of 203 degrees F. During the performance of this analysis, engineers discovered a discrepancy in the piping design temperature. Portions of the LPCI and Core Spray systems were designed for 165 degrees F instead of the design basis temperature of 203 degrees. An operability determination was completed which demonstrated that all components associated with the LPCI and Core Spray systems were operable. No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991003 | Millstone 1 | 03/01/1991 | 07/30/1991 | 9108070204 | <strong>LPCI Motors High Vibration</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1991 while at 100 percent power (525 degrees Fahrenheit, 1030 psig) the 'B'and 'D' Low Pressure Coolant Injection (LPCI) Pumps were declared inoperable due to high motor vibration and could not be repaired within the time limits established by Technical Specification. As required by the Technical Specification a plant shutdown to cold shutdown was commenced. The plant reached cold shutdown at 0812 hours on March 2, 1991. No safety systems were required as a result of this event and no safety consequences resulted from this event.
2451991004 | Millstone 1 | 03/07/1991 | 08/22/1991 | 9109030168 | <strong>Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1991, at 1140, with the plant in Cold Shutdown (170 degrees F, 0 psig), the Emergency Diesel Generator was declared inoperable following an automatic trip on low lube oil pressure. Failure to reach minimum lube oil pressure has been attributed to a low ambient room temperature condition which increased the lube oil viscosity. Plant procedural revisions have been implemented to assure lube oil temperature will not decrease to a level at which Emergency Diesel Generator operability could be compromised. <br /><br /> The Emergency Diesel Generator is designed to automatically start on loss of normal power, low-low reactor water level or high containment pressure. The Emergency Diesel Generator provides emergency power for necessary auxiliaries important to the engineered safeguards systems and power needed during the shutdown mode of operation. <br /><br /> No safety systems were required to actuate as a result of this event.
2451991005 | Millstone 1 | 03/10/1991 | 04/09/1991 | 9104190364 | <strong>LLRT FAILURE</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1991, at 0520 hours with the plant at 75% power during start up, the drywell personnel air lock failed to pass the local leak rate test (LLRT). While performing the LLRT for the drywell personnel air lock in accordance with Plant Technical Specification Surveillance requirement 4.7.A.3.d(2), the leakage rate recorded was 19.3 SCFH which exceeded the maximum allowable leakage rate for a single penetration of 18.8 SCFH. A plant shut down was commenced and activities started to investigate the cause for the drywell personnel air lock leakage. <br /><br /> With the plant at 30% power, the Personnel Air Lock was satisfactorily retested subsequent to repairs. There were no safety consequences due to this event.
2451991006 | Millstone 1 | 03/01/1991 | 11/13/1991 | 9111220237 | <strong>Unjacketed Cable Resulting in Loss of Environmental Qualification</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1991, at 1400 hours, with the plant at 89% power (530 degrees Fahrenheit and 1030 psig), the as built configuration of the pigtail to field termination for a cable in the drywell was determined not to be fully environmentally qualified. This condition is reportable under 10CFR50.73. <br /><br /> On February 25, 1991, an evaluation was initiated when a question arose as to whether a cable jacket was reconstructed on Kerite cable at the pigtail to field termination following the installation of Raychem heat shrink tubing sleeve. Kerite cable must be fully jacketed to take credit for beta radiation shielding to the cable insulation to ensure environmental qualification. Specifically, with the cable insulation exposed to an accident drywell environment, operability of the cable end device could be affected and thus the ability of the device to mitigate the consequences of a Loss of Coolant Accident.<br /><br /> An operability evaluation was performed on the unjacketed Kerite cable found on 19 end devices located in the drywell. Of the 19 end devices evaluated, all were found to remain operable to perform their Design Basis Accident (DBA) function with the exception of the field cable to the air solenoid on valve 1-CU-2A. The solenoid supplies air to containment isolation valve 1-CU-2A. 1-CU-2A is a 1/2" bypass valve around 1-CU-2, the reactor water clean-up (RWCU) system in-board containment isolation valve. Bypass valve 1-CU-2A allows the system piping to be slowly pressurized when the system is returned to service with the reactor at normal operating pressure. <br /><br /> Upon determination that the cable was not qualified, 1-CU-2A was verified in the closed position and the electrical circuit for 1-CU-2A was de-energized. Plant operation was unaffected by de-energizing the circuit since the normal valve position for 1-CU-2A is closed. Additionally, since the valve has been verified in the closed position as required by Technical Specifications and remains closed upon a Group V containment isolation signal, no safety consequences resulted from this immediate corrective action.
2451991007 | Millstone 1 | 04/07/1991 | 05/07/1991 | 9105150144 | <strong>Manual Reactor Scram Due to High Reactor Water Conductivity</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1991, at 0723 hours, while shutting down for Refueling (Startup mode, IRM Range 2) at 515 degrees Fahrenheit and 780 psig, a manual reactor scram in response to high reactor water conductivity was initiated. Off Normal Operating Procedure (ONP) 515C, "High Conductivity Reactor Water," requires a manual scram when the conductivity reaches 2.0 umho/cm. <br /><br /> Prior to the high reactor water conductivity condition, three Standby Liquid Control (SBLC) surveillances were performed. Investigation revealed that these SBLC Surveillances performed earlier during the shift created this high conductivity condition. The contents of the SBLC Test Tank were injected into the reactor vessel during the performance of the last of these surveillances. Analysis of the tank revealed that it contained a diluted concentration of sodium pentaborate. This concentration was determined to be the cause of the conductivity excursion. Within 2 hours of the initiation of the conductivity increase, the reactor water cleanup system reduced the conductivity to less than 2.0 umho/cm. The plant continued its cooldown to cold shutdown for refueling. The test tank should have contained demineralized water. It has been determined that the root cause of this event is personnel error during the conduct of the SBLC surveillances.
2451991008 | Millstone 1 | 04/07/1991 | 09/19/1991 | 9110020026 | <strong>Isolation Condenser Automatic Isolation</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1991, at 1805 hours, with the plant in hot shutdown (265 degrees Fahrenheit and 24 psig), an automatic isolation of the Isolation Condenser occurred while manually placing the system in service. The Group IV isolation signal was generated at approximately the same time valve IC-3 "Condensate Return Valve" reached the full open position. Following the isolation event, operations personnel performed an inspection to verify the integrity of the Isolation Condenser steam and condensate piping in the Reactor Building. The Isolation Condenser isolation logic was reset and the system was satisfactorily placed in service. <br /><br /> No other safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991009 | Millstone 1 | 04/08/1991 | 12/04/1992 | 9212100114 | <strong>LLRT Failure</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1991, at 0100 hours with the plant shut down for refueling, it was identified that the main steam header stop drain valves 1-MS-5 & 1-MS-6 (Penetration X-8) exceeded the maximum allowable leakage rate as specified by Technical Specification 4.7.A.3.e. Testing of all primary containment isolation valves, cable penetrations, and manways as required by 10CFR50 Appendix J revealed additional valves and manways that did not meet the local leak rate test requirements. <br /><br /> All valves and manways that failed to meet the local leak rate test requirements were satisfactorily retested subsequent to repairs.
2451991011 | Millstone 1 | 04/17/1991 | 05/15/1991 | 9105280193 | <strong>Technical Specification Fire Penetration</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1991, at 2000 hours, with the plant in Cold Shutdown and the core off-loaded, (less than 100 degrees Fahrenheit and 0 psig), it was discovered that the fire watch requirements specified by work order procedures were not correctly implemented and did not meet the requirements of technical specification 3.12.F.2. Upon discovery of the open fire penetration, a temporary fire penetration seal was installed until a fire watch was established. The automatic fire detection system and the fire suppression systems in the Turbine Building area affected by the penetration were operable throughout the event. The available fire protection features provided in the areas, and the low combustible loading, minimized any potential adverse impact on maintaining the safe shutdown condition. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991013 | Millstone 1 | 04/22/1991 | 05/21/1991 | 9105300327 | <strong>Unplanned Standby Gas Treatment System Initiation</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1991, at 1000 hours, with the plant in Cold Shutdown (94 degrees Fahrenheit and 0 psig), the Standby Gas Treatment System (SBGT) initiated. This occurred when a fuse was pulled as part of a work order tag out to deenergize the Drywell Equipment Drain Valve pilot solenoids in order to install Local Leak Rate Test (LLRT) connections. The removal of this fuse deenergized a Group II isolation relay (904/(595-134)) which initiated SBGT. The fuse was replaced, the Group II isolation relay energized, the SBGT System was secured and the Reactor Building Ventilation was restored. The Standby Gas Treatment System functioned as designed. Secondary containment was not required at the time of the event. No safety consequences resulted from the event.
2451991014 | Millstone 1 | 04/26/1991 | 07/22/1992 | 9207290319 | <strong>High Energy Line Break Interaction with Closed Cooling Water</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1991, at 1500 hours, with the plant in Cold Shutdown and the core off-loaded, (less than 100 degrees Fahrenheit and 0 psig), it was determined that a postulated feedwater line break could result in a complete loss of AC power. The postulated High Energy Line Break (HELB) could have disrupted power lines in overhead cable trays associated with the Gas Turbine generator. This HELB interaction was previously identified. However, potential HELB damage to the Turbine Building Secondary Closed Cooling Water (TBSCCW) lines used to supply cooling to the Diesel Generator room coolers was not evaluate(:[. Diesel Generator room cooling is required for Diesel Generator operability. This consequence, along with the assumed Loss of Normal Power coincident with a feedwater or condensate line break would result in the total loss of AC power. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991015 | Millstone 1 | 05/01/1991 | 05/31/1991 | 9106070340 | <strong>Standby Gas Treatment Initiation When SRM/IRM Dry Tube Broke the Surface of the Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1991, at 1030 hours, with the plant in cold shutdown for the scheduled refueling outage (0 percent power, 90 degrees Fahrenheit), Source Range Monitor and Intermediate Range Monitor Dry Tube replacement was in progress when an irradiated dry tube assembly momentarily broke the surface of the fuel pool during transfer from the reactor vessel. The event resulted in the automatic initiation of Standby Gas Treatment System due to refuel floor high radiation. All Systems functioned as designed and there were no significant safety consequences from this event. The dry tube was subsequently disposed of using a special procedure.
2451991017 | Millstone 1 | 05/03/1991 | 06/07/1991 | 9106120160 | <strong>Safety/Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1991, with the plant shut down for a planned Cycle 13 Refueling Outage (0% power, 100 degrees F, 0 psig) bench testing of the main Steam system safety/relief valves indicated that five of six valves lifted at pressure in excess of the Technical Specification limit and one lifted less than the Technical Specification Limit. Analysis indicates the ASME Code/Safety limit would not have been exceeded during a limiting transient when the as found setpoints are considered. All valves will be refurbished and recertified to their desired set pressures. Replacement valves have already been installed.
2451991018 | Millstone 1 | 04/17/1991 | 06/19/1993 | 9306250334 | <strong>Hydraulic Snubber Visual Inspection Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1991, at 18:45 hrs with the plant in Cold Shutdown (less than 100 degrees Fahrenheit and 0 psig) a procedural inadequacy was identified with respect to the evaluation of Bergen Patterson hydraulic snubber fluid reserve capacity. The subject procedure MP 739.5, Revision 2, Change 1, 'Hydraulic Snubber Visual Inspection,' acceptance criteria for fluid level did not properly assess the fluid volume required to fully extend a snubber. This error was caused by the misapplication of Bergen Patterson Technical Information Bulletin 1-104-5/79-300, Rev. 0, 'Hydraulic Shock and Sway Arrestor Fluid Level Operability Criteria.' The subject procedure was promptly revised to employ an equation which adequately considers the effect on variable main piston position. The associated surveillance was satisfactorily reperformed. Six (6) snubbers were identified with low fluid levels, however, they were subsequently demonstrated operable on a test stand. <br /><br /> An evaluation of previous surveillances since 1981 was performed to address the impact of undetected inoperable snubbers from previous fuel cycles. Nineteen (19) snubbers were identified with low fluid levels, of these (19), two (2) snubbers were conservatively determined to have been inoperable by Engineering evaluation. Records indicate that all nineteen have since been rebuilt and retested and are now operable. <br /><br /> This event is reportable pursuant to 10CFR50.73(a) (2) (v).
2451991019 | Millstone 1 | 06/10/1991 | 01/06/1992 | 9201150131 | <strong>ECCS Equipment Room Temperature</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1991, at 1530 hours, with the plant in Cold Shutdown (82 degrees Fahrenheit and 0 psig), an ongoing engineering analysis concluded that the Low Pressure Coolant Injection (LPCI) system and the Core Spray system motors could not be demonstrated to be operable during postulated accident conditions. This conclusion was based upon higher calculated post accident torus temperatures combined with higher than previously assumed ambient room temperatures. The cooling water supply for the LPCI and Core Spray motor bearings is supplied from the containment torus water via the pump discharge piping. The postulated increase in the torus and reactor building temperatures adversely affected the operation of the upper motor bearings.<br /><br /> On June 19, 1991, at 1510, with the plant in Cold Shutdown, it was also determined as a result of the postulated increase in reactor building temperatures near the torus area that the wide range torus level instruments did not meet the environmental temperature conditions postulated during accident conditions. <br /><br /> On December 11, 1991, at 1100 hours, with the plant in Cold Shutdown, it was determined that insulation removed from the LPCI and Core Spray system piping located in the reactor building could adversely affect the post accident reactor building temperature profile. The piping insulation was removed as a result of an asbestos removal program. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991020 | Millstone 1 | 07/12/1991 | 09/30/1992 | 9210070237 | <strong>Containment Isolation Valve Electrical Wiring Separation and HELB Analysis Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1991, at 1215 hours, with the plant in cold shutdown (155 degrees Fahrenheit and 0 psig), it was discovered that the Isolation Condenser logic (associated with high flow isolation) did not meet separation design criteria. In addition, all four (4) valves in the Isolation Condenser system, which provide containment isolation in the event of a line break, were found to be powered from the same electrical division. <br /><br /> On July 15, 1991, at 1515 hours, with the plant in cold shutdown (155 degrees Fahrenheit and 0 psig), as a result of reviewing design changes for the Isolation Condenser wiring separation criteria, it was determined that the line break analysis (for breaks outside containment) associated with the Isolation Condenser system was potentially nonconservative. The line break analysis associated with the Isolation Condenser system did not consider the time delay effects that could exist during an isolation condition concurrent with a loss of normal power. In this event, the delay associated with the Diesel Generator start time could add several seconds to isolation valve closure. <br /><br /> Design changes have been implemented to correct the deficiencies in the containment isolation valve power supplies and wiring separation issues. A final analysis has been completed to account for the delay associated with the Diesel Generator start time in isolating an Isolation Condenser line break. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991021 | Millstone 1 | 06/19/1991 | 07/19/1991 | 9107250209 | <strong>Inadequate Recirculation Time for Decontamination Solution Tank</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1991, at 1530 hours, with the plant in Cold Shutdown at 137 degrees Fahrenheit and 0 psig, it was determined that the recirculation time for the Decontamination Solution Tank (DST) did not meet the Technical Specification requirement for minimum tank recirculation prior to sampling for discharge. Upon discovery of the inadequate recirculation time, a hold was placed on the discharge of the DST and a procedural change to Operating Procedure 312B, "Liquid Radwaste-Floor Drain System," was initiated to increase the recirculation time. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991022 | Millstone 1 | 08/02/1991 | 09/03/1991 | 9109130182 | <strong>Failure of SP 412S (Wide Range Yarway RPV Level Calibration)</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1991, a 1500 hours, with the plant in cold shutdown (120 degrees Fahrenheit, 0 psi) and the mode switch in Refuel, Instrumentation and Controls surveillance, SP 412S, Wide Range Yarway RPV Level Calibration, failed to meet the procedure acceptance criteria. Investigation revealed the cause of the failed surveillance was a lifted lead (Reference Attachment) that defeated the 2/3 core height LPCI Containment Cooling interlock for the "B" LPCI Containment Cooling loop. The remaining interlocks in the "A" and "B" LPCI Containment Cooling loops were determined to be operable. The lead was landed and the surveillance was satisfactorily completed. No safety consequences resulted from this event.
2451991023 | Millstone 1 | 08/21/1991 | 09/20/1991 | 9110020025 | <strong>Unplanned Standby Gas Treatment System Initiation</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1991, at 0833 hours, during plant start-up (246 degrees Fahrenheit and 15 psia) the "A" Standby Gas Train initiated and a partial Group II isolation was received. Operations personnel verified that there were no valid initiation signals and secured "A" Standby Gas and reset the partial Group II isolation. This event occurred two additional times at 0849 hours on August 21, 1991, and at 1311 hours on August 27, 1991, and it was determined to be related to work being performed in the control panel. Investigation revealed a loose connection to be the cause of the "A" Standby Gas Train initiation. The connection was tightened and the Standby Gas Treatment System Operability surveillance was successfully performed. No safety consequences resulted from the event.
2451991024 | Millstone 1 | 08/04/1991 | 09/04/1991 | 9109130177 | <strong>Main Steam Line High Flow Trip</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1991, while at 0 percent power and 122 degrees Fahrenheit and shutdown for refueling, review of the setpoint calculation for the Main Steam Line High Flow Trip identified the uncertainty assumed for the measurement of main steam line flow was non-conservative resulting in a potentially non-conservative trip setpoint with respect to the Technical Specification limit of 120 percent rated steam line flow. This Main Steam Line High Flow Trip was previously revised in March 1990 using Regulatory Guide 1,105, "Instrument Setpoints for Safety Related Systems" methodology. The instrument setpoint uncertainty calculation was revised using a new value for flow measurement uncertainty. The new setpoint was implemented and functionally tested while the unit was shutdown. Plant operation was unaffected and there were no safety consequences as a result of this event.
2451991025 | Millstone 1 | 08/16/1991 | 12/20/1991 | 9112310046 | <strong>Control Rod Failure to Scram</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1991, while at 23 percent power and 530 degrees Fahrenheit, eight control rods exhibited significant delays in scram insertion times and approached the Technical Specification requirement for a maximum scram time of 7 seconds for 90 percent insertion. Subsequent review of the two control rods previously reported as failing the 90 percent insertion time indicated that, although the full insertion times exceed 7 seconds, the 90% insertion times were acceptable. However, a 2 x 2 array was identified which would have failed the 2 x 2 array analysis. The affected array contained two of the slow control rods and would have failed the technical specification requirements for the 5, 20, and 50 percent times for the 3 fastest rods of a 2 x 2 array. The slow rods were identified during the performance of beginning of cycle control rod scram time testing. As each was identified, the control rod was left fully inserted and electrically disarmed. The delayed scram was determined to be caused by the slow venting of air from the scram pilot solenoid valves (117 and 118) located on the associated Hydraulic control units. The solenoid valves were rebuilt and the control rods scram timed. All affected control rods successfully passed with nominal scram times and were returned to service. There were no safety consequences from this event.
2451991026 | Millstone 1 | 08/29/1991 | 09/30/1991 | 9110110177 | <strong>Inadequate Emergency Diesel Generator Fuel Oil Supply</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1991, at 1730 hours, with the plant at 2% power, 413 degrees Fahrenheit and 287 psig, it was determined the usable fuel stored on site in the Diesel Fuel Oil and Diesel Fuel Oil Day Tank may not meet the Technical Specification requirement of 23,400 gallons. It was identified the portion of unusable fuel in the diesel fuel oil storage tank could be as high as 2180 gallons. Upon the discovery, both tank levels were checked. The total usable fuel quantity on site was found to be 23,019 gallons. An additional 1000 gallons of fuel oil were immediately ordered for the storage tank and was added to the tank on August 30, 1991. <br /><br /> No safety systems were required to function as a result of the event and no safety consequences resulted from this event.
2451991027 | Millstone 1 | 11/01/1991 | 01/31/1992 | 9202060114 | <strong>345KV System Instability</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1991, at 1340 hours, with the plant shutdown (142 degrees Fahrenheit and 0 psig), an engineering evaluation concluded a single electrical fault could result in a loss of all offsite power. This condition is reportable pursuant to 10CFR50.73(a)(2)(ii). <br /><br /> During a recent design review in August 1991 of the Millstone Unit One 345KV transmission system for stability, it was recognized a transfer trip time of 8.5 cycles for the switchyard breakers to open under a three phase bolted fault inside the main step-up transformer could result in loss of offsite power sources to Millstone One and loss of the Millstone switchyard. The loss of the Millstone switchyard could then cause instability in the 345KV system in the Northeast. A plant design change has been implemented to correct the deficiency. <br /><br /> This event was the subject of a reportability evaluation in accordance with Northeast Utilities procedure (NEO 2.25). The evaluation was initiated August 21, 1991, however, the actual report was not made until November 1, 1991 due to a failure to recognize the existence of sufficient technical data to make a reportability determination. In addition the reportability timeliness limits were not met per procedure NEO 2.25. These were an oversight. Recent improvements have been initiated to correct the timeliness issue.
2451991028 | Millstone 1 | 11/07/1991 | 03/05/1993 | 9303180225 | <strong>Seismic Interaction on TBSCCW System</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1991, at 1300 hours, with the plant in cold shutdown (142 degrees Fahrenheit and 0 PSIG) for inspection of piping susceptible to erosion/corrosion, it was determined that a postulated seismic event could result in inoperability of the Emergency, Diesel Generator and the Feedwater Coolant Injection System. The postulated seismic event could have disrupted inadequately anchored room coolers and resulted in a subsequent loss of Turbine Building Secondary Closed Cooling Water (TBSCCW). TBSCCW heat removal capability is required for long term operation of the Emergency Diesel Generator and the Feedwater Coolant Injection Pumps. Modifications were performed to restore the room coolers anchorage to its correct configuration. No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991029 | Millstone 1 | 12/14/1991 | 01/13/1992 | 9201270012 | <strong>Fire Door Found Open With No Fire Watch Present</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1991, at 1030 hours, with the plant in Cold Shutdown (130 degrees Fahrenheit and 0 psig), a hatchway door from the Turbine Building 34'6" elevation to the Condenser Bay mezzanine area was found open with no fire watch posted. The hatchway door was immediately closed. The Turbine Building 34'6" elevation contains switchgear that supplies equipment required to be operable with fuel in the reactor vessel. There is no equipment important to safety on the condenser bay side of the hatchway door. The automatic fire detection system for the Switchgear area and the automatic fire detection and suppression systems for the Condenser Bay were operable at the time of the event. The available fire protection features and the low combustible loading of the areas minimized any potential adverse impact of maintaining the plant in a safe shutdown condition. <br /><br /> No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451991030 | Millstone 1 | 11/19/1991 | 12/19/1991 | 9112300224 | <strong>Reactor Power Determination</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991, at 1420 hours with the plant in cold shutdown (140 degrees Fahrenheit and 0 psig), it was determined after review of current (Cycle 14) plant performance data that reactor power had exceeded the license power limit during previous cycles by as much as 1 percent. This is reportable as a condition not permitted by Technical Specifications. During the 1991 refueling outage, both feedwater flow nozzles were replaced with new flow calibrated venturis. Review of plant operating data while evaluating the performance of the new venturis led to the determination regarding previous plant operation. There were no safety consequences as a result of this event.
2471991001 | Indian Point 2 | 01/07/1991 | 03/05/1991 | ML10033165 | <strong>RPS Low Pressurizer Pressure Logic Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1991 at approximately 11:02 a.m., with the unit operating at 96.5% power, the reactor tripped. The trip was generated by the reactor protection system (RPS) two out of four coincidence logic for a low pressurizer pressure. The low pressurizer Pressure logic actuation occurred as a result of maintenance activity on pressurizer pressure transmitter PT 455. The operators responded to the event in accordance with established plant procedures and the plant systems responded as designed, with the exception of auxiliary feedwater pump No. 21. This pump started and tripped after running for approximately 120 seconds. Consequently, at 11:05 a.m., the plant entered a 72 hour limiting condition of operation (LCO) as required by Technical Specification 3.4.B(1)(a). Also during the event, the isolation of the chemical volume control system normal letdown occurred and the bank "C" rod "L3" bottom light did not illuminate as required by design. <br /><br /> The plant achieved hot shutdown at approximately 11:30 a.m. and restart was subsequently initiated with the generator breakers closed on the grid on January 8, 1991 at approximately 8:36 p.m. No NRC limit was exceeded. Likewise there was no impact on public health and safety.
2471991002 | Indian Point 2 | 01/09/1991 | 02/08/1991 | ML10033164 | <strong>Incorrect Amptector Settings for Fan Cooler Unit Motors</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1991, during resumption of power operation after a plant trip, the plant entered Technical Specification 3.0.1 as a conservative action when it was determined that the long delay time setpoints for the amptectors for three Containment fan motors were incorrectly established. The amptectors provide over current protection for the fan motors. The setpoints were readjusted to the correct value in less than 60 minutes and the plant exited Technical Specification 3.0.1. Technical Specification 3.0.1 applies when plant conditions exceed the conditions permitted by the Technical Specifications. <br /><br /> During subsequent analysis, it was determined that the setpoints, although inappropriately set, did not render two of the three fan motors inoperable. The plant was never in a condition not permitted by the Technical Specifications nor outside its design basis. Therefore, this Licensee Event Report is being submitted for the sole purpose of clarifying the record. There was no impact upon the health and safety of the public.
2471991003 | Indian Point 2 | 01/20/1991 | 02/19/1991 | ML10033165 | <strong>Toxic Gas Monitor / ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1991 at approximately 0200 hours, with the unit operating at 97% power, the toxic gas monitor ammonia (NH sub 3) channel 1 inadvertently alarmed, resulting in the transfer of the Central Control Room (CCR) Ventilation system from the normal mode to the incident mode.<br /><br /> As designed, the detection of NH sub 3 by the toxic gas monitor channels 1 or 2 will generate an alarm in the CCR and isolate the CCR ventilation system. The toxic gas monitor system and the CCR isolation system are engineered safety features. No Technical Specification or NRC limits were exceeded. Likewise there was no impact on public health and safety.
2471991004 | Indian Point 2 | 02/12/1991 | 09/27/1991 | ML10033175 | <strong>Damaged Hold-Down Bolts for Polar Crane Rail</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1991, while the plant was shutdown for a refueling outage, some of the studs used to secure the containment building polar crane rail to the concrete support wall were determined to have failed. 47 out of the 140 studs in one quadrant were affected. Based on the NUREG 0612 analysis, sufficient margin existed such that with the reduced bolt configuration, original acceptance criteria were met. Nevertheless, repairs were made before a heavy load lift was made. Root cause analysis indicates that the failures occurred several years ago and were caused by either a single overload event or corrosion fatigue/stress corrosion cracking, possibly due to excess torquing during installation. This report is provided as a voluntary submittal of information of interest to the NRC.
2471991005 | Indian Point 2 | 02/28/1991 | 03/30/1991 | ML10033165 | <strong>Loss of 6.9 kv Bus 5 Normal Feed</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1991, during a cold shutdown outage for refueling, a 6.9 kv bus normal feed breaker tripped open causing a loss of power to two 6.9 kv buses and their associated 480V buses. Approximately 30 seconds later, two station service transformer supply breakers tripped open upon actuations of two time delay relays which functioned when the 6.9 kv buses lost power. The loss of power to the 480V buses initiated the start up of two Emergency Diesel Generators (EDG's). A third EDG was out for maintenance. The EDG's did not automatically pick up the load of the 480V buses because the unit trip lockout relays were reset. As a result, equipment rendered out-of-service included one service water pump and one component cooling pump. Residual heat removal was not affected. The normal feed breaker was closed in approximately two minutes and power was restored to the 480V buses.
2471991006 | Indian Point 2, Indian Point 3 | 03/20/1991 | 04/19/1991 | ML10033166 | <strong>Loss of 138 kv Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1991, during a cold shutdown outage for refueling, the 138 kv normal offsite power supply was lost. This resulted in a loss of power to all station 6.9 kv and 480V buses. Due to maintenance being performed on two emergency diesels, only the third diesel automatically started. This diesel was manually connected to 480V bus 6A, and power was restored to two other 480V buses through the tie breakers which allowed for restoration of service water and component cooling pumps. Due to maintenance being performed on one of the batteries, there was a loss of one DC bus when its battery charger lost power. This bus was manually re-energized by means of a connection to another DC bus through a tie breaker. At the time of the event there was no fuel in the core and the spent fuel cooling flow was never lost because the spent fuel pump was being fed from an alternate source. Another 138kv feeder and 13.8kv offsite power remained available during this event. 138kv offsite power was restored within half an hour, and all 480V buses were returned to normal supplies by 2100 hours.
2471991007 | Indian Point 2 | 03/28/1991 | 04/29/1991 | ML10033166 | <strong>Auto-Start of Emergency Diesel</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1991, during a cold shutdown refueling outage, with fuel out of the core, emergency diesel No. 23 automatically started. The diesel had received an undervoltage signal from one of the 480V buses which initiated the start and stripped the loads on the bus. There was no apparent actual undervoltage condition on the 480V or 6.9 kv buses. All offsite power remained available, and all Engineered Safety Features performed as expected. A perturbation on the DC circuit associated with the undervoltage relays or an inadvertent bumping of a relay are the most probable causes for initiating the undervoltage signal.
2471991008 | Indian Point 2 | 04/03/1991 | 11/27/1991 | ML10033177 | <strong>Safety Injection Design Inconsistencies</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage, at Con Edison's initiative the six high pressure safety injection flow orifices were removed and inspected. It was determined that three plates were interchanged and one was reversed. New orifice plates were installed and the flow transmitters were recalibrated. Full flow tests and flow balancing tests were conducted and the results met the acceptance criteria.
2471991009 | Indian Point 2 | 06/05/1991 | 07/04/1991 | ML10033168 | <strong>Improper Installation of CONAX Connectors</strong><br /><i>Abstract:&nbsp;</i>During a planned preventive maintenance procedure for the limit switches associated with the Steam Generator Blowdown (SGBD) Containment isolation valves, it was determined that Conax connectors associated with limit switches were installed incorrectly. At the time of discovery the plant was at cold shutdown for a refueling outage. An evaluation of the Conax connector installation was initiated for those associated with the solenoid operated valves (SOVs) controlling operation of the SGBD isolation valves and subsequently to all installed Conax connectors. All 46 Conax connectors currently in service are located external to containment. Other equipment served by the Conax connectors include the main steam isolation valves (MSIVs) and associated limit switches as well as the recirculation valves/limit switches for the motor driven auxiliary feedwater pumps. <br /><br /> To determine operability of the "as found" configuration, the connectors together with SOVs/limit switches were subjected to functional testing in the "as found condition", with positive results being obtained. Test parameters enveloped the environment which would be seen under postulated accident scenarios. Accordingly, despite the discrepancy in the installed configuration, it was determined that all safety functions would have been fulfilled.
2471991010 | Indian Point 2 | 06/22/1991 | 07/22/1991 | ML10033169 | <strong>Diesel Generator Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1991, during testing of emergency diesel generator (EDG) No. 21 with the reactor at cold shutdown for refueling, the diesel output breaker to 480V bus 5A tripped. Loss of power on 480V bus 5A resulted since the normal offsite power breaker was open as part of the test configuration. The loss of power to 480V bus 5A initiated the "blackout" logic which started the other two EDGs and stripped the 480V buses of offsite power. These two EDGs automatically loaded to 480V buses 3A and 6A. Bus 2A was not automatically loaded because its diesel supply breaker had been racked out as part of the test configuration. One service water pump auto-started, and the residual heat removal, component cooling water, charging and additional service water pumps were started manually within one minute. The tie breaker between 480V buses 2A and 3A was then manually closed, thereby energizing bus 2A. Lighting and motor control centers (MCC's) were reset, and spent fuel pool cooling was re-established 36 minutes after the initial occurrence. Throughout the event offsite power was available, and there was no increase in either reactor coolant system (RCS) or spent fuel pool temperature. Offsite power to the 480V buses was restored and the diesels were subsequently unloaded.
2471991011 | Indian Point 2 | 07/07/1991 | 07/30/1991 | ML10033169 | <strong>Toxic Gas Monitor / ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1991, at about 0927 hours, with reactor power at 0%, the Anhydrous Ammonia (NH3) toxic gas monitor Channel 2 alarmed, resulting in the transfer of the Central Control Room (CCR) Ventilation System from the normal mode to the incident mode. A similar actuation of the Channel 1 Ammonia toxic gas monitor occurred on July 12, 1991. <br /><br /> As designed, the detection of ammonia by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The Toxic Gas Monitoring System is classified as an Engineered Safety Feature (ESF). No Technical Specification or NRC limits were exceeded.
2471991012 | Indian Point 2 | 07/21/1991 | 08/20/1991 | ML10033171 | <strong>Service Water System Leakage into Containment</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1991 a pinhole leak was detected in the 2" Service Water System piping (90% Cu; 10% Ni) supplying cooling water to the motor of fan cooler unit (FCU) #23. On August 1, 1991 a pinhole leak was detected in the return line from FCU #24. The location of the leak in both cases was approximately 1/8" from a weld. The cause has yet to be ascertained.<br /><br /> In the earlier event the plant was at 90% power. Due to extenuating summer weather conditions it was not possible to isolate the FCU, effect a Code repair and also maintain containment temperatures below the limiting temperature of 130 degrees F. Therefore a "housekeeping" repair (patch) was applied to the leak in FCU #23 and the line maintained "functional" although not "operable" in view of the Technical Specifications. An Limiting Condition of Operation (LCO) was entered and a code repair effected within the time limit for the LCO. <br /><br /> In the later event the plant was at 80% power. Cooler weather permitted isolation of the affected FCU and a code repair was accomplished within the applicable 7 day LCO. There was no impact upon the health and s fety of the public since minimum safeguards equipment was always available.
2471991013 | Indian Point 2 | 07/25/1991 | 08/26/1991 | ML10033172 | <strong>Reactor Trip due to RPS Over Temperature Delta Temperature</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1991 at 1556, with the unit operating at approximately 90% power and Reactor Protection System channel calibrations in progress, the reactor tripped. The trip was generated by the reactor protection system two out of four coincidence logic for Over Temperature Delta Temperature. The operators responded to the event in accordance with established plant procedures and plant systems responded as designed.<br /><br /> Following the review of the events by the Station Nuclear Safety Committee a reactor restart was initiated with the generator breakers closed on the grid on July 26, 1991 at approximately 1814. There was no impact on the health and safety of the public.
2471991014 | Indian Point 2 | 07/30/1991 | 08/29/1991 | ML10033171 | <strong>Inadvertent Actuation of EFS - Hydrogen Cyanide Toxic Gas Monitor</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1991, at approximately 1130 hours, with reactor power at 100%, the Hydrogen Cyanide (HCN) toxic gas monitor channel 1 alarmed inadvertently, resulting in the transfer of the Central Control Room (CCR) Ventilation System from the normal mode to the incident mode. <br /><br /> As designed, the detection of HCN by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The Toxic Gas Monitoring System is classified as an Engineered Safety Feature (ESF). No Technical Specification or NRC limits were exceeded.
2471991015 | Indian Point 2 | 08/05/1991 | 09/04/1991 | ML10033172 | <strong>Actuation of Toxic Gas Monitor, Initiating ESF</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1991, at about 1100 hours, with reactor power at 100%, the Anhydrous Ammonia (NH3) toxic gas monitor Channel 1 alarmed, resulting in the transfer of the Central Control Room (CCR) ventilation system from the normal mode to the incident mode. The source of the ammonia release was from the handling of ammonium hydroxide within the plant. <br /><br /> As designed, the detection of ammonia by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The Toxic Gas Monitoring System is classified as an Engineered Safety Feature (ESF). No Technical Specification or NRC limits were exceeded.
2471991016 | Indian Point 2 | 08/06/1991 | 09/05/1991 | ML10033172 | <strong>Inadvertent Actuation of Toxic Gas Monitors, Initiating ESF</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1991, at approximately 1150 hours, with reactor power at 100%, the Hydrogen Cyanide (HCN) toxic gas monitor channel 2 alarmed inadvertently, resulting in the transfer of the Central Control Room (CCR) Ventilation System from the normal mode to the incident mode. <br /><br /> As designed, the detection of HCN by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The Toxic Gas Monitoring System is classified as an Engineered Safety Feature (ESF). No Technical Specification or NRC limits were exceeded.
2471991017 | Indian Point 2 | 08/19/1991 | 09/18/1991 | ML10033174 | <strong>Inadvertent Actuation of Toxic Gas Monitors (ESF)</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1991, at approximately 0605 hours, with reactor power at 0%, the Hydrogen Cyanide (HCN) toxic gas monitor channel 2 alarmed inadvertently, resulting in the transfer of the Central Control Room (CCR) Ventilation System from the normal mode to the incident mode. Subsequent actuations of the hydrogen cyanide, chlorine and ammonia toxic gas monitor channels occurred on August 24, 28, 30, 31, September 6 and 10. <br /><br /> As designed, the detection of the respective gas by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The Toxic Gas Monitoring System is classified as an Engineered Safety Feature (ESF). No Technical Specification or NRC limits were exceeded.
2471991018 | Indian Point 2 | 08/31/1991 | 09/30/1991 | ML10033175 | <strong>Containment Radiogas Monitor Spurious Electrical Spike Cause ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>During the performance of a pressure relief of containment on August 31, 1991, with the plant at 100% power, the Containment Radiogas Monitor (R-42) experienced a spurious electrical spike, which in turn initiated Containment Ventilation Isolation and partially actuated the Weld Channel and Containment Penetration Pressurization (WCCPP) system. The WCCPP system is classified as an Engineered Safety Feature and it functioned as designed. After determining there had been no actual increase in gaseous activity, radiation monitor R-42 was reset and pressure relief was reinstituted. The health and safety of the public were not affected by this event.
2471991019 | Indian Point 2 | 09/11/1991 | 10/11/1991 | ML10033175 | <strong>Containment Spray Pump and NaOH Spray educator Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1991, and again on September 12, during the conduct of surveillance testing of a containment spray pump, the plant entered Technical Specification 3.0.1 which requires the unit to be shutdown within 7 hours unless corrective measures are completed that restore compliance to the Limiting Condition for Operation (LCO). In each case one containment spray pump and its associated spray additive eductor flow path were simultaneously declared inoperable and in each case the provision of Technical Specification 3.0.1 was exited within 20 minutes.
2471991020 | Indian Point 2 | 09/27/1991 | 10/28/1991 | ML10033175 | <strong>Determination of 480V Switchgear Room Temperature</strong><br /><i>Abstract:&nbsp;</i>Based on an engineering evaluation, it was determined on September 27, 1991 that the 480 Volt Switchgear room temperature, under certain conditions, could exceed the maximum temperature recommended by the safeguards equipment switchgear manufacturers. Specifically, during a loss of Coolant Accident with offsite power available, a postulated single failure could render the room's ventilation system unavailable, resulting in a calculated maximum ambient temperature of 135 degrees F after several hours for the worst summer design outside temperature of 95 degrees F. <br /><br /> Immediate corrective actions consisted of procedural changes to verify operation of the ventilation system during periodic operator rounds and, in the event of an accident, to open doors to establish natural circulation (stack effect).
2471991021 | Indian Point 2 | 10/04/1991 | 11/04/1991 | ML10253028 | <strong>Inadvertent Actuation of Hydrogen Cyanide Toxic Gas Monitor</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1991, at approximately 2340 hours, with reactor power at 99.5%, the Hydrogen Cyanide (HCN) toxic gas monitor channel 2 alarmed inadvertently, resulting in the transfer of the Central Control Room (CCR) Ventilation System from the normal mode to the incident mode. Subsequent toxic gas monitor channel actuations occurred on October 11, 12 and 17. <br /><br /> As designed, the detection of the respective gas by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The Toxic Gas Monitoring System is classified as an Engineered Safety Feature (ESF). No Technical Specification or NRC limits were exceeded.
2471991022 | Indian Point 2 | 11/28/1991 | 12/30/1991 | ML10033179 | <strong>Inadvertent Actuation of NH3 Toxic Gas Monitor</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1991, at approximately 0450 hours, with reactor power at 100%, the Anhydrous Ammonia (NH sub 3) toxic gas monitor channel 2 alarmed inadvertently, resulting in the transfer of the Central Control Room (CCR) Ventilation System from the normal mode to the incident mode. A subsequent NH sub 3 toxic gas monitor channel actuation occurred on November 29. <br /><br /> As designed, the detection of the respective gas by either Channels 1 or 2 of the toxic gas monitors will generate an alarm in the CCR and isolate the CCR Ventilation System. The Toxic Gas Monitoring System is classified as an Engineered Safety Feature (ESF). No Technical Specification or NRC limits were exceeded.
2471991023 | Indian Point 2 | 12/19/1991 | 01/21/1992 | ML10033179 | <strong>Venting of Charging Pump During VC Pressure Relief Causes ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1991, with the plant at 100% power, a gaseous release was in progress through the plant vent due to venting of a charging pump suction stabilizer during operational lineup of the pump following maintenance activities. The release was sufficient to exceed the setpoint of the Plant Vent Gaseous Activity Monitor (R-44) which resulted in isolation of the containment Ventilation system and automatic actuation of the Weld Channel and Containment Penetration Pressurization System. It was subsequently determined that the release corresponded to a maximum value of only 15% of the maximum instantaneous concentration permitted by Technical Specifications for an unrestricted area. The total noble gas radioactivity released was 0.072 curies. No Technical Specification or NRC limits were exceeded. The health and safety of the public was not affected by this event.
2491991001 | Dresden 3 | 01/14/1991 | 02/06/1991 | 9102140202 | <strong>De-energization of Reactor Protection System Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1244 hours on January 14, 1991 with Unit 3 in Shutdown at 0% rated core thermal power, Dresden Technical Staff Surveillance (DTS) 500-2, Functional Testing of Reactor Protection System (RPS) Motor Generator (MG) Set and RPS Reserve Power Supply, was being performed. When the power feed to the B RPS was transferred from the MG Set to Unit 3 Bus 39-5, an unplanned reactor scram signal occurred. During the test a half scram would normally occur when this step is performed. However, the reactor was already under a full manual scram, and because the scram discharge volume (SDV) high water level RPS trips were bypassed, both channels of RPS produced a scram signal. The safety significance of this event was considered minimal because the reactor was already in Shutdown mode, with all control blades fully inserted, and a full scram signal was already inserted. <br /><br /> The cause attributed to the de-energization of both RPS channels is procedural deficiency. The procedure lacked sufficient constraints concerning performance of the surveillance under a preexistent scram condition. A revision to the functional testing procedure, DTS 500-2, will be made to include the steps necessary to adequately perform the surveillance. This was the first occurrence of this type.
2491991002 | Dresden 3 | 05/06/1991 | 05/23/1991 | 9106030201 | <strong>Violation of Primary Containment Post Accident Monitor Surveillance Interval Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1230 hours on 5/6/91, with Unit 3 operating at 80% rated core thermal power, the Instrument Maintenance Department (IMD) Lead Scheduler notified Operations that the surveillance interval concerning functional check of the 3B Primary Containment Post Accident Hydrogen/Oxygen monitor had been exceeded. Technical Specification Table 4.2.4 requires a 31 day surveillance interval for this activity; application of all allowable extension criteria indicated that the functional check should have been performed prior to 5/5/91. Investigation revealed a root cause of management deficiency due to inadequate awareness of surveillance program requirements on the part of IMD Supervision, with a contributing cause of incognitive personnel error. This event was of minimal safety significance because Primary Containment post accident monitoring could have been performed via the High Radiation Sampling System gas chromatograph if necessary; a 30 day Limiting Condition for Operation was entered in accordance with Technical Specification Table 3.2.6 Note 5 since the redundant 3A monitor was inoperable. The LCO was terminated at 1850 hours on 5/6/91 upon satisfactory completion of the 3B monitor surveillance. Corrective actions initiated to prevent recurrence included review and clarification of surveillance tracking policy with appropriate personnel. A previous event involving a Technical Specification surveillance interval violation was reported by LER 88-14/050237.
2491991003 | Dresden 3 | 06/05/1991 | 07/01/1991 | 9107110176 | <strong>Inoperable Torus Wide Range Level Transmitters Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1991 at 2300 hours with Unit 3 at 53% core thermal power, a Nuclear Station Operator (NSO) discovered the Pressure Suppression Chamber (Torus) Wide Range Level Indicators 3-1640-10A and 3-1640-10B were reading approximately 13 feet. This conflicted with Torus Narrow Range Indicator 3-1602-3. The Torus Narrow Range Indicator has a scale from -20 to +20 inches and its reading on this band was approximately 0 inches, which corresponds to approximately 15 feet. The Torus Narrow Range local sightglass level was promptly verified at approximately 15 feet. The Instrument Maintenance Department (IMD) backflushed the sensing lines of the Torus Wide Range Level Transmitters 3-1641-5A and 3-1641-5B; no change in indication was noted. Dresden Instrument Surveillance (DIS) 1600-17, Torus Wide Range Level Transmitter Cali ration and Maintenance Inspection, was then performed to calibrate the transmitters. <br /><br /> While subsequently investigating the event, the System Engineer learned that the transmitters had apparently drifted out of calibration prior to the NSO's discovery, meaning that the 7 day Technical Specification Table 3.2.6 Limiting Condition for Operation with inoperable Torus Wide Range Level instruments had been exceeded. The root cause of the instrument drift is unknown; a supplemental report will be provided. Safety significance was minimal due to availability of the Narrow Range instrumentation. Corrective actions will include transmitter replacement.
2491991004 | Dresden 3, Dresden 2 | 07/08/1991 | 07/24/1991 | 9108050295 | <strong>Unplanned SBGTS Auto-start During Area Radiation Monitor Calibration Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1991 at 0810 hours with Unit 2 at 50% power and Unit 3 at 62% power, the Instrument Maintenance Department was conducting Dresden Instrument Surveillance (DIS) 1800-2, Area Radiation Monitor Calibration. An Instrument Mechanic (IM) had reached a portion of the procedure which required the disconnecting of a cable from the back of an Isolation Condenser Area Radiation Monitor Indicator Trip Unit which is located inside Control Room Panel 903-11. However, the IM inadvertently disconnected a cable supplying the Reactor Building Fuel Pool Channel A Process Radiation Monitor Indicator Trip Unit which is located inside an adjacent Control Room Panel. When the incorrect cable was disconnected the Standby Gas Treatment System automatically started and the Unit 2 and Unit 3 Reactor Building Ventilation Systems isolated. Prompt investigation by Control Room personnel identified the error and the affected systems were returned to normal. This event had no affect on normal power operation and the automatic actuations that occurred were as expected when challenged by the spurious Fuel Pool Area Radiation signals. A previous event involving an unplanned Engineered Safety Feature actuation due to personnel error was reported by LER 90-010/050237.
2491991005 | Dresden 3 | 07/11/1991 | 08/02/1991 | 9108120234 | <strong>Primary Containment Isolation Valve Closure Due to Reactor Water Cleanup System Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1991 at 0948 hours with Unit 3 at 63% power, a Reactor Water Cleanup (RWCU) System isolation occurred with Primary Containment Isolation Motor Operated valves (MOVs) 3-1201-1 and 3-1201-2 fully closing. Operational Analysis Department personnel were performing testing following modification to the RWCU water sample panel, when the unplanned RWCU isolation occurred. Investigation revealed that a momentary short circuit occurred when the power supply to the sample panel was turned on. This was evident by the fact that none of the sample panel instruments energized and the electrical feed went dead as soon as the power supply was turned on. It was discovered later that the main fuse which supplies 120 VAC to the sample panel had opened. The power supply to the RWCU high temperature indicating switches is also protected by this same fuse. When the fuse opened, power to the RWCU high temperature indicating switches was lost. The deenergization of these switches initiated a RWCU system isolation signal. Corrective actions included successful replacement of the fuse and prompt return of the RWCU system to normal operation. This event had no safety significance because the RWCU system properly isolated on the high temperature signal and isolation of the RWCU system for short periods has no affect on power operation or coolant chemistry limits. A previous unplanned RWCU system isolation was reported by LER 91-14/050237.
2491991006 | Dresden 3 | 08/17/1991 | 09/16/1991 | 9109190263 | <strong>Reactor Scram Due to Degraded Main Stop Valve Fast Acting Solenoid Valve Fast Acting Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1991, at 0116 hours, with Unit 3 operating at 56% rated core thermal power, a reactor scram occurred during surveillance testing of the Main Turbine Stop Valves (MSVs). While testing the #2 MSV, the Fast Acting Solenoid Valve (FASV) was not positioning properly, thus allowing a drop in the Emergency Trip System (ETS) oil pressure. This allowed the Combined Intermediate Valve Stop Valve (CIV SV) disk dump valves to actuate, resulting in the subsequent fast closure of the CIV SVs. Generator load dropped from 394 MWe to 25 MWe. As Reactor Recirculation flow was reduced, the Generator electrical output dropped to -1.5 MWe. This caused the generator to trip on reverse power. The generator trip caused a subsequent turbine trip, which resulted in an automatic reactor scram when the turbine MSVs closed. Subsequent testing of the MSVs, following the event, could duplicate closure of only one of the CIV SV's. <br /><br /> Following the reactor scram, voltage on Bus 33-1 dropped below 4000 volts (normal is 4160 volts). The voltage drop was addressed and compensatory actions were taken per Operating Order #20-91, Compensatory Actions Associated with Degraded Voltage. As corrective actions for this event, the #1 and #2 MSV FASVs were replaced. Periodic replacement of the FASVs will be made a preventative maintenance item. Also, orifice plugs will be installed at the ETS inlet to FASVs to prevent temporary loss of ETS pressure. These plugs will be installed during the current Unit 3 Refuel Outage. The safety significance of this event was considered to be minimal since all reactor scram functions operated properly and the reverse power relay functioned to prevent damage to the main generator. MSV FASV failures of this type have not been a previous adverse trend.
2491991007 | Dresden 3 | 09/10/1991 | 09/25/1994 | 9411010307 | <strong>Type B and C Primary Containment Local Leak Rate Testing Limit Exceeded due to HPCI Turbine Exhaust Check Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1991 with Unit 3 in a refueling outage, while performing Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing of Primary Containment Isolation Valve B, the leakage between the 3-2301-74, High Pressure Coolant Injection (HPCI) [BJ] Turbine Exhaust To Suppression Chamber Stop Check Valve, and the 3-2301-45, HPCI Turbine Exhaust Check Valve, was unable to be determined. Further diagnosis and previous LLRT history indicated that the 32301-45 was the leaking valve. This valve leakage exceeded the Technical Specification 3.7.A.2.b(2)(a) limit of 488.452 scfh. Inspection of the check valve revealed a torn seat. The valve was replaced. The valve seat failed as a result of excessive valve cycling. The operating procedures for the turbine have been modified to prevent low turbine exhaust pressure operations which will in turn prevent cycling of check valve 3-2301-45. The safety significance of this event was minimal because the redundant in-line isolation valve leaked 84 scfh. <br /><br /> The total as-found minimum pathway leakage (Type A test) was 1.4595 wt%/day which exceeded the Technical Specification limit of 1.2 wt%/day. Calculations have been performed to prove this leakage did not exceed 10 CFR 100 limits.
2491991008 | Dresden 3 | 08/30/1991 | 09/27/1991 | 9202030258 | <strong>Unplanned Primary Containment Group V Isolation Due to a Blown Bulb</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1991, at 1503 hours with Unit 3 in the Run mode at 51% of rated core thermal power, while replacing a burned out light bulb on the Control Room position indication for Low Pressure Coolant Injection (LPCI) System inboard manual isolation valve 3-1501-26A, the light bulb caused a short circuit and caused fuse 595-714B to open. Simultaneously, a Primary Containment Group V Isolation was received, and the appropriate Isolation Condenser isolation valves closed as designed. The bulb and fuse were immediately replaced; subsequent replacement of the socket was completed under Work Request (WR) 03389. Inspection of the removed socket indicated that the root cause was a cracked housing. The safety significance of this event was minimal since the Isolation signal was reset and all active components of the High Pressure Coolant Injection (HPCI) system remained operable during the event. To prevent recurrence of this event, during the current Unit 3 refueling outage (D3R12) and the next Unit 2 refueling outage (D2R13) a minor plant modification will add two fuses in series to isolate the LPCI indication circuit from the isolation condenser isolation valve control circuitry. A previous event involving an unplanned Primary Containment Group V isolation was reported by LER 90-005 on Docket 0500237.
2491991009 | Dresden 3 | 09/20/1991 | 10/04/1991 | 9209240030 | <strong>Failure to Perform Post-Maintenance Local Leak Rate Test Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>During performance of 10CFR50 Appendix J Local Leak Rate Testing (LLRT) with Unit 3 in a refuel outage, the test volume containing containment vent and purge system valves 3-1601-23, -24, -60, -61, -62 and -63 was identified to have excessive leakage. Further testing identified the 3-1601-24 valve as the leakage source. Further investigation revealed that maintenance work had been performed on the 3-1601-24 valve air operator during the previous refuel outage without completion of a proper post-maintenance LLRT as required by 10CFR50 Appendix J. The review determined that the air operator closure stroke was inadvertently misadjusted during installation of a new piston rod. The root cause was attributed to management deficiency in that inadequate controls were provided within the work package to prohibit activities affecting closure integrity without completion of a post-maintenance LLRT. Safety significance was mitigated by the fact that actual containment leakage under design basis accident conditions would have been prevented by redundant isolation valves which were proven intact via LLRT during the current refuel outage and during satisfactory performance of a Type A Integrated Leak Rate Test during the last refuel outage. Review of work packages from the last Unit 2 refuel outage was promptly initiated, and identified two additional LLRT violations. Corrective actions will include improvements to the work control process. A previous event involving an LLRT violation was reported by LER 90-018/050237.
2491991010 | Dresden 3 | 09/23/1991 | 10/17/1991 | 9207080251 | <strong>Bus 38 Undervoltage Relay Actuation Due to Inadvertent Shorting of Relay Terminals</strong><br /><i>Abstract:&nbsp;</i>During performance of Dresden Electrical Surveillance (DES) 500-2, HFA Relay Electrical Maintenance Inspection, on September 23, 1991, with Unit 3 in cold shutdown for a refuel outage, 480V Bus 38 partially load shedded upon actuatuation of undervoltage relay #227-B38-X1 when an Electrician unintentionally shorted a tool across two terminals of the relay. This actuation caused trips of the Reactor Water Cleanup Auxiliary Pump, the 3C Reactor Building Vent Fan, the 3B Reactor Building Exhaust Fan, and the 3A South Turbine Building Vent Fan. DES 500-2 was immediately terminated and all affected equipment was restored to normal operation. The safety significance of this is event is considered minimal because the load shedding trips occurred properly when challenged by the undervoltage signal and there was no affect on redundant division equipment, nor was there any significant affect on normal plant status. Corrective actions included a review of the event with the personnel involved. The Electrical Maintenance Department purchased insulated nut drivers for this type of activity. A previous event involving an unplanned start of a Diesel Generator during use of a hand held voltage tester was reported by LER 90-01/050249.
2491991011 | Dresden 3 | 09/23/1991 | 10/15/1991 | 9110280218 | <strong>Loss of Main Control Room Annunciator Power Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1991, during the Unit 3 refuel outage with all fuel removed from the reactor vessel, audible and visual alarms were received indicating a loss of power to Main Control Room (MCR) Panels 903-3, -4, -5, -6, -7 and -8. Operations personnel determined fuse F-25 in Annunciator Input Cabinet 903-34 had opened. At 1100 an Alert was declared in accordance with the Dresden Emergency Action Levels. At 1113, fuse F-25 was replaced and proper annunciator operation was restored. All work in the MCR and the Auxiliary Electric Equipment Room (AEER) was stopped pending further investigation. A review of the circuitry revealed that the negative 125 VDC to all annunciator chassis commons was fed from fuse F-25. A copper link was installed in place of F-25, with Nuclear Engineering Department concurrence, and the Alert was terminated at 1445. The original plant design did not have a fuse in this circuit. The fuse was installed in January, 1990, as part of an annunciator system modification. This is a large modification which is being installed in stages and construction is continuing during the current refuel outage. As a corrective action for this event, the designers of the modification are reviewing the circuit to determine if individual fusing of the chassis commons is feasible. The safety significance of this event was considered minimal as all fuel was removed from the reactor vessel and normal annunciator operation was promptly restored. This is the first event involving loss of multiple annunciator panels due to a single fuse failure.
2491991012 | Dresden 3 | 11/20/1991 | 12/19/1991 | 9112300036 | <strong>Partial Primary Containment Group II Isolation During Maintenance Repairs Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 2213 hours, with Unit 3 in the shutdown mode, 14 of the 44 Group II Primary Containment Isolation Valves went closed when an Electrician lifted a neutral lead in preparation for replacement of a terminal block under Work Request 04380. This event has been attributed to personnel error on the part of the Electrical Work Analyst who prepared the work package. The Analyst did not fully research the wiring diagram for the panel which contains the terminal blocks, and thus did not identify the circuits "daisy-chained" to the neutral lead connected at the terminal block to establish the correct Out-Of-Service (OOS) boundaries. One of these "daisy-chained" circuits contains the trip contacts for the 14 valves which closed. This event had minimal safety significance because the unplanned valve closures had no effect on the plant status, and the Group II isolation function was not impaired. As a corrective action, this event will be discussed with the Electrical Maintenance Department Work Analysts. One previous event involving inadvertent Group II valve closures due to a lifted lead is reported in LER 90-22/0500237.
2491991013 | Dresden 3, Dresden 2 | 10/14/1991 | 11/12/1991 | 9209300074 | <strong>250 Volt DC Battery Discharge Voltage Decreased Below Design Basis Limit Due to Inaccurate Vendor Data</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1991, with Unit 3 in a refuel outage, the Unit 3 250 volt battery was removed from service in preparation for a discharge test as required by Technical Specification 4.9.A.3. Unit 2 was operating at power at this time. This placed Unit 2 in a 7 day Limiting Condition for Operation, in accordance with Technical Specification 3.9.B.4.a. During the first minute of the service test, the battery voltage dropped below the acceptance criterion of 210 volts. The voltage stabilized above 210 volts for the remainder of the four-hour test. A subsequent performance test indicated a battery capacity of 96% of rated value. A comprehensive review of the tested load profile was begun. Since resolution of the issue was still pending, and battery operability had not been re-instated, an orderly shutdown of Unit 2 was initiated on October 21, 1991. A review of the Unit 3 250 volt battery inter-tier cable resistances indicated that their resistances had increased since the replacement battery was originally installed in May, 1988. The inter-tier cables were replaced and their resistances were verified satisfactory. An abbreviated one minute service test was then performed on October 27, 1991; the battery voltage acceptance criterion was again not met. On November 1, 1991, a service test was successfully performed utilizing a revised load profile. The root cause of this event is attributed to inaccurate vendor one minute discharge curves. The use of this inaccurate information has been previously reported by the Nuclear Engineering Department per 10CFR21. The safety significance of this event is mitigated by availability of redundant equipment powered by separate sources. The safety significance of this event is mitigated by availability of redundant equipment powered by separate sources. Corrective actions include the installation of four more battery cells to the existing 116 cells of the 250 volt batteries and the installation of an auxiliary relay in the High Pressure Coolant Injection logic circuit. This is the first event of this type at Dresden Station.
2491991014 | Dresden 3 | 10/22/1991 | 11/07/1991 | 9111260211 | <strong>3-1105A and 3-1105B SBLC Relief Valves Lifted Under the Acceptance Criteria Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1991 at 0900 hours with Unit 3 in the refuel mode with all fuel removed, Standby Liquid Control (SBLC) relief valves 3-1105A and 3-1105B opened at 1410 psig when tested during the performance of Dresden Maintenance Procedure (DMP) 1100-2, Standby Liquid Control Relief Valve Setting. This exceeded the Technical Specification limit of 1455 to 1545 psig. New relief valves were installed by the Mechanical Maintenance Department, and during subsequent testing the valves lifted within the Technical Specification limit. The cause of this event is relief valve setpoint drift. <br /><br /> While the SBLC relief valves were being tested per DMP 1100-2, the SBLC system was not required to be operable. The as-found relief valve settings would not have diverted SBLC flow from the reactor under design basis conditions with both pumps operating. In addition, the Control Rod Drive (CRO) hydraulic system was operable when required during the operating cycle prior to this event, and therefore was available for shutting down the reactor. <br /><br /> A previous event involving the Unit 3 SBLC relief valves was reported by LER 88-07/050249.
2491991015 | Dresden 3, Dresden 2 | 11/05/1991 | 12/05/1991 | 9202280197 | <strong>Unplanned Standby Gas Treatment System Automatic Initiation Signal Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, with Unit 2 shutdown and Unit 3 in a refuel outage, the Electrical Maintenance Department (EMD) was scheduled to perform a preventive maintenance surveillance of the Unit 3 Reactor Protection System (RPS) Motor Generator (MG) Set Output Breakers. With the 'B' Train of the Standby Gas Treatment System (SBGTS) already operating and the Reactor Building Ventilation System (RBVS) isolated, the EMD installed a temporary power supply to the Channel 'B' Refuel Floor and Reactor Building Ventilation Radiation Monitors to prevent an automatic start of the SBGTS and an isolation of the RBVS upon the removal of the 'A' RPS MG Set from service. The Operations Department then removed the 'B' RPS MG Set from service, resulting in the de-energization of the 'A' RPS bus. This produced an unplanned SBGTS automatic start signal and an unplanned RBVS isolation signal. The Control Room operators anticipated an automatic start of the 'A' Train of the SBGTS under these conditions; however, this did not occur. This event had minimal safety significance because there was no effect on plant status. Corrective actions include review of this event with Operations personnel, procedural improvements, and a labelling evaluation. A previous event involving an unplanned automatic SBGTS start was reported by LER 91-04/050249.
2501991001 | Turkey Point 3 | 01/03/1991 | 04/05/1991 | 9104120246 | <strong>Material Discrepancy Involving the 3C Component Cooling Water Heat Exchanger Tubes</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1991, with Turkey Point Unit 3 shutdown and defueled, a loss of water inventory in the surge tank for the Component Cooling Water (CCW) System was detected. Inspection of the 3C CCW Heat Exchanger (HX) found two tubes which exhibited through-wall erosion corrosion characteristics. The defects were present at the inlet end of the tubes where Intake Cooling Water (ICW) enters the HX. The through-wall erosion corrosion resulted in a leak path being created between the CCW system and the ICW system. Records reviewed established that the two through-wall erosion corrosion tubes were installed in March 1990. Material testing on the two tubes determined that they were made of admiralty brass and not aluminum brass as specified for the HX. The most significant performance characteristic difference between admiralty brass and aluminum brass is that admiralty brass has a lower maximum recommended flow velocity of 4-6 ft/sec compared to 8 ft/sec for aluminum brass. The average operating flow velocity through the HX is approximately 5 ft/sec; however, inlet velocities could be higher due to water entry patterns. Both admiralty brass tubes were replaced.
2501991002 | Turkey Point 3 | 07/23/1991 | 08/19/1991 | 9108230165 | <strong>Inadvertent Reactor Trip Signal Due To Inadequate Work Controls</strong><br /><i>Abstract:&nbsp;</i>At 1126 on July 23, 1991, with both units shut down and defueled, a Reactor Protection System (RPS) actuation occurred. With RPS Channel I already actuated for maintenance work, an I&C Specialist working in Channel III bumped a breaker, de-energizing the Eagle Partial Trip module. This resulted in actuation of RPS Channel 3 which made up a 2 out of 3 logic, generating a Reactor Trip Signal. This event was caused by licensed operators closing the reactor trip breakers without first ensuring that planned activities would affect only one protection channel at a time. All work in sensitive areas was stopped. Meetings were held to emphasize required work controls. Work is now allowed on only one channel/train at a time (work has been allowed in multiple channels during the dual unit outage). The Plant Supervisor - Nuclear and a member of the Configuration Control Team must approve all work before it can begin. Licensed operators must review the Sequence of Events (Recorder) once per shift. A special edition of the plant's weekly newsletter, and a Training Brief, were issued to increase plant personnel awareness.
2501991003 | Turkey Point 3 | 07/24/1991 | 08/19/1991 | 9108230204 | <strong>Loss Of 3A And 3B 4KV Vital Busses Due To Generator Lockout Signal</strong><br /><i>Abstract:&nbsp;</i>Power to Unit 3 4KV vital busses A and B was being backfed through the main and Auxiliary transformers from the switchyard. At 1729 on July 24, 1991, a main generator lockout signal tripped the generator output breaker, and power was lost to the Unit 3 vital busses for 14 minutes. The most probable cause is a Potential Transformer (PT) drawer improperly closed, resulting in inadequate contact between the drawer stabs and wipes. The stabs and wipes in all PT drawers have been cleaned and the wipes resilvered. The closure linkage has been checked and all drawers verified closed. Caution tags have been added to each drawer front (until permanent signs become available) to remind personnel to ensure drawers are closed completely and locked. A training brief has been distributed to all operators and electrical maintenance personnel describing the incident and the corrective actions. Control of the keys to the PT cabinets has been transferred formally to Operations.
2501991004 | Turkey Point 3 | 08/22/1991 | 09/19/1991 | 9109240318 | <strong>Inadvertent Start Of 3A Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At 1955 on August 22, 1991, the 3A Emergency Diesel Generator (EDG) inadvertently started. Startup personnel were performing a scheme verification on wire leads located in a newly replaced cable in the 3A EDG rapid start circuit. When they lifted the rapid start leads the EDG started, due to shorting the leads together. The leads were relanded, and the EDG was shut down. The cause of the event was inadequate communication between Startup personnel and licensed operators. The Nuclear Watch Engineer and the Assistant Plant Supervisor - Nuclear knew the work involved the 3A EDG but were unaware that leads would be lifted. The Unit 3 Reactor Control Operator knew that leads would be lifted, but thought the work was on the 3B EDG. Startup Field Procedures have been revised to require that the Plant Supervisor - Nuclear give concurrence, by signature, to perform any scheme verifications on an energized circuit. Startup personnel have been trained on the procedure revisions. Operators will be briefed on this event, and the implications of ineffective communications.
2501991005 | Turkey Point 3 | 08/30/1991 | 09/30/1991 | 9110080350 | <strong>Automatic Start Of 3A Component Cooling Water (CCW) Pump On Low Pressure Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1250 EDT, on August 30, 1991, with Unit 3 in Mode 6 (Refueling) and Unit 4 defueled, the 3A Component Cooling Water (CCW) Pump started automatically on a low CCW system pressure signal. After removing the temporary spent fuel pool cooling connections, the CCW piping to and from the spent fuel pool heat exchanger was refilled with CCW water to restore normal spent fuel pool cooling. While refilling these lines, the CCW surge tank level decreased to five percent. At five percent surge tank level, the control room operator stopped the 3A and 3B CCW Pumps to prevent cavitation. The 3A CCW pump restarted automatically. The 3A CCW pump was immediately secured. Both 3A and 3B CCW pumps were placed in "pull to lock" to prevent another automatic start. After restoring the surge tank level, CCW pump 3A was restarted. A four hour non-emergency report was made to the NRC at 1417 EDT in accordance with 10 CFR 50.72. <br /><br /> The root cause of this event was non-cognitive personnel error by plant licensed operators. An inadequate briefing coupled with less than adequate coordination between the personnel involved resulted in a failure to anticipate reduced water inventory. The immediate cause was the failure to place the CCW pumps in "pull-to-lock" when the pumps were secured to prevent cavitation. To prevent recurrence, a series of meetings were held with applicable operations personnel to discuss proper briefings for fill and vent operations.
2501991006 | Turkey Point 3, Turkey Point 4 | 09/21/1991 | 10/04/1991 | 9110110207 | <strong>Mode Change Without Meeting Requirements Of Technical Specification 3.0.4 Due To Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On September 21, at 0340, contrary to the requirements of Technical Specification (TS) 3.0.4, Unit 3 entered Mode 3. Unit 4's Refueling Water Storage Tank (RWST) had less than the 320,000 gallons of borated water required by TS 3/4.5.4 for an operable RWST. The Unit 4 Safety Injection (SI) Pumps' suction was aligned to the Unit 4 RWST. There- fore, both Unit 4 SI pumps were inoperable because they were not aligned to an operable flow path. Action e. of TS 3.5.2 allows 72 hours to restore one of the Unit 4 SI pumps to operable status or be in Mode 3 in an additional 6 hours and Mode 4 within the following 6 hours. This condition was discovered on September 23, 1991, at 2340. The Unit 4 SI Pumps were made operable at 0100 on September 24, 1991, by opening the cross-connect valves allowing them to take suction from the Unit 3 RWST. The Unit 3 RWST was operable since it contained more than 320,000 gallons of borated water. Thus the Action requirements of TS 3.5.2 were met. The root cause of this event was procedural inadequacies which did not require the system configuration to consider RWST operability in the acceptance criteria for system operability. Procedures 3/4-OP-062, "Safety Injection"; 3/4-OSP-201.1, "RCO Daily Logs"; 3/4-OSP-202.1, "Safety Injection/Residual Heat Removal Flowpath Verification"; and 3/4-GOP-503 "Cold Shutdown to Hot Standby" have been revised to add the RWSTs to the acceptance criteria for system operability and alignment verification.
2501991007 | Turkey Point 3 | 09/25/1991 | 10/22/1991 | 9110300012 | <strong>Unit 3 Entered Mode 2 With One Of Two Intermediate Range Nuclear Instrumentation Channels Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0851 on September 25, 1991, Unit 3 logged entry into Mode 2. At 0950, the Unit 3 Reactor Control Operator declared Excore Nuclear Instrument Intermediate Range Channel N-35 inoperable, prior to going critical, when it did not respond to increasing neutron counts. The detector cables for the N-35 channel were found disconnected at the back of the drawer. The root cause of the event was personnel error by non-licensed utility personnel, in that inadequate control of the lifted leads between the N-35 drawer and the detector occurred. The cables for all other Unit 3 excore detectors were checked to ensure that no other cables were disconnected. The maintenance procedure has been revised to include lifted lead/connector documentation and independent verification. Outstanding plant work orders involving mode-deferred testing have been reviewed to ensure similar concerns for other systems do not exist.<br /><br /> Maintenance personnel have been trained on the significance of the event. A policy letter has been issued requiring the use of Lifted Lead Control procedures for work involving lifted leads, when the leads are not specified and independently verified in a procedure. Turkey Point's lifted lead controls will be reviewed against INPO and industry practices.
2501991008 | Turkey Point 3 | 10/03/1991 | 11/01/1991 | 9111060336 | <strong>Manual Reactor Trip Following Loss of Main Turbine Generator Load Due to a Mechanical Failure of a Piping Nipple Control Oil System</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1991, at 1200 EDT, with Unit 3 at 50 percent power and Unit 4 in Mode 6 (Refueling) the Unit 3 reactor was tripped manually due to a loss of main turbine generator load. The unit was stabilized in Mode 3 (Hot Standby) with steam generator water levels being maintained by the Main Feedwater System and steam being dumped through the atmospheric dump valves. An Event Response Team was formed to determine the cause of this event and to recommend applicable corrective actions. As part of this investigation, a pipe break was discovered in the control oil piping to the North-East Intercept valve. Examination of the break area indicated the cause of the pipe break to be fatigue failure at the root of the pipe nipple at the control orifice. The fatigue was caused by pipe vibration. A significant contributor to the vibration was a spring-can support for the low pressure steam line that had one of the compression nuts restraining spring-can movement. The broken pipe was repaired and the spring retainers have been removed from the spring-cans. The nipples upstream of the other three Unit 3 intercept valves will be replaced during the next refueling outage. The supports for the control oil piping on both units will be modified to prevent excessive vibration. The Unit 4 nipples upstream of the intercept valves were replaced and the removed nipples inspected for fatigue damage. No fatigue damage was found.
2501991009 | Turkey Point 3 | 10/18/1991 | 11/15/1991 | 9111260004 | <strong>Axial Flux Difference Was Outside the Limits of Technical Specification 3.2.1 For Greater Than the 15 Minutes Allowed by Action a. Due to an Inadequate Procedure.</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1991, at 0010 EDT, with Unit 3 at 100 percent power and Unit 4 in Mode 5 (Cold Shutdown), the 15 minutes allowed by Technical Specification (TS) 3.2.1 (a) (Axial Flux Difference) for axial flux difference outside the target band was exceeded.<br /><br /> On October 18, 1991, at 0135 EDT, the condition was determined to be inconsistent with the TS. Reactor power was then reduced to below 90 percent and the axial flux value was returned to within the target band. An evaluation of the event showed that for the worst case, indicated axial flux was outside the target band for about two hours. The Turkey Point Nuclear Steam Supply System Vendor performed a safety evaluation on this event. The safety evaluation concluded that the nuclear safety parameters F sub Q and DNBR stayed within their limits. <br /><br /> This event was caused by a procedure that did not meet the TS requirements and an error that was discovered in the plant TS. A TS amendment request has been submitted to correct the TS error. A temporary waiver of compliance was issued on October 30, 1991, allowing Turkey Point to perform the surveillance. Operations Procedure OP-12304.8, "Inducing Xenon Oscillations to Produce Various Incore Axial Offsets," is being revised to require performance of the procedure below 90 percent power.
2501991010 | Turkey Point 3, Turkey Point 4 | 01/23/1991 | 03/24/1992 | 9203300323 | <strong>Inadequate Leak Testing of Iron-55 Source</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1992, during a review of industry information, Health Physics personnel identified a deficiency in the leakage testing of sealed sources. Leak testing is required by Technical Specification (TS) 3/4.7.7. It was determined that the instrument used for leak testing of a metal alloy analyzer containing an Iron-55 sealed source did not have the required sensitivity to detect the low energy emissions produced by the Iron-55 source. Therefore TS 3/4.7.7 was violated as of January 23, 1991, when the six month surveillance interval was exceeded. The cause of this event was the failure of the individuals involved to recognize the limitation of the leak test equipment. A contributing factor was failure to address sealed sources that contain radioactive material other than alpha, beta, or gamma emitting radionuclides in the procedure for leak testing of radioactive sources. The analyzer was impounded until proper leak tests were performed, which verified that the source was free of leakage. Health Physics reviewed the site source inventory and ensured that all other sealed sources on site are being adequately leak tested. Other corrective actions include revisions to the procedures controlling purchase and leak testing of sealed sources, and transfer of the alloy analyzer to Florida Power and Light Company's Purchasing Quality Control Department, under the General License provisions of the Florida Administrative Code. Since no contamination levels were found in excess of TS limits, there were no safety consequences as a result of this event.
2501991011 | Turkey Point 3, Turkey Point 4 | 10/11/1991 | 12/18/1991 | 9201090114 | <strong>10 CFR 50 Appendix R Safe Shutdown Analysis Design Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1991, at 0700 EDT, Florida Power and Light identified an Appendix R Safe Shutdown Analysis design inadequacy at Turkey Point. Originally considered not reportable, further review resulted in the decision to report the condition as one not covered by procedures. As described in the Turkey Point Appendix R Alternate Shutdown analysis, our design and procedures are required to be able to shut down the plant for a fire which may occur in the control room or the cable spreading room. Additionally, a loss of offsite power is assumed to occur. The procedure for control room evacuation directs the removal of power from the safeguards relay racks, but this action may not prevent a spurious short from occurring on the output side of a safeguards relay. The resulting spurious actuation of a safeguards auxiliary relay, coupled with disabling of the Emergency Diesel Generator (EDG) load sequencer, will result in tripping of the EDG output breaker. This scenario applies to the 3B and the 4B EDGs. The Manual Action List in the Safe Shutdown Analysis, and the Off-Normal Operating Procedure for control room evacuation, have both been revised to require the removal of fuses which will prevent the spurious actuation of the auxiliary relay.
2501991012 | Turkey Point 3, Turkey Point 4 | 10/07/1991 | 12/19/1991 | 9112300269 | <strong>Use of Design Delta-Temperature (Delta-T) Rather Than Indicated Delta-T for Delta-T sub o in Overpower Delta-T and Overtemperature Delta-T Setpoints as Required by Technical specifications for Units 3 and 4.</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, with Unit 3 at 50% of rated power, during calibration of a new digital instrumentation rack, the Delta-T sub o factor in Overpower Delta-T and Overtemperature Delta-T setpoint formula was found to be set at the design value (56.1 Degrees F) instead of the indicated value as required by Technical Specifications. A safety evaluation was performed to assess the effect of the higher Delta-T sub o factor. The evaluation concluded that the plant had been operating within its design bases during all past cycles. Indicated Delta-T values at rated thermal power were obtained following calibration and inserted for the Delta-T sub o factor in OP Delta-T and OT Delta-T setpoint formula. <br /><br /> The event was determined to be reportable, in accordance with 10 CFR 50.73(a)(2)(i)(B), during a detailed review of a safety evaluation which was submitted to the Plant Nuclear Safety Committee for review on November 29, 1991.
2501991013 | Turkey Point 3, Turkey Point 4 | 12/06/1991 | 12/13/1991 | 9112260025 | <strong>Uncontaminated Leakage From Waste Container Due To Inadequate Container Lower Door Seal.</strong><br /><i>Abstract:&nbsp;</i>Between December 2 and December 4, 1991, two 20-foot Sea-Land containers were loaded with contaminated scaffolding. Several inspections of the containers were performed prior to loading to identify defects which could compromise the containers integrity. No leakage was observed during any inspection. On December 5, 1991, this shipment was released and consigned to the Quadrex Recycle Center in Oak Ridge, Tennessee. <br /><br /> On December 6, 1991, at 0908, Health Physics (HP) was notified by the consignee that a small amount of liquid had leaked onto the ground where the vehicle was parked, in Jasper, Florida. HP requested the Quadrex Recycle Center to immediately dispatch their radiological emergency response team to take radiological measurements and report their findings to FPL, and to control the leak and clean up any contamination found. <br /><br /> The leaking fluid was determined to be uncontaminated water. Condensation was observed in the container, and there was evidence that some water had escaped through the lower door seal. This event occurred because the lower door seal of the container did not prevent leakage of condensation. The condensation developed as the temperature of the air around the container dropped from over 80 degrees F at Turkey Point, to less than 40 degrees F in Jasper. Door seals will be caulked with a flexible silicon sealant. Containers that are already filled and ready for shipment will be unloaded, inspected, and reloaded. <br /><br /> This is a voluntary LER submitted in accordance with the guidance of NUREG 1022 Revision 1.
2511991001 | Turkey Point 4 | 03/13/1991 | 04/12/1991 | 9104180370 | <strong>Unit 4 Startup Transformer De-Energized</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1991 at 1528 EST, with Unit 3 and Unit 4 defueled, the Unit 4 startup transformer locked out, which caused the 4A 4160 volt bus to de-energize. The 4B 4160 volt bus was already out of service. Two of four available non-safety related diesel generators were started and made available to provide power to the 4A bus. Power was restored to the 4A bus at 1635. Loss of power to the 4A bus resulted in the loss of normal spent fuel pool cooling. The pool temperature increased by approximately 3 degrees F. to 87 degrees F. during the time the cooling system was not in operation. An Unusual Event was declared at 1550 and terminated at 1727 when the spent fuel pool cooling was restored. State and NRC notifications were made as required. An Event Response Team (ERT) could not determine a root cause for this event. The ERT concluded that the most probable root cause of this event was inadequate process control. Construction waste materials (metal shavings) fell into a control panel that was still energized. These metal shavings may have caused a short that initiated the event. The waste materials were removed. Applicable procedures were revised to ensure clean work practices. Another procedure was revised to identify and provide additional controls for work on, and around, sensitive equipment. A training brief describing this event was issued to emphasize the importance of good housekeeping.
2511991002 | Turkey Point 4 | 01/07/1991 | 10/02/1991 | 9110100196 | <strong>4A Emergency Diesel Generator Permanent Magnet Generator Failures Due To Design Inadequacy</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being submitted following the guidance provided in NUREG 1022, Supplement 1, Item 19.1. <br /><br /> On January 7, 1991, and on July 29, 1991, with both units defueled and during performance of the 4A Emergency Diesel Generator (EDG) tests, the Permanent Magnet Generator (PMG) failed. The January test was being performed as part of phase 1 of the FPL acceptance testing prior to turnover of two new EDGs to the plant. The July 29 failure occurred during a 24 hour test run required prior to declaring the EDGs operable. EDGs 4A and 4B have been installed as part of the Emergency Power Systems Enhancement Project (EPS). The January event was caused by a drive shaft failure determined to have been caused by misalignment of the shaft. Following the January event, new PMG shafts were installed on both 4A and 4B EDGs. In addition, a new alignment procedure was provided by the vendor. Both events were determined to have been caused by inadequate design in that the drive shaft arrangement was unable to maintain sufficient clearance between the PMG rotor and stator. The PMG was removed from EDGs 4A and 4B and replaced with a system powered from the 125 VDC station battery. Note, the PMG arrangement on EDGs 4A and 4B was a one-of-a-kind addition designed specifically for Turkey Point Unit 4. EDGs 3A and 3B do not have PMGs, therefore this problem was not applicable to Unit 3.
2511991003 | Turkey Point 4 | 06/26/1991 | 06/28/1991 | 9107080098 | <strong>De-Energization Of Intake Cooling Water System Pump Causes The Interruption Of Spent Fuel Pool Cooling Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being submitted following the guidance provided by NUREG 1022, Supplement 1, Item 19.1. <br /><br /> On June 26, 1991, at 0308 EDT, with both units defueled, the Unit 4, 4D 4kV bus locked out. The bus lockout resulted in the de-energizing of the 4C Intake Cooling Water pump and the 4C Component Cooling Water (CCW) Pump. CCW pump 4A was in service and remained in service during this event. With 4A and 4B ICW pumps out of service for maintenance, the de-energizing of the 4C ICW pump made the Spent Fuel Pool (SFP) cooling system inoperable since the normal heat sink was not available. <br /><br /> On June 26, 1991, at 0403 EDT, the 4C CCW pump was started and at 0412 EDT, 4C ICW pump was started restoring the normal heat sink for the Unit 4 SFP cooling system.<br /><br /> The root cause of this event was inadequate administrative controls. A sensitive equipment list used in preparing a work package was superseded which resulted in a bumped relay 174, device RB inside cubicle 4AD06. Relay 174, device RB tripped causing the lockout of the 4D 4kV bus. <br /><br /> All work in the area of the relay that actuated (relay 174, device RB) was stopped so the cause of the actuation could be evaluated. Work will not resume until the event has been reviewed with applicable contractor personnel emphasizing the sensitivity of the equipment in the areas being worked and also emphasizing attention to detail.
2511991004 | Turkey Point 4 | 07/20/1991 | 08/19/1991 | 9108230170 | <strong>Inadvertent Phase A Containment Isolation Due To Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>At 1407 on July 20, 1991, with both units shut down and defueled, a partial Engineered Safety Feature (ESF) actuation occurred. A Phase A Containment Isolation signal on Train A was generated when a fuse was installed in a Containment Isolation relay rack. Due to the configuration of the plant, only three automatic actions occurred. This event was caused by licensed operators using an inadequate procedure. Corrective actions include revision of the procedure, verification of safeguards relay positions, and awareness training of plant personnel.
2511991005 | Turkey Point 4, Turkey Point 3 | 08/09/1991 | 09/06/1991 | 9109160073 | <strong>Containment And Control Room Ventilation Isolation Following Inadvertent Opening Of Output Breaker To Inverter 4B Due To Personnel Error By Construction Worker</strong><br /><i>Abstract:&nbsp;</i>At 0947 on August 9, 1991, with both units defueled, the Unit 4 containment and control room ventilation systems isolated. After verifying that the cause of the event was not a valid signal, all systems were reset and returned to normal alignment. At 1030, FPL notified the NRC Operations Center of a non-emergency event (Engineered Safety Feature {ESF} actuation) requiring a four hour report in accordance with 10 CFR 50.72(b)(2)(ii). This event was caused by a momentary loss of power to Radiation monitors R-11 and R-12 (Containment Noble Gases and particulate monitors). The root cause of this event was non-cognitive personnel error. A non-licensed contract worker inadvertently opened the 4B inverter output breaker. To prevent occurrence of similar events, and a repeat of this type of event, all construction personnel working in the control room and the inverter rooms were immediately removed from their jobs for additional training. This training was performed to sensitize them to the potential consequences resulting from a lack of care while working in these vital areas.
2511991006 | Turkey Point 4 | 10/29/1991 | 06/17/1992 | 9206250017 | <strong>Autostart of Auxiliary Feedwater Pumps Following Low Suction Pressure Trip of Main Feedwater Pump Due to Malfunction of the Condensate Polishing Vessel Inlet Valve (CV-4-6351D) Close Limit Switch</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1991, at 2316 EST, with Unit 4 at approximately 22 percent power, and Unit 3 at 100 percent power, all three auxiliary feedwater (AFW) pumps autostarted following a trip of the only operating main feedwater (MFW) pump for Unit 4. Autostart of the AFW pumps is an engineered safety feature (ESF) actuation. A plant operator immediately started the 4B MFW pump. At 2323, the AFW pumps were secured and returned to standby mode. The NRC was notified of this event in accordance with 10 CFR 50.72 at 0020 EST, October 30, 1991. <br /><br /> The immediate cause of the AFW pumps autostart was the trip of the 4A MFW pump upon loss of suction pressure. The loss of suction pressure was caused by the diversion of condensate flow to the "D" polisher vessel, through the open inlet valve, and through the discharge valve to the backwash receiver. A misaligned Close limit switch on the "D" polisher vessel inlet valve, CV-4-6351D, provided a permissive to open the discharge valve to the backwash receiver. <br /><br /> The limit switch was adjusted, tested satisfactorily and returned to service. Operating procedure OP-7001.3, "Condensate Polishing System - Powdex Vessel Operation," has been revised to require a visual verification of the vessel inlet valve closure prior to initiation of backwash.
2511991007 | Turkey Point 4 | 12/10/1991 | 03/16/1992 | 9203240057 | <strong>Completion of Technical Specification Required Shutdown due to Failure of 4A Load Sequencer Auto Test Output Card</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1991, with Unit 4 at 100% power, during a routine system walkdown by the system engineer, the 4A sequencer was found in a condition where the automatic testing feature was not in service. Since the functionality of the sequencer could not be verified, the sequencer was declared inoperable at 1345 on that date. No Technical Specification specifically covers the load sequencer. However some safety related systems rely on the sequencer under various analyzed conditions of the plant. Technical Specifications that cover safety related systems that involve the sequencer have specific Action statements. The most conservative applicable Action statement required a reactor shut down to hot standby (Mode 3) within 6 hours. The plant was taken to Mode 3 at 1937 that same day. <br /><br /> An investigation revealed the root cause of the out-of-service auto test feature to be a failed sequencer auto test output card relay because of current inrush during each auto test sequence. The card has been replaced and the auto test feature disabled. <br /><br /> This item is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A).
2541991001 | Quad Cities 1 | 01/05/1991 | 02/04/1991 | 9102080122 | <strong>Partial Group II Actuation from Fuse Removal for OOS Work.</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1991, at 1820 hours, Unit One was in the SHUTDOWN mode at 0 percent of rated core thermal power. At that time several fuses FU! were pulled as part of an out of service (OOS). Pulling these fuses caused several primary containment isolation valves ISV! to close in addition to those addressed in the OOS, which constitutes a partial Group II Isolation. <br /><br /> After an evaluation to determine the cause of the actuation, the fuses were reinserted and the affected valves were reopened. Further corrective actions will include more detailed review of equipment out of service requests.<br /><br /> On January 10, 1991, at 0755 hours, Unit One was in the REFUEL mode. At that time, conduit containing wires to the Drywell Floor Drain Sump Discharge Isolation Valve limit switches was moved. The movement of a chaffed wire inside the conduit created an electrical short and caused a fuse to blow. This caused two of the same valves to close that were affected in the January 5 event, which constituted another partial Group II Isolation. The fuse was replaced and the affected valves were reopened. Further corrective actions will include replacement of the chaffed wire prior to restoring the system to service. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(iv).
2541991002 | Quad Cities 1 | 01/08/1991 | 02/06/1991 | 9112160061 | <strong>PARTIAL GROUP II ISOLATION DUE TO MAINTENANCE IMPROPERLY REMOVING TEMPORARY JUMPER MAINTAINING POWER</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. AT 1553 HOURS ON 1/8/91, UNIT ONE WAS IN A REFUEL OUTAGE AT 0% OF RATED CORE THERMAL POWER WITH THE MODE SWITCH IN REFUEL. AT THIS TIME, AN ELECTRICAL MAINTENANCE (EM) ELECTRICIAN WORKING ON CR120A RELAY (RLY) REPLACEMENTS MISSED A STEP IN AN ATTACHMENT TO THE STATION TRAVELER. IN DOING SO, HE ERRONEOUSLY REMOVED A JUMPER REQUIRED TO BYPASS THE RELAY HE WAS WORKING ON. THIS ACTION CAUSED THE 1-AO-4720 (DRYWELL (NH) PENUMATIC SUCTION VALVE (V) AND 1-AO-2001-15 (DRYWELL EQUIPMENT DRAIN VALVE) TO CLOSE. THIS CONSTITUTED A PARTIAL GROUP II ISOLATION EVENT AND AN UNPLANNED ENGINEERED SAFETY FEATURE (ESF) ACTUATION. THE ELECTRICIAN IMMEDIATELY NOTIFIED THE UNIT 1 NUCLEAR STATION OPERATOR (NSO), AND THEN REPLACED THE JUMPER AND LEFT THE WORK AREA. THE LACK OF PROCEDURAL ADHERENCE WAS DISCUSSED WITH THE RESPONSIBLE ELECTRICIAN FOLLOWING THE EVENT. THIS REPORT IS BEING SUBMITTED TO COMPLY WITH THE REQUIREMENTS OF 10CFR50.73(A)92)(IV).
2541991003 | Quad Cities 1 | 01/18/1991 | 02/11/1993 | 9302220345 | <strong>Specific Points In ACAD/CAM Lines Exceed USFAR Allowable Stresses</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1991, at 1532 hours, Unit One was in the SHUTDOWN mode at 0 percent of rated core thermal power. At this time, the Boiling Water Reactor Systems Design department notified the station that twelve specific points on four Containment Atmospheric Monitoring (CAM) [IP] and Atmospheric Containment Atmosphere Dilution (ACAD) [BB] lines exceeded UFSAR allowable stresses. This determination was made during analyses for Modification 4-1-88-103. Further analyses showed that all piping was operable. The cause of the event was preservice error involving the design and construction of the affected lines. No immediate corrective action is required since all lines are operable. This condition will be resolved when Modification M04-1-88-103 is implemented. Subsequent walkdowns and analysis on the Unit 2 ACAD/CAM piping revealed that support modifications would be required to bring this piping within UFSAR/FSAR design margins. Operability for the Unit 2 piping was verified in January, 1991. These necessary support modifications/additions for Unit 2 will be included as part of modification No. M04-2-88-103 (Partial 'B'). This report is being submitted in accordance with the requirements of the Code of Federal Regulations Title 10 Part 50.73 (a)(2)(ii)(B). DVR 368
2541991004 | Quad Cities 1 | 03/20/1991 | 04/18/1991 | 9104220316 | <strong>Inadvertent Actuation of RHR Pumps Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>At 1345 hours on March 20, 1991, Unit one was shutdown for a scheduled refueling outage.<br /><br /> During performance of testing on the 'B' Loop of the Residual Heat Removal (RHR) BO! System the 1C and 1D RHR pumps P! unexpectedly auto started. The Nuclear Station Operator (NSO) immediately stopped the pumps by placing the control switches in pull to lock. <br /><br /> Upon investigation it was determined that a step which required placing the control switches for the RHR 1C and 1D Pumps in pull to lock was misread. The NSO placed the RHR Service Water pump control switches in pull to lock. This resulted in the unexpected auto initiation. <br /><br /> Following correction to the system lineup the test was completed successfully. <br /><br /> This event will be required reading for licensed personnel. In addition the station is in the process of implementing a 'Self Check Program', which is designed to improve individual's awareness.
2541991005 | Quad Cities 1 | 01/31/1991 | 03/08/1991 | 9103260175 | <strong>1/2 B SBGT Unexpected Autostart During RPS B Power Swap Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1991, at 2013 hours, Unit One was in SHUTDOWN mode and Unit Two was in RUN mode at 94 percent of rated core thermal power. Operating personnel performed a Reactor Protection System (RPS) power supply transfer. As expected, it caused a 1/2 scram and 1/2 Group II and III isolations, which resulted in the 1/2 B Standby Gas Treatment System (SBGTS) autostart timer starting. <br /><br /> The NSO reset the 1/2 scram. 1/2 B SBGTS unexpectedly autostarted before the NSO reset the 1/2 group II and III isolations. The NSO secured 1/2 B SBGTS and operability tested 1/2 A SBGTS. <br /><br /> An Emergency Notification System (ENS) phone notification was completed at 0001 hours on February 1, 1991, under 10CFR50.72(b)(2)(ii). <br /><br /> Both units entered a 7 day LCO until Operating personnel verified the accuracy of the 1/2 B SBGTS 25 second autostart timer. Operating personnel determined that RPS and SBGTS functioned as designed. <br /><br /> The cause of the event was that the procedure failed to specify that the NSO must reset the 1/2 group II and III isolations within 25 seconds of loss of power to RPS in order to prevent autostart of 1/2 B SBGTS. A procedure correction was implemented.
2541991006 | Quad Cities 1 | 02/19/1991 | 03/19/1991 | 9103270067 | <strong>ESF Actuation Due To Unexpected Loss of B RPS Power Caused By MG Set Underfrequency Relay False Tripping During Repair Work</strong><br /><i>Abstract:&nbsp;</i>At 0805 hours on February 19, 1991, Unit One was in SHUTDOWN mode and Unit Two was in RUN mode at 99.8 percent of rated core thermal power. During repair work on the Unit One Channel B Reactor Protection System (RPS) Motor-Generator (MG) set underfrequency relay with the MG set in service, B RPS power was unexpectedly lost. This caused a 1/2 scram signal, and Primary Containment Isolation (PCI) 1/2 Group II and III isolation signals to be received in the control room. It also caused 1/2 B Standby Gas Treatment System (SBGTS) to autostart and Reactor Water Clean-up (RWCU) A & B pumps to trip as designed.<br /><br /> The apparent cause of the event is mechanical vibration. The investigation of the event showed that the relay contacts bounced when the relay paddle was inserted to reconnect the relay into its circuit.<br /><br /> Normal power was re-established and systems returned to normal within 42 minutes of loss of normal power to 1B RPS. <br /><br /> The MG set will be taken out of service for any future work on the relay.
2541991007 | Quad Cities 1 | 02/16/1991 | 03/18/1991 | 9103210225 | <strong>Electromatic Relief Valve 1-203-3B Lifted During Hydrostatic Testing Due To Foreign Material On Seat of Pilot Valve</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1991, at 1900 hours, Unit One was in the SHUTDOWN mode at 0 percent rated core thermal power for scheduled refuel outage Q1R11. The Operating Department was pressurizing the reactor in accordance with part one of the vessel hydrostatic test when the 1-203-3B Electromatic Relief Valve actuated, allowing a small discharge of water through the relief valve exhaust line. The actuation was determined to be an Emergency Safety Feature actuation at 2030 hours. NRC notification was completed at 0024 hours on February 17, 1991, to comply with 10CFR50.73(a)(2)(iv). <br /><br /> Visual inspection of the pilot valve revealed that a metal chip, lodged on the pilot valve seat, prevented the pilot valve from seating properly. The improper seating vented the main disc, causing the main disc to actuate. The Electromatic Relief Valve pilot valve assembly was replaced. Subsequently, the main valve disc was found to leak when vessel level was raised above the main steam lines. The Electromatic Relief Valve was removed, inspected, "pop" tested and reinstalled using a third rebuilt pilot valve.
2541991008 | Quad Cities 1, Quad Cities 2 | 03/22/1991 | 04/19/1991 | 9104240127 | <strong>Reactor Building Ventilation Isolation Due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1991 at 2035 hours, Unit one was in the SHUTDOWN mode at 0% of rated core thermal power for a refueling outage. Unit Two was in the RUN mode at 98% of rated core thermal power. At 2035 hours, lightning struck in a Transmission Substation (TSS) where line 0402 (Barstow) terminates. The lightning strike caused the Reactor Building VA! and Control Room Vents VI! to isolate, a channel 'B' 1/2 scram, and oil circuit breaker (OCB) 10-11 to trip. Other systems also had actuations caused by the lightning strike. At 2057 hours, the Reactor Building Vent Fans were returned to normal, the Control Room Vents were reset and Toxic Gas sample point 'A' was selected. Line 0402 (OCB 10-11) was closed back in at 2141 hours. The 4 hour Emergency Notification System (ENS) phone call was made at 2205 hours on March 22, 1991. <br /><br /> This event is being reported according to 10CFR50.73(a)(2)(iv).
2541991009 | Quad Cities 1 | 04/27/1991 | 05/28/1991 | 9106050051 | <strong>RCIC Inoperable From Not Meeting Tech. Spec. Requirements Due To Controller & Governor Problems.</strong><br /><i>Abstract:&nbsp;</i>At 0100 hours on April 26, 1991, Unit One Reactor was operating in the RUN mode at 22 percent rated core thermal power. At this time, the Unit One Reactor Core Isolation Cooling (RCIC) system was declared inoperable due to failure to meet pump requirements. <br /><br /> Troubleshooting of the system continued throughout this event due to repeated failures of the RCIC controller and governor. The system was successfully tested and declared operable on May 3, 1991 at 0345 hours. <br /><br /> The most significant cause of this event was due to an inadequate calibration procedure which resulted in unstable responses from the controller and governor. Also, because the system control parameters changed, the result affected the operation of the flow controller. <br /><br /> This event is being reported according to 10CFR50.73(a)(2)(v)(D) and 10CFR50.73(a)(2)(i)(A).
2541991010 | Quad Cities 1 | 06/14/1991 | 07/12/1991 | 9107230318 | <strong>ECCS Automatic isolation of Shutdown Cooling while performing instrument functional test due to procedural deficiencies.</strong><br /><i>Abstract:&nbsp;</i>At 0901 hours on June 14, 1991, during the performance of functional testing, the Residual Heat Removal (RHR) Shutdown Cooling (SDC) isolation valves 1-1001-47 & 50 isolated.<br /><br /> This event was due to procedural deficiencies. The procedure required that the RHR system not be in the SDC mode, but did not question the position of the isolation valves, or state that these valves would auto close.<br /><br /> The auto isolation function, although not anticipated in the procedure, was the correct design action of the system. <br /><br /> The calibration and functional test procedure will be revised to provide proper guidance to prevent reoccurrence of this event.
2541991011 | Quad Cities 1, Quad Cities 2 | 08/13/1991 | 09/12/1991 | 9109170233 | <strong>Failure of Secondary Containment Due to Air Inleakage</strong><br /><i>Abstract:&nbsp;</i>At 1321 hours on August 13, 1991 Unit One and Unit Two were in the RUN mode operating at 100 percent of rated core thermal power. A GSEP unusual event was entered due to the results obtained while performing Temporary Procedure 7008, QTS 160-5, Secondary Containment Capability Test. It was determined that the differential pressure required by Technical Specification 4.7.C.1.c. could not be maintained. <br /><br /> At 1330 hours Temporary Procedure 7007, SBGT Flow Variations for Secondary Containment Test was entered. The results indicated that an adequate differential pressure could be maintained in the Secondary Containment with a SBGTS flow rate of 4300 cfm. <br /><br /> At 1815 hours a Regional Waiver of Compliance was granted allowing the SBGTS flow rate to be increased to a maximum of 4400 cfm in order to maintain an adequate differential pressure in the Secondary Containment. <br /><br /> The cause of this event is attributed to excessive air inleakage to the Secondary Containment via the Reactor Building roof. Significant repairs were completed on the Reactor Building roof by August 16, 1991 and the waiver was then exited. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73(a)(2)(ii).
2541991012 | Quad Cities 1, Quad Cities 2 | 05/07/1991 | 06/06/1991 | 9106190281 | <strong>HPCI Inoperable Due To Failed Bushing In Stop Valve</strong><br /><i>Abstract:&nbsp;</i>At 1015 hours on May 7, 1991, Unit One was in the RUN mode at 93 percent rated core thermal power. Unit One High Pressure Co lant Injection (HPCI) system was declared inoperable to perform QCOS 2300-13, HPCI System Manual Initiation Test. During this test the HPCI turbine stop valve failed to stroke fully open.<br /><br /> Upon investigating the problem, it was identified that the long bushing in the stuffing box of the stop valve had slid down the valve stem and the bushing pin had sheared. Unit Two HPCI stop valve was checked to verify that the same problem did not exist. It was discovered that the long bushing was also partially out of the stuffing box with no bushing pin in the bushing. Unit Two HPCI was declared inoperable as of 1000 hours, May 8, 1991. <br /><br /> The failure of both HPCI systems was due to inadequate vendor instructions which resulted in the stuffing boxes not being peened. Unit One HPCI system was successfully repaired, tested, and declared operable on May 17, 1991, at 1745 hours. Unit Two HPCI was repaired and declared operable on May 19, 1991, at 1320 hours. <br /><br /> This event was being reported in accordance with 10CFR50.73(a)(2)(v)(D).
2541991014 | Quad Cities 1, Quad Cities 2 | 08/07/1991 | 09/03/1991 | 9109170291 | <strong>SBGT Heater Logic Circuitry Missing Due to an Inadequate Review of the Original SAR</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1991 at 1900 hours, a discrepancy was discovered at Quad-Cities between the Final Safety Analysis Report (FSAR) and the SBGT design specifications. The FSAR stated Quad-Cities had a heater logic circuitry but plant design showed otherwise. The Emergency Notification System (ENS) phone call was made at 2004 hours on February 8, 1991. <br /><br /> The cause of the discrepancy between the Quad Cities SBGT design and the FSAR is an inadequate review of the original Safety Analysis Report (SAR). <br /><br /> Corrective actions include revising procedures QCOA 7500-1 and QCOP 7500-1 to test for heater operability. Two modifications are also currently proposed to correct the problem. The 50.59 safety evaluation process is being looked into for possible changes. <br /><br /> This is a voluntary Licensee Event Report.
2541991015 | Quad Cities 1 | 08/26/1991 | 09/15/1991 | 9109200234 | <strong>Unit One Cable Tunnel Flow Switch OOS For Greater Than 14 Days.</strong><br /><i>Abstract:&nbsp;</i>At 0800 on August 26, 1991 Quad Cities Unit was in the RUN mode at 99 percent core thermal power. At this time the Unit One Cable Tunnel Sprinkler System Flow Switch exceeded the 14 day reporting criteria due to being out of service for system enhancements. Previously on August 12, 1991, the Unit One Cable Tunnel Sprinkler System Flow Switch was taken out of service for modification MO4-1-84-36H which transferred the electrical supervision of the flow switch from the security computer to the Pyrotronics XL3 fire protection system. The modification was a result of 10CFR50 appendix R commitments. The scope of work and the required testing for this modification was more than could be completed in 14 days. <br /><br /> Corrective action for this situation is to continue the modification and return the Unit One Cable Tunnel Sprinkler System to service. Compensatory measures are in effect as required. This report is submitted to comply with Technical Specifications 3.12.A.2 and 6.3.A.
2541991017 | Quad Cities 1, Quad Cities 2 | 09/04/1991 | 10/03/1991 | 9110100242 | <strong>"B" Train of CR HVAC Emergency Air Filtration Unit Unable to Attain Proper Delta T and Proper Delta P Across Filter Train Due to Equipment Failure and Inappropriate Heater Performance Criteria.</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1991 at 1115 hours, Unit One and Unit Two were in the RUN mode at 95 and 89 percent of rated core thermal power, respectively. At this time the Control Room VI! (CR) "B" Train Air Filtration Unit (AFU) was declared inoperable due to the failure of the heater (EHTR) to attain a 15 degree differential temperature (dT) and a differential pressure (dP) across the filter train that was not less than 6 inches of water as required by Technical Specification 4.8.H.2.b. An Emergency Notification System (ENS) phone call was completed at 1403 hours per 10CFR50.72(b)(2)(iii)(D).<br /><br /> The apparent causes of this event were a marginally sized heater for the dT needed, and a broken dP indicator PDI! DPIS 1/2-5741-311, and inadequate testing methods for the charcoal adsorber. <br /><br /> Corrective actions include replacing the dP indicator, heater and charcoal adsorber trays. Further corrective actions are a permanent Tech Spec change, and revising procedures.<br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(v).
2541991018 | Quad Cities 1 | 09/14/1991 | 10/11/1991 | 9110170061 | <strong>RCIC Made Inoperable To Repair 125 VDC Ground In EG-M Control Box</strong><br /><i>Abstract:&nbsp;</i>At 0135 hours on September 14, 1991 Unit One was operating in The RUN mode at 98 percent rated core thermal power. At this time, a 125 VDC ground had been isolated and RCIC was declared inoperable in order to repair the ground . Also, RCIC System Outage Report was initiated. The magnitude of the ground exceeded its limit set in QOP 6900-7, thus entering the battery system into a 14-day Administrative LCO at 2100 hours on September 13, 1991. <br /><br /> IM located the ground in the RCIC EG-M control box. The EG-M was replaced and at 1915 hours on September 14, 1991, the SE declared RCIC operable and terminated the outage report.<br /><br /> At 0139 hours on September 14, 1991 the NRC was notified of the event via the Emergency Notification System (ENS) to comply with the requirements of 10CFR50.72(b)(2)(iii)(D). <br /><br /> The cause of the ground was because of a failed EG-M control box.
2541991019 | Quad Cities 1, Quad Cities 2 | 10/05/1991 | 10/28/1991 | 9111120179 | <strong>"B" Train CR HVAC Emergency Filtration Unit Unable To Attain Proper dT Across Heater And Proper dP Across Filter Train Due To Improper Equipment Configuration And Partially Fouled HEPA Filters.</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1991 at 1255 hours, Unit One was in the RUN mode at 80 percent of rated core thermal power. Unit Two was in the SHUTDOWN mode. At this time the Control Room VI! (CR) "B" Train Air Filtration Unit (AFU) was declared inoperable. During surveillance testing, the heater EHTR! failed to attain a 15 degree Fahrenheit differential temperature (dT). Also, the differential pressure (dP) across the filter train exceeded 6 inches of water. An Emergency Notification System (ENS) phone call was completed at 1358 hours per 10CFR50.72(b)(2)(iii)(D). <br /><br /> The apparent causes of this event were a design deficiency involving the thermowells of the Resistance Temperature Devices (RTD) used to measure dT across the heater, and HEPA filters FLT! that were partially fouled due to normal usage. <br /><br /> Corrective actions included filling the thermowells with thermally conductive oil and replacing the HEPA filters. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(v).
2541991020 | Quad Cities 1 | 09/19/1991 | 11/06/1991 | 9111140040 | <strong>Missed Off Gas Recombiner Technical Specification Surveillance (4.8.A.5) Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1991, Unit One was in the RUN mode at 100% of rated core thermal power. The shift three Nuclear Station Operator (NSO) noticed that the recombiner temperatures had not been verified to be in the allowable band as required by Technical Specification 4.8.A.5 since shift three the previous day. <br /><br /> The recombiner temperature recorder was not working properly during shifts one and two on September 19, 1991. The shift one NSO tried to interpolate the temperature values, and notified the Shift Engineer of the malfunctioning recorder. The shift two NSO recognized that the recorder was not working, but took no corrective actions. The temperature recorder appears to have been in standby mode during this event. The recorder was repaired and disciplinary action was given to the shift two NSO for failing to notify the Shift Engineer of the problem. <br /><br /> This report is being written per 10CFR50.73(a)(2)(i)(b).
2541991021 | Quad Cities 1 | 10/25/1991 | 11/21/1991 | 9112020349 | <strong>RCIC Declared Inoperable Due To High Pump Flow In IST Required Action Range</strong><br /><i>Abstract:&nbsp;</i>At 1300 hours on October 25, 1991, Unit One was in the RUN mode at 100 percent rated core thermal power. At this time, the Unit One NSO was performing the IST portion of QCOS 1300-5, RCIC Quarterly Pump Operability Test. The RCIC pump flow reading indicated 540 gpm which moved the pump flow into the IST required action range. <br /><br /> The SE declared the system inoperable as of 1300 hours, and initiated QCOS 1300-2, RCIC System Outage Report. <br /><br /> The NRC was notified of the event via the Emergency Notification System (ENS) at 1322 hours to comply with 10CFR50.72(b)(2)(iii)(D). <br /><br /> At 1840 hours, the IST portion of QCOS 1300-5 was performed again using a hand held strobe tachometer. The IST test was successful in achieving the correct pump flow. The SE declared RCIC operable and terminated the outage report. <br /><br /> The cause of the high pump flow reading was due to instrument drift. <br /><br /> IM will replace both units RCIC control room tachometer indicators under NWR's Q96146 and Q96539.
2541991022 | Quad Cities 1, Quad Cities 2 | 11/04/1991 | 09/16/1992 | 9209250006 | <strong>Failure Of Control Room HVAC To Reach Proper DT Across The Heater.</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991 at 1940 hours Unit One was in the RUN mode at 100 percent of rated core thermal power. Unit Two was also in the RUN mode at 79 percent of rated core thermal power. At this time, the Control Room VI! (CR) "B" Train Air Filtration Unit (AFU) was declared inoperable. During the surveillance testing, the heater EHTR! failed to attain a 15 degree Fahrenheit differential temperature (dT). An Emergency Notification System (ENS) phone call was completed at 2104 hours per 10CFR50.72(b)(2)(iii)(D). <br /><br /> Technical Specification Amendments 133 and 128 were approved and implemented on November 18, 1991 following a 30 day comment period. <br /><br /> The apparent cause of the failure to reach the proper differential temperature was an inaccurate flow measuring device. <br /><br /> Corrective actions included the new Technical Specification heater dT requirements, revising the monthly surveillance to incorporate the new requirements, and performing the monthly operability surveillance. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(v).
2541991023 | Quad Cities 1, Quad Cities 2 | 11/26/1991 | 12/20/1991 | 9201030148 | <strong>Control Room HVAC Isolation Due to a Dried Out Chlorine Analyzer Probe Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1991, Unit One was in the RUN mode at 100 percent of rated core thermal power. Unit Two was also in the RUN mode at 74 percent of rated core thermal power. At 1330 hours, the Control Room (CR) HVAC Toxic Gas Analyzer annunciated the "Control Room Standby HVAC System Major Trouble" alarm in the CR and caused the CR Vents to isolate. The Instrument Maintenance Department was getting ready to perform their functional test when the event occurred. An Emergency Notification System (ENS) phone call was completed at 1454 hours per 10CFR50.72(b)(2)(ii). <br /><br /> The apparent cause of the event is unknown. The potential cause of the event is allowing the probe to dry out by not performing the preventative maintenance.<br /><br /> Corrective actions include declaring the Toxic Gas Analyzer inoperable, the Instrument Maintenance Department (IMD) speaking with the vendor, and ordering new probes. <br /><br /> Future corrective actions will include revising procedures to include vendor information on the care and operation of the probes in the storeroom. A new procedure will be written on how to revive a probe once it has been dried out. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(iv).
2541991024 | Quad Cities 1, Quad Cities 2 | 12/03/1991 | 12/30/1991 | 9201070362 | <strong>Failure of CO2 Extinguishing Systems Due to Inadequate Flow Rates</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1991 at 0225 hours, Unit One was in the RUN mode at 98 percent of rated core thermal power. While performing Special Test 1-170, the CO2 flooding system KQ! for the Unit One Diesel Generator EK! (DG) room did not meet the specified concentration requirement, and the system was declared inoperable. On December 3, 1991 at 1400 hours, the Unit 1/2 DG room CO2 system was declared inoperable. Based on flow rate calculations, it was determined that the required discharge time for the CO2 systems for the Unit One and Unit 1/2 DG rooms exceeded the required time of one minute. On December 3, at 1429 hours an Emergency Notification System call was made in accordance with 10CFR50.72(b)(1)(ii)(B). <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(II)(B) and Technical Specification 3.12/4.12.D.5. The apparent cause of the event was improper system installation. <br /><br /> The immediate corrective action included establishing backup fire suppression and fire watches for the affected areas, The discharge nozzles will be replaced with larger nozzles, and the systems will be further tested.
2541991025 | Quad Cities 1 | 12/11/1991 | 01/06/1992 | 9201210158 | <strong>Reactor Scram Due to Turbine Trip From Reactor High Level Due to 1A Feed Reg V1v Failing Full Open</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1991, Quad Cities Unit One was in the RUN mode at 78 percent of rated core thermal power. At 0425 hours, a reactor scram occurred due to turbine stop valve closure as a result of a high reactor water level turbine trip. The high reactor water level was caused by a feedwater regulating valve failing full open. All safety feature actuations occurred as designed. Emergency Notification System (ENS) notification was completed at 0632 hours on December 11, 1991, to comply with the requirements of 10CFR50.72(b)(2)(ii).<br /><br /> An investigation revealed the cause of the event to be due to misalignment of the 1A Feedwater Regulating Valve causing the valve to bind. The manual operator assembly broke in an attempt to close the valve manually which allowed the valve to open fully due to spring force. The failed open feedwater regulating valve caused the high reactor water level and subsequent turbine trip.
2541991026 | Quad Cities 1, Quad Cities 2 | 12/10/1991 | 01/08/1992 | 9201150175 | <strong>Breach of Secondary Containment - 1A and 2A Drywell to Torus Purge Fan Dampers</strong><br /><i>Abstract:&nbsp;</i>Beginning on December 9 and continuing into December 10, 1991, Operations staff placed the 1A and 2A Drywell/Torus Purge Fans Out-of-Service for Mechanical Maintenance to seal access door leaks and replace filters. Due to a misconception by the Equipment Attendants, and the lack of labels on the damper operators of the purge system, the dampers were wired OPEN instead of wired CLOSED as the Out-of-Service request required. <br /><br /> When Mechanical Maintenance pulled the access cover from the 1A purge fan, a breach in Secondary Containment was created via the Reactor Building Ventilation Exhaust system through the wired open discharge dampers and out the open access cover. Deinerting and reinerting of the Unit 2 Drywell was underway simultaneous to this maintenance work. <br /><br /> Soon after Mechanical Maintenance pulled the access cover to the 2A purge fan the Control Room received a high differential pressure alarm on the purge filters. An Equipment Attendant sent to investigate recognized that the dampers were OOS in the wrong position and initiated the actions which placed the dampers in the correct, CLOSED, position. This action restored Secondary Containment. <br /><br /> Corrective actions include labelling purge fan damper positions, revising station procedures to more clearly define the verification process for dampers, and investigate the installation of damper inspection doors.
2541991027 | Quad Cities 1 | 12/16/1991 | 11/27/1993 | 9312170045 | <strong>U-1 Shutdown From Water Leaking Onto Bus 14-1</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1991, Unit one was in the RUN mode at 100 percent of rated core thermal power. A large leak was discovered to be coming from an open drain valve in the U1 Reactor Building ventilation [VA] heating steam system. The water drained through a floor pipe penetration onto Emergency Bus [BU] 14-1 switchgear [SWGR]. Several alarms were received in the control room, including '4kV Overcurrent,' '125 V Battery Ground,' and 'Diesel Gen 1 Relay Trip.' The U1 Diesel Generator (DG) [DG] was then declared inoperable. The leak was isolated, Bus 14-1 was covered with plastic, and a load drop was started at 1430 hours for removal of Bus 14-1 from service. Bus 14-1 was removed from service at 1450 hours. The station entered Technical Specifications (TS) LCO 3.0.A due to one whole division of Emergency Core Cooling System (ECCS) pumps and the U1 DG being inoperable. A Generating Station Emergency Plan (GSEP) Unusual Event was declared due to TS LCO 3.0.A. Unit One was manually scrammed at 0113 hours on December 17, 1991. Unit One was in COLD SHUTDOWN at 0622 hours. TS LCO 3.0.A and the GSEP Unusual Event were then terminated. \
2541991028 | Quad Cities 1 | 12/20/1991 | 01/17/1992 | 9201310215 | <strong>Loss of Power To 1A RPS Bus Caused By EPA 1A-1 Tripping On Undervoltage Due To Low M-G Set Output Voltage</strong><br /><i>Abstract:&nbsp;</i>At 1720 hours on December 20, 1991, UNIT ONE was in the RUN mode at 100% of rated core thermal power. Reactor Protection System (RPS) Bus 1A unexpectedly lost power. This caused a 1/2 scram and Primary Containment Isolation (PCI) Groups I, II, and III isolation signals to be received in the Control Room. It also caused Reactor Water Clean-up (RWCU)pumps to trip, and Control Room Vents and Reactor Building Vents to isolate as designed. <br /><br /> The loss of power was due to an undervoltage trip on an Electrical Protection Assembly for the RPS 1A Motor-Generator (M-G) Set. At 1735 hours, RPS Bus 1A was energized from its reserve feed. The 1/2 scram and PCI Group Isolations were reset, and RWCU, Control Room Vents, and Reactor Building Vents were returned to service. <br /><br /> The apparent cause of the event is low generator output voltage. The exact cause for the drop in voltage is unknown. No apparent electrical load failure was discovered during the investigation. The possible causes are believed to be normal wear or corrosion of the voltage regulator rheostat at the point of previous adjustment, or a spurious voltage regulator failure. After adjusting the rheostat for a higher generator output voltage, the M-G Set functioned properly and was returned to service. <br /><br /> The Station is investigating replacement of the voltage regulator and rheostat.
2541991029 | Quad Cities 1 | 04/24/1991 | 03/04/1992 | 9203120124 | <strong>U-1 RCIC MOV 1-1301-49 Valve Failed to Open Due to Unknown Causes</strong><br /><i>Abstract:&nbsp;</i>At 1321 hours on April 24, 1991, Unit One was in STARTUP mode at 1 percent rated core thermal power. The Reactor Core Isolation Cooling (RCIC) system was inoperable in preparation for RCIC turbine overspeed testing. During QCOS 1300-3 "Monthly RCIC Motor Operated Valve Test", the RCIC 1301-49 pump discharge valve failed to open. <br /><br /> The cause of this event is unknown. Two contacts in the limit switch assembly were cleaned and the valve was successfully stroked. <br /><br /> On January 24, 1992 the Station received a severity Level IV violation in Inspection Report 254/91024; 265/91020 for failing to report this event as an LER in accordance with the requirements for 10CFR 50.73(a)(2)(v)(D). This report is being submitted to fulfill this requirement.
2551991001 | Palisades | 11/28/1990 | 01/02/1991 | 9101100086 | <strong>Plant Operation In Literal Non-Compliance With Technical Specifications Table 3.17.1</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1990, the plant was in cold shutdown and the core was totally defueled for the replacement of the steam generators. During review of a revision to System Operating Procedure (SOP) No. 36, "Reactor Protection System and Anticipated Transient without Scram System," it was identified that the bypass of the log range nuclear instrumentation reactor trip and the loss of load reactor trip was set at 16.5% of rated power. This is consistent with Technical Specifications Table 3.17.1, item 3, which indicates the log range nuclear instrumentation trip is automatically bypassed above 15% power, but inconsistent with item 7 in the table which indicates that the loss of load trip is automatically bypassed below 15% power. No immediate actions were required as the plant was in cold shutdown. As described in the FSAR, the high rate of change reactor trip, which is associated with the log range nuclear instrumentation, and loss of load reactor trip, are anticipatory trips which are not required to protect the reactor.<br /><br /> A setpoint change will be completed prior to startup to change the 16.5% bypass value to 15% consistent with the present Technical Specifications.<br /><br /> This event is attributable to procedural weakness and inadequate reviews in the preparation and implementation of Technical Specifications changes.
2551991002 | Palisades | 12/28/1990 | 01/28/1991 | 9102040119 | <strong>Non-Qualified Cable Splices Inside Containment</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1990, the plant was in cold shutdown and the core was totally defueled for the replacement of the steam generators. While working on a DC ground in the reactor head vent valve circuitry, it appeared that a Raychem cable splice on a containment penetration connector inside the containment for reactor head vent valve PRV-1067 was improperly installed. Further investigation revealed that the cable. splice inner sleeve was too small and the outer sleeve was shrunk directly onto braided cable jacket. No immediate actions were required as the plant was shutdown for refueling and steam generator replacement. A plant corrective action document was initiated to assure that the problem was resolved prior to startup from the refueling outage. <br /><br /> Further investigation of all the (127 total) containment penetration connector pigtails on penetrations inside containment, revealed eight additional containment penetration connector pigtails with out of specification splices. This resulted in equipment being in a condition outside its design basis. <br /><br /> The cause of the event is attributable to inadequate modification or design control during the time the equipment was installed or modified. <br /><br /> All identified out of specification splices will be reworked prior to start-up from the present refueling outage.
2551991003 | Palisades | 05/20/1990 | 01/28/1991 | 9102050262 | <strong>Failure To Test Diesel Auto Start Circuits</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1990, during the review of testing requirements, it was determined that, on May 20, 1990 and again on June 17, 1990, the emergency diesel generators (K6A and K6B) auto start initiating circuits had not been tested prior to start-up as required by Technical Specifications. At the time of discovery the plant was in cold shutdown for refueling and steam generator replacement. <br /><br /> This event was caused by a procedural inadequacy in Operations Check List (CL) 36. The procedural inadequacy resulted when the responsible engineer and procedure reviewers failed to identify that a recent facility change which caused a revision to CL 36 deleted a required TS test. No provision was made to ensure that this required test was incorporated into other procedures.<br /><br /> Corrective action for this event includes the development of technical specifications test procedures to test the auto start circuit of the diesel generators. Additionally, a review of technical specification surveillance requirements will be conducted to identify the testing requirements which are not performed by the technical specification surveillance procedures. The test requirements identified in this review will be incorporated into TS surveillance test procedures or flagged in the non-surveillance type procedures to reduce the possibility of inadvertent deletion. <br /><br /> This event did not involve the failure of any systems or components.
2551991004 | Palisades | 01/05/1991 | 02/06/1991 | 9102130351 | <strong>Containment Emergency Airlock Leakage Results In Containment Cumulative Local Leak Rate Excess Of Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1991, at 2100 hours, the plant was in cold shutdown and the reactor was totally defueled for the replacement of the steam generators. Containment local leak rate testing was being performed on the containment emergency airlock (MZ-50). During this testing, plant operators noticed that the inner door viewing port gasket was a source of leakage. The calculated airlock leak rate was determined to be 42,905 cubic centimeters per minute (cc/min). This resulted in an as found cumulative local leak rate testing total of 98,994 cc/min which exceeded the Technical Specifications limit of 65,200 cc/min. The gasket was later found to be degraded and was replaced. The containment emergency airlock was subsequently tested satisfactorily. This occurrence is attributable to inadequate preventative maintenance procedures for inspection and replacement of the escape lock door viewing port gasket, and is reportable as a deviation from the plant's Technical Specifications. Preventative maintenance procedures to replace viewing port gaskets on both the emergency and personnel airlocks will be developed by July 1, 1991.
2551991005 | Palisades | 01/25/1991 | 02/25/1991 | 9103040008 | <strong>Inadvertant Left Channel Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1991, at 0115 hours, the plant was in cold shutdown and the core was being refueled. Instrument and control technicians were preparing for removal of the containment radiation detector RE-1805 in preparation for the containment structural integrity and integrated leak rate testing. In accordance with the work order instructions the technicians removed the power from radiation monitor RIA-1805. As this was done the power for refueling radiation monitor RIA-2316 was also de-energized which caused the inadvertent left channel containment isolation. The control room operators verified that the technicians had caused the actuation, verified proper equipment response, re-energized RIA-1805 and RIA-2316, and reset the left channel containment isolation signal. A corrective action document was initiated to determine root cause, corrective actions and assure that this condition was resolved so that the work could be completed. The containment isolation is considered an engineering safety feature actuation. Plant electrical schematics will be changed to more clearly show that both radiation monitors are powered from the same power scheme.
2551991006 | Palisades | 02/20/1991 | 12/20/1991 | 9201030206 | <strong>Failure To Compensate For Open Fire Barrier Penetration Seal, Revision 1</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1991, at approximately 1600 hours, a passive fire barrier penetration seal between the turbine building corridor and the 1C switchgear room was opened to permit the passage of temporary cables used for the performance of the refueling frequency surveillance procedure RT-8C. At the time, the plant was in cold shutdown. Contrary to plant Fire Protection Implementing Procedure FPIP-4, no work order was issued to open the penetration and no compensatory action in the form of an hourly fire tour was initiated. This situation resulted from inadequate communication between the responsible engineer and the shift supervisor, incomplete guidance in Administrative Procedure 4.02, "Control of Equipment Status," which does not address fire barrier penetrations, and the lack of adequate interface information between Administrative Procedure 4.02 and the Fire Protection Implementing Procedure FPIP-4. <br /><br /> Revisions will be made to the Plant Administrative Procedure 4.02, Fire Implementing Procedure FPIP-4 and surveillance procedure RT-8C to clarify whether a work order is required and to improve the interface between Administrative Procedure 4.02 and Fire Protection Implementing Procedure FPIP-4. Additionally, this event will be reviewed with electrical system engineers.
2551991007 | Palisades | 02/25/1991 | 03/27/1991 | 9104080007 | <strong>Unplanned Reactor Trip Caused By Inadequate Surveillances Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1991, at 1058 hours, the plant was in cold shutdown. In preparation for leaving cold shutdown Technical Specification surveillance testing was being performed. Technical Specification Surveillance Procedure QO-23, "Auxiliary Hot Shutdown Panel Instrumentation Checks," which demonstrates the operability of the alternate hot shutdown panel (AHSP) monitoring instrumentation by comparison to corresponding control room indications, was in progress. <br /><br /> In accordance with the procedure, operators pushed the 'cal' button on the AHSP panel source/wide range drawer which causes a test signal to be generated to both the control room and AHSP nuclear instrumentation drawers. The test signal causes an upscale wide range reactor flux signal on all associated indications. Since the test signal was above the 10**-4% power level the zero power mode (ZPM) bypass is automatically disabled. The reactor tripped on low primary coolant system (PCS) flow, as this trip feature had not been by-passed by the procedure controls. The reactor trip is considered an engineered safety feature actuation.<br /><br /> The operators verified that the reactor protective system (RPS) responded properly. The reactor tripped due to a low PCS flow since only two primary coolant pumps were operating. A corrective action document was initiated to determine the root cause and corrective actions. The occurrence is attributable to an inadequate surveillance procedure. The appropriate procedures will be revised and operators trained on this occurrence.
2551991008 | Palisades | 04/09/1991 | 05/09/1991 | 9105170137 | <strong>Qualified Core Exit Thermocouple Inoperable Greater Than Seven Days</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1991, at 0900 hours, with the plant operating at 100% power, qualified core exit thermocouple (CET) No. 16, was declared inoperable due to inaccurate readings. The method of discovery was the performance of technical specifications surveillance test D/WO-1, "Qualified Core Exit Thermocouple Calibration Check". A work order was written to troubleshoot and repair the CET and the CET was listed on the limiting condition of operation (LCO) board. The work order for the CET was released for repair on April 11, 1991, at 1256 hours, with repairs being initiated at that time. CET No. 16 was repaired by the Instrument & Control Department (I&C) with the work being completed on April 12, 1991. The work order remained in the I&C Department undergoing administrative review until April 17, 1991 at which time the work order was returned to the Control Room. After undergoing Operations Department review, CET No. 16 was declared operable on April 17, 1991, at 1200 hours. This was approximately 1 day beyond the 7 day proposed LCO action time limit. <br /><br /> The cause of the event was a combination of personnel error and ineffective communication. Various communication opportunities were not fully effective and the responsible individuals were not alerted of the approaching deadline for the LCO. <br /><br /> A corrective action document (Event Report PAL-91-011) was initiated to document the event and to ensure that the 30 day special report required by the proposed technical specifications was submitted.
2551991009 | Palisades | 05/19/1991 | 06/14/1991 | 9106240324 | <strong>Qualified Core Exit Thermocouple Inoperable and Cannot Be Repaired While the Plant is at Power</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1991, at 1903 hours, with the plant operating at 100% power, qualified core exit thermocouple (CET) No. 16, was declared inoperable due to inaccurate readings. The method of discovery was erratic readings on the primary information processor (PIP). A work order was written to troubleshoot and repair CET 16 and the CET was listed on the limiting condition of operation (LCO) board. The work order for CET 16 was released for repair on May 20, 1991, at 1419 hours, with repairs being initiated at that time. Repairs were attempted by the Instrument & Control Department (I&C), however, none of the repair techniques that had been successful in the past were successful on this occasion. On May 21, 1991 it was determined that CET 16 could not be repaired while the plant was at power, thus CET 16 was declared inoperable. <br /><br /> The cause of the event was a failure of the instrument.<br /><br /> A corrective action document was initiated to document the event and to ensure that the 30 day special report required by the proposed technical specifications via administrative procedures was submitted.
2551991010 | Palisades | 02/24/1991 | 06/14/1991 | 9106240346 | <strong>Emergency Diesel Generator Unanticipated Start During The Performance Of Special Test T-297, "D/G 1-1 Load Reject"</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1991, at 0618 hours, with the Plant in cold shutdown, an unanticipated start of the 1-2 diesel generator occurred during the performance of Special Test T-297, "D/G 1-1 Load Reject". This test was being performed as a result of commitments made to Nuclear Mutual Limited (NML) regarding compliance with IEEE 387, Regulatory Guide 1.108 and Regulatory Guide 1.9 for diesel generator load rejection. The cause of the event was an inadequate procedure. No precautionary statement existed in the procedure to alert the operator that a diesel generator start may occur. The following corrective actions were assigned as a result of the analysis of this event: <br /><br /> 1. Review electrical special test procedures and surveillance procedures to identify voltage transients which will cause diesel generator starts. Revise procedures as necessary. <br /> 2. Replace relay 63x/LS-0204 with a relay having a time delay such that it will not actuate during a transfer of power sources to Y-01. <br /> 3. Replace PCX-0218B. <br /> 4. Review application of normally energized HFA relays on Y-01 with respect to Y-01 power transfer. <br /><br /> This event did not involve the failure of any systems or components.
2551991011 | Palisades | 06/27/1991 | 07/29/1991 | 9108050222 | <strong>Seismic Qualification Of Qualified Incore Detector Electrical Connectors</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1991, at 0900 hours, with the plant operating at 100% power, it was determined that the Core Exit Thermocouple (Incore Detectors) electrical connectors were not fastened to their supports as intended in the seismic analysis for the incore detectors. An interim operability justification for continued operation has determined the seismic response to be negligible and the present configuration acceptable. <br /><br /> The cause of the event was an inadequate procedure. <br /><br /> Corrective action for this event includes providing new incore instrument flange lifting posts to replace those which have been broken; revising technical specification surveillance procedure to incorporate the requirements to attach the incore instrument cable to the support plate following re-connection of the electrical connectors; and revising permanent maintenance procedure to incorporate the requirement to attach the reactor vessel level and core exit thermocouple instruments to the support plate following the re-connection of the electrical connectors. <br /><br /> This event involved the failure of the attendant seismic support for the incore electrical cable.
2551991012 | Palisades | 07/03/1991 | 08/02/1991 | 9108070063 | <strong>Reactor Trip When 'A' Channel Reactor Protective System TM/LP Bistable Was Inserted</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1991, at 1435 hours, with the plant operating at 100% power, the reactor tripped. Troubleshooting and repair of the channel "A" Thermal Margin/Low Pressure (TM/LP) protection circuit was in progress at the time of the trip. Investigation into the cause of the trip indicated that a reactor trip signal was created when, during the performance of troubleshooting and repair of the TM/LP channel "A" circuit, a trip coil to test coil short, which existed in the circuit, activated the reactor protective system (RPS) trip relays for the A-D logic matrix. <br /><br /> The cause of the event was the failure of electrical components in the reactor protective system circuitry. <br /><br /> Corrective action for this event includes evaluating periodic monitoring the RPS test circuitry for indications of failed bistable trip relays, evaluating isolating signal ground from earth ground at the Thermal Margin Monitor (TMM) and Auxiliary Feedwater Actuation System (AFAS), evaluating isolating Feed Only Good Generator (FOGG) system from RPS, evaluating a PM prog am to perform a coil to coil resistance test on all trip relays in the RPS and reviewing a proposed modification to the RPS circuitry to determine if a similar failure mechanism will exist. <br /><br /> The event involved the failure of electrical components in the reactor protective system circuitry.
2551991013 | Palisades | 05/07/1991 | 08/02/1991 | 9108070061 | <strong>Operation of Plant with leak in Containment Spray Line Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1990 with the plant shutdown, a leak was identified in one of the containment spray headers at the upper containment elevation. At the time a work order was initiated and a determination made that the weld was structurally adequate to maintain the piping system integrity, and that the leak would not affect the operation of the system. The plant was shortly thereafter returned to power production. During the following September 1990 refueling outage, it was determined that the leakage condition was not in conformance with the ASME code requirements and that the leak should have been repaired at the time of discovery. An NRC reportability determination was lso made at this time and based on the judgments that the pipe would have performed it's design basis function, it was determined to be in an operable condition during the plants power operation. Therefore, the event was not reported to the NRC. Later reviews determined this decision to be in error and that the plant had been in an unanalyzed condition, outside of the design basis of the plant. <br /><br /> The cause of the event was due to personnel error. Corrective actions are to review this occurrence with plant management, engineering, maintenance and operations planners, shift supervisors and shift engineers so that a better understanding of this issue is acknowledged.
2551991014 | Palisades | 07/09/1991 | 04/24/1992 | 9205010259 | <strong>Safety Related Circuits Routed With Opposite Channel Circuits - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>Through the on-going Palisades Configuration Control Project a number of apparent discrepancies in circuit routing have been identified. Previous NRC correspondence dated September 4, 1990 and March 12, 1991 provided details of the "Circuit and Raceway Schedule Enhancement Project" and status of the projects activities. The electrical circuit channelization and separation deficiencies which have been evaluated at this time, while not conforming to FSAR criteria in all respects, have resulted in identification of very few conditions involving a loss of electrical or protection system independence; or noncompliance with 10CFR50, Appendix R requirements. In those few cases compensatory measures and corrective actions have been taken as stipulated in plant Technical Specifications and/or the condition was promptly corrected. <br /><br /> The physical separation and channelization deficiencies that have been identified appear to result from two separate failures: 1) A non-uniform interpretation of design criteria for channelizing and routing electrical circuits, and 2) the unavailability of a single, complete and reliable source of design documentation for electrical circuit routing and channelization.<br /><br /> At the time of the discovery of the latest discrepancy (engineered safeguards room cooler circuitry channelization), the plant was shutdown for a refueling outage.
2551991015 | Palisades | 07/12/1991 | 08/12/1991 | 9108220112 | <strong>Plant Trip Following Main Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1991, at 1838 hours, with the plant operating at 100% power, the plant tripped. At the time of the trip, troubleshooting of an indication of low bearing oil pressure on the K-7A main feedwater pump turbine was in progress. Based on alternate indications, the System Engineer felt that the indication was incorrect. He tapped the pressure gauge with his hard hat which caused the main feedwater pump turbine to trip. The reactor tripped 54 seconds later on low steam generator level. <br /><br /> The cause of the event was a combination of personnel error and equipment failure. <br /><br /> Corrective action from this event includes electrical check out of all feedwater pump turbine instruments and controls, replacement of selected feedwater pump turbine trip circuit components, repair of control cabinet oil and steam leaks and briefing instrument and control (I&C) technicians on proper equipment control.
2551991016 | Palisades | 05/23/1991 | 08/22/1991 | 9109040188 | <strong>Inoperability of Containment Spray Pump</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1991, with the Plant operating at 100% power, containment spray pump, P-54C, failed to start using the local control switch at the station breaker. The last documented run of containment spray pump P-54C was on February 11, 1991. At the time of occurrence the pump was being tested using a technical specifications surveillance procedure. The auxiliary operator (AO) conducting the test notified the control room of the failed first attempt and was instructed to perform a second closure attempt. The pump failed to start on the second closure attempt. The AO was then instructed by the control room to check both sets of fuses. The AO pulled both the closing coil and the control fuse holders. The AO visually inspected the holders and the fuses and found the them to be in good condition. The AO then performed a continuity check of the fuses, found them to be good, re-installed the fuses and the fuse holder and attempted another pump start. The pump started on the third attempt. <br /><br /> The most probable cause of the breaker's failure to close on the first and second attempts was the failure of the closing coil fuses to complete the closing circuit.<br /><br /> Corrective action associated with this event include ensuring electrical maintenance workers are aware of breaker troubleshooting methods, providing local and remote indication of closing coil power for solenoid operated breakers on selected buses, providing training to the operators on this event, incorporating information on this event into operator initial training and revising Administrative Procedure 4.02 concerning electrical breaker testing.
2551991017 | Palisades | 08/05/1991 | 09/05/1991 | 9109130154 | <strong>Potential Inter-System LOCA Within The Primary Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>At 1000 hours on August 5, 1991, the plant was operating at approximately 100% power. An evaluation by the Reactor and Safety Analysis engineering group determined that a postulated break in the primary coolant pump (PCP) integral heat exchanger could result in a primary coolant system leak outside the containment building. This determination was based on Palisades specific calculations developed as result of the review of Information Notice No. 89-54, "Potential Overpressurization of the Component Cooling Water System." A preliminary evaluation of the radiological consequences resulting from an inter-system LOCA within the primary coolant pump indicates that, if the leak was not isolated, the site boundary thyroid dose limit, as specified in 10 CFR 100, would be exceeded in approximately 90 minutes.<br /><br /> The postulated failure. leading to an inter-system LOCA within the primary coolant pump was not covered in the original design basis of the plant.<br /><br /> Corrective action for this event includes determining the appropriate modifications to address the issue and documenting the radiological consequences analysis of an inter-system LOCA within the primary coolant pump.
2551991018 | Palisades | 09/13/1991 | 10/14/1991 | 9110240019 | <strong>Unidentified Cable Penetrations In The Control Room</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1991, at approximately 0930 hours, three 4-inch diameter holes adjacent to control room floor penetration H-131 were found by electrical contractors employed by the configuration control project. At the time of discovery the plant was operating at approximately 100% power. The three holes (penetrations) were not identified on existing record prints. The cables routed through the unidentified penetrations were also not identified on existing electrical prints. <br /><br /> The cause of this event is indeterminate. No records could be found describing the installation, maintenance or surveillance of these penetrations. <br /><br /> The immediate corrective action taken was to initiate hourly fire tours in the area of the penetrations and determine if the penetrations were adequately sealed for control room HVAC and 10 CFR 50, Appendix R requirements and seal if necessary. Proposed long term corrective action includes: identifying the penetrations and updating the appropriate drawings, adding the new penetration seals to the technical specifications surveillance program and to the equipment data base and inspecting the cable spreading room ceiling for additional open or unidentified penetrations into the control room and initiating corrective action as required.
2551991019 | Palisades | 10/03/1991 | 10/31/1991 | 9111120145 | <strong>Stack Gas Radiation Monitor Cartridge/Filter Assembly O-Ring Failure</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1991, at approximately 0830 hours, it was determined that the radioactive gaseous effluent monitor (RGEM) on the plant stack was not functioning properly. At the time of discovery the plant was operating at 100% power. The condition was discovered during the performance of technical specification surveillance test DWR-10, "Stack Effluent Sampling, Calculations and Records". <br /><br /> The cause of this event was the failure of the O-ring on the RGEM system that seals the inlet side of the sample holder from the outlet side. Because of the O-ring failure, continuous sampling was not provided. <br /><br /> The immediate corrective action included notifying the Shift Engineer and the RMC Administrator of the condition, replacing the worn O-ring and reestablishing sample flow and conservatively estimating radioactive iodine and particulate activity for the period of September 26, 1991 through October 3, 1991. Long term corrective action includes revising the technical specification surveillance procedure to include recording of the differential pressure reading across the filter, training all Radiation Safety Department personnel on RGEM system operation and surveillance procedures and verifying the conservatism of the iodine and particulate activities estimate.
2551991020 | Palisades | 11/12/1991 | 12/13/1991 | 9112180150 | <strong>Inadequate Documentation - Environmental Protection Plan</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1991, the NRC resident inspector notified the Palisades Licensing Department that during a routine inspection he reviewed an example of our evaluation of an Unreviewed Environmental Question (UEQ). At the time the plant was operating at 100% power. He found no documentation that an unreviewed environmental question evaluation had been performed in the manner required by Appendix B, the Environmental Protection Plan (EPP), of the Palisades Operating License. Further investigation by Palisades staff determined that no UEQ evaluation had been performed or documented as required by the Environmental Protection Plan (EPP) since February 1987 when the administrative procedure covering this process was revised (i.e. there was not proper documentation to support the conclusions than no UEQs existed). The processing of Environmental Impact Reviews was immediately suspended and the condition reported to the NRC within 24 hours per the requirements of the operating license. Failure to follow the evaluation and documentation requirements of the EPP was due to the deletion, during the revision of Administrative Procedure 4.22 in February 1987, of a form which asked specific questions required by the EPP for evaluating UEQs. <br /><br /> Administrative Procedure 4.22 is being revised to require an UEQ evaluation to be performed in the manner required by the EPP. Additionally, all events occurring since February 1987 which required an Environmental Impact Review are being again reviewed to determine the necessity of performing and documenting an unreviewed environmental question evaluation in the manner prescribed by the EPP.
2591991001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 01/02/1991 | 02/08/1991 | 9102140008 | <strong>Failure of Two Trains of Standby Power Caused by Auxiliary Switch Contact Failure to Close</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1990, during the performance of diesel generator "A" load acceptance test the shutdown board "A" diesel generator voltage available relays (DGVA) failed to stay energized. On December 31, 1990, during the performance of diesel generator "D" load acceptance test, the shutdown board "D" DGVA relays failed to energize. Investigations showed the breaker stationary auxiliary switch contacts failed to close when the diesel generator breaker closed. The combination of these two events could have resulted in a failure of both core spray pumps to start, resulting in the potential loss of both loops of a critical safety function.<br /><br /> The root cause of this event was an unexpected failure affecting the reliability of the equipment.<br /><br /> Corrective actions include the addition of parallel redundant contacts on the Unit 1 and Unit 2 shutdown boards and an evaluation of the Unit 3 shutdown boards. In addition, preventative maintenance procedures will be modified to include a visual inspection of these switches.
2591991002 | Browns Ferry 1 | 02/01/1991 | 03/01/1991 | 9103110024 | <strong>A reactor vent exhaust monitor sample was missed when a filter holder assembly was improperly prepared, thereby causing a technical specification monitoring requirement to be exceeded.</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1991, TVA discovered that the reactor/turbine building ventilation radiation monitor (1-RM-90-250) did not contain the particulate filter and the charcoal cartridge in the filter holder assembly. The failure to install the sample media occurred during a routine changeout on January 26, 1991. Without the sampling media, BFN did not meet the Technical Specification Requirement to continuously collect samples for periods of 7 days and analyze within 48 hours at the end of sampling.<br /><br /> The root cause of this event was personnel error. The Radiochemical Laboratory Analyst (RLA) failed to follow the procedure that controls filter changeout. As a result, the RLA installed an empty holder assembly into the radiation monitor. There were two contributing factors to this event: (1) the filter holders had not been prepared according to an approved procedure, and (2) the supervisor did not ensure that RLAs were familiar with a newly revised procedure. <br /><br /> Immediate corrective actions were to replace the improperly prepared filter holder assembly and to verify that other in-service effluent CAMs had the required sampling media. Long-term corrective actions to preclude reoccurrence are: (1) appropriate personnel corrective actions were administered to chemistry personnel, (2) chemistry laboratory personnel were instructed to review procedures revisions prior to performance, and (3) chemistry laboratory personnel were required to review this event.
2591991003 | Browns Ferry 1 | 03/01/1991 | 04/01/1991 | 9104040246 | <strong>Gaseous and liquid effluent samples that were missed due to improper work activities caused Technical Specification requirements to be exceeded.</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1991, TVA discovered that a liquid sample and a gaseous effluent flow rate measurement were missed. Although a Radiochemical Laboratory Analyst (RLA) had documented that the work activities were completed, security keycard data could not support that the RLA was in the sampling areas at the time of the sampling. TVA, therefore, believes that technical requirements were not met and submits this report in accordance with 10 CFR 50.73(a)(2)(i). <br /><br /> The root cause of this event was poor work practices. Specifically, the RLA signed off steps in surveillance instructions (SIs) that he personally did not perform. A contributing factor to this event was inadequate supervision in that the chemistry shift supervisor did not ensure compensatory SIs were completed when performed. <br /><br /> Immediate corrective actions were to notify the Operations Manager and to remove the affected RLA from safety related activities. The long-term corrective actions to preclude recurrence are: (1) appropriate personnel corrective actions were administered to chemistry personnel, (2) TVA is continuing to investigate this event, (3) chemistry personnel were retrained on their responsibility when initializing steps in procedures, (4) chemistry managers are required to review and sign-off compensatory SI data on a shift-by-shift basis for completeness and accuracy, (5) chemistry compensatory SIs will be revised to include sign-off spaces for chemistry managers, (6) chemistry management conducted a review of chemistry laboratory work activities, and (7) a site-wide memorandum on the significance of signatures has been written.
2591991004 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/11/1991 | 06/17/1991 | 9106200151 | <strong>Unplanned Start of Unit 1 and 2 Diesel Generators Resulting from Personnel Error During Performance of Common Accident Signal Logic Surveillance Instruction</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1991 at 1819 hours, emergency diesel generators (EDGs), 1A, 1B, 1C and 1D and the associated emergency equipment cooling water (EECW) pumps unexpectedly auto-started during performance of Surveillance Instruction "Common Accident Signal Logic." <br /><br /> The root cause of this event was personnel error. An Assistant Unit Operator (AUO) placed the wrong keylock switch in the test position and started the EDGs. <br /><br /> Corrective actions were to return the EDGs and EECW pumps to standby readiness. The AUO was counseled, Larger keylock switch identification labels were installed. This event will be reviewed by Operations personnel.
2591991005 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/12/1991 | 05/11/1991 | 9105170319 | <strong>Potential Failure of Residual Heat Removal Service Water and Emergency Equipment Cooling Water Systems following Seismic Event as a Result of Inadequately Documented Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, TVA determined that a previously recognized condition had not been reported in accordance with the requirements of 10 CFR 50.73. This condition involved the potential for failure of the Residual Heat Removal Service Water (RHRSW) and Emergency Equipment Cooling Water (EECW) Systems during a seismic event. <br /><br /> The root cause of this condition was a failure to clearly document the design basis of flexible couplings used for Class I piping. Drawings did not accurately depict the as-designed or as-constructed configuration of the couplings, and specifications were not available to clearly describe the design and installation requirements. <br /><br /> In response to this condition programs were established to resolve past deficiencies which led to inadequately documented or analyzed designs. Design documents were revised to establish guidelines and requirements for design and analysis of flexible joints. In addition, Class I piping with Dresser couplings was evaluated and necessary modifications for Unit 2 performed. Modifications for Units 1 and 3 will be performed before each respective unit's restart. Finally, the Final Safety Analysis Report will be revised to reflect the results of the analysis and modifications.
2591991006 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 05/07/1991 | 06/06/1991 | 9106110271 | <strong>Unplanned Engineered Safety Feature Actuation During Maintenance Activities Due to Proximity of Components</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1991 at 1325 hours, an unplanned Engineered Safety Features (ESF) actuation occurred when the Control Room Emergency Ventilation System initiated. The ESF occurred when maintenance personnel performing work in a control panel inadvertently bumped the contacts of a relay associated with a radiation monitor.<br /><br /> The root cause of this event was a design which made it difficult to perform the work. The location of the components in the control panel does not provide adequate space to perform maintenance and/or calibration on the pressure switch without the possibility of bumping the relay contacts. In addition, the relay does not have a protective cover. Factors which contributed to this event included a lack of cautionary notes in the procedure and an unlabeled relay. <br /><br /> As a result of this isolated event TVA will evaluate the need for a design change to correct the instrument layout in the affected control panel and to provide a cover for the relay. TVA will also provide a specific procedure for performing maintenance/calibration on this pressure switch. Finally, the affected relay will be appropriately labeled.
2591991007 | Browns Ferry 1 | 05/31/1991 | 07/01/1991 | 9107110208 | <strong>Emergency Diesel Generators Auto-Started Due to a Degraded Voltage Condition on 4kV Shutdown Board</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1991 at 1406 hours, emergency diesel generators (EDGs) A and B automatically started due to a degraded voltage condition on 4 kilovolt (kV) shutdown boards A and B respectively. The shutdown boards are fed from the unit station service transformer (USST). The event occurred because the winding selection switch of the USST 1B automatic tap changer was set to monitor the lighter loaded winding of the transformer. As a result, when the tap changer responded to lower the voltage on this winding, the voltage of the heavier loaded winding of the transformer dipped below the degraded voltage setpoint of the 4kV shutdown boards for the automatic start of EDGs A and B. <br /><br /> The root cause of the event was inadequate procedure control. There was no procedure or checklist in place that required the loading of the USST with auto tap changer to be checked periodically to ensure that the heavier loaded winding of the USST is monitored. <br /><br /> Corrective actions include a revision of the Assistant Shift Operations Supervisor's daily electrical log of the operations routine sheets to include a note that informed personnel to set USST winding selector switch to monitor the heavier loaded winding. Additionally, live time training on this event has been completed with Operations personnel.
2591991008 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 07/24/1991 | 08/23/1991 | 9108300083 | <strong>Fire Wrap Removed During Unit 3 Integrated Walkdown Activities Without Establishing A Fire Watch</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1991, at 1945 hours, an NRC Resident Inspector informed the Shift Operations Supervisor that fire wrap was removed from a junction box in the intake structure. At that time, the Unit 2 reactor was at approximately 90 percent power and Unit 1 and 3 were defueled. On investigation, it was discovered that fire wrap had been removed from several junction boxes and a pull box and a continuous fire watch had not been established as required by Technical Specifications. The fire wrap had been removed, by an approved work order, on July 24, 1991, to support Unit 3 Walkdown activities. These junction boxes are associated with Residual Heat Removal Service Water System (RHRSW) pumps, which are required for safe shutdown per the Appendix R Safe Shutdown Analysis. As immediate corrective action, a fire watch was established at 2050 hours on July 28, 1991, and Unit 3 work activities were stopped pending investigation. <br /><br /> The root cause of this event is management failure to ensure that Unit 3 planning and implementation of work was in full compliance with site procedures. The failure to establish the required fire watch was a direct result of personnel not following procedures. The duties, responsibilities, and accountabilities of Field Services-Modifications personnel have been clearly defined. Training has been conducted on the requirement to be knowledgeable of and adhere to policy and procedures. Appropriate personnel corrective actions will be taken by September 9, 1991.
2591991009 | Browns Ferry 1 | 09/05/1990 | 09/23/1991 | 9110010302 | <strong>Fire Penetration Discovered Open Without Fire Watch in Place as Required by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1991 a maintenance planner conducting a review of open work requests on Unit 1 discovered that a fire penetration under 480v reactor motor operated valve (MOV) board 1B was not sealed. The planner notified the Shift Operations Supervisor (SOS) of the condition and a fire watch was established. This penetration was opened on May 11, 1990 for modifications and a fire watch established. On September 5, 1990 the fire watch was terminated. <br /><br /> The root cause of this event was inappropriate personnel action in that the cable pulling activity was signed off as completed without visual verification that the penetration was sealed. Contributing to this event was closure of the work plan without sealing the penetration, failure to immediately notify the SOS when the unsealed penetration was discovered, and failure of the SOS to recognize the open penetration placed the plant in a limiting condition of operation. <br /><br /> The immediate corrective actions included sealing the open penetration and performing a review of open work request/work orders for similar problems. Personnel will be trained on this event.
2601991001 | Browns Ferry 2 | 01/16/1991 | 02/14/1991 | 9102210047 | <strong>Unplanned Engineered Safety Features Actuation Due to a Blown Fuse Caused By a Failed Relay</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1991 at 0430 hours, a blown fuse in the Primary Containment Isolation System (PCIS) logic circuitry resulted in unplanned actuations of various engineered safety features. This would normally include isolation of the drywell equipment and floor drain discharge isolation valves, isolation of the main steam line drain valve, and withdrawal of any inserted traversing incore probes (TIPs). However, the main steam line drain valve did not isolate because it was tagged out of service, and the TIPs did not withdraw because they were not inserted. <br /><br /> The root cause of this event was the failure of a General Electric (GE) type CR120 relay in the PCIS circuitry due to a faulted coil. The relay failure caused a faulted condition which resulted in blowing the fuse and subsequent loss of PCIS logic power. <br /><br /> As a result of this event, the relay coils in GE type CR120 relays used in normally energized, safety-related applications in all three units will be replaced.
2601991002 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 02/23/1991 | 03/21/1991 | 9103270242 | <strong>Unplanned Engineered Safety Feature actuation due to Radiation Monitors downscale caused by degraded radioactive bug source in the radiation monitor detectors</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1991 at 0210 hours, the two reactor building ventilation radiation monitors simultaneously had radiation count rates below their respective downscale trip setpoints. This condition resulted in an unplanned automatic actuation of engineered safety features. <br /><br /> The root cause of this event was the lack of a program to control the degraded (low radiation count rate) bug sources in the radiation monitor detectors. (A bug source is a vendor installed source for ensuring an on-scale radiation reading). <br /><br /> The bug source for the 2-RM-90-142 detector was readjusted to obtain count rates above the downscale trip setpoint. Even though sufficient counts could be attained with the adjustment of the 2-RM-90-143 bug source, the 2-RM-90-143 detector assembly was replaced to ensure a higher count rate could be detected. Periodic adjustments of the bug source in the radiation monito detector will be proceduralized.
2601991003 | Browns Ferry 2, Browns Ferry 3 | 02/23/1991 | 03/25/1991 | 9104010387 | <strong>Unplanned ESF actuation of RHRSW pump D3</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1991 at 1726 hours, residual heat removal service water (RHRSW) pump D3 unexpectedly auto-started following the racking in of the 4160 volt breaker feeding core spray (CS) pump 2B. This resulted in an unplanned actuation of an Engineered Safeguard Feature. <br /><br /> The cause of this event could not be determined. In-depth testing performed on the CS pump 2B breaker did not reveal a root cause for this unforeseen failure.<br /><br /> The corrective action taken during the event was to return RHRSW pump to standby readiness. Further corrective actions were to perform an evaluation of the breaker to determine a failure mechanism.
2601991004 | Browns Ferry 2 | 03/26/1991 | 06/24/1991 | 9106270339 | <strong>Reactor Protection System Actuation as a Result of Exceeding the Hi-Hi SRM Channel Setpoint During Testing.</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991, at 2024 hours, Unit 2 Reactor Protection System actuation occurred when the count rate on the source range monitor (SRM) channel C spiked while a time domain reflectometer (TDR) trace was being performed on the Unit 2 intermediate range monitor (IRM) channel C detector cable shield. <br /><br /> The root cause of this event could not be determined. The scram was the result of an unexpected hi-hi trip generated during the performance of TDR tracing on an IRM cable located in the proximity of the SRM channel C cable. However, the cause of the hi-hi trip signal could not be determined or repeated. <br /><br /> The ground fault in the IRM channel C detector cable shield was removed. In addition, the neutron monitoring system, including the interaction between channels, was evaluated. From the information gathered during this evaluation, TVA developed and implemented corrective actions directed to both the neutron monitoring hardware and to the maintenance procedures.
2601991005 | Browns Ferry 2 | 03/27/1991 | 04/25/1991 | 9104290290 | <strong>Unplanned Engineered Safety Features Actuation Due To Clearing Of A Fuse Caused By A Failed Relay Coil.</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1991, at 0322 hours, a fuse in the Primary Containment Isolation System (PCIS) cleared, resulting in Engineered Safety Feature actuations. These actuations included closure of the drywell floor drain isolation valve, drywell equipment drain sump isolation valve, and the suppression pool drain valve. <br /><br /> This event was caused by an unexpected failure of a PCIS relay resulting from a faulty relay coil. The coil in a General Electric (GE) type CR120 relay, used in the normally energized state, failed. <br /><br /> Corrective actions included replacing the relay coil and realigning the affected systems. Further corrective actions will include replacement of the relay coil in the GE type CR120 relays used in normally energized, safety-related applications in all three units.
2601991006 | Browns Ferry 2 | 03/29/1991 | 06/24/1991 | 9106270359 | <strong>Unplanned Reactor Protection System Actuation Resulting From Local Power Range Monitor Leakage Current</strong><br /><i>Abstract:&nbsp;</i>At 2139 hours on March 29, 1991, an unplanned Reactor Protection System actuation occurred on Unit 2 when average power range monitor (APRM) B drifted high and exceeded the hi-hi setpoint. The input to the APRM is provided by the local power range monitors (LPRMs). During this event, a single LPRM drifted high due to a high leakage current and this resulted in the associated APRM exceeding its setpoint. This event was terminated at 2330 hours on March 29, 1991 when the LPRM was bypassed and the reactor scram was reset. <br /><br /> The root cause of this event was an unexpected failure of the LPRM due to a high leakage current which was apparently caused by a cracked ceramic seal on the LPRM cable. <br /><br /> The initial corrective action was to troubleshoot the LPRM. Additional testing showed a high leakage current in the LPRM cable. Since present plant conditions preclude the repair or replacement of this detector, the LPRM has been placed in the bypass mode.<br /><br /> In addition, the neutron monitoring system, including the interaction between channels, was evaluated. From the information gathered during this evaluation, TVA developed and implemented corrective actions directed to both the neutron monitoring hardware and to the maintenance procedures.<br /><br /> Additional corrective actions include the replacement of the LPRM during the cycle 6 refueling outage.
2601991007 | Browns Ferry 2 | 04/09/1991 | 05/05/1991 | 9105130308 | <strong>ESF Actuation Resulting from Leaking Packing on Check Valve Differential Pressure Transmitters on the Main Steam System</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1991, at 0156 hours Central time, an unplanned Engineered Safety Feature (ESF) actuation occurred when the Group 1 primary containment isolation (PCIS) initiated. The Group 1 PCIS occurred during the performance of a Surveillance Instruction (SI) when Instrument Mechanics (IMs) placed Channels A and B in an isolated mode and a leak from 2-PDT-1-25B valve caused the depressurization of the low side of the Channel B transmitter. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an event that resulted in an automatic initiation of an ESF.<br /><br /> The cause of this event was that one process instrument had entrapped air in the low-side sensing line, and one process instrument had a water leak from the packing in the low-side manifold valve. <br /><br /> The unit operator contacted the IMs, and work on SI was stopped. The IMs returned the affected instruments to service. Subsequent corrective actions were: IMs vented trapped air and backfilled line for the first process instrument and tightened packing nuts on the other process instrument. In addition, SIs that test excess flow check valves were revised to require constant communications with control room Unit Operator and to install jumpers to bypass the initiation of Group 1 PCIS logic on main steam line high flow.
2601991008 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 04/11/1991 | 05/11/1991 | 9105170322 | <strong>Unplanned Engineered Safety Features Actuations Due to a Failed PCIS Relay</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1991, at 1055 hours, a Unit 2 Primary Containment Isolation System logic relay failed. This resulted in the unplanned actuations of various Engineered Safety Features. <br /><br /> The root cause of this event was the end-of-life failure of a normally energized General Electric (GE) type CR120 relay. The failed relay was due to a burned coil in the relay. <br /><br /> The faulty coil was identified and replaced. TVA has committed to replace GE type CR120 relay coils used in normally energized safety-related applications in all three units.
2601991009 | Browns Ferry 2 | 04/12/1991 | 06/26/1991 | 9107020359 | <strong>Inadvertent Main Steam Isolation Valve Closure During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, at 0034 hours, the outboard main steam isolation valve (MSIVs) closed during the performance of a Surveillance Instruction (SI). Prior to the beginning of the surveillance test a relay associated with the MSIV isolation logic had been removed and was scheduled for replacement. The removal of the relay placed the MSIVs in a 1-out-of-2 isolation signal condition. In accordance with the SI, a reactor vessel water level transmitter was isolated at the manifold, and the transmitter high side began to depressurize through valve packing leaks. This simulated a low-low-low reactor water level signal which completed the isolation logic to close the outboard MSIVs. <br /><br /> The root cause of this event was personnel error. The personnel involved with the evaluation of the impact of the missing relay failed to adequately assess its effect on the MSIV isolation logic.<br /><br /> Immediate corrective actions were taken to terminate the surveillance test and to return the reactor water level transmitter to service. Licensed Operations personnel, Maintenance foremen, Maintenance planners, and System Engineering personnel will be required to review this event. A design change will be implemented to provide a means to monitor MSIV pilot solenoid circuit continuity.
2601991010 | Browns Ferry 2 | 05/15/1991 | 08/23/1991 | 9108300088 | <strong>Plant Technical Specification Violation When 24-Hour Limiting Condition for Operation Expired Without Declaring Affected Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1991 at 1438 hours, a violation of the plant Technical Specifications (TSs) occurred when a 24-hour Limiting Condition for Operation (LCO) expired and the systems affected by a reactor vessel water level transmitter were not declared inoperable. <br /><br /> The root cause of this event was inadequate procedures. The procedure used in this event required that Operations be notified that TS related equipment would be removed from service prior to starting work on the equipment. The procedure also required Operations to be notified if it appeared that an LCO time limit would be exceeded. However, the procedure did not require Operations to be notified of the exact time the equipment was removed from service, even though the time was documented in the procedure. <br /><br /> The immediate corrective action was to declare the affected systems inoperable.<br /><br /> Additional corrective actions will include training of the affected plant personnel and revision of plant procedures.
2601991011 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 05/14/1991 | 06/14/1991 | 9106200168 | <strong>Dresser Coupling Failure Lead to a Condition That Could Have Presented Standby Gas Treatment System From Fulfilling Safety Function</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1991 at 2010 hours, the Standby Gas Treatment (SGT) System was declared inoperable following the discovery that the SGT system flow was oscillating. <br /><br /> The root cause of this event was an unexpected failure of the Dresser coupling seal on one of the 30-inch exhaust ducts. This was compounded by capping of the discharge ducts drain pipe and a record rainfall which caused the ground water table level to rise above the Dresser coupling elevation. <br /><br /> Corrective actions included determining the cause of the oscillations, draining the water from the discharge duct and repair the Dresser coupling seal. A loop seal was added to the SGT drain line, and the drain pipe was left uncapped.
2601991012 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 05/19/1991 | 06/17/1991 | 9106200144 | <strong>Unplanned Engineered Safety Features Actuation Following Reactor Protection System Bus De-energization Caused by Random Equipment Failure.</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1991 at 1359 hours, an unplanned emergency safety features actuation occurred following de-energization of Reactor Protection System (RPS) bus 2A. This resulted in actuation of the Primary Containment Isolation System, which included closure of valves in the Residual Heat Removal and Reactor Water Cleanup Systems, withdrawal of any inserted traversing incore probes, and isolation of plant ventilation systems. In addition, the Control Room Emergency Ventilation System (CREVS) and Standby Gas Treatment System (SGTS) received actuation signals. However, the CREVS was already in service and the SGTS was removed from service. <br /><br /> The root cause of this event was equipment failure. The RPS bus deenergized after the motor from its normal power source, motor-generator set 2A, failed. The motor failure was attributed to winding insulation breakdown between phases A and C in the outboard endturn area of the motor. <br /><br /> The failed RPS MG set motor (General Electric Model 5K326AK2060; a 460 volt, 3-phase AC motor) was removed and replaced.
2601991013 | Browns Ferry 2 | 06/05/1991 | 07/19/1991 | 9107290065 | <strong>Technical Specification Violation Following Loss of Primary Containment Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1991 at approximately 0245 hours a loss of primary containment integrity occurred when both drywell personnel airlock doors were opened. This condition occurred after the interlock which prevents both doors from being simultaneously open was disarmed. Upon notification the Shift Operations Supervisor re-established primary containment integrity at approximately 0645 hours. <br /><br /> The root cause of this event was an unauthorized personnel action. The individual involved (utility, non-licensed) performed unauthorized work by disarming the interlock on the drywell airlock. A contributing cause of this event was the lack of action taken by those in the direct area during the event. <br /><br /> TVA's corrective actions to address the specifics of this event included general and specialized training for plant personnel, procedure enhancements to ensure Operations personnel are responsible for the operation of the drywell doors, and personnel corrective action in accordance with TVA policy. In addition, TVA performed an independent review to identify areas in which improvements were prudent to further enhance maintenance-related activities and to reinforce requisite operational attitudes. This review resulted in additional procedure improvements, guidelines to enhance pre-test briefings, and identification of future training upgrades.
2601991014 | Browns Ferry 2 | 06/29/1991 | 08/30/1991 | 9109090125 | <strong>Manual Reactor Scram Required Due to Bulk Suppression Pool Water Temperature Exceeding Technical Specification Limit Caused by Inadequate Procedural Control</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1991, during performance of power ascension testing the Unit 2 reactor was manually scrammed at 0248 hours from approximately 25 megawatts thermal power due to the bulk suppression pool water temperature exceeding the Technical Specification limit of 110 degrees F. This occurred as a result of suppression pool thermal stratification while operating Reactor Core Isolation Cooling (RCIC). <br /><br /> The root cause of this event was inadequate procedures. Plant procedures did not provide information on the possibility for thermal stratification of suppression pool water which can result from operation of RCIC. Contributing to this event was the location of the temperature elements in the suppression pool, malfunction of the suppression chamber atmospheric temperature recorder (manufactured by Leeds & Northrup) and failure of the Shift Technical Advisor and the General Electric shift advisor to analyze the expected torus water heatup during the plant evolution. <br /><br /> TVA revised the procedure for operating RCIC to note the potential for thermal stratification of the suppression pool, and to require evaluation of the necessity to initiate suppression pool cooling. Other plant procedures will be revised as necessary to add this information. TVA also issued an Operations Standing Order which specifies the expected rate of suppression pool heatup during RCIC and High-Pressure Coolant injection system operation, and when suppression pool cooling should be initiated. Operating crews were trained on the standing order and the details of this event.
2601991015 | Browns Ferry 2 | 07/31/1991 | 08/30/1991 | 9109090134 | <strong>High Pressure Coolant Injection (HPCI) System Did Not Fulfill Its Safety Function Resulting From Low Suction Pressure Condition During a Fast Start-up.</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1991 at 1313 hours, TVA began a performance test of the High Pressure Coolant Injection (HPCI) System. This test was part of the Unit 2 power ascension program. At the time, Unit 2 was at 77 percent power with a reactor temperature and pressure of 542 degrees F and 965 psig. The HPCI system tripped from a low suction pressure transient. This HPCI system trip was reset automatically after approximately 10 seconds. This trip could have prevented the HPCI system from fulfilling its intended safety function. Therefore, this event is reportable in accordance with 10 CFR 50.73(a)(2)(v). <br /><br /> The root cause of this event is a problem not anticipated in design. It is apparent that the HPCI system may be subject to momentary, suction pressure transients capable of tripping the HPCI turbine. Ten seconds after the HPCI system tripped, the HPCI system restarted due to a start signal still being present. During the restart no low-pressure transient was experienced and the HPCI system ran for approximately five minutes. <br /><br /> The Immediate Corrective Action was to declare the HPCI system inoperable and the HPCI turbine was manually tripped. Temporary time delay relays were installed under a Temporary Alteration Control Form. HPCI injection to the reactor vessel was retested and HPCI was declared operable. <br /><br /> The long-term corrective action is to install permanent time delay relays on Units 1, 2 and 3. These installations will preclude a recurrence of this event.
2601991016 | Browns Ferry 2 | 08/19/1991 | 09/18/1991 | 9109240391 | <strong>Unplanned Engineered Safety Features Actuation Due to a Blown Fuse Caused by a Failed Relay</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1991 at 1335 hours, during Unit 2 normal operations at 100 percent power (3290 megawatts thermal), a blown fuse in the Primary Containment Isolation System (PCIS) logic circuitry resulted in unplanned actuations of various engineered safety features. This included isolation of the Radwaste system drywell floor drain isolation valve, the drywell equipment drain sump isolation valve, and the Core Spray system suppression pool drain valve. In addition, the Main Steam system main steam line inboard drain valve and the Traversing Incore Probe system isolation valves would have isolated. However, they were isolated at the time of this event. <br /><br /> The root cause of this event was the failure of a General Electric (GE) type CR120A relay in the PCIS circuitry due to a faulted coil. <br /><br /> As a result of previous events, TVA committed to replacing the GE type CR120A relays used in normally energized, safety-related applications on Unit 2 during the Unit 2, Cycle 6 refueling outage. As a result of this event, TVA will accelerate the replacement of some of the relay coils. Specifically, the relay coils in applications where a relay failure could result in a plant shutdown will be replaced prior to the Unit 2, Cycle 6 refueling outage.
2601991017 | Browns Ferry 2 | 09/14/1991 | 10/15/1991 | 9110280223 | <strong>Failed Soldered Connection on Air Supply Line to Steam Packing Exhauster Bypass Flow Control Valve Resulted in Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1991 at 1832 hours, with Unit 2 operating at 100 percent power, an automatic reactor scram occurred on low reactor water level. The low water level was caused by a momentary loss of reactor feedwater. The loss of reactor feedwater was a result of a failed soldered connection on the air supply line to the steam packing exhauster bypass flow control valve (FCV) allowing the FCV to close. The loss of flow condition subsequently caused 'A' and 'B' condensate booster pumps and 'A' and 'B' reactor feed pumps to trip on low suction pressure. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition which resulted in manual or automatic actuation of engineered safety features including the reactor protection system. <br /><br /> The root cause of this event was poor workmanship on the failed air supply line soldered connection. TVA's analysis determined that the bonded area of the failed solder joint was less than 15 percent. <br /><br /> The soldered connection was repaired. Those required soldered connections in air supply lines whose failure could cause a reactor scram will be inspected by visual examination using liquid leak detection solution.
2601991018 | Browns Ferry 2 | 10/18/1991 | 11/15/1991 | 9111250170 | <strong>Failure to Open the Generator Exciter Field Breaker After Manual Turbine Trip Resulted in a Reactor Scram Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1991 at 0458 hours, during a controlled shutdown, Browns Ferry Unit 2 reactor was manually scrammed from approximately eight percent thermal power due to unexpected equipment responses.<br /><br /> The root cause of this event was inappropriate personnel action. A plant operator failed to follow the procedure for turbine generator shutdown when he did not open the exciter field breaker after the manual turbine generator trip. This action caused unexpected equipment responses including actuation of the generator reverse power relay and subsequent tripping of the reactor recirculation pumps. <br /><br /> The reverse power relay was tested. The evaluation and testing of the recirculation pump boards was completed. Operations personnel will receive live-time training on the event. TVA will change the plant design to include automatic tripping of the generator field breaker when the turbine generator is tripped. The Browns Ferry simulator will be upgraded to match plant conditions.
2601991019 | Browns Ferry 2 | 12/08/1991 | 01/07/1992 | 9201130145 | <strong>Automatic Reactor Scram Following a Turbine Trip Which was a Result of an Unexpected Fuse Failure</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1991 at 2320 CST, Browns Ferry Unit 2 automatically scrammed from approximately 80 percent power following a turbine trip. In addition, during this event, an unexpected loss of one of the offsite power supplies occurred. <br /><br /> The root cause of this event was an unexpected and unforeseen fuse (Gould-Shawmut) failure. <br /><br /> TVA has replaced the existing 500kV Bus Potential Transformer secondary fuses to minimize the possibility of spurious relay operations. <br /><br /> TVA will evaluate reconfiguring the existing plant design to eliminate the possibility that the loss of the relaying potential from a single bus will result in the loss of the generating unit. In addition, TVA will investigate the spurious trip of Trinity line 1 line during this event and correct any identified deficiencies.
2611991001 | Robinson 2 | 01/12/1991 | 02/18/1991 | 9102250176 | <strong>Inoperable Pressurizer Power Operated Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1991 with the H. B. Robinson Unit No. 2 in cold shutdown for Refueling Outage No. 13, Copes-Vulcan notified Carolina Power and Light Company that certain parts supplied by them were not Qualified Safety Related parts as required by the Purchase Order. The parts in question had been installed in the Pressurizer Power Operated Relief Valve Operators on January 6 and 7, 1991. The Power Operated Relief Valves (PORVs) were not required to be operable at the time this condition was discovered, but were required to be operable for Low Temperature Overpressure Protection during Fill and Vent operations conducted between 1521 hours on January 12, 1991 and 1211 hours on January 13, 1991, a period of 20 hours and 40 minutes. Technical Specification 3.1.2.1.d allows an LCO for inoperable PORVs of 12 hours; therefore this event is being reported as an operation not allowed by Technical Specification.
2611991002 | Robinson 2 | 02/28/1991 | 03/28/1991 | 9104020377 | <strong>Reactor Trip Due To Lo-Lo Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1991, at 0102 hours with Unit No. 2 in cold shutdown, an automatic reactor trip was received from a lo-lo level in steam generator (S/G) "A". The cause of the trip is attributed to personnel error associated with the S/G draindown which was in progress. Although the plant was in cold shutdown, the reactor trip breakers were closed to allow the performance of control rod drop testing. All three S/Gs were being drained to clear high levels so as to allow feedwater isolation resets and to obtain normal narrow range level indication. The control operator was aware that the lo level alarm had come in but did not anticipate the narrow range S/G level dropping as fast as it did. Throughout this event, LT-476, one of three narrow range level instruments on S/G "A" was off scale high thus causing the high level alarm to be locked in. The operator has been counseled regarding his actions in this event and this event continues to be evaluated via the plant Corrective Action Program. This event was reported via the Emergency Notification System at 0138 hours pursuant to 10CFR50.72(b)(2)(ii). This Licensee Event Report is submitted pursuant to 10CFR50.73(A)(2)(iv).
2611991003 | Robinson 2 | 02/14/1991 | 03/22/1991 | 9103290201 | <strong>Containment Vessel Fire During Refueling Due To Non-Approved Equipment Heating Process</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1991, H. B. Robinson Unit No. 2 was in cold shutdown condition for refueling. The Reactor Vessel Head had been removed from the vessel and was in its storage area in the containment building, where it was being "warmed" to facilitate head reassembly and installation. At 2154 hours, a fire was reported on the ground level of the containment building at the head storage area. The fire was extinguished within eight minutes of discovery. The cause of the fire was attributed to localized heating of extension cords used to supply temporary incandescent lighting for the vessel head warming process. An overloaded electrical condition, combined with the resistance of a knotted electrical cord connection, resulted in sufficient heat to ignite the electrical cord insulation, which subsequently ignited combustible materials around the Reactor Vessel Head. <br /><br /> Plant recovery activities included a root cause investigation and an assessment of the effects of the fire on the Reactor Vessel Head and on other equipment in the containment building. These activities were completed, and the Plant was returned to operating status. <br /><br /> This event was reviewed pursuant to 10 CFR 50.73, and was determined not to be reportable. This LER is provided as an event of potential interest to the industry.
2611991004 | Robinson 2 | 03/19/1991 | 04/17/1991 | 9104220320 | <strong>Rod Control System Urgent Failure</strong><br /><i>Abstract:&nbsp;</i>At 0741 hours on March 19, 1991, with no apparent warning and no control rod motion in progress, a Rod Control System Urgent Failure alarm was received. The condition was the result of failed printed circuit boards (PCB) in the phase control and firing control circuits for the Control Bank C, Group 2 stationary gripper control in Power Cabinet 2AC. The Urgent Failure alarm within Power Cabinet 2AC prevented all overlap rod motion within that Power Cabinet, which resulted in the inoperability of 12 of the 45 control rod assemblies. Since this condition exceeded the requirements of the Technical Specification Limiting Condition for Operation, Technical Specification 3.0 was entered. The failed PCBs were replaced, and the affected control rods were successfully tested and declared operable at 1200 hours. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), in accordance with the guidance provided within NUREG-1022, Supplement 1, as a condition prohibited by the plant's Technical Specifications.
2611991005 | Robinson 2 | 04/12/1991 | 05/13/1991 | 9105230277 | <strong>TECH. SPEC. 3.0 ENTRY TO ADJUST SI ACCUMULATOR BORON CONCENTRATION</strong><br /><i>Abstract:&nbsp;</i>
2611991006 | Robinson 2 | 05/14/1991 | 06/21/1991 | 9106180356 | <strong>Unanalyzed Condition Due To Inadequate Calculations For Post- LOCA Core Cooling</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1991, a review of details and supporting analysis for the safety injection switchover portion of emergency operation procedures for the H. B. Robinson Plant revealed that insufficient analysis existed for assurance of adequate long term core cooling in the post-LOCA condition. Specifically, previous calculations misinterpreted terminology and therefore did not account for all phenomena depleting the liquid inventory of the reactor core under post LOCA conditions. Thus, the adequacy of procedures for switchover from the injection phase to the long-term cold leg recirculation phase were brought into question. At 1525 hours, the licensee invoked Technical Specification 3.0, and the Plant commenced a power reduction to sixty percent, which was believed to be an analyzed condition. The NRC was notified via the ENS of this condition at 1612 hours pursuant to 10 CFR 50.72(b)(ii)(A).<br /><br /> At 2138 hours, a specific evaluation which justified ninety-five percent power operation was eceived, and the Technical Specification 3.0 action was exited. Reactor power was increased to ninety percent while additional calculations were performed. Full power operation was justified and achieved on May 29, 1991. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(ii)(A).
2611991007 | Robinson 2 | 05/17/1991 | 06/06/1991 | 9106170046 | <strong>Failure To Perform Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>At about 2000 on May 19, 1991, with the H. B. Robinson Unit No. 2 Operating at about 92% power, it was identified that the Maintenance Surveillance Test, MST-902, Battery Test - Daily 5 Days Per Week, had not been performed on May 17, 1991, to meet the 5 days per week requirement for the week of May 11 through 17, 1991. This surveillance test is required by Technical Specification 4.6.3. When it was identified that the scheduled surveillance test was missed, Licensee Technicians performed the test proving Station Battery Operability by 2015 May 19, 1991. The Licensee Instrumentation and Control (I&C) Supervisor and the Shift Supervisor were notified of the missed surveillance at 2030 May 19, 1991, and the Shift Supervisor documented that the Station Batteries were administratively Out of Service from 2000 to 2015.<br /><br /> This LER is the result of personnel error and is being reported under 10CFR50.73 (a) (2) (i) and 50.73 (a) (2) (vii).
2611991008 | Robinson 2 | 07/11/1991 | 08/02/1991 | 9108120222 | <strong>Technical Specification 3.0 Implementation: IVSW Isolation To Perform Maintenance</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1991, in order to conduct planned post maintenance testing on a Reactor Coolant Drain Tank Pump Discharge Line Isolation Valve, Isolation Valve Seal Water (IVSW) was required to be isolated from the containment penetrations it serves. This necessitated implementation of Technical Specification 3.0 because Plant Technical Specifications do not have an action statement for IVSW isolation while at power operation. Thus, as provided by NUREG 1022, Supplement No. 1, the Plant was considered to be operating in a condition prohibited by the Plant's Technical Specifications. Containment integrity was maintained throughout the process. The testing was satisfactorily completed, and the system was returned within the time period allowed by the action statement. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B)
2611991009 | Robinson 2 | 08/16/1991 | 09/16/1991 | 9109240379 | <strong>OVERTEMPERATURE DELTA TEMPERATURE CHANNELS INOPERABLE DUE TO SUMMATOR MODULE LAG CONSTANTS</strong><br /><i>Abstract:&nbsp;</i>
2611991010 | Robinson 2 | 08/16/1991 | 09/10/1991 | 9109170282 | <strong>Source Range Reactor Trip While At Hot Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 1958 on August 16, 1991, with the H. B. Robinson Unit No. 2 in hot shutdown, a trip of Shutdown Bank "A" Rods was initiated by Source Range channel N-31. The trip occurred when the Source Range instrumentation was manually energized as part of the process of reactor shutdown under a Limiting Condition of Operation unrelated to this event. The Reactor Trip was caused by a valid signal generated from Channel N-31 greater than the 100,000 Counts Per Second (CPS) Reactor Trip Setpoint.
2611991011 | Robinson 2 | 08/30/1991 | 09/18/1991 | 9109250071 | <strong>Reactor Trip Due to Failure of Condensate Pump Shaft</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1991, at 0700 hours with Unit No. 2 operating at one hundred percent power, an automatic reactor trip was received from a "C" Steam Generator low level coincident with a steam flow/feed flow mismatch. The cause of this trip is attributed to failure of the "B" Condensate Pump shaft, which resulted in inadequate feedwater flow to the steam generators. The Plant was brought to shutdown conditions using Emergency Operating Procedures, and was stabilized at 0711 hours. The NRC was notified of this event via the ENS at 0830 hours pursuant to 10 CFR 50.72(b)(2)(ii). <br /><br /> Repairs to the "B" Condensate Pump will require use of a pump that has been previously in service, and is awaiting refurbishment. Until this pump can be placed back in service, the Plant will operate at approximately sixty five percent power, which can be achieved with adequate feedwater being supplied with only one condensate pump in operation. <br /><br /> This Licensee Event Report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv).
2611991012 | Robinson 2 | 09/14/1991 | 10/08/1991 | 9110160248 | <strong>Entry Into Technical Specification 3.0 Due To Inadequate Undervoltage Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1991, an engineering review determined that current surveillance procedures did not completely address Technical Specification (TS) required testing for the 480V Emergency Bus Undervoltage circuitry. As a result, all four channels of the 480V Emergency Bus Undervoltage (Loss of Voltage) circuit were declared inoperable at 1650 hours on September 14, 1991. TS Table 3.5-3 Item 3a requires that a minimum of two channels per bus be maintained operable or the plant must maintain hot shutdown conditions. In that this requirement could not be complied with, the plant entered TS 3.0 at that time. The NRC was notified at 1750 hours of this condition via the ENS. TS 3.0 requires that the plant be placed in hot shutdown within 8 hours, at which time the plant is again in compliance with TS 3.5-3 Item 3a. In order to preclude the plant transient associated with placing the plant in hot shutdown conditions, a Regional Waiver of Compliance from the requirement of TS Table 3.5-3 Item 3a was requested and granted to allow continued plant operation with all four channels technically inoperable only on the basis of not performing the required surveillance. A TS change was issued on September 27, 1991, which resolves this issue until the surveillance testing can be performed. <br /><br /> This LER is submitted pursuant to 10 CFR 50.73(A)(2)(i)(B).
2611991013 | Robinson 2 | 09/17/1991 | 10/08/1991 | 9110180037 | <strong>Diesel Driven Fire Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>AT 1100 hours on September 17, 1991, with the H. B. Robinson Unit No. 2 operating at 100% power the Diesel Engine Driven Fire Pump was declared inoperable. The Fire Pump was declared inoperable based on a Preventative Maintenance procedure, PM-103, Fire Pump Diesel Inspection Number 1 (Annual), that was completed on April 29, 1991, and recorded an engine oil temperature of 104 degrees F which is less than the manufactures recommended 120 degrees F. PM-103 references Technical Specification 3.14, 4.14.6.1, and 4.14.6.2. Of these paragraphs 4.14.6.1.b was not satisfied due to the engine oil temperature being less than the manufactures recommended 120 degrees F. Technical Specification 4.14.6.1.b requires that an inspection be performed in accordance with a procedure prepared in conjunction with manufacture recommendations.
2631991001 | Monticello | 01/09/1991 | 02/08/1991 | ML11311135 | <strong>Loss of Power to Radiation Monitor Resulting in Unplanned Emergency Filtration Treatment System Actuation to High Radiation Mode</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1991 with the plant operating at 100% power, the Control Room Emergency Filtration Treatment system transferred to the High Radiation mode during performance of the monthly surveillance test. A loss of power to the "A" 'Radiation Monitor resulted in the transfer but the cause of the loss of power cannot be determined. A thorough investigation into the event has not identified any unusual conditions which may have caused the loss of power. Following verification of normal system operation, the High Radiation signal was reset and the system returned to normal operation. The monthly surveillance test was completed without further unplanned actuations. No further corrective actions are planned.
2631991002 | Monticello | 01/09/1991 | 02/08/1991 | ML113111355 | <strong>Control Power Circuit Breaker for Filtration Unit Heater Found Open Resulting in Inoperability of Control Room Emergency Filtration System</strong><br /><i>Abstract:&nbsp;</i>
2631991003 | Monticello | 02/11/1991 | 03/13/1991 | ML11311135 | <strong>Unexpected Intermediate Range Monitor Response to Flux Redistribution Results in Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>With the reactor critical, the mode switch in STARTUP, Reactor Pressure Vessel heat-up in progress (Reactor Pressure Vessel temperature = 165 degrees Fahrenheit), and the Intermediate Range Monitors reading approximately 40/125 of scale on range 7, control blade 18-39 was withdrawn from notch position 06 to notch position 08. Immediately following the control blade withdrawal, flux levels indicated by the Intermediate Range Monitors increased to the scram setpoint too quickly for the Operator to reinsert the control blade. High-High signals from Intermediate Range Monitors 12 and 16 resulted in a Reactor Protection System trip. All withdrawn control blades inserted normally. The mode switch was placed in SHUTDOWN and the trip was reset. The Intermediate Range Monitor High-High signal was caused by flux redistribution which was not accounted for in Operator guidance. Operator guidance provided by the Nuclear Engineers now accounts for flux redistribution.
2631991004 | Monticello | 03/15/1991 | 04/12/1991 | ML11311135 | <strong>Failed 4kv Breaker Could Have Disabled Low Pressure Coolant Injection</strong><br /><i>Abstract:&nbsp;</i>High resistance contacts in the trip circuit of the 4KV breaker powering the control rod drive pump motor disabled all electrical trips of the breaker. The control rod drive pump motor is non-safety related and a fault on this motor would have tripped essential bus #15. This could have disabled two of four residual heat removal pumps and caused the loss of the low pressure coolant injection subsystem, which requires three residual heat removal pumps for operability. <br /><br /> The causes were failed auxiliary switch contacts on the 4KV breaker and lack of training and procedures to make the operations crew aware of the significance of losing the control room red indicating light. The auxiliary switch was replaced and the 4KV breaker maintenance program upgraded to include cleaning the auxiliary switch contacts. The auxiliary switch contacts in all safety related 4KV breakers powering non-safety related loads will be cleaned during the present refueling outage. This event will be communicated to the industry using Nuclear Network. The operations staff will review this report to heighten awareness of this event and plant operating procedures have been revised to provide operators with instructions for this condition.
2631991005 | Monticello | 04/01/1991 | 05/01/1991 | ML113111361 | <strong>Primary Containment Isolation Valves LLRT Exceeded</strong><br /><i>Abstract:&nbsp;</i>
2631991006 | Monticello | 04/17/1991 | 05/17/1991 | ML11311136 | <strong>Inadequate Procedures When Restoring Power to Emergency Filtration Train Result in Unplanned Transfer to High Radiation Mode</strong><br /><i>Abstract:&nbsp;</i>With the plant shutdown for a refueling outage, operations personnel attempted to start an air compressor on a circuit breaker temporarily supplying power to a motor control center. The starting current associated with this load was sufficient to trip the temporary breaker. This resulted in the loss of power to the "A" train of the Emergency Filtration Train and loss of normal control room ventilation. Upon restoring power to "A" train, both trains of the system transferred to the High Radiation mode. The transfer of "B" train to the High Radiation mode was not expected and was therefore an unplanned actuation of an Engineered Safety Feature. Both trains were immediately reset and the system was returned to normal. The cause of the event is inadequate procedures. Procedures were revised to inform operations personnel of the effects of restoring power to a train of the Emergency Filtration Train and to provide further guidance for starting loads on the temporary source.
2631991007 | Monticello | 04/19/1991 | 05/20/1991 | ML11311136 | <strong>Personnel Error Causes 4KV Electrical Fault Resulting in Automatic Start of Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage, an electrical fault in 4160 Volt bus 11 switchgear caused the normal offsite power source, 2R Station Transformer, to lockout and transfer plant power to the 1AR Reserve Transformer. The transfer of power automatically started 12 Emergency Diesel Generator. <br /><br /> The cause of the event was personnel error by electric maintenance technicians. While performing bus maintenance, one technician mistakenly entered a breaker cubicle that contained energized stabs from 2R Station Transformer. The technician contacted the energized stabs causing the fault and sustaining severe burns. Corrective actions include conducting safety meetings with all work groups, repairing the damaged switchgear, forming an Investigative Team to formally review this event, and providing training.
2631991008 | Monticello | 04/22/1991 | 05/22/1991 | ML113111412 | <strong>Inadequate Control Rod Drive Cap Screw Design Resulting in Stress Corrosion Cracking Indications</strong><br /><i>Abstract:&nbsp;</i>
2631991009 | Monticello | 04/27/1991 |  | ML113111369 | <strong>Inadequate Control of Construction Activities Causes Failure to Meet Cable Separation Requirements</strong><br /><i>Abstract:&nbsp;</i>
2631991010 | Monticello | 05/07/1991 | 06/06/1991 | ML11311141 | <strong>Spurious Increase of Intermediate Range Monitor Signals Results in Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>With the plant shutdown, the mode switch in the refuel position, and fuel loading in progress, a spurious increase in the signal from Intermediate Range Monitors 14, 16, and 18 resulted in a Reactor Protection System trip. The investigation of the spurious signal increase could not determine the cause. The scram was reset and refueling activities continued. No control blade movement resulted because all operable control blades were fully inserted at the time of the scram.
2631991011 | Monticello | 05/13/1991 | 06/12/1991 | ML11311136 | <strong>Failure of Voltage Regulator Chips in Control Circuitry Causes Containment Combustible Gas Control System Inoperability</strong><br /><i>Abstract:&nbsp;</i>While testing Containment Combustible Gas Control System during the 1991 Refueling outage both divisions of the system were determined to be inoperable. The Combustible Gas Control System was not required to be operable while the plant was in cold shutdown, but the condition could have prevented the system from performing its function while at power. <br /><br /> Set points for several instrument channels had drifted, which would have prevented both divisions of the Combustible Gas Control System from reaching the temperature required for the recombination of oxygen and hydrogen present in the primary containment atmosphere after a loss of coolant accident. The root cause of the problem was the failure of a voltage regulator chip for circuit boards which comprise each instrument channel. <br /><br /> The problem was corrected by repairing the affected instrument channels. After the repairs, all of the affected instrument channels were tested with satisfactory results. To prevent recurrence, procedures used to calibrate and operate the system will be revised to include checks to detect similar failures.
2631991012 | Monticello | 05/24/1991 | 06/21/1991 | ML113111367 | <strong>Improper Fuse Setting and Wire Error Causes Unplanned Emergency Filtration Train Actuation</strong><br /><i>Abstract:&nbsp;</i>
2631991013 | Monticello | 06/01/1991 | 07/01/1991 | 9107050123 | <strong>Insufficient Maintenance Of Reactor Protection System Monitor Generator Set Overvoltage Relay Causes Standby Gas Initiation And Reactor Building Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1991, with the plant operating at 90% power, a partial Group II isolation and Standby Gas Treatment System initiation occurred. This was the result of loss of power to the channel "A" Spent Fuel Pool and Reactor Building Exhaust Plenum Radiation Monitors due to the inadvertent trip of the "A" Reactor Protection System motor generator set. The isolation and Standby Gas Treatment system initiation were unplanned actuations of Engineered Safety Features. Power was immediately restored to the "A" Reactor Protection System bus from an alternate source. The Partial Group II isolation was reset and the Standby Gas Treatment System was placed back in standby. The cause of the motor generator set trip was determined to be inadequate maintenance of the generator set's overvoltage relay. The overvoltage relay setpoint was later re-calibrated and the generator set returned to service. The overvoltage relay for the "B" motor generator set will also be re-calibrated. The need for further motor generator set component maintenance will be evaluated. Transfer of the Radiation Monitors to a more reliable power supply will be investigated.
2631991014 | Monticello | 06/05/1991 | 07/05/1991 | ML11311137 | <strong>Spurious Signal Causes Main Steam Isolation and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>A reactor scram occurred from 100% power due to a spurious Main Steam isolation signal occurring in the A channel while the B channel was tripped in accordance with an approved surveillance procedure which was in progress at the time. Normal post-scram recovery procedures were followed. Investigative efforts to determine the source of the signal did not identify the root cause. After the safety aspects of the occurrence were examined and found to be acceptable, the plant was restarted with data gathering instrumentation in place to give better resolution in the event of a recurrence. Plant Instrument and Control personnel were reminded that passive preparation work should never go beyond the channel that is currently tripped. A Technical Specification revision is being pursued which will minimize the time channels are tripped during surveillance procedures. Improvements are being considered for the sensor relay inputs to the plant computer.
2631991015 | Monticello | 06/06/1991 | 07/08/1991 | ML11311137 | <strong>A Failure to Adequately Monitor and Analyze the Trends of the Intermediate Range Monitor Recorder Traces Results in a Reactor Protection System Trip.</strong><br /><i>Abstract:&nbsp;</i>With reactor shutdown in progress (the mode switch in STARTUP), high-high signals from Intermediate Range Monitors 12 and 16 resulted in a Reactor Protection System trip. All withdrawn control blades inserted normally. The mode switch was placed in SHUTDOWN and the trip was reset. The Intermediate Range Monitor high-high signals were caused by cooldown due to a lack of decay heat. The root cause of the event was a failure to adequately monitor and analyze the trends of the Intermediate Range Monitor recorder traces. Corrective actions include re-focusing on control room personnel responsibilities during power transitions, simulator training with low decay heat scenarios, and improved guidance to Operations for low decay heat situations.
2631991016 | Monticello | 06/13/1991 | 07/15/1991 | ML113111375 | <strong>Inadequate Design of Emergency Service Water Discharge Header Results in Potential for Loss of Control Room Cooling</strong><br /><i>Abstract:&nbsp;</i>
2631991017 | Monticello | 08/15/1991 | 09/16/1991 | ML113111377 | <strong>Inoperable Fire Barrier Penetration Seal Due to Failure to Identify Penetration as a Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>
2631991018 | Monticello | 08/23/1991 | 12/04/1991 | ML113111384 | <strong>Due to Non-Conservative Assumptions in the Internal Flooding Analysis a Break in the Plant Service Water System may have Resulted in a Loss of Redundant Trains of Safety Related Equipment</strong><br /><i>Abstract:&nbsp;</i>
2631991019 | Monticello | 08/25/1991 | 09/24/1991 | ML11311137 | <strong>Failed Insulator on 115KV Line Causes Loss of Normal Electrical Power Resulting in Reactor Scram and ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>At 0609 hours on August 25, 1991 while operating at 100% power, an interruption in off-site power resulted in a reactor scram and actuated several Engineered Safety Feature systems. The cause of the event was a failed insulator on the 115KV line supplying the Station Reserve Transformer. The event occurred during a lightning storm and it is suspected that the insulator failure was caused by a lightning strike. The failed insulator caused a lock-out of the Station Reserve Transformer, resulting in an interruption of normal electrical power to all plant 4KV busses and a reactor scram. The essential busses were automatically reenergized from the Auxiliary Reserve Transformer in about 5 seconds as designed. All Engineered Safety Features operated as designed. Procedures were used to place the plant in a stable condition. The plant was restarted after all insulators on the affected 115KV tower were replaced, insulators on remaining 115KV towers were inspected, and protective relaying was functionally checked.
2631991020 | Monticello | 08/27/1991 | 09/26/1991 | ML11311138 | <strong>Inadequate Design and Procedures Related to Ventilation Systems Could Cause a Potential Failure of Safety Related Electrical Equipment</strong><br /><i>Abstract:&nbsp;</i>During a review prompted by a concern at another utility, it was determined that a sustained loss of ventilation may cause electrical equipment required for safe shutdown to become inoperable during normal operation or a design basis event. Loss of ventilation events were not considered in the original design and procedures were not developed to insure adequate compensatory measures were taken. <br /><br /> Actions were taken to: place thermometers in the areas of concern; locally pre-stage portable ventilation equipment; and revise the operating procedures. Tests were performed to confirm engineering analysis that the compensatory measures implemented would insure equipment operability for safe shutdown and long term decay beat removal. <br /><br /> Additional testing will be performed at higher outside air temperatures. Evaluation of equipment qualifications at higher temperatures is continuing.
2631991021 | Monticello | 09/30/1991 | 10/30/1991 | ML11311138 | <strong>Inoperable fire Penetration Due to Pipe Movement Resulting From Possible Water Hammer</strong><br /><i>Abstract:&nbsp;</i>While conducting a Radiation Protection survey, Health Physics personnel discovered a pipe penetration which did not appear to be properly sealed. The Fire Protection Engineer was notified. The engineer determined that the penetration was in a fire barrier and was not properly sealed. The penetration was declared inoperable and a one hour roving fire watch was established. The penetration was inspected, sealed, and returned to operable status. <br /><br /> The postulated cause of the event is pipe movement due to possible water hammer. This occurred as a result of a momentary loss of power to the Condensate Service pumps on August 25, 1991. It is believed that the August event caused the failure of the penetration since the penetration was inspected in May 1991 and determined to be sealed. <br /><br /> System improvements to ensure long term fire barrier integrity will be investigated. Interim any inspections of this penetration seal will be performed following an identified water hammer events in the condensate service system.
2651991001 | Quad Cities 2, Quad Cities 1 | 01/02/1991 | 01/30/1991 | 9102060187 | <strong>HPCI Declared INOP Due To MO 2-2301-5, Significant Valve Packing Leak</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1991, at 0143 hours, Unit Two was in the RUN mode at 92 percent rated core thermal power. While on rounds, an Equipment Attendant (EA) discovered a severe packing leak on the High Pressure Coolant Injection (HPCI) Turbine TRB! Steam Supply Isolation Motor Operated (MO) valve ISV! 2-2301-5. The Nuclear Station operator (NSO) closed the valve. HPCI was declared inoperable and an Outage Report was initiated. Mechanical Maintenance (MM) replaced the packing on the valve and determined a steam cut in the valve stem had worn the packing away. At 2005 hours, January 3, 1991, the HPCI MO-2-2301-5 valve was successfully tested and declared operable. The outage report was terminated. Corrective actions include repairing and/or replacing the valve stem. <br /><br /> NRC notification of the event via the Emergency Notification System (ENS) phone was made at 0407 hours, January 2, 1991, to comply with the requirements of 10CFR50.72(b)(2)(iii)(D). <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(V)(D).
2651991002 | Quad Cities 2 | 01/19/1991 | 02/16/1991 | 9102250314 | <strong>High Pressure Coolant Injection Steam Exhaust Check Valve Excessive Leakage Due To Degradation of Valve Seat</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1991, at 1230 hours, Unit Two was in the SHUTDOWN mode at 0.0 percent of rated thermal power. A local leak rate test (LLRT) was performed on the High Pressure Coolant Injection BJ! (HPCI) steam exhaust check valve NH! ISV! 2-2301-45. The valve failed the LLRT with a leakage of 249.4 standard cubic feet per hour (SCFH). This put the combined leakage rate for all penetrations PEN! and valves V! except Main Steam Isolation Valves SV, ISV! (MSIV) above the limit of 0.60 La (293.75 SCFH) as required by Technical Specifiction 3.7.A.2.a.2. <br /><br /> The excessive leakage of the HPCI steam exhaust check valve was caused by degradation of the Nordel elastomer valve seat. It appears that as the check valve cycled open and closed, the edge of the valve disks wore against the raised ribs on the seat causing gaps between the seat and disks. Repeated cycling of the check valve occurs during low speed operation of the HPCI turbine.<br /><br /> The steam exhaust check valve was replaced with a new check valve with several design improvements. The HPCI surveillance procedure was changed to avoid operating the turbine at low speed for extended periods. A modification is under development to take advantage of a water seal on the HPCI steam exhaust line. The test interval for the valve has been changed to six months.
2651991003 | Quad Cities 2 | 01/22/1991 | 02/20/1991 | 9102260146 | <strong>HPCI Turbine on Fast Start-Up From Low Pump Suction</strong><br /><i>Abstract:&nbsp;</i>At 1730 hours on January 22, 1991, Unit Two was in the RUN mode at 10 percent rated core thermal power. The Unit Two Nuclear Station Operator (NSO) was performing High Pressure Coolant Injection (HPCI) Quarterly Pump Operability Test QCOS 2300-5 when the HPCI turbine tripped unexpectedly during the fast start portion of the test. The NSO repeated that portion of the test successfully. <br /><br /> At 1937 hours, the NSO repeated QCOS 2300-5, and the HPCI turbine again tripped the first time. The Shift Engineer (SE) declared HPCI inoperable retroactive to 1730 hours. <br /><br /> NRC notification of the event via the Emergency Notification System (ENS) phone was made at 2036 hours, January 22, 1991, to comply with requirements of 10CFR50.72(b)(2)(iii)(D). <br /><br /> A strip chart recorder was connected to monitor the output signals of local pressure transmitters, and HPCI turbine was fast started again with the same results. <br /><br /> Further investigation indicated that a brief low pump suction pressure transient occurred on fast startup of the turbine while performing new HPCI test procedures. HPCI was successfully tested following the removal of the low pump suction trip. At 2205 hours, January 27, 1991, HPCI was declared operable. Corrective Actions include installing a time-delayed relay on Units One and Two to eliminate sporadic trips due to pressure transients during initial startup.
2651991004 | Quad Cities 2, Quad Cities 1 | 02/11/1991 | 03/08/1991 | 9103130068 | <strong>Both Units SBLC Declared Inop Due to Inadequate Testing and Calculation of Pump NPSH</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1991, at 1320 hours, Unit One was in the SHUTDOWN mode, and Unit Two was in the RUN mode at 86 percent of rated core thermal power. During the performance of a special test on Unit One to determine the available Net Positive Suction Head (NPSH) of the Standby Liquid Control (SBLC) pumps, the pumps began to cavitate unexpectedly. The SBLC systems of both units were declared inoperable and a 24 hour Limiting Condition of Operation (LCO) was entered for Unit Two, until the ability of the pumps to fulfill their design function was proven. <br /><br /> On February 12, 1991, at 0900 hours, upon approval of an evaluation of the system, administrative controls were placed on the tank level and temperature to ensure adequate NPSH was available, and one pump on each unit was declared operable. This put Unit Two in a seven day LCO. <br /><br /> On February 14, 1991, a second evaluation, which verified the ability of SBLC to perform properly during two pump operation, was approved. The SBLC systems for both units were subsequently declared fully operable, and the LCO terminated. <br /><br /> The causes of this event are inadequate modification testing and an error in the original design calculations. Corrective actions included analysis of test data and administrative controls to assure adequate NPSH was available to the pumps. Additional testing will be performed to further demonstrate the adequacy of the pumps.
2651991006 | Quad Cities 2 | 04/20/1991 | 05/16/1991 | 9105280064 | <strong>HPCI Pump Operability Test Fell Into IST Required Action Range Due to Unknown Causes</strong><br /><i>Abstract:&nbsp;</i>At 1355 hours on April 20, 1991, Unit Two was in the RUN mode at 10 percent rated reactor core thermal power. While performing QCOS 2300-5, High Pressure Coolant Injection (HPCI) Pump Operability Test, the system failed to meet the Inservice Testing (IST) Pump Surveillance Acceptance Criteria portion of the test. An operability evaluation was completed and approved. Subsequently, HPCI was declared operable. <br /><br /> The cause of this event was due to an inadequate procedure that led to inconsistent data which caused HPCI to fall into the IST required action range. <br /><br /> The IST turbine speed requirements will be changed in QCOS 2300-5 to allow the turbine speed to be set at both the Motor Gear Unit and Motor Speed Changer high speed stops. This change will assist operations in setting consistent test conditions which will result in accurate test data that complies with both Technical Specifications and ASME Section XI. <br /><br /> Also, a new type of throttling valve will be installed which will help the operator in setting the pump discharge pressure more consistently. <br /><br /> This report is being submitted in accordance with 10CFR50.72(b)(2)(iii)(D).
2651991007 | Quad Cities 2 | 07/13/1991 | 08/09/1991 | 9108220199 | <strong>Reactor Water Low Level Scram Due to 2B Feedwater Regulating Valve Failing to Full Close.</strong><br /><i>Abstract:&nbsp;</i>
2651991008 | Quad Cities 2 | 07/23/1991 | 08/22/1991 | 9108300094 | <strong>Closure of AO-2-220-45 Due To Defective Connections in the Control Circuitry.</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1991 at 1027 hours, Unit Two was in the RUN mode at 100% rated core thermal power. On July 30, 1991 at 0905 hours, Unit Two was in the RUN mode at 95% rated core thermal power. At these times, the outboard Recirculation Sample Valve AO-2-220-45 closed with no apparent signal. This valve is part of Group I Primary Containment Isolation.<br /><br /> Corrective actions included fuse verification and an inspection of all terminations associated with the valve control circuitry. <br /><br /> The causes of these events were loose connections in the control circuitry of the valve. Cable movement during wiring verifications inadvertently caused valve closure into the safe position. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv).
2651991009 | Quad Cities 2 | 08/17/1991 | 09/12/1991 | 9109190227 | <strong>Failure of the Core Spray Room Drain Check Valves Due to Foreign Material Becoming Lodged in Check Valves</strong><br /><i>Abstract:&nbsp;</i>At 0510 hours on August 17, 1991, Unit Two was in the Run mode at 87 percent of rated core thermal power. <br /><br /> At 0510 hours, the station entered Technical Specification 3.5.A.6 due to the 2A and 2B Core Spray Room check valves leaking by and failing the quarterly surveillance testing. <br /><br /> At 0530 hours a floor drain plug was installed in each drain line for flood protection. Operations initiated a twice per shift surveillance of both 2A and 2B Core Spray Rooms until the valves were returned to service.<br /><br /> Corrective actions included installing drain line plugs, and performing a twice per shift surveillance of these rooms until maintenance could determine the cause and correct the problem. Work Requests Q94776 and Q94777 were written to investigate and correct the cause of the leakage by the valves. Foreign material had become lodged in the valves and was removed. The 2A Core Spray Room check valve was returned to service at 1330 hours on August 18, 1991 and the 2B Core Spray Room check valve was returned to service at 2045 hours on August 18, 1991. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(v)(D).
2651991010 | Quad Cities 2 | 09/07/1991 | 09/27/1991 | 9110080186 | <strong>HPCI Inop Due To Broken Room Cooler Belts</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1991 at 2300 hours, Unit Two was in the run mode at 91% of rated core thermal power. On September 7, 1991 it was discovered by the Unit Two operator, while completing QOS 005-S14, that the belt for the High Pressure Coolant Injection System (HPCI) BJ! Room Cooler w s broken. At 2353 hours the HPCI system was declared inoperable in accordance with Technical Specification 3.5.C.3. On September 8, 1991 at 0024 hours the four hour Emergency Notification System (ENS) phone call was made. Work Request Q95024 was written to replace the belt. On September 8, 1991 at 1338 hours HPCI was declared operable. <br /><br /> This event is being reported as a voluntary LER.<br /><br /> The corrective actions are to have the Tech Staff Systems Engineer look into replacing the current belt guards with mesh covered belt guards. The Station's Technical Specification Interpretation Book will be revised to address the Nuclear Fuel Services (NSF) study and how it affects the operability of safety systems.
2651991011 | Quad Cities 2 | 10/15/1991 | 11/08/1991 | 9111190188 | <strong>Unit Two HPCI Declared Inoperable Due To Failure Of Gland Seal Hotwell Pump Caused By High Seal Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1991, at 1304 hours, Unit Two was in the RUN mode at 88 percent of rated core thermal power. At this time, the High Pressure Coolant Injection (HPCI) Gland Seal Hotwell Pump was observed to be cycling on and off. The HPCI system was declared inoperable after further investigation and a HPCI System Outage Report was initiated. <br /><br /> October 15, 1991 at 1442 hours, an Emergency Notification System (ENS) phone notification was completed as required by 10CFR50.72(b)(2)(iii)(D). <br /><br /> At 1125 hours on October 16, 1991, Electrical Maintenance (EM) had discovered the High Level switch for the HPCI Gland Seal Hotwell Pump had slipped out of the C-clip. The switch was repaired and the system was successfully tested. Corrective Actions include the continuation of the inspection and preventive actions documented in LER 2-90-009. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(v)(D).
2651991012 | Quad Cities 2 | 10/07/1991 | 11/05/1991 | 9111140183 | <strong>Inadvertent Opening Of Electromatic Relief Valve 2-203-3C Due To Binding In The Pilot Valve Assembly.</strong><br /><i>Abstract:&nbsp;</i>At 0223 hours on October 7th, 1991, Unit Two was in the Startup mode at 1 percent rated reactor core thermal power. When the reactor RCT! RPV! reached approximately 63 psig, a spurious actuation of Electromatic Relief Valve (ERV) RV! 2-203-3C occurred. At 0253 hours, Unit Two was manually scrammed and cooldown was initiated. Later, when a Drywell entry was made, the pilot valve V! for the 2-203-3C was found stuck open. <br /><br /> The cause of this event was binding of the pilot valve for the 2-203-3C ERV. The Mechanical Maintenance Department replaced the pilot valve internals for each ERV as a precautionary measure. On October 7th 1991, at 1912 hours, the ERV's were stroked manually and tested successfully. Unit Two startup was initiated at 2054 hours on October 7th, 1991. QCOS 203-3, Main Steam Valves Operability Test, was performed on October 8th, 1991 at 1020 hours, and the ERV declared operable. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(iv).
2651991013 | Quad Cities 2 | 08/19/1991 | 11/14/1991 | 9111210050 | <strong>Entering EGC Without Performing Required Surveillance Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1991, Quad Cities Unit Two was in the RUN mode at 95% of rated core thermal power. At 0730 hours, the Nuclear Station Operator (NSO) placed the unit into Economic Generation Control (EGC) without performing the required surveillances to comply with Technical Specification 4.3.F. <br /><br /> An investigation revealed that the cause for this event was personnel error. The NSO did not follow Quad Cities Station operating procedures for EGC operation. Upon identification of the error, the Shift Control Room Engineer (SCRE) instructed the NSO to trip the unit out of EGC. Subsequent actions will include training on EGC operation for all the NSOs, as well as additional training for the NSO who was involved in the event. This report is provided to satisfy the requirements of 10CFR50.73 (a)(2)(i)(b).
2651991014 | Quad Cities 2 | 12/18/1991 | 01/16/1992 | 9201270338 | <strong>2A RHR Heat Exchanger Support Beams Found To Be Outside Basis During Lifting Due To Notches In The Flange Area.</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1991, at 0810 hours Unit Two was in the RUN Mode at 66 percent of rated core thermal power. At this time the station was notified by Engineering of an analysis which determined that two beams supporting the 2A Residual Heat Removal HR) BO! Heat Exchanger HX! exceeded Final Safety Analysis Report (FSAR) allowable limits. This over stressed condition was due to notches which had been cut in the beam flanges. <br /><br /> Engineering examined the degraded support beams, and determined that no excessive deformation or deflection existed. It was determined that the degradation did not diminish the operability of the heat exchanger or the RHR system. <br /><br /> Work Request Q96769 was initiated to reinforce the degraded support beams. This work will insure that the supports are within the FSAR allowable design limits. The reinforcement of the beams will be performed during the Unit Two refuel outage, January 1992 (Q2R11).
2651991015 | Quad Cities 2 | 12/24/1991 | 01/18/1992 | 9201310221 | <strong>U2 Rx Bldg Vent Isolation During Return to Service Verification</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1991 at 0445 hours Unit Two was in the Run mode at 65% of rated core thermal power. While performing a Return to Service verification on Out of Service 3639, the Unit 2 Equipment Operator (EO) inadvertently removed fuse F-3 and a white plastic fuse holder obstructing view of the fuse, from the 2252-24X panel, Unit Two (U2) Reactor (Rx) Building (Bldg) Vent Control Panel. The fuse removal caused the U2 Rx Bldg Vent Isolation Dampers to fail close and tripped the supply and exhaust fans. <br /><br /> The immediate corrective actions was to notify the Control Room of the event and reinstall the fuse. The Return to Service was completed and the U2 Rx Bldg Vents turned back on. Further corrective actions will be to remove the white plastic fuse holders completely. <br /><br /> The apparent cause of the event was a design deficiency from a human factors standpoint. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(iv).
2651991016 | Quad Cities 2, Quad Cities 1 | 12/27/1991 | 01/23/1992 | 9201290028 | <strong>Design Discrepancy Between FSAR and As-Built for TIP Ball Valves</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1991, at 1600 hours, Unit Two was in the RUN mode at 63% of rated core thermal power. At this time, Technical Staff Engineers performed a walkdown of the Traversing Incore Probe (TIP) system and discovered that the 902-3, A-16 and 901-3 F-8 annunciators would be activated by loss of power or shear valve actuation and not by a ball valve ISV! open with Group II isolation signal present as stated in the Updated Final Safety Analysis Report (UFSAR) Section 7.4.5.4. Further reviews did not reveal any adverse effect on the operation of the TIP ball valves with a Group II isolation signal present. The discrepancy resulted from failure to reconcile the UFSAR with the as-built condition. The UFSAR will be changed to reflect the as-built condition. This report is provided to satisfy the requirements of 10CFR50.73(a)(2)(ii)(b).
2661991001 | Point Beach 1, Point Beach 2 | 04/05/1991 | 05/06/1991 | 9105090353 | <strong>Minimum AFW Flow for Automatic Actuation to Both Units</strong><br /><i>Abstract:&nbsp;</i>During the evaluation of a Quality Assurance Audit Finding Report, it was discovered that, under the circumstances of a loss of off-site power to both units resulting in a loss of normal feedwater (which results in the simultaneous initiation of auxiliary feedwater in both units), coincident with the failure of the turbine-driven auxiliary feedwater (AFW) pump in one unit, the AFW system may be incapable of providing automatic feedwater flow to one of the units without operator intervention. The accident analysis in FSAR Section 14.1.11, "Loss of All AC Power to the Station Auxiliaries," assumes the AFW system is capable of providing at least 100 gpm to each steam generator coincident with a single active failure. This event is reported pursuant to 10 CFR 50.73 (a) (2) (v) and (vi).
2661991002 | Point Beach 1 | 04/19/1991 | 05/17/1991 | 9105280190 | <strong>Degradation of Steam Generator Tubes</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was shut down for Refueling 18 on April 6, 1991. Eddy current examination of the steam generator tubes began on April 13, 1991 and was completed on April 18, 1991 using the digital multi-frequency eddy current system. Inspection results in the 'A' steam generator hot leg showed one tube degraded >/=40%. This tube was then plugged.<br /><br /> In the 'B' steam gen rator, one tube showed indications up to 38% degradation. This tube was plugged as a preventative measure. <br /><br /> Inspections of each steam generator tube bundle were performed using remote video equipment. The condition of the tubes at all inspected locations was very good. Boiler scale was detected throughout the steam generators (as was expected) and a sample was removed for examination.
2661991003 | Point Beach 1 | 04/29/1991 | 05/21/1991 | 9105300234 | <strong>Containment Isolation Valve Leakage In Excess Of Tech Spec Limits</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1991, during Appendix J, Type C containment leak rate testing, charging system check valve 1-370 was discovered with leakage in excess of limits cited in Technical Specifications 15.4.4.II.B and 15.4.4.III.B. In this case, the required test pressure could not be achieved; therefore, a leak for design basis conditions could not be quantified.<br /><br /> The valve was repaired, tested and restored to operation. This report is filed pursuant to 10 CFR 50.73 (a) (2) (i), "Any operation or condition prohibited by the plant's Technical Specifications."
2661991004 | Point Beach 1 | 05/10/1991 | 09/16/1991 | 9109230051 | <strong>Primary Temperature > 200 Degrees Without Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1991, steam generator crevice flushing was being performed on the Point Beach Nuclear Plant Unit 1 steam generators while the unit was shutdown. During this evolution, primary system temperatures exceeded 200 degrees F as indicated by residual heat removal (RHR) heat exchanger inlet temperature for approximately 17 minutes with a peak temperature of 201 degrees F. During this time, containment integrity was not set as required by Technical Specification 15.3.6.A.a. Immediate corrective action consisted of cooling the primary system to less than 200 degrees F using the RHR system.
2661991005 | Point Beach 1 | 05/30/1991 | 06/28/1991 | 9107020427 | <strong>Loss of Instrument Bus Resulting in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1991, the Point Beach Nuclear Plant Unit 1 was operating at 100% power. At 1146, power to the Unit 1 red instrument bus was lost due to the failure of the inverter (1DY01) supplying the bus. This resulted in a reactor trip. However, loss of power to the bus does not directly cause a trip. The Plant Process Computer System (PPCS) sequence of event recorder did not indicate the exact cause of the trip. Start-up tests were performed and all results were satisfactory. <br /><br /> The instrument bus was transferred to the spare inverter and Unit 1 was started up and returned on line at 0047 on May 31, 1991. 1DY01 was subsequently repaired, tested, and returned to service supplying the Unit 1 red instrument bus.
2661991006 | Point Beach 1, Point Beach 2 | 06/15/1991 | 07/15/1991 | 9107190049 | <strong>Inadvertent Start of Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1991 emergency diesel generator G01 received a spurious fast start signal when an operator opened the generator's annunciator panel. The operator had difficulties opening the door, and when sufficient force was applied, relays were disturbed as the door opened. Subsequently, diesel generator G01 fast started, the "START FAILURE" alarm annunciated locally and the "DIESEL GENERATOR G01 STARTING SYSTEM DISABLED" alarm annunciated in the control room. G01 shutdown and examination was accomplished, and the generator's operation was declared normal. Because this event is an actuation of Engineered Safeguards Features (ESF) equipment, a four hour notification to the NRC was made in accordance with 10 CFR 50.72 (b) (2) (ii).
2661991007 | Point Beach 1, Point Beach 2 | 06/26/1991 | 07/26/1991 | 9107300239 | <strong>Inoperable Fire Barrier Penetration Seals</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1991, holes were discovered in two fire barrier penetration seals in the walls of the Safety Injection - Containment Spray pump room. The openings measured approximately six by twelve inches in one and six by fifteen inches in the other. PBNP Technical Specification (TS) 15.3.14.C.1.a requires all fire barrier penetration seals protecting safety-related areas to be operable. <br /><br /> The barriers had been opened and temporarily sealed in preparation for an electrical conduit installation. Contrary to PBNP Procedure 3.4.11, "Penetrating Barriers," the temporary Fiberfrax-Durablanket barriers were not reinstalled following the conduit installation. The condition was discovered when the seal installer contractor returned to permanently repair the penetrations.<br /><br /> The contractor provided a fire watch in the area while both barriers were made operable. Both seals have been permanently repaired. All similar barriers disturbed as part of the same installation were inspected and found to be operable. The PBNP engineer responsible for fire barrier penetration seals has reviewed the requirements for working on these components with the personnel responsible for the conduit installation.
2661991008 | Point Beach 1 | 06/29/1991 | 07/29/1991 | 9108010295 | <strong>Unit 1 Reactor Trip on Loss of 1-DY03 White Inverter</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1991, while operating at 100% power, an automatic reactor trip occurred on Unit 1 at 6:38 P.M. The reactor trip was caused by the loss of power from 1DY03, the inverter supplying power to the "white" instrument bus. The loss of power to this bus resulted in a steam flow to feed flow mismatch coincident with a low steam generator water level on the "B" steam generator, resulting in a reactor trip. <br /><br /> The instrument bus was transferred to the spare inverter, DY0C, and Unit 1 was started up and returned to service at 11:52 a.m. on June 30, 1991. Full power was achieved at 2:15 a.m. on July 1, 1991. Currently, power to the "white" instrument bus is being supplied by the spare inverter.
2661991009 | Point Beach 1 | 07/27/1991 | 08/26/1991 | 9108300112 | <strong>Nuclear Instrumentation Turbine Runback</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1991 at 2231, while Unit 1 was operating at 100% power, a 20% runback of the Unit 1 turbine generator was initiated by a power range channel output transient. This channel of nuclear instrumentation was subsequently removed from service for testing by Instrumentation and Control personnel. After thorough examination, the detector was declared operable and returned to service. This event is an actuation of a reactor protection system. A four hour notification to the NRC was made in accordance with 10 CFR 50.72 (b)(2)(ii).
2661991010 | Point Beach 1, Point Beach 2 | 08/16/1991 | 09/16/1991 | 9109200330 | <strong>Four Hydrogen Monitors Found with Default Calibration Parameters During ICP 13.2</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1991, while operating at 100% power, and conducting Instrumentation and Control Procedure (ICP) 13.2, "Calibration Procedure, Containment Hydrogen Monitors," the technician performing the test determined that the four hydrogen monitor channels powered from the "white" instrument bus contained their default calibration parameters. The technician immediately corrected this problem by inserting the proper calibration parameters, restoring these four channels to proper operation. <br /><br /> Review of this event revealed that these four monitors were only capable of indicating 48% to 80% of actual hydrogen concentration with the default calibration parameters inserted. It was also determined that these default calibration parameters were inserted into the four monitors when their associated microprocessor was reinitialized following a momentary loss of power to the "white" instrument bus that occurred on June 29, 1991. For this reason these monitors could not be considered operable subsequent to June 29, 1991. This resulted in a violation of the Technical specifications requirements in Table 15.3.5-5 Item 10 for both Units 1 and 2.
2661991011 | Point Beach 1 | 09/06/1991 | 10/04/1991 | 9110150252 | <strong>Nuclear Instrumentation Turbine Runback</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1991 at 0818, Unit 1 experienced a turbine runback from 100% to approximately 80% power during Reactor Protection System (RPS) logic testing of the power range high setpoint. The runback was caused by an output transient on power range channel N41.<br /><br /> The RPS logic test was immediately halted when the runback occurred. Because the output transient was believed to be attributed to the RPS logic testing, the rod drop circuitry was placed in "bypass" and the test was resumed. All instrumentation and control systems operated as designed. Unit 1 was returned to full power at 0954. This event is an actuation of a reactor protection system. Therefore, a four hour notification to the NRC was made in accordance with 10 CFR 50.72 (b)(2)(ii).
2661991012 | Point Beach 1 | 09/24/1991 | 11/27/1991 | 9112040021 | <strong>Nuclear Instrumentation Turbine Runback</strong><br /><i>Abstract:&nbsp;</i>At 1027 on September 24, 1991 unit i experienced a turbine runback from 100% to approximately 80% power during maintenance on inverter DY0D. The runback was caused by a voltage loss on instrument buses 1Y04 and 1Y104 when the supply breaker from DC bus D04 to inverter DY0D was closed. Prior to this event, swing inverter DY0D (Elgar Model 253-1-103) had been taken out of service for maintenance. The turbine runback occurred when the D04 to DY0D supply breaker was closed while bringing the inverter back into service. The input circuit breaker filter capacitors to inverter DY0D had not been charged prior to attempted closure. The uncharged capacitors caused a voltage spike to occur on the DC supply bus to inverter 1DY04 (bus D04). This voltage spike scrambled the inverter's logic, blowing a fuse and shutting down inverter 1DY04. Also, the uncharged capacitor created an excessive current draw on inverter DY0D, causing the DC supply breaker to trip on overcurrent. Power to yellow instrument buses 1Y04 and 1Y104, which was being supplied by inverter 1DY04, was subsequently lost. This loss of power produced a negative voltage spike on nuclear instrument channel N44, activating the dropped rod turbine runback circuitry. All instrumentation and control systems operated as designed. Unit 1 was returned to full power at 1257. This event is an actuation of a reactor protection system. Therefore, a four-hour notification to the NRC was made in accordance with 10CFR50.72 (b) (2) (ii).
2661991013 | Point Beach 1 | 10/03/1991 | 11/01/1991 | 9111070001 | <strong>Nuclear Instrumentation Turbine Runback Caused by a Voltage Spike on Power Range Channel N44.</strong><br /><i>Abstract:&nbsp;</i>At 1917 on October 3, 1991, while Unit 1 was operating at 100% power, a 20% runback of the turbine generator occurred. This runback was caused by an output transient on Power Range Nuclear Instrumentation Channel N44. The Reactor Protection System sensed a dropped control rod and initiated the turbine runback. Following the runback, the dropped rod circuit was reset at 1922. The load increase was commenced at 1935. Full power was attained at 2010.
2661991014 | Point Beach 1 | 11/03/1991 | 11/27/1991 | 9112040123 | <strong>Nuclear Instrumentation Turbine Runback Caused by a Voltage Spike on Power Range Channel N44</strong><br /><i>Abstract:&nbsp;</i>At 1140 on November 3, 1991, while Unit 1 was operating at 100% power, a 20% runback of the turbine generator occurred. This runback was caused by an output transient on Power Range Nuclear Instrumentation Channel N44. The Reactor Protection System sensed a dropped control rod and initiated the turbine runback. Following the runback, the load increase was commenced at 1145. Full power was attained at 1228.
2661991015 | Point Beach 1 | 11/27/1991 | 01/23/1992 | 9201290068 | <strong>"A" Steam Generator Main Steam Isolation Bypass Valve Left Open</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1991, Unit 1 was in hot shutdown; and Operating Procedure OP-13B, "Secondary Systems Shutdown," was in progress. This procedure was being performed in order to conduct a condenser inspection following a 17 gallon per minute condenser tube leak. After shutting both main steam isolation valves (MSIV), per the procedure, the operators noticed that the main steam header was still pressurized to approximately 200 psig. An investigation revealed that 1MS-234, the main steam isolation bypass valve for the "A" steam generator, was open. The valve was immediately shut, correcting the problem.
2691991001 | Oconee 1, Oconee 2, Oconee 3 | 01/08/1991 | 02/07/1991 | 9102150098 | <strong>Potential Single Failure During a LOCA/LOOP Event May Result in The Loss of Emergency Power Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1991, at 10:00 hours, while all three Oconee Units were at 100% full power, it was discovered that a single failure could result in damage to both trains of Oconee's emergency power source resulting in the loss of emergency power during a postulated Design Basis Event. Keowee Hydro Station, Oconee's Emergency power source, provides power to Oconee by two independent paths, one of which is through air circuit breakers and an underground feeder. The postulated scenario is a Loss of Coolant Accident/Loss of Offsite Power Design Basis Event when one Keowee unit is in operation and the other unit shutdown concurrent with a single failure causing a Keowee air circuit breaker to close, simultaneously connecting the two Keowee generators together. As the idle generator automatically starts due to the emergency signal, the single failure would connect the two generators together while they were out of phase resulting in probable damage to the generators and probable loss of emergency power to Oconee. The damage could also occur, though less likely, if both Keowee generators are idle. The root cause of this event is classified as Design Deficiency, unanticipated interaction of systems. On January 9, 1991, Oconee implemented administrative procedural controls preventing the detrimental effects of this postulated failure.
2691991002 | Oconee 1, Oconee 2, Oconee 3 | 12/07/1990 | 04/03/1991 | 9104120234 | <strong>Licensed Operator Improperly Exempted From Requalification Exam Due To Management Deficiency, Results In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1991, the site Director of Operator Training realized, during review of an exemption letter, that a Senior Reactor Operator (SRO A) had been improperly exempted from a facility administered requalification examination (requal exam). SRO A had been assigned as the Facility Representative for preparation and review of the 1990 NRC administered requal exam. Training and management personnel misapplied a provision that allows preparers of an exam to exempt that exam. SRO A was reassigned to shift duties on Dec 7, 1990. On nine duty shifts he filled positions required by Technical Specifications to be filled by licensed personnel. This affected all three Oconee Units which were operating at 100% Full Power. After discovery, SRO A's license was declared invalid and he was removed from duty until he passed a requal exam. The root cause of this event is Management Deficiency, inadequate policy/directive. The Employee Training and Qualification System Standard authorizing the exemption will be revised.
2691991003 | Oconee 1, Oconee 2, Oconee 3 | 04/11/1991 | 05/13/1991 | 9105210276 | <strong>Technical Inoperability of Oconee Backup Electrical Power Sources Results From Deficiently Designed Circuit Breaker Arrangement of Keowee Hydro Auxiliary Loads</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 12, 1991 at 1350 hours, with all three Oconee units at 100% full power, an ongoing review of breaker and relay trip setpoints by Duke Design Engineering found that a problem with Keowee Hydroelectric Station auxiliary load power distribution equipment made both Keowee units technically inoperable. The two Keowee units serve as an emergency electrical power supply to Oconee. This placed all three Oconee units in a Limiting Condition for Operation (LCO) per Technical Specifications. The Keowee units were removed from service individually and corrective actions initiated which defeated ground fault protective relays, changed overcurrent trip setpoints, or removed from circuitry Keowee auxiliary load breakers. The Keowee units were then declared operable and the Oconee units exited the LCO on April 13, 1991. The root cause was Design Deficiency, unanticipated interaction of components. Design Engineering will continue their review of safety related breaker trip setpoints.
2691991004 | Oconee 1, Oconee 2, Oconee 3 | 05/06/1991 | 06/05/1991 | 9106110260 | <strong>Technical Inoperability of an Emergency Electrical Power Path Due to Incorrect Relay Trip Setpoints Results From Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1991, at approximately 1500 hours with all three Oconee units operating at 100 percent full power, it was discovered during a review of relay setpoints that zone protection differential relays in the 230 KV switchyard were incorrect. The review had been initiated as an action item associated with a Design Basis Document preparation. As a result of subsequent investigations, the Unit 1 startup transformer (CT-1) and the electrical bus which provides an emergency power path to all three units (yellow bus), both of which are required by Technical Specifications, were found to be subject to inadvertent lockouts if a fault occurred on certain non-safety related equipment. At 1800 hours on May 6, 1991, CT-1 was declared technically inoperable. The yellow bus was declared technically inoperable at 1030 hours on May 7, 1991. After correcting the relay setpoints, all emergency power equipment was declared operable on May 7, 1991 at 1740 hours. The root cause of this event was inappropriate action, inattention to detail, on the part of the personnel who calculated the trip setpoints for relay replacement in August, 1987. The review of safety related relay trip setpoints will continue.
2691991005 | Oconee 1, Oconee 2 | 05/09/1991 | 06/13/1991 | 9106240309 | <strong>Incorrect Flow Orifice Orientation Due to Installation Deficiency Causes Reactor Building Spray Trains To be Inoperable During Certain Accident Scenarios</strong><br /><i>Abstract:&nbsp;</i>During Post Modification Testing, in March, 1991, a safety related flow transmitter on the Unit 3 High Pressure Injection (HPI) System was found to be inoperable. During the corrective action to inspect other safety related instrumentation, a flow transmitter orifice was found to be installed backwards in the HPI System. The inspection of all other accessible safety related flow instrumentation has revealed two other occurrences of incorrectly installed orifice plates. On May 9, 1991, with Unit 1 at 100% Full Power, a flow orifice on the '1B' train of the Reactor Building spray (RBS) System was found to be installed improperly, causing the '1B' train to be inoperable. On May 16, 1991, with Unit 2 at 100% Full Power, a flow orifice on the '2B' train of the RBS System was found to be installed improperly, causing the '2B' train to be inoperable. During certain accident scenarios that require RBS to be recirculated from the Reactor Building Emergency Sump, each respective train would be inoperable because the incorrectly installed orifice could result in particle buildup and therefore give inaccurate flow measurements. The actual flow rate would be higher than indicated and therefore could cause RBS pump runout. Both orifices were removed and installed correctly. All other accessible safety related orifices have been inspected and verified to be correctly installed. A search of equipment records indicates that these orifices have been installed incorrectly since the initial installation before unit startup in 1973. The root cause is Installation Deficiency, improper installation.
2691991006 | Oconee 1 | 05/16/1991 | 10/29/1991 | 9111070160 | <strong>Unit Trip for Unknown Reason, Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1991, at 1507 hours, Unit 1 tripped from 100 % Full Power, during a thunderstorm. The unit Events Recorder failed immediately prior to the trip, so it is unknown which trip signal was received first. Computer and Chart Recorder outputs indicated that an Instrument and Electrical (I&E) Technician may have erroneously opened the high pressure impulse line isolation valve instead of the low pressure valve on a non-safety related Reactor Coolant System flow transmitter following calibration. This may have caused a momentary dip in the pressure signal to four channels of Reactor Protective System flow instruments which share the impulse lines from the flow element. The pressure dip would have caused a trip on Flux/Flow/Imbalance. Alternatively, the trip could have occurred due to a switchyard transient. Operators took immediate action to stabilize the unit following the trip. The root cause is Unknown, Possible Inappropriate Action. Additional investigation performed during a subsequent Unit 1 refueling outage failed to clarify the cause.
2691991007 | Oconee 1, Oconee 2, Oconee 3 | 05/29/1991 | 06/27/1991 | 9107080056 | <strong>Breaker Coordination Problem Due to Design Deficiency Results in Technical Inoperability of Safety Related Equipment</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1991 at 1015 hours, with all three Oconee units at 100% full power, an ongoing review of breaker and relay trip setpoint by Duke Design Engineering found that a breaker coordination problem existed with motor control centers 1, 2, and 3XS2. On each unit, if an overcurrent condition occurred on a non-safety related panelboard (1, 2, or 3KM) during an emergency situation, the feeder breaker to 1, 2, or 3XS2 could trip open, isolating safety-related loads, before the breaker supplying the panelboard would trip. No such failure has actually occurred. Panelboards 1, 2, and 3KM were rewired to be supplied from a non-safety related motor control center. The root cause was Design Deficiency, unanticipated interaction of components. Design Engineering is continuing their review of safety related breaker and relay setpoints.
2691991008 | Oconee 1, Oconee 2 | 06/12/1991 | 07/10/1991 | 9107190072 | <strong>Inappropriate Actions Cause Breach of Fire Barriers Resulting In Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1991 at approximately 1245 hours, Safety personnel, on a routine plant tour, discovered that a fire barrier had been breached without compensatory actions on Unit 1 from approximately 1730 hours on June 11, 1991 until approximately 0730 hours on June 12, 1991. A Nuclear Station Modification (NSM) was in progress in the immediate area. The craft personnel that had been pulling cables for the NSM had inadvertently left a fire door opened upon leaving the area on the previous day. When this discovery was made on Unit 1, the corresponding fire door on Unit 2 was also inspected and found to be opened and unattended. The craft personnel stated that this door had been closed after work had been completed in this area during the previous week. On June 15, 1991 at approximately 0800 hours, while performing daily rounds, Operations personnel discovered the fire door separating the East and West Penetration Rooms opened and unattended. Upon each discovery of a breached fire barrier, the door was closed and secured or compensatory measures were taken. Both Unit 1 and 2 were operating at 100% Full Power during these events. The root cause of these events is Inappropriate Actions, failure to dhere to policies, directives, or procedures. <br /><br /> Corrective actions for these events include personnel counseling and training to all site personnel emphasizing the importance of fire protection systems.
2691991009 | Oconee 1, Oconee 2, Oconee 3 | 07/03/1991 | 08/02/1991 | 9108130100 | <strong>One of Two Diverse Actuation Systems for Loss of Main Feedwater Mitigation S stems Was Found Inoperable Due to a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1991, all Oconee units were operating at 100 percent full power (FP) when Unit 3 tripped due to a loss of feedwater at 1118 hours. A post-trip review showed that feedwater pump discharge pressure remained slightly above the 750 psig setpoint required to actuate the Emergency Feedwater (EFDW) system, the loss of feedwater Reactor Protective System anticipatory trip, and the ATWS Mitigation Safety Actuation Circuit. This prevented the Technical Specification required systems from receiving one of the two initiation signals when Main Feedwater pumps tripped. EFDW did actuate from the independent signal. The problem was caused by the D heater drain pumps (HDP) charging the closed feedwater system. The other two Oconee units were subject to the same potential problem. The root cause of this event was a design deficiency, failure to anticipate the interaction of systems, during the original design of the these systems. Units 1 and 2 reduced power to 72 percent FP to remove the D HDPs from service. Unit 3 increased power to 71 percent FP, but did not place D HDPs in service. Feedwater pump low discharge pressure setpoints were changed to 800 psig on all units prior to allowing HDP operation and a return to 100 percent FP on July 7, 1991.
2691991010 | Oconee 1, Oconee 2, Oconee 3 | 09/18/1991 | 10/21/1991 | 9110290445 | <strong>High Pressure Injection System Technically Inoperable For Some Single Failure LOCA Scenarios Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1991, at 1225 hours, while reviewing an alarm setpoint change, Design Engineering determined that the operating limit curve for Letdown Storage Tank (LDST) Pressure versus Level was inadequate. Use of this curve could permit operation outside the design basis for the emergency injection function of the High Pressure Injection (HPI) system. It was determined that, under certain small break LOCA scenarios, a single failure could result in hydrogen gas from the LDST expanding into the suction piping of the HPI pumps, causing the pumps to be damaged. This deficiency has existed on all three Oconee units since initial startup. At the time of discovery, Unit 1 was shutdown for refueling and Units 2 and 3 were both at 100 % full power. Corrective actions were to revise the operating limit curve and to provide additional instructions for operator action. The root cause was Design Deficiency.
2691991011 | Oconee 1 | 10/02/1991 | 06/17/1992 | 9206290096 | <strong>Reactor Trip Results From Electrical Generator Lockout After Equipment Failure In A Generator Protective Relay Circuit</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991, Unit 1 reactor tripped from 73 percent full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout. The lockout occurred when a protective relay circuit spuriously actuated. Investigation found that the relay circuitry was interrupted when either a terminal wire or a connector became loose. The root cause was assigned equipment failure in the 41MXa circuitry. Posttrip operator response stabilized the plant. After the trip, the Emergency Feedwater System was actuated due to low feedwater pump discharge pressure during a condensate-feedwater pressure oscillation. One main feedwater pump was manually secured. The second main feedwater pump tripped due to high pressure at the pump discharge. Corrective actions include tightening connections, evaluating the need for a preventive maintenance program on electrical connectors near vibrating equipment, and investigation into low demand feedwater oscillations.
2691991012 | Oconee 1, Oconee 2, Oconee 3 | 10/14/1991 | 11/26/1991 | 9112060073 | <strong>Design Deficiency In Establishing Relief Valve Setpoint Results in Technical Inoperability of Alternate Reactor Coolant Makeup System</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1991, Duke Power Design Engineering (DE) initiated an investigation into a possible inadequately low actuation setpoint on a relief valve which was installed on the Reactor Coolant Makeup System (RCMU). RCMU is a portion of the Standby Shutdown Facility (SSF) used to establish hot shutdown conditions following a fire, flood, or sabotage event. It injects borated water into the seals of the Reactor Coolant Pumps (RCPs). The RCMU pump is required by a proposed Technical Specification. On October 28, 1991, with all three units at 100 percent full power, an operability evaluation performed by DE declared the RCMU system on all three units inoperable based on the inability to provide adequate RCP seal flow to prevent seal failure and a loss of reactor coolant under certain accident conditions. The RCMU system was technically inoperable since its original design in 1981. Conditional operability for all units was attained on November 4, 1991, by verifying new Test Acceptance Criteria for SSF equipment and by implementing SSF Emergency Operating Procedure changes. The root cause of the event was a functional design deficiency. Properly set relief valves will be installed on each unit.
2691991013 | Oconee 1, Oconee 2, Oconee 3 | 11/04/1991 | 11/26/1991 | 9112060084 | <strong>Post LOCA Decay Heat Removal System Declared Technically Inoperable Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991, at 1645 hours, Babcock and Wilcox (B&W) notified utilities that boron precipitation inside the core would occur sooner than previously analyzed after certain LOCA scenarios. As a result, the Post LOCA Boron Dilution System (BDS) must be in service significantly earlier than previously required to avoid boron crystallization on fuel assemblies and the resulting degraded heat transfer. Operators were instructed to place BDS in service within 90 minutes of the LOCA in accordance with preliminary guidance from B&W. On November 5, 1991, Duke Power calculated that BDS must be in service within 9 (rather than 24) hours after the LOCA. Corrective action was to revise procedures to initiate system operation within the new time limit. The Low Pressure Injection system was declared technically inoperable from installation of the BDS (in 1976) until November 5, 1991, because the BDS may not have been placed in service when needed. All three Oconee units were at 100 % full power when notified. The root cause is Design Deficiency.
2701991001 | Oconee 2 | 02/10/1988 | 03/07/1991 | 9103150259 | <strong>Missed Technical Specification Surveillance Due to Inappropriate Action Causes Fire Detection System to Be Technically Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1991, at 0830 hours with Unit 2 at 100 percent Full Power, it was discovered that the Technical Specification requirement to perform surveillance at six month intervals on the Unit 2 Fire Detection System had been missed on three prior occasions. While preparing to perform IP/1&2/B/0250/05A (Fire Detection System Accessible Detector Functional Test and Sensitivity Checkout), an Instrument and Electrical (I&E) technician questioned applicability to Unit 2. An investigation into the past performance of this surveillance determined that on three occasions the Unit 2 surveillance had not been performed. It was determined that the system was technically inoperable during the time periods from 2/10/88 to 4/11/88 and from 2/10/90 to 8/19/90. This event is assigned the root cause of Inappropriate Action on the part of the two I&E Supervisors who marked the procedure steps for Unit 2 as "Not Applicable". Immediate corrective action was the verification of the operability of the Unit 2 Fire Detection System. To prevent future occurrence of this event, the work request instructions were changed to specifically state that this procedure is to be performed on both Unit 1 and Unit 2. Also, this event will be reviewed with I&E Supervisors and crews with emphasis on Station Directive 2.2.1, concerning when procedural steps may be declared "Not Applicable", and Technical Specification surveillance requirements.
2701991002 | Oconee 2 | 04/08/1991 | 05/20/1991 | 9105300206 | <strong>Flow Orifice Installed Backwards Due to Unknown Cause Results in Degraded Emergency Core Cooling System During Certain Small Break Loss of Coolant Accident Scenarios</strong><br /><i>Abstract:&nbsp;</i>During Post Modification on Unit 3, a flow transmitter was found to be inoperable. As part of the corrective action, on April 8, 1991, an inspection on Unit 2, while at 100% Full Power, revealed that the flow transmitter orifice for the High Pressure Injection loop 'A' Crossover Flow instrumentation was installed backwards. Investigations indicate that this flow orifice was installed backwards when the Crossover Flowpath was initially installed in 1980. The Crossover Flowpath consists of piping and associated valves connecting at each of the HPI pump normal discharge headers. This provides a parallel flowpath, bypassing the installed throttle valves, for protection against a single failure. The improperly installed orifice would give an indicated flow rate that is less than what is actually being delivered, and therefore could result in pump runout damage in some accident scenarios. As part of the corrective action, Design Engineering provided a revised indicated flow limit which was incorporated into the operating procedure. The root cause of this event is Unknown, possible Inappropriate Action.
2701991003 | Oconee 2 | 04/16/1991 | 05/16/1991 | 9105300311 | <strong>Excessive Letdown Storage Tank Pressure for Unknown Reason Makes High Pressure Injection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1991, at 1607 hours, while Unit 2 was operating at 100% Full Power, a Control Room Operator completed addition of Hydrogen (H2) gas to the Letdown Storage Tank (LDST) by closing a solenoid valve. During subsequent isolation of the H2 fill piping, a Non-Licensed Operator heard additional flow through the pipe. She finished manual isolation and observed that the LDST pressure exceeded the procedural maximum limit. At 1610 hours this was reported to the Control Room Operators, and the excess H2 was vented to the Gaseous Waste Disposal System. At 1628 hours pressure was within the allowed operating range. Both trains of the High Pressure Injection System (HPI), an Emergency Core Cooling System, were declared inoperable for the duration of the overpressurization due to the potential for H2 to enter the HPI pump suction following a LOCA event. This could damage the HPI pumps and make the system inoperable. The root cause is Unknown, Possible Equipment Malfunction. A solenoid valve is believed to have stuck open temporarily during the H2 fill, but this could not be confirmed. A contributing cause is Inappropriate Action, Lack of Attention to detail. Planned corrective actions include procedure enhancement, inspection of the valve, and counseling of the operator.
2701991004 | Oconee 2 | 12/04/1991 | 01/10/1992 | 9201170217 | <strong>Breach of Fire Barrier due to Unknown Cause Results In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1991 at approximately 1940 hours, Operations personnel, on a routine plant tour, discovered that a fire barrier on Unit 2 had been breached without taking compensatory actions as required by Technical Specifications. The Unit was operating at 100% Full Power when this discovery was made. The breach was a hole approximately three quarters inch in diameter in the Cable Spreading Room wall at penetration number 2ME4. A fire barrier inspection was performed in August 1990 that documented operability of this penetration. It is unknown when the penetration became inoperable after that date. Cables had been pulled in the immediate area in preparation for Unit 2 outage work. Upon the discovery of this breach, compensatory measures were taken until the breach was resealed at approximately 0940 hours on December 5, 1991. The cause of this event is assigned Unknown since it could not be determined how or when the breach originated. Corrective actions will include a review of this event by personnel who perform maintenance or modifications in the areas requiring fire barriers.
2711991001 | Vermont Yankee | 01/04/1991 | 01/23/1991 | 9101290360 | <strong>Entry Into A High Radiation Area By A Radiation Protection Technician Without A Dose Rate Monitoring Device Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1991, at approximately 1115 hours, a Radiation Protection (RP) technician entered a posted High Radiation Area, the radioactive waste Cask Room, to check the condition f the resin and move a resin cask, without a dose rate monitoring device, as required by Technical Specification 6.5.B.1. <br /><br /> A RP Supervisor went to the Cask Room to check on the job progress, discovered the problem and immediately directed the technician to return to the step-off pad until a dose rate monitoring device could be obtained, as required. The general area dose rate during this event was less than 100 mr/hr. <br /><br /> The root cause of this event is personnel error. The technician failed to use a dose rate meter as required by procedures and Tech Specs when entering a High Radiation Area.
2711991002 | Vermont Yankee | 06/18/1986 | 03/13/1991 | 9103210131 | <strong>Fire Protection System Surveillance Not Completed Within The Required Interval</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991 it was discovered that a Technical Specification required surveillance test had exceeded the specified test interval. The plant was operating at 100 percent power and was unaffected by this occurrence. <br /><br /> Technical Specification 4.13.D.1.b requires that high pressure carbon dioxide extinguishing systems be demonstrated operable at least once per 18 months. In 1986, even though the test interval was exceeded, the tests were completed successfully. This occurrence was discovered during a routine review of surveillance test completion dates. The root cause of this occurrence was an incorrect interpretation of the surveillance interval for this item. <br /><br /> No other discrepancies were identified as a result of this review. Modifications and revisions to the surveillance program since this event, have served to correct this issue.
2711991003 | Vermont Yankee | 02/27/1991 | 03/26/1991 | 9103280306 | <strong>Missed Diesel Fire Pump Fuel Oil Surveillance Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 2/27/91, during a Yankee Nuclear Services Division Quality Assurance audit, it was identified that the viscosity test of the Diesel Fire Pump (EIIS=KP) Fuel Oil Storage Tank contents was not performed in the last quarter of 1990 and the first quarter of 1991 as required by Technical Specification 4.13.2.B and plant procedures. <br /><br /> When this was identified, a sample of the oil was immediately taken and it was determined that the viscosity was satisfactory. <br /><br /> The root cause of this event was determined to be an inadequate procedure.
2711991004 | Vermont Yankee | 02/28/1991 | 03/29/1991 | 9104020049 | <strong>Incomplete Surveillance Testing Of Reactor Protective System Logic Instrument Channels Due To Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On 2/28/91, with the reactor operating at 100% power, it was identified that two Reactor Protection System (RPS) (EIIS=JC) Trip inputs, the Main Steam Line Isolation Valve Closure Trip and the Turbine Stop Valve Closure Trip, had not been tested to the extent required by the plant's Technical Specifications (TS) Table 4.1.1. The applicable portions of two plant surveillance procedures did not completely satisfy the TS requirement to functionally test the circuits from sensor to actuating device by tripping the channel and verifying the alarm. Both procedures only required that the applicable valve's sensor relay be monitored while each valve was stroked closed approximately 10%.<br /><br /> Following identification of this event, an assessment of equipment operability was made by the Plant Operations Review Committee and Plant Management. The assessment concluded that all equipment was fully operable and sufficient justification existed to maintain system operability in the short term until the required surveillance procedures could be thoroughly prepared, reviewed, approved, and safely implemented. The procedures were revised and the tests were successfully performed approximately 66 hours after the deficiency was identified. The root cause of this event was inadequate procedures.
2711991005 | Vermont Yankee | 03/13/1991 | 04/12/1991 | 9104180244 | <strong>Reactor Scram Due To Mechanical Failure Of 345KV Switchyard Bus Caused By Broken High Voltage Insulator Stack</strong><br /><i>Abstract:&nbsp;</i>On 3/13/91 at 2228 hours, with reactor power at 100%, a Reactor scram occurred due to a generator/turbine trip as a result of the failure of an 80 ft. vertical section of 345KV Switchyard Bus (B Phase) between the Main Transformer aerial T1 disconnect switch and the horizontal bus bar spanning the 1T-11 and 81-1T-2 disconnect switches. The cause of the bus failure is attributed to a broken insulator stack which secured the bus to the tower. The plant was subsequently stablized by resetting Primary Containment isolations, restarting Reactor Water Cleanup and establishing level control using the 10% Feedwater Regulator valve. Shutdown Cooling was later employed at 0504 hours on 3/14/91 and maintained until the necessary repairs and testing were completed. The reactor was returned to critical on 3/18/91 at 0055 hours. The need to expand present Switchyard system maintenance is being evaluated.
2711991006 | Vermont Yankee | 03/14/1991 | 01/09/1992 | 9201140004 | <strong>Loss Of "B" Loop Shutdown Cooling Due To Pressure Switch Activation</strong><br /><i>Abstract:&nbsp;</i>On 03/14/91 at 0450 hours, with Reactor vessel cooldown in progress following a Reactor Scram on 03/13/91 (subject of Licensee Event Report 91-05), and with the "B" loop Residual Heat Removal (RHR)(BO*) system flushed and lined up for Shutdown Cooling, a Group 4 Primary Containment Isolation Signal (PCIS)(JM)* was received during two attempted starts of the "B" RHR pump. The Group 4 Isolation signal resulted in a trip of the "B" RHR pump and closure of Shutdown Cooling Suction Isolation valves. The second failed pump start attempt was initiated at 0455 hours. At 0504 hours, after isolations were reset a second time, the "D" RHR pump was successfully started on the "B" RHR loop. Shutdown Cooling remained in operation on the "B" RHR loop for the duration of the shutdown. The reactor was returned to critical on 03/18/91 at 0055 hours. Root cause investigations and testing completed to date have identified a section of RHR piping between the inboard discharge check valve and outboard injection valve which remains in a depressurized state at the completion of loop flushing and is responsible for the pressure surges occurring in the "B" RHR loop. Procedure changes are being implemented which will repressurize the section of piping prior to system startup and additional testing is planned for the upcoming 1992 Refueling Outage to verify adequacy of the corrective actions. If required, additional corrective actions will be developed based upon analysis of test results and will be reported to the commission in a supplemental LER. Energy Information Identification System (EIIS) Component Identifier
2711991007 | Vermont Yankee | 03/13/1991 | 10/12/1991 | 9110150258 | <strong>HPCI Inoperable Due to Flow Controller Set Point Drift</strong><br /><i>Abstract:&nbsp;</i>On 03/13/91 at 0955, with the reactor at 100% power, during monthly High Pressure Coolant Injection (EIIS-BJ) surveillance testing, the HPCI turbine speed indicator was reading 3800 rpm. This speed corresponds to a HPCI flow rate of approximately 4195 gpm and is 50 rpm below the speed required to obtain the required Tech. Spec. flow rate of 4250 gpm. The low flow rate was caused by the HPCI flow controller high end set point drifting from 50 milliamps to 45 milliamps. <br /><br /> The root cause of this event is a defective Flow Controller.<br /><br /> The immediate corrective action was to recalibrate the flow controller. The long term corrective action plan established a program to monitor the Flow Controller set points. As a result of additional drift problems encountered during the first week of the program, the existing Flow Controller was replaced with a spare. Additional monitoring of the replacement Flow Recorder was continued for a period of one month. No additional problems were identified with the replacement during this period at which point the monitoring was suspended and the Controller returned to its normal surveillance interval.
2711991008 | Vermont Yankee | 03/25/1991 | 12/13/1991 | 9112230233 | <strong>Potential Environmental Conditions Not Previously Evaluated as a Result of Omission From Original Line Break Analyses</strong><br /><i>Abstract:&nbsp;</i>On 3/25/91, at approximately 1805 hours with the plant at 100% power, it was determined that failure of house heating steam lines had not been addressed in previous High Energy Line Break (HELB) analyses. This could create environmental conditions outside those previously evaluated. This was identified as a result of investigation relative to USNRC Info. Notice 90-053 that notified Licensees of similar conditions at other facilities.<br /><br /> Two Justifications For Continued Operation (JCO) were prepared and approved, the first on 4/1/91, supporting continued operation of the Heating system for the remainder of the 1990/91 heating season, and the second on 10/9/91 supporting operation of the Heating system for the 1991/92 heating season. <br /><br /> The House Heating System was erroneously omitted from HELB analyses performed in 1973 and 1974.<br /><br /> A design modification, procedure revisions and reviews of other systems have been completed and revision of d?sign basis documentation to address the House Heating Steam lines and related analyses is ongoing.
2711991009 | Vermont Yankee | 04/23/1991 | 08/30/1991 | 9109040243 | <strong>Reactor Scram Due to Loss of Normal Off-site Power (LNP) Caused By Inadequate Procedure Guideline</strong><br /><i>Abstract:&nbsp;</i>On 04/23/91 at 1448 hours, during normal operation with Reactor power at 100%, a Reactor Scram occurred as a result of a Generator/Turbine trip on Generator Load Reject due to the receipt of a 345KV Breaker Failure Signal. The Failure Signal was the result of Breaker Failure Interlock (BFI) signals that occurred simultaneously in the 345KV and 115KV Breaker control circuitry during the restoration of a battery bank to Switchyard Bus DC 4A. The cumulative effects of both (BFI) signals resulted in a total loss of 345KV and 115KV off-site power. An Unusual Event was declared at 1507 hours. Both Emergency Diesel Generators provided power for essential safety related systems during the LNP until approximately 0430 hours on 04/24/91 at which point off-site 345KV power was restored and backfed through the Station Auxiliary Transformer. During the event, Torus Water volume exceeded the Technical Specification limit of 70,000 cubic ft. The Unusual Event was terminated at 1950 hours on 04/24/91. The reactor reached Cold Shutdown at 0357 hours on 04/25/91 and was returned to critical at 0300 hours on 04/30/91.<br /><br /> The Root Cause of this event is failure of the repair department personnel to recognize the consequences of operating a DC bus without a connected battery bank. <br /><br /> Corrective actions to prevent reoccurrence are outlined within this report.
2711991010 | Vermont Yankee | 04/12/1991 | 05/08/1991 | 9105130372 | <strong>Failed Relay Coil Results in Primary Containment Isolation S stem Actuation</strong><br /><i>Abstract:&nbsp;</i>On 04/12/91 at 1158, with the reactor operating at 100% power, valve V12-15 closed isolating the Reactor Water Cleanup (RWCU) System (EIIS=CE). The cause of the valve closure was a failure of the 16A-K26 relay coil which caused the output contacts to change state and initiated the closure of the RWCU inboard isolation valve V12-15. Electrical interlocks caused the in-service RWCU pump to trip when the suction valve began closing. The relay coil was replaced and the RWCU System was tested and returned to service at 1535. <br /><br /> The root cause of this failure is the lack of an established service life for normally energized General Electric (GE) CR120 Relays. Due to the fact that no service life was previously established, plant preventative maintenance did not include a coil replacement schedule. Vermont Yankee is planning to replace all original General Electric CR120 relay coils in the Primary Containment Isolation System in the near future. <br /><br /> A similar occurrence was reported to the Commission as LER 87-01.
2711991011 | Vermont Yankee | 04/30/1991 | 05/28/1991 | 9106050307 | <strong>Inadvertent Group Six Primary Containment Isolation System Actuation Due to an Incomplete Procedure</strong><br /><i>Abstract:&nbsp;</i>On 04/30/91 at 0555, during plant heatup at approximately 2% power and with reactor pressure at 116 PSIG, operators unbypassed and returned to service the trip functions for the Group Six, Primary Containment Isolation System (PCIS)(EIIS=JM), trips of the High Pressure Coolant Injection System (HPCI)(EIIS=BJ) and the Reactor Core Isolation Cooling System (RCIC)(EIIS=BN) on low steam supply pressure. When the trips were returned to service, a PCIS Group Six Isolation occurred which isolated two steam supply valves in the HPCI system and two steam supply valves in the RCIC System. These trip signals are normally bypassed during plant start-up and before reactor pressure reaches 150 PSIG to allow warming the HPCI and RCIC steam lines. <br /><br /> The cause of this event is attributed to an incomplete procedure. The procedure which governs the operation of the bypass switches states that the trip functions are to be restored before exceeding 150 PSIG, however, it does not specify any minimum pressure above which the switches can be operated without incurring a PCIS Group Six isolation.
2711991012 | Vermont Yankee | 04/23/1991 | 11/07/1991 | 9111150113 | <strong>Reduced Cooling Water Flow to Diesel Generator Heat Exchangers and Station Service Air Compressors Due to High Service Water System Backpressure Caused by Weak Design</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1991, at 1448 hours, and at 100% power, a Loss of Normal Power (LNP) was experienced. Following the expected start of both Emergency Diesel Generators (EDG), it was observed that the EDG heat exchangers were operating at reduced flow and that the station air compressor coolers were operating with reduced/reverse flow. <br /><br /> The root cause of the event was a weak design modification resulting in an incorrect procedure. The incorrect procedure established an alternate cooling discharge path to the cooling towers and produced a high service water system backpressure of approximately 40 psid. System backpressure was further increased due to various system design and operating characteristics present during the LNP. <br /><br /> A task force was convened to analyze and test the response of the service water system. The service water system was reconfigured to eliminate the primary contributor of backpressure. <br /><br /> A Corrective Action Report was generated to further identify and confirm the root cause of the event and provide detailed long term corrective actions.
2711991013 | Vermont Yankee | 05/28/1991 | 06/20/1991 | 9106260110 | <strong>RPS MG "A" OUTPUT BKR TRIP</strong><br /><i>Abstract:&nbsp;</i>At approximately 0839 hours on 05/28/91 with the plant at full power, a Reactor Protection System (RPS) Motor Generator set (MG) output Breaker (BKR) tripped. The resulting loss of power to half of RPS caused a half SCRAM, a Group 3 primary containment isolation, shutdown of Reactor Building ventilation and start of the Standby Gas Treatment System. <br /><br /> Extensive testing/inspection of this breaker and the associated MG protective circuitry has not resulted in any evidence which would allow for root cause analysis. Therefore, the cause of the tripped output breaker is indeterminate. The events of this report did not have adverse safety implications. The RPS and Primary Containment Isolation System (PCIS) operated as designed upon experiencing a power loss to half of RPS.
2711991014 | Vermont Yankee | 06/15/1991 | 07/15/1991 | 9107160385 | <strong>Reactor Scram Due to Loss of 345KV Switchyard Caused by Defective Off-Site Carrier Equipment</strong><br /><i>Abstract:&nbsp;</i>On 06/15/91 at 2224 hours, during normal operation with Reactor power at 100%, a Reactor Scram occurred due to a Turbine Control Valve Fast Closure on Generator Load Reject resulting from a loss of the 345KV North Switchyard Bus. The event was initiated during a thunderstorm in which a lightning strike occurred on the "B" phase of the 381 transmission line between Vermont Yankee and Northfield. The fault resulted in the opening of all 345KV Air Trip Breakers (ATBs). During the event, a subsequent Reactor Scram and corresponding Primary Containment Isolation Signals (PCIS)(*JM) Groups 2 and 3 were received due to Low Reactor Water level. The Reactor was stabilized in Hot Standby using the Main Condenser, Condensate, and Feedwater systems. At 2100 hours on 06/16/91, after Reactor depressurization was completed, Shutdown Cooling using the "D" RHR pump on the "B" loop was initiated. The reactor reached Cold Shutdown at 0500 hours on 06/17/91. The reactor was returned to critical at 1413 hours on 06/20/91. The Root Cause of this event is a defective (shorted) transistor in offsite (Scobie Pond) Protective Relaying System Carrier equipment. The need to perform additional testing of Carrier systems is being evaluated. <br /><br /> *Energy Information Identification System (EIIS) Component Identifier
2711991015 | Vermont Yankee | 06/14/1991 | 07/10/1991 | 9107150337 | <strong>Containment Isolation Valve Failure to Close Due to Erosion/Corrosion and Displacement of Screw-In Seat.</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1991, at 1800 hours, and at 100% power, Residual Beat Removal Valve V10-34A failed to close. RHR Valve V10-34A valve is a Primary Containment Isolation Valve which provides a return path to the torus for the "A" Containment Cooling Subsystem. The associated "in-series" primary containment isolation valve was closed and the redundant "B" Containment Cooling Subsystem was demonstrated operable. <br /><br /> The root cause was determined to be erosion/corrosion of the threads of the removable screw-in seat. The valve seat separated from the valve body as a result of erosion/corrosion of the valve seat ring threads. During valve closure, movement of the valve stem and disc was limited due to the displacement of the seat ring resulting in significant damage to the valve actuator assembly. <br /><br /> The valve was repaired by welding a new seat into the valve body. The actuator assembly was also replaced. All other like valves were identified. One of these valves, will be disassembled and inspected during each of the next three refueling outages to determine if this is an isolated event.
2711991016 | Vermont Yankee | 12/20/1991 | 01/17/1992 | 9201230249 | <strong>Failure To Perform Correct Daily Instrument Checks Due To Tech Spec Human Factors Weakness</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1991 it was determined that Daily Instrument Checks for 3 of the 15 Post Accident Parameters (EIIS=IP) were performed on instruments different than listed in the applicable Technical Specification (TS) Table. For each parameter the instrument check was being performed on another control room indication of the parameter which originated from the same sensor instrumentation. Therefore, a valid indication of parameter availability and equipment operability, was determined daily, however the specific instrument in TS was not being checked and logged on the Control Room Operators rounds sheet. <br /><br /> The cause of the event was determined to be a human factors weakness in the content and arrangement of two TS tables.<br /><br /> Immediate corrective actions consisted of revision of the Control Room Operators Rounds Sheet and reviewing all Daily instrument checks to verify that no similar conditions existed. A revision to the procedure governing Operator rounds will be completed to reference applicable TS requirements.
2721991001 | Salem 1 | 01/11/1991 | 02/11/1991 | 9102150148 | <strong>ESF Actuation Signal: Containment Vent. Isol. Due To Equipment Concerns</strong><br /><i>Abstract:&nbsp;</i>On 1/11/91 at 1108 hours, a Containment Purge/Pressure-Vacuum Relief System (CP/P-VRS) isolation signal actuated as a result of a high channel spike on the Radiation Monitoring System (RMS) Containment Particulate Radiation Monitor, 1R11A. Subsequently, Tech. Spec. 3.4.6.1 Action Statement was entered. The isolation valves were closed at the time of this signal; they did not change position as a result of the isolation signal. The Action Statement was exited at 2230 hours on 1/11/91 based on not finding any specific equipment concern and the opinion that the channel actuation may have been caused by high Containment activity (i.e., Rb-88). However, since then, it has been determined that this channel spike was the result of an equipment concern, not high activity. On 1/17/91 at 2050 hours, another CP/P-VR System isolation signal actuation occurred as a result of a high channel spike of the 1R11A RMS channel. Subsequently, Tech. Spec. 3.4.6.1 Action Statement was entered. The isolation valves were closed at the time both 1/11/91 signals; they did not change position. The cause of the CP/P-VR System channel isolation signals is attributed to equipment failure. Troubleshooting, did not reveal the specific cause of the 1R11A channel failure. The channel's detector connectors were checked in addition to checking the channels electronic circuits. A specific parts failure could not be found. A recorder was connected to the channel for 2 weeks. No additional channel spikes were observed. Upon successful completion of a channel functional test, the channel was returned to service. On 1/25/91 at 1240 hours, the Tech. Spec. 3.4.6.1 Action Statement was exited.
2721991002 | Salem 1 | 01/17/1991 | 02/20/1991 | 9103040112 | <strong>ASME Code Class 3 Piping Leakage Caused By Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>This Licensee Event Report (LER) addresses three (3) occurrences of ASME Code 3 piping leakage at dissimilar metal weld locations. Based upon discussion with the NRC, notifications were made for each occurrence as agreed in accordance with Code of Federal Regulations 10CFR 50.72. In all cases, Tech. Spec. 3.4.10.1 Action "c" was complied with. The root cause of the listed ASME Code component leakage has been attributed to equipment failure. The leaks are believed to be the result of galvanic corrosion at dissimilar metal weld sites. These welds were made in 1983 as part of design changes which upgraded the Room Coolers. The "new" Room Cooler pipe (upstream and downstream) was type 316 stainless steel and was welded to the existing SW pipe (carbon steel). The components which exhibited leakage were declared inoperable in accordance with Tech. Specs. and the appropriate Action Statements met. The components were not declared operable until completion of repairs, which were done in accordance with the ASME code for Class Code components. An ongoing program, at Salem Generating Station, for the upgrade of Service Water System piping is continuing. The scope and prioritization of pipe replacement and the need for additional inspections is being reviewed and modified, as applicable. A detailed weekly walkdown, by System Engineering, of Room Cooler SW pipe (initiated as per Salem Unit 2 LER 311/90-042-00) to provide early identification of SW leakage is continuing. This compliments routine Operations Department operator observation, of Room Cooler areas, performed each shift.
2721991003 | Salem 1 | 02/09/1991 | 10/24/1991 | 9111050073 | <strong>Tech. Spec. 3.0.3 Entry; 2 Stm Flow Channels for 1 Steamline Inop. Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 2/9/91, during reactor shutdown (in support of the upcoming ninth refueling outage), a No. 14 Steam Generator (S/G) steamline flow channel I transmitter sensing line was isolated during investigation of a 14 S/G steamline flow channel II erroneous reading. Subsequently, Action Statement 3.0.3 was entered since the Action Statements for Tech. Specs. 3.3.2.1 and 3.3.3.1 do not address required actions with more than one inoperable steamline flow channel for any one S/G. The root cause of this event is personnel error as attributed to inappropriate supervisory direction. The supervisor involved acted upon an invalid assumption. When the transmitter sensing line would not stop venting (after the root valve was closed) the supervisor incorrectly assumed either the schematic was not read correctly, the valves were mislabeled or the schematic was incorrect. The supervisor did not consider that the correct transmitter sensing line root valve was closed but was leaking by (due to it not being closed tight enough). Contributing to this event was that the schematic drawing, which details component alignment, (for the transmitter sensing lines) was not taken to the job site. Upon notification of the isolation of the Channel I sensing line, the supervisor reopened the wrong root valve and successfully closed the correct root valve (i.e., the first one closed) and vented the subject sensing line. This event has been reviewed by Maintenance management. Corrective disciplinary action was taken with the supervisor involved. This event has been reviewed with applicable Maintenance personnel.
2721991004 | Salem 1 | 02/06/1991 | 09/10/1992 | 9209210054 | <strong>Reactor Protection System actuation: Turbine runback on overtemperature delta temp. signal.</strong><br /><i>Abstract:&nbsp;</i>On 2/6/91 at 1511 hours, during routine power operations, a turbine runback from 100% to 90% power occurred due to an Overtemperature Delta Temperature (OTDT) signal. The plant was stabilized at 90% power and remained there pending further investigation. At the time, the power range Nuclear Instrumentation System (NIS) channels were being recalibrated with revised currents. Two of the channels recalibration was complete and a third channel was being recalibrated when the runback occurred. To support NIS recalibration, the NIS channel bistable is placed in the tripped position deenergizing the OTDT turbine runback relay. This gives a 1/4 signal to the protection circuitry for OTDT turbine runback which uses 2/4 relay logic. One of the other channel signal comparators tripped to the 'off' condition deenergizing a second turbine runback relay to satisfy the turbine runback relay logic. The root cause of this event is equipment failure. The OTDT runback signal was caused by Resistance Temperature Detector (RTD) faulty connectors in combination with the OTDT setpoint summator higher than normal output signal which was due to failed electrolytic capacitors. Recorders were attached to the RPS comparator circuits; however, the failure mechanism did not recur. The Unit was subsequently returned to full power operation on 2/8/91. The failed connectors were identified following a second event (which did not involve a runback since the necessary logic was not made up). New connectors with gold plated pins have been installed.
2721991005 | Salem 1 | 02/09/1991 | 04/02/1991 | 9104100199 | <strong>Cont. Fan Coil Units Do Not Meet Design Heat Removal Req'ts. Due To Inad. Admin. Controls</strong><br /><i>Abstract:&nbsp;</i>On 2/9/91 at 1945 hours, engineering completed an analysis of thermal performance testing for Containment Fan Coil Units (CFCUs) heat removal capacity. This review concluded that 3 of the 5 CFCUs did not meet their design accident requirements as identified by the Updated Final Safety Analysis Report (UFSAR). The Nos. 12, 13 and 14 CFCUs were not capable of heat removal at a rate of 81x10**6 BTU/hr each. Also, the UFSAR accident analysis assumption that 3 remaining CFCUs (after the failure of a single Vital Bus) would be capable of removing 243x10**6 BTU/hr (at 85 degrees F river water temperature) could not be met. Testing of the CFCUs, to verify their heat transfer capability, was conducted in accordance with NRC Generic Letter 89-13. It was conducted with the Unit at full power operation. The Unit was brought to Mode 3 on 2/9/91 in support of its ninth refueling outage. The root cause of the CFCU loss of heat removal capacity is attributed to inadequate admin. control. CFCU heat capacity testing has not been required nor performed since CFCU installation. Due to lack of a test program, degrading performance was not identified and corrected. The reduction in heat removal capacity is attributed to CFCU cooling coil partial blockage. An evaluation by Westinghouse, justifying plant operation between 1/28/91 and 2/7/91, was performed and was confirmed by PSE&G engineering. Recurring tasks have been initiated (both Salem Units) to test heat removal capacity of the CFCUs. The Salem U-2 CFCUs were recently tested for heat removal capacity. All 5 units exceeded UFSAR heat removal capacity design requirements. The Salem U-1 CFCUs will be cleaned during the current refueling outage and subsequently retested.
2721991006 | Salem 1 | 02/16/1991 | 03/18/1991 | 9103210001 | <strong>ESF Actuation Signals For Cont. Vent. Isolation Due To Inad. Admin. Controls</strong><br /><i>Abstract:&nbsp;</i>Three Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation events occurred on 2/16/91, 2/20/91 and 2/27/91. They were initiated by the 1R11A Radiation Monitoring System (RMS) Containment Particulate Radiation Monitor channel. The CP/P-VR System isolation is an Engineered Safety System (ESF). On 2/16/91 and 2/20/91, the isolation valves were closed at the time of the signal actuation; they did not change position as a result of the isolation signal. On 2/27/91, Containment Purge was in progress at the time of the signal actuation; the isolation valves closed as designed. The Unit was in Mode 5 on 2/16/91 and 2/20/91; it was in Mode 6 during the 2/27/91 event. Tech. Spec. 3.9.9 Action Statement was entered after the 2/27/91 event. The 1R11A channel is not required to be operable in Mode 5. The cause of the 3 CP/P-VR System isolation signal events is attributed to equipment failure. The 1R11A channel circuit board contacts and the reset switch contacts were found oxidized. The root cause of this event is attributed to inadequate administrative controls. Analysis of recurring failures of this RMS channel and other RMS channels failed to adequately define appropriate preventive maintenance. The 1R11A channel reset switch contacts and the circuit board connections were cleaned. Upon successful completion of a channel check, the 1R11A channel was returned to service. The Tech. Spec. 3.9.9 Action Statement was exited on 2/28/91. As indicated in prior LERs, engineering has investigated the concerns with the Salem U-1 and U-2 RMS channels. Design modifications include a proposal for RMS channel equivalent replacement.
2721991007 | Salem 1 | 02/17/1991 | 08/15/1991 | 9108260040 | <strong>ESF Actuation: Auto Start OF Aux Feedwater Pumps Due To Inad. Admin. Controls</strong><br /><i>Abstract:&nbsp;</i>On 2/17/91 at 2200 hours, the Motor Driven Auxiliary Feedwater (MDAFW) Pumps automatically started after the 1CCDC 125 VDC Distribution Cabinet power supply was transferred to its emergency power supply in preparation for a 1C 125VDC Bus outage. The Unit's 911 refueling outage was in progress when this event occurred. The automatic start of the MDAFW Pumps is an engineered safety feature (ESF) actuation. Investigation into the root cause of this event is attributed to inadequate administrative controls. To support removal of a DC Distribution Cabinet from service, operations procedure IV-5.3.3, "DC Breaker - Administrative Control" is used in conjunction with schematics and the Tagging Request Information System. The procedure is used to identify DC breakers. It does not detail the steps necessary to remove DC Busses from service. Subsequently, the auto start capability of the MDAFW Pumps (on a "loss of both Steam Generator Feedwater Pumps" signal) was not recognized as possibly occurring prior to removing the 1CCDC 125VDC Distribution Cabinet from service. This signal will automatically be initiated, upon changing the power supply to the Distribution Cabinet, due to relay deenergization and subsequent reenergization, unless applicable equipment is removed from service (tagged out). A review of electrical schematics was conducted to identify the cause of the event. New procedures will be developed to detail the steps required in support of removal of DC Distribution Cabinets from service. In the interim, Operations Procedure IV-5.3.3 as been revised to prevent event recurrence.
2721991008 | Salem 1 | 02/17/1991 | 08/15/1991 | 9108260034 | <strong>Rx Protection System Trip Signal Actuation Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 2/17/91, at 0530 hours, a Reactor Protection System (RPS) signal from the Nuclear Instrumentation System (NIS) was received. The overhead annunciation, indicating the cause of the RPS signal, was "IR Flux High". The Unit was in Cold Shutdown (Mode 5) in support of its ninth refueling outage. The root cause of this event is personnel error as attributed to inattention to detail. At the time of the event, the 1N32 Source Range NIS channel cable replacement was in progress. In support of this work, the subject channel's RPS functions are blocked and then the channel is deenergized by removing its fuses. The Maintenance-I&C technician, performing this work, had inadvertently pulled the fuse for the 1N36 Intermediate Range NIS channel instead of the 1N32 fuse. This resulted in the RPS actuation by satisfying the 1 out of 2 solid state protection system (SSPS) logic when the high flux bistable failed to its safe position on loss of power. The technician involved did not apply good work practices. He did not perform a "self check" to ensure that he would remove the correct fuse. The 1N32 channel drawer is located approximately 6' above the floor, directly above the 1N36 channel drawer. The fuses for each channel are located on the drawer outside face in the lower left section. This event has been reviewed by Maintenance Department management. The individual involved was counseled. The need to perform self-checks during work activities was stressed. This event has been reviewed with applicable Maintenance Dep't. personnel in the form of small group discussions.
2721991009 | Salem 1, Salem 2 | 12/20/1990 | 06/11/1992 | 9206240010 | <strong>High Energy Line Break Concern Between Mechanical Pene. Area & Chiller Room</strong><br /><i>Abstract:&nbsp;</i>On 2/15/91, Probabilistic Risk Assessment of a missing portion of the Unit 1 seismic gap seal, between the Inboard Mechanical Penetration Area and the Chiller Room, showed a calculated change in core damage frequency for Salem Unit 1 from 5.8E-5/Yr to 8.5E-5/Yr (assuming a worst case Main Steamline break in the Inboard Mechanical Penetration Area). Assessment shows that the health and safety of the public was not affected due to available mitigating capabilities. A similar Unit 2 seismic gap section had been found unsealed prior to discovery of the Unit 1 concern. The root cause of both Units' seismic gap seal(s) not being fully installed is "Design, Manufacturing, Construction/Installation" error (per NUREG 1022). The subject unit 2 seismic gap section was sealed on 2/22/91. The missing portion of the Unit 1 seismic gap seal was installed on 4/12/91. The remaining seismic gap areas (both Units) have been inspected and those seals requiring repair have been repaired. Administrative controls for Appendix R penetrations have been extended to include HEBA barrier impairments.
2721991010 | Salem 1 | 02/20/1991 | 03/15/1991 | 9103270120 | <strong>ESF actuation signal: Cont. Vent. Isolation; 2 Events Due To Proced. Inad.</strong><br /><i>Abstract:&nbsp;</i>On 2/20/91 and 3/4/91, Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation signals actuated. CP/P-VR System isolation is an Engineered Safety System (ESF). The 2/20/91 signal was initiated by the 1R12A Radiation Monitoring System (RMS) Containment radioactive noble gas activity channel and the other occurred on 3/4/91 from the 1R11A Containment radioactive particulate monitor channel. The isolation valves were closed at the time of the signal actuations. On 2/19/91 the 1R11A and 1R12A channel setpoints were changed to 2X background in support of the upcoming Unit mode change to Mode 6 (on 2/20/91). On 2/20/91, the 1R12A RMS channel alarmed after opening the S/G manways. On 3/4/91, with the reactor defueled, the 1R11A channel alarmed. The alarm setpoint was set at 5000 cpm while the channel was indicating approximately 4000 cpm. The root cause of these actuations is procedure inadequacy. The assumptions used in determining the channel alarm setpoint are too conservative. It currently requires the setpoint determination to be made based upon average background levels (experienced over the past few outages) and Reactor Coolant System sample analysis. Containment outage support work activities (e.g., Steam Generator work) will cause periodic fluctuation of background activity resulting in the alarm actuations. These fluctuations are not considered in determining the setpoint. The procedure used to determine the 1R11A and 1R12A alarm setpoints will be revised to address the concerns associated with determination of the setpoints and changing background levels associated with Containment work activities.
2721991011 | Salem 1 | 02/20/1991 | 03/20/1991 | 9104010366 | <strong>High Rad Area Found Unlocked/Unguarded Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1991 at 1020 hours, the RHE Room was discovered to be unlocked and unguarded by Radiation Protection Department supervision. The access door to this room was found closed. On February 19, 1991 at 2300 hours, during ninth refueling outage activities, the Regenerative Heat Exchanger (RHE) Room High Radiation Area (HRA) key was obtained by a Radiation Protection technician to support work in the area. Work in the area was completed at 0200 hours on February 20, 1991. The area has accessible (by climbing) radiation levels of up to 2.0 R/hr at 18 inches from the heat exchanger. The ground level area radiation levels are less than 1 R/hr. The root cause of this event is personnel error. The Radiation Protection technician, who was supporting work in the RHE Room, did not ensure the door was locked after personnel vacated the area. The technician upon closing the door verified it latched closed but did not ensure it was locked (turned the knob). This event has been reviewed by Radiation Protection Department management. Corrective discipline was taken with the technician responsible for this event. This event has been reviewed with applicable Radiation Protection Department personnel stressing the need for ensuring positive control of HRA's. Access logs and personnel dosimetry data were reviewed for the period between February 19, 1991 at 2300 hours to February 20, 1991 at 1200 hours. No inadvertent entry into the RHE room was apparently made. The RHE access door is now chain locked. The door locking mechanism will be replaced with a mechanism that requires key removal for the door to be locked.
2721991012 | Salem 1, Salem 2 | 03/06/1991 | 04/05/1991 | 9104100206 | <strong>ESF Actuation Signal: 1R1B RMS Channel Spike Resulted In Control Rm Vent. Switch</strong><br /><i>Abstract:&nbsp;</i>On 3/6/91, the Control Room Ventilation automatically switched from the normal to the accident mode of operation (100% recirculation) for both Salem Unit 1 and Salem Unit 2 (by design). This was due to a false high activity alarm signal on the Control Room Air Intake Radiation Monitoring System (RMS) channel, 1R1B. The switching of the Control Room Ventilation system to the emergency mode of operation is an Engineered Safety Feature (ESF). During this event, one of the Salem Unit 2 ventilation outlet dampers (2CAA18) did not close fully. The root cause investigation of the 1R1B Channel ESF actuation is continuing. The specific cause of the actuation has not been determined. After the event, the control circuit (including the electrolytic noise suppression capacitors (reference LER 272/91-031 00) were visually inspected. Also, field cable connections were inspected. The connections, capacitors and the circuit were found to be satisfactory. The 1R1B channel was returned to operable status on March 27, 1991. The 2CAA18 linkage arm was repaired. As identified in LER 311/91-006-00, equipment with similar types of linkage configuration will be inspected. As indicated in prior LERs, engineering has investigated the concerns with the Salem U-1 and U-2 RMS channels. Design modifications include a proposal for RMS channel equivalent replacement.
2721991013 | Salem 1 | 03/16/1991 | 04/10/1991 | 9104190299 | <strong>TS Noncompliance; Cold Leg Side Of S/G Tube Found Unplugged Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1991, during eddy current inspections of the No. 14 Steam Generator (S/G), it was discovered that the cold leg side of the tube in location row 18 column 12 was not plugged. The cold leg side of the tube next to it (row 18 column 11) was found plugged. Tube plugging had last been performed in May 1989 (8th refueling). The tube in row 18 column 12 was required to be plugged at that time due to an indicated wall degradation of 41%. The tube in row 18 column 11 had not required plugging. Therefore, the Unit had been operated with a S/G tube greater than the plugging limit specified by Technical Specification Surveillance 4.4.5.4b (i.e., 40%). The root cause of the wrong tube being plugged is attributed to personnel error. The wrong tube was marked for plugging (8th refueling). Also, the Station Quality Assurance (SQA) verification did not identify this mistake. This event has been reviewed by SQA and Inservice Inspection department management. The circumstances surrounding the incorrect tube plugging event will be reviewed with appropriate ISI and SQA personnel. Modifications to the independent review process were implemented in the spring of 1990. The process now requires SQA to prepare a separate map of the tubes to be plugged and to then independently verify that the correct tubes have been marked. All tubes previously plugged have been verified as being correctly plugged. The hot leg side of the No. 14 S/G column 18 row 11 and the cold leg side of the No. 14 S/G column 18 row 12 tube were plugged.
2721991014 | Salem 1 | 03/22/1991 | 04/17/1991 | 9104240210 | <strong>Two Channels Made Inoperable In A Single System Due To A Common Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On 3/22/91 at 0112 hours, a Control Room Operator observed a low flow indication for the 1R11A/1R12A/1R12B Containment Radiation Monitoring System (RMS) pump. These 3 channels analyze a sample of Containment atmosphere provided by this single pump. It was observed that the local pump flow indication was low and that the pump was making "grinding" noises. Subsequently, the 1R11A, 1R12A and 1R12B RMS channels were declared inoperable and applicable Technical Specification Action Statements were entered. The root cause of this event is attributed to equipment design concerns. Prior LERs have identified the concern for the adequacy of the pump design (e.g., LER 272/89-010-00). The sample pump is an internal rigid rotor vane pump which uses graphite vanes. Inspection of the sample pump revealed that the four (4) pump graphite vanes had each chipped, on the same outside corner (approximately 0.5"). The specific cause of the vanes chipping could not be identified. The sample pump was replaced. On 3/22/91 at 1101 hours the 1R11A and 1R12A monitors were declared operable and the applicable Technical Specifications were exited. The pump is scheduled to be replaced with a more reliable pump as part of the RMS Upgrade Project. An interim measure is to replace the pump every 6 months. This failure occurred 2 weeks prior to the scheduled replacement date. The frequency for pump replacement will be increased to every three (3) months.
2721991015 | Salem 1, Salem 2 | 03/29/1991 | 04/26/1991 | 9105060224 | <strong>ESF Signal Actuation: Containment Vent. Isolation Due To 1R41C Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1991 at 1700 hours, the Radiation Monitoring System (RMS) Plant Vent Radioactive Noble Gas Monitor, 1R41C, channel failed low resulting in a Containment Purge/Pressure-Vacuum Relief System (CP/P-VRS) isolation signal. Technical Specification Table 3.3-13 Action Statement 31 was entered upon identification of the 1R41C channel failure. At the time of the event, neither Containment pressure/vacuum relief or Containment purge were in progress. The root cause of the CP/P-VRS actuations is attributed to equipment design concerns. The type detector system used for the Salem Unit 1 1R41 RMS channels is manufactured by Victoreen. Periodic problems with this system have been experienced, as indicated in prior LERs. The specific cause of this 1R41C channel failure was the failure of the scalar test jack, which is used to input dummy alarm signals for testing. The 1R41C channel scalar test jack was replaced. A channel functional test was then successfully completed. The channel was declared operable and Technical Specification Table 3.3-13 Action Statement 31 was exited at 1330 hours on April 15, 1991. As indicated in prior LERs, (e.g. 311/90-040-00) involving ESF signal actuations, engineering has investigated the concerns associated with Victoreen RMS equipment. Design modifications include a proposal for RMS channel equivalent replacement.
2721991016 | Salem 1 | 03/31/1991 | 04/30/1991 | 9105060164 | <strong>TSAS Noncompliance: High O2 In Waste Gas System For > 48 Hours</strong><br /><i>Abstract:&nbsp;</i>Oxygen concentration within the Waste Gas Holdup System was > 2% for > 48 hours. On 3/29/91, Tech. Spec. Action Statement 3.11.2.5.a was entered due to an oxygen concentration of 2.3% by volume in the No. 13 Waste Gas Decay Tank (WGDT). The tank was purged with nitrogen. Tank discharge was attempted on 3/30/91; however, due to a prior failure of the 1R41C Plant Vent Radiation Monitor, the waste gas discharge valve (1WG41) could not be remotely opened. Failure of the 1R41C channel results in a 1WG41 isolation signal. The Nos. 11 and 14 WGDTs also exceeded 2% oxygen on March 31 and March 30, respectively. The maximum oxygen concentration observed in any tank was 2.7%. The root cause, of not reducing the oxygen concentration within 48 hours to < 2%, is attributed to equipment failure of the 1R41C channel. A contributing factor was the misunderstanding of the 1WG41 valve isolation signal circuit design. The source of the oxygen is attributed to the CVCS Holdup Tanks' cover gas. Oxygen concentration, in the No. 13 CVCS Holdup Tank, was 7.56% as of 3/19/91. Oxygen, entrained in reactor coolant due to refueling outage activities, comes out of solution in the CVCS Holdup Tanks. The Waste Gas System oxygen level was reduced to below the 2% limit. This event has been reviewed by Operations Department management. It will be discussed with applicable department personnel. Procedure modifications will be assessed to allow operation of the 1WG41 valve given failure of the 1R41C radiation monitoring channel.
2721991017 | Salem 1, Salem 2 | 01/09/1991 | 07/09/1992 | 9207200055 | <strong>4KV Vital Bus UV Relay Setpoints Found Below Minimum Tech. Spec. Allowable Value</strong><br /><i>Abstract:&nbsp;</i>On 4/13/91, the 91.6% sustained undervoltage relay's minimum drop out voltage, for all 3 Vital Busses, were found to be below the Technical Specification minimum allowable value of 91%. This was discovered during Technical Specification Surveillance 4.3.2.1.1 testing which requires monthly testing of undervoltage relay setpoints. New procedures (S1.MD-FT.4KV-0001(Q) (0002 or 0003), 'ESFAS Instrumentation Monthly Functional Test-1A (1B or 1C) 4KV Vital Bus Under Voltage') were being used (first use) to support the surveillance testing. The surveillance test was last performed on 1/9/91 using procedure M3T, 'Undervoltage and Underfrequency Trip and Time Response Surveillance Test'. It had not been performed since 1/9/91 due to ninth refueling outage activities (operability required only in Modes 1, 2, and 3). The causal factors of the setpoint variance are relay design inadequacy and procedure inadequacy. Special relay tests show that the relay circuitry is influenced by the amount/type of harmonics present in the external test signal; the relay trip/reset setpoints change on subsequent checks when the test signal contains a different range of harmonics/noise plus the relay's allowable design setpoint drift. For additional root cause and corrective action details refer to LER 311/91-008-01. Contributing factors to the cause of this event are test equipment inaccuracies and test methodology. Procedure enhancements have been made to address human factor and test methodology concerns found during System Engineering's investigation.
2721991018 | Salem 1 | 04/13/1991 | 05/13/1991 | 9105150357 | <strong>Inop. of Several Components Required For Feedwater Isolation (ESF)</strong><br /><i>Abstract:&nbsp;</i>On 4/10/91, Solid State Protection System (SSPS) manual safety injection surveillance testing was in progress, using procedure SP(O)4.3.2.1.1.A1, "ESP Manual SI - SSPS". During the surveillance testing, buffer relay No. BC-621 apparently failed to energize which resulted in the failure of the trip functions to 13BF13 valve, 14BF13 valve, and 11 SGFP. Troubleshooting of the circuits associated with buffer relay No. BC-621 was performed. The accessible wiring connectors were inspected and the lug connector screws checked for tightness. Also, relay No. BC-621 was replaced. Several tests were perfomed after this work with one test failing with the same components affected. On 4/13/91, the terminal lug electrical connectors (connected by crimping) were checked for tightness. An uncrimped connector was discovered. It was the cause of the failed surveillance. The root cause of this event is attributed to a "design, manufacturing, construction/installation" concern, as defined by NUREG 1022 ("Licensee Event Report System"). The specific details as to why the connection was not crimped is unknown. Based on inspection of the uncrimped connector, it appears that this condition has existed since initial installation. The wiring connection was crimped and the original buffer relay was re-installed after successful testing. The surveillance test was completed satisfactorily. The other similar connections in the SSPS circuits (both trains) were checked for tightness. No other improperly connected wires were identified.
2721991019 | Salem 1 | 04/28/1991 | 05/30/1991 | 9106100093 | <strong>Three Cases of Technical Specification Noncompliance; all Due To Personnel Error Concerns</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 3 events involving Technical Specification Surveillance and Action Statement noncompliance. Although different Tech. Specs. and plant systems are involved, each of the events involve administrative control and personnel error causal factors. The first event was identified on 5/1/91. A Special Report required by Technical Specification 3.3.3.1b had not been issued to the Nuclear Regulatory Commission. It is required when the Radiation Monitoring System (RMS) main steamline monitor (1R46) channels are inoperable for greater than 7 days. The second event was discovered on 5/13/91. A Pressurizer pressure transmitter's (1PT-456) monthly functional surveillance had not been completed as required. The surveillance was required to be performed on or before 5/12/91. The third event was discovered on May 14, 1991. The Containment Fan Coil Unit (CFCU) service water discharge was not being sampled every 24 hours as required by Technical Specification 3.3.3.8 Action 28. This Technical Specification requires sampling when the 1R13 RMS CFCU Service Water discharge monitors are inoperable. The events addressed by this LER have been reviewed by Salem Station senior management. INPO Good Practice OE-906, will be applied at department level working meetings. Current line management review of personnel error related events and other event review programs will be assessed. Enhancements to the existing programs or implementation of new programs will be made as appropriate.
2721991020 | Salem 1 | 05/10/1991 | 06/06/1991 | 9106130295 | <strong>ESF Actuation: Control Room Vent. Switch To Accident Mode Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1991 at 1400 hours, during normal plant operation, the Co trol Room general area Radiation Monitoring System (RMS) monitor (1R1A) spiked high. This resulted in the automatic switching of the Control Room ventilation from normal operation to its accident mode of operation (100% recirculation) for both Salem Unit 1 and Unit 2 (by design). The root cause of this event is attributed to equipment failure. At the time of the channel spike, a Maintenance-I&C technician was restoring power to the 1R33 RMS channel (Ion Exchange Filter Monitor). The 1R33 channel control drawer is located in the same cabinet, physically next to the 1R1A channel. A similar event occurred on September 17, 1990 (reference LER 272/90-031-00); however, the cause of that event was different. The 1R33 channel was inspected. A failed light socket, for "power on/fail" indication was found. The socket had developed a short. This is believed to be the cause of the spike. When the 1R33 channel was turned on, the light socket short resulted in an EM/RFI (Electro-Magnetic/Radio Frequency Interference) signal causing the 1R1A channel spike. The failed 1R33 channel light socket was replaced.
2721991021 | Salem 1 | 05/22/1991 | 08/06/1991 | 9109100337 | <strong>Tech. Spec. 3/4.8.3.1 Noncompliance; Inadequate Amendment Implementation & Surv. Not Done</strong><br /><i>Abstract:&nbsp;</i>This LER supplement addresses an additional Containment penetration overcurrent protection device Tech. Spec. 3/4.8.3.1 noncompliance (1GPXA) discovered on 8/6/91. The original LER addressed 3 Tech. Spec. 3/4.8.3.1 noncompliance events. In all events, Surv. 4.8.3.1 was not fully satisfied. The first event (discovered on 5/22/91) identified a Containment penetration overcurrent protection device which was not included in the UFSAR listing. The second event involved a determination that this device had not been surveilled as per the Surv. requirements nor had the associated Action Statements been applied on 5/22/91. The third event (discovered on 6/3/91) identified that Tech. Spec. Amendment 105 implementation, in April 1991 (i.e., completion of the ninth refueling outage) was inadequate. The Surv. requirements were not met for all applicable devices. The first event root cause is an incorrect schematic (which was corrected) and the second and third events are due to personnel error (i.e., a combination of poor work practices and inadequate communications). The cause of the 1GPXA noncompliance is due to the inadequate implementation of Amendment 105 (i.e., related to third event). These events were reviewed with the individuals involved. As previously committed to by Unit 1 LER 272/91-019-00, INPO Good Practice OE-906 is being presented to station personnel. The U-1 UFSAR breaker list is being reviewed. A Personnel Performance Enhancement Panel meeting was held with station management and personnel directly involved in the event.
2721991022 | Salem 1 | 06/06/1991 | 07/08/1991 | 9107120113 | <strong>2 Engineered Safety Feature Actuations, 1B & 1C 4KV Vital Bus Undervoltage</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 2 Engineered Safety Feature (ESF) signal actuation events. Both involve Safeguard Equipment Control (SEC) system operation "Mode Op" on a single 4 KV Vital Bus due to undervoltage. The first event occurred on June 6, 1991 and involved 1C 4KV Vital Bus. The second event occurred on June 13, 1991 and involved 1B 4KV Vital Bus. At the time of both events, an undervoltage functional surveillance was being conducted. The root cause of the 1C 4KV event is inadequate human factors design. The initiating cause of this event was personnel error. The technician did not maintain adequate attention to detail while positioning himself for placement of a temporary electrical jumper. The root cause of the 1B 4KV Vital Bus event is personnel error. The technician performing undervoltage relay functional testing did not fully comply with the procedure resulting in the blowing of a PT fuse and the subsequent ESF actuation. The 1C 4KV Vital Bus and the 1B 4KV Vital Bus events will be reviewed with applicable supervisors and technicians to make them aware of the details surrounding these events. The 4KV Vital Bus cubicle design will also be reviewed to determine the feasibility for installation of more accessible terminal test connections and/or test switches. Corrective disciplinary action was taken with the technician involved in the 1B 4KV Vital Bus event. The 1B 4KV failed fuse was replaced.
2721991023 | Salem 1 | 06/10/1991 | 07/08/1991 | 9107120107 | <strong>2 Channels in a Single System Made Inoperable Due To Common Equip. Failure</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1991 at 1940 hours, it was observed that the 1R11A/1R12A/1R12B Containment Radiation Monitoring System (RMS) pump was not operating. These 3 RMS channels analyze a sample of Containment atmosphere provided by this single pump. Subsequently, the 1R11A, 1R12A and 1R12B RMS channels were declared inoperable and Technical Specification Action Statements 3.4.6.1 and 3.9.9 were entered as per Technical Specification Table 3.3-6 Action 22 (i.e., 1R11A inoperable) and Actions 22 and 23 (i.e., 1R12A inoperable). The 1R12B channel is not taken credit for in the accident analyses and therefore has no applicable Technical Specification. The cause of this event is attributed to equipment failure. Prior LERs have identified the concern for the adequacy of the pump design; however, this event is not attributed to pump design inadequacy. The pump had failed when its drive belt broke. The drive belt was last replaced on July 27, 1990. The last time the pump was replaced, including belt inspection and adjustment (as required) was March 27, 1991. The pump belts were replaced and the pump was restored to service. Subsequently, the associated Technical Specification Action Statements were exited.
2721991024 | Salem 1, Salem 2 | 06/16/1991 | 07/15/1991 | 9107190202 | <strong>Reactor Trip From 100% Power Due To Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1991, at 1940 hours, during normal full power operation, Salem Unit 1 experienced a Reactor Trip/Turbine Trip. The first out overhead annunciation was "4KV Group Bus Undervoltage". At the time of the event a severe thunderstorm was in progress. Investigation revealed that lightning had struck in the vicinity of the phase B Generator Step-Up (GSU) transformer (EL). Evidence of the lightning strike included carbonization of the high voltage bushing, damage to the corona rings and lightning arrestor and eyewitness accounts. The root cause of the reactor trip event is attributed to an act of nature; i.e., a lightning strike in the vicinity of the phase B GSU transformer, resulted in a 4KV Group Bus Undervoltage and subsequent reactor trip. Lightning protection was assessed by engineering and found to be appropriate. The damage to the Phase B GSU transformer was repaired. Subsequently, on June 24, 1991, the Unit 1 was returned to service. Also as a result of the lightning strike, 500 KV breaker flashover protection was initiated due to sufficient current through the transformer neutral. This resulted in the loss of the No. 2 Station Power Transformer and subsequent de-energization of the 1F and 1G Group Busses. An engineering review has been initiated to prevent flashover protection actuation from a coasting generator. Design changes will be implemented as appropriate.
2721991025 | Salem 1 | 07/27/1991 | 08/15/1991 | 9108260091 | <strong>ESF Signal Actuation: Cont. Vent. Isolation Signal Due To RMS Channel Failure</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1991, a Plant Vent noble gas Radiation Monitoring System (RMS) monitor (1R45) channel spiked. This caused the Plant Vent Noble Gas RMS channel (1R41C) to de-energize resulting in a Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation signal (by design). Technical Specification 3.3.3.1 Action 23 was subsequently entered. The root cause of this event is attributed to equipment failure. Troubleshooting did not find a specific component failure; however, the pins for the circuit board at the Central Processing Unit were cleaned and the monitor was reset. It could not be determined which 1R45 channel spiked causing the 1R41 channel de-energization. The 1R45B and 1R45C channels were functionally tested successfully and were successfully source checked. A channel calibration was successfully completed on the 1R45A and D channels. Upon completion of testing, the 1R45 channels were returned to service and declared operable on July 31, 1991 at 2250 hours. Technical Specification 3.3.3.1 Action 23 was exited at this time. A review of 1R45 Eberline RMS channel historical maintenance activities was conducted. Based on this review, it has been determined that the preventive maintenance requirements for these channels is adequate.
2721991026 | Salem 1 | 07/12/1991 | 08/06/1991 | 9109100385 | <strong>S/G Pressure Protection Ch. Inop. Due To Lead & Lag Switch Incorrect Setting</strong><br /><i>Abstract:&nbsp;</i>On 8/7191, at 0657 hours, a technician found the lead and la g controller switches in the test position for the No. 13 Steam Generator (S/G) Pressure Channel III. With these switches in this position, the channel is inoperable since safeguard signal initiation from this channel will not occur until 47.7 seconds after the time accredited for by the plant safety analysis. The channel safeguard signals include input to Main Steamline Isolation and Safety Injection. The root cause of this event is personnel error. The technician had inadvertently left these switches in this position since the previous functional surveillance due to inadequate self verification. The prior surveillance was completed on 7/12/91 at 0210 hours. Work had not been performed in the No. 13 S/G Pressure Channel III cabinet, since the last functional surveillance. Appropriate corrective disciplinary action will be taken with the technician involved. The S/G Pressure Protection Channel functional procedures will be revised to include independent verification of lead switch and lag switch position restoration. Engineering is continuing to review the safety significant concerns associated with the incorrect positioning of the lead and lag switches.
2721991027 | Salem 1 | 08/15/1991 | 09/12/1991 | 9109190250 | <strong>ESF Actuation: Safeguard Equip. Control Cabinet "Mode Op" Signal Due To Equip. Failure</strong><br /><i>Abstract:&nbsp;</i>On 8/15/91, two (2) partial "Mode Op I" (Loss-of-Coolant Accident) 1A Safeguard Equipment Control (SEC) Cabinet signal actuations occurred. The first occurred at 1908 hours and the second occurred at 1914 hours. The 1A SEC was declared inoperable and Technical Specification 3.3.2.1 Action 13 was entered upon the first "Mode Op I" signal actuation. In accordance with the Technical Specification 3.3.2.1 Action 13, a Unit shutdown commenced. The 1A SEC chassis was replaced on August 15, 1991, at 2253 hours, and upon successful completion of functional testing, Technical Specification 3.3.2.1 Action 13 was exited. Unit load had been reduced to 43%. The cause of these partial "Mode Op I" events is equipment failure. Troubleshooting of the 1A SEC chassis circuits identified two (2) failed circuit cards. These cards are being sent back to the manufacturer to help determine cause of failure. System Engineering has initiated a review of SEC failures (including LERs 272/90-008-00 and 272/89-026-00) to determine if there are any factors common to the failures. Upon completion of this investigation, appropriate corrective action will be implemented.
2721991028 | Salem 1 | 08/23/1991 | 09/19/1991 | 9109300259 | <strong>ESF Equipment Operation: Valve 12GB4 Failed Closed Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1991, at 1046 hours, the No. 12 Steam Generator Blowdown Outlet Isolation Valve (12GB4) failed closed. The four blowdown isolation valves (11-14GB4) had been opened, at 1004 hours, after completion of 1R19A Radiation Monitoring System (RMS) Blowdown monitor channel calibration. The 11-14GB4 valves are containment isolation valves. Containment isolation is an Engineered Safety Feature. The cause of the valve closure is equipment failure. The valve actuator's diaphragm had failed. System Engineering is continuing to investigate to determine why the 12GB4 valve diaphragm failed. Included is a review of the preventive maintenance requirements for the GB4 valves. Valve repair was completed on August 24, 1991 at which time the valve was returned to service.
2721991029 | Salem 1 | 09/07/1991 | 10/04/1991 | 9110160004 | <strong>2 Channels in a single system made inoperable due to inadequate design</strong><br /><i>Abstract:&nbsp;</i>On 9/7/91, at 0800 hours, a Control Room low flow "trouble" alarm, for the 1R11A/1R12A/1R12B Containment Radiation Monitoring System (RMS) pump, was received. Investigation revealed the pump had seized. The RMS channels monitor a sample of Containment atmosphere pulled by this pump. With the pump not operating, the RMS channels were declared inoperable and Technical Specification Action Statements were entered. The sample pump is a positive displacement vacuum pump which has a rotor and sliding graphite vanes. Pump seizure, due to vane failure, has occurred previously as addressed by LER 272/91-014-00. The pump was subsequently replaced on 9/7/91, at 2122 hours, at which time the Technical Specification Action Statements were exited. The root cause of this event is inadequate equipment design. The pump is not adequately suited to the application it is being used resulting in a high failure rate. An interim measure to mitigate the possibility of pump failure is to replace the pump every three (3) months. However, contrary to this commitment the work order to implement has been on hold since 4/17/91. The engineering support request has been dispositioned and pump replacement has been scheduled for completion every three (3) months, as previously committed. Corrective disciplinary action has been taken with those individuals involved. This event will be reviewed with applicable Maintenance Dep't. and Tech. Dep't. personnel. A review of the methods for identifying work orders related to station commitments has been initiated. A review of overdue preventive maintenance work orders is continuing.
2721991030 | Salem 1, Salem 2 | 09/20/1991 | 08/25/1995 | 9509010010 | <strong>Both Pressurizer Pressure Operated Relief Valves Failed An Operability Check</strong><br /><i>Abstract:&nbsp;</i>On 9/20/91, during a Unit 1 shutdown to support a maintenance outage, both Pressurizer Pressure Operated Relief Valves (PORVs) 1PR1 and 1PR2, failed to open upon demand. Visual inspection revealed operation of the valves was prevented as the result of air leakage from the valves' actuator diaphragm enclosures. This Yes due to loosened fasteners on the enclosures. The cause of this event was inability of the Buna-N diaphragm material to maintain its physical properties and subsequent loss of fastener preload coupled with loosening of the fasteners due to pipeline induced vibration (unknown at time of event). Immediate corrective action was installation of new Buna-N fabric reinforced diaphragm material in the Unit 1 PORVs and Pressurizer Spray Valves (PSCVs). In 1992, EPDM/fabric reinforced diaphragm material and a back-up O-ring were installed in the PORVs and PSCVs of both Units until a more reliable diaphragm material could be installed. In 1993, silicone rubber/fabric reinforced diaphragm material and prevailing torque type replacement fasteners that are frictionally resistant to rotation were installed in these valves on both Units. This event is reportable pursuant to 10CFR50.73(a)(2)(v)(D) and (a)(2)(vii)(D).
2721991031 | Salem 1 | 09/23/1991 | 10/18/1991 | 9110280261 | <strong>ESF Actuation: Main Steam Line Isolation Signal Due To Design Concern</strong><br /><i>Abstract:&nbsp;</i>On 9/23/91 at 1414 hours, a Main Steam Isolation (MSI) actuation occurred. At the time, the Unit was in Mode 4 and heating up in preparation for startup. The MSI signal occurred upon receipt of a High Steamline Flow signal coincident with a Low Steamline Pressure signal. In Mode 4, the bistables for low steamline pressure are tripped providing half the logic signal required for MSI. At the time of the event, the No. 14 Steam Generator (S/G) Steamline flow channel No. I bistable was in the tripped position to support channel functional testing. When No. 11 S/G steamline flow channels I and II bistables tripped the MSI signal logic was satisfied. MSI is an Engineered Safety Feature. Similar MSI events have occurred (reference LERs 272/90-019-00 and 272/90-027-00). The root cause of this event is attributed to design inadequacy associated with the main steamline flow transmitter sensing lines during plant heatup. Assessment of this event, by Maintenance personnel, was that the false high steam flow signals were not caused by failed components. The false signals cleared after a few hours. At the time of the event, Maintenance was performing channel monthly functional testing as per Tech. Spec. Surveillances 4.3.1.1.1 and 4.3.2.1.1. The channel I and channel II flow transmitters functional testing, for all 4 steamlines, was successfully completed on 9/23/91 and 9/28/91, respectively. Engineering is continuing to evaluate the modifications made to the main steam flow measuring system completed during the Unit 1 ninth refueling outage.
2721991032 | Salem 1 | 11/14/1991 | 12/12/1991 | 9112260010 | <strong>ESF Activation Signal for Cont. Vent. Isolation Due To Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On 11/14/91, a Maintenance Instrument and Controls (I&C) technician began a preventive maintenance (PM) task to open, clean, inspect and close the sample box for the Radiation Monitoring System (RMS) Containment Particulate Radiation Monitor, 1R11A. At 0842 hours the same day, during the performance of the PM task, a Containment Purge/Pressure-Vacuum Relief System (CP/P-VR) isolation signal actuated as a result of a high channel spike on 1R11A. The associated containment isolation valves were closed at the time and did not change position as a result of the isolation signal. The CP/P-VR System isolation is an Engineered Safety Feature (ESF). The root cause of the channel spike is attributed to a design inadequacy. As indicated by prior LERs, the RMS channels are subject to intermittent spikes due to external influences. Investigation could not identify the specific cause of this channel spike. The 1R11A channel was restored following the investigation. A channel calibration check was completed satisfactorily. Subsequently, the Action Statement was exited November 14, 1991, at 1105 hours. The event was discussed with the appropriate Maintenance I&C RMS qualified technicians. The Maintenance Department Work Standard "Paperchange" has been revised to provide instructions for blocking the channel trip function. The design of the entire RMS system is being reviewed and the appropriate design changes will be implemented to enhance the system.
2721991033 | Salem 1 | 11/16/1991 | 12/16/1991 | 9112190188 | <strong>ESF Actuation: 1B Diesel Generator Start Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1991, at 0105 hours, during the installation of a test recorder to monitor 1B Safeguards Equipment Control (SEC) circuitry, a Maintenance Department Electrical Supervisor improperly reconnected test leads, at the recorder, causing an unplanned start of 1B Diesel Generator (D/G). The test recorder was being installed in support of 1B SEC monitoring. The 1B SEC had its chassis replaced as a result of an Auto Test Fault alarm indication. The start of a D/G is an Engineered Safety Feature (ESF). The root cause of this event is personnel error (improper use of test equipment). A contributing factor to this event was the incorrect labeling of the voltage indications on the test recorder. The connections at the recorder were reversed to their correct configuration and the faulty indicator labels were corrected. The Maintenance Supervisor and the applicable Maintenance Department Controls Technicians were counseled about the importance of attention to detail, in the use of test equipment, relative to this event. The event was discussed with the applicable Maintenance Department personnel.
2721991034 | Salem 1 | 11/26/1991 | 12/31/1991 | 9201070203 | <strong>2 ESF Signal Actuations; 1R11A Channel Spikes Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 2 Engineered Safety Feature (ESF) signals initiated through the Radiation Monitoring System (RMS). These signals were for Containment Purge/Pressure-Vacuum Relief (CP/P-VR) system isolation. On 11/26/91, the 1R11A Containment Particulate RMS Monitor channel spiked high resulting in a CP/P-VR System isolation signal. The isolation valves were closed at the time of both events and did not change position as a result of the isolation signal. The 1R11A RMS channel indication returned to normal approximately 4 minutes after the spike. The 1R11A RMS channel was declared inoperable and an investigation to determine the cause of the event was initiated. On 11/26/91, a channel calibration check was satisfactorily performed for the 1R11A channel and the channel was returned to service. On 12/26/91, the 1R11A RMS channel again spiked high, momentarily, resulting in a CP/P-VR System isolation signal. The 1R11A RMS channel was declared inoperable and an investigation to determine the cause of the event was initiated. The root cause of both 1R11A RMS channel CP/P-VR System isolation signal actuations has been attributed to equipment failure (degraded cable connection). The 1R11A detector connection will be repaired and a satisfactory channel calibration check will be performed. The feasibility of replacing the existing connector with a more reliable connector will be explored. Other RMS monitors with similar detector connectors will be inspected to determine if similar degraded cable connector conditions exist.
2721991035 | Salem 1 | 11/27/1991 | 05/04/1993 | 9305120061 | <strong>Engineered Safety Feature signal initiated from the Radiation Monitoring System.</strong><br /><i>Abstract:&nbsp;</i>This LER is a supplement to LER 272/91-035-00. The Apparent Cause of occurrence section has been revised to address the results of subsequent investigation. On November 27, 1991, at 0042 hours, the Radiation Monitoring System (RMS) 1R12A Containment Noble Gas Radiation Monitor channel alarmed resulting in a Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation signal. Investigation of the event was initiated which included taking a portable Containment air sample. The sample did not indicate any increased activity. The 1R12A RMS channel was declared inoperable and Technical Specification 3.3.3.1 Table 3.3-6 Action 20 was entered on November 27, 1991, at 0334 hours. The root cause of the ESF signal actuation is equipment failure. investigation identified that the detector connector had failed. The signal ground wire, in the connector, had broken. Also, the cable shield wire was found unconnected and pushed back into the connector. The connector was subsequently replaced. The channel was then tested successfully and returned to service. A program to replace older RMS channel connectors has been initiated.
2721991037 | Salem 1 | 12/16/1991 | 01/16/1992 | 9201210142 | <strong>Plant Vent Continuous Monitoring Not Maintained Due To Inad. Admin. Control</strong><br /><i>Abstract:&nbsp;</i>On 12/16/91, at 2300 hours, Operations personnel discovered that the Plant Vent effluent release composite iodine and radioactive particulate samples were not obtained as required by Tech. Spec. Table 3.3-13. These samples are obtained by pulling a sample from the 1R41 (Plant Vent low level radiation monitor) flow path. With the 1R41 pump off, the flow through the composite sampling line recirculates preventing a representative sample unless the composite sample outlet line is disconnected. On December 16, 1991, at 1104 hours, the breaker for the 1R41 RMS channels was opened, removing the channels from service, to support maintenance activities. By design, de-energization of the 1R41A channel will cause the 1R41 sample pump to de-energize. When this occurred, the composite sample pump line was not disconnected. The root cause of this event is inadequate administrative control. Specifically, controls were not implemented to ensure that Operations personnel were aware that de-energization of the 1R41A channel will cause de-energization of the sample pump by design. Administrative controls were not implemented which could have prevented this event from occurring. The Tagging Request Information System and Procedure OP IV-11.3.4, "Operation of Radiation Monitoring System Samples", will be revised. This event has been reviewed with applicable Operations Department personnel. This event will be reviewed by the Nuclear Training Center for incorporation into applicable training programs.
2721991038 | Salem 1, Salem 2 | 12/19/1991 | 06/04/1992 | 9206240284 | <strong>Control Room Habitability Concern From Postulated Ammonium Hydroxide Release</strong><br /><i>Abstract:&nbsp;</i>On 12/19/91, an interim calculation concluded that a Control Room habitability concern was possible, due to postulated failure of a 3000 gallon ammonium hydroxide storage tank. In accordance with Regulatory Guide 1.78, the maximum concentration release was postulated from a catastrophic failure of the largest storage tank of ammonium hydroxide (27.5 wt%). The liquid ammonium hydroxide would vaporize to ammonia upon release, exhaust to the environment, and disperse to the Control Room air supply intakes. The calculation indicated that the Regulatory Guide 1.78 guideline could be exceeded. Immediate actions were taken to mitigate the potential consequences. Continued evaluation has shown that the interim calculation did not accurately simulate plant conditions. A more appropriate calculational method was since used which shows that PSE&G does conform to Regulatory Guide 1.78. The root cause of not addressing the ammonium hydroxide concern in the Final Safety Analysis Report (FSAR) is design, manufacturing, construction/installation error. Compensatory actions were taken to ensure control room habitability under postulated accident conditions when the concern was first identified. A survey for additional hazardous chemical on-site storage concerns was conducted. An Engineering Evaluation, including a 10CFR50.59 Safety Evaluation, was completed addressing ammonium hydroxide and other applicable hazardous chemical issues. A change to the UFSAR has been initiated. The chemical control program and procedures were evaluated and applicable procedure revisions made.
2751991001 | Diablo Canyon 1 | 01/03/1991 | 02/04/1991 | 9102110197 | <strong>Entry Into Technical Specification 3.0.3 When Both RHR Pumps Were De-Energized Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1991, at 0305 PST with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Residual Heat Removal (RHR) Pump 1-2 was rendered unavailable when its control power was de-energized during a time period when Diesel Generator 1-1, the emergency power source for emergency core cooling system (ECCS) train 1-1, was removed from service. This resulted in ECCS inoperability, violation of Technical Specification (TS) 3.5.2, and entry into TS 3.0.3. Control power to the pump was de-energized by an Auxiliary Operator (AO) during performance of Surveillance Test Procedure (STP) V-3M4, "Exercising Valves 8700A and 8700B, Residual Heat Removal (RHR Suction Valves," which requires the RHR pumps to be individually rendered unavailable by de-energizing control power to allow stroking of the valves while maintaining operability of the ECCS. Upon receipt of alarms in the control room, the Senior Control Operator instructed the AO to immediately restore power to the pumps. TS 3.0.3 was exited on January 3, 1991, at 0308 PST, when control power to the RHR pumps was restored. <br /><br /> The root cause of the event was personnel error due to miscommunication. Although a tailboard meeting was conducted on the actions required for STP V-3M4, the AO did not understand his actions following the meeting. An Operating Incident Summary will be prepared for this event and will be reviewed with all operations personnel. The Summary will stress the importance of performing a proper tailboard and the "two train" concept for Engineered Safety Features systems at DCPP.
2751991002 | Diablo Canyon 1 | 02/01/1991 | 05/17/1991 | 9105290214 | <strong>Reactor Trip On Steam Generator Low Level With Steam Flow/Feedwater Flow Mismatch Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1991, at 0909 PST, with Unit 1 operating at approximately 90 percent power, a Unit 1 reactor trip occurred due to Steam Generator (SG) 1-4 low level coincident with a steam flow/feedwater flow mismatch. A four-hour, non-emergency report was made in accordance with 10 CFR 50.72 (b)(2)(ii) on February 1, 1991, at 1149 PST. <br /><br /> The root cause of the event was determined to be personnel error (cognitive). Personnel erecting scaffolding in the area of feedwater regulating valve FCV-530 inadvertently closed valve AIR-I-1-1041, which isolated instrument air supply to feedwater regulating and bypass valves FW-1-FCV-530, 540, 1530, and 1540. The regulating and bypass valves failed closed on loss of instrument air, isolating feedwater flow to two SGs. SG levels decreased and the unit tripped. <br /><br /> The corrective actions include: (1) issuance of a procedure to secure sensitive air valves against accidental closure; (2) issuance of a maintenance policy requiring that all work to be performed prior to the outage must be on the approved daily schedule; (3) issuance of a Work Planning policy on marking work packages; and (4) revision of Administrative Procedure (AP) C-59, "Elevated Work Structures," to clarify responsibilities and restrictions for erection and removal of scaffolding.
2751991003 | Diablo Canyon 1 | 02/07/1991 | 03/08/1991 | 9103190414 | <strong>Loss Of RHR Flow While Filling The Refueling Cavity Due To Inadequate Shift Turnover And Late Issuance Of The 4-Hour Nonemergency Report Required By 10 CFR 50.72</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1991 at 2120 PST, while filling the refueling cavity from the refueling water storage tank (RWST), a RWST low level (33 percent) signal tripped residual heat removal (RHR) pump 1-2. Operating procedure B-2:II requires the RWST low level trip of RHR pumps be disabled during refueling cavity fill. Nightshift operators did not disable the RHR pump trip due to an inadequate shift turnover briefing. When RHR pump 1-2 tripped, operators immediately recognized the error and restarted the pump within four minutes. <br /><br /> Operators did not recognize that this event was reportable in accordance with 10 CFR 50.72. The 4-hour, nonemergency event report required by 10 CFR 50.72 was not made until 0746 PST on February 8, 1991, when the dayshift recognized the event during turnover as reportable. <br /><br /> An Operations Incident Summary has been prepared stressing the importance of a proper shift turnover and review of plant conditions following shift turnover. A memorandum has been sent to all Shift Supervisors, Shift Foremen, and Shift Technical Advisors to review the importance of notifying plant management promptly of any significant plant event and of proper documentation of events in the log.
2751991004 | Diablo Canyon 1 | 03/07/1991 | 07/29/1992 | 9208040263 | <strong>Loss Of Offsite Power During Refueling Caused By A Crane Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1991, at 0807 PST, with Unit 1 in Mode 6 (Refueling), a loss of offsite power (LOOP) to Unit 1 occurred when a mobile crane boom came too close to the 500 kV power lines. The 500 kV line arced to ground through the crane boom, and caused the LOOP. The emergency diesel generators (DGs) started and loaded to the vital busses. An Unusual Event was declared at 0830 PST, March 7, 1991. A one-hour emergency report was made in accordance with 10 CFR 50.72(a)(3) at 0900 PST. A four-hour non-emergency report was made in accordance with 10 CFR 50.72(b)(2)(ii) and (b)(2)(iii) on March 7, 1991, at 1011 PST, due to the actuation of engineered safety features and momentary loss of residual heat removal, respectively. Special Report 91-02 was submitted as the result of a DG 1-1 valid failure that occurred during the event. <br /><br /> The root cause was determined to be personnel error by the crane operator and the foreman in implementation of PG&E's accident prevention rules. <br /><br /> Corrective actions to prevent recurrence include training applicable personnel on electrical safety issues, posting warning signs and barriers around high voltage lines and transformers within the plant protected area, issuing a memorandum stressing the importance of tailboards, and revising the operating experience assessment process to assure more timely and thorough response. 1033S/85K
2751991005 | Diablo Canyon 1 | 03/23/1991 | 04/19/1991 | 9104250394 | <strong>Actuation Of Wrong Test Switch Causes Unplanned Diesel Generator Start (ESF Actuation) Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1991, at 0525 PST, with Unit 1 in Mode 5 (Cold Shutdown) at o percent power, an unplanned start of Diesel Generator 1-1 and a realignment of safety injection valves occurred when a non-licensed operator inadvertently actuated the wrong SSPS test switch. This event constitutes an engineered safety feature (ESF) actuation. The control room operators returned all actuated equipment to normal status. <br /><br /> On March 23, 1991, at 0546 PST, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii).<br /><br /> The root cause of this event was personnel error due to failure by operators to follow established procedures and policies. The concurrent verification process and self-verification processes required by Procedure NPAP C-104, "Independent Verification of Operating Activities," and Operations Policy B-1, "Conduct of Operations," were improperly implemented and resulted in the incorrect switch being actuated.<br /><br /> An Operations Incident Summary will be prepared, re-emphasizing the importance of the self-verification process and reviewing the requirements and content of the concurrent verification process. The operators involved were counseled concerning their failure to implement the guidance in Procedure NPAP C-104 and Operations Policy B-1.
2751991006 | Diablo Canyon 1 | 03/26/1991 | 04/25/1991 | 9104290286 | <strong>Actuation Of Containment Ventilation Isolation Due To A Spurious High Radiation Alarm Resulting From Radio Frequency Energy Generated By A Faulted Motor</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991, at 0015 PST, with Unit 1 in Mode 5 (Cold Shutdown) at 0 percent power, a containment ventilation isolation (CVI) actuation occurred. This event constitutes an Engineered Safety Features actuation. The actuation occurred due to a spurious high radiation alarm from containment air particulate monitor RM-11. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.73(b)(2)(ii) on March 26, 1991, at 0216 PST. <br /><br /> The root cause for the spurious high radiation alarm and resulting CVI was radio frequency interference (RFI) produced when the RM-11 sample pump seized. After the sample pump seized, the pump motor faulted and arced over to a bus ground. The arcing produced sufficient RFI to induce the spurious high radiation alarm signal. Immediate corrective actions were to verify that the high radiation alarm was spurious and reset the CVI logic; the RM-11 sample pump and motor were also replaced.
2751991007 | Diablo Canyon 1 | 04/23/1991 | 05/21/1991 | 9105300346 | <strong>High Steam Generator Level (P-14) Turbine Trip Causes Reactor Trip Due To Feedwater Pump Speed Controller Component Failure</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1991, at 0846 PDT, with Unit 1 in Mode 1 (Power Operation) at approximately 50 percent power, the unit experienced a reactor trip due to a turbine trip caused by high steam generator (SG) 1-3 level (P-14). <br /><br /> Preceeding the trip, all main feedwater (MFW) control components were in automatic except SG 1-3 feedwater regulating valve (FCV-530) which was in manual control mode with feedwater regulating bypass valve (FCV-1530) in automatic control mode. At 0834 PDT, MFW pump 1-1 speed had increased by approximately 1000 rpm, initiating a feedwater control transient. <br /><br /> On April 23, 1991, at 0849 PDT, following the turbine trip and reactor trip, plant operators manually closed the main steam isolation valves to terminate an unanticipated cooldown. At 0903 PDT, the unit was stabilized in Mode 3 at normal reactor coolant temperature and pressure. The 4-hour non-emergency report required by 10 CFR 50.72(b)(2)(ii) was made at 1015 PDT. <br /><br /> The root cause of the initiating feedwater transient was determined to be a random component failure of an operational amplifier in the MFW pump 1-1 speed controller "track and hold" board. The component was replaced and the plant was returned to operation. No corrective actions to prevent recurrence are required. As a prudent action, an operations incident summary will be prepared for review by all plant operators to aid in identifying and responding to abnormal feedwater control occurrences.
2751991008 | Diablo Canyon 1 | 04/24/1991 | 05/23/1991 | 9105300097 | <strong>Manual Reactor Trip Caused By Rod Control Power Supply Fuse Failure Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1991, at 1827 PDT, with Unit 1 in Mode 2 (Startup) at 2 percent power, a plant operator manually tripped the reactor due to inability to manually move control rods into the core due to a rod control urgent failure alarm condition.<br /><br /> Immediately preceeding the trip, on April 24, 1991, at 1819 PDT, the unit had been taken critical and reactor power stabilized for plant testing. Following initial data collection, the plant operator stepped control rods out to increase power to approximately 2.0 percent reactor thermal power (RTP) for further testing. At 1822 PDT, a rod control urgent failure alarm was received in the control room. Plant operators confirmed that manual rod control was inhibited, confirmed locally that rod control power cabinet PN1AC had an urgent failure, and initiated a manual reactor trip to terminate the power increase at approximately 2.5 percent RTP. On April 24, 1991, at 2054 PDT, a four-hour, non-emergency notification was made in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The root cause of this event is unknown. However, based on investigations of possible causes, PG&E believes that the most probable root cause is personnel error. Due to misleading information contained in a 1989 work order, a contract electrician had replaced the power supply fuses in the wrong electrical cabinet thereby inadvertently leaving low reliability fuses in the system. Corrective actions to prevent recurrence include labeling of the fused disconnect panels for the rod control system and tailboarding of maintenance personnel.
2751991009 | Diablo Canyon 1 | 05/17/1991 | 06/14/1991 | 9106240321 | <strong>Reactor Trip Due To Personnel Error And Safety Injection Due To Leaking Steam Dump Valves</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1991, at 0624 PDT, with Unit 1 operating at 100 percent power, a reactor trip occurred due to nuclear instrumentation power range two-out-of-four channels high flux at high setpoint signals: At 0625 PDT, a safety injection occurred due to two-out-of-four low pressurizer pressure signals. During the event, reactor coolant system cooldown exceeded the allowable rate of 100 degrees Fahrenheit per hour of Technical Specification 3.4.9.1.b. An Unusual Event was declared at 0625 PDT on May 17, 1991. A one-hour emergency report required by 10 CFR 50.72(a)(1)(i) was made on May 17, 1991, at 0633 PDT.<br /><br /> The cause of the reactor trip was determined to be personnel error. An I&C technician inadvertently deenergized a second nuclear instrumentation power range channel (N42) while performing surveillance testing on another power range channel (N41). The cause of the safety injection was steam dump valves that failed open and overcooled the reactor coolant system. <br /><br /> Corrective actions for the event included: (1) temporary stoppage of all I&C work until I&C personnel were tailboarded on the necessity of self-verification; and (2) installation of switch and fuse covers on each channel to act as a physical barrier to prevent inadvertent actions. <br /><br /> Corrective actions for the steam dump valves will be discussed in Licensee Event Report 1-90-017-01.
2751991010 | Diablo Canyon 1, Diablo Canyon 2 | 04/10/1991 | 06/17/1991 | 9106240341 | <strong>Lack Of Procedural Control To Maintain Seismic Qualification Of Refueling Water Storage Tank Due To Programmatic Failure</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On June 13, 1990, during the preparation of a design change, a concern with the seismic integrity of the refueling water storage tank (RWST) was identified due to the design class II refueling water purification (RWP) system being aligned to the design class I RWST during power operation. An analysis performed in December 1990 concluded that the reduction of volume in the RWST that could result from a break in the RWP system would not render the RWST inoperable. <br /><br /> On April 10, 1991, the concern was discussed with the NRC AEOD, and it was concluded that the problem was not reportable; however, the AEOD requested that PG&E submit an informational LER describing the problem. <br /><br /> The root cause was determined to be a programmatic failure to adequately implement engineering operational constraints into plant procedures.<br /><br /> The corrective actions are: (1) identification of valve operational constraints for the RWP system in the design criteria memorandum; (2) identification of sealed or locked valves on P&IDs that are not included in the sealed valve program; (3) provide the basis and method for controlling the valves identified above; and (4) incorporating the results into appropriate operating procedures.
2751991011 | Diablo Canyon 1 | 07/05/1991 | 08/01/1991 | 9108130186 | <strong>Actuation Of Wrong Test Switch Due To Personnel Error Causes Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1991, at 0103 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, an unplanned start of Engineered Safety Features (ESF) equipment occurred when a licensed operator inadvertently actuated the wrong Solid State Protection System (SSPS) test switch. The control room operators returned all actuated equipment to normal status. <br /><br /> On July 5, 1991, at 0133 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The root cause of this event was personnel error (inattention to detail). The operator performing the test had the test procedure in hand, but failed to pay adequate attention to the test content or to the steps requiring alarm verification. The operator did not discover that the test procedure did not test relays in both trains of the SSPS. <br /><br /> Corrective actions to prevent recurrence include: (1) preparation of an Operations Incident Summary on this event, reviewing the requirements for and stressing the importance of proper attention to the concurrent verification process, (2) counseling of the operators involved concerning their failure to perform their duties with adequate attention to detail, (3) issuance of an Operations Department Policy on control of the SSPS keys, requiring that the SSPS keys will be issued only for one train at a time on a job-by-job basis, and (4) issuance of an Operations Department Policy to specify in detail which type of verification is to be utilized for various operating activities.
2751991012 | Diablo Canyon 1, Diablo Canyon 2 | 07/05/1991 | 08/07/1991 | 9108120308 | <strong>Emergency Diesel Fuel Oil Inventory Surveillance Missed Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1991, the surveillance required by Technical Specification (TS) 4.8.1.1.3, including the allowed extension of TS 4.0.2, was exceeded when Surveillance Test Procedure (STP) M-10A, "Diesel Fuel Oil Storage Tank Inventory," was not completed. <br /><br /> On July 10, 1991, while entering completed STP records into storage, it was determined that the completed May monthly performance of STP M-10A had not been entered into the surveillance tracking system as closed, thus preventing the automatic scheduling of the June performance of the STP. On July 10, 1991, TS 4.0.3 was entered and STP M-10A was acceptably completed. <br /><br /> The root cause of this event was personnel error in that the requirements of Administrative Procedure C-3S4, "Use of PIMS Recurring Task Scheduler," were not met when the individual responsible for reviewing completed STPs failed to update the surveillance tracking system. <br /><br /> Test Coordinators and Shift Technical Advisors have been informed of this event and advised of the proper use of the surveillance tracking system reports. The surveillance tracking system will be enhanced to emphasize approaching STPs being overdue in its routine report.
2751991013 | Diablo Canyon 1 | 08/10/1991 | 09/06/1991 | 9109170215 | <strong>Containment Ventilation Isolation During Maintenance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1991, at 0129 PDT, with Unit 1 in Mode 1 (Power Operation) at approximately 100 percent power, a spurious Containment Ventilation Isolation (CVI) actuation occurred. This constitutes an Engineered Safety Feature (ESF) actuation. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on August 10, 1991, at 0211 PDT. <br /><br /> An Instrumentation and Controls (I&C) technician installed a jumper that shorted a coil for a slave relay and caused a momentary voltage transient in the PY-12 power panel. The momentary PY-12 power panel voltage transient actuated the output relays of radiation monitors RM-14A and RM-28A, which caused a CVI actuation. <br /><br /> The root cause of the event was determined to be personnel error, failure to follow procedures, in that an I&C technician incorrectly installed a jumper without complete knowledge of the results of the action. <br /><br /> The corrective actions to prevent recurrence include: (1) disciplining the technician involved regarding the written I&C policy on proceeding with work when unsure of the results of actions taken; (2) issuing an I&C maintenance bulletin that discusses this event and the policy which emphasizes the importance of stopping work when unsure of the results; (3) issuing an Operations Department maintenance bulletin emphasizing the importance of completion and approval of all parts of Administrative Procedure (AP) C-154, "Control of Main Annunciator System Problems," prior to performance of any annunciator system work controlled by AP C-154; (4) training all I&C technicians on the requirements of AP C-154; and (5) including AP C-154 in I&C recurring administrative procedure training.
2751991014 | Diablo Canyon 1 | 02/13/1991 | 10/10/1991 | 9110160186 | <strong>Technical Specification 3.8.1.2 Was Not Met Due To Inadequate Guidance On Operability Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1991, at 0225 PST, with the Unit 1 core offloaded (not in any operational mode), all three diesel generators were inoperable while the spent fuel crane was operating with heavy loads over the fuel storage pool. <br /><br /> A QA audit team identified this condition and an extensive review determined that the intent of Technical Specification 3.8.1.2(b) was not met. <br /><br /> The root cause of this event was lack of written guidance for control of diesel generator operability. The Technical Specification was unclear with regard to a requirement for diesel generator operability during movement of irradiated fuel within the spent fuel storage pool or crane operation with heavy loads over the spent fuel storage pool and no fuel in the reactor vessel. <br /><br /> Procedural guidance was issued to clarify the requirements of Technical Specification 3.8.1.2(b). This guidance requires that during fuel movement within the fuel storage pool or crane operation with loads over the fuel storage pool, at least one fuel handling building ventilation train must be capable of being powered from an operable emergency diesel generator.
2751991015 | Diablo Canyon 1, Diablo Canyon 2 | 09/17/1991 | 10/16/1991 | 9110250155 | <strong>Violation Of Technical Specification 3.7.10 When An Hourly Fire Watch Patrol Was Not Performed Due To Inadequate Instructions</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1991, at 0300 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, and Unit 2 defueled, the action statement for Technical Specification 3.7.10 was not met for Units 1 and 2 when the required hourly fire watch patrol was not performed in the required safety-related equipment rooms. <br /><br /> The hourly fire watch patrol was not performed because the hourly roving fire watch was unable to exit from the radiologically controlled area (RCA) of the plant and exchange duties with another fire watch in the turbine building.<br /><br /> The root cause of the event was determined to be that no written instructions existed to assure that TS related fire impairments would be inspected each hour during unexpected conditions which could delay fire watch personnel. <br /><br /> The corrective actions to prevent recurrence include (1) providing written instructions to fire watch personnel on actions to take if delayed during rounds; and (2) preparing an incident summary of this event, reviewing it with all fire watch personnel, and including the incident summary in initial roving fire watch training.
2751991016 | Diablo Canyon 1 | 09/27/1991 | 10/28/1991 | 9111060213 | <strong>Missed Surveillance Of Airlock Door Seals Due To Personnel Error Caused By Inadequate Knowledge Of Leak-Rate Monitor Operation</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1991, at 0947 PDT, the conditional surveillance required by Technical Specification (TS) 4.6.1.3.a was missed when a leak rate test of the containment personnel airlock door was not satisfactorily performed following opening of the inner and outer doors. <br /><br /> On September 26, 1991, the operator performing daily surveillance checks noted that the personnel airlock leak-rate monitor was out-of-service because of a clearance for calibration. When the surveillance test was reviewed by plant engineering on September 27, 1991, the out-of-service status of the leak-rate monitor was noted and reported to the system engineer, who inquired as to the operability status of the leak-rate monitor. The shift supervisor at that time determined that the leak-rate monitor was inoperable, after which the door seals were successfully leak-rate tested. A review determined that an acceptable leak rate test was not performed following 17 containment entries during the period from June 11, 1991, to September 27, 1991. <br /><br /> The immediate cause of the missed surveillances was a faulty solenoid valve that rendered the leak-rate monitor incapable of performing automatically. The root cause is due to personnel error caused by inadequate knowledge of the leak-rate monitor operation. To prevent recurrence, an Operations Incident Summary has been prepared, a standard clearance has been created for the leak-rate monitor, the operations training lesson guide has been revised, and appropriate plant procedures will be revised.
2751991017 | Diablo Canyon 1 | 11/14/1991 | 12/16/1991 | 9112310094 | <strong>Missed Surveillances Of Rod Position Indications Because Of An Inadequate Plant Process Computer Program</strong><br /><i>Abstract:&nbsp;</i>From approximately 1615 PST on November 14, 1991, to 2305 PST on November 16, 1991, conditional surveillances of the control rod positions required by Technical Specifications (TS) 4.1.3.1.1 and 4.1.3.2, including the allowed extension of TS 4.0.2, were missed. Control room operators were unaware that the rod position deviation monitor (RPDM) of the plant process computer (PPC) was inoperable.<br /><br /> On November 17, 1991, licensed operators completed Surveillance Test Procedure (STP) I-42, "Rod Position Deviation Monitor Functional Test," and discovered that the RPDM failed to initiate an alarm on the main annunciator panel, the PPC typewriter, and the PPC alarm video screen at the appropriate procedural step. Operations declared the RPDM inoperable and initiated four-hour conditional surveillances in accordance with TS 4.1.3.1.1 and 4.1.3.2. The four-hour surveillances were missed from approximately 1615 PST on November 14, 1991, to 2305 PST on November 16, 1991. During that time, rod positions were checked every 12 hours as required by TS when the RPDM is operable. <br /><br /> The immediate cause of this event was that after the PPC was shut down and restarted on November 14, the RPDM logic inhibited the alarm function because the PPC incorrectly statused the reactor trip breakers as open. The root cause of this event was that the vendor software was not designed for all transient situations which might be encountered. <br /><br /> To prevent recurrence, the PPC software is being revised to allow the PPC to obtain the correct sequence of event (SOE) status after computer startup transients. Training will be provided to enable operators to identify RPDM inoperability. Procedure AP C-27, "Computer Software Quality Assurance," will be revised to ensure that significant computer functions will be verified in accordance with an appropriate schedule.
2751991019 | Diablo Canyon 1 | 03/27/1991 | 06/05/1992 | 9206100032 | <strong>Containment Fan Cooler System Improper Maintenance</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1992, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that three containment fan cooler unit (CFCU) backdraft dampers were stuck in the open position. The stuck open dampers were originally assumed to have caused their associated CFCUs to be inoperable during certain design basis accidents. This condition may have existed since Unit 1 entered Mode 4 (Hot Shutdown) on March 27, 1991. A one-hour, non-emergency report was made for Unit 1 in accordance with 10 CFR 50.72(b)(1)(ii)(B). Revision 0 of this LER was submitted pursuant to 10 CFR 50.73. <br /><br /> PG&E recently completed an evaluation which demonstrates that the stuck open backdraft dampers would not have prevented the CFCUs from performing their safety function during the entire period of concern. Based on this information, this event is no longer reportable pursuant to 10 CFR 50.73 and Revision 1 is submitted as a voluntary LER for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> The root cause of this event is the failure to perform proper maintenance. The corrective actions include: (1) formation of a CFCU High Impact Team; (2) revision of CFCU surveillance test and post-maintenance testing procedures; (3) preparation of a detailed maintenance procedure; (4) formation of an Integrated Problem Response Team; (5) training in evaluating degraded plant conditions; (6) assuring maintenance personnel are qualified in HVAC systems; and (7) developing an action plan to ensure the adequacy of attention to HVAC systems.
2751991020 | Diablo Canyon 1 | 11/30/1991 | 03/31/1992 | 9204070323 | <strong>Technical Specification 3.7.9.4, Action A. Not Performed On Time Due To Lack Of Available Design Information</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1991, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.9.4 was not met when a continuous fire watch with backup fire suppression equipment was not established in the Unit 1 solid state protection system (SSPS) room within one hour of discovering a damaged ceiling tile in that room. <br /><br /> The damaged tile was temporarily reinstalled on November 30, 1991, and on December 13, 1991, the damaged tile was replaced with a new tile, which made the ceiling functional. <br /><br /> On March 3, 1992, the results of PG&E engineering evaluations concluded that the Unit 1 SSPS room Halon system was inoperable from November 30 to December 13, 1991 because the damaged ceiling tile had not been replaced and the ceiling was not functional. <br /><br /> The root cause of this event was lack of available design information. The TS-required action was not implemented because available documents did not specify the gas barrier function that the SSPS room ceiling performs in maintaining Halon concentration for fire suppression. Since the 1978 design change that specified the design of the SSPS room ceiling, the PG&E design process has undergone significant changes to ensure design documents and procedures supporting design changes are also changed to include required revised design information. To prevent recurrence, an Operations Night Order has been issued to describe SSPS room ceiling integrity and its effect on SSPS room Halon system operability.
2751991021 | Diablo Canyon 1, Diablo Canyon 2 | 09/16/1991 | 08/28/1992 | 9209020333 | <strong>Failure Of Motor Pinion Keys In Limitorque SMB-3-80 Motor Operators Due To Inadequate Design Of Material</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On September 16, 1991, due to a miscommunication resulting from inadequate procedures, the motor operator for cold leg isolation valve SI-2-8809B electrically engaged while the valve was being manually stroked open during post-modification testing. The motor operator electrically engaged and closed the valve ('short stroking'). Investigation determined that this electrical 'short stroking' of the valve caused the motor pinion key to shear. <br /><br /> On October 3, 1991, other safety-related Unit 2 SMB-3-80 motor operators were inspected. The motor operators for accumulator discharge isolation valves SI-2-8808B and SI-2-8808D were identified as having failed keys similar to the failed key identified in SI-2-8809B. Further investigation revealed small cracks emanating from both corners of the keyway on the SI-2-8809B motor shaft. <br /><br /> The root cause of the sheared motor pinion key was that the key material was inadequate. The key was supplied with the motor operator by the vendor. The key material is considered outdated but still acceptable according to the vendor's design. <br /><br /> Corrective actions to prevent recurrence include: (1) replacing the motor pinion keys with stronger material on safety-related SMB-3-80 motor operators; and (2) revising operating and maintenance procedures to prevent valve 'short stroking.' 1031S/85K
2771991001 | Peach Bottom 2 | 01/18/1991 | 02/18/1991 | 9102260196 | <strong>Voluntary LER Concerning the Potential for the Inoperability of the High Pressure Coolant Injection System Due to the Use of Two Non-Environmentally Qualified Relays</strong><br /><i>Abstract:&nbsp;</i>On 1/18/91, at 2130 hours, it was determined as a result of review of procurement engineering documents that the Unit 3 High Pressure Coolant Injection (HPCI) system was potentially inoperable due to the use of two non-environmentally qualified (EQ) relays in the control circuitry for the HPCI Auxiliary Oil Pump (AOP). The equivalent Unit 2 relays were similarly deficient. The cause of the condition was an inadequate EQ review of the components in the HPCI room performed in March, 1990. The Unit 3 relays were replaced with qualified relays on 1/20/91. The Unit 2 relays will be replaced with qualified relays prior to restart from the current refuel outage. A walkdown of both the Unit 2 and 3 HPCI rooms will be performed to ensure that equipment in the rooms which is required to be EQ has been appropriately evaluated. There was one previous similar event.
2771991002 | Peach Bottom 2 | 01/21/1991 | 02/18/1991 | 9102250287 | <strong>Shutdown Cooling Isolation During Blocking Due to Poor Drawing Legibility</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1991, at 0822 hours, a Residual Heat Removal System (RHR) shutdown cooling isolation occurred on Peach Bottom Unit 2 when a system blocking permit for the Automatic Depressurization System (ADS) was being applied during a refueling outage. The permit was then restored to normal and the isolation reset. Shutdown cooling was returned to service within 22 minutes after the isolation, and reactor water temperature increased only 2 degrees F. <br /><br /> The isolation occurred because the permit writer, when preparing the permit, did not recognize that opening the circuit breaker specified would remove power from both the ADS and RHR logics. This occurred because the drawing did not show that the circuit breaker supplied power to both RHR and ADS logics. The drawing will be enhanced to correct this problem. <br /><br /> The blocking permit was rewritten to isolate ADS logic using fuses and applied without incident. There were no actual safety consequences as a result of this event. Thirteen previous similar LERs were identified.
2771991003 | Peach Bottom 2 | 01/21/1991 | 02/18/1991 | 9102250279 | <strong>'2B' Reactor Pressure System Bus Trip on Undervoltage due to '3B' Recirc Pump Start</strong><br /><i>Abstract:&nbsp;</i>On 1/21/91, at 0252 hours, a Unit 2 Primary Containment Isolation System (PCIS) Group III outboard isolation occurred along with initiation of the Standby Gas Treatment System (SBGT) when the 'B' Reactor Protection System (RPS) bus tripped on undervoltage. These actions occurred when the Unit 3 'B' recirculation pump motor-generator (M-G) set was started. Starting the recirc M-G set lowered the voltage on the Unit 2 startup source which caused an undervoltage condition on the same bus that was supplying the '2B' RPS logic and the outboard PCIS logic. The '2B' RPS was being supplied by the alternate supply with the static inverter bypassed. The low voltage condition caused an undervoltage trip of the alternate source breaker thereby removing power to the '2B' RPS and outboard PCIS logic. No actual safety consequences occurred as a result of this event. The procedure used for starting a recirculation motor-generator set has been revised to inform operations personnel that when starting a M-G set which is powered by the same startup source as the RPS Alternate power supply they may receive a half scram, half Group III isolation, and a SBGT start if RPS is being supplied from its alternate source with the static inverter bypassed. There are four previous similar events.
2771991004 | Peach Bottom 2 | 02/02/1991 | 03/02/1991 | 9103110005 | <strong>Automatic Actuation of Emergency Service Water Pump Due to Wrong and Incomplete Procedure Information</strong><br /><i>Abstract:&nbsp;</i>On 2/2/91 at 1445 hours, during the performance of a bus undervoltage surveillance, the 'B' Emergency Service Water (ESW) pump received an unexpected automatic start signal. The start signal was the result of the use of the wrong control switch to close the 'B' ESW pump breaker during the surveillance. The cause of the event was wrong and incomplete procedural information in the procedure being performed and technical error during the procedure development process. No actual safety consequences occurred as a result of this event. The procedure will be revised before its next use. Guidance for procedure development and technical review will be enhanced. There were no previous similar events.
2771991005 | Peach Bottom 2 | 02/12/1991 | 03/14/1991 | 9103190403 | <strong>PCIS Isolation During Unblocking Due To An Existing Ground Caused By Modification Installation Error</strong><br /><i>Abstract:&nbsp;</i>On 2/12/91, at 0910 hours, the Unit 2 Primary Containment Isolation System (PCIS) actuated as a result of a blown fuse during removal of a blocking permit. This resulted in a Standby Gas Treatment System start and the appropriate outboard isolation valve line-ups. The cause of the event was the introduction of a ground in the PCIS circuitry due to recent modifications work. The ground was isolated and corrected and the fuse was replaced. The isolation was reset at approximately 1030 hours. No actual safety consequences occurred as a result of this event. Modifications installation and plant staff personnel involved have been informed of this event. The appropriate Nuclear Engineering Department personnel will be informed of this event to stress the importance of performing field walkdowns during modification design. There was one previous similar event.
2771991006 | Peach Bottom 2 | 02/20/1991 | 03/21/1991 | 9103270074 | <strong>Scram As A Result Of De-energizing The 'C' IRM Due To Failure To Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On 2/20/91 at 1310 hours a reactor scram occurred when the 'C' Intermediate Range Monitor (IRM) became de-energized during maintenance on the 'G' IRM. At the time of the event the 'B' RPS logic was in the tripped condition as a result of Scram Response Time testing which provided one of the two required signals for a full scram. A Maintenance Electrician was performing a power supply cable replacement on the 'G' IRM. While in the process of replacing of cable, the electrician lifted two leads that were connected to a common terminal. One lead was the power feed to the 'G' IRM. The second lead was the power feed to the 'C' IRM. Removing the power feed to the 'C' IRM caused the 'A' RPS logic to trip, resulting in a full automatic reactor scram. The cause of the event was failure to follow procedure in that the blocking permit was not adequate to support the work being performed on the 'G' IRM. The scope of the work was expanded following the Safety Related System Blocking Review. An updated review was not performed following the expanded scope, resulting in an inadequate block being applied to the system. Individuals involved will be counseled on the adequacy of performing Safety Related System Blocking Reviews following work scope changes. No previous similar LERs have been identified.
2771991007 | Peach Bottom 2 | 02/21/1991 | 03/22/1991 | 9103270347 | <strong>Shutdown Cooling Isolation Due To A Less Than Adequate Blocking Permit</strong><br /><i>Abstract:&nbsp;</i>On 2/21/91 at 0001 hours the Residual Heat Removal (RHR) Motor Operated (MO) Inboard Isolation Valve MO-2-10-25B closed on an isolation signal when a wire being lifted for a blocking permit was inadvertently grounded. The blocking permit required a Plant Operator to lift and tape a lead. During this activity the wire became grounded and caused a fuse to blow which resulted in closure of MO-2-10-25B. The Cause of the event was that the specified blocking permit was less than adequate. The leads that were lifted for the blocking permit were in a hard to access location. The consequences were minimal. The affected equipment operated as designed. Shutdown cooling was available after approximately 1 hour. Reactor coolant temperature did not exceed allowable limits while Shutdown Cooling was isolated. Permit writers have been directed to walkdown permits which required lifting leads to verify accessibility. There were 14 previous similar LERs identified.
2771991008 | Peach Bottom 2 | 04/07/1991 | 05/03/1991 | 9105100357 | <strong>Technical Specification Violation Due to Failure to Perform Reactor Coolant Temperature Logging Caused by Failure to Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On 4/7/91 at 1915, Shutdown Cooling (SDC) was removed from service to allow performance of Surveillance Testing. At this time, 15 minute reactor vessel skin temperature readings were started. At 2130 it was discovered that the reactor vessel coolant temperatures were required rather than the reactor vessel skin temperatures. The correct readings were then started and review of the applicable temperature recorders verified that no heat-up violations had occurred. The cause of the event was personnel error in that the involved operator used the incorrect data sheet for temperature monitoring. This event has been reviewed by the involved shift team and other shift teams will also review this event. Applicability of the process computer to assist the operator will be investigated. There were no previous similar events.
2771991009 | Peach Bottom 2, Peach Bottom 3 | 04/20/1991 | 05/20/1991 | 9105290107 | <strong>Primary Containment Isolation System Isolation Due to a Failure of the No. 2 Startup Emergency Feed Cable and a Unit 2 and 3 Shutdown for Cable Replacement</strong><br /><i>Abstract:&nbsp;</i>On 4/20/91 at 1015 hours, actuations occurred on the Unit 2 and 3 Primary Containment Isolation System (PCIS)(EIIS:JM). A failure of the No. 2 Startup Emergency Transformer (EIIS:XFMR) secondary side cables caused a fault which opened the No. 2 Startup Emergency Breaker (EIIS:BKR). The 4 KV Emergency Busses (EIIS:BU) associated with the No. 2 Startup Emergency Feed fast transferred to the No. 3 Startup Emergency Feed as designed. The PCIS logic momentarily de-energized during this fast transfer which resulted in a one half PCIS Group 2 and 3 isolation on both units. System isolations were reset immediately following the event. A review of other plant cable configurations have indicated that the Startup Emergency Feeds are the only cables requiring replacement at this time. Power supply cables on both units from the Startup Emergency Breaker down to the 4KV Emergency Busses have been replaced with a new type cable. <br /><br /> The 4 KV Emergency Busses have been returned to their normal Startup Emergency Feeds. No actual safety consequences occurred as a result of these events and there were no previous similar events identified.
2771991010 | Peach Bottom 2 | 04/26/1991 | 05/28/1991 | 9106040112 | <strong>Technical Specification 100 degrees F Per Hour Heatup and Cooldown Rate Violation Due to Failure to Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On 4/26/91 while in single Recirculation (Recirc) loop operation, several attempts were made to heatup the idle Recirc loop which resulted in Technical Specification thermal heatup and cooldown rate violations. The cause of these events was that the idle Recirc loop warming procedure was not followed exactly. This event has been discussed with the individuals involved. The pertinent information from this LER will be issued to the appropriate personnel and incorporated into Licensed Operator Initial and Requalification Training. Additionally, the second Recirc pump start and the single loop operating procedures will be reviewed and revised as necessary to ensure that idle Recirc loop warming is only attempted under more easily controlled conditions. No actual safety consequences occurred as a result of these events.
2771991011 | Peach Bottom 2, Peach Bottom 3 | 05/08/1991 | 06/06/1991 | 9106100347 | <strong>Technical Specification due to a missed surveillance on the Fire System as a result of a procedural deficiency.</strong><br /><i>Abstract:&nbsp;</i>On 5/8/91 at 0900 hours, it was discovered that ST 16.2.1, "Fire System Weekly Check", was inadvertently deferred to a time beyond its Technical Specification required due date. The cause of this event has been attributed to a misleading test frequency listed on ST 16.2.1 which conflicted with the scheduled date for the performance of the test. No actual safety consequences occurred as a result of this event. ST 16.2.1 was revised to remove the misleading test frequency reference. There were no previous similar events.
2771991012 | Peach Bottom 2, Peach Bottom 3 | 05/14/1991 | 06/10/1991 | 9106190282 | <strong>Technical Specification Violation due to Failure to Perform Testing as a result of Improper Development of Original Procedure</strong><br /><i>Abstract:&nbsp;</i>On 5/14/91 during the performance of a Local Leak Rate Test (LLRT), it was discovered that a primary containment isolation valve on both the Unit 2 and 3 Traversing Incore Probe (TIP) System purge lines was not being leak rate tested. This is a violation of Technical Specification 4.7.A.2.F, which requires that LLRT's be performed on primary containment isolation valves once each operating cycle. Although LLRT's had been performed each operating cycle on the TIP System purge line isolation valves, the outboard isolation valve (SV-109) was not actually being leak rate tested due to a rotometer type flow indicator (FI-110) installed between the test input tap and SV-109. The cause of the event was an inadequate review of the TIP system purge piping configuration during the development of the LLRT procedure. No actual safety consequences occurred as a result of this event. The SV-109's on both Unit 2 and 3 were subsequently tested and leakage was verified to be within acceptable limits. The LLRT procedure for SV-109 will be revised to allow leak rate testing downstream of FI-110. A modification will be considered to either relocate the test tap or FI-110 to provide a more suitable means of adequately leak rate testing SV-109. No previous similar events were identified.
2771991013 | Peach Bottom 2 | 03/19/1991 | 06/13/1991 | 9106190190 | <strong>Unqualified Fire Seals Due to Original Design Result in Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 5/30/91 an engineering evaluation including physical testing determined that two penetration fire seals were not qualifiable as required by 10 CFR 50 Appendix R. The two seals had recently been discovered to contain voids and uncured polyurethane sealant material. This could have resulted in not having the capability to achieve plant shutdown per 10 CFR 50 Appendix R had a fire occurred in the affected fire areas. The cause of the event is improper original seal installation during plant construction. There were no actual safety consequences. The affected seals have been replaced. Compensatory firewatches have been put in place on similar seal configurations. The similar seals will be inspected and repaired as necessary. There were three previous similar events.
2771991014 | Peach Bottom 2 | 05/21/1991 | 06/13/1991 | 9106190218 | <strong>Engineered Safety Feature Actuation During Surveillance Testing Due to a Leaking Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 5/21/91, at 1815 hours, with Unit 2 operating at 25% power, an isolation of the High Pressure Coolant Injection (HPCI) system occurred unexpectedly during the performance of a Surveillance Test (ST). This is an Engineered Safety Feature (ESF) actuation. The cause of the event was a leaking isolation valve which allowed the switch being tested to become pressurized, causing the isolation signal to occur sooner than expected. There were no actual safety consequences as a result of this event. The isolation valve was replaced on 6/8/91 and the ST was performed satisfactorily. There were four previous similar events.
2771991015 | Peach Bottom 2 | 05/15/1991 | 06/13/1991 | 9106190224 | <strong>Primary Containment Isolation System Actuation During Surveillance Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 5/15/91 at 1805 hours during a Primary Containment Isolation System (PCIS) (EIIS:JM) Logic System Functional Surveillance Test (ST), the Reactor Building and Refueling Floor ventilation systems tripped and the Standby Gas Treatment System (SBGTS) (EIIS:BH) automatically initiated when an incorrect fuse was pulled. The Engineer inadvertently pulled fuse 16A-F34A at location F-29 instead of 16A-F33A at location F-28 as specified in the ST. Pulling the incorrect fuse resulted in a one half Group 3 isolation. The cause of this event has been attributed to the Engineer's failure to properly identify the fuse to be pulled. System isolation was reset following the event. The event has been discussed with the involved individuals. The learning experience from this event has been presented to other System Engineers by the individual responsible for the event. A project is now in place to label these fuses along with other fuses in the Main Control Room and the Cable Spreading Room. The existing ST rewrite project will perform a human factors review on this ST and other similar long STs. No actual Safety consequences occurred as a result of this event.
2771991016 | Peach Bottom 2, Peach Bottom 3 | 05/17/1991 | 06/19/1991 | 9106240269 | <strong>Technical Specification Violation as a Result of a Missed Surveillance Test due to Programmatic Weaknesses</strong><br /><i>Abstract:&nbsp;</i>On 5/17/91 for Unit 2 and 5/24/91 for Unit 3, a Technical Specification violation occurred when the mode switches were placed in the STARTUP mode with the Reactor Water Level Instrument Perturbation Surveillance Tests (ST) being out of surveillance. When identified that the STs were out of surveillance, the tests were immediately completed satisfactorily. The cause of this event has been attributed to the inadequacy of the STs and processes which ensure that these tests are completed prior to placing the mode switch in STARTUP. Several programmatic and procedural enhancements will be incorporated. No actual safety consequences occurred as a result of this event. There have been several previous similar LERs involving missed STs. The corrective actions taken as a result of these LERs addressed the specific causes only. Although this event is also specific in nature, a Task Force is presently evaluating the issue of missed STs and will provide recommendations regarding ST performance, scheduling, and tracking.
2771991017 | Peach Bottom 2, Peach Bottom 3 | 05/18/1991 | 06/20/1991 | 9106260156 | <strong>Potential for the Inoperability of the High Pressure Injection System due to the use of Unqualified Relays in the Cardox Logic</strong><br /><i>Abstract:&nbsp;</i>On 5/21/91, it was discovered that the High Pressure Coolant Injection (HPCI) system had been unknowingly rendered inoperable on 5/18/91 during the performance of a Surveillance Test (ST). As a result of additional investigation, it was determined on 5/22/91 that the Unit 2 & 3 HPCI systems were possibly inoperable due to non-Qualified (Q) and non-Environmentally Qualified (EQ) relays in the HPCI Room Cooler fan logic. The cause of these events has been attributed to a procedural inadequacy and a less than adequate design review and subsequent system reviews. Temporary Plant Alterations have been installed to maintain HPCI operable and a modification will be initiated to upgrade the relays or remove the trip signal. The ST involved will be enhanced. A review has been completed on other fire suppression system interlocks and no additional non-Q interlocks were identified. Finally, investigations will be performed to determine why the existing processes failed to identify these relays. No actual safety consequences occurred as a result of this event. There were three previous similar LERs.
2771991018 | Peach Bottom 2, Peach Bottom 3 | 05/23/1991 | 06/21/1991 | 9106270209 | <strong>Voluntary Report Concerning Entry Into Technical Specification 3.0.C. due to Belief That Diesel Generators Inoperable due to Non-Safety Classified Switches</strong><br /><i>Abstract:&nbsp;</i>On 5/23/91 at 1545 hours, Technical Specification 3.0.C was entered and a plant shutdown initiated due to a belief that the 4 station Emergency Diesel Generators (EDG's) could potentially be rendered inoperable during design basis events. This could result in the inability of Unit 2 and 3 safety systems to perform their function during design basis events coincident with a loss of off-site power event. The cause of the event was due to misclassification of the EDG day tank temperature switches (TS's) as not safety related during the safety related component list generation in 1987-1988. It was believed that this could result in inadvertent tripping of the day tank transfer pump thereby not allowing fuel oil to be automatically transferred for longer term EDG operability. A temporary plant alteration was completed by 2200 hours to remove the TS from the circuit. Further engineering review concluded on 6/17/91 that the existing TS's were operable and could function properly in design basis events. Therefore the EDG's were operable. The EDG day tank TS's will be reclassified as safety-related. Other components will be reviewed. There were no safety consequences or previous events.
2771991019 | Peach Bottom 2 | 06/03/1991 | 07/03/1991 | 9107110149 | <strong>Primary Containment Isolation Valve Logging Not Being Performed as Required by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 6/3/91, a Technical Specification (Tech Spec) violation occurred when the Unit 2 Reactor Operator (RO) failed to initial Surveillance Test (ST) 5.3. "Inoperable Isolation Valve Position Daily Log", which signifies that containment penetrations with inoperable isolation valves are still isolated as required by Tech Specs. The cause of this event is personnel error due to failure to follow procedure. The ST requires the RO to initial daily to verify that the penetration is isolated. The individuals involved in this event were counseled and coached following the incident on the performance of administrative tasks associated with the RO's responsibilities. Additional corrective action included development of a Reactor Operator task list to be posted at the Reactor Operator's console. Pertinent information from this LER will also be routed to the appropriate Operations personnel. There were no safety consequences as a result of this event. <br /> ?
2771991020 | Peach Bottom 2, Peach Bottom 3 | 06/07/1991 | 07/08/1991 | 9107150051 | <strong>Two Diesel Generators Inoperable Concurrently as a Result of a Mispositioned Valve due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 6/7/91 at 0930 hours, it was discovered that the E-4 Emergency Diesel Generator (D/G) was inoperable due to a fuel oil transfer valve being in the closed position which would have prevented the transfer of fuel oil from the E-4 Diesel Oil Storage Tank to the D/G Day Tank. Additionally, the E-3 D/G was out of service for minor maintenance. Since both the E-4 and E-3 D/Gs were inoperable at the same time, the plant was outside its design basis. Having two D/Gs inoperable concurrently is a condition prohibited by Technical Specifications. The cause of this event has been determined to be that the E-4 D/G fuel oil transfer pump discharge valve was inadvertently left in the locked closed position during a previous Surveillance Test. The valve was immediately opened and the other D/G fuel oil transfer systems were verified to be in the proper lineup. The involved individuals have been counselled. No actual safety consequences occurred as a result of this event. There have been no previous similar events identified.
2771991021 | Peach Bottom 2 | 06/24/1991 | 10/09/1991 | 9110170241 | <strong>Potential Primary Containment Leakage as a Result of Non- Seismically Qualified Pressure Transmitters not being Isolated due to Incorrect Labels</strong><br /><i>Abstract:&nbsp;</i>On 6/24/91 at 1410 hours, two pressure transmitters were determined to be non seismically supported. This was discovered by an Installations Engineer during an instrument rack walkdown for a future modification. The Suppression Chamber Wide Range Pressure Transmitter and Suppression Chamber Containment Atmospheric Dilution Vent Pressure Transmitter were the instruments identified. This could have resulted in excessive leakage from the Primary Containment if a design basis accident would have occurred coincidental with a seismic event. The cause of the event was improper rack installation. The racks were installed during initial plant construction and the installation of this rack was less than adequate. Shift Permits were applied to the incorrect instrument lines due to labeling error. The incorrect labeling was identified on 9/9/91 and the labels were immediately corrected. A review will be performed on similarly mounted safety related instrument racks and a Non Conformance Report has been initiated which will provide the interim repair method and the final repair disposition. No actual safety consequences occurred as a result of this event. There have been no previous similar events identified.
2771991022 | Peach Bottom 2 | 06/27/1991 | 08/21/1991 | 9108260130 | <strong>Manual Scram due to Loss of Condenser Vacuum Following Isolation of the Offgas Recombiner caused by Relief Valve Lifting Prematurely</strong><br /><i>Abstract:&nbsp;</i>On 6/27/91 at 1052 hours, an Offgas Recombiner isolation occurred causing main condenser vacuum to begin decreasing. A fast reactor power reduction was initiated in accordance with the procedure for a loss of main condenser vacuum. At 1106 hours, a manual scram was initiated by placing the mode switch in shutdown following the receipt of a reactor auto half scram signal. A Group II and III isolation occurred as a result of the manual scram. The cause of the event has been determined to be a defective relief valve and the lack of complete guidance for restoring the isolated system. The event has been discussed with the involved individuals and the pertinent information will be provided to Operations and other members of the technical Staff. The operating procedure for recovery will be revised to prevent future recurrences. No actual safety consequences occurred as a result of this event. There were two previous similar events.
2771991023 | Peach Bottom 2, Peach Bottom 3 | 07/02/1991 | 07/23/1991 | 9107290266 | <strong>Control Room Emergency Ventilation Initiation due to Component Failure</strong><br /><i>Abstract:&nbsp;</i>On 7/02/91 at 2240 hours, the Control Room Ventilation system (CRVS) transferred to the Emergency Ventilation mode due to component failure in the "A" Main Control Room (MCR) radiation monitor. A Temporary Plant Alteration was installed which allowed CRVS to be returned to its normal configuration. The defective components were repaired. The cause of the event has been determined to be a component failure in the "A" MCR radiation monitor. A modification has been initiated to replace the existing instrumentation. There were six previous similar events identified. There were no adverse safety consequences as a result of this event.
2771991024 | Peach Bottom 2 | 06/30/1991 | 08/01/1991 | 9108060068 | <strong>Technical Specification Violation Due to Missed Average Power Range Monitor Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On 6/30/91 at 1125 hours, a Technical Specification violation occurred when the mode switch was placed in the STARTUP mode with the Average Power Range Monitors Surveillance Tests (ST) out of surveillance. The causal factors for this event include personnel error due to failure to self check when signing the plant startup procedure and procedural weaknesses. The event has been discussed with the involved individuals. The plant procedures and STs will be revised. No actual safety consequences occurred as a result of this event. There have been several previous similar LERs involving missed STs. A task force is evaluating the issue of missed surveillances.
2771991025 | Peach Bottom 2 | 07/28/1991 | 08/26/1991 | 9109030203 | <strong>Engineered Safety Feature Actuation Which Occurred During the Performance of a Surveillance Test as a Result of Failure to Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On 7/28/91, at 0027 hours, an isolation of the High Pressure Coolant Injection (HPCI) system occurred unexpectedly during the performance of a Surveillance Test (ST). This is an Engineered Safety Feature (ESF) actuation. The causes of the event include failure to follow procedure, procedural weakness and less than adequate shift turnover between technicians. The event has been discussed with the involved individuals. The pertinent information from this event will be presented to the appropriate Operations personnel and I&C technicians. The STs will be reviewed and revised to include a check of the control room pushbutton lights. There were no actual safety consequences as a result of this event. There were thirteen previous similar events identified. Attention to detail corrective actions are in progress.
2771991026 | Peach Bottom 2 | 07/27/1991 | 08/26/1991 | 9109030207 | <strong>Primary Containment Isolation System Isolation due to a Failure of the No. 3 Startup Feed Disconnect</strong><br /><i>Abstract:&nbsp;</i>On 7/27/91 at 2100 hours, actuations occurred on the Unit 2 Primary Containment Isolation System (PCIS)(EIIS:JM) when the 4 KV Emergency Busses (EIIS:BU) associated with the No. 3 Startup Feed was dead bus transferred to the No. 2 Startup Feed. The PCIS logic momentarily de-energized during this fast transfer which resulted in one half PCIS Group 1, 2, and 3 isolations and a one half scram signal due to a Reactor Protection System (RPS) motor-generator set output breaker trip. The Emergency Busses were manually transferred when a failure of the No. 3 startup feed disconnect caused "B" phase arcing. The cause of the arcing is due to the disconnect not being fully closed by the operator due to mechanical binding and no existing operating procedure for the disconnects. The cause of the RPS Motor Generator (M/G) set trip has been determined to be the RPS M/G set supply breaker time delay relay timed out prior to the supply bus re-energization. System isolations were reset immediately following the event. The disconnect has been repaired and the 4 KV Emergency Busses have been returned to their normal Startup Emergency Feeds. A disconnect operating procedure will be generated. The design of the RPS M/G trip will be reviewed. No actual safety consequences occurred as a result of these events and there were no previous similar events identified.
2771991027 | Peach Bottom 2 | 07/29/1991 | 05/27/1992 | 9206010080 | <strong>Violation of Tech Specs due to Weaknesses in the Planning and Equipment Maintenance Process and Control of Equipment Status Changes</strong><br /><i>Abstract:&nbsp;</i>On 7/30/91, at 0600 hours, it was discovered during a panel walkdown that a half Group IV High Pressure Coolant Injection (HPCI) system isolation signal had not been manually inserted as required by Technical Specification (Tech Spec) 3.2.B. Tech Spec 3.2.B was violated when temperature switches TS-4943C and TS-4944C were removed from service for maintenance at 1200 hours on 7/29/91 until 0000 hours on 7/30/91 when HPCI was taken out of service for unrelated reasons. The cause of the event has been determined to be the lack of guidance for operations personnel concerning the control of equipment status changes required to satisfy Tech Spec operability statements. Guidance will be developed. No actual safety consequences occurred as a result of this event. No previous similar events were identified.
2771991028 | Peach Bottom 2 | 08/05/1991 | 04/16/1992 | 9204270457 | <strong>Engineered Safety Feature Actuations as a Result of Pulling the Incorrect Fuse and Two Component Failures</strong><br /><i>Abstract:&nbsp;</i>On 8/5/91 at 1432 hours, a trip of an emergency bus breaker caused an automatic 4 KV fast transfer which resulted in a Primary Containment Isolation System (PCIS) half Group 1, Group II, and Group III isolations. At 1510 hours, a reactor scram occurred due to a turbine trip from moisture separator high level which resulted in PCIS Group II/III isolations. The scram and isolations were reset and the affected systems were restored to normal. The cause of the event has been determined to be that an Electrician pulled an incorrect fuse during Preventive Maintenance activities. The 'D' moisture separator dump valve failed closed due to a positioner failure. The event has been discussed with the involved individuals and the pertinent information has been provided to the appropriate personnel. The failed components have been repaired and the Preventive Maintenance activities have been reviewed and revised as necessary. No actual safety consequences occurred as a result of this event. One previous similar LER was identified.
2771991029 | Peach Bottom 2 | 08/24/1991 | 09/11/1991 | 9109130199 | <strong>Engineered Safety Feature Actuation due to a Failed Rheostat on the Reactor Protection System Motor Generator Set</strong><br /><i>Abstract:&nbsp;</i>On 8/24/91 at 1407 hours, a Unit 2 "B" channel Reactor Protection System (RPS) half scram occurred when the 'B' RPS Motor Generator (M/G) set output breaker tripped. The tripped breaker caused Primary Containment Isolation System half Group I and half Group III isolations which included a Standby Gas Treatment System initiation. The cause of the event has been determined to be an overvoltage condition of the 2B RPS bus due to a broken wire inside the rheostat and less than adequate rheostat installation during a recent maintenance activity. Following the event, the 2B RPS was aligned to its alternate feed which allowed the half scram and isolations to be reset. Subsequently, the affected systems were restored to normal. The rheostat was replaced and RPS was restored to its normal power supply. No actual safety consequences occurred as a result of these events. No previous similar LERs have been identified.
2771991030 | Peach Bottom 2 | 08/27/1991 | 09/25/1991 | 9110010160 | <strong>Two Diesel Generators Inoperable Concurrently as a Result of Generator Rectifier</strong><br /><i>Abstract:&nbsp;</i>On 8/27/91 at 2240 hours, it was believed that the E-2 Emergency Diesel Generator (D/G) was inoperable due to a ground in the Generator field. Additionally, the E-3 D/G was out of service for annual maintenance activities. Since two D/Gs were believed inoperable dt the same time, the plant was outside its design basis. The ground was identified to be in the "No. 2" Generator rectifier bank so the "No. 1" bank was placed in-service. This made the E-2 D/G available for operation. An evaluation was performed which proved that the E-2 D/G would have been operable with only the "No. 1" Generator rectifier bank. Therefore, the E-2 D/G was only inoperable during troubleshooting activities. The cause of the ground could not be recreated during a static test of the "No. 2" Generator rectifier circuit. Additional investigations will be performed on the circuit with the D/G in service. The grounded circuit was isolated and the circuit will be inspected. The other D/G rectifier circuits have been inspected. No actual safety consequences occurred as a result of this event. There have been no previous similar LERs identified.
2771991031 | Peach Bottom 2 | 09/17/1991 | 10/05/1991 | 9110110117 | <strong>Engineered Safety Feature Actuation Due To A Failed Voltage Regulator On The Reactor Protection System Motor Generator Set</strong><br /><i>Abstract:&nbsp;</i>On 9/17/91 at 1300 hours, a Unit 2 'B' channel Reactor Protection System (RPS) half scram occurred when the '2B' RPS Motor Generator (M/G) set output breaker tripped. The tripped breaker caused Primary Containment Isolation System half Group I and half Group III isolations which included a Standby Gas Treatment System initiation. The cause of the event has been determined to be an overvoltage condition on the output of the '2B' RPS M/G set due to an unexpected failure of the voltage regulator. Following the event, the '2B' RPS was aligned to its alternate feed which allowed the half scram and isolations to be reset. Subsequently, the affected systems were restored to normal. The failed voltage regulator was replaced and RPS was restored to its normal power supply. No actual safety consequences occurred as a result of these events. No previous similar LERs have been identified.
2771991032 | Peach Bottom 2 | 09/17/1991 | 10/16/1991 | 9110250228 | <strong>Engineered Safety Feature Actuations of the Control Room Emergency Ventilation due to a Wire Connector Short</strong><br /><i>Abstract:&nbsp;</i>On 9/17/91, 9/18/91, and twice on 9/24/91, the Control Room Ventilation system (CRVS) transferred to the Emergency Ventilation mode due to several instrument spikes in the "B" Main Control Room (MCR) radiation monitor. The operable MCR radiation monitor indicated normal background radiation levels. The cause of these events have been determined to be the result of spikes of the "B" MCR radiation monitor. An investigation has identified shorts at the detector cable connection. After each spike, the CRVS was returned to its normal configuration. The connections have been repaired and other similar connections will be inspected. The procedure used to install these connectors will be revised to provide guidance for the installation of these specific connectors. A modification has been initiated to replace the existing instrumentation. There were no adverse safety consequences as a result of this event. There were seven previous similar LERs identified.
2771991033 | Peach Bottom 2 | 10/16/1991 | 11/15/1991 | 9111200280 | <strong>High Pressure Coolant Injection System being Inoperable as a Result of a Packing Leak on the Steam Supply Inboard Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 10/15/91 at 2112 hours, during the performance of a surveillance test, a Drywell pressure and temperature increase was identified when the High Pressure Coolant Injection (HPCI) Steam Supply Inboard Isolation valve was stroked. The valve was backseated to isolate the leak and plant shutdown was completed on 10/17/91. The cause of the event has been determined to be excessive valve packing leakage due to a gouged stem. This is the result of a reversed packing configuration and the valve operator being horizontally mounted. This combination changed the load supporting characteristics of the valve which resulted in the valve bonnet area gouging the stem. The packing had been previously reversed in accordance with a Non Conformance Report (NCR) because of an unqualified stem leak-off plug weld. The evaluation performed as part of the NCR did not adequately evaluate the effect of packing configuration reversal on horizontally mounted motor operators. The weld was reworked and the valve packing was reinstalled to its normal configuration and the valve stem was replaced. The plant was returned to power operation on 10/21/91. A review has been conducted to ensure that similar packing configurations do not exist on horizontally mounted valves. No actual safety consequences occurred as a result of these events. There were no previous similar LERs identified.
2771991034 | Peach Bottom 2 | 10/22/1991 | 11/19/1991 | 9111260203 | <strong>Reactor Core Isolation System Being Inoperable due to a Dirty Transfer Switch Contact</strong><br /><i>Abstract:&nbsp;</i>On 10/21/91, a Technical Specification violation occurred when the mode switch was placed in the STARTUP position with the Reactor Core Isolation Cooling (RCIC) system inoperable. On 10/22/91 at 0545 hours, the Shift Technical Advisor identified the RCIC flow controller output signal to be 0% instead of the expected 100%. The cause of this event has been determined to be a dirty contact on the RCIC flow controller output signal transfer switch. It is presumed that the transfer switch contacts failed to makeup during the performance of the Surveillance Test (ST) on 10/19/91 even though the switch was in the proper position. The ST used to test this transfer switch provided no means to ensure that the RCIC Flow controller contacts were properly made-up after switch operation. This type of transfer switch is not checked on a periodic basis to ensure that the switch contacts are clear of dirt or oxidation. The RCIC flow controller transfer switch was exercised and the output signal from the flow controller was verified to be functioning properly. An evaluation will be performed to identify if additional testing or maintenance may be necessary. The ST will be revised to enhance the system restoration requirements. Other similar tests which involve transfer switch operation will be evaluated to determine additional appropriate corrective actions. The pertinent information from this event will be provided to the appropriate personnel. No actual safety consequences occurred as a result of this event. There have been no previous similar LERs identified.
2771991035 | Peach Bottom 2 | 10/25/1991 | 11/21/1991 | 9112020244 | <strong>Engineered Safety Feature Actuations when the Incorrect Test Plug was Installed During a Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On 10/25/91 at 1230 hours, a trip of an emergency bus breaker caused an automatic 4KV fast transfer which resulted in a Control Room Emergency Ventilation system actuation. The cause of the event was that the I&C technician incorrectly installed test equipment due to inadequate labeling. The test plugs and connections have been relabeled. The event has been discussed with the involved individuals and the pertinent information has been provided to the appropriate I&C personnel. No actual safety consequences occurred as a result of this event. There were no previous similar LERs identified.
2771991036 | Peach Bottom 2, Peach Bottom 3 | 11/03/1991 | 11/29/1991 | 9112060156 | <strong>Technical Specification Violation Occurred when the 'A' Waste Sample Tank was Released Without Proper Sampling due to Failure to Follow Procedure</strong><br /><i>Abstract:&nbsp;</i>On 11/03/91 at 0530 hours, it was discovered that the "A" Waste Sample Tank (WST) treated liquid was released without the appropriate sample and release approval. The "B" WST was sampled instead of the "A" WST. This condition resulted in a violation of Technical Specification 4.8.B.1b because the Surveillance Requirements were not performed. The cause of the event has been determined to be that the Radwaste Plant Operator (PO) failed to properly follow the Surveillance Test (ST) used to sample and release the WST contents. Additionally, miscommunication between the Radwaste PO and the Shift Chemist led to the wrong WST being sampled. No actual safety consequences occurred as a result of this event. The release was terminated and a liquid sample was obtained from the "A" WST. The pertinent information from this event will be provided to the appropriate personnel. The ST will be revised with focus on human factors considerations. There was one previous similar LER identified.
2771991037 | Peach Bottom 2 | 11/04/1991 | 11/29/1991 | 9112060193 | <strong>'2B' Reactor Protection System Motor Generator Set Trip Undervoltage due to Degraded Diodes</strong><br /><i>Abstract:&nbsp;</i>On 11/4/91 at 1535 hours, a Unit 2 "B" channel Reactor Protection System (RPS) half scram occurred when the '2B' RPS Motor Generator (M/G) set output breaker tripped. The tripped breaker caused a Primary Containment Isolation System half Group III isolation which included a Standby Gas Treatment System initiation. The cause of the event has been determined to be an undervoltage condition on the output of the '2B' RPS M/G set due to degraded diodes. Following the event, the '2B' RPS was aligned to its alternate feed which allowed the half scram and isolations to be reset. Subsequently, the affected systems were restored to normal. Several diodes were replaced, a Temporary Plant Alteration was installed to monitor the 2B M/G Set. The RPS was restored to its normal power supply. No actual safety consequences occurred as a result of these events. No previous similar LERs have been identified.
2771991038 | Peach Bottom 2 | 12/05/1991 | 01/06/1992 | 9201130176 | <strong>Unexpected Engineered Safety Feature Actuation which occurred During the performance of a Surveillance Test as a Result of a Spurious Trip</strong><br /><i>Abstract:&nbsp;</i>On 12/5/91, at approximately 1500 hours, an isolation of the Reactor Core Isolation Cooling (RCIC) system occurred unexpectedly during the performance of a Surveillance Test (ST). This is an Engineered Safety Feature actuation. The cause of the event is a spurious actuation of the RCIC isolation logic. Test equipment and panel test sockets were inspected satisfactorily. The ST was re-performed with no adverse effects. Additionally, interviews were conducted with individuals involved with ST performance and other individuals who were in the areas which could have adversely affected the ST. Operations reset the RCIC isolation. Operating history of this logic was reviewed and no significant problems were noted. This event has been reviewed with involved individuals. System monitoring will be performed. There were no actual safety consequences as a result of this event. There were no previous similar events identified.
2771991039 | Peach Bottom 2 | 12/06/1991 | 01/06/1992 | 9201090003 | <strong>Technical Specification Required Shutdown for a Residual Heat Removal System Valve Repair</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was brought to a cold shutdown on 12/6/91 due to a determination made on 12/3/91 by plant staff engineering that the Residual Heat Removal (RHR) System "B" Loop Injection Check Valve and/or its associated Bypass Valve had excessive through valve leakage. The RHR "B" Loop Outboard Isolation Valve was then de-energized closed in accordance with the Technical Specifications. The condition made the RHR "B" loop inoperable and the appropriate seven day Limiting Condition for Operation was entered. It was then decided to shut down Unit 2 since the RHR "B" Loop Injection Check Valve or its associated Bypass Valve repairs could not be completed without entering the inerted drywell. The cause of the event has been determined to be that the RHR "B" Loop Injection Check Bypass Valve had excessive through valve leakage of approximately 5 gpm. The valve plug was cut and valve seat imperfections were identified. It appears that some small obstruction was present in the valve seating area. An investigation is continuing. No actual safety consequences occurred as a result of this event. The RHR "B" Loop Injection Check Bypass was disassembled and repaired. The appropriate post maintenance testing was completed satisfactorily and the plant was returned to power operation on 12/18/91. There were no previous similar events identified.
2781991001 | Peach Bottom 3 | 01/16/1991 | 02/15/1991 | 9102210225 | <strong>Reactor Scram Following '3A' Main Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On 1/16/91 at 1238 hours a reactor scram occurred on Unit 3 due to Turbine Control Valve fast closure on a Main Generator Load Reject signal caused by a Main Transformer sudden pressure lockout signal. A Primary Containment Isolation System (PCIS) Group II/III isolation occurred as expected due to the Reactor Water level decrease following the scram. The load reject was initiated by actuation of the sudden pressure trip device on the '3A' Main Transformer when the fire system deluge was manually actuated in an attempt to cool down the overheating transformer. The transformer was overheating due to a loss of power to its cooling system. During performance of the procedure for resetting a scram, a second scram occurred as a result of procedural non-compliance. The cause of the first event was component failure and inadequate equipment design. The adequacy of the cooling system power supply circuit design is being evaluated. Information on this event will be included in Plant Operator and Licensed Operator training. The Operator involved in the second scram was coached by the Shift Manager and the Superintendent of Operations with regard to following procedures. No previous similar LERs have been identified.
2781991002 | Peach Bottom 3 | 01/21/1991 | 02/18/1991 | 9102250284 | <strong>Hourly Fire Watch Patrol Missed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 21,1991, between 1116 hours and 1857 hours, the hourly Fire Watch Patrol for a Unit 3 'B' Residual Heat Removal (RHR) Fire Damper was not performed due to personnel error. During a verbal shift briefing with the Shift Security Coordinator and the Nuclear Security Section Lead Protection Technician, the Lead Protection Technician closed out the wrong fire watch patrol for the Unit 3 'B' RHR Fire Damper. <br /><br /> To prevent recurrence an effective means of communication was established on a shift-to-shift basis between the Shift Security Coordinator and the Lead Protection Technicians for additions or deletions to Fire Watch Patrols. No previous similar events were identified.
2781991003 | Peach Bottom 3 | 02/25/1991 | 03/23/1991 | 9103280301 | <strong>High Pressure Coolant Injection System Being Declared Inoperable Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 2/25/91 at 1930 hours during the performance of a High Pressure Coolant Injection (HPCI) System surveillance test, HPCI was declared inoperable when the spring tension on the manual and overspeed trip tappet was found to be less than what is required. The tappet spring tension is checked weekly as a result of a previous failure in which the manual and overspeed trip tappet assembly spring did not have adequate spring tension to maintain the tappet in the reset position. The cause of the event is procedure inadequacy. The problem, which was identified in a previous LER, is that the spring tension force may not be enough to reset the tappet. The corrective actions taken only measured the spring tension and indicated a point at which HPCI was to be declared inoperable. The procedure did not provide a point at which the spring should be adjusted prior to reaching the inoperable state. No actual safety consequences occurred as a result of this event. The weekly surveillance has been revised to require that the spring tension be adjusted prior to a point requiring HPCI to be declared inoperable. A new design, to replace the tappet assembly, is installed on Unit 2 and will be installed on Unit 3 during the the upcoming refuel outage. One previous similar LER was identified.
2781991004 | Peach Bottom 3 | 03/24/1991 | 04/24/1991 | 9104290150 | <strong>Primary Containment Isolation Valve Logging Not Performed as Required by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 3/24/91 and 3/25/91, a Technical Specification (Tech Spec) violation occurred when the Unit 3 Reactor Operator (RO) failed to initial Surveillance Test (ST) 5.3, "Inoperable Isolation Valve Position Daily Log", signifying that he had verified containment penetrations containing inoperable isolation valves were isolated as required by Tech Specs. The cause of this event is personnel error due to failure to follow procedure. ST 5.3 requires the RO to initial daily that he has verified the penetration is isolated. Corrective actions include routing the pertinent information from this LER to the appropriate Operations personnel and reviewing the on the job portion of the licensed operator training program. The RO involved in this event was counselled and coached by Shift Management following the incident on the performance of administrative tasks associated with the RO's responsibilities. There were no safety consequences as a result of this event.
2781991005 | Peach Bottom 3 | 04/10/1991 | 05/09/1991 | 9105140176 | <strong>Inoperability of the High Pressure Coolant Injection System due to High Water Level in the Turbine Exhaust Line</strong><br /><i>Abstract:&nbsp;</i>On 4/10/91 at 2045 hours during the performance of a High Pressure Coolant Injection (HPCI) System Surveillance Test, HPCI was declared inoperable when water was found in the turbine exhaust line. The cause of the event has been attributed to the vacuum relief valves failure to prevent siphoning of Torus water into the turbine exhaust line. Loose locking nuts on the vacuum relief valves allowed the valve internals to disassemble and partially block vacuum relief flow. The maintenance procedure for the vacuum relief valves did not provide torquing requirements on the locking nut. The valves were repaired and the exhaust drain line steam trap was replaced. Maintenance procedures have been revised. No actual safety consequences occurred as a result of this event. There were no previous similar events identified.
2781991006 | Peach Bottom 3 | 04/10/1991 | 05/09/1991 | 9105140180 | <strong>Technical Specification Violation due to a Mispositioned Valve on the Drywell Radiation Monitor as a REsult of an Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On 4/10/91 at 0745 hours with Unit 3 operating at 100% power, it was discovered that the Drywell Atmospheric Radiation Monitor (DARM) had been isolated from the drywell atmosphere for an indeterminate period of time. This is a violation of Technical Specification 4.6.C.2, which requires that drywell atmospheric radiation levels be monitored and recorded at least daily. The isolation of the DARM was a result of a mispositioned valve on the sample line to the DARM. The cause of the event is unknown. The mispositioned valve was returned to the normal position and drywell atmospheric radiation levels were verified to be within expected normal operating values. This report will be distributed to the appropriate site groups for review with their personnel. There were no actual safety consequences as a result of this event. No previous similar LER's were identified.
2781991008 | Peach Bottom 3 | 05/20/1991 | 06/14/1991 | 9106240002 | <strong>Engineered Safety Feature Actuation During Surveillance Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 5/20/91 at 0730 hours during the performance of a Residual Heat Removal "B" Channel Logic System Functional Surveillance Test (ST), the 3C RHR pump unexpectedly started when a test switch was inadvertently left in the wrong position during testing. The system was secured and the ST was completed satisfactorily. The cause has been attributed to personnel error caused by a repetitive pattern set up in the ST which was then suddenly changed. The event has been discussed with the involved individuals and the pertinent information has been presented to other I&C personnel. Additionally, the ST will be enhanced. No safety consequences occurred as a result of this event. There was one other previous similar event that involved the mispositioning of a test switch.
2781991009 | Peach Bottom 3 | 05/30/1991 | 07/09/1991 | 9107160375 | <strong>Standby Liquid Control System Net Positive Suction Head</strong><br /><i>Abstract:&nbsp;</i>On 5/30/91 at 1700 hours, the Standby Liquid Control (SBLC) system was declared inoperable because the SBLC tank was inadvertently heated to a temperature which was believed to create inadequate Net Positive Suction Head (NPSH) to the SBLC pumps. Subsequently, NED provided new calculations to confirm that the SBLC was never inoperable during this event because adequate NPSH existed. The Reactor Operator incorrectly selected the procedure used to initially fill and setup the system instead of the procedure used for chemical Makeup. The individuals involved have been coached as to the importance of attention to detail with respect to using the correct procedure. No actual safety consequences occurred as a result of this event. There have been no previous similar events.
2781991010 | Peach Bottom 3 | 07/07/1991 | 08/05/1991 | 9108120121 | <strong>Reactor Scram as a Result of a Main Generator Load Reject due to a Deteriorated Generator Output Circuit Breaker Block Switch</strong><br /><i>Abstract:&nbsp;</i>On 7/7/91 at 2312 hours, a reactor scram occurred on Unit 3 due to Turbine Control Valve fast closure on a Main Generator Load Reject trip signal. This trip was caused when the Generator output breaker position indication relays received a false signal due to a ground in a block switch. A Primary Containment Isolation System Group II/III isolation occurred as expected due to the reactor water level decrease after the scram. The cause of the event has been determined to be the result of lightning. The scram and isolations were reset, systems were returned to normal, and the damaged components were replaced. Engineering will evaluate the possibility of block switch removal, upgrade, or provisions to protect the Generator output breaker position indication relays from lightning strikes. Three previous similar LERs have been identified.
2781991011 | Peach Bottom 3 | 07/10/1991 | 08/08/1991 | 9108120323 | <strong>Scram and PCIS Isolation due to Reactor Protection System Motor Generator Breaker Trip During Troubleshooting and Spurious Local Power Range Monitor Spike</strong><br /><i>Abstract:&nbsp;</i>On 7/10/91 at 1928 hours, a "B" channel Reactor Protection System (RPS) half scram occurred when the 'B' RPS Motor Generator (M/G) set output breaker tripped during troubleshooting. This caused a Primary Containment Isolation System Group III outboard half isolation. At 2041 hours, RPS initiated a full reactor scram signal. The full reactor scram was a result of a "A" channel RPS half scram signal being received in conjunction with a "B" channel RPS half scram signal already inserted. The cause of the events has been determined to be a RPS M/G set output breaker trip during an electrical transient and a Local Power Range Monitor spike due to problems with the design of the detector. The scram and isolations were reset and the systems were returned to normal. No actual safety consequences occurred as a result of these events. Two previous similar LERs have been identified involving RPS output breaker trips and Local Power Range Monitor spiking.
2781991012 | Peach Bottom 3 | 07/24/1991 | 08/23/1991 | 9109030190 | <strong>Shutdown of U/3 per Tech Spec 2.0.C due to Loss of Division II Core Spray and Loss of the Anticipatory Auto Start of Two Diesels Generators as a Result of a Shorted Light Socket</strong><br /><i>Abstract:&nbsp;</i>On 7/24/91 at 1430 hours, a controlled shutdown of Unit 3 was initiated in accordance with Technical Specification 3.0.C due to a loss of the auto start capability of the Division II Core Spray system concurrent with the loss of the anticipatory auto start on loss of coolant accident signal capability of the E-2 and E-4 Emergency Diesel Generators (EDGs). Either a reactor vessel low-low-low water level or high drywell pressure signal will provide this anticipatory start. The loss of offsite power start signal was unaffected for the EDGs. The event was the result of d blown fuse which occurred during the performance of a monthly surveillance test. The cause of the fuse failure was a shorted Dialco miniature light socket. Technical Specification 3.0.C was exited at 1750 hours on 7/24/91 after the light socket was removed from the circuit and the fuse was replaced. A review of similar applications of Dialco miniature light sockets will be performed and the appropriate corrective actions will be taken. The pertinent information from this report will be distributed to the appropriate personnel. There were two previous similar events.
2781991013 | Peach Bottom 3 | 08/25/1991 | 09/23/1991 | 9110010152 | <strong>High Pressure Coolant Injection System being Inoperable due to Room Cooler Fan Trip on Thermal Overloads</strong><br /><i>Abstract:&nbsp;</i>On 8/25/91 at 1415 hours, the HPCI system was found to be inoperable during the performance of a Surveillance Test (ST). The 'A' HPCI room cooler fan failed to start when the fan motor breaker tripped on thermal overloads. This occurred while the 'B' HPCI room cooler was out of service to support ESW maintenance activities. The Technical Specifications require that the HPCI system have at least one room cooler available to support HPCI operability. The cause of this event has been determined to be that the 'A' HPCI room cooler fan breaker tripped on thermals. The Operator immediately reset the thermal overloads and the fan was subsequently operated for several hours without another thermal overload trip. The 'A' HPCI room cooler will be inspected to ensure proper performance of the room cooler fan motor and corrective actions will be taken as necessary. No actual safety consequences occurred as a result of this event. There have been no previous similar LERs identified.
2781991014 | Peach Bottom 3 | 09/05/1991 | 10/01/1991 | 9110080367 | <strong>High Pressure Coolant Injection System Being Inoperable Due to a Power Supply Inverter Inadvertently Being Turned Off</strong><br /><i>Abstract:&nbsp;</i>On 9/05/91 at 1412 hours, the High Pressure Coolant Injection (HPCI) system (EIIS:BJ) was found to be inoperable when the HPCI Flow control loop power supply inverter (EIIS:INVT) was inadvertently turned off. At the time of the event, Installation workers were pulling cables through the area for an unrelated plant activity and the switch was inadvertently bumped during this work. No actual safety consequences occurred as a result of this event. The operator immediately returned the HPCI Flow control loop power supply inverter to service. The event has been discussed with the involved individuals. The pertinent information from this event will be provided to other installations personnel. These components are to be relocated. There have been no previous similar LERs identified.
2781991015 | Peach Bottom 3 | 09/08/1991 | 10/08/1991 | 9110150239 | <strong>Core Spray Pump Inoperability Due to a Room Cooler Not Being Available Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 9/8/91 at 0940 hours, during the performance of a Surveillance Test (ST), the "3D" Core Spray pump was found to be inoperable since the control switch for its room cooler (3GV024) was not in the proper position to ensure fan operation. This condition resulted in Technical Specification violations because the appropriate LCO actions and Surveillance requirements were not performed while the "3D" CS pump was inoperable. The cause of the event has been determined to be that the Shift Supervisor failed to understand and properly act on the information on the Administrative Clearance. Since no Administrative Clearance tags existed on the control switch, the switch was probably returned to its normal "RUN" position after 8/31/91 during system restoration. The Room cooler control switch for 3GV024 in the ""3D" CS room was placed in the "MANUAL" position and an Administrative Clearance was applied. The event has been discussed with the involved individual. The pertinent information from this event will be provided to the appropriate Operations, Technical, and Work Control Center personnel. No actual Safety consequences occurred as a result of this event. There have been no previous similar LERs identified.
2781991016 | Peach Bottom 3 | 09/14/1991 | 10/18/1991 | 9110290059 | <strong>Technical Specification Violation due to a Missed Fire Watch Patrol</strong><br /><i>Abstract:&nbsp;</i>On 9/14/91 at 1120 hours, the fire watch required by Technical Specification (Tech Spec) 3.14.D, for the four Unit 3 4kv Switchgear and the two Unit 3 Battery rooms, were not performed by the Fire Watch Patrol. This condition resulted in a Tech Spec violation. This deficiency was discovered on 9/20/91. The cause of the event has been determined to be that the Clearance Review Form was too general based on the complexity of the block and did ot specifically list all Fire System components which were impaired by the Clearance. This condition contributed to the incorrect decision by the Shift Supervisor to approve the application of a Clearance without establishing the appropriate Fire Watch Patrol. The appropriate Fire Watch Patrol was immediately established and the event has been discussed with the involved individuals. The pertinent information from this event will be provided to the appropriate personnel. No actual safety consequences occurred as a result of this event. No previous similar LERs were identified.
2781991017 | Peach Bottom 3 | 09/24/1991 | 07/20/1992 | 9207240185 | <strong>Automatic Depressurization System Inoperability Due to Components Being Unqualified as a Result of Insulation not being Installed Properly</strong><br /><i>Abstract:&nbsp;</i>On 9/24/91 at 1300 hours, the Main Steam Relief Valve (MSRV) solenoid valves (SV) wiring insulation was discovered to be degraded. An investigation revealed that the MSRV thermal insulation had been improperly installed. This caused an unusually high temperature environment in the immediate vicinity of the SVs and associated wiring. On 11/8/91, it was determined by engineering analysis that there was no longer a reasonable assurance that certain Automatic Depressurization System relief valves were operable. The temperature increase from the insulation installation error caused the expiration of the Environmental Qualification life of the components. A causal factor analysis has been performed concerning this event and corrective actions will be implemented as appropriate. The insulation was properly reinstalled and the SVs were replaced. No previous similar LERs identified.
2781991018 | Peach Bottom 3 | 12/16/1991 | 01/14/1992 | 9201230031 | <strong>Engineering Safeguard Feature Actuation as a Rsult of Less Than Adequate Programmatic Guidance</strong><br /><i>Abstract:&nbsp;</i>On 12/16/91 at 2205 hours, an isolation of the Main Steam Line Brain and the Recirculation System Sample Valves occurred unexpectedly during the performance of an in-service leak test. At the time of the event, Operations personnel were valving into service the instrument valves on a Feedwater Control system flow transmitter. The cause of the event has been determined to be a pressure transient in the instrument line. This was a result of the instrument line not being backfilled prior to the instrument being returned to service. No documented station guidance existed to address operation of instrument valves and responsibilities. A contributing factor to this event was less than adequate communication. After the Group I Primary Containment Isolation System (PCIS) isolation occurred, the PCIS logic was reset at 2220 hours and the affected valves were restored to the proper position. Station guidance will be developed. The event will be reviewed to determine adequacy of the present methods used to perform in-service leak testing. No actual safety consequences occurred as a result of this event. There were no previous similar events identified.
2781991019 | Peach Bottom 3 | 12/18/1991 | 01/16/1992 | 9201290034 | <strong>Engineering Safeguard Feature Actuation as a Result of a Relay Coil Failure</strong><br /><i>Abstract:&nbsp;</i>On 12/18/91 at 1822 hours, an isolation of the Shut Down Cooling (SDC) mode of the Residual Heat Removal system occurred when power was lost to the Primary Containment Isolation System (PCIS) control logic. The Unit 3 reactor operator immediately maximized Reactor Water Cleanup, Control Rod Drive, and Core Spray Stayfull flows. The cause of the SDC isolation has been determined to be a PCIS relay coil failure. This condition caused the PCIS control logic fuse to blow. The blown fuse and relay were replaced. Subsequently, the isolation was reset and SDC was restored to service. There were no actual safety consequences as a result of this event. There were no previous similar events identified.
2801991001 | Surry 1, Surry 2 | 03/09/1991 | 04/05/1991 | 9104160481 | <strong>High Energy Line Inspection Not Performed Within Technical Specifications Required Interval Due to Administrative Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1991, at approximately 0830, it was discovered that the Technical Specifications (TS) frequency for the visual inspection of high energy lines in the main steam valve house had been exceeded. TS 4.15.C.1 requires a visual inspection of all weld locations in the main steam valve house on a weekly basis for the detection of leaks. The TS frequency was exceeded on March 9, 1991 at 1800 hours with Unit 1 at 100 % power and Unit 2 at 85% power. The inspection was satisfactorily performed at approximately 0930 hours on March 11, 1991. The cause of this event is attributed to administrative inadequacies within the Nondestructive Examination (NDE) Department. To prevent recurrence, enhancements were made in the NDE Department's periodic test scheduling process. In addition, a Task Team was formed to review this and similar events, and appropriate corrective action is being taken. This event is being reported, pursuant to 10CFR 50.73(a)(2)(i)(B), since the failure to perform the inspection within the required frequency is prohibited by TS 4.15.C.1.
2801991002 | Surry 1 | 03/26/1991 | 04/23/1991 | 9104300189 | <strong>Two Charging Pumps and One Charging Pump Service Water Pump Inoperable Simultaneously Due to Instrument Air Line Failure Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991, with Unit 1 operating at 100% power, Charging Pump 1-CH-P-1B was declared inoperable due to a failed instrument air line to its lube oil temperature control valve, 1-SW-TCV-108B. This resulted in two of three charging pumps being considered inoperable, since the "A" and "C" Pumps were both aligned to the same emergency bus. At the time the "B" Charging Pump was declared inoperable, Charging Pump Service Water Pump 1-SW-P-10A was out of service for maintenance. With two charging pumps and one charging pump service water pump inoperable simultaneously, a condition not allowed by Technical Specifications existed and a six hour action statement was entered in accordance with Technical Specification 3.0.1. The failed instrument air line was isolated. The "C" Charging Pump was transferred to the redundant bus at 1443 hours and the six hour action statement was exited. The "B" Charging Pump could have been operated if safety injection had been required and there were no actual or potential consequences to public health and safety. The event was caused by personnel error. A contractor-employed painting foreman inadvertently made contact with and caused failure of the instrument air line during painting of the charging pump cubicle. The event is being communicated to station and construction craft personnel. This report is required by 10 CFR 50.73(a)(2)(i)(B) because the unit was operated in a condition not allowed by the Technical Specifications.
2801991003 | Surry 1, Surry 2 | 04/08/1991 | 05/07/1991 | 9105150181 | <strong>Technical Specifications Requirements For Records Storage Vault Halon System Violated Due To Personnel Error During Performance of Periodic Test</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1991, with Unit 1 at 100% power and Unit 2 in Cold Shutdown, it was determined that the Technical Specifications (TS) requirements for the halon system in the station records storage vault had been violated. TS 3.21.A.7 requires the halon storage tanks to be at least 95% of full charge weight and 90% of full charge pressure. During a QA review of periodic test (PT) records, it was discovered that the PT conducted January 3, 1990 to check the conditions for proper operation of the records storage vault halon system was performed improperly, resulting in the PT being considered satisfactory when two of the four halon storage tanks were actually below the minimum acceptable storage pressure. Further review of the PT records indicated that the storage pressures of the deficient tanks were satisfactory by the next month, as evidenced by the February, 1990 PT. The cause of this event is attributed to a personnel error in that the minimum storage pressure for the halon storage tanks was determined incorrectly. To prevent recurrence, the subject PT procedure was revised to simplify the method for determining the minimum acceptable storage pressure. This event is being reported, pursuant to 10CFR 50.73(a)(2)(i)(B), since this condition is prohibited by TS 3.21.A.7.
2801991004 | Surry 1, Surry 2 | 04/09/1991 | 05/08/1991 | 9105150273 | <strong>Two of Three Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1991, at 0050 hours, with Unit 1 at 100% power and Unit 2 at Cold Shutdown, it was discovered that both #2 and #3 Emergency Diesel Generators (EDG) had been rendered inoperable because of personnel error. EDG #2 had been removed from service for maintenance on April 6, 1991, and operating personnel had erroneously tagged out one of #3 EDG's two Fuel Oil Transfer Pumps, rendering #3 EDG technically inoperable as well. Operating either unit without emergency power available to two of the three Main Control Room and Emergency Switchgear Room Chiller Refrigeration Units is not permitted. Upon discovery, a six hour action statement to Hot Shutdown was entered for Unit 1, the incorrectly tagged out fuel oil transfer pump was tested and restored to operability, and the six-hour action statement was exited at 0147 hours. A Root Cause Analysis is in progress and appropriate long term corrective actions will be taken based on its results. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2801991005 | Surry 1, Surry 2 | 04/13/1991 | 05/10/1991 | 9105210287 | <strong>Failure to Sample Service Water From Component Cooling Heat Exchanger Within Technical Specification Required Interval Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1991, with Unit 1 operating at 100% power and Unit 2 at Cold Shutdown, it was discovered that the Technical Specification requirement for sampling the Service Water (SW) discharge from the "C" Component Cooling (CC) Heat Exchanger had not been performed within the specified interval. Technical Specification Table 3.7-5(a) required that the SW effluent from a CC Heat Exchanger be sampled and analyzed for radioactivity at least once every 12 hours when the effluent radiation monitor was out of service. Consecutive samples were taken 12 hours and 33 minutes apart. The event had no safety consequences since analysis of the late sample detected no radioactivity, indicating that leakage of radioactive liquid into the SW system was not occurring. The event was caused by personnel error. Following the event, the sampling frequency was increased to twice each 12 hour shift. An improved radiation monitoring system for the SW discharge from the CC Heat Exchangers has been installed and placed in service. This report is required by 10CFR50.73(a)(2)(i)(B) since failure to obtain the required SW sample within the 12 hour maximum sampling interval is a condition not allowed by Technical Specification 3.7.
2801991006 | Surry 1, Surry 2 | 04/19/1991 | 05/17/1991 | 9105300252 | <strong>Unit 1 Auxiliary Feedwater System Cross-Connect Capability From Unit 2 Inoperable In Excess of Technical Specifications Allowed Time Due to a Drawing Error</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1991 at 1605 hours, with Unit 1 at 100% power and Unit 2 in Cold Shutdown, it was determined that the Technical Specifications (TS) requirements for the Unit 1 Auxiliary Feedwater (AFW) system Unit 2 cross-connect capability had been violated. On April 11, 1991 at 1400 hours, a diver installed a plug in what was designated on station drawings as the piping penetration for the Unit 2 Emergency Condensate Storage Tank fill line. On April 19, 1991 at 1605 hours, it was determined that the plugged tank penetration actually provided suction for the 2-FW-P-3B AFW pump, rendering the pump inoperable. It was also determined at that time that the 2-FW-P-3A AFW pump was required to be considered inoperable since April 17, 1991 at 0205 since the Number 2 Emergency Diesel Generator and the 2-FW-P-3B pump had been inoperable concurrently for a period in excess of that permitted by TS 3.16.B.4.b. Therefore, on April 19, 1991 at 1605 hours, a Unit 1 Limiting Condition for Operation requiring Hot Shutdown within six hours was entered since the three Unit 2 AFW pumps had been inoperable for more than 72 hours. The event was caused by an error on the station drawings. The affected drawings are being revised to accurately reflect the as-built configuration. The event is being reported, pursuant to 10CFR 50.73(a)(2)(i)(B), since this condition is prohibited by TS 3.6.G.2.
2801991007 | Surry 1, Surry 2 | 04/22/1991 | 05/20/1991 | 9105300254 | <strong>Both Trains of Auxiliary Ventilation Exhaust Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1991, at 0910 hours, with Unit 1 at 100% power and Unit 2 at Refueling Shutdown, it was discovered that both trains of auxiliary ventilation exhaust were inoperable. After Train "A" had been removed from service to accomplish a planned modification, operating personnel realized that the emergency power source for the redundant "B" Train was also out of service. Operation under this condition is prohibited by Technical Specification 3.0.2. The event was caused by cognitive personnel error on the part of shift operating personnel who have since been reinstructed. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2801991008 | Surry 1, Surry 2 | 04/25/1991 | 05/22/1991 | 9105300145 | <strong>Two Main Control Room/Emergency Switchgear Room Chillers Inoperable Due to Relay Failure and Inoperable Emergency Power Source</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1991, with Unit 1 operating at 100% power and Unit 2 in Refueling Shutdown, Main Control Room/Emergency Switchgear Room (MCR/ESGR) Chiller 1-VS-E-4A tripped and could not be restarted. The chiller was declared inoperable at 2255 hours. With Chiller 1-VS-E-4A inoperable, Technical Specification 3.0.2 no longer allowed Chiller 1-VS-E-4B to be considered operable because its emergency power source was out of service. With two of three MCR/ESGR chillers considered inoperable, a condition not allowed by Technical Specification 3.23 existed and an action statement requiring Hot Shutdown within six hours was entered in accordance with Technical Specification 3.0.2. A power decrease was begun on April 26, 1991 at 0115 hours and a Notification of Unusual Event (NOUE) was declared. The problem with the "A" Chiller was determined to be a failed oil pressure/overload reset relay. The oil pressure/overload reset relay from the "B" Chiller was installed in the "A" Chiller and the "A" Chiller was declared operable at 0222 hours. The power decrease was stopped and the NOUE terminated at that time. No significant safety consequences resulted from the event. An upgrade of the MCR/ESGR Air Conditioning System is in progress and will include the installation of two additional 50% capacity chillers. This report is required by 10 CFR 50.73(a)(2)(i)(B).
2801991009 | Surry 1 | 05/09/1991 | 06/05/1991 | 9106100383 | <strong>Technical Specifications Surveillance Requirements Violated or In-service Inspection of Unit 1 Reactor Vessel Due to a Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1991, with Unit 1 at 100% power and Unit 2 in Cold Shutdown, a violation of the Technical Specifications (TS) surveillance requirements for the Unit 1 in-service inspection (ISI) and testing of American Society of Mechanical Engineers (ASME) Code Class 1, 2, and 3 components was identified during an internal audit of the Unit 2 ISI Program. The visual (VT-2) examinations of the Unit 1 reactor vessel partial penetration welds and the bottom of the reactor vessel were not performed during the 1990 refueling outage. The cause of this event was an administrative oversight attributed to a cognitive error on the part of utility engineering personnel responsible for the ISI Program. The subject examinations will be performed at the next outage of sufficient duration. Leakage monitoring of the Reactor Coolant System has been enhanced and the normal weekly frequency of Unit 1 containment air sampling and analysis has been increased to daily until the examinations are performed. The ISI plan will be revised to include the subject examinations. The procedure governing the RCS pressure test will also be revised to clarify the subject Section XI ASME Boiler and Pressure Vessel Code required examinations. The event is being reported, pursuant to 10CFR 50.73(a)(2)(1)(B), since this condition is prohibited by TS 4.0.3.a.
2801991010 | Surry 1, Surry 2 | 05/30/1991 | 08/16/1991 | 9108230254 | <strong>ASME Section XI Inservice Testing Program Requirements Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1991, with Unit 1 at 100% power and Unit 2 at Cold Shutdown, it was discovered that flow instrumentation used for testing pumps in accordance with Surry Units 1 and 2 ASME Section XI Inservice Testing Programs may not have instrument accuracies within the code required 2%. A review of the IST Pump Program was initiated which revealed: the accuracies of certain flow instruments exceeded 2%, the full scale range of certain indicators was greater than three times the reference value being measured, and dead head testing was being performed as inservice testing for certain pumps. Retesting was performed where possible and corrections for the decreased instrument accuracies of the remaining pumps were made which determined that pumps which were previously considered operable remained operable. Therefore, no safety implications were posed by this event, This event occurred as the result of cognitive personnel errors in implementing ASME Section XI Inservice Testing Program requirements. This was considered to be a violation of Technical Specification 4.0.3 and is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2801991011 | Surry 1, Surry 2 | 05/30/1991 | 06/27/1991 | 9107080078 | <strong>Service Water Radiation Monitoring Pumps Inoperable Due to Air Binding as a Result of Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1991, with Unit 1 at 100% power and Unit 2 in Cold Shutdown, a functional test of the Unit 2 Service Water (SW) radiation monitoring pumps under simulated design basis accident conditions resulted in a failure of the pumps to develop design flow and discharge pressure. This condition impairs the capability of the radiation monitors to detect radioactive leakage into the SW system from the Recirculation Spray Heat Exchangers; however, alternate means of leakage detection would have been available if a design basis accident had occurred. This condition was caused by a transient vacuum condition at the pump suction which resulted in air binding of the pumps. The transient vacuum condition in the Circulating Water (CW) discharge tunnel resulted from isolation of the main condenser and prevented normal self-priming of the radiation monitor pumps. The automatic starting of these pumps has been defeated. Emergency Operating Procedures have been revised to require manually breaking CW discharge tunnel vacuum to permit normal self-priming of these pumps and to provide for manually starting the pumps. Permanent modification of the radiation monitoring system is being evaluated. This report is required by 10CFR50.73(a)(2)(vii)(C).
2801991012 | Surry 1 | 07/20/1991 | 08/16/1991 | 9108220178 | <strong>Pressurizer Level Channel Not Placed in Trip Within Six Hours Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1991 at 0635, with Unit 1 at 100% power, it was discovered that pressurizer level indicator 1-RC-LI-1461 had exceeded channel check acceptance criteria specified in a surveillance procedure for greater than six hours and had not been declared inoperable. Consequently, the channel was not placed in trip as required by Technical Specification 3.7 Table 3.7-1. Following this discovery, the channel was declared inoperable and placed in trip. An emergency work order was initiated which checked channel calibration and vented the transmitter to resolve the problem. No safety implications were posed by this event. This event occurred as the result of cognitive personnel errors in failing to recognize an out of specification condition, and failure to properly supervise a trainee. Personnel involved were reinstructed in the review of recorded data and the supervision of trainees. This occurrence was considered to be a violation of Technical Specification 3.7 and is being reponed pursuant to 10CFR50.73(a)(2)(i)(B).
2801991013 | Surry 1 | 07/23/1991 | 08/22/1991 | 9108270126 | <strong>MCC Room Fire Suppression System Inoperable Due To Personnel Error In Administratively Controlling The MCC Room Exit Door</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1991, at approximately 1030 hours, with Unit 1 at 100% power and Unit 2 at 100% power, the Unit 1 Cable Vault upper level Motor Control Center (MCC) room exit door was found blocked open. This condition, which limited the ability of the carbon dioxide fire suppression system to perform its intended function, had existed for a period in excess of that allowed by Technical Specifications (TS) 3.21.B.4. On July 23, 1991, at approximately 1430 hours, a continuous firewatch was posted at the Unit 1 MCC room and at approximately 1630 hours, a door blocking device, designed to release upon actuation of the fire protection system, was installed and tested. The cause of this event is attributed to a cognitive error on the part of utility personnel in administratively controlling the MCC room exit door. To prevent recurrence, signs have been installed on both sides of the Unit 1 and Unit 2 MCC room exit doors cautioning that the door is a carbon dioxide fire protection system boundary. In addition, station doors will be evaluated and labeled or color coded, as appropriate, to indicate their safety significance to station operation. The event is being reported, pursuant to 10CFR 50.73(a)(2)(i)(B), since this condition is prohibited by TS 3.21.B.4.
2801991014 | Surry 1, Surry 2 | 07/24/1991 | 02/11/1992 | 9202210408 | <strong>Main Steam Flow Setpoints in Excess of Technical Specifications Due to Flow Transmitter Scaling Inaccuracies Resulting From Incorrect Scaling Methodology</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1991, with Unit 1 and Unit 2 operating at 100% power, it was determined after analyzing recent special test data that the scaling for the Unit 2 Main Steam (MS) flow transmitters was incorrect. These flow transmitters provide input to certain Reactor Protection System (RPS) and Engineered Safety Features (ESF) actuation signals. It was determined that the scaling resulted in Unit 2 setpoints in excess of the maximum allowed value of 110% (at full load) of full steam flow specified in Technical Specification (TS) 3.7.D. On July 22, 1991, voltage biases were placed on the uncompensated Unit 2 steam flow signals to reduce the Hi Steam Flow ESF function actuation to a value below 110%. This event was caused by the use of incorrect scaling methodology, employed in 1977, to rescale the MS flow transmitters to correct an observed difference in the MS and feedwater flow indications. Since the same incorrect scaling information was used in 1977 for Unit 1, similar voltage biases were introduced on Unit 1 on July 24, 1991. Following an evaluation of special test data, the Unit 2 steam flow and feedwater flow transmitters were respanned and the steam flow circuitry rescaled. Independent testing is being performed to enable these measures to be implemented for Unit 1. The event is being reponed, pursuant to 10 CFR 50.73(a)(2)(i)(B).
2801991015 | Surry 1, Surry 2 | 08/08/1991 | 09/09/1991 | 9109120241 | <strong>Two Main Control Room/Emergency Switchgear Room Chillers Inoperable Due to Thermostat Failure and Inoperable Emergency Power Source</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1991, with Unit 1 and Unit 2 operating at 100% power, Main Control Room/Emergency Switchgear Room (MCR/ESGR) Chiller 1-VS-E-4A tripped. The chiller was declared inoperable at 0210 hours. With Chiller 1-VS-E-4A inoperable, Technical Specification 3.0.2 no longer allowed Chiller 1-VS-E-4C to be considered operable because its emergency power source, Emergency Diesel Generator No. 2, was out of service. With two of three MCR/ESGR chillers considered inoperable, a condition not allowed by Technical Specification 3.23 existed and an action statement requiring Hot Shutdown within six hours was entered in accordance with Technical Specification 3.0.2. Emergency Diesel Generator No. 2 was returned to service on August 8, 1991 at 0608 hours, terminating the six hour action statement. The cause of the "A" Chiller trip was determined to be a failed thermostat. The thermostat was replaced and the chiller was returned to service on August 11, 1991 at 0240 hours. No significant safety consequences resulted from the event. An upgrade of the MCR/ESGR Air Conditioning System is in progress and will include the installation of two additional 50% capacity chillers. This report is required by 10 CFR 50.73(a)(2)(i)(B).
2801991016 | Surry 1, Surry 2 | 08/11/1991 | 09/10/1991 | 9109190295 | <strong>Two Main Control Room/Emergency Switchgear Room Chillers Inoperable Due to Thermostat Replacement and Inoperable Chiller Service Water Pump</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1991, with Unit 1 and Unit 2 operating at 100% power, Main Control Room/Emergency Switchgear Room (MCR/ESGR) Chiller 1-VS-E-4C tripped and could not be restarted. The chiller was declared inoperable at 0152 hours. With chiller 1-VS-E-4C inoperable and chiller 1-VS-E-4A already in a 7-day Action Statement in accordance with Technical Specification 3.23.B for thermostat replacement, two of three MCR/ESGR chillers were considered inoperable. A condition not allowed by Technical Specification 3.23 existed and an Action Statement requiring Hot Shutdown within six hours was entered in accordance with Technical Specification 3.0.1. The problem with the "C" chiller was determined to be a failed service water pump motor due to an open phase. The replacement of the thermostat in the "A" Chiller was completed at 0249 hours. While the control room and Emergency Switchgear room temperatures were being monitored, MCR/ESGR chillers were secured for re-alignment. Following satisfactory testing, the "A" chiller was declared operable at 0420. With the "A" and "B" chillers operable, the 6-hour clock to Hot Shutdown was exited. The seven day clock remained in effect as originally scheduled while "C" chiller service water pump motor repairs continued. No significant safety consequences resulted from the event. An upgade of the MCR/ESGR Air Conditioning System is in progress and will include the installation of two additional 50% capacity chillers. This report is required by 10 CFR 73.(a)(2)(i)(B).
2801991017 | Surry 1, Surry 2 | 05/09/1991 | 11/13/1991 | 9111210045 | <strong>Emergency Diesel Generator Rendered Inoperable Due to Personnel Error in That Specified Testing Was Not Performed</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1991, with Unit 1 and Unit 2 at 100% power, it was determined that Emergency Diesel Generator (EDG) #3 had been inoperable since May 9, 1991. This determination was made while performing a root cause evaluation of the observed performance of EDG #3 during an August 2, 1991, Engineered Safeguards Feature (ESF) actuation on Unit 2. This safety injection/reactor trip, which occurred as a result of vital bus power oscillations on one channel and a failed steam generator pressure transmitter on another channel, is being reported separately by Licensee Event Report S2-91-007-00. A root cause investigation team appointed to determine the cause of the failure of EDG #3 to achieve rated speed found that inadequate Post Maintenance Testing (PMT) was performed following replacement of the governor on May 7, 1991. This was due to a cognitive error on the part of utility personnel in that an approved work order step which specified a fast start test of the EDG was not performed. During the period EDG #3 was inoperable, the Unit's other source of emergency power, EDG #2, was inoperable for approximately thirteen hours on July 15, 1991. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) and (ii)(B).
2801991018 | Surry 1, Surry 2 | 08/26/1991 | 09/24/1991 | 9109270190 | <strong>Switchyard Transformer Fault Results in Loss of 4160V Transfer Buses, Start of Emergency Diesel Generators (EDG), and Identification of EDG Underspeed Condition</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1991, at 0329 hours, with Units 1 and 2 operating at 100% and 60% power, respectively, power was lost to 34.5 KV switchyard Bus Number 5. As a result, 4160 volt Transfer Buses "D" and "E", which supply power to Emergency Buses "1J" and "2H", were de-energized causing the automatic start and loading of Emergency Diesel Generators (EDGs) Number 2 and 3. During the event, a Control Room operator noted an underspeed condition on EDG Number 2 and responded by manually adjusting the speed. Following an evaluation of this condition, it was determined that EDG Number 2 was inoperable from August 12 to August 26, 1991 due to the speed control governor being incorrectly set. The loss of power to Bus Number 5 was caused by a fault in 34.5 KV switchyard Station Service Transformer (SST) Number 1. The EDG underspeed condition was caused by a personnel error in incorrectly setting the speed control governor. SST Number 1 was replaced with a standing spare and the EDG Number 2 speed control governor was properly adjusted, tested, and determined operable on August 26, 1991. The switchyard configuration will be evaluated and appropriate corrective actions taken. EDG governor maintenance and testing procedures are also being upgraded. This event is being reported, pursuant to 10 CFR 50.73(a)(2)(iv), 10 CFR 50.73(a)(2)(i)(B), and 10 CFR 50.73(a)(2)(ii)(B).
2801991019 | Surry 1 | 08/28/1991 | 09/26/1991 | 9110010058 | <strong>Loss of Containment Integrity Due to a Crack in Component Cooling Water Piping</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1991, with Unit 1 at 100% power and Unit 2 at 60% power, while investigating the erratic behavior of a portion of the primary plant instrumentation inside Unit 1 containment, a through-wall crack was discovered in the Component Cooling Water (CCW) supply to the "B" Reactor Shroud Cooler (1-VS-E-6B). This portion of the CCW System utilizes an automatic return line isolation valve and a membrane barrier for containment isolation. When the piping wall was breached, containment integrity no longer existed. A six-hour action statement to hot shutdown was entered at 0500 hours on August 28, 1991. The leak was isolated, and the action statement exited at 0611 hours. The health and safety of the public were not affected. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2801991020 | Surry 1, Surry 2 | 08/21/1991 | 09/20/1991 | 9109240322 | <strong>Potential Failure of Charging/High Head Safety Injection Pumps to Start Automatically in a Design Basis Accident Due to Undervoltage Lockout</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1991, with Unit 1 operating at 100% power and Unit 2 operating at 80% power, an engineering review of Charging/High Head Safety Injection (HHSI) Pump interlocks resulted in the determination that automatic initiation of HHSI would not occur in certain accident sequences, a condition outside the design basis. Charging/HHSI Pump 1-CH-P-1A was declared inoperable. With the "A" Pump inoperable, Technical Specification 3.0.2 no longer allowed the "B" Pump to be considered operable because its emergency power source was out of service. Since the "C" Pump was initially out of service, all three Charging/HHSI Pumps were inoperable, a condition not allowed by Technical Specifications. An action statement requiring hot shutdown within six hours was entered. The Unit 1 pumps were re-aligned to a configuration where the "B" and "C" Pumps were operable and the action statement was exited. The Unit 2 pumps were in an acceptable configuration. No safety consequences resulted from this event because procedures and operator training addressed the potential need for manual HHSI initiation. The event was caused by inadequate review of the interlock design. Changes in the methods of operating the Charging/HHSI Pumps are being evaluated. This report is required by 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(ii)(B).
2801991021 | Surry 1 | 10/28/1991 | 11/18/1991 | 9111260230 | <strong>Emergency Diesel Generator No. 1 Room Fire Suppression System Inoperable Due to Personnel Error in Administratively Controlling the Exit Door</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1991, at approximately 0900 hours, with Unit 1 at 100% power and Unit 2 at Intermediate Shutdown, utility QA personnel found the Emergency Diesel Generator (EDG) Number 1 room rear exit door tied open. This condition, which limited the ability of the carbon dioxide fire suppression system to perform its intended function, had existed for a period in excess of that allowed by Technical Specifications (TS) 3.21.B.4. On October 28, 1991, at approximately 0920 hours, the automatic door release device was repaired and engaged. The cause of this event is attributed to a cognitive error on the part of contractor personnel in failing to provide explicit instructions on how to properly secure open the EDG number 1 room rear exit door. To prevent recurrence, the general employee training program will be revised to include a discussion of the significance of fire suppression system boundary doors and how to use the automatic door release device. Signs are also being installed on both sides of doors equipped with an automatic release device, cautioning that the door is a fire protection system boundary. In addition, station doors are being evaluated and labeled or color coded, as appropriate, to indicate their safety significance to station operation. The event is being reported, pursuant to 10CFR 50.73(a)(2)(i)(B), since this condition is prohibited by TS 3.21.B.4.
2801991022 | Surry 1 | 12/04/1991 | 12/30/1991 | 9201060366 | <strong>Containment Spray Pump Surveillance Testing Exceeded Technical Specification Requirements Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1991, with Unit 1 at 100% power, it was discovered that the Containment Spray Pumps (1-CS-P-1A and 1-CS-P-1B) had not been demonstrated operable between January 1, 1991 and May 14, 1991. This exceeded the allowed 92 day interval between surveillance tests and thus was a violation of Technical Specification 4.0.3. Since the containment spray pumps remained operable throughout the period, the health and safety of the public were not affected. The cause of these events was personnel error in the conduct of the surveillance test program which occurred during the late January/early February 1991 time frame. A Task Team had been formed earlier this year to review these and similar events, and appropriate corrective action was taken. These events are being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2811991001 | Surry 2 | 03/07/1991 | 04/05/1991 | 9104160505 | <strong>Failure to Demonstrate PORV Block Valves Operable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1991, at 1600 hours, with Unit 2 at 87% power, it was discovered that the Pressurizer Power Operated Relief Valve (PORV) Blocking Valves (2-RC-MOV-2535 and 2-RC-MOV-2536) had not been demonstrated operable at least once during the previous 92 days. This failure is a violation of Technical Specification 4.1.B.2. The block valves were declared inoperable until the required surveillance testing was satisfactorily accomplished. Since the PORVs remained operable throughout the period, the health and safety of the public were not affected. The cause of the event was personnel error. A Task Team was formed to review this and similar events, and appropriate corrective action is being taken. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2811991002 | Surry 2 | 03/26/1991 | 04/23/1991 | 9104290115 | <strong>Main Steam Safety Valves Out of Tolerance Due to Minor Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991, with Unit 2 at 75% power during end of fuel cycle coast down, setpoint testing of the fifteen Main Steam Code Safety Valves revealed that the lift setting of 2-MS-SV-205B was outside of the 3% "as found" range allowed by Surry's Technical Specifications. The valve exhibited a lift setting of 3.3% below its nominal value (1135 psig). The safety valve was readjusted to be within the required setpoint tolerance. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for conditions prohibited by Technical Specifications 3.6.A, 3.6.B.3 and 3.6.D.
2811991003 | Surry 2 | 04/24/1991 | 05/22/1991 | 9105300191 | <strong>Pressurizer Safety Valve Setpoints Outside of Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1991, with Unit 1 at 100% power and Unit 2 at Refueling Shutdown, two Unit 2 pressurizer safety valves were found to have lift setpoints lower than the minimum setpoint allowed by Technical Specifications. The "A" safety valve actuated at 2433 psig while the "B" safety valve actuated at 2397 psig. This is contrary to Technical Specification 3.1.A.3, which requires the lift setpoints to be 2485 psig +5%/-1%. The event had no safety consequences since the safety valves were capable of performing their overpressure mitigating function and no adverse effects would result from the lower lift setpoints. The valves were refurbished, reset to 2485 psig +/-1%, and re-installed. This report is required by 10CFR50.73(a)(2)(i)(B) since a condition not allowed by Technical Specifications existed.
2811991004 | Surry 2 | 05/14/1991 | 06/13/1991 | 9106190421 | <strong>Inadvertent Overfilling of Refueling Water Storage Tank</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1991, with Unit 1 at 100% power and Unit 2 at Cold Shutdown, during a technical review of an inadvertent overfilling of the Unit 2 Refueling Water Storage Tank (RWST), the as-built configurations of both Units' RWSTs were reevaluated. The reevaluation determined that the positioning of the Unit 2 RWST overflow line would permit the tank to be filled in excess of the Technical Specification capacity limit. Through consultation with the Architect/Engineer, it was determined that no structural limits were exceeded. Therefore, the health and safety of the public were unaffected. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2811991005 | Surry 2 | 06/02/1991 | 06/27/1991 | 9107100129 | <strong>Reactor Coolant System Leakage Exceeded Technical Specification Limits Due to the Mechanical Failure of Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1991, at 1431 hours, with Unit 1 at 100% power and Unit 2 at Hot Shutdown, leakage from the Unit 2 Reactor Coolant System (RCS) exceeded that allowed by Technical Specifications (TS). On June 2, 1991, at 0659 hours, the three inch diameter RCS loop "C" resistance temperature device manifold isolation valve (2-RC-95) was identified as the source. At 1432 hours, a 30 hour Limiting Condition for Operation to Cold Shutdown was entered in accordance with TS 3.0.1 since the leakage exceeded the TS allowed RCS total leakage criteria (10 gallons per minute) and a cooldown from Hot Shutdown to Cold Shutdown was initiated. A Notification of Unusual Event was declared on June 2, 1991, at 1431 hours. The event was terminated on June 3, 1991, at 0506 hours, when Unit 2 was placed in Cold Shutdown. On June 3, 1991, at approximately 1300 hours, valve 2-RC-95 was closed and leakage from the valve was reduced to 0.5 to 1.0 gallons per minute. On June 4, 1991, following an Engineering review, the valve internals were removed and a blank cap was installed on the valve body. The cause of this event is attributed to a mechanical failure of valve 2-RC-95. The event is being reported, pursuant to 10CFR 50.73(a)(2)(i)(B), since this condition is prohibited by TS 3.1.C.5.
2811991006 | Surry 2 | 07/19/1991 | 08/16/1991 | 9108230272 | <strong>Safety Injection System Interlock Rendered Inoperable and Unit Not Placed in Hot Shutdown Within Six Hours Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1991 at 2030 hours, with Unit 1 operating at 90% power and Unit 2 operating at 100% power, a Unit 2 Refueling Water Storage Tank level channel failed low. On July 20, 1991 at 1500 hours, the Unit 2 Recirculation Mode Transfer (RMT) System was placed in the "Refuel" mode, defeating automatic RMT. This was done to prevent an additional channel failure from causing a spurious RMT actuation. Administrative control was established to ensure RMT would be returned to the "RMT" (automatic) mode if needed. Discussions with the Nuclear Regulatory Commission on July 23, 1991 resulted in the determination that Technical Specifications had been violated, since a Safety Injection interlock had been rendered inoperable and the unit had not been placed in hot shutdown within six hours. The RMT System was returned to the "RMT" mode. RMT capability existed throughout the event, hence there were no adverse consequences to public health and safety. The event was caused by personnel error in that operations and management personnel improperly concluded that placing RMT in the "Refuel" mode did not violate Technical Specifications. A proposed Technical Specification change specifically addressing RMT will be submitted and the use of administrative control will be restricted. This report is required by 10 CFR 50.73(a)(2)(i)(B).
2811991007 | Surry 2 | 08/02/1991 | 11/12/1991 | 9111210038 | <strong>Safety Injection/Reactor Trip From Vital Bus IVA Electrical Fault and Failure of Steam Generator Pressure Transmitter</strong><br /><i>Abstract:&nbsp;</i>At 1657 hours on August 2, 1991, with Unit 1 at 100% power and Unit 2 at 92% power, an Engineered Safeguards Feature actuated in Unit 2. A safety injection/reactor trip occurred as a result of a high steam flow signal coincident with a low steam line pressure signal. These conditions did not actually exist, but were generated by a combination of an erratic steam generator pressure channel and an electrical fault in a vital bus distribution panel. Troubleshooting was in progress on both problems, but the actuation occurred before corrective action could be completed. ESF functions performed as expected except for the failure of Emergency Diesel Generator #3 to achieve rated speed and the failure of the Containment Sump Pump Discharge Trip Valve (02-DA-TV-200A) to fully shut. A Notification of Unusual Event (NOUE) was declared at 1710 hours, and appropriate reports were made. On-shift operating personnel promptly placed the plant in a stable condition. The NOUE was terminated at 1840 hours. A Root Cause Evaluation of the Emergency Diesel Generator problem is being conducted. The results of this evaluation will be reported in Licensee Event Report S1-91-017. A Component Failure Analysis of the Containment Sump Discharge Trip Valve has been conducted, and the results are included in this supplementary report. This event is reportable pursuant to 10CFR50.73(a)(2)(iv).
2811991008 | Surry 2 | 08/14/1991 | 09/13/1991 | 9109190269 | <strong>Unit 2 "A" Charging Pump Component Cooling Pumps Exceeded Its 24- Hour Limiting Condition for Operation Due to Unexpected Events and Problems</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1991, at 0552 hours, with Unit 1 at 100% power, and Unit 2 ramping from 85% to 100% power, the Charging Pump Component Cooling (CC) pump, 2-CC-P-2A, was tagged out to replace the pump discharge check valve. A 24 hour Limiting Condition for Operation (LCO) was entered in accordance with Technical Specification (TS) 3.13.B. Return to service testing activities were delayed by a dropped rod and turbine runback transient that occurred at 1753 hours. When Post-Maintenance Testing (PMT) activities were resumed at 2235 hours, a pump flange leak resulted in unplanned maintenance. The maintenance activities affected the system response of this ASME XI system, and the PMT results required engineering evaluation. The 24-hour LCO expired at 0552 hours on August 15, and a 6-hour clock to Hot Shutdown (HSD) was then centered as per T.S. 3.0.1. At 0657 hours, with repairs and testing complete, the pump was evaluated by Engineering personnel as operable, and the 6-hour clock to HSD was exited. The redundant system remained operable throughout this event, and the health and safety of the public were not adversely affected. The event was caused by unanticipated delays in maintenance and testing activities. This event is being reported pursuant to 10CFR50.73(b)(2)(i).
2811991009 | Surry 2 | 09/03/1991 | 09/30/1991 | 9110070353 | <strong>Failure to Full Flow Test 2-RH-47 Due to Producer Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1991, with Unit 2 at 59% reactor power, it was determined that check valve 2-RH-47 had not been full flow tested during the Unit 2 Cycle 10 refueling outage as required by the Unit 2 ASME Section XI Inservice Testing Program Revision 2. This determination was made during the station inservice inspection group's independent review of the implementation of the Surry ASME Section XI Program. This event occurred as the result of personnel procedural error in that the test procedure used to satisfy the full flow testing requirement contained an improper valve lineup. Following this discovery, the affected procedure was changed and full flow testing was satisfactorily performed on September 8, 1991 during a forced outage. Because the system had been verified capable of delivering design basis flow during the Unit 2 Cycle 10 refueling outage and subsequent valve testing determined that 2-RH-47 was operable, no safety implications were posed by this event. This missed surveillance test was determined to be a violation of Technical Specification 4.0.3 and is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2811991010 | Surry 2 | 10/31/1991 | 06/02/1992 | 9206100174 | <strong>Loss of Containment Integrity Caused by Failed Main Steam Trip Valve Bypass Valve</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1991, at 0017 hours, with Unit 2 critical at 10E-8 amps intermediate range indication, it was determined that damage to the "C" Main Steam Trip Valve (MSTV) Bypass Valve, 2-MS-155, rendered the valve incapable of immediate closure. The on-shift operations staff determined that the inability to close this manual valve immediately was contrary to the requirements of Technical Specification 3.8.A.1 concerning containment integrity. An action statement was entered in accordance with Technical Specification 3.0.1. The "C" Main Steam Non-Return Valve and associated drain valves were closed at 0605 hours to re-establish containment integrity and terminate the action statement. The "C" MSTV Bypass Valve was closed using a hydraulic jacking device and mechanically blocked closed by 0900 hours. No adverse consequences to public health and safety were created since the Non-Return Valve was available to isolate the main steam line. The event was caused by failure of the yoke bushing threads in 2-MS-155, which is believed to be the result of galling on the valve stem threads. Valve 2-MS-155 was replaced and a failure evaluation will be performed. This report is required by 10 CFR 50.73(a)(2)(i)(B).
2811991011 | Surry 2 | 12/17/1991 | 01/14/1992 | 9201210284 | <strong>High Steam Generator Level due to Main Feedwater Regulating Valve Oscillations Results in ESF Actuation and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1991, at 2254 hours, with Units 1 and 2 at 100% and 23% power, respectively, a Unit 2 automatic reactor trip occurred as a result of a turbine trip due to high steam generator (SG) level. The required safety systems performed as designed, appropriate operator actions were taken to ensure the performance of system automatic actions, and the unit was quickly brought to a stable no-load condition. The cause of this event is attributed to the failure of the "B" main feedwater regulating valve (MFRV) to maintain a demand position. This condition resulted in a high SG level, the main feedwater pumps tripping, automatic start of auxiliary feedwater (AFW) pumps, turbine trip, and an automatic reactor trip. The "B" MFRV was inspected on December 18, 1991. The positioner was found to be worn and was replaced and tested. During the subsequent unit startup on December 18, 1991, a similar less severe oscillation of the subject valve was noted. Therefore, a Root Cause Evaluation is being performed to determine the cause of this condition. A non-emergency four-hour report, pursuant to 10CFR 50.72(b)(2)(ii), was made to the Nuclear Regulatory Commission at 0235 hours on December 18, 1991. This event is being reported, pursuant to 10 CFR 50.73(a)(2)(iv), as an unplanned Engineered Safety Feature actuation as a result of a valid signal.
2821991001 | Prairie Island 1, Prairie Island 2 | 03/14/1991 | 04/12/1991 | 9104190220 | <strong>Auto-Start Of Spent Fuel Pool Special Ventilation System Due To Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1991, both units were operating at full power. Surveillance procedure SP1115, Spent Fuel Pool Special Ventilation System Test, was being performed. This test verifies that the Spent Fuel Pool Special Ventilation System is activated and the normal spent fuel pool ventilation system isolated by actuation of redundant radiation monitors. Spent Fuel Pool Special Ventilation Train A had been tested satisfactorily. When Train B was to be tested, the Train A radiation monitor was put in RESET per the procedure. After high radiation was simulated on the Train B radiation monitor, control room operators observed that spent fuel pool normal ventilation had isolated as required but that both trains of the Spent Fuel Pool Special Ventilation System were running. Actuation of Train A was a non-ESF actuation of an ESF system. Troubleshooting of the Train A radiation monitor revealed no problems. SP1115 was then performed again in its entirety; the monitors and the actuation circuitry operated as designed. Further investigation was done. No cause for the event could be assigned and the spurious actuation of Train A of the Spent Fuel Pool Special Ventilation System could not be duplicated: Possible causes were investigated but no cause could be assigned. Observation of the equipment is continuing.
2821991002 | Prairie Island 1, Prairie Island 2 | 03/23/1991 | 12/07/1992 | 9212140163 | <strong>Auto-start of Control Room Special Ventilation System Due to Spike on Newly Installed Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1991, both units were operating at full power. At 0019 hours a spike on radiation monitor R-23 caused control room annunciation of control room High Radiation Train A, which resulted in auto-start of No. 121 Control Room Cleanup Fan and isolation of the control room outside air supply. <br /><br /> Several unplanned actuations of Engineered Safety Features ventilation systems had taken place over a period of several years as a result of spiking in the circuitry of radiation monitors. To help prevent recurrences, upgraded monitor modules had been ordered from the manufacturer, received, and installed. Spurious high radiation alarms occurred in these new monitors in the first few hours of operation.
2821991003 | Prairie Island 1, Prairie Island 2 | 04/23/1991 | 05/23/1991 | 9105300152 | <strong>Auto-Start of One Train of Auxiliary Building Special Ventilation System Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1991, both units were operating at full power. At 0938 control room operators observed annunciation of a RADIATION MONITOR DOWNSCALE FAILURE, and noticed that No. 121 Auxiliary Building Special Ventilation System was running. Inspection of the control room radiation monitoring panel showed a failure alarm for radiation monitor 2R-37, which actuates the Auxiliary Building Special Ventilation System on a high radiation signal. No high radiation alarms were received, and normal background response was indicated on the panel meter and also by the redundant monitor 1R-37. Since there was no high radiation condition in the Auxiliary Building, the control room operator reset the alarm on the radiation monitor and returned the Auxiliary Building Special Ventilation System to the normal standby condition and returned the Auxiliary Building Normal Ventilation System to service. The system engineer was contacted and an investigation of the downscale failure was begun. <br /><br /> Testing by the plant and by the manufacturer have identified no cause for the actuation.
2821991004 | Prairie Island 1 | 05/09/1991 | 06/10/1991 | 9106140186 | <strong>Failure of Redundant Heat Trace Circuits as Result of Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1991, Unit 1 was at 85% power, coasting down to a refueling outage. An outplant operator was in the process of hanging a replacement identification tag on a valve. In order to reach the valve, the operator stepped on an insulated and heat traced section of safety injection piping. When he stepped down off the pipe, at 1255, the operator smelled and observed smoke emitting from beneath the pipe insulation. <br /><br /> Nearby heat trace circuits were de-energized to prevent additional arcing in the area. Circuit continuity checks showed, at 1345, that both ET-53 Normal and Redundant (ET-53N and ET-53R) heat trace circuits had failed. Technical Specifications require two channels of heat tracing to be operable on that section of piping. Since the there was no action statement for the inoperability of the two heat trace circuits, Technical Specification 3.0.C was applied at 1345. Temperature monitoring of the pipe was begun to insure it remained greater than 145 degrees F for boric acid solubility. Repairs began immediately. <br /><br /> Repairs to the ET-53R heat trace circuit were completed at 1745, the circuit was tested operable and placed in service. Heat trace circuit ET-53N was repaired the next day. The cause of the event was an electrical fault resulting from a heat trace conductor shorting to stainless steel banding that supports a heat trace junction box attached to the piping.
2821991005 | Prairie Island 1, Prairie Island 2 | 05/16/1991 | 08/09/1993 | 9308170048 | <strong>One Pressurizer Safety Valve Lift Setpoint</strong><br /><i>Abstract:&nbsp;</i>Historically, pressurizer safety valves used at Prairie Island have been set using nitrogen. As a result of NRC Information Notice 89-90 and guidance in Westinghouse WCAP-12910, it was decided to test pressurizer safety valves using steam. The 6 valves were tested at a contract facility over the period of 2 years as the valves became available after replacement at refuelings. <br /><br /> Testing with steam showed 4 of the 6 pressurizer safety valves lifted slightly below the nameplate setting of 2485 psig plus or minus 1%. Future testing of the safety valves will be done using steam.
2821991006 | Prairie Island 1, Prairie Island 2 | 05/25/1991 | 06/24/1991 | 9106270380 | <strong>Rad Waste Building Ventilation Discharge Continued Following The Placement Of Its Associated Noble Gas Monitor In Reset</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1991, Unit 1 was at 65% power coasting down to a June refueling and Unit 2 was at 100% power. At 0105, a control room operator, while performing the daily radiation monitor surveillance, discovered that the selector switch for radiation monitor R-35, the Radwaste Building Ventilation Monitor, was in RESET. The high radiation alarm function for R-35 is inoperable with its selector switch in RESET. There are no other automatic actions associated with this monitor. Upon discovery, the monitor selector switch was returned to the OPERATE position. <br /><br /> With the selector switch in any position but OPERATE, a local indicating light is illuminated; no alarms are generated.<br /><br /> During the day previous to this event, several radiation monitor evolutions took place. It is believed that the inadvertent switch movement took place during one of those evolutions. R-35 is physically adjacent to one of the other monitors whose status was changed during the previous day.<br /><br /> No releases via the Radwaste Building Ventilation System took place during the event.
2821991007 | Prairie Island 1, Prairie Island 2 | 05/28/1991 | 06/26/1991 | 9107030323 | <strong>Auto-Start of Auxiliary Building Special Ventilation System Caused By Testing They Wrong Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1991, Unit 1 was at 64% power coasting down to a June refueling and Unit 2 was at 100% power. An Instrument and Control Specialist had just completed maintenance on radiation monitor 1R-37, an Auxiliary Building Ventilation Gas Monitor. The functional response of monitor 1R-37, upon receipt of a high radiation signal, is to deactivate the Auxiliary Building Normal Ventilation System and actuate the No. 121 Auxiliary Building Special Ventilation System. The functional response of the redundant monitor, 1R-30, is to deactivate the Auxiliary Building Normal Ventilation System and actuate the No. 122 Auxiliary Building Special Ventilation System. To complete functional testing of monitor 1R-37, the Instrument and Control Specialist arranged for the assistance of a Radiation Protection Specialist. The Radiation Protection Specialist approached monitor 1R-30, the redundant monitor, with a radiation source, and reported via radio that he was standing by monitor 1R-37. When the Instrument and Control Specialist asked the Radiation Protection Specialist to simulate high radiation on the monitor, No. 122 Auxiliary Building Special Ventilation System started, an unplanned auto-start.
2821991008 | Prairie Island 1, Prairie Island 2 | 06/19/1991 | 07/19/1991 | 9107240070 | <strong>One Unit 1 Safety-related Snubber Failed Its Functional Test</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1991 Unit 1 was shutdown for refueling. The snubber at location 1-SIRH-23B was being functionally tested in accordance with Technical Specification 4.13.C. The snubber had been in service for 5 years on a Safety Injection Accumulator discharge line. The snubber failed its functional test. Fluid condition was also found to be unacceptable; the fluid, usually translucent with a blue or pink tint added, had deteriorated such that it was dark and opaque. The snubber was declared inoperable and corrective actions were taken. <br /><br /> The snubber experiences a small-amplitude constant vibration. It is believed that this vibration, which causes constant movement of the snubber piston, results in localized heating of the snubber fluid. In those snubbers utilizing metal piston rings, it is believed that the localized heating is sufficient to cause degradation of the snubber fluid. Fluid degradation allowed heating and abnormal wear of metal piston rings and cylinder walls. The degraded fluid partially plugged internal control valves, preventing proper piston movement. <br /><br /> An adjacent snubber, which uses elastomer rings, was inspected and found to be in good condition. Snubbers of the vendor's later design use elastomer rings.
2821991010 | Prairie Island 1, Prairie Island 2 | 07/19/1991 | 08/08/1991 | 9108120370 | <strong>Auto-Start of Control Room Special Ventilation System Due to Spurious Radiation Monitor Actuation During Monitor Calibration</strong><br /><i>Abstract:&nbsp;</i>On July 19,1991, both units were operating at 100% power. SP1027, Radiation Monitoring System Annual Calibration, was in progress. Technicians were calibrating R-1, Control Room Area Monitor, by simulating high radiation with application of a radiation source. Two-way radios are sometimes used by the technicians during the calibration procedure. The technician with the source made a decision not to use the two-way radio during this calibration, since the technician thought radio use in the control room was not prudent. The technician's action had the effect of lengthening the calibration procedure. At 1325 control room operators noted receipt of a high radiation alarm, auto-start of control room cleanup fans and isolation of the control room outside air supply. The high radiation alarm and auto-start were a result of high radiation sensed by radiation monitors R-23 and R-24, Control Room Air Supply Monitors, whose detectors are physically located nearby radiation monitor R-1. When operators had determined the cause of the monitor actions, they returned the control room ventilation system to normal. <br /><br /> Cause of the event is procedure inadequacy. The calibration procedure does not caution the technician concerning the consequences of leaving the radiation source in place too long.
2821991011 | Prairie Island 1, Prairie Island 2 | 08/16/1991 | 09/16/1991 | 9109190255 | <strong>Unit 1 Trip As A Result Of Rod Control System Failure</strong><br /><i>Abstract:&nbsp;</i>At 0127 hours on August 16, 1991 Unit 1 tripped unexpectedly from 100% power. The "first out" annunciator was the negative flux rate trip. Review of rod position indication just prior to and after the trip indicated that the four Control Bank A, Group 2 rods that are powered from power cabinet 2AC began to fall into the core prior to receipt of the reactor trip signal. Extensive testing of the rod control system was done. Testing of the failure detection circuitry (urgent failure alarm) showed some conditions exist under which some rods would unexpectedly drop. The system does not provide protection against dropping rods for all component malfunctions or failures. <br /><br /> The most likely cause of the event was intermittent failure in a firing card for the stationary grippers supplied by power cabinet 2AC, causing interruption of power to the Control Bank A, Group 2 rods. During post trip testing which simulated high temperatures found on firing components during normal operation, the card developed an unacceptable wave form in an oscillator circuit. This card had previously tested satisfactorily at room temperature. The intermittent control circuit failure occurred such that the failure detection circuitry did not protect the affected rods against dropping.
2851991001 | Fort Calhoun | 01/09/1991 | 02/08/1991 | 9102120030 | <strong>Containment Tendon Surveillance Determined Not In Accordance With Tech. Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1991, with the reactor in Mode 1 at approximately 26% power, it was determined that prior to the performance of the containment tendon surveillances in 1981 and 1985, the test procedures were changed to reflect the guidance of Revision 3 to Regulatory Guide 1.35. Technical Specification 3.5(7)a, which incorporates the guidance in Revision 1 of Regulatory Guide 1.35, is more restrictive relative to detensioning of tendons. By using guidance not reflected in the Technical Specifications, both these tests failed to completely detension all the required tendons. This violation of the Technical Specification is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root cause for this event was inadequate administrative control of the tendon surveillance program, with inappropriate actions by personnel as a contributing factor. <br /><br /> Corrective actions include: enhancement of station engineering support, including implementation of a Containment Testing Program Plan; improvements in the safety evaluation process for procedure changes; and submittal of a proposed license amendment to incorporate appropriate Regulatory Guide 1.35, Revision 3 guidance into the Technical Specifications.
2851991002 | Fort Calhoun | 12/09/1990 | 03/18/1991 | 9103250353 | <strong>VIAS Actuation During Primary System Sampling</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1990, the shift chemist was obtaining a sample from the Reactor Coolant System pressurizer surge line. A Ventilation Isolation Actuation Signal (VIAS) was generated by a high alarm on process radiation monitor RM-062 when gas from the drain header was exhausted to the plant stack via the sample sink fume hood. This was apparently caused by accumulation of noncondensible gases in the sample piping due to a packing leak on a containment isolation valve, which caused a sampling line relief valve to lift and pressurize the waste disposal header. <br /><br /> Following re-evaluations of reportability, it was determined that the VIAS caused the containment isolation valves on the Containment Atmosphere Sampling Penetrations to close as designed. This actuation of a portion of the Containment Isolation Engineered Safety Feature System is reportable pursuant to 10 CFR 50.73(a)(2)(iv). <br /><br /> Corrective actions include repair of the valve packing leak, evaluation of and changes to the sampling procedure, and monitoring of the primary sample system.
2851991003 | Fort Calhoun | 02/04/1991 | 03/04/1991 | 9103120198 | <strong>Containment Penetration M-3 Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1991 with the plant operating at 100% power, the Plant Review Committee determined that containment penetration M-3 which is associated with the Chemical Volume Control System (CVCS) was outside the design basis specified in a Safety Evaluation Report (SER) which allowed exclusion from Type C testing required by 10 CFR 50 Appendix J. Past approval of Emergency Operating Procedure requirements and implementation of modifications which changed the post-accident containment pressure profile had invalidated the SER basis. <br /><br /> This condition resulted from failure to incorporate design basis information into the Updated Safety Analysis Report (USAR Procedural controls have been instituted to assure the design basis for penetration M-3 is met; these controls will be further enhanced in the future. The USAR will be updated to include the design basis for this penetration..
2851991004 | Fort Calhoun | 02/12/1991 | 06/21/1991 | 9106260205 | <strong>Offsite Power Low Signal Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>The Offsite Power Low Signal (OPLS) provides degraded voltage protection to safeguards equipment; when a degraded voltage condition exists concurrent with a Safety Injection Actuation Signal (SIAS), the OPLS signal isolates safeguards buses 1A3 and 1A4 from their offsite power supply (161 KV) and initiates automatic actions to load the safeguards equipment onto the emergency diesel generators. Engineering analysis revealed that, during a postulated accident, the voltage supplied to some 480 V safeguards loads could degrade to as low as approximately 87.5% of rated voltage without OPLS being actuated. Since the possibility existed for voltage to be lower than the recommended 90% of rated voltage for certain 480 V safeguards loads without an OPLS actuation, management determined on February 12, 1991 that the plant was outside of its design basis. <br /><br /> Corrective actions include administrative controls of equipment configurations and bus loadings, as well as resetting of the OPLS setpoints. A modification will be implemented to alter existing logic circuitry such that, upon receipt of an SIAS, large 4160V motors/equipment which are not required to mitigate consequences of an accident will be load shed.
2851991005 | Fort Calhoun | 02/28/1991 | 04/01/1991 | 9104080196 | <strong>Violation of Instrumentation and Control Technical Specification 2.15</strong><br /><i>Abstract:&nbsp;</i>At 0004 hours on February 28, 1991, it was discovered that Steam Generator (SG) pressure indicator B/PIC-905 was reading approximately 56 psig lower than normal, and was declared inoperable. At 0025 Reactor Protective System (RPS) trip units #6 (Low SG Pressure), and #7 (Asymmetric SG Transient on "B" channel were bypassed in accordance with Technical Specification (TS) Limiting Condition for Operation (LCO) 2.15, Table 2-2. <br /><br /> At 1144 I&C technicians installed a mechanical jumper (bypass) on B/PIC-905 to support corrective maintenance on the indicator. TS LCO 2.15, Table 2-4 was entered requiring the bypass to be installed within 8 hours due to one input to channel "B" Engineered Safety Features (ESF) Steam Generator Low Pressure (SGLS) being inoperable. At that time it was realized that the ESF function for B/PIC-905 should have been bypassed within 8 hours from the time of discovery of inoperability. Since the bypass was not installed within 8 hours, this constituted a condition prohibited by the TS. At 1641 hours, B/PIC-905 was restored to operability. <br /><br /> This condition resulted from misinterpretation of the Technical Specifications by Operations personnel. Corrective actions include training on this event and implementation of a written Technical Specification Interpretation.
2851991006 | Fort Calhoun | 03/05/1991 | 04/04/1991 | 9104100014 | <strong>Failure to Establish Compensatory Firewatches</strong><br /><i>Abstract:&nbsp;</i>At 0812 on March 5, 1991, fire detection Zone 6 alarmed in the Control Room. This alarm could not be reset, and was determined to be a false alarm of an individual detector caused by maintenance activities. Prior to this event, 2 fire barriers within detection zone 6 had been declared inoperable and an hourly fire watch had been implemented in accordance with Technical Specification 2.19(7). When detection Zone 6 became inoperable, a continuous fire watch should have been established for these inoperable barriers in accordance with the requirements of the Technical Specification. <br /><br /> The root cause of this event was inadequate administrative control to assure the modification which installed the XL-3 panel was properly reflected in the Operating Procedures and the Training Lesson Plans. This resulted in inadequate understanding by Operations personnel of how the modified detection system works; thus, Operations personnel did not realize the entire detection zone was inoperable. The required continuous fire watch, as well as several hourly fire watches required by Technical Specification 2.19(1), were not established. <br /><br /> Corrective actions include clarification of system functions to Operations personnel, and revision of the appropriate Operations procedures and the Training Lesson Plans to provide better guidance on Fire Detection System operation. Operations personnel will receive training on these changes.
2851991007 | Fort Calhoun | 03/20/1991 | 02/10/1993 | 9302220168 | <strong>480V Circuit Breaker Coordination Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>During reconstitution of the design basis for the electrical distribution overcurrent tripping scheme, preliminary results (March, 1991) of a Breaker/Fuse Coordination Study identified twenty-one 480 volt molded case circuit breakers which had overlapping breaker coordination curves with safety-related 480V Motor Control Center (MCC) feeder circuit breakers. The lack of coordination could have resulted in the tripping of a MCC due to a fault on one of its non-coordinated loads. On March 20, 1991, this condition was determined to be outside the design basis of the plant. Two of the twenty-one loads were determined to have an unacceptable probability of faulting during a Design Basis Accident. The two affected loads were isolated from the 480V system. <br /><br /> This condition was caused by deficiencies in the original system design as constructed by the plant Architect/Engineer. A contributing cause was the lack of comprehensive design basis documentation to substantiate that coordinated breaker fault protection existed. <br /><br /> Since submittal of LER 91-007 Revision 00, a detailed walkdown of MCCs has been conducted, safety significant coordination problems have been corrected (under Modification MR-FC-89-013), and the Breaker/Fuse Coordination Study completed. During incorporation of walkdown data into the study, an additional inadequate coordination was identified. However, it had been corrected by MR-FC-89-013 prior to discovery.
2851991008 | Fort Calhoun | 04/17/1991 | 05/17/1991 | 9105280089 | <strong>Inappropriate Surveillance Requirements for RPS Level 1 Bistables</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1991 with the plant at 70% power, the Level 1 Bistables on the Power Range Safety Channel Nuclear Instrument units (A thru D) of the Reactor Protective System (RPS) were declared inoperable due to the bistables not being tested monthly pursuant to a Technical Specification (TS) Interpretation of TS Table 3-1 requirements. However, the RPS trip units were determined to be operable. Subsequently, the interpreted requirement for monthly surveillance of the Bistables was determined to be invalid based on system design constraints; the Bistables were then declared operable.<br /><br /> This event was caused by the existance of inappropriate TS surveillance requirements for the Level 1 Bistables since initial issuance, and by inadequate documented verification of the incorporation of all applicable TS surveillance requirements into FCS Surveillance Test procedures. <br /><br /> Procedures have been implemented to calibrate and test the Level 1 Bistables prior to reactor startup. The affected TS Interpretation will be changed. A Technical Specifications Verification Action Plan is being implemented.
2851991009 | Fort Calhoun | 04/30/1991 | 05/30/1991 | 9106050396 | <strong>VIAS Actuation Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1991, at 0937 hours, an electrician was removing a label from inside a Control Room breaker cabinet and inadvertently tripped a normally closed breaker. Realizing what he had done, the electrician immediately reclosed the breaker, causing the Ventilation Isolation Actuation Signal (VIAS) to actuate due to a resultant spike of radiation monitors. The VIAS caused an unplanned actuation of some Engineered Safety Features. <br /><br /> This event resulted from inappropriate action by the electrician after realizing that he had accidentally tripped the breaker. Corrective actions include policy revisions to clearly state that all personnel are required to contact the Shift Supervisor or Control Room operators prior to correcting any unplanned situation.
2851991010 | Fort Calhoun | 05/17/1991 | 10/30/1992 | 9211030237 | <strong>Auxiliary Steam Piping in Room 57 Outside Design Basis (HELB)</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1991, at 1420 hours, plant management determined that Room 57 (the Upper Electrical Penetration Room), was outside the design basis of the plant as a result of discovering the presence of high energy Auxiliary Steam (AS) piping in the room. This piping had not been identified during the initial plant High Energy Line Break (HELB) evaluation. The major concern for this condition was the impact on the operability of safety-related electrical equipment in the high humidity/temperature environment that would occur based on a critical crack in the two-inch Auxiliary Steam line in Room 57. <br /><br /> The cause for this concern in Room 57 was the lack of attention to detail during original drawing review and physical walkdowns prior to performing the plant HELB evaluation in 1973. This resulted in failure to identify the subject piping and to take proper corrective actions. The immediate action taken was to separate the redundant trains of equipment by closing the normally-open fire dampers between those areas and Room 57, then to isolate the steam supply to the AS piping in the affected room. Long-term corrective actions included completion of an engineering analysis to evaluate the remainder of the AS system for similar HELB concerns and isolation of AS supply piping to the diesel generator rooms prior to energizing the AS header to the Auxiliary Building.
2851991011 | Fort Calhoun | 06/06/1991 | 07/22/1991 | 9107260159 | <strong>Pressurizer Pressure Low Signal (PPLS) Setpoints</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1991, at 1728 hours, plant management determined that the potential existed for the pressurizer pressure instrument loops to be calibrates in a manner which could have resulted in the inoperability to trip Pressurizer Pressure Low Signal (PPLS) within the design analysis limit. Although all four PPLS channels were set within the analysis limits, up to four instrument channels of the PPLS could have been inoperable due to calibration procedure deficiencies. <br /><br /> The root cause of this event resulted from the lack of an established program to assure that the calibration procedures were written to meet the assumptions/inputs used in the setpoint calculations. Corrective actions include the following: performing an evaluation (Calculation FC05565) to ensure that the existing PPLS trip setpoints (as calibrated) meet the Technical Specification requirements; revising the PPLS loop calibration procedures to eliminate the potential for error prior to their next expected use (January, 1992); and, establishing a program to evaluate and assure that design basis assumptions/inputs are met with current plant configuration and procedures.
2851991012 | Fort Calhoun | 06/20/1991 | 07/22/1991 | 9107260176 | <strong>Emergency Diesel Generator Auto-start Due to Loss of Transformer (T1A-4)</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1991, Fort Calhoun Station was operating at 55 percent power with the "B" Condenser isolated for repair work on a backwash valve (MOV-B-6B). The electrical distribution system was in its normal line up. Two electricians were troubleshooting a ground on the house service transformer (T1A-4) cooling fan, when one electrician inadvertently bumped the unlabeled Fault Pressure Auxiliary Relay (63FPX/T1A-4) inside the panel.<br /><br /> Energizing 63FPX/T1A-4 caused the transformer lockout relay, 86/T1A-4 to actuate, isolating the transformer from the 4160V bus 1A4. Additionally, this caused the 161KV supply breaker (Breaker 111) to open and lockout relay 86/BRK-111 to actuate as a protective measure for the 161KV supply system. As a result of the 86/T1A-4 lockout relay actuating, the Emergency Diesel Generator DG-2 auto-started-and accelerated to idle speed. <br /><br /> The causes of this event include personnel error, an exposed relay (63FPX/T1A-4) that contained several wires in close proximity, and an unlabeled relay in the cabinet. <br /><br /> Corrective actions include the following: label the 63FPX relays in the cabinet for proper identification, evaluate whether a different type of relay or a cover could be used to protect the relay from actuating should it be bumped, and revise the electricians' training program to include discussion on the unique wiring configuration within the transformer panels.
2851991013 | Fort Calhoun | 06/26/1991 | 07/26/1991 | 9107290205 | <strong>Diesel Generator Autostart Due to ST on DG-1</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1991, while Fort Calhoun Station was operating at 100 percent power, Diesel Generator DG-2 was inadvertently started during the performance of surveillance test OP-ST-DG-0001, "Diesel Generator Check", Attachment 4. An operator trainee, under the supervision of a Licensed Operator, was attempting to synchronize DG-1 to its associated 4160V bus. The trainee was late in closing the diesel generator output breaker, 1AD1, resulting in the instantaneous overcurrent relays tripping on phases 2 and 3, thus tripping the 86/D1 relay. Tripping 86/D1 caused the following to occur: breaker 1AD1 tripped and locked out, DG-1 tripped off, and DG-2 started. Throughout this event, the safeguard buses remained energized, and both diesel generators were available to perform their design functions. <br /><br /> The cause of this event is attributed to Human Error. The trainee closed the diesel output breaker, 1AD1, after the 12 o'clock position on the synchroscope. <br /><br /> As a corrective action, this event will be discussed in Licensed Operator Initial and Requalification Training.
2851991014 | Fort Calhoun | 06/29/1991 | 07/29/1991 | 9108050115 | <strong>Radiation Monitor RM-054A Out of Service</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1991 at 1659 hours, Fort Calhoun Station was operating at 100 percent power when the mode selector switch for steam generator blowdown radiation monitor RM-054A was discovered in the calibrate position. Upon discovery, the mode selector switch was returned to the operate position and steam generator A was sampled. For the approximately seventeen hours that the RM-054A mode selector switch was in the calibrate position, steam generator A blowdown radioactivity was not automatically recorded, nor was it manually recorded every four hours as required by Technical Specification 2.9.1(1)e. This violation of the Technical Specification is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The cause of this event was personnel error. During the performance of surveillance test OP-ST-SHIFT-0001 (Operations Technical Specification Required Shift Surveillance) on June 29, 1991 at 0020 by a senior reactor operator trainee, RM-054A's calibration was checked by taking the mode selector switch to the calibrate position. After the calibration check, the mode selector switch is required to be returned to the operate position. On this occasion, the mode selector switch was not returned to the operate position. <br /><br /> The corrective actions for this event consist of revising OP-ST-SHIFT-0001 to include a check-off when all radiation monitors being calibration checked are returned to operation and providing guidance on expectations for on-the-job training to both trainees and trainers.
2851991015 | Fort Calhoun | 07/10/1991 | 08/09/1991 | 9108140049 | <strong>Radiation Monitor RM-060 Inoperable Due To Seismic Concern</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1991 at 1711 hours, Fort Calhoun Station Unit No. 1 personnel declared radiation monitor RM-060 (stack iodine) inoperable due to the flow totalizer located inside the RM-060 radiation monitor cabinet not being seismically mounted. Thus, plant operations entered into Technical Specification (TS) Limiting Conditions for Operation (LCO) 2.9.1(2)(e) and 2.15(2), Table 2-4, Item 3. <br /><br /> Modification work to seismically support the flow totalizer was completed. Seismically mounting the flow totalizer returned the radiation monitor to within the criteria of Appendix F of the Updated Safety Analysis Report (USAR). RM-060 was declared operable and all associated TS LCOs were cleared.<br /><br /> Although actions were immediately taken to rectify the condition upon its discovery, this condition has existed since the installation of the flow totalizer in 1977. During this period all other functional requirements for RM-060 were met, and no releases occurrence with this monitor unavailable. However, because RM-060 would not have been available in a worst case scenario this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The primary cause of this event was the failure to analyze for seismic considerations during the development of the modification for installation of the flow totalizer in 1977. This can be attributed to inadequacies in the design process at the time. Corrective actions include seismically supporting the flow totalizer for RM-060 and previously implemented improvements to the modification control process.
2851991016 | Fort Calhoun | 08/02/1991 | 08/30/1991 | 9109040030 | <strong>Diesel Generator Failed Roll Pins</strong><br /><i>Abstract:&nbsp;</i>With the complete failure of a roll pin for diesel generator (DG-2) exhaust damper linkage on July 11, 1991, and the discovery of a crack in a roll pin for DG-1 exhaust damper linkage on July 18, 1991, it was decided to test the material composition/failure mechanism of these roll pins by an off-site laboratory. On August 2, 1991, Omaha Public Power District (OPPD) received preliminary notification from the metallurgical laboratory that the failure mechanism was probably due to a manufacturing defect. A four-hour report pursuant to 10 CFR 50.72(b)(2)(iii)(B) was made after the Plant Review Committee determined that a potential common mode failure existed. <br /><br /> The cause of failure of the split roll pins was determined to be temper-embrittlement. Subsurface cracking was found in the examined pins and all of the cracks emanated from lines of inclusions, thus the pins had failed prior to installation and not due to operating conditions. OPPD also reported this event to the NRC as a 10 CFR Part 21 "Reporting of Defects and Noncompliance" on August 23, 1991. <br /><br /> This event is safety significant due to the potential for common mode failure of both DGs. However, corrective actions taken by OPPD ensured the diesel generators would be able to perform their design safety function. <br /><br /> Corrective actions include installing a temporary modification to block open the exhaust dampers for both DGs, evaluating the adequacy of the existing roll pin design, revising/developing appropriate preventive maintenance procedures and initiating a modification request to move the position indicating switches of the DG exhaust dampers.
2851991017 | Fort Calhoun | 08/19/1991 | 09/17/1991 | 9109240389 | <strong>Potential for Radiological Release Through Safety Injection Refueling Water Tank Vents</strong><br /><i>Abstract:&nbsp;</i>As a result of evaluations prompted by similar industry events, Omaha Public Power District (OPPD) identified a potential radiological release path through the Safety Injection Refueling Water Tank (SIRWT) vents. Due to the possible post-LOCA backleakage of containment sump water to the SIRWT through SIRWT discharge valves LCV-383-1 and LCV-383-2, in the event of failure of a SIRWT discharge check valve SI-139 or SI-140, the design basis Loss of Coolant Accident (LOCA) dose consequences could exceed 10 CFR 100 and Standard Review Plan (SRP) 6.4 limits. This was identified as a reportable condition outside the Fort Calhoun Station design basis on August 19, 1991 at which time the NRC was notified pursuant to the requirements of 10 CFR 50.72(b)(1)(ii)(B). This Licensee Event Report is being submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) requirements. <br /><br /> Corrective actions included analyzing the radiological consequences of the identified limiting case condition using revised, but still conservative, source term and dispersion assumptions. These analyses showed Exclusion Area Boundary (EAB), Low Population Zone (LPZ), and Control Room doses to be less than regulatory limits (10 CFR 100 and SRP 6.4, as applicable). OPPD is pursuing replacement of LCV-383-1 and LCV-383-2 during the 1992 refueling outage, and plans to initiate a leak test program during the 1992 refueling outage for valves which isolate recirculating containment sump water from the SIRWT.
2851991018 | Fort Calhoun | 09/12/1991 | 10/15/1991 | 9110240226 | <strong>Inoperable Station Batteries Due to Inadequate Design of Terminal Post Seals</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1991, with Fort Calhoun Station operating at 100 percent power, a crack developed in the front wall of cell #17 of station battery #1. This cracked cell was the latest in a history of less severe cracks which had developed previously in the batteries. Lacking engineering analysis to support battery qualifications with cracked or overstressed jars, and finding a common mode failure mechanism for the batteries, the station batteries were declared inoperable on September 12, 1991. A Notification of Unusual Event (NOUE) was declared due to the Technical Specification 2.0 1 required shutdown. The NRC was notified pursuant to the requirements of 10 CFR 56.72 b)(1)(i)(A) and 10 CFR 50.72(b)(1)(ii)(A). <br /><br /> Although this event resulted in a plant shutdown, the direct safety significance of this event was minimal because the batteries were administratively inoperable, however, they were still functional. <br /><br /> The root cause of this event was an inadequate design of the battery cell terminal post seals. The seal design did not adequately allow for the buildup of corrosion products at the positive terminal. Since the incident, the station batteries have been replaced with batteries having an improved seal design which does allow for corrosion product buildup, and will permit plant operation until the 1992 refueling outage.
2851991019 | Fort Calhoun | 09/13/1991 | 10/15/1991 | 9110240258 | <strong>Approved Procedure Could Have Prevented Containment Spray From Fulfilling Design Function</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1991, while Fort Calhoun Station was operating in Mode 3 (Hot Shutdown) due to a concern with the station batteries, a potential unreviewed safety question was identified in which an approved procedure specified an incorrect position for valves in a backup nitrogen system. A discrepancy was discovered between the valve line-up checklists in two procedures, OI-NG-1 and OI-SI-1, regarding the valve positions of IA-HCV-344-N and IA-HCV-345-N, the N sub 2 bottle isolation valves to the Instrument Air header for the Containment Spray header isolation valves. This discrepancy was brought to the immediate attention of plant management, the positions of these isolation valves were verified open, and OI-NG-1 was revised to change the positions of IA-HCV-344-N and IA-HCV-345-N from closed to open. The Plant Review Committee determined that the incorrect positions of IA-HCV-344-N and IA-HCV-345-N in OI-NG-1 did not provide a positive means for opening the N sub 2 isolation valves, and thus could have prevented the Containment Spray system from fulfilling its design function. A four-hour report was made to the NRC pursuant to 10 CFR 50.72 (b)(2)(iii)(D). This Licensee Event Report is being submitted pursuant to 10 CFR 50.73(a)(2)(v)(D). <br /><br /> The safety significance of this event is low since the position of the valves were verified open and the upgraded procedure was never actually utilized in the field. <br /><br /> The root cause of this event is inadequate preparation and review of the 10 CFR 50.59 safety evaluation accompanying a procedure revision. In addition to revising OI-NG-1, corrective actions include revising the procedure writer's guides and incorporating the safety evaluation prepared for OI-NG-1 into 10 CFR 50.59 training.
2851991020 | Fort Calhoun | 09/19/1991 | 10/21/1991 | 9110290451 | <strong>Unmonitored Steam Generator Release to Missouri River</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1991 with Fort Calhoun Station (FCS) in a cold shutdown condition, steam generator water containing approximately 2.25 pounds of hydrazine was inadvertently released to the Missouri River, and no monitoring of this event took place. This is contrary to Technical Specification 2.9.1(e) which requires that liquid releases to the river be monitored, and 40 CFR, Table 302.4 "Lists of Hazardous Substances and Reportable Quantities" which limits the amount of hydrazine that may be released to the environment. The NRC was notified of this event pursuant to the requirements of 10 CFR 50.72(b)(2)(vi). <br /><br /> This event had no safety significance for FCS, although it did result in a failure to meet Technical Specification requirements and exceeded federal release limits. <br /><br /> The root cause of this event was the failure of a procedure, OI-FW-6, to specify the proper sequence for the performance of a valve checklist and the tagout clearance for the installation of a temporary jumper hose. Since this incident, OI-FW-6 has been revised to require verification that the temporary jumper hose installation tagout has been cleared prior to the performance of OI-FW-6-CL-D.
2851991021 | Fort Calhoun | 10/04/1991 | 11/04/1991 | 9111080110 | <strong>Inadvertent Containment Isolation Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1991, at 1248 hours, an inadvertent partial actuation of Containment Isolation Actuation Signal (CIAS) occurred at Fort Calhoun Station while the plant was heating up from Mode 4 (Cold Shutdown) to Mode 3 (Hot Shutdown). During the performance of Engineered Safety Feature (ESF) Surveillance Test (ST) OP-ST-ESF-0009, the components associated with the "A" Containment isolation panel AI-43A were inadvertently actuated and went to the required positions for a CIAS. Immediate investigation of the switch alignment revealed that the CIAS Override Switch did not have complete contact stackup when a trainee turned the switch to the "TEST" position. The ST was successfully performed the second time with the switch properly positioned. The containment isolation components that were activated performed their design function and there was no safety concern. A four-hour report was subsequently made to the NRC at 1430 hours pursuant to 10 CFR 50.72(b)(2)(ii). <br /><br /> Corrective actions include placing a caution tag on the switch to alert the operators of the potential problem with operating the switch, placing a caution statement in the procedure regarding the proper operation of the switch, and inspecting the switch during the next refueling outage.
2851991022 | Fort Calhoun | 10/09/1991 | 11/08/1991 | 9111120303 | <strong>Nuclear Instrumentation Channels B & D Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>Omaha Public Power District (OPPD) initiated an evaluation of the potential failure to meet the Regulatory Guide 1.97, Revision 2 (RG 1.97) design basis requirements for neutron flux indication. This review was in response to neutron flux channel concerns that occurred during shutdown for the Fort Calhoun Station (FCS) September 12, 1991 battery outage. OPPD concluded that the neutron flux monitoring channels selected to meet RG 1.97 (NE-002 and NE-004) do not meet the RG 1.97 single failure criteria. Failure of DC Bus No. 2 in a Design Basis Accident (DBA)/Post DBA (i.e., Loss of Coolant Accident or Main Steam Line Break in containment) could result in the loss of both NE-002 and NE-004. This condition is outside the FCS design basis and was reported to the NRC pursuant to 10 CFR 50.72(b)(1)(ii)(B) at 1651 hours on October 9, 1991. This event is not safety significant as reactor safe shutdown could be achieved without this wide range neutron flux indication. The root cause is the failure to follow procedure PED-QP-5. Contributing causes are lack of guidance and failure to understand the procedural requirements with regard to updating analyses/studies. A Nonconformance Report was issued to evaluate and correct the environmental qualification problem with the neutron flux channels, and to track final resolution of this condition which is outside the design basis of FCS.
2851991023 | Fort Calhoun | 10/22/1991 | 11/21/1991 | 9111260216 | <strong>Failure to Comply With Technical Specification 2.10.4(1)(b)(iii)</strong><br /><i>Abstract:&nbsp;</i>At 1308 hours, on October 22, 1991, while Fort Calhoun Station was operating at 99.3 percent power (Mode 1) with All-Rods-Out (ARO), the Emergency Response Facilities (ERF) computer system was taken offline for maintenance activities. However, this was done without meeting the requirements in Technical Specification (TS) 2.10.4(1)(b)(iii) which states that if the ERF is being used to monitor linear heat rate and becomes inoperable, then power operation may continue provided "power is not increased nor has it been increased since the time of the last incore power distribution." The last incore power distribution had been obtained at 0728 hours on October 22, 1991, at 98.2 percent power. Power then steadily increased from 98.2 percent at 0933 hours to 99.3 percent at 1300 hours where it was stabilized in the ARO configuration. Prior to taking the ERF offline, another incore power distribution should have been obtained in accordance with TS 2.10.4(1)(b)(i), since power had increased. The ERF was returned to service and the power distribution was obtained at 1339 hours, indicating that all monitored parameters were within their TS limits. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i). <br /><br /> A Human Performance Enhancement System (HPES) evaluation was performed and the cause of this event was human error due to failures in communications and work practices. The operators failed to perform a full review of the appropriate TS and all of its required actions in a timely manner. The safety significance of this event was evaluated and found to be minimal. Corrective actions include developing an Abnormal Operating Procedure to provide specific guidance when the ERF is offline, adding a precaution to the appropriate operating procedure and including this event in operator requalification training.
2851991024 | Fort Calhoun | 11/06/1991 | 12/06/1991 | 9112100191 | <strong>Unplanned Engineered Safety Feature Actuation After Pulling Fuses</strong><br /><i>Abstract:&nbsp;</i>At 0831 hours, on November 6, 1991, while Fort Calhoun Station was operating at 100 percent power (Mode 1), an electrician was removing fuses from inside a control panel in the Control Room when he pulled a fuse from the wrong fuse block. The removal of the fuse caused the Ventilation Isolation Actuation Signal (VIAS) relays B/94-1, B/94-2 and B/94-3 to de-energize. Loss of power to the VIAS relays caused two containment radiation monitor sample valves to close and the Control Room air conditioning unit and radiation monitor RM-065 to start. The electrician was instructed to reinstall the fuse and power was restored to the VIAS relays allowing the operators to reset the components. The components were returned to their normal configuration within two minutes of their actuation. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv). <br /><br /> The safety significance of this event is minimal based on the short duration of the event and the components which were affected. <br /><br /> The cause of this event was attributed to personnel error. The electrician failed to check the danger tag sheet to ensure that he was in the correct fuse block prior to pulling the fuse. <br /><br /> Corrective actions include a procedure change and an evaluation of the need to establish a formal self-checking program for the Electrical Maintenance and Instrument and Control groups.
2851991025 | Fort Calhoun | 11/14/1991 | 12/16/1991 | 9112200198 | <strong>Safety Injection Pipe Supports Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>While Fort Calhoun Station was operating at 100 percent power (Mode 1), it was determined that the upset and faulted loadings on two Safety Injection System pipe supports exceeded the design capacity of the embedded unistrut to which they are attached. This is a condition outside the plant design basis and was reported on November 14, 1991, pursuant to 10 CFR 50.72(b)(1)(ii)(B). This report is being submitted pursuant to the requirements of 10CFR 50.73 (a)(2)(ii)(B). <br /><br /> The primary cause of this event is attributed to a design analysis deficiency (i.e., inadequate consideration of Zero Period Acceleration (ZPA) loadings in an analysis performed by a consultant). A contributing factor was the lacks of experienced personnel at Omaha Public Power District (OPPD) to review the consultant's work. OPPD has since developed in-house expertise in the area of seismic analysis and has purchased a computer program which accounts for ZPA. <br /><br /> Corrective action involves modifying these piping supports to meet design basis requirements during the 1992 refueling outage. Although the loads on the unistrut exceeded the design basis, these pipe supports are considered operable based on interim operability criteria previously provided to the NRC.
2851991026 | Fort Calhoun | 11/05/1991 | 12/05/1991 | 9112100044 | <strong>Expired NRC Licensed Operator Medical Examination</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, while Fort Calhoun Station (FCS) was operating at 100 percent power (Mode 1), it was discovered that a Senior Reactor Operator (SRO) at FCS did not have a current NRC Licensed Operator medical examination as required in 10 CFR 55.21. Therefore, it was conservatively assumed that FCS did not meet the manning requirements specified in Technical Specification Table 5.2-1 "Minimum Shift Crew Composition" during the times the SRO stood watch. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).<br /><br /> The safety significance of this event is minimal based on the fact that the SRO involve did pass a subsequent NRC physical with no restrictions or discrepancies noted by the attending physician. <br /><br /> The root cause of this incident is a lack of single point control (procedure) of the NRC Licensed Operator (LO) Medical Examination Program. Contributing causes include the following: administrative procedures with inadequately defined responsibilities, inadequate tracking program for NRC LO physicals, and a lack of understanding of NRC LO physical requirements by personnel involved. Corrective actions consist of establishing one single definitive procedure to control the process, upgrading the OPTIM (Online Personnel Training Information Management) computer program, and issuing a management memorandum that ensures that licensed operators are aware of the requirements of 10 CFR 55.21.
2851991027 | Fort Calhoun | 11/18/1991 | 01/31/1992 | 9202040011 | <strong>Violation of Containment Integrity by Opening WD-1060 During Sampling</strong><br /><i>Abstract:&nbsp;</i>While operating at 100 percent power, reactor coolant drain tank (RCDT) pump discharge test valve WD-1060 was used to obtain 20 RCDT samples between October 16, 1991, and November 18, 1991, during the investigation of abnormal increases in tank level. WD-1060 is a 3/8 inch seal wired closed containment isolation valve (CIV) which taps off the RCDT pump discharge header between CIVs HCV-500A and HCV-500B. Opening of WD-1060 violated containment integrity as required by Technical Specification 2.6.(1). This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root cause of this event was the lack of formality in establishing the RCDT sampling program for the RCDT increased leakage investigation. Contributing causes include: no approved procedure for non-routine sampling, lack of understanding/training related to opening seal wired valves, and no labeling of seal wires.<br /><br /> Although containment integrity was violated, this event did not endanger the health and safety of the public because WD-1060 was closed after the sample was obtained; during the very short period for sampling, the Shift Chemist maintained control of WD-1060; the General Design Criterion was met by CIV HCV-500B; HCV-500A/B have been successfully quarterly stroke tested; and, the 1990 Refueling Outage Local Leak Rate Test results show that there is no leakage through these valves. <br /><br /> Corrective actions include: development of a method to ensure adequate review and approval for troubleshooting and non-routine sampling activities, revision of chemistry procedures, review of station standing orders, appropriate training, and development of a label for locked closed valves.
2851991028 | Fort Calhoun | 12/01/1991 | 02/28/1992 | 9203020077 | <strong>Unmonitored Release on Loss of 161KV System</strong><br /><i>Abstract:&nbsp;</i>At 0205 on December 1, 1991, it was discovered that the sample pump for the Laboratory and Radioactive Waste Processing Building (LRWPB) Exhaust Stack Gas, Iodine and Particulate Monitors was not running. At the time of the discovery, the Chemistry and Radiation Protection (CARP) Building exhaust fan was running. Operation of the exhaust fan while the sample pump was not running was determined to constitute an unmonitored release in violation of Plant Technical Specification 2.9.1(2)h(i), and is reportable under 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The event is considered to have been caused by a power excursion the previous day due to severe winter weather. 161KV offsite electrical power was lost and subsequently restored twice on November 30, 1991. It is assumed that when the initial loss of 161KV power occurred at 0430, the LRWPB Stack Radiation Monitors sample pump stopped, and did not restart when power was restored. The sample pump is designed not to reenergize following a power interruption until the Start/Stop switch is manually pushed. The CARP Building exhaust fan restarted when power was restored, resulting in the unmonitored release. During the time that the sample pump is assumed to have been deenergized, routine releases occurred which were found to be not significant. <br /><br /> A temporary modification has been installed to automatically restart the sample pump upon restoration of power after a loss of power. A change will be installed to provide Control Room indication of a flow fault or loss of power to the sample pump. In addition, the design configuration of the sample pump and exhaust fan control circuits is being further evaluated. Also a Facility License Change related to this issue will be submitted.
2851991029 | Fort Calhoun | 12/04/1991 | 01/03/1992 | 9201090139 | <strong>Personnel Air Lock Leak Rate Test Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1991, while Fort Calhoun Station was operating at 100 percent power (Mode 1), a Special Services Engineer (SSE) was reviewing a procedure for containment leak rate testing, when it was realized that this procedure did not adequately test the inner Personnel Air Lock (PAL) equalizing valve as required under Technical Specification 3.5.(3)d. Specifically, this specification requires that "the entire PAL assembly be tested to 60 PSIG" on a six month basis. However, because the procedure did not adequately test the equalizing valve, the "entire assembly" was not tested. A procedure was written to test the equalizing valve and this test was successfully conducted on December 7, 1991. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(v). <br /><br /> The safety significance of this event is minimal based on previous Integrated Leak Rate Tests which have proven containment integrity, and the fact that once properly tested, the equalizing valve was found to be operable. <br /><br /> The cause of this event was attributed to past inadequate procedure change reviews. A change was made to the testing procedure in 1974, which removed the equalizing valve from the test boundary. <br /><br /> Corrective actions included declaring the equalizing valve inoperable, generating a new procedure to test the equalizing valve, testing the valve, and reviewing all Type B Leak Rate Test Procedures along with the current configuration of Type B penetrations.
2851991030 | Fort Calhoun | 12/10/1991 | 01/09/1992 | 9201140007 | <strong>Radiation Monitors Out of Service With Containment Pressure Reduction In Progress</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1991, Fort Calhoun Station was operating at 100 percent power (Mode 1) with a Containment Pressure Reduction (CPR) in progress. A Licensed Operator was directed to terminate the CPR early so that it would not interfere with filter replacements on Auxiliary Building stack radiation monitors RM-060 (iodine), RM-061 (particulate) and RM-062 (gas). However, CPR was not terminated when RM-060 was removed from service to replace the filter cartridge as part of the weekly surveillance test (CH-ST-VA-0001). This violated the requirements of Technical Specification 2.9.1(2)g which states that during containment venting to the Auxiliary Building exhaust stack, the gas, iodine and particulate monitors shall be monitoring the stack. Therefore, this report is being submitted pursuant to 10 CFR 50.73(a)(23(i)(B).<br /><br /> The safety significance of this event is minimal due to the short time that the monitors were removed from service. Additionally, containment radiation monitors, RM-050 and RM-051, were in service at the time of this event and neither monitor showed any increase in containment activity. <br /><br /> This event resulted from a breakdown in verbal and written communication and work practices. CH-ST-VA-0001 does not comply with the existing surveillance test program in properly notifying Shift Supervisors prior to removing RM-060 from service. Also, the Operators involved did not verify the status of CPR.<br /><br /> Corrective actions include revising procedures (CH-ST-VA-0001 and OI-RM-1) and discussing this event in licensed operator requalification training.
2851991031 | Fort Calhoun | 12/16/1991 | 01/15/1992 | 9201210244 | <strong>Personnel Air Lock Door Connections Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1991, at 1305 hours while operating at 100 percent power (Mode 1), it was determined that the connections to the Personnel Air Lock (PAL) bulkheads for leak rate testing were potentially outside the original design requirements. The connections had been installed in 1974 to facilitate testing of the PAL and its door seals, however, design documentation could not be located to prove that the components were seismically qualified as a containment isolation boundary. This report is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(ii). <br /><br /> The PAL was determined to be operable with the unqualified components installed based on past seal leakage tests and by maintaining the inner door closed and sealed. Therefore, the health and safety of the public was not at risk.<br /><br /> The cause of this event is attributed to lack of procedures to control the plant configuration change process when these connections were installed in 1974. A contributing factor was the lack of understanding of the design basis of the PAL by those involved with the 1974 installation.<br /><br /> Immediate corrective action included establishing administrative control by danger tagging the outer PAL door to restrict access, thus ensuring that containment integrity was maintained. The unqualified components identified as being outside the design basis were then removed from the PAL and the resulting penetration openings were capped. This restored the PAL to the original design configuration. Long term corrective actions include completing a modification to install new valves and tubing, and revising the Technical Specifications and Updated Safety Analysis Report to reflect the new valves.
2861991001 | Indian Point 3 | 12/05/1990 | 01/03/1991 | ML09344135 | <strong>Inoperable Motor Operated Containment Valve Caused By An Undersized Spring Pack</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1990, with the plant at cold shutdown for the Cycle 7/8 refueling outage, plant staff determined that an automatic containment isolation valve normally open during plant operation, would not have been able to function during its design basis accident condition. Plant staff determined that this inability to function made the valve inoperable. This condition is prohibited by the plant's Technical Specifications whenever the plant is above the cold shutdown condition. The cause of the inoperability was an undersized spring pack in the valve's motor operator. The inoperability determination was made using the methodology of Generic Letter 89-10. Plant staff replaced the spring pack, retested the valve, and restored it to operable status on November 3, 1990.
2861991002 | Indian Point 3 | 12/05/1990 | 01/15/1991 | ML09344135 | <strong>Emergency Generator Operability Concerns Following Modification</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1990, during the cycle 7/8 refueling outage, control power fuses for 32 emergency diesel generator blew. Thirty-three (33) emergency diesel generator was out of service for the installation of a modification. This put the plant in a condition where it did not meet the minimum Technical specifications requirement that two of three emergency diesel generators be operable for all plant conditions. The blown fuse problem was caused by the installation of an improperly sized jacket water pressure switch (JWPS). A modification was designed and installed which resolved the problem. All three diesel generators were returned to operable status on December 9, 1990.
2861991003 | Indian Point 3 | 12/27/1990 | 01/21/1991 | ML09344135 | <strong>Manual Reactor Trip From Loss Of All Condenser Cooling Water</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1990, with the reactor at 48 percent power, a manual unit trip was initiated because control room operators observed all circulating water pumps had tripped off. Plant systems functioned properly following the trip, with the exception of 32 reactor coolant pump, which tripped during 6.9KV transfer from onsite to offsite power. The cause of the loss of circulating water pumps was a fault in a non-safety-related transformer. Following repairs, the unit was returned to service on December 28, 1990.
2861991004 | Indian Point 3 | 03/20/1991 | 04/15/1991 | ML09344135 | <strong>Plant Trip Resulting From Electrical Fault On 345 KV System</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1991 with the reactor at 100 percent power, a unit trip was initiated as the result of an electrical fault on a 345 KV bus section, remote to the site. The fault isolation circuitry opened both generator output breakers and generated a plant trip via the generator lockout relays. The components affected were subsequently repaired and tested. The plant returned to service on March 22, 1991.
2861991005 | Indian Point 3 | 03/22/1991 | 04/19/1991 | ML09344135 | <strong>Unit Trip Caused By Faulty Check Valve In Main Feed Pump Line</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1991, with the reactor at 25 percent power, a unit trip was initiated as the result of a steam generator low-low level trip. All plant systems functioned properly following the trip. The cause of this event was determined to be cyclic fatigue failure of the locking pin on the 31 main boiler feed pump check valve. The discharge check valves on both main feed pumps were overhauled and retested.
2861991006 | Indian Point 3 | 11/20/1990 | 04/26/1991 | ML09344135 | <strong>Voluntary LER Detailing Problems Identified During Generic Letter 89-10 Review</strong><br /><i>Abstract:&nbsp;</i>This LER is a voluntary submittal detailing the New York Power Authority's response to Generic Letter 89-10. On November 20, 1990, with the reactor in cold shutdown, the plant engineers conducted a design basis review on various safety-related valves. The engineers determined that eleven valves did not meet new criteria established in Generic Letter 89-10. Problems identified included inadequate spring packs, gear ratios, torque settings, and motors. All eleven valves were modified to meet Generic Letter 89-10 criteria.
2861991007 | Indian Point 3 | 05/10/1991 | 06/13/1991 | ML09344135 | <strong>Inoperability Of Reactor Protection System Train A</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1991, with the reactor operating at 100 percent power, instrumentation and controls technicians performing a surveillance procedure on reactor protection system train A discovered that the turbine trip - reactor trip logic in that train would not initiate a reactor trip. The technicians found that a relay associated with the P-7 permissive was not fully dropped out and they manually operated the relay to free it. They then completed the surveillance procedure. On May 12, 1991 the reactor was shut down for a planned maintenance outage. On May 13, 1991, with the reactor at cold shutdown, instrumentation and controls technicians replaced the faulty relay in reactor protection system train A. Power operation was resumed on May 23, 1991.
2861991008 | Indian Point 3 | 07/10/1991 | 09/26/1991 | ML09344136 | <strong>Cable Separation Barrier Construction Installation Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1991, with the unit operating at 100% power, it was identified that some of the electrical cable trays for redundant safeguards equipment did not conform to the separation criteria as described in the Indian Point Unit 3 Final Safety Analysis Report (FSAR). During original plant construction some cable trays and barriers were not installed as specified on the drawings. An engineering assessment to verify the installation of barriers as described on plant drawings was performed for all areas except for the vapor containment building, which will be performed during the scheduled April, 1992 refueling outage. Based on the engineering assessment, some barriers have been and are being installed.
2861991009 | Indian Point 3 | 07/11/1991 | 01/31/1992 | ML09344137 | <strong>Inadvertently Missed Backup Sample for Inoperable Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1991, he reactor at 100 percent power, a backup sample of condenser air ejector noble gas activity required while the associated radiation monitor was inoperable was missed. The required sampling frequency of twelve hours was exceeded. On October 30, 1991, during an NRC followup investigation to LER 286-91-009, the NRC resident inspector identified five overdue backup samples required by Technical Specifications. The Chemistry Department subsequently identified three additional occurrences of overdue backup samples. The evaluation of the original event was inadequate. The Operational Experience Review Group re-evaluated the events. The causes are insufficient prompting, sample status tracking and backup sample scheduling. The Chemistry Department has implemented a procedure change to ensure sample schedule consistency. <br /><br /> The Operations Department has issued a night order to senior control room operators to track backup sample status. An Administrative Procedure AP-21.9 has established a log of all limiting conditions for Operations in effect requiring compensatory action.
2861991010 | Indian Point 3 | 07/18/1991 | 01/31/1992 | ML09344137 | <strong>Missed Special Report for Out of Service Steam Line Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>During an assessment of the Indian Point 3 radiation monitoring system, with the plant at 90 percent power, plant staff discovered that the 32 steam generator steam line radiation monitor, R62A, had been out of service beyond seven days with no 14 special report submitted to the NRC as required by technical specifications. The event was caused by cognitive personnel error by licensed operations staff members who, on two occasions, did not identify the limiting condition for operations (LCOs) associated with R62A being out of service. A procedure providing direction for limiting condition for operation actions has been implemented. In addition, the site licensing group will independently review all plant occurrence reports for reportability. This event will be discussed in continuing operator training.
2861991011 | Indian Point 3 | 10/15/1991 | 11/14/1991 | ML09344137 | <strong>Safeguards Initiation Train B Inoperable Due To Failed Indicating Lamp</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1991, with the reactor operating at 100 percent power, an indicating lamp on safeguards initiation train B electrically faulted. As a result, a ten ampere control power fuse blew, rendering the automatic initiation feature of safeguards train B inoperable. The limiting condition for operation action statement of Technical specifications for safety injection and residual heat removal systems was entered and preparations for a plant shutdown were started. An identical replacement fuse was not available, so a temporary modification was written to permit use of a five ampere fuse of the same class. The temporary modification verified that the smaller fuse was adequate for the loads of a safeguards actuation and would not degrade any plant system function. A technician installed the smaller fuse before any change was made to reactor power. Technicians exchanged the fuse with the correct fuse on October 18, 1991. Technicians replaced the damaged lamp socket on October 19, 1991 while the plant was at hot shutdown due to a problem in the main generator. The plant staff will determine if a better quality indicating lamp can be procured for use in the safeguards initiation racks.
2861991012 | Indian Point 3 | 11/21/1991 | 08/25/1992 | ML09344139 | <strong>Design Bases Reconstitution Revealed Procedural Inadequacy that Could Have Resulted in Overloading Vital Buses During a LOCA</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1991, with the reactor at one hundred percent power, a vital bus load study completed as part of a design basis reconstitution effort revealed a procedural inadequacy that could potentially result in an overload of the vital buses during a loss of coolant accident with offsite power available. On January 9, 1992 a one hour report was made to the NRC regarding an unanalyzed condition that could occur while operating under degraded voltage conditions coincident with an Engineered Safeguards actuation. The root cause of the events was insufficient correlation between plant design documents and the plant emergency procedures. Emergency and operating procedures have been revised to correct the procedural inadequacy and preclude the postulated events. The validation of a computer model of the 480 volt electrical distribution system has been completed. Long term corrective actions are planned to make hardware changes to minimize the need for load management through procedures.
2871991001 | Oconee 3 | 02/13/1991 | 03/14/1991 | 9103210211 | <strong>Unplanned Reactor Protective System Actuation During Unit Cooldown and Depressurization Due to Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On 2/13/91 at 2148 hours, Unit 3 experienced an unplanned Reactor Protective System (RPS) actuation during a unit shutdown for refueling. The Reactor was subcritical with Safety Rod Group 1 (GP1) at approximately 45% withdrawn. Three out of four Reactor Coolant Pumps (RCP) were in operation resulting in a 21 to 43 psig differential pressure between the two Reactor Coolant System (RCS) loops. The operator controlled the RCS depressurization using an inappropriate RCS pressure indicator. The operator was decreasing RCS pressure in accordance with the shutdown procedure when one RPS channel tripped unexpectedly on low RCS pressure. The operator attempted to secure depressurization and insert GP1 rods, but a second RPS Channel low pressure trip occurred, initiating an RPS actuation. An investigation discovered that the pressure of the RCS Loop with 2 RCPs operating, B Loop, was 30 to 35 psig less than A Loop; a condition due specifically to operating with 3 RCPs. The pressure instrument that the operator chose did not indicate the actual pressure in the B loop. The unit shutdown continued in accordance with the shutdown procedure. The Root Cause of this event is Inappropriate Action, action taken was incorrect because action taken was not the best alternative. The operator has been counseled in regard to this event.
2871991002 | Oconee 3 | 03/08/1991 | 04/08/1991 | 9104170014 | <strong>Loss of Reactor Coolant Inventory, Due to Inadequate Procedure and Labeling Policy, Results in Loss of Decay Heat Removal Ability While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1991, at 0848 hours, Oconee Unit 3, while shut down during a refueling outage, spilled 14,000 gallons of water from the Reactor Coolant System (RCS) and Borated Water Storage Tank to the Reactor Building during a valve test. A Reactor Building Emergency Sump (RBES) isolation valve had been cycled without installing a blank flange to prevent flow to the RBES. The blank flange had been incorrectly installed on the other suction train. Reactor vessel level dropped from approximately 12 feet above the top of the core to 4 feet above the top of the core. This loss interrupted decay heat removal for 18.5 minutes. Remote reactor building radiation monitors were unavailable due to system upgrade. Operator action isolated the leak, reestablished reactor vessel level and core decay heat removal. The maximum RCS temperature in the core reached approximately 117 degrees Fahrenheit. <br /><br /> Radiation dose rates above the reactor vessel increased significantly. A local evacuation of areas in the reactor building prevented excessive radiation exposure. Two root causes of the event were identified: deficient procedure, incomplete information and management deficiency, inadequate labeling policy. Contributing causes were inappropriate actions, improper action and poor communication. Corrective actions include upgraded procedures and labeling to identify flanges and review of work activities affecting decay heat removal ability.
2871991003 | Oconee 3 | 03/19/1991 | 04/17/1991 | 9104240434 | <strong>High Pressure Injection System Crossover Flow Transmitter Inoperable Due to Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1991, with Unit 3 in a refueling outage, it was discovered that the impulse lines to the High Pressure Injection (HPI) loop 'B' Crossover Flow instrumentation had been installed incorrectly. The Crossover Flowpath consists of piping and associated valves connecting at each of the HPI pump normal discharge headers. This provides a parallel flowpath, bypassing the installed throttle valves, for protection against a single failure. A Nuclear Station Modification (NSM) had been implemented to replace the Crossover Flow instrumentation with a more accurate transmitter. During the Post Modification Testing (PMT), no flow was indicated by the flow transmitter. This led to the discovery that the impulse lines were crossed and had been since 1984. After a 1984 NSM was completed, which replaced the flow instrumentation and the impulse lines, a less than adequate PMT was performed. This instrumentation is necessary in order to monitor flow rates through the HPI crossover line. The crossed impulse lines were corrected and another functional test was performed that verified operability of the flow transmitter. This event is assigned a root cause of installation deficiency. The impulse lines to the corresponding flow instrumentation on the other two Oconee Units were inspected and verified to be installed correctly.
2871991004 | Oconee 3 | 02/08/1991 | 04/19/1991 | 9104230278 | <strong>Inappropriate Action, Failure to Follow Procedure, During a Nuclear Station Modification Implementation Results in a Degraded Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1991, during the implementation of a Nuclear Station Modification (NSM), a work crew installed 3/4 inch conduit through the firewall separating the East and West Penetration rooms for Unit 3. The breach was not sealed nor was a fire watch established as required by Technical Specifications. The crew had mistakenly assumed the wall was not a firewall and failed to follow the implementation procedure for the NSM. On March 20, 1991, at 0800 hours, a Technical Support Leader was reviewing the paperwork on the NSM due to questions by one of the crew members concerning the unsealed penetration. His review identified the wall as a fire barrier. It was determined that the breach had indeed been made to a firewall without the required compensatory actions. They then initiated action to get the breach sealed. The repairs were completed that afternoon and the fire barrier was declared operable at 1950 hours. Unit 3 was at 100% full power when the incident occurred and remained there until it was shutdown for a scheduled refueling outage on February 13, 1991. The unit reached cold shutdown on February 15, 1991, at 1235 hours. The root cause of this incident was assigned Inappropriate Action, failure of the work crew to follow procedure. A contributing cause was Management Deficiency, inadequate planning. Corrective actions included repairing the breached fire barrier, counseling of the individuals involved, and procedure revision.
2871991005 | Oconee 3 | 04/01/1991 | 05/01/1991 | 9105070336 | <strong>Design Deficiency and Procedure Deficiency Cause Spurious ATWS Systems Actuation Resulting in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1991, at 0415 hours, one channel of the Unit 3 Diverse Scram System (DSS), an Anticipated Transient Without Scram (ATWS) mitigation system, spuriously actuated and both channels were bypassed. After some troubleshooting verified the input instrument was not at fault., the Operations Unit Supervisor attempted to return both channels to service, while the unit was operating at 87% Full Power. As he did so, at 1119 hours, spurious signals actuated both channels, resulting in three groups of control rods automatically dropping into the core. Per procedure, the control room operator manually tripped the reactor in response to the dropped rods. The trip response was normal and the unit was stabilized, with no safety system actuations either required or received. Troubleshooting discovered that one channel had actuated due to Equipment Failure of a bad circuit board (contributing cause) and the second actuated due to a Design Deficiency (root cause) which generated a high signal spike in the second channel when returning the first channel to service. A second root cause of Deficient Procedure was assigned due to less than adequate steps to reset the system. Corrective actions included replacing the bad circuit board, modifying the system, and enhancing procedures.
2871991006 | Oconee 3 | 06/09/1991 | 08/15/1991 | 9108280249 | <strong>Equipment Failure While Performing Testing Results in Control Rod Group Drop and Subsequent Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1991, with unit 3 at 100 percent full power, a Control Rod Drive (CRD) system verification test required by Technical Specifications was being performed. At 1506 hours, after transferring a single control rod in Group 5 to its auxiliary power supply, the entire rod group fell into the core. Reactor power dropped to approximately 30 percent full power prior to a reactor trip three seconds later on low pressure/temperature ratio. The plant post-trip response was normal. The unit was stabilized at hot shutdown conditions. The root cause of the event was found to be equipment malfunction: a failed transfer switch allowed the normal and alternate CRD power supplies to simultaneously energize the Group 5 CRD mechanisms. The failed transfer switch was replaced. Further investigations are centered around the history of the transfer switch, methods to prevent its failure, and methods to give the operator indication when power supply transfer failures occur.
2871991007 | Oconee 3 | 07/03/1991 | 08/02/1991 | 9108120383 | <strong>Equipment Failure Closes Pneumatic Valve In Condensate Demineralizer System Causing Loss of Feedwater and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1991, at 1118 hours, while operating at 100 % Full Power, Oconee Unit 3 tripped as a result of a loss of feedwater. The loss was initiated when particles from a degraded seal clogged an Instrument Air flow path in the master valve controller for the condensate demineralizer system. This caused five parallel valves to fail closed, blocking all condensate flow. Demineralizer bypass valves could not open to compensate because an Operator had failed to return them to Automatic control. The loss of condensate flow resulted in the trip of condensate booster pumps due to low suction pressure, which then caused a trip of the main feedwater pumps, followed by the reactor trip. Emergency feedwater pumps started, but a solenoid valve failed, requiring manual operator action to control flow to one steam generator. The operators stabilized the unit at hot shutdown. Corrective actions included replacement of the defective parts and counselling of the Operator. The root cause was Equipment Failure with a contributing cause of Inappropriate Action.
2871991008 | Oconee 3 | 11/23/1991 | 12/23/1991 | 9201020381 | <strong>Excessive Reactor Coolant Leak, Reactor Trip, And Inadvertent Protective System Actuation Result From Management Deficiencies and Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1991, Oconee Unit 3 was operating at 100% Full Power (FP) when the Control Room Operators (CROs) received several alarms at 0141 hours which indicated failed instruments inside the reactor building (RB). At 0143 hours, the CROs observed symptoms of excessive Reactor Coolant System (RCS) leakage and began assessing the leak rate. At 0203 hours, they started a rapid controlled shutdown. At 0214 hours, the Shift Supervisor concluded that leakage was approximately 60 to 70 gpm, and declared an ALERT. At 0327 hours, the unit tripped from 33% FP due to a control oscillation while the CROs were attempting to secure a feedwater pump. At 0641 hours, an additional unanticipated Reactor Protective System actuation occurred due to operator error. At 1720 hours the unit reached cold shutdown and the ALERT was terminated. The leak was determined to be a failed fitting on an instrument line at the top of a steam generator. A total of approximately 87,000 gallons of RCS leakage was confined within the RB. The instrument line was replaced, and additional fittings inspected. The root causes are Management Deficiency and Equipment Failure.
2871991009 | Oconee 3 | 12/01/1991 | 01/10/1992 | 9202260066 | <strong>Technical Specification Required Containment Integrity Valve Found Mispositioned During Forced Outage Due to Unknown Cause, Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>The Unit 3 Reactor Building containment is supplied with Instrument Air (IA) through a three-inch line with normally closed isolation valves (3IA-90 and 3IA-91) on either side of containment. On December 1, 1991 at approximately 2130 hours and with Unit 3 at cold shutdown conditions, a non-licensed operator who had been sent to open 3IA-91 (inside the Reactor Building) discovered the valve in the open position. Investigation could not determine when the valve was last opened. The other isolation valve, outside the RB, was found closed. It was conservatively assumed that 3IA-91 had been open since March 22, 1991 at 1550 hours. Unit 3 operated with the Reactor Coolant System (RCS) above 200 degrees F and 300 psig, the conditions required by Technical Specifications for containment integrity, from March 22, 1991 at 1550 hours to March 24, 1991 at 1130 hours and from March 27, 1991 at 1900 hours to November 23, 1991 at 1720 hours. The root cause of this event is considered unknown, possible inappropriate action. Corrective actions included changes to the method of documentation of this and other routinely operated containment integrity valves.
2891991001 | Three Mile Island 1 | 07/07/1991 | 08/06/1991 | 9108090190 | <strong>Inoperability Of Degraded Grid Voltage Relays From Reinstallation Of A 4160V Breaker</strong><br /><i>Abstract:&nbsp;</i>At 2011 hours on July 7, 1991, following the completion of Preventive Maintenance, breaker 1SA-D2 was reinstalled. During this process, the breaker shifted causing damage to the external resistor on relays 27-1 and 27-3 which was immediately detected by the personnel who had installed the breaker. These relays are two (2) of the three (3) degraded grid voltage relays on the 1D 4160V Engineered Safeguards (ES) Bus. TMI-1 Technical Specification (Tech. Spec.) Table 3.5-1 item C.5.a. requires two channels (relays) to be operable, with a minimum degree of redundancy of one. Failing to satisfy these conditions places the unit into Tech. Spec. Limiting Condition for Operation (LCO) 3.5.1.1, which states that Tech Spec 3.0.1 applies. Tech. Spec. 3.0.1 requires that action shall be initiated, within one (1) hour, to shutdown the plant in a controlled manner. However, it was not known at the time of the event whether relays 27-1 and 27-3 were inoperable. At 2335 hours, relay 27-3 was repaired. Subsequent testing, at 2355 hours, determined that relays 27-1 and 27-3 had been inoperable at the time of the event (i.e., 2011 hours). Therefore, the required actions per Tech. Spec. 3.0.1 had applied. This event is reportable per 10 CFR 50.73 (a)(2)(i)(B). Relay 27-1 was repaired at 0005 hours on July 8, 1991. Root cause of this event is attributable to the physical configuration of the switchgear cubicle and a lack of adequate caution by personnel reinstalling the breaker. An engineering evaluation of this event is being performed to determine the appropriate changes in order to minimize the potential for future occurrence of this type event. Additionally, this event will be reviewed with appropriate Operations and Maintenance personnel.
2891991002 | Three Mile Island 1 | 07/24/1991 | 08/23/1991 | 9108260275 | <strong>Low RCS Pressure Reactor Trip Due To Control Rod Group 7 Drop</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1991 at 0520 the reactor tripped on low RCS pressure due to control rod Group 7 dropping into the reactor core as a result of personnel error in combination with an equipment failure. During the performance of a weekly Reactor Protection System surveillance procedure, an Instrument and Controls technician failed to follow the procedure which resulted in a failure to re-energize the primary power supply to the rod drive programmer assemblies. Failure of the "A" phase gate drive of the Group 7 control rods on the secondary power supply, resulted in a degradation of that power supply. During restoration of the Integrated Control System to AUTO upon completion of the surveillance, the Group 7 control rods received a command to move. The primary power supply remained in a de-energized state and the programmer cycled through the failed gate drive on the secondary group power supply. Due to the inadequate number of phases on the secondary group power supply to support rod movement, the Group 7 control rods dropped into the core. The Reactor Protection System inserted the remaining rod groups when RCS pressure decreased to 1900 psig.<br /><br /> The event was reported per 10 CFR 50.73(a)(2)(iv).
2891991003 | Three Mile Island 1 | 09/27/1991 | 10/28/1991 | 9111040168 | <strong>Reactor Trip During Turbine Valve Testing Due To Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1991 during plant shutdown for the 9R outage reactor power was stablized at 13% to support completion of turbine valve tightness testing and a special test of the turbine overspeed mechanical trip device. The turbine load limit control was turned to the minimum setting to close the turbine control valves and begin the tightness test while the stop valves remained open. The control valves closed as expected and the turbine decelerated indicating the leak tightness of the valves. After about seven minutes of deceleration, the turbine speed was 1200 rpm. In accordance with procedure, the CRO selected the "FAST" acceleration rate on the turbine control panel and turned the load limit control to maximum setting. The turbine control valves immediately started opening rapidly and OTSG pressure began dropping rapidly. Approximately ten seconds later at 18:37, the turbine tripped on overspeed. Subsequently, main feedwater was isolated to both OTSGs due to low OTSG pressure and both Emergency Feedwater Trains were auto initiated due to the low OTSG levels. The reactor tripped at 18:38 on high pressure. Normal feedwater flow to the OTSG's was re-established and post trip response was considered normal. <br /><br /> The NRC was notified in accordance with 10 CFR 50.72(b)(2)(ii).
2891991004 | Three Mile Island 1 | 10/08/1991 | 02/26/1992 | 9203020310 | <strong>Movement Of Irradiated Fuel Assembly Without Containment Isolation Due To Personnel Errors And Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1991, TMI-1 was in refueling shutdown. Licensed operators were performing 1303-11.4, "Refueling Systems Interlocks" test of the Main Fuel Bridge hoist. This test is normally performed in conjunction with 1505-1, "Fuel and Control Component Shuffles." Section 6.3.3.1, of 1303-11.4 requires fuel movement; however, it also requires, by reference, that no movement of fuel take place until the prerequisites of 1505-1 were complete. In this event, the Bridge Crew did not adequately prepare for the evolution about to take place and moved fuel to test the hoist interlocks without having verified containment isolation. All of the 1505-1 prerequisites for containment isolation were completed, except for the open Reactor Building personnel and emergency airlock doors NH/AL!. Technical Specification 3.8.6 requires that at least one door in each airlock be closed when moving irradiated fuel in the Reactor Building. This event was caused by: personnel error, due to a lack of understanding that the test involved fuel movement; and, procedural inadequacy, because 1303-11.4 did not clearly caution the operators that containment isolation was required prior to test of the interlocks. The causes of the event were reviewed with all fuel handling personnel prior to the commencement of the fuel shuffle. 1303-11.4 was revised to strengthen the procedure, provide prerequisites, and add warnings to prevent recurrence of this event. <br /><br /> This event is reportable per 10 CFR 50.73(a)(2)(i)(B).
2891991005 | Three Mile Island 1 | 11/01/1991 | 11/27/1991 | 9112040015 | <strong>Inadvertent ESAS Actuation Channel "A" Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1991, at 11:56 p.m. TMI Unit 1 was in a Refueling Shutdown condition. The "C" inverter was being returned to service after preventive maintenance was completed. Vital Bus "C" (VBC) was being powered from Transformer Regulated Bus "B" (TRB) while the "C" inverter was out of service. ESAS trains "A" and "B" were both bypassed. <br /><br /> Utilizing Enclosure V of procedure 1107-2 requires that vital bus "C" be de-energized. This causes Channel 3 of "A" & "B" ESAS to de-energize, putting each train in a one out of two actuation logic. Upon re-energizing VBC from the "C" inverter, ESAS Channel 3 "A" & "B" must be bypassed to clear all ESAS channels putting the system back in a fully bypassed condition. The Shift Supervisor directing the bypass of Channel 3 "A" and "B" ESAS observed the bypass of train "B" and then witnessed the enabling of Channel 1 of the "A" ESAS train which actuated the system. Channel 3 and Channel 1 were quickly bypassed and the affected components were returned to their desired positions. <br /><br /> The root cause of the event was personnel error. The CRO mistakenly pushed the wrong button. The event was reviewed with the individual involved by addressing the need to be more aware of his actions. <br /><br /> The event was reported per 10 CFR 50.72 II(b)(2)(ii).
2891991006 | Three Mile Island 1 | 11/04/1991 | 12/04/1991 | 9112100260 | <strong>Discovery of Increased Potential for Post LOCA Boron Precipitation Due to an Error in the NSSS Vendor's Licensing Basis Analysis</strong><br /><i>Abstract:&nbsp;</i>Discovery of Increased Potential for Post LOCA Boron Precipitation Due to an Error in the NSSS Vendor's Licensing Basis Analysis <br /><br /> TMI-1 was shutdown for refueling. At approximately 5:45 pm on November 4, 1991 GPU Nuclear was informed by the NSSS vendor that an updated preliminary calculation does not support the previous conclusions attributed to BAW 10103A Rev. 3 regarding boron concentration during the long term cooling period following a large break Loss of Coolant Accident (LOCA). Based on the revised analysis, the vendor concluded that the auxiliary pressurizer spray mode of recirculation for long term cooling may not provide sufficient flow and that the time allowed to initiate a long term cooling mode would be significantly less than that previously relied upon for operator action. This deficiency was reported at approximately 6:35 pm on November 4, 1991 in accordance with 10 CFR 50.72(b)(2)(i). Prior to restart of the unit, GPU Nuclear performed calculations and prepared a report which justifies operation at full power. Procedures were revised to reflect the conservative time proposed by BWNS as that required for actuation of boron recirculation and to identify the drop line method as the preferred mode of long term recirculation. GPU Nuclear's report concludes that there are two active methods (DHR System recirculation and auxiliary pressurizer spray) and a passive method (clearance gap flow) available to mitigate boron precipitation. Calculations used to support conclusions of the GPU Nuclear report will be confirmed.
2891991007 | Three Mile Island 1 | 11/13/1991 | 12/13/1991 | 9112190194 | <strong>Inadvertent EFW Actuation During Plant Heatup Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Inadvertent EFW Actuation During Plant Heatup Due to Personnel Error <br /><br /> TMI-1 was heating up on November 13, 1991 following the 9R Refueling Outage. A Surveillance Procedure "HSPS-EFW Auto Initiation" had been conducted to demonstrate operability of the EFW auto-initiation channels. The surveillance requires at least one main feedwater pump not be in the tripped condition. Heat Sink Protection System (HSPS) defeat/enable switches were left in "Enable" by procedure at the completion of the test. Later, when placing the main feedwater pump in operation from the reset condition, it was intentionally tripped per procedure to verify stop valve closure. The feedwater pump trip caused the HSPS to initiate an automatic start of the EFW system. The HSPS performed as designed. Both motor-driven EFW pumps started. The steam-driven EFW pump did not start because the steam supply valves were tagged out for maintenance. EFW was not supplied to the OTSGs because the levels were adequate. The surveillance was performed under plant conditions different from those for which the procedure was specifically written. The root cause of the event was personnel error. An evaluation should have been made to determine if the final status of equipment under test was appropriate for existing plant conditions. The event will be reviewed by all Shift Foremen, Shift Supervisors and Operations Engineers.
2891991008 | Three Mile Island 1 | 12/23/1991 | 01/29/1993 | 9302100045 | <strong>Missed Technical Specification Surveillance Sample For Core Flood Tank Boron Concentration</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1991, TMI-1 was operating at 100% power. A Chemistry Group Supervisor discovered a misfiled surveillance notification form which specified that the core flood tank monthly boron sample was two days beyond its late date. This event is reported as a voluntary LER in accordance with a TMI-1 policy issued January 14, 1993. <br /><br /> The root cause was a failure of the Chemistry Group Supervisor to recognize that the surveillance was outstanding. The Chemistry Department promptly obtained and analyzed the core flood tank samples and verified that the boron concentration remained within the specified limits. Additionally, Chemistry supervision has revised their practice to include a redundant means of checking surveillance performance status.
2931991001 | Pilgrim | 01/25/1991 | 02/25/1991 | 9103010183 | <strong>Automatic Closing of the Primary Containment System Group 5 Isolation Valves During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1991 at 0956 hours and at 1407 hours, an automatic Primary Containment Isolation Control System (PCIS) Group 5 actuation occurred during surveillance testing. The actuations resulted in the automatic closing of the Reactor Core Isolation Cooling System (RCICS) turbine steam supply isolation valves. The RCICS was declared inoperable and a 7 day Technical Specification Limiting Condition for Operation (LCO) began. <br /><br /> The actuations were caused by a RCICS turbine steam supply line high flow condition. The high steam flow condition occurred due to a failed transistor in the system's turbine speed control electric governor (EG-M) which was manufactured by the Woodward Governor Company (part number 8720-849). An exact cause of the transistor failure could not be identified. However, the signal cable connecting the EG-M to the turbine control valve hydraulic actuator (EG-R) was found to be degraded. This degradation could have led to the transistor failure. The cable was supplied by the Woodward Governor Company (part number 232007). The transistor and the cable were replaced. The RCICS turbine speed control system was subsequently calibrated. The RCICS was satisfactorily tested and the 7 day LCO was terminated on January 29, 1991 at 2139 hours. <br /><br /> This event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. This report is submitted in accordance with 10 CFR 50.73 subparts (a)(2)(iv) and (a)(2)(v)(D), and this event posed no threat to the public health and safety.
2931991002 | Pilgrim | 02/11/1991 | 03/12/1991 | 9103190232 | <strong>One Salt Service Water System Pump Not Surveillance Tested In Accordance With Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1991 it was determined that one of the five Salt Service Water System (SSWS) pumps had not been surveillance tested once per three months as specified by Technical Specification 4.5.B.1.b. Specifically, the pump had not been surveillance tested during the period December 13, 1990 to January 17, 1991. The pump was surveillance tested on January 17, 1991 with satisfactory as-found results.<br /><br /> The cause was an error (inappropriate instructions) in the procedure that is used when a system or component is inoperable. The error resulted in signing the Master Surveillance Tracking Program (MSTP) on October 17, 1990 for an inoperable component test even though the pump was not tested. The pump was not tested because the other four SSWS pumps were tested and were operable. <br /><br /> Corrective action taken included a review of the dates entered in the MSTP for testing performed for inoperable equipment testing or routine surveillance testing. The procedure was changed to preclude recurrence. The MSTP was corrected to reflect when the routine surveillance testing was performed. <br /><br /> The discovery occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was approximately 1030 psig with the RV water temperature at 548 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) and the condition posed no threat to the public health and safety.
2931991003 | Pilgrim | 03/07/1991 | 04/08/1991 | 9104150261 | <strong>High Pressure Coolant Injection System Made Inoperable Per Technical Specifications Due to Reactor Pressure Transmitter Replacement</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1991 at 1315 hours, the High Pressure Coolant Injection (HPCI) System was made inoperable and a seven day Limiting Condition for Operation began in accordance with Technical Specification (TS) 3.5.C.2. The system was made inoperable because the two HPCI turbine steam exhaust vacuum breaker containment isolation valves were closed. The valves were closed because the operability of the circuitry that controls the valves was questioned due to the removal from service for replacement of one of four reactor pressure transmitters that function to provide an isolation signal to the valves. Because the operability of the circuitry for the isolation valves was questioned, a utility licensed operator decision was made to close the valves in accordance with TS 3.7.A.2.b. Because the valves were closed, the HPCI System was declared and made inoperable. <br /><br /> The cause for the removal from service of the transmitter was a gradual loss of fill-oil in the transmitter's sensing module. The transmitter was replaced and the HPCI System was returned to service on March 7, 1991 at approximately 1516 hours. The transmitter was manufactured by Rosemount Incorporated, model number 1153GB9RCN0012, serial number 412894, and was originally put into service in May 1987. The Reactor Core Isolation Cooling System was operable. This event occurred during power operation while at 25 percent reactor power. The reactor mode selector switch was in the RUN position. The reactor vessel (RV) pressure was 965 psig with the RV water temperature at approximately 540 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and this event posed no threat to the public health and safety.
2931991004 | Pilgrim | 03/19/1991 | 04/12/1991 | 9104230002 | <strong>Reactor Core Isolation Cooling System Made Inoperable Per Technical Specifications Due To An Inoperable Area Temperature Switch</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1991 at 2345 hours, the Reactor Core Isolation Cooling (RCIC) System was made inoperable and a seven day Technical Specification Limiting Condition for Operation (LCO) began. The system was made inoperable due to an area temperature switch terminal (Weidmuller SA K6N) being stripped during a quarterly functional test and calibration. <br /><br /> The cause of the stripped terminal was repeated torquing of the screws. The temperature switches are replaced quarterly with a calibrated spare. The temperature switch leads are disconnected from their terminal during this process. This repeated torquing weakened the terminal. <br /><br /> The broken terminal was replaced with an installed spare terminal from the same terminal block. The broken terminal was inserted into the spare terminal's space and a Maintenance Request was written to replace the broken terminal. Long term corrective action includes evaluating the feasibility of changing the circuitry to make it more suitable for frequent calibration. Following terminal replacement, the Channel 'A' portion of the logic circuitry was successfully tested. RCIC was declared operable and the seven day LCO was terminated on March 20, 1991 at 0450 hours. <br /><br /> This condition occurred during power operation at 100 percent reactor power. The reactor mode switch was in the RUN position. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and this condition posed no threat to the public health and safety.
2931991005 | Pilgrim | 03/25/1991 | 08/16/1991 | 9108230298 | <strong>Loss of AC Power to 'B' Trains of Safety Systems due to Diesel Generator 'B' Voltage Regulator Failure During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1991 at 0610 hours, the Emergency Diesel Generator (EDG) 'B' became inoperable, a loss of AC power to Train 'B' components of safety systems, and actuations of portions of the Primary Containment and Secondary Containment Isolation Control Systems occurred during a Technical Specification required surveillance test of the EDG 'B'. <br /><br /> The cause for the event was a failure of the automatic voltage regulator (AVR) of the EDG 'B' that was fully loaded on its safety bus at the time of the event. The voltage regulator was manufactured by the Basler Electric Company, model number SVR01A05B2B1B, serial number 9047500105. The affected safety system components were re-energized and returned to normal service by March 25, 1991 at 2100 hours. The EDG 'B' voltage regulator was replaced and the EDG 'B' was surveillance tested with satisfactory results. The surveillance was completed on March 28, 1991 at approximately 0915 hours. The failure of the AVR was caused by the failure of the AVR magnetic amplifier due to low insulation resistance. A manufacturer search of its production failure and returned materials data indicated the failure was an isolated occurrence. <br /><br /> This event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1035 psig with the RV water temperature at 548 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73 subparts (a)(2)(iv) and (a)(2)(v)(D), and this event posed no threat to the public health and safety.
2931991006 | Pilgrim | 03/26/1991 | 04/24/1991 | 9104290246 | <strong>High Pressure Coolant Injection and Reactor Core Isolation Cooling Systems Become Inoperable Due to Tripped Inverters</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991 when starting the 'B' Reactor Recirculation Pump, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) System inverters tripped on high voltage. The HPCI and RCIC Systems were inoperable for nine minutes. The cause of the inverter trips was a voltage fluctuation that occurred during pump start. The load required by the pump start caused the battery charger that supplies DC voltage to the inverters to overcompensate resulting in a voltage surge. The trip setpoint of the inverters was exceeded during this surge.<br /><br /> Corrective action was taken to reset the inverters. An engineering evaluation has been initiated to investigate enhancements to preclude the inverters from tripping as a result of large pump starts. Interim measures will include an administrative change to caution operations personnel that the potential for inverter trips exists. The inverters were manufactured by Topaz Electronics, Model No. 125-GW-125 (60). <br /><br /> The event occurred at power operation with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was approximately 956 psig and the RV water temperature was 542 degrees Fahrenheit. The reactor power level was 30 percent. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and the event posed no threat to the public health and safety.
2931991007 | Pilgrim | 04/29/1991 | 05/29/1991 | 9106040400 | <strong>Completion of a Shutdown Due to Drywell Floor Sump Leakage Rate And Subsequent Scram Signal While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1991 at 1912 hours, a Technical Specification required shutdown was completed. A voluntary shutdown had been initiated at 1415 hours because of fluctuating recirculation pump seal pressures. The required shutdown was initiated at 1650 hours as a result of Drywell sump monitoring data. An Unusual Event (UE) was declared at 1650 hours because the Drywell floor sump (unidentified leakage) leakage rate was greater than 5 gpm. The shutdown was required by Technical Specification 3.6.C.3. After the shutdown, an unplanned Reactor Protection System (RPS) scram signal occurred at 1935 hours when the Scram Discharge Volume (SDV) high water level scram bypass switch was moved to the NORMAL position while a sensed SDV high water level condition existed. The RPS was reset at 1937 hours. The UE was terminated on April 30, 1991 at 0025 hours. The cause for the shutdown was the end of useful life of the Recirculation System Loop 'B' pump cartridge type dual mechanical seal that was manufactured by Byron Jackson Pumps, Inc. The Recirculation System Loops 'A' and 'B' pump seals were previously scheduled for replacement and will be replaced prior to startup from the current refueling outage. The cause for the scram signal was utility licensed operator error. The responsible operator was counseled. The approved procedure for resetting the RPS was strengthened. The required shutdown was initiated when the reactor mode selector switch was in the RUN position, the RV pressure was 958 psig with the RV water temperature at 539 degrees Fahrenheit, and the reactor power level was 48 percent. This report is submitted in accordance with 10 CFR 50.73 subparts (a)(2)(i)(A) and (a)(2)(iv), and these events posed no threat to the public health and safety.
2931991008 | Pilgrim | 04/30/1991 | 02/24/1992 | 9202280048 | <strong>Three Automatic Group 1 isolations Due to False High Reactor Water Level Signals While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1991, three automatic Primary Containment Isolation Control System (PCIS) Group 1 isolations occurred while shutdown at 0116 hours, 0933 hours, and 1037 hours, respectively, due to a false high Reactor Vessel (RV) water level signal. The actuations resulted in the automatic closing of the related Primary Containment System isolation valves. <br /><br /> The Group 1 isolations were initiated by the reactor water level trip units downstream of reference leg condensing chamber 12B. The false high RV water level signals were primarily due to undersized RV water level head equalizing lines. Contributing causes included sensing line hanger interference, air entrapment and marginal sensing line slope. Corrective actions taken include: increasing the head equalizing line size from one inch to two inch, eliminating the hanger interference, backfilling sensing lines at a higher flush velocity and improving sensing line slope.<br /><br /> These events occurred when in the hot shutdown mode of operation with the reactor mode selector switch in the SHUTDOWN position. The reactor power level was zero percent. The RV pressures and RV water temperatures for the three events were as follows: first event, 60 psig and 308 degrees Fahrenheit; second event, 12 psig and 248 degrees Fahrenheit; third event, 3 psig and 168 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and these events posed no threat to the health and safety of the public.
2931991009 | Pilgrim | 05/18/1991 | 06/14/1991 | 9106200165 | <strong>Fire Barrier Found Breached in Intake Structure</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1991 at 1000 hours during a refueling outage, the east wall of the "B" train Salt Service Water (SSW) pump room in the Intake Structure was found to be breached. The breach consisted of a 4 inch drain check valve that was found in the open position. The wall is a Technical Specification Appendix R fire barrier that separates the safety related SSW pump room from the non-safety related "A" Circulating Water pump enclosure. <br /><br /> The barrier was breached when an air hose was run through the drain check valve penetration in order to support an ongoing work activity. The personnel performing the work did not recognize the wall was a Technical Specification barrier. Corrective actions taken include labeling the barrier and penetration to identify they are Technical Specification components and requiring the Nuclear Watch Engineer be notified prior to altering the barrier. Long term corrective action being considered includes eliminating the penetration and grouting the opening. <br /><br /> The condition was identified with the reactor mode selector switch in the REFUEL position. The reactor power level was 0 percent. The Reactor Vessel (RV) water temperature was 84 degrees Fahrenheit and the RV pressure was 0 psig. The report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) and the condition posed no threat to the public health and safety.
2931991010 | Pilgrim | 05/27/1991 | 06/26/1991 | 9107030307 | <strong>Inadvertent Secondary Containment System Isolation While Backing Out of Surveillance Testing Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1991 at 0034 hours, an inadvertent actuation of the Channel "A" Reactor Building Isolation Control System (RBIS) occurred while backing out of a surveillance test. The actuation resulted in the automatic closing of the Train "A" Secondary Containment System/Reactor Building ventilation dampers, and the automatic start of the Standby Gas Treatment System Train "A" fan. The RBIS circuitry was reset and the affected components were returned to normal service.<br /><br /> The cause of the actuation was a momentary loss of power to the "A" 125 VDC battery bus. The loss of power resulted from an improper sequence used to restore the 125 VDC system to normal alignment. This occurred while backing out of a battery capacity test prior to the completion of the test. Specifically, the "A" battery charger was connected to the "A" bus prior to connecting the 125 VDC battery to the bus. This caused erratic battery charger operation and resulted in the momentary loss of power. Corrective actions planned include adding a caution to the battery capacity test procedure alerting personnel not to connect the battery charger to its associated bus without the associated battery connected to the bus. <br /><br /> The actuation occurred during a refueling outage. The reactor mode selector switch was in the REFUEL position with the Reactor Vessel (RV) completely defueled and no fuel movement in progress. The RV/Refuel Cavity was flooded with the RV water temperature at 98 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
2931991011 | Pilgrim | 06/04/1991 | 07/05/1991 | 9107160263 | <strong>Inadvertent Primary Containment and Secondary Containment Isolation Signal During Surveillance Testing While Shutdown For Refueling</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1991 at 0056 hours, an inadvertent actuation of the Primary Containment Isolation Control System and Reactor Building Isolation Control System occurred during a surveillance test. The actuation resulted in isolations of the Primary and Secondary Containment Systems. The event occurred because of concurrent Reactor Protection System (RPS) Channel 'A' and 'B' low water level trip signals.<br /><br /> The root cause for the event was utility licensed operator error. The shift Nuclear Watch Engineer (senior licensed operator) did not ensure a sufficiently detailed review of plant conditions had been performed prior to authorizing the performance of the surveillance test. A Channel 'A' trip signal existed at the time of the event because a normally energized Channel 'A' relay had previously been tagged and de-energized for a maintenance activity. The surveillance test resulted in the expected trip of an electrical protection assembly that is part of the power supply for the Channel 'B' circuitry. The responsible Watch Engineer was counseled regarding the importance of ensuring plant conditions have been thoroughly reviewed prior to authorizing a surveillance test. <br /><br /> This event occurred during a refueling outage with the reactor mode selector switch in the REFUEL position. The Reactor Vessel (RV) was completely defueled and no fuel movement was in progress. The Control Rod Drive System was removed from service for maintenance. The RV/Refuel Cavity was flooded with the water temperature at 85 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
2931991012 | Pilgrim | 06/07/1991 | 07/05/1991 | 9107160242 | <strong>Automatic Start of Diesel Generator During Surveillance Testing Due to Non-Licensed Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1991 at 1745 hours, an inadvertent automatic start of the Emergency Diesel Generator (EDG) 'A' occurred during a scheduled surveillance test while shutdown for a refueling outage. The EDG did not provide power to its related bus because the EDG feeder breaker to the bus was racked down at that part of the test. The start of the EDG was not the result of a degraded voltage or undervoltage condition. <br /><br /> The cause for the event was utility non-licensed electrical maintenance engineer error. A lead, lifted as part of the test, was relanded prior to racking up a feeder breaker to the bus. This inadvertent action was contrary to the sequence of steps identified in the approved surveillance test procedure. The surveillance was completed without further incident. The engineer was counseled regarding the performance of procedure steps in the order identified. Additional corrective action being considered includes a change to the surveillance procedure for the EDG 'A' and 'B'. The focus of the change is to position the EDG 'A' (or 'B') emergency switch to preclude a start during the restoration portion of the surveillance procedure and to reposition the switch at the end of the surveillance.<br /><br /> The event occurred during a refueling outage with the reactor mode selection switch in the REFUEL position. The Reactor Vessel (RV) was completely defueled and no fuel movement was in progress. The RV/Refuel Cavity was flooded with the water temperature at 82 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
2931991013 | Pilgrim | 06/13/1991 | 07/11/1991 | 9107170257 | <strong>Local Leak Rate Test Results of Feedwater Check Valves in Excess of Limits</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage No. 8 between June 8 and June 13, 1991, 10 CFR 50 Appendix 'J' local leak rate testing of the 18 inch Anchor Darling, tilting disc, feedwater check valves was conducted. The as-found test results showed leakage for the four feedwater check valves to be in excess of the limits established in Pilgrim Nuclear Power Station Technical Specifications. <br /><br /> The Local Leak Rate Test Failure Analysis Team investigated root cause and recommended corrective actions. Results of the investigation indicate damaged soft seats and improper disc alignment caused the failures. Corrective action taken includes rebuilding the valves to the latest factory tolerances. This involved installing new discs using a new hinge pin design, replacing the soft seat material and rechecking alignment to ensure proper tolerances. The four valves were retested with satisfactory results between July 2 and July 4, 1991. <br /><br /> The leakages were identified during a refueling outage with the reactor mode selector switch in the REFUEL position. The Reactor Vessel (RV) was completely defueled with no fuel movement in progress. The RV/Refuel Cavity was flooded and the RV water temperature was approximately 82 degrees Fahrenheit. This event posed no threat to the health and safety of the public.
2931991014 | Pilgrim | 06/27/1991 | 07/16/1992 | 9207210320 | <strong>Setpoint of Dresser Safety Valve and Target Rock Relief Valves Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1991 it was determined that the initial as-found popping pressures one Dresser main steam safety valve and the pilot valves for two Target Rock two-stage main steam relief valves were not within Technical Specification 3.6.D.1 limits including tolerance. The valves had been sent to Wyle Laboratories during the midcycle outage in March 1990. Test results were received from Wyle Laboratories on July 5, 1990; however, the appropriate corrective action documents were not written until June 1991. The set pressure for the pilot valves is 1115 psig plus or minus 11 psi. The initial popping pressures of the pilot valves S/N 1049 and 1054 were 1144 and 1129 psig, respectively. The set pressure for the safety valve is 1240 psig plus or minus 13 psi. The popping pressure of the safety valve S/N BK6262 was 1271 psig. <br /><br /> During refueling outage RFO #8, additional valves were sent to Wyle Laboratories or testing and found to be outside allowable tolerances. The primary cause of the of tolerance popping pressures was determined to be setpoint drift. Corrective action taken included refurbishing, retesting and certifying the valves to be within specification. The relief valves were manufactured by Target Rock Corp. (model no. 7567F) and the valve was manufactured by Dresser Industries (model no. 3777 QA-RT-21). <br /><br /> The conditions were discovered during a refueling outage with the reactor mode selector switch in the REFUEL position. The Reactor Vessel water temperature was 84 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) and the initial popping pressures posed no threat to the public health and safety.
2931991015 | Pilgrim | 06/28/1991 | 08/10/1991 | 9108190070 | <strong>Technical Specification Fire Barrier Found Breached in Intake Structure</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1991 at 1506 hours during a refueling outage, the north wall of the "A" train Salt Service Water (SSW) pump room in the Intake Structure was found breached. The breach consisted of a broken two inch conduit fitting located where the conduit penetrates the north wall outside the "A" train SSW pump room. The wall is a Technical Specification Appendix R fire barrier that separates the SSW pump room from the Service Water pump filter room. This condition was determined to be reportable on July 11, 1991. <br /><br /> The broken conduit fitting was a result of corrosion due to exposure to a marine environment. The conduit was identified as being corroded in July 1989. A fire barrier penetration walkdown conducted in December 1989 found the barrier intact. Subsequent to that inspection it is postulated that personnel used the conduit as a foot/hand hold that eventually broke the conduit fitting. A continuous firewatch was immediately established when the breach was identified. A fire seal was installed on July 25, 1991 and the fire watch was discontinued. Other actions planned include: repairing the conduit fitting; performing a thorough walkdown of the Intake Structure; and reviewing walkdown procedures and training to identify improvements.<br /><br /> This condition was identified with the reactor mode selector switch in the REFUEL position. The Reactor Vessel (RV) water temperature was 83 degrees Fahrenheit and the RV pressure was 0 psig. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). This condition posed no threat to the public health and safety.
2931991016 | Pilgrim | 07/18/1991 | 08/17/1991 | 9108230284 | <strong>Settings of Degraded Voltage Relays Found Out of Tolerance During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1991 it was determined that the as-found settings of the degraded voltage relays for one of the two safety-related 4160 VAC buses did not meet Technical Specifications during a 1990 surveillance test. The settings were adjusted to within the setpoint range during the surveillance using equipment having the appropriate accuracy. The as-found settings of the degraded voltage relays for the other safety-related bus were within the setpoint range including tolerance. <br /><br /> The direct cause of the as-found out of tolerance settings is believed to be due to differences in the accuracy of the measuring and test equipment used to calibrate the relays in 1988 and 1990. The root cause was utility non-licensed Electrical Maintenance Engineer error in that the measuring and test equipment used for the 1988 calibration was not as accurate as the relays being calibrated. The cause of not previously reporting the as-found out of tolerance settings was Electrical Maintenance Supervisor error. <br /><br /> Corrective action taken included counseling the responsible engineer and supervisor. Corrective action planned includes incorporating this report into the Electrical Maintenance training program.<br /><br /> The surveillance procedure and other surveillance procedures will be reviewed for improvement to preclude the likelihood of recurrence. The surveillance test was performed while shutdown with the reactor mode selector switch in the SHUTDOWN position. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). The as-found out of tolerance settings posed no threat to the public health and safety.
2931991017 | Pilgrim | 07/20/1991 | 08/16/1991 | 9108270166 | <strong>Automatic Cl sing of Reactor Water Cleanup and Reactor Core Isolation Cooling System Isolation Valves During Hydrostatic Test</strong><br /><i>Abstract:&nbsp;</i>On July 20 and 21, 1991 three automatic actuations of portions of the Primary Containment Isolation Control System (PCIS) occurred. Two of the actuations involved the Reactor Water Cleanup (RWCU) System and one involved the Reactor Core Isolation Cooling (RCIC) System. The actuations resulted in the automatic closure of isolation valves in the RWCU and RCIC systems. The PCIS was not required to be operable at the time of the actuations, which occurred prior to and during hydrostatic testing of the reactor vessel. <br /><br /> The cause of the actuations was air in the sensing lines of flow sensors that are part of the RWCU and RCIC logic circuitry. The air was trapped in the sensing lines following previous maintenance activities during the refueling outage. Backfilling of the RWCU and RCIC sensing lines was attempted but did not successfully purge the lines of air. Corrective action planned includes developing specific procedures to be used for backfilling the RCIC and RWCU instrumentation sensing lines when air could be introduced into the systems. Training of appropriate Instrumentation and Controls personnel will be conducted to ensure backfilling techniques are understood. <br /><br /> The actuations occurred during a refueling outage while in the cold shutdown condition with the reactor mode selector switch in the SHUTDOWN position. The reactor vessel was refueled with the head installed. The actuations posed no threat to the public health and safety. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv).
2931991018 | Pilgrim | 07/10/1991 | 09/10/1991 | 9109170209 | <strong>Setpoints of Degraded Voltage Relays Too Low During Low Probability Degraded Voltage Conditions</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1991 it was determined that under certain extremely low probability conditions, sufficient voltage may not be supplied to selected electrical loads at the 480 VAC and 120 VAC levels with the existing degraded voltage relay setpoints. The condition was identified as a result of a Nuclear Engineering Department degraded voltage analysis and during reviews conducted while preparing for an Electrical Distribution System Functional Inspection. <br /><br /> In 1988, a design review showed the sepoints of the degraded voltage relays were too low. A scenario considered to be the worst case for degraded voltage was analyzed and corrective action was taken. Subsequent analysis performed in 1991 proved the worst case scenario considered in 1988 to be incorrect.<br /><br /> Compensatory measures were implemented prior to startup. Essentially, the Emergency Diesel Generators will be started and loaded onto the respective 4160 VAC bus if 345 KV switchyard voltages could decrease to certain levels as a result of a Pilgrim Station trip. The compensatory measures will remain in effect until ongoing analysis is completed and planned modifications are implemented. The focus of the modifications is to replace applicable control power transformers, power cabling, and 480/120 VAC transformers. <br /><br /> The potential for this condition was identified during a refueling outage. The reactor mode selector switch was in the SHUTDOWN position. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). This condition poses no threat to the public health and safety.
2931991019 | Pilgrim | 05/25/1991 | 09/11/1991 | 9109170085 | <strong>General Electric Type AK-2A-50 Circuit Breaker Did Not Close During Bus Transfer</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1991 at 0215 hours, a 480 VAC circuit breaker that is part of a safety-related bus transfer scheme did not close during a planned bus transfer. The bus became de-energized for 10 minutes. At the time of the event, the Reactor Vessel was completely defueled and no fuel movement was in progress. The components and systems powered by the bus were not required to be operable. The breaker was manufactured by the General Electric Company, type AK-2A-50, serial number 0224A1126-310-AE.<br /><br /> The cause was interference between the breaker trip latch roller assembly and clevis pin. The interference was similar to that documented in Service Advice Letter (SAL) 306.0, issued on May 1, 1991. A 10 CFR Part 21 report regarding the breaker was submitted to the NRC on July 26, 1991. The breaker was repaired by General Electric personnel. The repair included machining the trip latch roller assembly and clevis pin to establish the clearance described in SAL 306.0. The other type AK-2A-50 breakers installed in safety-related applications were tested and inspected. Although none experienced a failure to close, it was possible to manipulate the operating mechanism of two of these breakers to create an interference. The trip latch roller assembly of those breakers was replaced as recommended in the SAL. The type AK-2A-50 circuit breakers installed in nonsafety-related applications were visually inspected and were evaluated as satisfactory for use in their applications. This event occurred while shutdown during a refueling outage. This report is submitted in accordance with 10 CFR 50.73(a)(2)(vii)(D). This event posed no threat to the public health and safety.
2931991020 | Pilgrim | 08/15/1991 | 09/13/1991 | 9109190283 | <strong>Reactor Core Isolation Cooling System Inoperable Due to Failure of Speed Control Hydraulic Actuator</strong><br /><i>Abstract:&nbsp;</i>On August 15 1991 at 0038 hours, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable and a seven day Technical Specification Limiting Condition for Operation (LCO) was entered. The system was declared inoperable when the RCIC turbine was manually tripped during a surveillance test. <br /><br /> The turbine was manually tripped due to turbine speed oscillations that occurred after several minutes of steady operation. The cause of the oscillations is believed to be a mechanical failure of the speed control system hydraulic actuator (EG-R). The EG-R was manufactured by Woodward Governor Company, part number A9903-026. The actuator was removed from service and will be sent to the manufacturer for examination. A new replacement EG-R was installed and calibrated. The RCIC System was retested with satisfactory results and the seven day LCO was terminated on August 16, 1991 at 0409 hours. While the RCIC System was inoperable, the High Pressure Coolant Injection System was verified to be operable as required by Technical Specifications. <br /><br /> The event occurred during startup from refueling outage number 8. The reactor mode switch was in the STARTUP position. The reactor power level was approximately 5 percent. The Reactor Vessel (RV) pressure was 928 psig and the RV temperature was approximately 521 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D). The event posed no threat to the public health and safety.
2931991021 | Pilgrim | 10/09/1991 | 11/08/1991 | 9111180327 | <strong>Reactor Core Isolation Cooling System Declared Inoperable Due to Insufficient Battery Charger Test</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1991 at 1802 hours, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable and a seven day Limiting Condition for Operation (LCO) began at that time. The system was declared inoperable because sufficient test data was not available to demonstrate that sufficient margin to the RCIC inverter trip setpoint existed if a 125 VDC Bus 'A' voltage transient were to occur. The DC voltage transient is possible if an AC voltage transient of sufficient magnitude occurs at the input of the 125 VDC battery charger. The 125 VDC Battery 'A' and backup battery charger were in service supplying power to the RCIC inverter via 125 VDC Bus 'A' when this condition was identified. <br /><br /> The RCIC System was maintained in the normal standby mode and was not removed from service as a result of declaring the system inoperable. A written request for relief from the requirement to shut down on October 16, 1991 because of this condition was granted by the NRC on October 16, 1991. Compensatory measures were implemented as a result of this condition. The plant was shut down on October 30, 1991 for reasons unrelated to the RCIC System LCO. Corrective action planned consists of testing and/or the implementation of modifications to preclude unacceptable voltage transients from occurring on the 125 VDC Bus 'A'.<br /><br /> This condition was identified during power operation with the reactor mode selector switch in the RUN position. The reactor power level was 100 percent. The Reactor Vessel (RV) pressure was 1028 psig with the RV water temperature at 548 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and this condition posed no threat to the public health and safety.
2931991022 | Pilgrim | 10/24/1991 | 10/31/1995 | 9511060235 | <strong>Settings of Reactor Water Cleanup High Flow Sensors Found Out of Tolerance During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1991, during a routine calibration, both Reactor Water Cleanup (RWCU) System high flow switches were found to have trip setpoints greater than the Technical Specification limit (calculated at 16.6" of water). The trip setting necessary to meet the Technical Specification limit has since been recalculated at less than or equal to 21.4" of water. Therefore, the as found trip settings in October 24, 1991, did not result in less than the minimum number of operable instrument channels per trip system specified by Technical Specification Table 3.2.A.<br /><br /> The cause of the as-found trip settings on October 24, 1991 was setpoint drift. The switches were manufactured by I.T.T. Barton, model number 288A. The switches were recalibrated with satisfactory results on October 24, 1991. The internal microswitches were later replaced and the linkages adjusted for the two high flow switches to improve repeatability. <br /><br /> This condition was discovered during normal plant operation at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1035 psig with the RV water temperature at 550 degrees Fahrenheit. <br /><br /> This report is voluntarily submitted. The as-found trip settings posed no threat to the public health and safety or to plant operation.
2931991023 | Pilgrim | 07/28/1991 | 11/27/1991 | 9112030002 | <strong>Loose Drywell Head Bolts Discovered During An Integrated Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1991 at approximately 2300 hours, 11 of 76 Drywell head bolts were discovered to be loose during a required 10 CFR 50 Appendix J integrated leak rate test (ILRT). The test was being performed at full pressure (45 psig), near the end of a refueling outage, and after a satisfactory local leak rate test (also at 45 psig) of the Drywell head gaskets. The cause of the loose Drywell head bolts was the failure of some of the spherical type washer sets that are part of the Drywell head flange connection. The primary cause of the failed washers was the use of washers made of case hardened AISI 8620 material instead of hardened and tempered AISI 4140 material. The exact source of the washers made of the AISI 8620 material had not been determined when this report was submitted. Factors possibly contributing to the failure of some of the washers were the inverted installation of some of the washers, corrosion, and crack propagation over time. Corrective action taken included the replacement of all Drywell head bolt washers. The new washers are made of AISI 4140 material hardened and tempered to the specified hardness. A subsequent ILRT was completed with satisfactory results on August 6, 1991. Corrective actions planned include revising the procedure used to install the Drywell head to include specific detail regarding how the Drywell head washer sets are to be installed. The Drywell was manufactured by the Chicago Bridge & Iron Company. The discovery occurred while shut down with the reactor mode selector switch in the REFUEL position. The Reactor Vessel (RV) head vent valves were open and the RV water temperature was 82 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(C). The loose Drywell head bolts were determined to be reportable on October 29, 1991. The loose bolts posed no threat to the public health and safety.
2931991024 | Pilgrim | 10/30/1991 | 11/29/1991 | 9112060194 | <strong>Loss of Preferred and Secondary Offsite Power Due to Severe Coastal Storm While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1991 at 1942 hours a loss of preferred offsite 345 KV power occurred while shut down during a severe coastal storm. The loss of preferred offsite power resulted in designed responses including automatic actuations of the Reactor Protection System, Primary and Secondary Containment Isolation Control Systems, and Emergency Diesel Generators. <br /><br /> The cause of the loss of preferred offsite power was the flashover of a 345 KV switchyard insulator, and separate operation of a stuck breaker circuit. The flashover caused three switchyard air circuit breakers (ACBs) to open as designed. A fourth ACB opened about 1.4 seconds later (stuck breaker circuit) even though the related ACB opened as designed. The most probable cause of the stuck breaker circuit operation was 345 KV electrical noise coupled into the stuck breaker circuit. Corrective actions planned include the installation of a high speed recorder to monitor switchyard circuitry. A loss of the secondary source of offsite power occurred at 1953 hours and an Unusual Event was declared at 2003 hours. The cause of the loss of secondary offsite power (23 KV) was also storm related, when a tree fell onto a 23 KV line. Preferred offsite power was restored at 2142 hours and the Unusual Event was terminated at 2230 hours. The loss of preferred offsite power occurred about two and one-half hours after a shutdown with the reactor mode selector switch in the REFUEL position. The Reactor Vessel (RV) pressure was approximately 920 psig with the RV water temperature at 530 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73 subparts (a)(2)(i)(B) and (a)(2)(iv). These events posed no threat to the public health and safety.
2931991025 | Pilgrim | 10/30/1991 | 11/29/1991 | 9112060011 | <strong>Reactor Core Isolation Cooling System Became Inoperable Due to Overspeed Trip and Inverter Trip</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1991 at 1942 hours, the Reactor Core Isolation Cooling (RCIC) System turbine tripped as operators manually started the system for Reactor Vessel (RV) water level control. The trip was reset and the RCIC System was manually started. However, the RCIC inverter had tripped when the "A" Residual Heat Removal (RHR) pump was started at 1946 hours resulting in the RCIC System not reaching rated flow. The operators manually shut down the RCIC System, reset the inverter and restarted the system successfully. <br /><br /> The RCIC turbine tripped due to mechanical overspeed. The licensed operator did not open the injection valve within four (4) seconds after opening the turbine steam inlet valve. During system restoration the RCIC inverter (Topaz Electronics, Model 125-GW-125 601! tripped due to a DC voltage transient caused when the "A" RHR pump was started. The battery charger was not originally designed to maintain DC output during AC voltage transients caused by starting large AC motors. Corrective actions for the overspeed trip include changing the procedure to require valves to be opened simultaneously. A modification was completed that installed new RCIC and High Pressure Coolant Injection inverters having a higher trip setpoint and an automatic reset function. Extensive testing was performed to ensure the inverters will not trip due to DC voltage transients. The RCIC turbine trip and inverter trip occurred with the reactor mode selector switch in the REFUEL position. The RV pressure was 920 psig and the RV water temperature was 530 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D). The event posed no threat to the public health and safety.
2931991026 | Pilgrim | 10/30/1991 | 11/27/1991 | 9112030115 | <strong>Automatic Actuations of Primary Containment System Group 6 Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On October 30 and 31, 1991 two automatic actuations occurred in the Reactor Water Cleanup (RWCU) System portion of the Primary Containment Isolation Control System (PCIS). The actuations resulted in the automatic closure of isolation valves in the RWCU portion of the Primary Containment System (PCS). The first actuation occurred on October 30, 1991 at 2335 when the RWCU System was being put into service. The second actuation occurred on October 31, 1991 at 0248 hours when the position of a RWCU valve was being adjusted. This caused interruptions in the operation of the RWCU System. <br /><br /> The cause of the actuations is believed to have been momentary fluctuations in RWCU System flow. The Nuclear Engineering Department is evaluating the high flow design setpoints and the system design to enhance detection capability without unnecessary isolations. <br /><br /> The actuations occurred while shutdown with the Reactor mode Selector Switch in the SHUTDOWN position. During the first isolation, reactor pressure was about 250 psig and reactor water temperature was about 400 degrees Fahrenheit. During the second isolation, reactor pressure was about 165 psig and reactor water temperature was about 365 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and the actuations posed no threat to the health and safety of the public.
2951991001 | Zion 1, Zion 2 | 01/29/1991 | 02/28/1991 | 9103060116 | <strong>Failure to Perform Type C Leakrate Testing on 2 Penetrations</strong><br /><i>Abstract:&nbsp;</i>On 01/29/91, at 1345 hours, Zion station entered Technical Specification Limiting Condition of Operation (LCO) 3.0.3 due to the identification of two untested containment penetrations, P-76 and P-80, for both units. At 1445 hours a controlled shutdown of Unit 2 was commenced and a Generating Station Emergency Plan (GSEP) Unusual Event was declared. At this time Unit 1 was already in Mode 5, Cold Shutdown. At 1720 hours the Unit 2 ramp down was terminated as authorized by the NRC based on the initial review of a requested temporary waiver of compliance. At 2015 hours the temporary waiver of compliance was approved and the GSEP was terminated. <br /><br /> P-76 consists of the Safety Accumulator Test Line and its associated containment isolation valve SI8961. This penetration should be Type C tested and is not. <br /><br /> P-80 consists of the Emergency Core Cooling System (ECCS) relief valves and their associated tail pipes. The tail pipes of the ECCS relief valves collect into one common header which returns to the Pressurizer Relief Tank located inside the containment. Penetration P-80 has one 4" check valve for a containment isolation valve. Check Valve RC8079 is not Type C tested.
2951991002 | Zion 1, Zion 2 | 02/22/1991 | 03/25/1991 | 9103290180 | <strong>Missed Surveillances for Projected Liquid Release Calculation, Containment Charcoal Filters and E-BAR sample</strong><br /><i>Abstract:&nbsp;</i>During Nuclear Quality Programs audit of License Compliance on February 22, 1991, it was discovered that three surveillances required by the Technical Specifications (Tech. Spec.) were not performed within their required time intervals. The first surveillance was the October, 1990 Unit 1 projected liquid dose calculation required by Tech. Spec. 4.11.4.A.1. The individual performing the calculations mistakenly selected the gaseous dose projection option of the computer program instead of the liquid dose projection option. The safety significance of this event is negligible. If the doses for the month are greater than 25 percent of the objectives, then the individual is required to notify the Operational Lead Health Physicist for the follow up actions. The same data that is input for the actual release calculation for the previous month is used for the liquid dose projection for the following month. Therefore, since the past months results were less than 25 percent of the objectives, no action would have been indicated necessary by the projected calculation. To prevent recurrence, changes have been initiated to ZRP's 1901-1 and 1901-2 to require an additional management review of the Offsite Dose Calculation results. <br /><br /> The second surveillance was the Technical Staff Surveillance (TSS) 15.6.14C "Activated Carbon Filter Laboratory Analysis" for the containment charcoal filter banks (CCFB) RV032 and RV033. Technical Specification 4.17.1.E requires a carbon sample from these filter banks to be analyzed yearly, but since 1980, TSS 15.6.14C has only been requiring these samples to be taken every 18 months. The cause of this missed surveillance is inadequate Tech. Spec. Amendment post review and procedure change implementation for Amendment Numbers 56 (Unit 1) and 53 (Unit 2). A procedure change to TSS 15.6.14C was initiated to increase the frequency to once a year. The health and safety of the public was not affected because the CCFB are not engineered safeguards features.
2951991003 | Zion 1, Zion 2 | 03/01/1991 | 04/01/1991 | 9104040232 | <strong>Failure to Issue 30-day Special Report</strong><br /><i>Abstract:&nbsp;</i>As a result of OA Fire Pump being inoperable for greater than seven days during January, 1991, Technical Specification 3.21.2.B. required a Special Report to be issued to the NRC within the following 30 days. No management tracking system existed to monitor the progress of Special Reports, and subsequently, the report was not issued within the allotted time period. Corrective actions taken to prevent recurrence of this problem include developing a tracking method for Special Reports, reviewing the event with the entire Technical Staff, and including instructions in the appropriate System Engineer Notebooks for issuing a Special Report. Since no safety systems were rendered inoperable due to the failure to issue the report, there is no safety significance to this event.
2951991004 | Zion 1, Zion 2 | 03/05/1991 | 04/04/1991 | 9104090315 | <strong>Failure to Perform Containment Type C Leak Rate Testing per Technical Specification 4.10.1.A.2</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1991, at 1700 hours, CECo identified three pathways (P-76, P-77, and P-86) which had not been properly Type C tested in accordance with 10 CFR 50, Appendix J. On March 7, 1991, at 1545 hours, in completing the Zion Station local leak rate testing self-assessment program, CECo identified two additional pathways (P-23 and P-33) which had not been properly Type C tested in accordance with 10 CFR 50, Appendix J.<br /><br /> In accordance with the self-assessment criteria provided in a CECo letter of February 13, 1991, requesting an Emergency Technical Specification Amendment, Zion Station personnel notified the NRC of the deficiencies pursuant to 10 CFR 50.72. At the time of both events, Unit 2 was in Mode 1 at 100% power and Unit 1 was in Mode 5, Cold Shutdown. No mode change of the units was required since the Emergency Technical Specification Amendment allowed relief from Type C testing of the untested penetrations identified during the self-assessment.
2951991005 | Zion 1 | 04/21/1991 | 05/21/1991 | 9105290170 | <strong>111 AC Instrument Inverter Spike Causing Loss Of RHR.</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1991, at 0805 hours, during cold shutdown condition with no testing in progress, Instrument Bus 111 was momentarily lost due to the loss of Instrument Inverter 111's output power causing Reactor Protection bistables to trip and the Residual Heat Removal (RHR) Loop Suction Valve, 1MOV-RH8702, to start closing. The Inverter recovered 0.22 seconds after the start of the event, re-energized the AC Instrument Bus and resumed operation without any further incident. The Reactor Protection bistables reset immediately after the AC Instrument Bus was re-energized. The NSO secured the 1A RHR pump before the RHR Loop Suction Valve, 1MOV-RH8702, was completely closed. The NSO re-opened 1MOV-RH8702 after it went closed and the event was concluded when the 1A RHR pump was restarted at 08:09 hours, approximately 4 minutes after the Inverter failure.<br /><br /> The loss of RHR was attributed to the momentary loss of the Instrument Inverter output power which resulted in the RCS pressure transmitter generating a momentary signal in excess of 600 psig which closed RHR Loop Suction Valve, 1MOV-RH8702. This signal provides protection to prevent overpressurization of the RHR system when it is in service. <br /><br /> Based on the duration of the event, the recovery of the Inverter, and the status of the Reactor Coolant System at the time, the safety significance of the event was minimal.<br /><br /> Extensive troubleshooting and testing of the Inverter was performed and no component internal to the Inverter was found to be defective or degraded. It is believed that the loss of output power was due to a fault on the load side of the inverter.
2951991006 | Zion 1 | 04/23/1991 | 05/23/1991 | 9105300173 | <strong>Blackout Signal Inadvertently Induced During the Performance of the System Auxiliary Transformer Backfeed</strong><br /><i>Abstract:&nbsp;</i>On 4/22/91, while Unit 1 was in cold shutdown, the Unit 1 System Auxiliary Transformer (SAT) was taken out of service for maintenance and inspections using System Operating Instruction (SOI) 63 Attachment A "Unit 1 System Auxiliary Transformer (SAT) Backfeed Procedure." The procedure allows the Unit 2 SAT to provide the necessary power for the Unit 1 SAT loads through an abnormal line-up. <br /><br /> On 4/23/91, at 0238, a blackout signal was generated in response to two out of three non-Engineered Safety Feature (ESF) buses which feed ESF buses being de-energized. The ESF buses were being fed by the Unit 2 SAT at this point in time, so they were unaffected. Various ESF equipment started in response to the blackout signal. The equipment was secured and the blackout signal was cleared when one non-ESF bus was re-energized. All plant equipment operated as required and the procedure was continued. <br /><br /> At 0258, the same day, a two out of four Reactor Coolant Pump (RCP) bus undervoltage signal was generated as two non-ESF buses were de-energized at the same time. Steam Supply Valve to the 1A Turbine Driven Auxiliary Feedwater (AFW) pump, 1FCV-MS57, cycled open in response to the signal and closed immediately. <br /><br /> The cause of the event was a logic sequence error in the backfeed procedure that was not identified during the procedure review. The section of the procedure that re-energized the Unit 1 SAT was subsequently tested on the simulator to ensure that no further inadvertent signals would occur. SOI 63 Attachment A was successfully completed and the Unit 1 SAT was re-energized.
2951991007 | Zion 1, Zion 2 | 05/07/1991 | 12/11/1992 | 9212150182 | <strong>Control Room HVAC Envelope Unfiltered Inleakage Found to be Higher than the Value Assumed in the Docketed Analysis</strong><br /><i>Abstract:&nbsp;</i>In February a control room envelope inleakage test was conducted to determine if General Design Criteria (GDC)-19 could be met with the existing control room HVAC (heating, ventilating and air conditioning) system VI! (PV). The test results were received from the testing contractor in early May, and they showed that the air inleakage rates into the control room envelope were higher than the docketed analysis. The control room positive pressure and the emergency make-up air flow rates also were lower than the values stated in the UFSAR (Updated Final Safety Analysis Report). Engineering and Nuclear Construction (ENC) performed an operability analysis on the PV system and determined that the system was operable and there was no safety significance.<br /><br /> This event was caused by incorrect assumed values used in the Control Room Habitability Analysis. Corrective Actions included repairs to fan flex joints and door gaskets that were identified as areas of inleakage, investigation into additional methods of further reducing in-leakage and redoing the Control Room Habitability Analysis using assumptions that more closely match actual conditions, within current regulatory guidance.
2951991008 | Zion 1 | 05/10/1991 | 06/10/1991 | 9106130331 | <strong>Inadvertent Safety Injection due to A.C. Instrument Inverter Failure.</strong><br /><i>Abstract:&nbsp;</i>At 0020 on May 10, 1991, with the Unit in Hot Standby and RTD cross-calibration testing in progress, A.C. Instrument Inverter 112 failed causing the Hi-Steam Flow bistables to trip. With the lo-lo Tave bistables previously tripped per the RTD cross-calibration test procedure, the 2 of 4 coincidence necessary for Safety Injection actuation was established. The operators entered the Emergency Procedures and Safety Injection was terminated at 0029. Total duration of the Safety Injection was 9 minutes. <br /><br /> During the transient, both PORVs were disabled in the automatic mode due to the loss of instrument bus 112. The operating crew alertly opened both PORVs manually to control RCS pressure. RCS pressure peaked at 2411 psig and pressurizer level increased 7.3 percent. All safety related equipment operated as designed during the event. <br /><br /> An investigative team consisting of highly experienced offsite corporate personnel and Zion system experts was formed to investigate this event. Despite extensive troubleshooting and testing, the exact cause of the inverter failure has not been pinpointed. However, several weakened components within the inverter were identified and repaired or replaced. Thorough subsequent testing has shown the inverter to be fully operable.
2951991010 | Zion 1 | 06/16/1991 | 07/16/1991 | 9107190207 | <strong>ORT-PR02B Radiation Monitor Missed Action Statement Due to the Unusual Configuration of the Radiation Monitor System</strong><br /><i>Abstract:&nbsp;</i>Work request Z10472 was written with the intent to replace the blower belt on radiation monitor IL! ORT-PR02B for preventative maintenance. The work request incorrectly identified the Equipment Part Number (EPN) for radiation monitor as ORT-PR10C instead of the blower for ORT-PR02B. When the Operating department took the radiation monitor for Z10472 out of service (OOS), they thought that the blower for ORT-PR10C was being de-energized. However, the blower that was actually de-energized was the blower for ORT-PR02B. Consequently, deenergizing that blower rendered the ORT-PR02B monitor inoperable. This OOS was performed on 6/14/91 at 1100 (OOS 10-1406). <br /><br /> Five shifts of required surveillance per Technical Specification 3.14-1 Action 27 were missed before it was realized that ORT-PR02B was inoperable. <br /><br /> This event was caused by the unusual configuration of the radiation monitor system where a cabinet contains the blower of one radiation monitor and the monitor of another. Contributing factors included the work request identified the wrong EPN which was used to take the monitor OOS, the reference information used by the Licensed Shift Supervisor (LSS) was not correct, and the label on the motor control center breaker which was de-energized for the OOS was incorrect. Radiation monitors located downstream of ORT-PR02B were operable and would have detected any release so there was no safety significance to this event. Corrective Actions included correcting the reference material and the labels for the radiation monitor system.
2951991011 | Zion 1, Zion 2 | 06/24/1991 | 07/24/1991 | 9107290232 | <strong>Violation of Technical Specification 4.3.3.A due to Incorrect Numbering in the Technical Specifications of Two Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>On 06-24-91 during a systematic program review of Technical Specifications, it was determined that the surveillance requirements were not being met for leakage Technical Specification Section 4.3.3.A. This section requires that the containment atmosphere be monitored by either R11 or R12 when the Reactor Coolant System (RCS) AB! is greater than 500 psig, or that manual samples be taken shiftly when both monitors are out of service. When R11 and R12 were replaced by radiation monitors 1(2)RIA-PR40 by (PR40) in 1985, Technical Specifications Section 4.3.3.A was never updated to reflect this replacement.<br /><br /> The cause of the event was that during the modification approval process, the Modification Approval Sheet specifically stated that a Technical Specification change was not required. <br /><br /> The health and safety of the public were not compromised. The PR40 radiation monitors are just as capable as R-11 and R-12 at sampling effluents in containment. Activity of Particulate, Noble Gas and Iodine effluents is sampled continuously. Iodine effluents were not detectable with the original R-11 and R-12 monitors. <br /><br /> Corrective actions include completing the review that identified this discrepancy to ensure no further problems exist, submitting a Technical Specification change to correct the discrepancy, reviewing the event with appropriate departments, and taking credit for the fact that the modification process has been changed.
2951991012 | Zion 1, Zion 2 | 07/11/1991 | 12/13/1991 | 9112170224 | <strong>Snubber Modification Misinterpretation</strong><br /><i>Abstract:&nbsp;</i>In preparation for a hydraulic snubber replacement modification, it was noticed that the field location of snubbers 1SIRS-1018 and 1SIRS-1019 did not agree with the drawing. Investigation showed that snubbers 1SIRS-1017 and 1SIRS-1020 as identified on the drawing were supposed to be removed by modification M22-1-89-14, but due to incorrect labels, 1SIRS-1018 and 1SIRS-1019 were removed instead. <br /><br /> On 09/30/91 and 11/13/91 per the corrective actions of this original investigation, walkdowns of the inaccessible Unit 1 and Unit 2 hydraulic snubbers were performed. Three discrepancies were found during these walkdowns. Snubber 2RCRS-2082 was removed instead of 2RCRS-2083A, snubber 2SIRS-2132 was removed instead of 2SIRS-2133, and snubber 1DTRS-1064 was removed instead of 1DRTS-1063. <br /><br /> These events were caused by personnel errors during the installation of modifications M22-1-89-14, M22-2-88-69, and M22-1-88-033. The Nuclear Engineering department performed calculations to determine if the revised snubber configuration could adequately support the design basis loads. The calculations concluded that all affected supports would have remained functional throughout a seismic event and piping stresses would not have exceeded design basis limits. <br /><br /> The correct snubbers were reinstalled and the incorrect snubbers were removed. All snubbers were verified to be correctly installed.
2951991013 | Zion 1, Zion 2 | 07/20/1991 | 08/19/1991 | 9108220177 | <strong>Missed Technical Specification Action Statement on the Fire Sump Discharge Radiation Monitor, ORT-PR25</strong><br /><i>Abstract:&nbsp;</i>On 6/10/91 at 0245 the fire sump radiation monitor, ORT-PR25, was declared Out of Service (OOS) due to a high alarm. The Chemistry department correctly performed the necessary surveillance until 7/20/91 when the second shift Chemistry Technician (CT) failed to perform the surveillance for his shift. The third shift CT realized the error and performed the required surveillance. This event was caused by a personnel error. The second shift CT incorrectly thought that the surveillance was required daily instead of shiftly. The surveillance frequency is stated in the OOS package, but the CT did not correctly read the package he was given. The water that drains into the sump is primarily a product of the secondary systems, and various radiation monitors on the secondary systems remained operable throughout the event. Corrective actions included a disciplinary meeting between plant management and the individual involved, and the RP department taking complete control of all liquid radiation monitor OOS surveillance packages to ensure that all necessary packages are reviewed for completeness at the end of each shift.
2951991014 | Zion 1, Zion 2 | 07/31/1991 | 11/24/1992 | 9212030050 | <strong>Missed Technical Specification Action Statement on Technical Support Center SPING Radiation Monitor ORIA-PR30</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1991, during the performance of Periodic Test (PT) 0 - Appendix N, Radiation Monitor Checksheet, the Unit Operator found that there was no indication from the Technical Support Center (TSC) Eberline SPING radiation monitor IL! on the control room SPING console. The Unit Supervisor contacted the Radiation Protection (RP) department and requested that the problem be investigated. The RP Supervisor found that a portable computer was connected to the radiation monitor and that the monitor was in the maintenance mode. He disconnected the portable computer and placed the monitor in the normal mode. This restored all indication to the control room SPING console. <br /><br /> Investigation showed that the Instrument Maintenance (IM) technician who was calibrating this monitor did not notify the Licensed Shift Supervisor (LSS) at the end of the shift that the monitor was being left in an inoperable condition. Thus, no Periodic Test (PT)-14, Inoperable Equipment Surveillance was initiated by the LSS on the affected channel. Technical Specification 3.14.1.A.a, Action Statement 23, requiring that the TSC ventilation be placed in the recirculation mode within two hours, was not initiated within two hours of the out of service condition. <br /><br /> This event was caused by a personnel error on the part of the IM technician who did not notify the LSS that ORIA-PR30 was being left in an inoperable condition, and also on the part of the IM Supervisor who did not verify that the IM technician made the necessary notification. <br /><br /> The health and safety of the public and Station personnel occupying the TSC were not compromised. Corrective actions included counselling the personnel involved in this event, reviewing this event with the appropriate departments, and revising a procedure to insure all Technical Specification Surveillances and sampling requirements are met.
2951991015 | Zion 1, Zion 2 | 10/03/1991 | 11/04/1991 | 9111120239 | <strong>Containment Integrity Broken at Power</strong><br /><i>Abstract:&nbsp;</i>On 10/3/91 at 0031 hours, operating personnel were exiting Unit 1 containment after performing their nightly rounds. The equipment attendant inadvertently opened the outer containment air lock door from the inside of containment. The equipment attendant immediately attempted to close the outer door, but failed to close it completely. The equipment attendant continued to make his containment exit by opening the inner door. This should have been prevented by the containment door interlock mechanism, but the interlock mechanism failed, so he was able to open the inner door. As the inner door was opened, the equipment attendant noticed an out-rush of air through the door. Realizing that both doors were open, the equipment attendant exited containment and immediately secured the inner door. He then secured the outer door and informed the shift supervisor about what had occurred. Since this was considered to be a breech of containment integrity, the unit air lock was declared inoperable placing the unit on a 24 hour clock to hot shutdown. <br /><br /> The air lock was returned to operable status on 10/3/91 at 1810 hours prior to the 24 hour clock expiration. <br /><br /> The cause of this event was a component failure of the containment interlock mechanism. This event did not affect the health and safety of the public. <br /><br /> Corrective actions include repairing the interlock mechanism, investigating improvements to ensure door reliability, including this event in a Station Operating Experience Report, and discussing the inappropriate actions with the individual involved.
2951991016 | Zion 1 | 11/07/1991 | 12/09/1991 | 9112120065 | <strong>Reactor Trip and Safety Injection due to A.C. Instrument Inverter Failure</strong><br /><i>Abstract:&nbsp;</i>At 0434 on November 7, 1991, with the Unit at 100% power and steady state conditions, A.C. Instrument Inverter 114 failed, causing the 'Low Steam Generator Level' and 'Low Steam Generator Pressure' bistables to trip. Six seconds later a Steam Flow/Feed Flow mismatch signal was generated due to 1C Feed Pump flow reduction causing a Reactor Trip. The reactor trip signal caused the High Steam Flow Program to reset as designed, resulting in a High Steam Flow signal. The High Steam Flow signal combined with the 'Low Steam Generator Pressure' bistables previously tripped to establish the coincidence necessary to actuate Safety Injection and Main Steamline Isolation. <br /><br /> The cause of the inverter failure was a component failure. A Silicon Controlled Rectifier (SCR) in the Master section of Inverter 114 misgated causing a reduction in the inverter output voltage. This voltage reduction was sufficient enough to trip the channels of Reactor Protection and Safeguards instrumentation fed from this inverter.<br /><br /> During this event all safety related equipment operated as designed and there was minimal safety significance to this event. <br /><br /> Corrective actions included replacing all Unit 1 inverter SCRs prior to startup, including the SCRs in the preventative maintenance program and ensuring all Unit 2 SCRs will be replaced during the next Unit 2 refueling outage. <br /><br /> Previous events (LERS 1-91-005 and 1-91-008) documented A.C. Instrument Inverter failures that occurred on April 27 and May 10, 1991 on Inverters 111 and 112 respectively. The corrective actions from these LERs would not have prevented this event.
2951991017 | Zion 1 | 11/08/1991 | 12/09/1991 | 9112120067 | <strong>Loss of Service Bus 142 due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1445 on Friday November 8, 1991, with Unit 1 in Hot Shutdown, 4KV service bus 142 lost power. Service bus 142 is the normal feed to Engineered Safety Features (ESF) bus 147. The loss of power to service bus 142 resulted in a loss of power to ESF bus 147. The loss of ESF bus 147 resulted in an auto start signal to the '0' Emergency Diesel Generator (EDG). The '0' EDG auto started due to the low voltage sensed on ESF bus 147. The emergency feed breaker to bus 147 closed, allowing 0 EDG to pick up bus 147. All ESF equipment operated as designed. <br /><br /> This event was caused by a personnel error on the part of the Operational Analysis Department (OAD) engineer. The OAD engineer did not reset the LBB trip relay prior to restoring the test switches for the five Unit 1 service buses. Contributing causes included OAD engineers performing the 345 KV switchyard protective relay systems tests using schematic diagrams, job specific vendor manuals, and job specific technical training, a lack of formal written procedures for OAD personnel to use when testing the 345 KV switchyard protective relay systems, a lack of clearly expressed guidance for checking for the presence of trip voltages, and inadequate communication between the OAD engineer and shift personnel. <br /><br /> The safety significance of this event is bounded by the FSAR loss of a ESF bus during hot shutdown analysis. All ESF equipment functioned as designed. There was no effect on the health and safety of the public. <br /><br /> Corrective Actions included counselling the individual, training OAD personnel on the proper method for verifying voltages, developing a list of OAD testing and its potential impact on plant equipment, consider including this information in the Licensed Operator training program, and requiring OAD personnel to obtain the concurrence of the Shift Engineer prior to entry into the switchyard.
2951991018 | Zion 1, Zion 2 | 12/06/1991 | 01/10/1992 | 9201210076 | <strong>Inadequate Shift Control Room Engineer Coverage per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1991, during a review of the Shift Engineer's log book, it was discovered that on December 6, 1991 none of the Licensed Shift Supervisor's (LSS) on duty were Shift Control Room Engineer (SCRE) qualified. Technical Specification Figure 6.1-1, Minimum Shift Crew Composition, requires that each shift crew have one qualified SCRE. <br /><br /> This event was caused by a management deficiency. An inadequate program existed to ensure that the Technical Specification requirements were satisfied for SCRE qualification. <br /><br /> The safety significance of the event was minimal. <br /><br /> Corrective actions included identifying SCRE and Fire Chief qualifications on the posted LSS schedule, and establishing a SCRE turnover log.
2951991019 | Zion 1 | 12/26/1991 | 01/27/1992 | 9201300268 | <strong>Reactor Trip Due to Accidental Deenergization of AC Instrument Bus 111</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1991 at 1617 while performing the routine Equipment Operator rounds, an equipment operator found the Instrument Inverter 111 output breaker switch in the 3/4 position and appearing to be loose. After contacting the unit operator, the equipment operator reset the breaker by opening it and then closing it. This action caused power to be lost to AC Instrument Bus 111 subsequently causing the reactor trip breakers to open. Unit 1 was in cold shutdown when this event occurred, but the reactor trip breakers were closed to enable main turbine latching for turbine stop valve/governor valve work. The unit operators took the appropriate actions to restore the unit to the normal shutdown cooling alignment. <br /><br /> This event was caused by a personnel error on the part of the equipment operator that was a result of inadequate communications between the equipment operator and the unit operator. <br /><br /> Since Unit 1 was in Mode 5 and the control rods were completely inserted when this event occurred, the safety significance to this event was minimal. <br /><br /> Corrective Actions included performing a Human Performance Enhancement System (HPES) evaluation, counselling the individuals involved, placing a caution label above all four Instrument Inverter output breakers on each unit, providing Equipment Operator Awareness Training, and reviewing the event with all Station personnel.
2961991001 | Browns Ferry 3, Browns Ferry 1, Browns Ferry 2 | 02/01/1991 | 03/01/1991 | 9103110026 | <strong>Deenergization Of Reactor Protection System Bus By Normal Supply Circuit Protector Operations Caused By Failure Of Overvoltage Voltage Monitor.</strong><br /><i>Abstract:&nbsp;</i>At 1345 hours on February 1, 1991, an unplanned actuation of engineered safety features (ESFs) occurred on Browns Ferry Unit 3. The actuations occurred because Unit 3 reactor protection system (RPS) bus 3A was deenergized. ESFs affected by this event include standby gas treatment system, control room emergency ventilation system, and Unit 3 primary containment isolation system. The actuated plant systems responded as expected to the loss of the RPS bus. <br /><br /> The RPS bus deenergization resulted from the tripping of RPS circuit protector 3A2. Troubleshooting revealed that the internal voltage monitor (Diversified Electronics UOA-0267) of the circuit protector had failed.<br /><br /> The root cause of this event was a random component failure of the circuit protector overvoltage voltage monitor. The type of voltage monitor that failed in this event had no history of any previous failures. <br /><br /> The faulty component was identified and replaced. TVA has contacted the vendor to arrange for an evaluation of the failed voltage monitor.
2961991002 | Browns Ferry 3, Browns Ferry 1, Browns Ferry 2 | 04/05/1991 | 05/05/1991 | 9105140382 | <strong>Unplanned Engineered Safety Features Actuation Following Deenergization of Reactor Protection System Bus by Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1991 at 1528 hours, an unplanned Engineered Safety Features actuation occurred following de-energization of a Reactor Protection System (RPS) bus. The RPS bus deenergized after one of its two circuit protectors tripped for unknown reasons. Deenergization of the RPS bus resulted in actuation of the Primary Containment Isolation System (PCIS), the Standby Gas Treatment System (SGTS), the Control Room Emergency Ventilation System (CREV), the Unit 3 Reactor Zone Ventilation System and the Units 1, 2 and 3 Refueling Zone Ventilation Systems. <br /><br /> The root cause of this event is unknown. <br /><br /> Corrective action included restoring the PCIS, SGTS, CREV and ventilation systems to normal standby alignment. The 3B1 circuit protector's overvoltage monitor was also replaced based on testing which indicated an anomaly in the overvoltage setpoint.
2961991003 | Browns Ferry 3, Browns Ferry 1, Browns Ferry 2 | 04/12/1991 | 06/25/1991 | 9107020148 | <strong>An Unplanned Engineered Safety Feature Occurred From Personnel Error While Performing a Common Accident Signal Logic Surveillance Instruction.</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991 at 1817 hours, an unplanned engineered safety feature (ESF) actuation occurred when the four Unit 3 emergency diesel generators (EDGs) unexpectedly auto-started during the performance of common accident signal (CAS) logic Surveillance Instruction (SI). The automatic initiation of an ESF is reportable in accordance with 10 CFR 50.73(a)(2)(iv). <br /><br /> The cause of this event is personnel error resulting from a lack of attention to detail during installation of an inhibiting boot between two contacts on the Division II core spray logic B relay.<br /><br /> Corrective actions performed were: Operations personnel ensured Electrical Maintenance (EM) personnel stopped the performance of the SI; an incident investigation was conducted to determine the cause of the event; and EMs resumed and successfully completed the 1/2 CAS SI. Maintenance personnel who install boots will receive training on the proper installation of boots by July 1, 1991.
2961991004 | Browns Ferry 3 | 11/04/1991 | 12/03/1991 | 9112110043 | <strong>Inability to identify and establish compensatory measures for loss of high pressure fire protection system hose stations which lead to a condition prohibited by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991 at 1310 hours, the Unit 3 control room was notified of a leak in a three-inch high pressure fire protection system pipe. A utility-licensed assistant shift operations supervisor dispatched to the scene isolated the leak. Parallel actions were taken to initiate required compensatory measures; however, required compensatory measures were not established within one hour as required by Technical Specifications. <br /><br /> The root cause of this event was an inadequate method for identifying which parts of the system required one hour compensatory actions and which allowed 24 hours. This resulted in an excessive amount of time required to identify and implement the one hour compensatory measures for isolated fire hose stations. Contributing to the failure to meet compensatory measure requirements is the existing design of the open nozzle fixed spray systems. <br /><br /> The immediate corrective actions included isolating the leak, initiating establishment of compensatory actions and the installation of a temporary patch. TVA will develop a method to enable personnel to begin compensatory measures immediately when a portion of the high pressure fire protection is isolated. An appropriate amount of compensatory action hose kits will be staged. TVA has staged patch kits. TVA will replace the open head fixed spray system.
2981991001 | Cooper Station | 01/07/1991 | 02/01/1991 | 9102150196 | <strong>Unplanned Actuation of Group VI Isolation During Surveillance Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1991, at 1:38 pm, with the plant in operation at full power, an unplanned actuation of the Group VI Isolation logic occurred, resulting in isolation of the Secondary Containment and initiation of the Standby Gas Treatment (SGT) System. The actuation occurred due to incorrect placement of a jumper during performance of Surveillance Procedure 6.3.7.5, Reactor Building Ventilation Radiation Monitor Source Check, which was being performed by I&C trainees, under the supervision of qualified I&C Technicians, The procedure was being conducted as a regularly scheduled surveillance test and as an On-the-Job Training (OJT) exercise. <br /><br /> The cause of the unplanned actuation was the failure of both the qualified Technician, acting as an OJT Instructor, and the trainee to refer to the procedure step prior to installation of the jumper. Corrective action taken included test termination, jumper removal, reset of the Group VI Isolation, and restoration of Reactor Building ventilation to normal. The procedure was reviewed and determined to be satisfactory from a content and human factors standpoint. Both the qualified I&C Technician and the trainee were counseled. Further corrective action to be taken includes incorporation of this event in Industry Events training for I&C Technicians.
2981991002 | Cooper Station | 03/24/1991 | 06/03/1991 | 9106100118 | <strong>Reactor Water Cleanup Isolations Due To High System Temperature Caused By Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1991, at 2:38 am and, again, at 4:15 am, Reactor Water Cleanup (RWCU) system isolations occurred due to high temperature conditions (140 degrees Fahrenheit) downstream of the Non-Regenerative Heat Exchangers (NRHX). At the time of these occurrences, the reactor was shutdown with the Residual Heat Removal (RHR) System providing shutdown cooling. The RWCU pumps were secured to facilitate feedwater system maintenance. Subsequent to these events, faulty instrumentation was repaired and further testing was planned to verify the source of the high temperature water. <br /><br /> On May 7, 1991, RWCU was removed from service to assist in investigating the cause of a slightly increased leakage inside the drywell. At 10:36 am, following closure of the inboard RWCU isolation valve, another RWCU system isolation from high temperature occurred, causing closure of the outboard RWCU isolation valve. During this occurrence, the Reactor was at approximately 100 percent power, 517 degrees and 998 psig. <br /><br /> Subsequent testing indicated the high temperature condition occurred as a result of backflow through the check valve in the 3/4 inch subcooling line installed between the NRHX outlet and the RWCU system inlet piping. The root cause of the backflow is Design (failure to anticipate all system operating modes), as the differential pressure available across the check valve when the RWCU pumps are secured is not sufficient to obtain a leaktight shutoff. <br /><br /> A caution tag has been placed on the RWCU pump switches requiring isolation of the subcooling line except during Reactor cooldown. The design of the subcooling line will be reviewed and the design review process enhanced to ensure evaluation of all anticipated modes of system operation.
2981991003 | Cooper Station | 03/25/1991 | 04/24/1991 | 9104290298 | <strong>Unplanned Actuation of Group VI Isolation During Surveillance Testing Due to Personnel Error and Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1991, at 10:59 pm, with the plant in Cold Shutdown for a maintenance outage, an unplanned actuation of the Group VI Isolation logic occurred, resulting in isolation of the Secondary Containment and closure of the Drywell Vent and Purge valves. The actuation occurred during surveillance testing, when the I&C Technician stationed in the Control Room failed to reset the Reactor Building Ventilation Radiation Monitor prior to removal of a test jumper. The test in progress was Surveillance Procedure (SP) 6.3.7.5, Reactor Building Ventilation Radiation Monitor Source Check. As the Technician began to remove the jumper, arcing was observed. The jumper was immediately relanded, restoring the radiation monitor logic circuit to its normally energized condition. This interrupted the Group VI actuation signal. The monitor was then reset and the ventilation systems were restored to their normal lineup. While Standby Gas Treatment System operation was not observed by the Control Room Operator, this would have been expected due to the effect of the momentary actuation signal on the control system logic. <br /><br /> The failure to properly reset the radiation monitor was due to ambiguity in the procedure and personnel error. Upon encountering the ambiguous step, the Technician was unsure that reset was required prior to removing the jumper. Nevertheless, he proceeded to remove the jumper without obtaining clarification. <br /><br /> A procedure change is being processed to provide improved direction for the required action. Further, as a means of both upgrading Technician attention to procedural requirements and to improve their understanding of technical details, guidelines for procedure performance and completion have been developed by I&C Shop personnel.
2981991004 | Cooper Station | 03/26/1991 | 04/25/1991 | 9104290307 | <strong>Unplanned Automatic Startup of Diesel Generator Number 1 Caused by Inadequate Planning and Poor Communication During Drawing Verification Project Activities</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991 at 9:26 am, Diesel Generator Number 1 (DG #1) automatically started, but was not required to load, when the fuse block for the 4160v 1A Bus undervoltage protection circuit was pulled during Drawing Verification Project activities. As a result of the circuit being deenergized, 4160v Breaker 1AF opened, deenergizing the 4160v 1F Critical Bus. This resulted in the receipt of an automatic start signal by DG #1, closure of several Primary Containment Isolation valves associated with Groups III and VI, and load shedding of pumps and load centers powered from the 4160v 1F Critical Bus. The Bus was automatically repowered from the Emergency Transformer, as designed. At the time of the event, the plant was shutdown, with the Residual Heat Removal (RHR) System in the Shutdown Cooling mode of operation. Reactor water temperature was 137 degrees Fahrenheit. <br /><br /> The cause of these unplanned actions was due to personnel error, coupled with inadequate communications and human factors considerations. The potential for, and impact of, losing the undervoltage protection circuitry had not been properly assessed by project personnel. The Shift Supervisor understood that the fuse was associated with the 1A Condensate Pump. The location of the fuse in the 1A Condensate Pump Switchgear compounded the communications and assessment deficiencies. <br /><br /> Corrective action was taken to restore Shutdown Cooling and realign systems to their prior configuration. "Hands-on" Drawing Verification Project activities were abated until such time as project instructions providing improved guidance associated with verification activities on energized circuits and familiarization of personnel with the improved guidance could be instituted.
2981991005 | Cooper Station | 05/11/1991 | 06/07/1991 | 9106130222 | <strong>Unplanned Startup Of Diesel Generator Number 2 Due To An Equipment Deficiency That Occurred During Plant Startup While Transferring Loads To The Normal Transformer</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1991, at 3:58 a.m., during plant startup following an unscheduled shutdown, Diesel Generator Number 2 (DG #2) automatically started, but was not required to load, due to a malfunction of the Normal Transformer supply breaker, 1BN. This occurred when transferring loads from the Startup to the Normal Transformer. See attached sketch. Upon closure of the 1BN 4160v Breaker and tripping of the 1BS Breaker (from the Startup Transformer), Breaker 1BG, the normal supply breaker for 4160v 1G Critical Bus, also opened. Upon sensing undervoltage on the 1G Bus, DC #2 automatically started. Within approximately one second, the 1G Bus was reenergized from the Emergency Transformer, functioning as designed. Therefore, the Diesel Generator was not required to load. <br /><br /> The cause of the event was due to insufficient action of the breaker auxiliary switch upon closure of the 1BN Breaker, such that switch contacts in the 1B Bus undervoltage circuit opened, allowing relay 27 X2/1B to deenergize. The subsequent breaker operations occurred due to the undervoltage trip logic being deenergized.<br /><br /> Corrective action taken included inspection of the breaker and auxiliary switch for proper operation and reshimming the breaker to slightly elevate the breaker in its installed position in the cubicle. This resulted in improving the action of the auxiliary switch to achieve contact closure. A further inspection of other 4160v breakers, including the associated auxiliary switches, will be made during the 1991 Refueling Outage. Based on the results of these inspections, further corrective actions will be taken as necessary.
2981991006 | Cooper Station | 07/09/1991 | 08/06/1991 | 9108120263 | <strong>4160 Volt Loss Of Voltage Relay Setpoint Noncompliance With Incorrectly Stated Technical Specification Requirements Determined During Design Basis Reconstitution Activities</strong><br /><i>Abstract:&nbsp;</i>During performance of a Design Basis Review of the Standby AC Power System, the setting limits prescribed in the CNS Technical Specifications for the 4160 Volt Loss of Voltage Relays were determined to incorrectly reflect original design basis requirements. The Technical Specification setting limit for these relays was listed as 2900 volts and five seconds, with tolerances. However, these limits were determined to be incorrect. The actual relay settings were confirmed to be consistent with the original design basis settings. Therefore, they were not in compliance with Technical Specification requirements. On July 9, 1991, when the condition was formally documented as a nonconforming condition, the plant was in operation at 99 percent power. <br /><br /> The incorrect setpoint information had been incorporated into the Technical Specifications with issuance of Amendment 43 in April, 1978. <br /><br /> The incorrect settings proposed by the District and incorporated into the Technical Specifications resulted from a misstatement of the setting which defined the existing inverse time-voltage characteristic operating curve of the Loss of Voltage Relays. <br /><br /> A Waiver of Compliance was issued by the NRC pending the processing of an Emergency Technical Specification change. This action was completed with issuance of Amendment No. 144 to the Technical Specifications on July 17, 1991. Additional corrective actions taken or in progress included a review and updating of the surveillance procedure for these relays, a review of the design drawings to ensure conformance of the prescribed relay settings for these relays with design and Technical Specification requirements, and development of updated information regarding these relays for a future revision to the Updated Safety Analysis Report.
2981991007 | Cooper Station | 07/30/1991 | 08/23/1991 | 9108270226 | <strong>Fan Coil Units For Diesel Generators Not Seismically Qualified Due To Inadequacies In Original Design</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1991, as a result of an open item identified during performance of design basis development activities, it was determined that the existing spring isolators supporting the safety related Diesel Generator Fan Coil Units (FCUs) did not satisfy the original installation requirements and could not be considered capable of satisfying seismic requirements. The FCUs were declared inoperable, resulting in the Diesel Generators also being declared inoperable. <br /><br /> This condition is a result of inadequacies in the original design. The information furnished by the Architect/Engineer to the organization performing the seismic qualification of these units indicated that rigid supports were provided. However, the units were installed with spring isolators. Upon determining that the existing supports were inadequate, immediate action was taken to modify the support scheme. All other safety related FCUs were verified to be correctly supported.
2981991008 | Cooper Station | 08/26/1991 | 09/25/1991 | 9110010231 | <strong>Technical Specification Violation For Failure to De-activate An Inoperable Containment Isolation Valve As A Result Of Inconsistent Technical Specifications And Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1991, with the plant in operation at approximately 80 percent power, valve RHR-MO-MO57 exceeded its Technical Specification closure time during surveillance testing. For the existing plant conditions, Technical Specifications require maintaining containment integrity and recording the position of the redundant valve. The failure of the valve was not recognized by licensed personnel performing the test, but instead was recognized by the IST Engineer on August 27. The Control Room was notified, the valve declared inoperable, and the position of the redundant valve recorded as required by Technical Specifications. On September 17, during a review of this condition by the Station Operations Review Committee, an additional action of "de- activating the valve while it was inoperable, as implied by the definition for containment integrity, was determined to have been required by the Technical Specifications. <br /><br /> The root causes of this event are personnel error and inconsistency in Technical Specification requirements for inoperable automatic containment isolation valves. The inoperable valve was repaired and returned to service. The personnel involved will be counseled regarding attention to detail, and this will also be emphasized to all licensed operators. A change to the Technical Specifications to eliminate the inconsistency, regarding actions required when a containment isolation valve is inoperable will be evaluated. Interim guidance to de-activate these valves will be provided to the Control Room.
2981991009 | Cooper Station | 09/04/1991 | 10/03/1991 | 9110100147 | <strong>Spurious Secondary Containment Isolations Caused By Actuation Of The "B" Reactor Building Ventilation Exhaust Radiation Monitor Due to A Malfunctioning Power Supply</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1991 at 3:31 a.m. and, again, on September 9, 1991, at 2:44 a.m., two unplanned Group 6 Isolations occurred due to an apparent spurious loss of power to the "B" Reactor Building Ventilation Exhaust Radiation Monitor. Plant power level on each occasion was approximately 80 percent. In each case, the Radiation Monitor panel indications on Panel 9-02 in the Control Room following each actuation were the same, in that both the high and downscale lamps were lit and the monitored radiation level was normal. In both situations, observing no problems, the licensed Control Room Operator reset the radiation monitor. Upon resetting the Group 6 Isolation, the Reactor Building Heating and Ventilating System automatically realigned to its normal operating configuration. <br /><br /> The cause of the first event was initially thought to be as a result of a loose connector which was then tightened. However, following the second event, a detailed investigation of the radiation monitor power supply was conducted. A faulty voltage regulator card was found. This failure is considered to be a random component failure<br /><br /> The defective card, subsequently identified as the cause of both trips, was replaced. Following satisfactory completion of testing, the radiation monitoring unit was returned to service.
2981991010 | Cooper Station | 10/02/1991 | 10/31/1991 | 9111070175 | <strong>Reactor Water Cleanup Isolation Due To High System Temperature Caused By Backflow From The Regenerative Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991, at 10:35 a.m., a Group 3 Isolation (Reactor Water Cleanup RWCU! System) occurred due to high temperature conditions (140 degrees Fahrenheit) downstream of the Non-Regenerative Heat Exchangers. The RWCU System had been removed from service and rapidly depressurized to allow maintenance on an RWCU pump suction valve which had developed a steam leak. Both RWCU System isolation valves were closed at the time of the event. During this event, the Reactor was at approximately 72 percent power, 517 degrees Fahrenheit and 973 psig. <br /><br /> The high temperature condition was the result of hot water being drawn backwards from the Regenerative Heat Exchangers into the section of piping containing the high temperature isolation switch. The backflow was a result of void formation caused by the rapid pressure reduction and subsequent cooling of the system. The effect of backflow on the temperature switch was an unforeseen result of the physical arrangement of the system. A procedure change will be processed to identify the need for a slow depressurization, when possible, since a slow depressurization should not result in an isolation signal. A caution will be added to expect a Group 3 Isolation should a rapid pressure reduction be necessary. This event will also be discussed in Industry Events Training.
2981991011 | Cooper Station | 10/07/1991 | 11/06/1991 | 9111140163 | <strong>RPS and ESF Trips Due To Spurious Trip Of Two RPS Reactor Vessel Water Level Instruments Caused By An Air Bubble At The Instrument Reference Leg Tap</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, at 1:43 a.m., with the plant shutdown and the Residual Heat Removal (RHR) system operating in the shutdown cooling mode of operation, an RPS trip and actuation of Groups 2 and 3 Isolations (Reactor Coolant System and Reactor Water Cleanup System) occurred due to a spurious low level actuation of two Reactor Vessel Water Level sensors. At the time, water level was 10-15 inches above the level maintained during normal operation. <br /><br /> The cause of the event is postulated to be as a result of either introduction of air through reference leg injection solenoid valve NBI-SOV-SPV739 into the condensing chamber 3B reference leg, which is common to all of the affected instruments, or water leakage through the solenoid valve into the reference leg, disturbing an existing air bubble. The postulated reference leg disturbance occurred, even though the solenoid valve was closed, upon restoration of the "B" Core Spray (CS) System following performance of Local Leak Rate Testing (LLRT). The air bubble in the reference leg eventually migrated to the condensing chamber reference column. The hydraulic effects of the air bubble in the column resulted in tripping the RPS level sensors. <br /><br /> Upon restoration of normal water level following refueling activities, instrument line venting or backflushing will be conducted to resolve any disparate indications. Additionally, a procedure change to aid in assuring that the reference leg injection piping is maintained full during performance of LLRT or is refilled subsequent to performance of LLRT will be pursued.
2981991012 | Cooper Station | 10/15/1991 | 11/14/1991 | 9111210099 | <strong>Unplanned ESF Actuations During Design Change Activities Resulting From Personnel Error, Human Factors, And Inadequate Precautions For Work In Sensitive Areas</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1991, at 2:03 a.m. and 3:31 a.m., Group 3 Isolations (Reactor Water Cleanup RWCU! System) occurred due to a blown fuse and de-energizing a relay, resulting in closure of the outboard isolation valve. At 9:41 p.m., a loss of normal offsite power occurred when a wire being moved inadvertently completed a relay trip circuit. The essential busses transferred to the Emergency Transformer and the #2 Diesel Generator started. During the transfer to emergency power, the "A" Reactor Protection System lost power, causing a half scram and various Group Isolations. These actuations were a result of design change activities associated with the CNS Annunciator Upgrade Project. During these events, the plant was in a refueling outage, and fuel was being offloaded to the Spent Fuel Pool. <br /><br /> These actuations resulted from an improperly installed relay identification tag and the failure to implement the precautions necessary to prevent inadvertent actuations when working in sensitive areas. Contributing causes were a design error, failure of the design change to identify the sensitive work areas, and incorrectly moving a wire. As a result of these events, design change work in the Control Room was stopped until the design change packages were independently reviewed to identify sensitive areas. Written guidelines for working near sensitive circuits were developed, and emphasized in craft briefings. This experience will be incorporated into training and instructions for design engineering.
2981991013 | Cooper Station | 10/18/1991 | 11/18/1991 | 9111250165 | <strong>Failure To Establish A Continuous Fire Watch for An Obstructed Fire Door As Required By Technical Specifications Due To Personnel Error And Procedural Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1991, during a review of Surveillance Procedure (SP) 6.4.5.1, Fire Protection System Monthly Examination, the Fire Protection Engineer noted that the door to the steam tunnel had been recorded as being open and obstructed for work in the steam tunnel. SP 6.4.5.1 had been conducted on October 18, 1991. The steam tunnel door, a Fire Door which is a required Fire Barrier as specified in Technical Specifications, is subject to specific procedural controls prescribed in CNS Procedure 0.16, Control of Fire Doors. The Fire Protection Engineer conducted a follow-up inspection to determine if the door was still obstructed, and if so, to ensure a Fire Watch was posted. The door was found to still be obstructed. However, no Fire Watch was posted, contrary to the requirements of CNS Procedure 0.39, Fire Watch/Fire Watch Patrol Activities. At the time, the plant was in cold shutdown for the 1991 Refueling Outage.<br /><br /> Two root causes contributed to this situation. Personnel Error has been assigned due to failure to follow procedural requirements for Fire Watches. Procedure Deficiency has been assigned because Procedure 0.39 was not referenced in Procedure 0.16, causing confusion as to the correct requirements. <br /><br /> Corrective action taken has included increased outage management attention to Fire Watch requirements and initiation of a roving Fire Watch to ensure that Fire Door requirements are met. Further action to be taken includes upgrading of the pertinent procedures and related training materials, and reviewing this event in Industry Events Training.
2981991014 | Cooper Station | 10/30/1991 | 11/27/1991 | 9112040285 | <strong>Unplanned Group 6 Isolation From Short Circuit During Design Change Activities</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1991, at 11:36 a.m., with the plant in Cold Shutdown for a refueling outage, an unplanned actuation of the Group 6 Isolation logic occurred, resulting in isolation of the Secondary Containment and startup of the B Train of Standby Gas Treatment. The A Train of Standby Gas Treatment was out of service for maintenance. Contract electricians, working in a Control Room panel, were preparing to install wiring for a design change. Upon moving the wiring, an uninsulated metal clip (used for surveillance testing) on the end terminal of a terminal board came in contact with the terminal board mounting hardware, resulting in a blown fuse and the Group 6 Isolation. After determining the cause, the fuse was replaced, the isolation reset, and the Reactor Building Ventilation System automatically returned to its normal lineup. <br /><br /> The cause of this event is the improper selection of an uninsulated metal clip for surveillance testing. The use of this style clip did not consider the potential consequences of its use. A tab on the terminal board mounting hardware was bent in toward the terminals, and the screw holding the clip may not have been tight due to installation activities or an oversize wire lug. Congested conditions in the panel prevented the clip and bent tab on the terminal board mounting hardware from being discovered during the inspections which preceded the installation activities.<br /><br /> The use of uninsulated metal clips had previously been recognized as undesirable and they are being replaced during this refueling outage. The terminal board mounting hardware was taped to prevent further inadvertent grounding, and the contract electricians were cautioned about the possible problems associated with loose terminals. This event will be covered in Industry Events Training for Engineering, I&C and Electrical Maintenance personnel.
2981991015 | Cooper Station | 11/05/1991 | 12/05/1991 | 9112100010 | <strong>Safety/Relief And Safety Valve Setpoint Variance Not Within Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>While the plant was shutdown for the 1991 Refueling Outage, testing of Safety/Relief Valves (S/RVs) and a Safety Valve (SV) was conducted at Wyle Laboratories, Huntsville, Alabama. The as-found setpoint for the S/RVs was not within the Technical Specification limit of +/- 1 percent (11 psi). Additionally, the setpoint for the SV was not within the Technical Specification limit of +/- 1 percent (13 psi) This is a voluntary report in accordance with 10CFR50.73 guidelines. <br /><br /> No specific discrepancies were identified during testing or subsequent disassembly and inspection efforts. Review of the test data indicates the safety relief valves generally displayed performance characteristics typical of industry-wide problems with corrosion bonding of the pilot disc. To date, the root cause and corrective action for this industry-wide problem remains unresolved. Also noted were performance characteristics typical of labyrinth seal induced friction. The failure of the safety valve is considered random setpoint drift. <br /><br /> The valves were inspected, refurbished and satisfactorily retested at Wyle Laboratories before their return to the site. A Technical Specification change request, increasing the setpoint tolerance to +/- 3 percent, had previously been submitted to the NRC on January 26, 1990. The proposed change was identified as corrective action in LER 89-015. Until such time as the S/RV setpoint deficiency being experienced and evaluated industry-wide is resolved, no further corrective action is planned.
2981991016 | Cooper Station | 11/10/1991 | 12/10/1991 | 9112180039 | <strong>Spurious RPS Trip While Shutdown Due To Decontamination Activities Under The Reactor Vessel</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1991, at 10:41 p.m., a spurious RPS trip occurred when a contractor assigned to decontamination work in the Drywell bumped his head on Nuclear Instrumentation (NI) assemblies while on the equipment platform under the reactor vessel. This incident caused an Intermediate Range Monitor (IRM) to spike to the Hi-Hi trip setpoint. At the time of the event the plant was shut down for the 1991 Refueling Outage, with all fuel off loaded into the Spent Fuel Storage Pool. Final preparations for reloading fuel into the reactor vessel were in progress. These preparations included activating the RPS non-coincidence trip function, such that actuation of a single NI channel would result in a full scram. <br /><br /> The root cause of this event is considered to be a programmatic deficiency, in that while the potential for an RPS trip was recognized, sufficient precautions were not taken to preclude its occurrence. Upon activating the non-coincidence trip function, decontamination work (and any other non-critical activity) that could potentially disturb the response of the NI System and cause a trip should not have been permitted. <br /><br /> Decontamination activities under the reactor vessel were suspended until fuel loading was completed and the RPS non-coincidence trip function was deactivated. Prior to the next refueling outage, pertinent procedures will be upgraded to provide additional guidance associated with plant operational
2981991017 | Cooper Station | 11/23/1991 | 12/23/1991 | 9112270356 | <strong>Partial Reactor Coolant System, Primary and Secondary Containment Isolations Received During Design Change Acceptance Testing Due to a Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1991, at 12:06 am, a spurious actuation of several Reactor Coolant System (RCS), Primary Containment and Secondary Containment Isolation Valves occurred when Fuse 16A-F21 blew upon or shortly following removal of a circuit lead. The fuse supplies 120 volt AC control power to a Primary Containment Isolation System (PCIS) circuit. At the time, the circuit was undergoing acceptance testing for a design change associated with installation of test jacks.<br /><br /> At the time of the event, the plant was shutdown for the 1991 Refueling Outage. Fuel had been loaded in the vessel, which was awaiting reassembly. The most immediate effects of these actuations were the temporary losses of Shutdown Cooling and normal Reactor Building ventilation. At 12:45 am, approximately 40 minutes following the spurious actuation, Shutdown Cooling was reestablished and normal Reactor Building ventilation was restored. During the period of time that Shutdown Cooling was off, the RCS temperature rise was insignificant. <br /><br /> For a very short time period, the lead was not under positive control of the Licensed Operator. It is suspected that the lead shorted to ground subsequent to its being released. <br /><br /> The acceptance testing activities performed by the Licensed Operator in the Control Room were reviewed, and found acceptable. Other than reviewing this event during Industry Events Training, no further corrective action is considered necessary.
2981991018 | Cooper Station | 03/23/1991 | 01/02/1992 | 9201090156 | <strong>Failure Of A 4160V Circuit Breaker To Trip Due To Sticking Trip Latch Roller Mechanism Caused By Hardened Lubricant</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1991, 4160V circuit breaker 1CN, which feeds the 'A' Reactor Recirc Motor Generator (RRMG) motor, failed to open upon actuation of the breaker control switch. A second attempt to trip the breaker was successful, although it took approximately ten seconds for the breaker to open. Inspection of the breaker immediately after the event revealed that the trip latch roller would not rotate freely, and therefore inhibited the breaker from tripping on demand. This problem was considered to be similar to three previous 4160V breaker deficiencies that had been documented in 1987. These events involved a failure of two Residual Heat Removal (RHR) Pump motor breakers to initially close.<br /><br /> The root cause of this condition was incomplete maintenance of the 4160V breakers, in that hardened grease deposits existed which inhibited breaker operation. The 4160V breakers are identical and were supplied as original plant equipment. With the exception of the refurbishment of ten safety related breakers to date, the maintenance practices for these breakers have been identical. Consequently, a number of 4160V breakers were potentially subject to the same failure mode. This condition was determined to be reportable during document close out activities for this event. At the time, the 1991 Refueling Outage was in progress. <br /><br /> Corrective actions taken included 1) the trip latch and cam follower rollers of all 4160V breakers which had not been refurbished were removed, cleaned, and regreased or replaced; 2) preventive maintenance was enhanced to periodically remove, clean and regrease all 4160V breaker trip latch and cam follower roller mechanisms; and 3) the cubicle space heaters for the 4160V breakers (except for EG1 and 2, the diesel generator output breakers) were de-energized.
2981991019 | Cooper Station | 12/09/1991 | 01/08/1992 | 9201150118 | <strong>Actuation Of Shutdown Cooling Isolation Valves While Performing the Containment Integrated Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1991, at 9:48 am, with the Primary Containment at 58 psig during the performance of the Primary Containment Integrated Leak Rate Test (ILRT), the Group 2 (Shutdown Cooling) isolation valves automatically closed while attempting to restart a Residual Heat Removal (RHR) pump in the Shutdown Cooling mode. The RHR pump had been secured to allow personnel using sonic detection equipment to locate sources of leakage. Upon restarting the RHR pump, the Shutdown Cooling high suction pressure interlock actuated. Both Shutdown Cooling isolation valves closed as a result of the actuation. At the time, the plant was in a refueling outage with a Reactor coolant temperature of 103 degrees Fahrenheit. The Reactor was vented to the Primary Containment during the test. Reactor coolant temperature increased to 128 degrees Fahrenheit over the 4 1/2 hours Shutdown Cooling was secured.<br /><br /> This event was the result of a momentary pressure transient resulting from starting the RHR pump combined with the ILRT pressure. A procedure change will be processed to provide the necessary guidance for starting an RHR pump in the Shutdown Cooling mode under ILRT conditions.
2981991020 | Cooper Station | 12/10/1991 | 01/09/1992 | 9201140294 | <strong>Failure Of The Primary Containment Integrated Leak Rate Test Due To Drywell Vent Monitor System and Containment Penetration Leakage</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1991, the Containment Integrated Leak Rate Test (ILRT) leak rate was determined to be 437.5 Standard Cubic Feet per Hour (SCFH) or 1.38 La, where La is the allowable containment leak rate. This leak rate included an ILRT penalty equal to 192 SCFH and a Type B and C Local Leak Rate Test (LLRT) adjustment of 143 SCFH. The penalty was incurred due to leakage from the Drywell Vent Radiation Monitor when the gaseous detector breached its shield chamber at a containment pressure of 51.6 psig during pressurization for the ILRT. The 143 SCFH adjustment, accounting for penetration repairs made prior to conduct of the ILRT, was principally due to two leaking containment isolation valve penetrations for the Reactor Water Cleanup (RWCU) System and the Reactor Feedwater (RF) System. <br /><br /> The cause of the Drywell Vent Radiation Monitor failure is attributed to design. Considerable periodic maintenance and testing, involving removal of the detectors from their shield chambers, has been performed over the years that the monitor has been in service. The numerous disassembly and reassembly evolutions resulted in the shield chamber threaded connections becoming degraded, such that when the unit was pressurized, the threaded engagement of the detector retaining bolts in the shield chamber failed. No definitive cause for the RWCU Isolation valve leakage was determined. The RF System leakage was due to normal wear of the soft seats of the two Reactor Feedwater check valves that comprise the penetration boundary. <br /><br /> The Drywell Vent Monitor detector shield housings (gaseous, particulate, and iodine) were retapped and the detectors were bolted into place with larger bolts. New soft seats were installed in the RF check valves. Replacement RWCU Isolation valves were installed. LLRTs were subsequently conducted with satisfactory results.
2981991021 | Cooper Station | 12/14/1991 | 01/13/1992 | 9201230149 | <strong>Diesel Generator Start And ESF Group Isolations During Surveillance Testing Due To Human Miscue</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1991, at 9:38 am, with the plant in Cold Shutdown for a refueling outage, an automatic start of the #1 Diesel Generator and actuation of the Group 2 Isolation (Shutdown Cooling), Group 3 Isolation (Reactor Water Cleanup), Group 6 Isolation (Reactor Building, including Standby Gas Treatment start), and Group 7 Isolation (Reactor Coolant Sampling) occurred. Licensed personnel were in the process of timing two relays to determine the reason for discrepancies in previously reported test results. While performing the surveillance procedure, a step which would block the undervoltage trip of Breaker 1FA was overlooked. Upon actuating the test switch, Breaker 1FA tripped, resulting in the actuations. The Reactor was in cold shutdown, with a Reactor coolant temperature of 150 degrees Fahrenheit. All equipment functioned as designed. <br /><br /> The cause of this event was the inadvertent failure of the licensed operator to perform an action specified by the procedure. A contributing cause was the use of a normal surveillance procedure with a significant number of steps marked "Not Applicable (N/A)". This resulted in the steps to be performed being separated by several pages. <br /><br /> The personnel involved in this event will be counselled, and this event will be covered in Industry Events Training.
2981991022 | Cooper Station | 12/21/1991 | 01/17/1992 | 9201230133 | <strong>Actuation Of The Primary Containment Group 3 Isolation Function When Placing A Partially Filled Reactor Water Cleanup Filter Demineralizer In Service</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1991, at 6:52 p.m., upon opening the inlet valve to the 'B' Reactor Water Cleanup (RWCU) Filter Demineralizer, a partial Group 3 Isolation was received, causing one of the two inlet isolation valves, RWCU-MOV-MO18 to close. The Group 3 Isolation occurred due to actuation of differential pressure flow switch RWCU-DPIS-170B. The setpoint was reached as a result of an apparent flow surge due to the filter demineralizer not being completely full of water. <br /><br /> At the time, the plant was operating at approximately 55 percent power (450 MWe). Power was being increased with control rods and Reactor Recirculation flow during the return to full power operation following the 1991 Refueling Outage.<br /><br /> An investigation revealed that the normally open Waste Sample Pump Discharge Valve to the Condensate Supply (CM) System, CM-AOV-643AV, was closed, preventing proper filling of the Filter Demineralizer. It is postulated that during other processing activities during the 00-0800 shift on December 21, the control switch for CM-AOV-643AV was mis-positioned to CLOSE.<br /><br /> The Filter Demineralizer was filled and vented. The Group 3 Isolation was reset, and at 7:01 p.m., the 'B' Filter Demineralizer was placed in service. In order to preclude a similar error in the future, a switch guard has been installed around the control switch for CM-AOV-643AV on panel LR-28. Further action to be taken includes a discussion of this event with Operations Department shift personnel and a review of Radwaste Procedure 2.5.3.4, RWCU Filter Demineralizer.
3011991001 | Point Beach 2 | 09/29/1991 | 01/24/1992 | 9201290058 | <strong>Failure of Main Steam Isolation Valves to Close</strong><br /><i>Abstract:&nbsp;</i>At 0930 on September 29, 1991, an attempt to shut the Point Beach Nuclear Plant Unit 2 Main Steam Isolation Valves (MSIVs) was made from the control room. Both MSIVs failed to leave the fully open position. An operator was dispatched to the valves and shut them by applying mechanical force to the valve operators. After the valve operators were freed by mechanical force, the valves shut unassisted. Unit 2 had been shut down and cooled down to approximately 325 degrees F for the beginning of its annual maintenance and refueling outage when this event occurred. An extensive investigation into the cause of the failure to close is being performed. The cause for the valves failure to close has initially been attributed to degradation of the valve operators due to corrosion. Steps are being taken to prevent recurrence of the corrosion and return the operators to service. Modifications to the valves and associated operators and changes to the valve maintenance program are being considered. An independent Nuclear Power Department team investigation was also performed to assess MSIV performance and perceptions of valve performance.
3011991002 | Point Beach 2 | 10/14/1991 | 11/08/1991 | 9111140246 | <strong>Steam Generator Tube Degradation</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was shut down for Refueling 17 (U2R17) on September 27, 1991. Leak testing and eddy current examination of the steam generator tubes began on October 4, 1991 and were completed on October 12, 1991. Inspection of the "A" steam generator hot leg revealed 5 tubes degraded greater than or equal to 40% of the wall thickness, 30 tubes with axial indications in the tube-end area, 12 tubes with squirrel indications, and 2 tubes with distorted roll indications. All of these tubes (49 total) were plugged. <br /><br /> In the "B" steam generator, eddy current testing revealed 5 tubes (4 hot leg, 1 cold leg) degraded greater than or equal to 40% of the wall thickness, 20 tubes with axial indications in the tube-end area, and 4 tubes with squirrel indications. All of these tubes (29 total) were plugged. <br /><br /> The results of the 800 psid leak test were satisfactory. The "A" steam generator revealed 5 sleeves, 6 plugs, and one open tube leaking less than 3 drops/min. The "B" steam generator revealed 12 plugs and 8 open tubes leaking less than or equal to 3 drop/min. No corrective actions were required as a result of this test.
3011991003 | Point Beach 2 | 10/10/1991 | 11/08/1991 | 9111140177 | <strong>Containment Hatch Temporary Third Door Blocked Open During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>At approximately 1250 on October 10, 1991, with Unit 2 in refueling shutdown with fuel movement in progress, contractor personnel blocked open the temporary third door to the personnel hatch on the containment 66 foot elevation. This is in violation of Technical Specification Section 15.3.8.1, which states, "A temporary third door on the outside of the personnel lock shall be in place whenever both doors in a personnel lock are open." The door remained open until approximately 1325 when it was shut by a plant employee who recognized that the door was open in violation of Technical Specifications.
3011991004 | Point Beach 2 | 10/08/1991 | 11/15/1991 | 9111220174 | <strong>Containment Isolation Valve Leakage in Excess of Tech Spec Limits</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1991, during the Unit 2 refueling shutdown, Operations Refueling Test (ORT) 67, "Component Cooling Water to and from the Excess Letdown Heat Exchanger, Unit 2," was in progress. This test, as well as the other tests discussed in this report, was being performed to meet the requirements of 10 CFR 50, Appendix J for Type C containment isolation valves. During the initial performance of this seat leakage test, check valve CC-767 failed to shut. Because the valve failed to shut, the required test pressure could not be achieved; therefore, the as-found leak rate could not be quantified. A second attempt was made to pressurize this line. This time the line pressurized to the required pressure. The leak rate measured during this second attempt was within the limits of Technical Specifications Section 15.4.4.III.B.
3011991005 | Point Beach 2 | 11/09/1991 | 12/06/1991 | 9112160037 | <strong>Both Safety Injection Pump Breakers Racked in with RC Temperature Less than 275 degrees F</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1991, a Reactor Coolant System (RCS) heatup was in progress for Unit 2. At approximately 1330, with the RCS at approximately 345 degrees F and 350 psig, it was discovered that both high head safety injection (SI) pump breakers were racked in, making both SI pumps operable. It was determined that this condition existed since November 9, 1991, when the RCS was closed with RCS cold leg temperature >/= 275 degrees F. Having both SI pumps operable under this condition is a violation of Technical Specification Section 15.3.15.B.1. Technical specification 15.3.15.B.1 requires that one SI pump be rendered inoperable by removing (racking out) its supply breaker or by shutting its discharge valve and removing control power any time the RCS is not open to atmosphere and temperature in either or both RCS cold legs is until approximately 1145 on November 11, 1991 during the plant heatup.
3011991006 | Point Beach 2, Point Beach 1 | 12/17/1991 | 01/15/1992 | 9201210228 | <strong>Reactor Trip During Modification Work on D11</strong><br /><i>Abstract:&nbsp;</i>At 1008 on December 17, 1991, Point Beach Nuclear Plant Unit 2 experienced a reactor trip during modification work on DC distribution panel D11. While a cable was being pulled from panel D11 as part of the modification, a cable connected to breaker 32 was displaced by the cable being removed. This movement caused the termination in breaker 32 to loosen and allow its associated cable to become disconnected. This cable supplies power to DC distribution panel D22. Panel D22 supplies power to the Unit 2 "A" train reactor protection circuitry. Panel D22 became deenergized, resulting in a reactor trip on Unit 2 and actuation of the crossover steam dumps on Units 1 and 2. The Unit 1 turbine was manually run back to 73% power to allow closure of the Unit 1 crossover steam dump without exceeding reactor power limitations. The Unit 2 condenser steam dumps were not enabled because of the loss of DC power to the arming circuit. Panel D22 was reenergized at 1037. Unit 1 was returned to full power at 1350. After the electrical connections in panels D11 and D13 were check-tightened, Unit 2 was placed back on line at 0346 on December 18. Unit 2 reached full power at 2245 on December 18, 1991. This event is an actuation of the Reactor Protection System (RPS). Therefore, a four-hour notification to the NRC was made in accordance with 10 CFR 50.72(b)(2)(ii).
3011991007 | Point Beach 2 | 11/10/1991 | 07/14/1992 | 9207220393 | <strong>Violation of Decay Heat Removal Requirements During Steam Generator Crevice Cleaning</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1991, Unit 2 was in its seventeenth annual refueling outage. While performing Wisconsin Michigan Test Procedure (WMTP) 11.19, Revision 7, 'Steam Generator Crevice Cleaning,' RHR pump 2P-10A was secured, leaving the unit without at least one method of decay heat removal in operation as required by Point Beach Nuclear Plant Technical Specification 15.3.1, 'Reactor Coolant System,' Specification A.3.a. (3) which states, 'At least one of the above decay heat removal methods shall be in operation except when required to be secured for testing.' <br /><br /> This event was identified as a potential Technical Specification violation during a special safety inspection conducted by the NRC Resident Inspectors on May 27 through June 14, 1992. wisconsin Electric management personnel discussed this issue with the NRC Resident Inspectors on June 15, 1992, during the NRC exit meeting.
3021991001 | Crystal River 3 | 01/24/1991 | 02/25/1991 | 9103010011 | <strong>Undersized Thermal Overload Devices for High Pressure Injection Recirculation Isolation Valve Motor Operator Due to Personnel Error Results in Operation Outside Des. Basis</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1991, Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 99% of RATED THERMAL POWER and 873 Megawatts Electric Power. At 1625, the "A" Engineered Safeguards (ES) train High Pressure Injection (HPI) recirculation isolation valve, MUV-53, was declared INOPERABLE due to undersized thermal overload elements associated with the motor operator per Section 6.1.2.4 of the Final Safety Analysis Report (FSAR). The determination of INOPERABILITY resulted from a walkdown of the system that was conducted as part of Florida Power Corporation's Electrical Calculation Enhancement Program. The undersized overload elements appear to have been sized based on the Full Load Ampere (FLA) rating for the MUV-53 motor operator found on a very early revision of the relevant motor control center (MCC) drawing. At some point in time, the MCC drawing was revised to indicate a higher FLA rating for the valve motor operator; however, due to personnel error, there was ho corresponding change in the status of the associated overload elements. The undersized elements were replaced with appropriately sized devices on January 25, 1991, thus allowing the plant to exit the relevant Technical Specification ACTION statement. The root cause of the undersized overload elements is not known. Engineering procedures and tracking and documentation systems presently in place will preclude recurrence of such an event.
3021991002 | Crystal River 3 | 01/29/1991 | 02/28/1991 | 9103050366 | <strong>Alternate Off-Site Power Source Transformer Determined To Be Incapable Of Supplying Power Requirements In LOCA Situation Due To Failure To Perform Detailed Modeling</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1991, Crystal River Unit 3 was operating in MODE I (POWER OPERATIONS) at 99% rated power. It was reported to plant management that the UNIT 3 STARTUP TRANSFORMER (SUX) is incapable of maintaining its voltage output above the setpoint of the Second Level Undervoltage Relays (SLURS) under certain Engineered Safeguards (ES) actuation conditions. The SUX is the alternate offsite power source for the ES busses. Calculations also show that the steady state loading on the 4160V winding of the SUX will exceed the Forced Oil and Air (FOA) 65 degree Centigrade rating of the winding during intermediate and large break Loss of Coolant Accident (LOCA) scenarios. <br /><br /> The cause of this inability to meet performance requirements is a failure to anticipate a specific combination of events and conditions in the initial design and subsequent plant modifications. <br /><br /> Immediate and permanent procedure changes were initiated to provide guidance to the licensed operators. A plant modification has been initiated to install a new alternate offsite power supply for the ES busses.
3021991003 | Crystal River 3 | 04/20/1991 | 07/17/1991 | 9107230370 | <strong>Water Intrusion Into Pump Motor Leads to Loss of Circulating Water Pump, Emergency Feedwater Actuation, and a Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1991, Crystal River Unit 3 was operating in MODE 1, at 47% rated thermal power, performing Main Condenser (COND) water box and Circulating Water Pump (CWP) maintenance. Two of the four COND water boxes were out of service. At 0650, CWP-1A tripped, removing cooling from the A COND and the Secondary Services Closed Cycle Cooling Water System (SC) which provides cooling to turbine and generator equipment. CWP-1D continued to supply its main COND with cooling water. <br /><br /> The operators began reducing power to take the turbine off line, then tripped the turbine as many turbine temperature alarms were received. The turbine trip was below the Anticipatory Reactor Trip System bypass setpoint so no automatic reactor trip resulted. After the turbine trip automatic control systems and plant systems responded as designed; however, the configuration resulted in the Anticipated Transient Without Scram Mitigation System Actuation Circuitry (AMSAC) logic detecting Main Feedwater and Reactor Power input signals which met actuation setpoints. AMSAC initiated Emergency Feed Water (EFW) and the operator manually tripped the reactor due to initiation of EFW at power.<br /><br /> This event was caused by water intrusion into the CWP motor during a severe rainstorm. Corrective action will be to provide additional rain protection for the CWPs.
3021991004 | Crystal River 3 | 05/14/1991 | 06/13/1991 | 9106200056 | <strong>Personnel Error Caused Reactor Vessel Level Indication Required for Inadequate Core Cooling To Be Incorrectly Calibrated</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1991, Crystal River Unit 3 discovered that the reactor vessel level instruments required by NUREG 0737 Item II.F.2. were incorrectly calibrated. The vessel level indicators were calibrated to monitor the standpipe level on the vessel head instead of actual vessel level. <br /><br /> The calibration error was caused by Florida Power Corporation (FPC) engineering personnel incorrectly transposing data from a contractor's document to FPC Instrument Data Sheets. The contractor's document did not clearly indicate zero reference elevation. <br /><br /> FPC has recalibrated the reactor vessel level instruments to their proper range. The Calibration Data Sheets and Instrument Data Sheets for safety-related (excluding pressure boundary only level transmitters) and Reg Guide 1.97 level transmitters will be reviewed for proper application of zero reference. FPC engineers will review this event for lessons learned to preclude recurrence.
3021991005 | Crystal River 3 | 05/30/1991 | 07/01/1991 | 9107100016 | <strong>ECCS Pump and Flow Paths Were Secured Due to Valve Packing Leak Resulting a Condition Outside the Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>Crystal River Unit 3 was operating at 100% Full Power on May 30, 1991. Between 2100 and 2107, operators received indications of elevated radiation levels in the Auxiliary Building. Operators located the leakage source by visual observations and by measuring piping surface temperatures. Leakage was originating from the inter-stage packing leakoff connection on a Makeup and Purification system valve. The leak was stopped at 2223 by backseating the valve. <br /><br /> Between 2142 and 2155, operators isolated the leakage source by stopping all makeup flow, closing two valves, and removing control power to the circuit breakers for one of the Makeup/High Pressure Injection Pumps. These actions placed the plant in a condition outside the design basis. This condition existed from 2142 until approximately 2305. At this time, operators opened valves and restored control power to the pump circuit breakers. <br /><br /> Utility licensing personnel are developing detailed guidance regarding High Pressure Injection flow path operability. Plant personnel will replace the failed valve packing during the 1991 maintenance outage.
3021991006 | Crystal River 3 | 06/07/1991 | 10/15/1991 | 9110250208 | <strong>Both Equipment Hatch Airlock Doors Open Simultaneously Due To Loose Door Chain Mechanism</strong><br /><i>Abstract:&nbsp;</i>At 0715 June 7, 1991, while investigating a problem with the Reactor Building (RB) equipment hatch airlock to pass its door interlock and seal test, an operator opened the outer door, entered the airlock and found the inner door slightly open. The period both inner and outer doors were open was less than one minute. The operator immediately exited the equipment hatch, closed the outer door and attempted to remotely close the inner door. At 1345, a repair team entered the equipment hatch and the inner door was again found open. The repair team immediately closed the outer door. Although they were able to close the inner door they were not able to determine what caused the malfunction. At 1835, a second repair team entered the hatch and discovered the inner door swing chain was loose and tightened the chain. At 2145, the airlock was restored to operable status following successful post maintenance testing. Both doors had been open simultaneously three times for approximately one minute each time.
3021991007 | Crystal River 3 | 06/28/1991 | 07/24/1991 | 9107290256 | <strong>Control Air Tubing Failure Causes Entry Into Technical Specification 3.0.3 Once For Recovery and Once for Repair</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1991 Crystal River Unit 3 was operating at 100% rated thermal power and conducting preventative maintenance on the Auxiliary Building (AB) Heating, Ventilation and Air Conditioning System. A maintenance technician noted that air was leaking in the control cabinet which houses solenoid valves for exhaust fan outlet dampers. The AB operator was notified and determined the leak was at the 'T'-connection supplying dampers for Air Handling Fans (AHF) 14A & C. During reconnection of A and C damper tubing, the tubing supplying the B damper slipped off its connector. The damper closed and AHF-14B tripped off. In accordance with procedures, the control room Nuclear operator secured AHF-14D and started AHF-14A & C. The tubing for AHF-14A & C fans blew off its connector and the fans tripped. This left the plant without the required OPERABLE AB exhaust system and required entry into Technical Specification (TS) 3.0.3. Temporary repairs were made and the fans were restarted in approximately 9 minutes. On July 5 while at 100% power, CR-3 voluntarily entered TS 3.0.3 and secured the AB exhaust system, for a total of 2 minutes, to allow repairs of other leaks identified in the control air lines. Causes of the entries into TS 3.0.3 were normal tubing degradation and a voluntary entry to make repairs. Tubing in the system will be replaced during the October 1991 mid-cycle outage.
3021991008 | Crystal River 3 | 09/05/1991 | 10/04/1991 | 9110160002 | <strong>Voltage Adjustment Leads to Inaccurate Control Rod Absolute Position Indication Causing Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, Crystal River Unit 3 was operating at 100% rated thermal power and preventive maintenance on control rod drive power supplies was being conducted. During the course of this maintenance, three power supplies for control rod position indication were adjusted. After the maintenance was completed, several plant computer alarms were received. Based on conflicting computer and main control board indications and computer problems experienced on the previous day, the computer alarms were believed to be invalid. Approximately one hour later, control rod exercise surveillance testing was begun. The performance of this procedure led operators to determine that multiple Absolute Position Indication (API) channels were outside the required 2% accuracy and, therefore, were declared to be inoperable. Technical Specification (TS) 3.0.3 was entered. The Shift Supervisor on Duty (SSOD) ordered the utility electricians to restore the power supplies to the previous "As Found" readings. API operability was restored and TS 3.0.3 exited. Later investigation revealed that guidance provided in the maintenance procedure for measuring power supply voltage was not sufficient to preclude the three power supplies from being improperly adjusted, thereby altering API. The procedure will be revised to ensure proper measurements in the future.
3021991009 | Crystal River 3 | 10/07/1991 | 11/06/1991 | 9111150023 | <strong>High Localized Temperature Causes Diesel Generator Components To Exceed Temperature Ratings</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1991 at 1700, Crystal River Unit 3 (CR-3) determined that several relays and fuses located in the control relay cabinets in the A and B Emergency Diesel Generator (EDG) rooms might experience temperatures above their design ambient temperature rating during diesel generator operation. CR-3 discovered this condition while evaluating NRC Information Notice 89-30, Supplement 1 "High Temperature Environments At Nuclear Power Plants". This design concern does not affect the EDG operability. <br /><br /> The higher temperature in the control cabinets is caused by the proximity of the cabinets to the EDG. This problem was caused by failure of the diesel generator vendor to meet the design specification. To resolve the concerns with the relays and fuses for future operation, actions will be taken to reduce the temperature in the cabinets. To address the currently installed equipment, the fuses will be replaced and an evaluation of the relays will be performed. Two relays from one diesel generator will be replaced. These relays will be tested for temperature effects on aging to determine if additional relays must be replaced.
3021991010 | Crystal River 3 | 10/20/1991 | 11/18/1991 | 9111260245 | <strong>Wiring Problem Causes Transformer Breakers To Open Actuating The Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1991, Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) for a scheduled maintenance outage. At 1443 the breakers for the offsite power transformer opened, disconnecting the engineered safeguards (ES) busses from the offsite power supply. Decay heat cooling was interrupted for less than a minute while the emergency diesel generator (EDG) loaded the ES bus and operators restarted the Decay Heat Pump (DHP). Upon starting the DHP, a purification relief valve lifted causing a drop in pressurizer level. Operators quickly identified the source and isolated the purification system. At 1447, the operators manually energized the remaining ES bus via the CR-3 startup transformer. This event was caused by a pre-existing wire installation which inadvertently applied 115V AC to the CR-3 battery bus. The erroneous wire has been removed. The associated breaker relays have been replaced with less sensitive relays to minimize the possibility of similar events in the future. Information will be provided to all operators concerning this event. The associated Emergency Procedure (EP) will be revised to address restarting the DHP.
3021991011 | Crystal River 3 | 11/04/1991 | 12/04/1991 | 9112090366 | <strong>Discovery of Condition Having Potential to Compromise Long Term Cooling Post-LOCA</strong><br /><i>Abstract:&nbsp;</i>Crystal River Unit 3 (CR-3) was in MODE 5, COLD SHUTDOWN, on November 4, 1991. At 1630 utility personnel determined from analyses that a condition existed which appeared to have the potential to affect long term cooling if a Loss of Coolant Accident (LOCA) occurred due to a break in one of the reactor coolant system cold legs. <br /><br /> The basis for CR-3's operating license includes the post-LOCA long term cooling analyses performed for Babcock & Wilcox plants, which indicates that actions to prevent boron precipitation in the core would not be required until approximately forty days following a cold leg break LOCA. More recent analyses indicated boron precipitation could begin much sooner and actions to prevent boron precipitation would be required within twenty four hours. Procedures for CR-3 already required these actions within twenty four hours. <br /><br /> Since notification of this problem, additional analysis has shown that flow phenomena within the reactor will prevent the boron concentration from increasing to the solubility limit. Therefore, no boron precipitation would occur so no procedural or hardware revisions are required.
3021991012 | Crystal River 3 | 11/14/1991 | 12/16/1991 | 9112300293 | <strong>Procedure Deficiency Leads To Inadvertent Emergency Diesel Generator Actuation During Engineered Safeguards Testing</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1991, at 2349 hours, Crystal River Unit 3 was in mode 5 (Cold Shutdown). During the performance of Engineered Safeguards (ES) surveillance testing, the "A" Emergency Diesel Generator (EDG) was started when an ES signal was inadvertently applied to the diesel start circuitry. The start signal was initiated when the diesel start circuitry was placed back into automatic after surveillance testing while the ES 'A' High Pressure Injection Auto Test Group 2 switch was still in the "Test" position. The Surveillance Procedure (SP) implied that this test switch would spring return out of the test position. By design, the switch does not have a return spring. The SP will be revised to correct the deficiencies discussed in this report. All equipment functioned as designed. This event is being reported under 10CFR50.73(a)(2)(iv).
3021991013 | Crystal River 3 | 11/19/1991 | 12/20/1991 | 9112260129 | <strong>Test Switch Installation Error Causes Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991 Crystal River Unit 3 (CR-3) was in Mode 3 performing start-up surveillance testing. The Steam Driven Emergency Feedwater Pump (SDEFP) was conservatively declared Inoperable (INOP) since a surveillance test had not been performed within 24 hours of entering Mode 3. When a difficulty with a system test associated with the Motor Driven Emergency Feedwater Pump (MDEFP) required its control switch to be placed in pull-to-lock, precluding an automatic start, it too was declared INOP. Technical Specification (TS) 3.0.3 was entered due to both emergency feedwater pumps being declared INOP. This condition existed for 24 minutes. The plant exited TS 3.0.3 as conditions allowed the MDFWP control switch to be returned to normal. Also, CR-3 did not comply with TS 3.0.5 when the emergency diesel generator was later declared INOP. The problem with the test was determined to be an incorrectly installed test switch due to a drawing error. The need to review similar drawings is being evaluated. The test was reperformed acceptably. The SDEFP surveillance test, which was later performed successfully, was not tested within the time interval due to the plant not establishing conditions for pump operation. Failure to comply with TS 3.0.5 was caused by a misinterpretation. This event has been discussed with shift supervisors to provide clarification of TS 3.0.5 requirements.
3021991014 | Crystal River 3 | 11/25/1991 | 12/26/1991 | 9201020226 | <strong>Gasket Failures Cause Feedwater Booster Pump And Main Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On the evening of November 25,1991, Crystal River Unit 3 was operating in Mode 1, power operation, at approximately 20 percent power. Plant startup was in progress. The output breakers were closed at 1716. Just after breaker closure, operators noticed the deaerator level was high and increasing. Efforts to restore proper deareator level were unsuccessful. At 1720 the 'B' Main Feedwater Booster Pump tripped, causing the Main Feedwater Pumps to trip. This caused an anticipatory reactor trip and initiation of Emergency Feedwater. <br /><br /> The Feedwater Booster Pump trip was caused by a false low level signal from the deareator level switch. The false signal resulted from age related failure of two gaskets on two other level switches sharing common sensing lines. Technicians replaced the gaskets with a different type gasket. Technicians also investigated the response of a deareator dump valve which had not operated properly as part of the level control scheme. Instruments were installed to monitor operation of condensate pumps and associated controls during subsequent startup to assure they controlled properly. <br /><br /> Guidance and training is being provided to the operations crew on startup evolutions to assure consistency.
3021991015 | Crystal River 3 | 11/25/1991 | 02/28/1992 | 9203030412 | <strong>Failure to Complete Required Technical Specification Surveillance Prior to Mode Change Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1991, Crystal River Unit 3 (CR-3) began mode ascension from Mode 3 to Mode 1. The shift supervisor believed the monthly reactor protection system surveillances for the anticipatory reactor trips on loss of main feedwater or main turbine were up to date and mode ascension was allowed. However, these surveillances had not been performed on the required schedule. Thus, at 1700, the plant entered Mode 1 in violation of Technical Specification requirements 4.3.1.1.1 and 4.0.4. This condition was discovered during review of the surveillance procedure on November 26, 1991. <br /><br /> This event was caused by personnel error. The responsible shop supervisor incorrectly thought the surveillance was current and so informed the shift supervisor. To prevent recurrence, the Unit Startup and Shutdown Surveillance Plans have been revised to require the status of surveillances to be presented to the nuclear shift supervisor and to require a sign-off by the responsible shop supervisor. Additionally, shop supervisors have been briefed on these changes and their associated responsibilities.
3021991016 | Crystal River 3 | 11/25/1991 | 12/26/1991 | 9201020170 | <strong>Loss of Integrated Control System Power Leads to Emergency Feedwater Initiation and Control System Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1991 at 1108, Crystal River Unit 3 (CR-3) experienced a loss of Integrated Control System (ICS) power. During the event recovery, emergency feedwater actuated due to low steam generator levels. The transient also caused power to increase from 13 percent to 19 percent Rated Thermal Power (RTP) which resulted in entering the region of applicability of Technical Specification 3.2.4, while the Limiting Condition for Operation (LCO) was not met. The emergency feedwater actuation is being reported per 10CFR50.73(a)(2)(iv). Entering the applicability of Technical Specification 3.2.4 while the LCO is not met is a condition prohibited by Technical Specifications and is being reported per 10CFR50.73(a)(2)(i)(B). <br /><br /> The corrective action for this event was to regain control of the Feedwater System, secure the Emergency Feedwater Pumps, reset Emergency Feedwater Initiation and Control, and return power to less than 15 percent RTP. All of these items were done immediately after the event began. All systems acted as expected. There are no further actions planned.
3021991017 | Crystal River 3 | 12/02/1991 | 01/06/1992 | 9201090151 | <strong>Reactor Trip Caused by Feedwater Reduction Due to Nuclear Power Instrumentation Channel Being Selected for Control Which Contained a Failed Detector</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1991 at 2000, Crystal River Unit 3 (CR-3) was commencing a shutdown from 100 percent Rated Thermal Power (RTP) to allow trouble shooting Power Range Nuclear Instrumentation (NI) Channel NI-8, which had previously gone to zero indicated power and tripped Reactor Protection System (RPS) Channel "D". As power was reduced, a pre-existing Quadrant Power Tilt (QPT) began to increase. At 2315, QPT exceeded steady state limit of Technical Specifications and reduction of the nuclear overpower trip setpoint was required. At 0200 on December 3, power was stabilized at 50 percent RTP to allow adjustment of the nuclear overpower trip setpoint. Technicians placed Channel "A" of RPS in bypass and began reducing the overpower trip setpoint. During adjustment of the overpower trip setpoint, an erroneous reactor power signal was sent to the Integrated Control System (ICS), due to NI-8 indicating zero, resulting in feedwater flow decrease to the steam generators and control rod withdrawal. The reactor tripped on high pressure in approximately 30 seconds. Several factors contributed to this event including incorrect operator training on the NI power averager/auctioneer circuit, and lack of cautions in the procedure regarding setpoint adjustment with a failed NI. Plant procedures are being revised to provide cautions and operators will receive training on operation of the averager/auctioneer.
3021991018 | Crystal River 3 | 12/08/1991 | 01/07/1992 | 9201130206 | <strong>Reduction in Reactor Coolant System Pressure Due to Failure of Pressurizer Spray Valve and Associated Position Indication Results in Actuation of Reactor Protection System and Engineered Safeguards</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1991, Crystal River Unit 3 was being returned to power operation. As reactor power was being increased from 11% RATED THERMAL POWER (RTP) to 15% RTP, Reactor Coolant System (RCS) pressure increased to the open setpoint for the Pressurizer Spray Valve, RCV-14. RCV-14 opened; however, the "closed" indicating lamp did not extinguish. On decreasing RCS pressure, RCV-14 did not close, resulting in a continued slow decrease in RCS pressure. Prior to RCS pressure reaching the Engineered Safeguards (ES) actuation setpoint, an operator inappropriately bypassed ES. Shift supervision directed ES out of bypass and ES actuation was initiated. After ES was reset, a plan was implemented which bypassed ES and used High Pressure Injection to raise RCS pressure. RCV-14 was manually isolated, terminating the event. The plant was placed in MODE 5 (COLD SHUTDOWN) and RCV-14 was repaired and tested satisfactorily. Plant Maintenance Procedures are being revised to preclude recurrence of this type of Motor Operated Valve failure. Administrative guidance has been developed on the bypassing of ES actuation signals.
3041991001 | Zion 2 | 01/04/1991 | 02/01/1991 | 9102060347 | <strong>Inoperable Safety Injection Pumps Due to Low Recirculation Flow</strong><br /><i>Abstract:&nbsp;</i>In accordance with Technical Specification 4.8.2.A.1, while Unit 2 was in the Power Operations Condition (Mode 1 - 99% Power), the monthly surveillance was performed for the Unit 2 Safety Injection pumps on January 4, 1991. Testing was conducted in accordance with Periodic Test 2A, entitled "Safety Injection System Tests." Both the 2A and the 2B Safety Injection pumps failed to satisfy the minimum recirculation flow required for Periodic Test 2A. The 2A and the 2B Safety Injection pumps were declared inoperable and the Limiting Condition for Operation as described in Technical Specification 3.8.2.D was entered. Unit 2 was brought to the Hot Shutdown Condition (Mode 3) within the required four (4) hours. Both Unit 2 Safety Injection pumps were shown to be operable within the allowed forty eight (48) hours thus terminating the Limiting Condition for Operation.
3041991002 | Zion 2, Zion 1 | 03/21/1991 | 01/19/1995 | 9501270353 | <strong>System Auxiliary Transformer Deluge and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 0930, during the performance of Operating Periodic Test (PT)-211, Wet Pipe Sprinkler System Test, the Unit 2 Unit Auxiliary Transformer (UAT) and the Main Power Transformer (MPT) were inadvertently deluged. At 1309, another deluge occurred on the System Auxiliary Transformer (SAT) causing the SAT to trip. The buses fed from the SAT automatically transferred to the UAT. The 2A feedwater pump tripped when the SAT tripped causing a Reactor Trip on Lo-Lo Steam Generator Level. When the main generator tripped, one diesel generator (DG) was Out of Service (OOS) for maintenance so an essential bus was not automatically re-energized. A Generating Station Emergency Plan (GSEP) Unusual Event (EAL 3D) was declared at 1335 and both units were started toward Cold Shutdown. The event was caused by spurious actuation of the Unit 2 transformer's Fire Protection deluge system and the improper positioning of the Fire Protection deluge nozzles. During this event all failures and actions taken were within the bounds of the Technical Specification limiting conditions for operation. Various corrective actions were developed and implemented to address the concerns that were raised as a result of this event.
3041991003 | Zion 2 | 06/08/1991 | 07/08/1991 | 9107120064 | <strong>2A AFW Pump Turbine Trip Valve was Found Closed Due to Procedure Step Being Performed Out of the Normal Sequence</strong><br /><i>Abstract:&nbsp;</i>At 1130 hours on June 8, 1991, the Licensed Shift Supervisor (LSS) observed the "Auxiliary Feedwater Pump 2A Turbine Trip Valve Closed" annunciator being lit. He questioned the reason for it being lit since at that time, Unit 2 was in Mode 3, during a unit startup, with the Reactor Coolant System at 2235 psig and 542 degrees F. The Auxiliary Feedwater (AFW) SJ! System was in split header configuration. Split header configuration provides a separate flow path from each of the motor driven AFW pumps to the steam generators. An Equipment Attendant (EA) was promptly dispatched to the pump and the turbine steam supply trip valve, 2MS-1063, was found closed. The valve was then opened and latched without any problems and the annunciator cleared. During the time that the trip valve was closed, the steam supply flowpath was isolated and the steam driven AFW pump was not capable of being powered from its steam supply. Therefore, the 2A AFW pump was inoperable.<br /><br /> The cause of the valve being closed was due to a step in General Operating Procedure (GOP)-1, Plant Heatup, being incorrectly performed. <br /><br /> The safety of the plant was not degraded. Corrective Actions included opening the 2A AFW Turbine Trip Valve, reviewing the event and the AFW Technical Specifications with the Operating Department and adding instructions to GOP-1 to verify the trip valve annunciator clears.
3041991004 | Zion 2 | 06/11/1991 | 07/11/1991 | 9107160290 | <strong>Unit 2 Reactor Trip Due To A Failed Capacitor In The Steam Generator Automatic Feedwater Control Circuitry</strong><br /><i>Abstract:&nbsp;</i>On June 11 1991, during Unit 2 plant startup, several unsuccessful attempts were made to use the bypass Feedwater Regulating Valves (FRV) SJ! in the automatic mode to control steam generator (S/G) level JO! while the unit operators were aligning the main feedwater pumps. The main feedwater system SJ! was successfully aligned with the bypass FRVs in the manual mode and the main turbine speed was increased to 1800 rpm. After the main generator was synchronized to the grid, the unit operators attempted to place the main FRVs in automatic and to close the bypass FRVs in manual. The main FRVs filled the S/Gs to 70% which then generated a turbine trip signal which then generated a reactor trip because reactor power was greater than 10%. <br /><br /> This event was caused by a failed capacitor in the power supply circuitry of the S/G level controller. Contributing to this event was a history of problems with leaking bypass FRVs. This lead to the incorrect diagnosis by the unit operators that the leaking bypass FRVs were causing the S/G level control problems. During this event all actions taken were within the bounds of the Technical Specification Limiting Conditions for Operation and there was no safety significance to this event. Corrective actions included determining the root cause of the capacitor failure, reviewing the S/G level control system to determine what information should be provided to the unit operators, identifying recurring Feedwater System problems, and verifying the calibration of the bypass FRV controller.
3041991005 | Zion 2 | 09/22/1991 | 10/22/1991 | 9110290243 | <strong>Missed Post Maintenance Verification Test of 2FCV-PR19B Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 09/22/91 at 1600, the Licensed Shift Supervisor (LSS) incorrectly instructed the unit operator to perform Periodic Test (PT)-300, Containment Isolation Valve Stroke Time Verification, on the train A reactor leak detector air space isolation sample valve IL!, 2FCV-PR19A, instead of the train B sample valve, 2FCV-PR19B. This test was being performed for post-maintenance verification. The LSS reviewed and approved the completed PT-300, signed the "tests completed" and "approved completion" sections of the maintenance work request, and completed the PT-14, Inoperable Equipment Surveillance, paperwork for 2FCV-PR19B. On 09/24/91, the surveillance co-ordinator, during review of completed PT's, identified that the PT-300 was completed on the wrong sample valve. PT-300 was performed on 2FCV-PR19B and the valve stroked well within the maximum allowable stroke time. <br /><br /> This event was caused by a personnel error on the part of the LSS who instructed the unit operator to perform post maintenance verification on the wrong sample valve. This event had minimal safety significance. <br /><br /> Corrective actions included counselling the LSS, reviewing the event with all Operating department personnel, reviewing the Self Check program with the Operating department, and performing a Human Performance Evaluation System (HPES) review on the Inoperable Equipment process to identify what improvements need to be made.
3041991006 | Zion 2 | 09/30/1991 | 10/30/1991 | 9111050215 | <strong>Unit 2 Pressurizer Cooldown Rate in Excess of 200 degrees F/hr</strong><br /><i>Abstract:&nbsp;</i>On 9/30/91 at 0328 hours, the unit operators were performing General Operating Procedure (GOP)-4, Plant Shutdown and Cooldown. The unit operators were attempting to cool down the pressurizer while at the same time take the pressurizer to a water solid condition using charging flow greater than letdown flow to increase the Reactor Coolant System (RCS) inventory. The high rate of charging flow resulted in difficulty in controlling RCS pressure during this evolution. Operator verification subsequent to this event showed pressurizer liquid space temperature decreased from 421 F at 0328 to 214 F at 0428. This is in excess of Technical Specification 3.3.2.D cooldown limit of 200 F/hour.<br /><br /> This event was caused by inadequate procedural guidance. An evaluation determined that the pressurizer structural integrity was not compromised by the high cooldown rate. The health and safety of the public was not affected. Corrective actions include procedure changes to GOP-4, enhanced classroom and simulator training on pressurizer cooldown, and reviewing the event with the operating department.
3051991001 | Kewaunee | 02/01/1991 | 04/18/1991 | ML11166173 | <strong>Securing of Pressure Relief Path in the Turbine Driven Auxiliary Feedwater Pump Room Results in Potential Inability to Meet High Energy Line Break Criteria</strong><br /><i>Abstract:&nbsp;</i>At 1505 CST on February 1, 1991 with the plant at 100% power, a concern was identified regarding the ability to meet design basis requirements for steam exclusion in the event of a high energy fine break (HELB) at KNPP. During a self initiated Safety System Functional Inspection, it was discovered that a blow-out panel previously installed in a penetration of the wall in the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) room did not appear to be in a condition that would meet its original design intent. This opening was designed to provide a relief path to limit the pressure increase in the TDAFWP room following a postulated steam release from the steam supply piping to the TDAFWP. If pressure relief were not provided, overpressurization of the TDAFWP room could occur. This overpressurization could result in a release of steam to adjacent rooms (steam exclusion areas) which contain safety-related electrical equipment. <br /><br /> The as-found condition of the TDAFWP room opening indicated that a modification had been made to the opening which defeated the relief capability. Based on the as-found condition and the information available at the time, it was concluded that the blow-out panel could not perform its design function and the plant was in a condition outside of its design basis.<br /><br /> The root cause of the event was a failure to perform an adequate safety evaluation to support a modification performed in 1978. Corrective actions include but are not limited to reopening the penetration to allow pressure relief capability and implementing a design change modification to return the penetration to its design condition.
3051991002 | Kewaunee | 02/20/1991 | 02/15/1993 | ML11188040 | <strong>Safety System Functional Inspection Discovers that the Safeguards Bus Undervoltage Protection is Outside of its Design Basis as a Result of an Inadequate Design Evaluation</strong><br /><i>Abstract:&nbsp;</i>At 1520 on February 20, 1991, with the plant at 100% power, it was determined that the second level undervoltage trips of the safeguard buses did not meet their design basis. The second level undervoltage trip isolates the 4160 volt safeguard buses from offsite power if bus voltage drops below 92.5% of nominal voltage for more than 5 minutes. Once isolated, the buses would be loaded onto their respective diesel generator. <br /><br /> The deficiency was identified during a self-initiated safety system functional inspection of the 480 volt and 4160 volt supply and distribution systems. The inspection identified a concern if a safety injection signal were to occur concurrent with an undervoltage condition. Under these circumstances there may have been insufficient voltage to actuate the contactors in the control circuitry for the safety related loads on the 480 volt motor control centers. <br /><br /> This event was a result of an inadequate design evaluation. Personnel involved in the design process did address this issue during the design of the undervoltage trip in 1981. However, due to a misinterpretation of pre-operational test results, they concluded Kewaunee was not susceptible to this type of failure. <br /><br /> Modifications were made during the 1991 refueling outage to correct the undervoltage monitoring system inadequacies. WPS has determined that additional modifications are not warranted at this time. The benefit of additional design enhancement modifications will be evaluated when field verification of the DAPPER load flow model is completed.
3051991003 | Kewaunee | 02/28/1991 | 04/01/1991 | ML11166172 | <strong>Inadequate Review of Fire Penetration List by Fire Watch Patrol Results in Violation of Technical Specification 3.15.f</strong><br /><i>Abstract:&nbsp;</i>At 0245 on March 3, 1991, and at 0146 on March 4, 1991, with the plant at 95% power, it was discovered that hourly fire watch inspections had not been performed as required by Technical Specification 3.15.f. The specification requires that a hourly fire watch inspection be performed, on at least one side of a penetration, if the fire barrier is not intact. The non-performance of inspections was discovered by a contract Security Shift Captain during review of the security computer personnel access printouts.<br /><br /> The March 3, 1991, review revealed that an area in which a penetration fire barrier was not intact had not been inspected by the assigned Security Officer during the time periods of 1300-1500 on February 28, 1100-1300 on March 1, and 0900-1100 on March 2, 1991. <br /><br /> The March 4, 1991, review revealed that an area in which a penetration fire barrier was not intact had not been inspected during the time period of 1000-1100 on March 3, 1991. The root cause of the event was determined to be inattention to detail by the two security officers involved. <br /><br /> Corrective actions will include reformatting of the open/degraded Fire Penetration List to group affected penetrations with the associated area; and performing a review of the Fire Watch Surveillance Procedure and revising the procedure as appropriate.
3051991004 | Kewaunee | 04/15/1991 | 05/15/1991 | ML11166173 | <strong>Communication Error Results in Actuation of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>This report describes the inadvertent closure of two containment isolation valves and actuation of several dampers in the auxiliary building special ventilation system. The valves and dampers are considered engineered safety features. The event occurred at 2123 on April 15, 1991, with the plant in refueling shutdown, during performance of design change request (DCR) procedure 2417-02. DCR 2417 was implemented to relocate non-safety related 120 VAC loads from the existing safety related distribution panels to new non-safety related panels. The event occurred when an Auxiliary Operator isolated a temporary power supply to a safety related distribution panel prior to connecting it to its normal power supply. This de-energized the panel and resulted in the actuations. <br /><br /> This event occurred as a result of a communication effort. The on duty Control Room Supervisor (CRS) had directed the Nuclear Auxiliary Operator (NAO) to perform the applicable steps in DCR procedure 2417-02. A misunderstanding between the CRS and the NAO resulted in the Auxiliary Operator performing the step that isolated the temporary power supply to the distribution panel out of sequence. <br /><br /> Discussions emphasizing the importance of clear communication were held with the individuals involved. Furthermore, this report will be included as part of the required reading material for all operators. <br /><br /> Since the event did not place the plant in an unanalyzed condition, this event had no affect on the health and safety of the public.
3051991005 | Kewaunee | 04/28/1991 | 05/28/1991 | ML11166173 | <strong>Intergranular Attack and Intergranular Stress Corrosion Cracking Results in Both Steam Generators Being Categorized as C-3</strong><br /><i>Abstract:&nbsp;</i>At 1930, on April 28, 1991, with the plant in refueling shutdown, eddy current inspection, sleeving, and plugging of the Steam Generator (SG) tubes were completed for the 1991 refueling outage. The inspection found that 84 tubes in SG A and 91 tubes in SG B met the Kewaunee Nuclear Power Plant (KNPP) Technical Specification (TS) definition of defective. Since the number of defective tubes exceeded 1 percent of the total number of tubes inspected in each steam generator, both SGs were categorized as C-3. As required by KNPP TS, the Nuclear Regulatory Commission (NRC) was notified within four hours of the SGs being classified C-3. <br /><br /> The majority of the defects were likely caused by outside diameter intergranular attack and outside diameter intergranular stress corrosion cracking (IGA/IGSCC). <br /><br /> All defective tubes were plugged or sleeved. Furthermore, as a preventative measure 59 tubes were plugged, and 219 tubes were sleeved. To slow the effects of outside diameter IGA/IGSCC and reduce the probability of further tube degradation, KNPP continues to implement its program of on-line secondary system boric acid addition, low power soaks with boric acid in the secondary system, crevice flushing, sludge lancing, and annular searches. <br /><br /> In addition 150 tubes in the A SG and 246 tubes in the B SG were unplugged and sleeved. This decreased the overall equivalent plugging percentage from 12.2 percent to 9.1 percent for the 1991-1992 operating cycle.
3051991006 | Kewaunee | 05/29/1991 | 06/28/1991 | ML11166174 | <strong>Improper Use of Control Room Supply Sheet Results in an Inadvertent ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1991, at 1027 CDT, with the plant at 100 percent power, the condenser air ejector radiation monitor, R-15, failed downscale. As designed, the failure caused the steam generator blowdown isolation valves and the blowdown sample isolation valves to close. <br /><br /> The downscale failure of R-15 and subsequent associated Engineered Safeguards Feature actuation was caused by the misinterpretation of a note on the control room supply sheet. The Nuclear Control Room Operator used the control room supply sheet as guidance to determine the applications of replacement bulbs. A handwritten note on the control room supply sheet was used to determine a replacement bulb. As a result, an incorrect replacement bulb was chosen and when it was installed it caused a fuse to open in the R-15 control room drawer, which in turn caused R-15 to fail downscale. <br /><br /> The intent of the control room supply sheet is to help locate replacement bulbs from storage and to assist in reordering when supplies are low. The supply sheet will be updated and this LER will be placed in required reading for operations personnel.
3051991007 | Kewaunee | 07/10/1991 | 08/09/1991 | ML11166174 | <strong>Technical Specification Surveillance Period Exceeded Due To Human Error</strong><br /><i>Abstract:&nbsp;</i>At 1300 hours on July 10, 1991, with the plant at 100% power a routine internal quality assurance audit determined that item 8B of Technical Specification Table 4.1-1 had been violated. Item 8B requires monthly (31 days) testing of the first level undervoltage trip of the safeguard buses. Technical Specification 4.1.C provides a 7 day grace period in which to perform the test. Contrary to this requirement, the audit found a 39 day period between December 20, 1990 and January 28, 1991 in which the second level undervoltage trip was not tested. <br /><br /> The event occurred as a result of human error. The Electrical Maintenance Supervisor had originally scheduled the test for Friday, January 25, 36 days between tests. However due to a scheduling conflict, the test was rescheduled until the next working day (Monday, January 28). The Electrical Maintenance Supervisor stated that had he realized that the surveillance period was ending, he would have scheduled the test for January 26. When the test was performed on January 28, the setpoints were found within all Technical Specification limits.<br /><br /> The individual was counseled on the importance of ensuring compliance with TS. Furthermore this LER will be made required reading for all Plant Group Supervisors and Department Heads.
3051991008 | Kewaunee | 09/10/1991 | 10/10/1991 | ML11166175 | <strong>Inadequate Resistance Temperature Detector Response Time Results in Potential Inability to Meet High Energy Line Break Criteria</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1991, at 1400, with the plant at 99% power Wisconsin Public Service Corporation determined that a condition existed at the Kewaunee Nuclear Power Plant that was outside the design basis of the plant. The Steam Exclusion System is designed to prevent the steam environment that will exist following a High Energy Line Break (HELB) from entering adjoining areas which contain equipment necessary to mitigate the event. The ventilation system design for the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) room uses ventilation dampers that will close to isolate the room following a HELB in the room. The sensors used to initiate the damper closure are Resistance Temperature Detectors (RTDs) that sense temperature rise in the room following a HELB. A concern regarding the sensor response time has been identified. The as-found condition could allow the steam environment in the TDAFWP room following a HELB to affect equipment in the adjoining rooms that is required to mitigate the event.<br /><br /> The cause of the events appears to be a failure to consider the RTD response time during the original construction of the plant. Corrective actions include but are not limited to closing the steam exclusion dampers to limit the amount of steam released to the adjoining areas and initiating a design change to enable the return of forced air cooling to the TDAFWP room.
3051991009 | Kewaunee | 09/09/1991 | 11/15/1991 | ML11166175 | <strong>Error in Safety Injection Accumulator Level Indication Caused by Not Compensating For Effects of Nitrogen Density During Calibration</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1991, with the plant at 99% power, an error in the calibration of the safety injection accumulator level transmitters was identified. The error was caused by the failure to consider the effects of the nitrogen density at 750 psig on the ITT Barton Model No. 384/352 differential pressure transmitters used for level measurement. The level transmitters are used to measure liquid level in the accumulators over a twenty-eight (28) inch span and provide an indication of 0-100% level. Without compensation for the effects of nitrogen density, at 750 psig, the level error, which is linear over the measured span, is 5.52% high at 0% actual level and 0% error at 100% actual level. <br /><br /> The root cause for the event could not be conclusively determined. The methodology for determining the calibration reference values was developed prior to initial plant startup and had remained unchanged until the identification of this event. <br /><br /> As an interim measure, to ensure that the Technical Specification for minimum accumulator water volume is satisfied, the low level alarm setpoints have been set at 6.5% above the level required by the specification. During the 1992 refueling outage the transmitters will be recalibrated to compensate for the level error due to the nitrogen density. The decision to not recalibrate the transmitter during at-power conditions was based on the prudency of maintaining personnel radiation exposure as-low-as-reasonably-achievable (ALARA).
3051991010 | Kewaunee | 10/12/1991 | 11/11/1991 | ML11166175 | <strong>Unit Trip Due To Inadequate Non-Safeguard Breaker Coordination</strong><br /><i>Abstract:&nbsp;</i>At 1400 CDT on October 12, 1991, with the plant at full power, a reactor/ turbine trip occurred returning equipment to service during the implementation of Preventive Maintenance Procedure (PMP) 38-10, "DC Supply and Distribution (EDC) 20 KVA Inverter Maintenance." During this process 125 VDC Distribution Cabinet BRD-103 was de-energized as a result of inadequate non-safeguard breaker coordination. This de-energization caused the feedwater regulating valves (FW-7A and B) to close, resulting in a trip signal from the subsequent steam flow-feedwater flow mismatch coincident with low water level in steam generator A. As expected, the auxiliary feedwater pumps started, which was an ESF actuation, in response to plant conditions.<br /><br /> A main contributor to this event was inadequate coordination between the 300 amp breaker which supplies 125 VDC Distribution Cabinet BRD-103 and the 200 amp breaker from BRD-103 to a non-safeguard inverter. To prevent recurrence the magnetic trip settings of the respective breakers were adjusted accordingly. In addition, any modifications necessary to further ensure proper coordination of non-safeguard DC breakers will be scheduled for the 1992 refueling outage. <br /><br /> The plant safety systems responded as designed and the operators followed appropriate recovery procedures for plant stabilization. In addition to the plant trip and corresponding ESF actuation, a Technical Specification required instrument channel check was not performed during recovery activities on the shift immediately following the plant trip. <br /><br /> This event is being reported as required by 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(2)(i).
3051991011 | Kewaunee | 10/23/1991 | 11/22/1991 | ML11166175 | <strong>Reactor Protection System Overpower and Overtemperature Delta-T Trip Setpoint Found Less Conservative Than Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>At 1000 on October 23, 1991, with the plant at 100 % power, it was determined that during the period of May 10-17, 1991, three of the four channels for Reactor Coolant System (RCS) Overtemperature and Overpower (OT/OP) Delta-T protection had reactor trip setpoints at values less conservative than that required by the Technical Specifications (TS). <br /><br /> During the 1991 refueling outage a number of previously plugged steam generator (S/G) tubes were restored to service by sleeving the defective tubes. Eddy Current testing identified other tubes which required plugging. However, the net result was an increase in area for RCS flow. This was confirmed on May 17, 1991, by RCS flow testing which indicated a 1.4% increase from the previous fuel cycle flow. The increased flow caused a corresponding decrease in the RCS Delta-T at rated power. The Technical Specifications require that the OP Delta-T and OT Delta-T trip setpoints be </= 1.10 and </= 1.11, respectively, of indicated Delta-T at rated power. On October 23, 1991, following the review of the newly determined rated power Delta-T values, it was discovered that during the period of May 10 (plant startup) to May 17, 1991, three of the four channels had OP/OT Delta-T trip setpoints which were an average of 0.56% less conservative than the Technical Specifications limits. <br /><br /> The event was caused by the personnel involved in the SG tube recovery effort failing to anticipate the magnitude of the RCS flow increase and the required change to OP/OT Delta-T trip setpoints. To preclude a recurrence of this event, the Instrument and Control Group is developing a procedure to conservatively reset several Reactor Protection Setpoints prior to startup from a refueling outage. The trips to be reset will include OP/OT Delta-T, Intermediate Range HI Flux, and Power Range HI Flux.
3051991012 | Kewaunee | 12/03/1991 | 01/03/1992 | ML11166176 | <strong>Unmarked Steam Exclusion Doors to Turbine Driven Auxiliary Feedwater Pump Room Resulted in Potential Inability to Meet High Energy Line Break Criteria</strong><br /><i>Abstract:&nbsp;</i>At 0935 on December 4, 1991, with the plant at 100% power, Wisconsin Public Service Corporation determined that for a period of approximately one-half hour on December 3, 1991, the Kewaunee Nuclear Power Plant had been in a condition outside of the design basis for the Steam Exclusion System. The Steam Exclusion System is designed to prevent the steam environment that will exist following a High Energy Line Break from entering adjoining areas which contain equipment necessary to mitigate the event. It was determined that during the time period of 1058 - 1115 on December 3, contracted welders ran a welding cable through the two doorways for the Turbine Driven Auxiliary Feedwater Pump Room. The cable would have prevented closing of the doors which are part of the steam exclusion boundary for the adjoining areas. The cable was removed and the two doors closed by 1129 on December 3. <br /><br /> The event occurred because the doors were not identified as steam exclusion boundaries. Signs with the appropriate wording have been permanently affixed to the doors which should prevent a recurrence of this type event.
3051991013 | Kewaunee | 12/06/1991 | 01/06/1992 | ML11166176 | <strong>Procedural Deficiency Results in Closure of Steam Generator Blowdown Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>This report describes an unplanned automatic actuation of the steam generator blowdown valves and steam generator blowdown sample valves, engineered safety features (ESF). At 0924 on December 6, 1991 with the plant at 100% power, the valves closed and isolated steam generator blowdown and blowdown sampling. The valves closed as designed on a high radiation signal from the steam generator blowdown monitor (R-19). The high radiation signal was generated during the monthly source check of R-19 when a nuclear control operator in training, directly supervised by a licensed operator, positioned the "Operation Sector Switch" from "Operate" to "Check Source". As expected, an upscale meter response was observed. However, the operator in training did not return the "Operation Selector Switch" to the "Operate" position prior to reaching the R-19 nominal high alarm setpoint (450 cpm) thus causing the unplanned ESF actuation. Past practice was to hold the "Operation Selector Switch" in the "Check Source" position only long enough to observe a response to the source and then return to the "Operate" position.<br /><br /> To prevent recurrence of this type event, operations will review and revise their procedures as necessary to ensure the procedures accurately instruct operators on the potential of reaching a high alarm setpoint when performing source checks.
3061991001 | Prairie Island 2, Prairie Island 1 | 03/27/1991 | 04/26/1991 | 9104300074 | <strong>Discovery That Certain Piping Inspections Are Not Being Made As Required By ASME Section XI Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 097%. ON MARCH 27, 1991, BOTH UNITS WERE OPERATING AT FULL POWER. SP1168.8, COOLING WATER OPERATIONAL PRESSURE TEST, WAS UNDERGOING REVIEW IN PREPARATION FOR ROUTINE PERFORMANCE OF THE PROCEDURE. DURING THE REVIEW, THE SYSTEM ENGINEER NOTICED THAT A PORTION OF THE REQUIRED TESTING WAS MISSING FROM THE PROCEDURE. THE PROCEDURE REQUIRES A WALKDOWN INSPECTION OF COOLING WATER PIPING IN UNIT 1 CONTAINMENT, BUT DOES NOT REQUIRE INSPECTION OF COOLING WATER PIPING IN UNIT 2 CONTAINMENT, AS IT SHOULD. ON MARCH 28, 1991, THE ASME SECTION XI TEST COORDINATOR REVIEWED THE PROGRAM FOR SIMILAR DEFICIENCIES AND FOUND THAT INSPECTION OF AUXILIARY FEED WATER PIPING IN UNIT 2 CONTAINMENT HAD ALSO BEEN OMITTED. THESE TESTS ARE REQUIRED TO BE PERFORMED EVERY 3 1/3 YEARS. AFTER DISCOVERY, WORK REQUESTS WERE WRITTEN TO PERFORM THE OMITTED INSPECTIONS. THESE INSPECTIONS WERE COMPLETED ON APRIL 5, 1991; NO PROBLEMS WERE IDENTIFIED. CAUSE OF THE EVENT WAS PERSONNEL ERROR; THERE WAS INADEQUATE REVIEW OF PROCEDURES. THE PROCEDURE FOR ADMINISTERING THE ASME SECTION XI PROGRAM WILL BE REVISED TO INCLUDE THE REQUIREMENT FOR A SECOND LEVEL REVIEW OF ALL PROGRAM ADDITIONS, DELETIONS AND INTERPRETATIONS.
3091991001 | Maine Yankee | 01/08/1991 | 04/08/1991 | 9104150326 | <strong>Plant Shutdown Due To Failure Of Manual Containment Integrity Valve</strong><br /><i>Abstract:&nbsp;</i>At 2122, on January 8, 1991, Maine Yankee commenced a plant shutdown from 19% reactor power as required by Technical Specifications due to the failure of a manual containment integrity boundary valve (MS-70). During a plant startup, stem and yoke bushing thread damage prevented shutting MS-70, a steam line bypass isolation valve. While attempting on-line repairs which involved replacing the damaged yoke threads, the stem and disc separated and the stem was ejected. It was subsequently determined that the stem had failed previously but this failure was not discovered prior to the attempt to repair the valve. A plant cooldown was required to replace the valve and restore the containment integrity boundary. <br /><br /> The valve failure caused a loss of the containment integrity barrier external to the containment. However, the internal membrane containment integrity barrier, formed by the steam generator was not breached. The previous valve stem failure did not affect valve closure and, therefore, it remained operable as an isolation valve. However, the stem and yoke bushing thread damage that occurred on January 8, prevented the valve from shutting and acting as a containment barrier. Compensatory measures to isolate MS-70 as allowed by the Technical Specification remedial action were implemented.<br /><br /> The valve which failed and one similar steam line bypass isolation valves were replaced and the third valve cleaned and lubricated. The Plant Manager implemented additional administrative controls to govern maintenance activities that can not be adequately isolated by the administrative tagging system. Changes to the administrative tagging procedure and discrepancy reporting procedure to ensure adequate reviews for activities performed without the use of tagging controls are scheduled to be implemented by July 1, 1991.
3091991002 | Maine Yankee | 01/30/1991 | 03/06/1991 | 9103130223 | <strong>Emergency Diesel Generator Testing</strong><br /><i>Abstract:&nbsp;</i>Maine Yankee Technical Specifications require a monthly test of each emergency diesel generator. Maine Yankee's practice had been to load the diesels for two hours at maximum expected KW loads and the continuous rating specified in the Final Safety Analysis Report. This loading was found to not reflect the expected KVAR loads. Both emergency diesel generators were subsequently tested at the maximum KVA load with acceptable results. <br /><br /> This is an informational report.
3091991003 | Maine Yankee | 02/14/1991 | 03/15/1991 | 9103270257 | <strong>Plant Shutdown Due To Reactor Coolant Leakage Through The 10 Path Transfer Device</strong><br /><i>Abstract:&nbsp;</i>At 1210, on February 14, 1991, control room operators commenced a plant shutdown required by Technical Specifications due to reactor coolant (RC) leakage through an incore instrument (ICI) assembly at the 10 path transfer device. Located above the ICI assembly seal table, the 10 path transfer device is used to insert a moveable fission chamber into the core through calibration tubes which traverse the center line of combination ICI assemblies. The leak was traced to the calibration tube of ICI assembly number 2. The plant was shut down to repair the leak and cold shutdown condition was reached at 0906 on February 15, 1991. <br /><br /> Repair of the leaking ICI assembly was completed by cutting the assembly just above its seal housing and installing a cap with gasket onto the seal housing. The cap was then seal welded to the seal housing as a secondary measure for leak tightness. <br /><br /> A visual inspection of ICI assembly number 2 is planned when it is removed during Maine Yankee's Cycle 12/13 refueling shutdown as part of an effort to determine a failure mechanism.
3091991004 | Maine Yankee | 02/20/1991 | 03/22/1991 | 9103260318 | <strong>Emergency Feedwater Control Wiring Separation Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1991, Maine Yankee determined that a wiring separation discrepancy existed in the emergency feedwater (EFW) pump control circuit. Due to the discrepancy, Maine Yankee elected to declare one train of the EFW system inoperable. The Remedial Action for the applicable Technical Specification was entered, which allowed up to 7 days to correct the problem. Work was commenced immediately to attain proper wiring separation. On February 23, the problem was corrected, and the Remedial Action was exited.
3091991005 | Maine Yankee | 04/29/1991 | 10/25/1991 | 9111010029 | <strong>Plant Trip on Main Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1991, Maine Yankee tripped from 100% power when one of the two main output transformers developed an internal fault. The electrical fault in the main transformer X-1A resulted in a generator primary relay trip of the main turbine. The Reactor Protective System tripped the reactor on Loss of Load. Protective relaying and the automatic transfer to reserve power performed as designed. <br /><br /> The transformer fault caused arcing at the neutral bus beneath the main generator. The arcing damaged hydrogen lines and the neutral leads bushings and resulted in a hydrogen fire beneath the main generator. The plant declared an Unusual Event due to the fire, which was allowed to burn itself out over a 3 hour period. <br /><br /> The damaged transformer has been replaced with an on-site spare (X-1S). The main generator repairs were completed and the plant resumed operation on May 31, 1991. <br /><br /> Two transformer failures (without fires) occurred previously at Maine Yankee on August 13, 1988 (X-1A) (LER-88-006), and on August 31, 1978 (X-1B). <br /><br /> The root cause of the transformer fault was an internal fault to ground. The transformer (X-1A) had been rebuilt following the fault in 1988 and had been in service for approximately 9 months.
3091991006 | Maine Yankee | 05/30/1991 | 07/01/1991 | 9107080123 | <strong>Plant Trip Due To Low Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>At 1754 on May 30, 1991, with the reactor at 12% power, an automatic reactor trip occurred due to actuation of the Reactor Protective system. Level in steam generator number one dropped below the low steam generator water level trip setpoint when main feedwater pump (P-2A) tripped on low suction header pressure. The feedwater pump tripped when the main feedwater regulating valves had been opened an excessive amount allowing a large inflow of feedwater. <br /><br /> During this event, standby main feedwater pump P2B did not run and standby condensate pump P27C did not automatically start when they should have. Subsequent testing and evaluation found pressure switch PS 1305B, which provides an auto trip signal to P2B, to be defective. A replacement pressure switch was installed and tested. <br /><br /> Pressure sensing switches associated with main feedwater pump auto start and auto trip functions were tested and calibrated. Pressure sensing lines were blown down. Pressure sensing equipment and circuitry associated with P27C auto start functions were inspected and functionally checked. <br /><br /> An attachment providing enhanced guidance for operating the feedwater station during plant startup at low power will be added to the plant startup procedure. During the next refueling outage, February 1992, a modification to the main feedwater regulating system will include installing new main feedwater regulating valve controllers.
3091991007 | Maine Yankee | 06/25/1991 | 11/04/1991 | 9111120215 | <strong>Component Cooling Valves Not Locked Open</strong><br /><i>Abstract:&nbsp;</i>During normal operation at 100% power, on June 25, 1991, it was determined that the open outlet valves from the component cooling surge tanks were not locked and therefore not in accordance with plant Technical Specification 3.6. This Technical Specification requires Emergency Core Cooling System manual valves be aligned and locked in the position required for safeguards operation. The valves were subsequently locked, controlling procedures were revised, and a review of the component cooling system revealed that no additional unlocked manual valves were required to be locked. A detailed root cause evaluation was completed and no change to this LER is required.
3091991008 | Maine Yankee | 08/08/1991 | 11/15/1991 | 9111250025 | <strong>Maine Yankee Atomic Power Company</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted to alert licensees to potential problems with fuel oil tanks. <br /><br /> On August 8, 1991, Maine Yankee discovered foreign material in the fuel oil tank supplying DG-2, the Appendix R alternate shutdown diesel. Maine Yankee pursued inspection plans and evaluated for potential failure modes. Subsequently, DG-2 successfully performed a four hour operability run. The fuel oil tank was then drained and inspected. It was determined that the foreign material was a loose section of internal tank epoxy coating. The tank lining was then stripped to bare carbon steel. A fuel oil sample was sent out for analysis and the lining went out for materials testing. The tank was refilled with new fuel oil and placed back in service. After another operability run, fuel oil filters were changed and the diesel was declared perable.
3091991009 | Maine Yankee | 09/27/1991 | 10/28/1991 | 9111060263 | <strong>Inoperable MFRV Feedwater Train Trip Solenoid</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1991 at 1030, a plant shutdown was initiated as required by Technical Specifications when both trains of the Feedwater Train Trip (FTT) System were declared inoperable. Maine Yankee determined that the Main Feedwater Regulating Valve (MFRV) FTT solenoid valves were receiving insufficient air to actuate under all plant conditions. The power reduction was stabilized at 15.5% power which allowed isolation of the MFRVs. The solenoids were returned to operable status by increasing valve positioning air pressure. The MFRV FTT solenoids were declared operable on September 30, 1991 at 0542.
3091991010 | Maine Yankee | 10/05/1991 | 11/04/1991 | 9111120222 | <strong>Plant Trip on Condensate Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>At 0237 on October 5, 1991, an automatic reactor trip from 100% power occurred due to actuation of the Reactor Protective System from a loss of load trip when the main turbine tripped. The turbine trip occurred when the steam driven feedwater pump (P-2C) tripped after a condensate pump (P-27C) breaker tripped due to a phase to phase short at the motor leads connection. <br /><br /> The generator primary relay (86P) actuation was delayed due to the slow closure of a main turbine stop valve; the backup relay (86BU) actuated and transferred station service to offsite power as designed. All safety systems performed as expected.
3091991011 | Maine Yankee | 10/11/1991 | 11/15/1991 | 9111250258 | <strong>Maine Yankee Atomic Power Company</strong><br /><i>Abstract:&nbsp;</i>During a review of the Emergency Diesel Generator (EDG) output breaker circuitry, Maine Yankee postulated that a lockout of the EDG breaker may occur when the breaker is required to be closed. If the EDG is phased onto the bus and a plant trip occurs concurrent with a loss of offsite power, the coincident open and close signals for the breaker may lock out the breaker due to its anti-pumping feature. <br /><br /> At the time of discovery, one EDG had been running phased to its emergency electrical bus for approximately 24 hours while maintenance was being performed on the redundant EDG. Operability of both EDGs had been questioned due to concerns with the air start systems. Since the postulated lockout could occur, the running EDG was also conservatively considered inoperable and therefore was immediately unloaded by disconnecting from its electrical bus. The EDG was left running at half synchronous speed in accordance with manufacturer's recommendations to resolve any question of diesel operability. <br /><br /> On October 16, 1991, Maine Yankee verified that the operating times of the relays could permit breaker lockout if the EDG is phased to its bus and a plant trip occurs with a loss of offsite power. The plant therefore had operated in a condition prohibited by Technical Specifications since both EDGs were inoperable for greater than one hour. <br /><br /> Maine Yankee plans to modify the circuitry so that the signals do not overlap in time and cause the breaker lockout. In the interim, an EDG is conservatively considered inoperable whenever it is phased to its bus. The circuitry modification is scheduled for the 1993 refueling.
3091991012 | Maine Yankee | 11/22/1991 | 12/20/1991 | 9112270212 | <strong>Plant trip due to Condensate Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>A reactor trip from 100% power occurred on November 22, 1991 at 0957 due to the failure of a condensate pump motor (P-27B). Internal motor lead arcing caused a drop in voltage on the bus. The condensate pump motor breaker tripped on overcurrent. The transient resulted in a trip of the steam turbine driven feedwater pump. This action tripped the main turbine. The reactor protective system tripped the reactor on loss of load. <br /><br /> All safety systems performed as expected. <br /><br /> This LER is similar to number 91-010, however, the cause of the LER 91-010 motor failure is not identical to this LER.
3111991001 | Salem 2 | 01/04/1991 | 01/30/1991 | 9102080093 | <strong>Tech. Spec. 3.7.11.a noncompliance; Firewatch Rove Greater Than 1 Hour; Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1991 at 1010 hours, it was discovered that the hourly roving fire watch patrol for several areas was not completed within one (1) hour (i.e., approximately 20 minutes late). The areas include the 55' and 64' Elevation Auxiliary Equipment Areas and the 84' Elevation Diesel Generator Fuel Oil Storage Tank Area. These areas require a roving fire watch patrol due to inoperable penetration seals. Missed roving fire watch patrols are contrary to the requirements specified by Technical Specification Action Statement 3.7.11. The root cause of this event has been attributed to personnel error. The individual responsible to complete the fire watch rove performed the rove out of sequence, not in accordance with procedure. This has been attributed to inattention to detail. This individual was properly trained on how to conduct the fire watch rove and had been properly briefed, prior to completing the fire watch rove (as explained below). Upon discovery of the fire watch rove being performed out of sequence, supervision was contacted and the affected fire areas were immediately checked. The individual who caused the fire watch rove to exceed one hour was initially suspended pending investigations. He was subsequently terminated. This event has been reviewed by Site Protection Department management and contractor management with appropriate department and contractor personnel. Attention to detail and the significance of performing hourly fire watch patrols within the required time frame was stressed.
3111991002 | Salem 2 | 01/16/1991 | 02/14/1991 | 9102260126 | <strong>ESF Signal Actuation: Control Room Vent. Swap To Emergency Mode Due To Equip. Design</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 3 Engineered Safety Feature (ESF) actuations associated with the Salem Unit 2 Control Room general area Radiation Monitoring System (RMS) monitor (2R1A). This RMS channel failed on 3 separate occasions. In each case, automatic switching of the Control Room ventilation from normal operation to its accident mode of operation (both Salem Units by design) occurred. On 1/16/91 at 0018 hours, the 2R1A RMS channel spiked high. Upon successful completion of a channel check on 1/21/91 the channel was made operable. On 1/23/91 at 1906 hours, the 2R1A RMS channel failed low. By design, when this RMS channel fails low it will conservatively initiate its ESF function. Several equipment concerns were identified. Upon successful completion of equipment repair and a channel calibration on 1/31/91 the channel was made operable. On 2/1/91 at 0529 hours, during normal plant operations for both Salem Units, the 2R1A RMS channel spiked high. The root cause of the 2R1A channel failures has been attributed to equipment design concerns. The type detector system used for the Salem Unit 2 RMS channels is manufactured by Victoreen. Periodic problems with this system have been experienced as indicated in prior LERs (e.g., 311/90-019-00). The 2R1A channel was inspected and repaired. The channel was returned to service on 2/13/91. It is being monitored in order to isolate the specific cause of the channel failures should either a high channel spike or a low failure occur again. As indicated in LER 311/90-019-00, Engineering has investigated the RMS channels concerns; system design modifications are being investigated.
3111991003 | Salem 2 | 01/10/1991 | 04/10/1991 | 9104190276 | <strong>ASME Code Class 3 Piping Leakage Caused By Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>This Licensee Event Report (LER) addresses three (3) occurrences of ASME Code 3 piping leakage. Based upon discussion with the Nuclear Regulatory Commission (NRC), notifications were made for each occurrence as agreed in accordance with Code of Federal Regulations 10CFR 50.72. In all cases, Technical Specification 3.4.11.1 Action c was complied with. The root cause of the listed ASME Code 3 component leakage has been attributed to equipment failure. The equipment failure component SW leaks were the result of erosion/corrosion factors. The components which exhibited leakage were declared inoperable in accordance with Technical Specifications and the appropriate Action Statements met. The components were not declared operable until completion of repairs, which were done in accordance with the ASME code for Class Code components. An ongoing program, at Salem Generating Station, for the upgrade of Service Water System piping is continuing. The scope and prioritization of pipe replacement and the need for additional inspections is being reviewed and modified, as applicable. A detailed weekly walkdown, by System Engineering, of Room Cooler SW pipe (initiated as per Salem Unit 2 LER 311/90-042-00) to provide early identification of SW leakage is continuing. This compliments routine Operations Department operator observation, of Room Cooler areas, performed each shift.
3111991004 | Salem 2, Salem 1 | 02/18/1991 | 03/18/1991 | 9103270116 | <strong>ESF Actuation Signal for Cont. Vent. Isol. Due To Equipment Failure (2R45B)</strong><br /><i>Abstract:&nbsp;</i>On 2/18/91, the 2R45B Radiation Monitoring System (RMS) intermediate range Plant Vent monitor spiked high several times. Upon spiking to the alarm setpoint, it caused the 2R41 RMS Plant Vent channels to deenergize. When the 2R41C (Noble Gas Plant Vent Monitor) deenergized, a Containment Purge/Pressure-Vacuum-Relief (CP/P-VR) System isolation and 2WG41 (Waste Gas Decay Tank Vent Control Valve) valve closure signals were initiated. No Waste Gas System discharge or Containment ventilation discharge was in progress at the time of the signal. Technical Specification 3.3.3.1. Action b26 (for 2R45 channel inoperability) was entered at the time of the event. The CP/P-VR System isolation signal is considered an Engineered Safety Feature (ESF) The root cause of this event is attributed to equipment failure. The 2R45B channel spikes were caused by a damaged detector cable connection. The detector cable shield wire had become severed due to stress placed on the cable connection when the lead shield door is closed. This wire filters electrical noise thereby preventing spurious channel spiking. It is believed that normal generated Electro-Magnetic/Radio Frequency Interference caused the spurious spiking. The damaged detector cable was replaced. Subsequently, upon successful completion of a channel functional test and a channel calibration check, Tech. Spec. 3.3.3.1 Action b.26 was exited on February 24, 1991 at 0448 hours. The other R45 channel wire connectors will be inspected. The procedures associated with periodic testing of the R45 channels will be modified to require inspection of the subject wire (and similar wires) connections.
3111991005 | Salem 2 | 02/26/1991 | 07/09/1992 | 9207200201 | <strong>4KV Vital Bus UV Relay Setpoints Found Below Minimum Tech. Spec. Allowable Value</strong><br /><i>Abstract:&nbsp;</i>On 2/26/91, the 91.6% sustained undervoltage relay's minimum drop out voltage, for all 3 vital Busses, were found to be below the Tech. Spec. minimum allowable value of 91%. This was discovered during monthly Surveillance testing of undervoltage relay setpoints. New procedures (S2.MD-FT.4KV-0001(Q) (0002 of 0003), 'ESFAS Instrumentation Monthly Functions Test-2A (2B or 2C) 4KV Vital Bus Undervoltage') were being used (first use) to support the surveillance testing. The surveillance test was last performed on 1/21/91 using procedure M3T, 'Undervoltage and Underfrequency Trip and Time Response Surveillance Test'. The causal procedure inadequacy. Special relay tests show that the relay circuitry is influenced by the amount/type of harmonics present in the external test signal; the relay trip/reset setpoints change on subsequent checks plus the relay's allowable design setpoint drift. For additional root cause/corrective action details refer to LER 311/91-008-01. A contributing factor to the cause of this event was personnel error. The new relay test procedures are unit and bus specific. The first use of these new procedures was on 2/26/91. Enhancements have since been made to address human factor concerns and test equipment setup. This event has been reviewed with the technician involved, stressing attention to detail and the need to question multiple out of tolerance as-found readings.
3111991006 | Salem 2 | 03/02/1991 | 08/15/1991 | 9108260094 | <strong>ESF Actuation: Auto Switch of Control Rm Vent. To Emer. Mode Due To Equip. Failure</strong><br /><i>Abstract:&nbsp;</i>On 3/2/91 at 2054 hours, during normal plant operation, the Control Room general area Radiation Monitoring System (RMS) monitor (2R1A) spiked high. This resulted in the automatic switching of the Control Room ventilation from normal operation to its accident mode of operation (100% recirculation). The switching of the Control Room ventilation system to its emergency mode of operation is an Engineered Safety Feature (ESF). The cause of this event was determined to be a failed wire in the detector cable Amphenol connector. The channel was subsequently returned to service on 3/4/91. On 3/5/91 at 1754 hours, a second automatic ventilation switching occurred from a 2R1A RMS channel low failure signal. Investigation revealed that a different wire in the detector cable Amphenol connector had broken causing the channel failure. This wire was resoldered. The root cause of both events is attributed to equipment failure. During the 3/5/91 event, one of the ventilation outlet dampers (2CAA18) did not close fully. The 2CAA18 linkage arm was repaired. Equipment with similar types of linkage configuration were inspected. It was determined that loose setscrews on damper linkages is not a prevalent problem. The existing preventive maintenance (PM) program (i.e., performed every 18 months) on these dampers provides adequate assurance of damper integrity.
3111991007 | Salem 2, Salem 1 | 05/22/1991 | 06/20/1991 | 9106260244 | <strong>ESF Actuation Signals for CVI: 2R12B and 1R41C Channel Failures</strong><br /><i>Abstract:&nbsp;</i>This LER addresses Containment Purge/Pressure-Vacuum Relief System (CP/P-VRS) isolation signals (3 events) (an Engineered Safety Feature (ESF)). Once from the Salem Unit 2 2R12B Containment Iodine Radiation Monitor Radiation Monitoring System (RMS) channel and twice from the Salem Unit 1 1R41C Plant Vent Radioactive Noble Gas Monitor RMS channel. Both RMS channels are manufactured by Victoreen. On May 22, 1991, the 2R12B RMS channel failed low. On May 29, 1991, the 1R41C RMS channel failed low. Tech. Spec. Table 3.3-13 Action 31 was entered. Investigation of this actuation did not identify the specific cause of the event. Upon successful completion of functional testing, the channel was returned to service (and Tech. Spec. Table 3.3-13 Action 31 exited) on June 3, 1991 at 1735 hours. On June 3, 1991 at 2100 hours, during normal power operations, the 1R41C RMS channel again failed low. The channel was declared inoperable and Tech. Spec. Table 3.3-13 Action 31 was re-entered. The root cause of the actuation of the CP/P-VRS isolation signals is attributed to equipment design concerns. Periodic problems with the Victoreen system have been experienced, as indicated in prior LERs (e.g., 311/90-040-00). Investigation of the second 1R41C channel failure identified the specific cause of the two (2) channel failures. The control module had failed. It was subsequently replaced. Several system design modifications will be implemented.
3111991008 | Salem 2, Salem 1 | 06/03/1991 | 07/09/1992 | 9207200059 | <strong>4KV Vital Bus UV Relay Setpoints Found Below Minimum Tech. Spec. Allowable Value.</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1991, the 91.6% sustained undervoltage relay minimum drop out trip setpoint voltage, for two (2) of the three (3) of the 2A 4KV Vital Bus undervoltage relays and for all three (3) 2B 4KV Vital Bus undervoltage relays, were found to be below the Technical Specification minimum allowable value of 91%. This was discovered during Technical Specification Surveillance 4.3.2.1.1 testing which requires monthly testing of undervoltage relay setpoints. Procedures (S2.MD-FT.4KV-0001(Q) (0002), 'ESFAS Instrumentation Monthly Functional Test-2A (2B) 4KV Vital Bus Under Voltage') were being used to support the surveillance testing. The lowest as-found trip setpoint, of the five subject relays was 90.5%. The causal factors of the setpoint variance are relay design inadequacy and procedure inadequacy. Special relay tests show that the relay circuitry is influenced by the amount/type of harmonics present in the external test signal. The worst case scenario (i.e., assume that the %THD measured was all third harmonics) would have the relays trip at 108.38 VAC. The minimum allowable Technical specification value is 108.2 VAC. Weekly testing of the installed relays was performed under the direction of System Engineering. in addition, controlled bench tests were performed on identical relays. The relay test procedure has been revised as applicable. The 4KV Vital Bus 91.6% undervoltage Rochester relays (both Salem Units) were replaced with ASEA Brown Boveri type 27N relays. Since installation, setpoint variance has not been observed.
3111991009 | Salem 2 | 06/30/1991 | 07/25/1991 | 9108060113 | <strong>ESF Actuation: No. 21 Aux. Feedwater Pump Auto Start Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1991, at 0237 hours, during full power operation, the No. 21 Motor Driven Auxiliary Feedwater (MDAFW) Pump {BA} started. Also, Steam Generator (S/G) blowdown {WE} and blowdown sampling isolated (i.e., valves closed) automatically. The pump could only be stopped from local manual control. Technical Specification 3.7.1.2 Action "a" was subsequently entered. The cause of the ESF actuation has been attributed to equipment failure. Investigation identified a failed output card in the Solid State Protection System (SSPS). The failed card was replaced. The SSPS and the No. 21 MDAFW Pump were functionally tested and returned to service on June 30, 1991. Testing of the failed output card has been initiated to identify the failure mechanism.
3111991010 | Salem 2 | 07/23/1991 | 08/15/1991 | 9108260024 | <strong>2 ESF Actuation Signals: Cont. Vent. Isol. & Auto Switch of Control Rm Vent.</strong><br /><i>Abstract:&nbsp;</i>This Licensee Event Report addresses two (2) Engineered Safety Feature (ESF) signals initiated through the Radiation Monitoring System (RMS). One ESF signal was for the automatic switching of the Control Room ventilation from normal to the emergency mode of operation (100% recirculation) and the other for a Containment Purge/Pressure-Vacuum<br /><br /> Relief (CP/P-VR) System isolation. Both events occurred on July 23, 1991. The cause of the Control Room Ventilation switch was a high channel spike on the 2R1B RMS channel (Control Room Ventilation Intake Duct monitor). The cause of the Containment Ventilation Isolation signal was a high channel spike on the 2R45C (Plant Vent High Range Noble Gas monitor) channel which caused the Plant Vent Noble Gas RMS channels (2R41C respectively) to de-energize. The root cause of the 2R1B channel spike is equipment design. The 2R1B RMS channel monitor is a Victoreen 843-22, Beta Scintillator. Periodic problems with the Victoreen system have been experienced, as indicated in prior LERs (e.g., 311/90-040-00). Also, the Salem Unit 2 RMS is susceptible to voltage transients. Investigation of the 2R1B channel CP/P-VRS isolation signal did not identify any failed components. The root cause of the 2R45C channel spike is equipment failure. A resistor in the detector assembly was found to have one of its connections broken. The assembly was subsequently replaced.
3111991011 | Salem 2 | 07/30/1991 | 08/28/1991 | 9109050228 | <strong>Non Rad Waste RMS Channel Setpoint Incorrect; Tech. Spec. Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On 7/30/91, during normal plant operation, it was discovered that the Non Radioactive Liquid Waste Discharge Radiation Monitoring System (RMS) channel (2R37) setpoint was not correct contrary to the requirements of Tech. Spec. 3.3.3.8. The 2R37 channel alarm/warning setpoints did not incorporate the maximum Clearwell Pump flowrate. In June 1985, the Non-Radioactive Liquid Waste Disposal system was upgraded with the implementation of design modifications. The modification included replacement of the Clearwell Pumps with higher capacity pumps. The setpoint was not modified in June 1985 to address the increased flowrate; therefore, the 2R37 channel has been technically inoperable due to the incorrect setpoints since that time. Tech. Spec. Table 3.3-12 Action 31 requirements were not implemented until discovery of the concern on 7/30/91. The root cause of this event is inadequate design review. The 1983/84 design change review/approval failed to fully assess the affect on the 2R37 channel setpoints. A review determined that since 1985, a release in excess of limits is highly unlikely. The ODCM has recently been validated by Radiation Protection/Chemistry Services. No other RMS channel setpoint concerns associated with system design modifications are evident other that the event discussed in LER 272/90-032-00. A design change, to modify the 2R37 channel setpoint, has been completed. The design change process administrative procedure will be revised to require assessment of the impact of a design change on the ODCM.
3111991012 | Salem 2, Salem 1 | 08/26/1991 | 09/19/1991 | 9109300250 | <strong>ESF Signal Actuation: 2A 4KV Vital Bus UV Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This LER addresses an Engineered Safety Feature (ESF) actuation event. On 8/26/91, 2A 4KV Vital Bus tripped. An SEC "Mode Op III" sequence initiated which included the starting and loading of 2A Diesel Generator. At the time, an undervoltage functional surveillance was being conducted on 2A 4KV Vital Bus. The root cause of this event is personnel error. The technician performing undervoltage relay functional testing connected a jumper to the wrong relay due to inattention to detail. The technician was aware of the correct relay to be jumpered but failed to do so. A contributing factor, to the cause of this event, was inadequate corrective actions taken after 2 prior 4KV Vital Bus undervoltage events at Salem Station (reference Salem Unit 1 LER 272/91-022-00). A detailed "Human Factors Review" of the 4KV Vital Bus undervoltage relay functional testing was conducted. The study identified several "human factors" which may have contributed to these events principal of which is design aspects (i.e., the terminal lugs to be jumpered being located near the floor). The technician involved was counseled. This event was critiqued with applicable supervisors and technicians. A lamacoid label was placed below the undervoltage relays inside the A, B, and C 4KV Vital Bus cabinets. Color coded banana jacks have been installed on the relay terminal lugs making them more accessible. The surveillance procedures have been revised to address the banana jacks. A design change to replace the undervoltage relays is being prepared. It includes relocation of the relays to a more accessible location.
3111991013 | Salem 2 | 08/28/1991 | 09/27/1991 | 9110020247 | <strong>ESF Signal Actuations: 4 Cont. Vent. Isolation Signals From RMS Due To Design</strong><br /><i>Abstract:&nbsp;</i>This LER addresses 4 Containment Purge/Pressure-Vacuum Relief System (CP/P-VRS) isolation signal events. These events occurred twice from the 2R41C Plant Vent Radioactive Noble Gas Monitor Radiation Monitoring System (RMS) channel (on 8/28/91 and 9/1/91), once from the 2R12B Containment Iodine Radiation Monitor RMS channel (on 9/10/91), and once from the 2R12A Containment Noble Gas Radiation Monitor RMS channel (on 9/10/91). All 3 channels are manufactured by Victoreen. The root cause of the 2R41C and 2R12B actuation of the CP/P-VRS isolation signals is equipment design. Problems with the Victoreen RMS have been experienced. These problems include susceptibility to voltage transients. The cause of the second 2R41C RMS channel event was caused by the failure of the scalar module, which was subsequently repaired. The scalar module failure could not be proved as the cause of the first 2R41C RMS channel failure. The 2R12B event was caused by damaged scalar module connecting pins which were repaired. The 2R12A event was caused by a 0.25" uninsulated sliver of wire on the backplane in the channel drawer. The 2R12A channel drawer and circuits were vacuumed. Channel functional tests were successfully completed prior to restoring the 3 RMS channels to service and exiting the appropriate Action Statements. Investigation is continuing as to why remote and local alarm indications did not identify the first 2R41C channel failure. Engineering has investigated the concerns with the Victoreen RMS channels. Several system design modifications are planned.
3111991014 | Salem 2 | 10/10/1991 | 01/09/1992 | 9201160135 | <strong>ESF Signal Actuation: Containment Vent. Isolation Due To 2R12B Channel Failure</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1991, at 0138 hours, the 2R12B (Containment Radioactive Iodine Monitor) Radiation Monitoring System (RMS) channel failed low. This resulted in an Engineered Safety Feature (ESF) actuation signal for Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System isolation. The channel was declared inoperable. At the time of the event the CP/P-VR System valves were closed. A functional check of the 2R12B channel did not reveal any failed components. The channel was observed for two (2) weeks, while its output functions were blocked, with no additional failures. The channel was subsequently returned to service. On November 19, 1991, at 1743 hours, the 2R12B RMS channel again failed low resulting in an actuation signal for CP/P-VR System isolation. The channel was declared inoperable. At the time of the event the CP/P-VR System valves were closed. The root cause of both events has been attributed to equipment design. The detector system used for the Salem Unit 2 RMS channels is manufactured by Victoreen. Periodic problems with this system have been experienced as indicated in prior LERs (e.g., 311/90-010-00, and 311/91-007-00). The 2R12B detector uses a Victoreen Model 843-34 Scintillator. The Victoreen RMS channels are subject to voltage transients. After the November 19, 1991 event, the channel was removed from service. It was not returned to service. The channel is being replaced with more reliable equipment during the current 611 refueling outage.
3111991015 | Salem 2 | 10/21/1991 | 11/19/1991 | 9111260013 | <strong>TS 3.0.3 Entry; 2 Power Range NIS Channels Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 10/21/91, Unit load was being increased. As required by Tech. Spec. 3.3.1.1 Table 4.3-1, the required daily heat balance check was performed. The power increase was stopped and stabilized at a calculated rated thermal power (RTP) of 29.8%. The 4 Nuclear Instrumentation System (NIS) power range channels indicated less than 29.8% RTP. Channels 2N41 and 2N44 satisfied the operability criteria (within 1.74% of RTP). Channels 2N43 and 2N44 did not meet the operability criteria. They were declared inoperable at 0400 hours on 10/21/91. Since Technical Specification Table 3.3-1 Action Statements for inoperable power range channels does not address inoperability of two (2) or more channels, Technical Specification Action 3.0.3 was entered. This event was caused by the application of the current methodology for defining when specific NIS operability criteria must be considered. This resulted in overly conservative requirements for NIS operability criteria during infrequent operation at low power levels and deep control rod insertions. The fine gain potentiometers of all four (4) power range NIS channels were adjusted to 30% RTP at 0425 hours on 10/21/91 at which time Technical Specification Action 3.0.3 was exited. Reactor Engineering personnel validated the calorimetric calculations as to the determination of power level and verified the appropriate application of the procedures. The reactor protection system trip setpoints in the accident analysis of the Updated Final Safety Analysis Report will be reviewed.
3111991016 | Salem 2 | 10/25/1991 | 11/22/1991 | 9111270002 | <strong>Missed Tech. Spec. Surv., 2 fire hoses not inspected at the required frequency.</strong><br /><i>Abstract:&nbsp;</i>On 10/25/91, a staff engineer discovered that procedure M10-SST-023-2 "Detailed Inspection of Technical Specification Related Hose Stations", used to satisfy surveillance requirements for Technical Specification 4.7.10.4.b. every 18 months, was incorrect. Two (2) hose stations, 2FP229 and 2FP230, had been inadvertently deleted from Attachment 1 of the procedure when it was revised in June 1989. The surveillance was performed once, in November 1990, since it was inappropriately revised. The last successfully completed surveillance, prior to the inappropriate procedure revision, was in May 1989. The Operating Shift was informed and Action Statement 3.7.4.10 was entered. The root cause of the inappropriate procedural revision is personnel error (inattention to detail). The procedure writer did not verify the accuracy of the revision which deleted fire hose stations 2FP229 and 2FP230 from Attachment 1. The procedure writer and procedure reviewer, who processed the procedure revision, have been counseled. The procedure error was corrected and hose stations 2FP229 and 2FP230 were inspected as per the corrected procedure. The Fire Protection Department will review their Technical Specification surveillance procedures revised after July 1989. The Fire Protection Department reviewed this event with their procedure writers and procedure reviewers. Procedure, NC.NA-AP.ZZ-0032(Q), "Preparation, Review and Approval of Procedures", will be reviewed and revised, as necessary.
3111991017 | Salem 2, Salem 1 | 11/09/1991 | 12/09/1991 | 9112120117 | <strong>Reactor/Turbine Trip on Low Auto Stop Oil Pressure Followed By Turbine/Gen. Failure</strong><br /><i>Abstract:&nbsp;</i>On 11/9/91, a Reactor Trip event occurred during performance of the monthly Auto Stop Oil System protection device testing. After the generator breaker opened (per design), a turbine overspeed condition developed resulting in failure of the turbine/generator. The reactor trip initiated while the Auto Stop Oil (AST) System test/normal lever was still in the "test" position. Following the initial drop in AST System header pressure, pressure returned. Once the AST bistable reset setpoint was reached, the turbine relatched allowing the turbine valves to reopen. Within 15 seconds of the generator output breakers' opening, the main stop valves fluctuated at the 90% open limit. Within the following 6 seconds the 4 main stop valves had gone full open. The governor valves then opened due to failure of the 63-3 AST turbine protection pressure switch to lock in the turbine trip signal in conjunction with the failure of 3 overspeed protection EHC solenoid valves (20/ET, 20-1/OPC and 20-2/OPC) to open. The operators at the front standard heard several highly unusual sounds from the turbine and manually tripped the turbine causing closure of the turbine valves. The trip cause was blockage of the AST pressure reduction orifice. Investigation to identify the source of the foreign material is continuing. Several causal factors of the turbine failure have been identified (see main report). Corrective actions have been taken or are in the process of implementation to address these causal factors.
3111991018 | Salem 2 | 11/29/1991 | 12/30/1991 | 9201060283 | <strong>4 ESF Actuation Signals: 2 Auto Switch of Control Rm Vent. & 2 Cont. Vent Isol.</strong><br /><i>Abstract:&nbsp;</i>This LER addresses four (4) Engineered Safety Feature (ESF) signals initiated through the Radiation Monitoring System (RMS). Two (2) were for the automatic switching of the Control Room Ventilation from normal to the emergency mode of operation. (11/29/91, 0835 hrs - 2R1A spiked high) & (12/05/91, 0640 hrs - 2R1A failed low). Two (2) were for Containment Purge/Pressure Vacuum Relief System isolation. (11/30/91, 1404 hrs - 2R45B spiked high, causing 2R41C to deenergize) & (12/02/91, 1100 hrs - 2R12A spiked high). The root cause of the 2R1A RMS channel spike/failure, 2R45B RMS and 2R12A channel spikes is attributed to design/equipment concerns, specifically susceptibility to voltage transients. The type of detector system used for the majority of the Salem Unit 2 RMS channels is manufactured by Victoreen. Periodic problems with this system have been experienced as indicated in prior LERs (e.g., 311/91-010-00 and 311/91-019-00). Since the 12/05/91, event, the channels have been operating satisfactorily. In each case, the affected channels were checked and returned to service. Engineering has investigated the concerns with the Unit 2 RMS channels. Several system design modifications are being implemented to eliminate spurious ESF actuation signals.
3111991019 | Salem 2 | 12/07/1991 | 01/02/1992 | 9201090079 | <strong>ESF Signal Actuation: Cont. Vent. Isolation due to 2R12A RMS Channel Response</strong><br /><i>Abstract:&nbsp;</i>On 12/7/91, the 2R12A (Containment Radioactive Noble Gas Monitor) Radiation Monitoring System (RMS) channel alarmed. This resulted in an Engineered Safety Feature (ESF) actuation signal for Containment Purge/Pressure-Vacuum Relief (CP/P-VR) System {BF} isolation. The channel was not declared inoperable since the cause of the alarm was due to airborne activity above normal background levels. This event occurred as a result of routine refueling activities. Reactor Coolant System (RCS) cover gas (containing radioactive noble gases) was pulled into Containment after the S/G primary manway diaphragms were removed. Portable ventilation, using HEPA filtration units, is attached to the primary cold leg manway to support S/G work. In Mode 6, the 2R12A channel setpoint is set at Technical Specification Table 3.3-6 Conditional Surveillance. Due to the background levels, prior to S/G primary manway diaphragm removal, the 2R12A channel alarm setpoint was set at 240 cpm. The 2R12A channel recorded activity levels up to 500 cpm after the diaphragm was removed. The procedure(s), which address refueling activities involving S/G work, will be appropriately revised to address primary manway diaphragm removal and its affect on the 2R12A RMS channel.
3111991020 | Salem 2 | 11/22/1991 | 01/13/1992 | 9201160125 | <strong>ESF Signal Actuation: Cont. Vent. Isolation Due To 2R12A RMS Channel Response</strong><br /><i>Abstract:&nbsp;</i>On 11/22/91, the Radiation Monitoring System (RMS) Containment Noble Gas Monitor, 2R12A, alarmed. This resulted in the initiation of a Containment Purge/Pressure-Vacuum Relief (CP/P-VR) system isolation signal. Prior to the event, the 2R12A channel alarm setpoint was reduced from 20,000 cpm to 240 cpm in preparation for entry into Mode 6 (Refueling). The root cause of this event is personnel error as a result of inattention to detail. The source of the 2R12A channel count rate increase was the gases released as a result of work on a valve leak-off line (which goes to the Reactor Coolant Drain Tank (RCDT)). The line had not been tagged and isolated to support the valve work. Subsequently, when Maintenance workers cut into the leak-off line the noble gases from the RCDT escaped to the Containment atmosphere eventually causing the 2R12A alarm. Corrective disciplinary action has been taken with Operations and Maintenance personnel involved in this event. This event has been reviewed with applicable personnel stressing the need for attention to detail. The WCC reviewed all existing tagouts. No similar situations were identified. Although the Containment Equipment Hatch was open during this event, the Auxiliary Building Ventilation maintained Containment negative pressure. An evaluation is being conducted to determine if a release to the environment (via the open hatch) occurred. The next issue of the RERR will incorporate the results of this evaluation as appropriate.
3111991021 | Salem 2 | 12/19/1991 | 01/20/1992 | 9201280109 | <strong>Tech. Spec Surveillance Overdue To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 12/19/91, it was discovered that the Waste Gas Analyzer channel functional, Technical Specification Surveillance, had not been performed. This monthly surveillance was overdue as of 12/16/91. The last time the test was successfully completed was on 11/9/91. The surveillance was originally scheduled for 12/9/91; however, the start date was shifted (by computer logic) to 12/19/91. The PREMIS computer program for outage scheduling is structured to control the start date for all work done during the outage, including Surveillances. When a job is delayed, the computer automatically reschedules the start date for jobs dependent on the delayed job, independent of Technical Specification or other commitment requirements. The root cause of this event is personnel error. Neither Outage Planning Department personnel nor the Technical Specification Surveillance Administrator observed the shift in the surveillance start date upon review of the "Technical Specification Overdue Surveillance Report". The surveillance was successfully completed on 12/19/91. Appropriate disciplinary action has been taken with those individuals involved in this event. This event has been reviewed with applicable Outage Planning Department personnel. A Technical Specification Surveillance review will be conducted to identify those Surveillances required when the core is defueled. A review of the applicable administrative procedures will be completed to ensure scheduling responsibilities for surveillances, during outage vs. non outage time periods, are adequate.
3131991001 | Arkansas 1 | 01/10/1991 | 04/29/1991 | 9105030252 | <strong>Automatic Reactor Trip Due To A Main Turbine Trip Which Was Caused By Failure Of The Turbine Generator Exciter</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1991, at approximately 2326, with the plant at 100 percent of rated power, a reactor trip occurred as a result of the main turbine tripping due to loss of field excitation to the main generator. An anticipatory Reactor Protection System (RPS) trip was initiated, as designed, when the main turbine tripped while reactor power was greater than 43 percent. Plant response to the trip was as expected. Reactor Coolant System (RCS) pressure decreased to 1828 psig and was quickly recovered into the post trip window. Minimum post trip RCS temperature was 553 degrees. A temporary exciter was installed while the plant remained in the hot shutdown condition and the reactor was returned to power on January 17, 1991. The temporary exciter was replaced with a permanent exciter during mid cycle outage 1M91, which began on April 7, 1991. The cause of the exciter failure was inadequate cleanliness/material accountability controls. Strengthened controls were implemented during the permanent exciter installation.
3131991002 | Arkansas 1, Arkansas 2 | 04/10/1991 | 07/26/1991 | 9107310313 | <strong>Inadvertent Actuations Of The Combined Control Room Emergency Ventilation System Due To An Invalid Unit Two Radiation Monitor Trip Which Was Initiated By A Transient Noise Spike</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1991 at approximately 0813, an automatic actuation of the Control Room Emergency Ventilation System (CREVS) occurred as a result of the tripping of the ANO-2 control room supply radiation monitor (2RE-8750-1). The radiation monitor was reset after the actuation and its indication returned to normal (approximately 60 CPM). The CREVS was then secured and the control room ventilation system was returned to its normal configuration. Another actuation was initiated by a noise spike on the same monitor at 2231 on May 9, 1991. The cause of these events was a transient noise spike which caused the radiation monitor indication to increase to its trip setpoint and initiate the CREVS actuation. However, the cause of the noise spike could not be determined. Evaluations performed subsequent to the May 9 actuation determined that the method for determining the setpoint for 2RE-8750-1 was overly conservative. This method calculated the setpoint daily at two times background as determined by the average of the last three previous readings. A new method was developed which determines background monthly by averaging the previous ninety readings and adds three standard deviations to the setpoint calculation.
3131991003 | Arkansas 1 | 04/21/1991 | 01/14/1994 | 9401260313 | <strong>Actuation of the Emergency Feedwater System During Plant Heatup due to Low Once Through Steam Generator Level Which Resulted From Inadequate Feedwater Flow Caused by a Degraded Auxiliary Feedwater</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1991, with the reactor subcritical, the Emergency Feedwater System (EFW) was automatically actuated due to a low level in the 'A' Once Through Steam Generator (OTSG). At the time of the event, OTSG levels were being lowered to 30 inches in accordance with the 'Plant Startup' procedure. However, when the 'A' OTSG reached its programmed level, the auxiliary feedwater pump (P-75) was unable to maintain the required level. OTSG level continued to decrease until the EFW system automatically actuated (13 inches). The EFW system operated as designed and quickly returned the OTSGs to their programmed level. it was originally believed that the root cause of this event was a leaking recirculation isolation valve (FW-8A). However, subsequent disassembly and inspection of P-75 revealed that the cause of the event was a loose first stage channel ring bushing which effectively reduced the inlet area to the second stage impeller and resulted in decreased pumping capacity at increased flow rates. P-75 was repaired and satisfactorily tested during refueling outage 1R10 (February - May, 1992).
3131991004 | Arkansas 1, Arkansas 2 | 05/02/1991 | 06/03/1991 | 9106070090 | <strong>Inadvertent Actuation of the Control Room Emergency Ventilation System due to a Chlorine Monitor Trip Which was Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1991, at approximately 1042, an automatic actuation of the Control Room Emergency Ventilation System (CREVS) occurred as a result of the inadvertent tripping of a chlorine monitor. At the time of the event, a technician was working from a ladder to remove a pressure switch from service for calibration. While performing his task, the technician shifted his position and inadvertently contacted the reset pushbutton of the chlorine monitor. The contact with the pushbutton resulted in the tripping of the monitor and actuation of the CREVS. Since the cause of the actuation was immediately known, the CREVS was reset and the Control Room ventilation lineup was returned to its normal configuration. The root cause of this event was personnel error. The technician failed to use caution while working in the vicinity of the chlorine monitor, which has a warning placard affixed next to its reset pushbutton. The technician was counselled regarding the importance of using caution when working around plant equipment. In addition, protective covers will be placed over the chlorine monitor reset pushbuttons to prevent them from being inadvertently depressed.
3131991005 | Arkansas 1 | 05/21/1991 | 06/14/1991 | 9106190426 | <strong>Automatic Reactor Trip On Loss of Main Feedwater Caused By Inadequate Procedural Guidance Regarding Cross-Tie of Electrical Load Centers</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1991, at approximately 0951, with the plant at 100 percent of rated power, an automatic anticipatory reactor trip on loss of main feedwater occurred when the circuit breaker supplying two cross-tied non-vital 480 volt load centers tripped on overload and de-energized the control oil pumps for both main feedwater pumps. Plant response to the trip was as expected. Water level was maintained in both steam generators by the emergency feedwater system. The load centers had been cross-tied to perform maintenance on one of the load center feeder breakers. The loading from both load centers exceeded the trip rating of one feeder breaker because the evolution was performed at power without first having shed the excess loads. The root cause of the event was inadequate procedural guidance contained in the electrical system normal operating procedure being used for the cross-tie evolution. The procedure has been revised to prevent recurrence. A contributing cause was insufficient review associated with the planning, scheduling, authorizing and performing of an infrequent and unusual evolution. Those personnel involved with this event have been counseled concerning their responsibilities.
3131991006 | Arkansas 1, Arkansas 2 | 05/30/1991 | 06/28/1991 | 9107030007 | <strong>Automatic Actuation of the Control Room Emergency Ventilation System Due to Spurious tripping of a Radiation Monitor Caused by an Inadequate Setpoint which Resulted from a Personnel Error During Procedure Development.</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1991, at approximately 1215, an automatic actuation of the Control Room Emergency Ventilation System (CREVS) occurred as a result of a spurious trip of the ANO-1 Control Room area radiation monitor (RE-8001). At the time of the actuation, a new procedure supplement was being performed which required the monitor's setpoint to be adjusted to two times background (0.4 millirem/hour). Previously, the setpoint for RE-8001 had been 1.0 millirem/hour. Shortly after the setpoint had been adjusted to 0.4 millirem/hour, a random spike caused the monitor to trip, actuating the CREVS. Performance of the procedure was terminated and the setpoint of RE-8001 was returned to 1.0 millirem/hour. The cause of this event was personnel error during procedure development. A verification/validation of the new supplement was not performed before implementation. Training was provided to appropriate personnel reemphasizing the need to perform verification/validation of procedure changes which add new tests or surveillances into existing procedures. A permanent change was made to the applicable procedure supplement to establish a minimum trip setpoint for RE-8001 to prevent random spikes from causing CREVS actuations.
3131991007 | Arkansas 1, Arkansas 2 | 06/14/1991 | 07/15/1991 | 9107190181 | <strong>Inadequate Fuse/Circuit Breaker Coordination Which Resulted From Design Inadequacies Related To Emergency Battery Replacement Created The Possibility Of A Loss Of Both Emergency DC Busses During A Design Basis Fire</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1991, during an internal inspection, it was identified that the fuses between the emergency batteries of both ANO-1 and ANO-2 and their associated DC control centers were not fully coordinated with the control center's load circuit breakers. This condition occurs at the upper range of available fault current and could, under certain fault conditions, result in the melting of the fuse and loss of the entire control center before the affected load circuit breaker could trip. This event, although unlikely, is postulated to occur if a very low resistance "pole to pole" or "both poles to ground" short circuit is created in close proximity to the affected DC bus such that the fault resistance is low enough to allow the high current necessary to cause fuse melt before or coincident with breaker trip. Several areas of common vulnerability were identified in both units where a fire in a single fire area could result in loss of both emergency DC busses. The root cause of this condition was determined to be design inadequacies related to the Design Change Packages which documented replacement of the emergency batteries for both units. Firewatches were posted in the areas of common vulnerability. The fuses for the emergency batteries of both units will be replaced with higher rated fuses during the next outage of sufficient duration.
3131991008 | Arkansas 1, Arkansas 2 | 08/27/1991 | 01/08/1992 | 9201150128 | <strong>Safety Related Instrumentation Not Installed in a Seismically Qualified Configuration Due to an Inadequate Design Change Documentation Review</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1991 at 1523, ANO-1 entered Technical Specification Limiting Condition For Operation (LCO) 3.0.3 based on an Engineering determination that certain safety related ANO-1 Foxboro Specification 200 instruments were inoperable due to inadequate seismic qualification. Although the condition was determined to be applicable to ANO-2 also, the extent of involvement was less and repairs were able to be performed within the framework of specific system LCOs. A 7 day 'Temporary Waiver of Compliance' from the shutdown requirements of the applicable LCOs was granted to ANO-1 by the NRC to allow sufficient time to make repairs without subjecting the plant to an unnecessary transient. Repairs were completed for ANO-1 on August 31, 1991 and for ANO-2 on September 10, 1991. The causes of this condition were determined to be obscure vendor documentation and an inadequate plant modification process review of vendor documentation. Technical manuals for seismically qualified Foxboro Specification 200 components were revised to include appropriate instructions for maintaining seismic configuration. Design review requirements for Design Change Package development will be clarified to ensure clear and specific instructions are provided concerning the qualified configuration of components or systems.
3131991009 | Arkansas 1, Arkansas 2 | 10/03/1991 | 11/01/1991 | 9111070112 | <strong>Safety Related 480 VAC Load Centers Not Installed in a Seismically Qualified Configuration During Initial Plant Construction Due to an Insufficient Design Documentation Review</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1991 during an Electrical Distribution System Functional Inspection on ANO-2, it was identified that 480 VAC Engineered Safety Features load centers 2B5 and 2B6 were not in a seismically qualified configuration. Further investigation revealed that B5 and B6 in ANO-1 were in the same configuration as 2B5 and 2B6 in ANO-2. Lifting trolleys used to assist in the installation and removal of circuit breakers were mounted on their guide and support rails on the load centers and were not secured in place. It was determined that the seismic qualification for the load centers, which was performed by the vendor, was not done with the trolleys or their guide rails in place. The lifting trolleys and rails were removed and stored in a remote area after determining that they were not seismically qualified, thereby restoring the load centers to a qualified configuration. Interim corrective actions included the establishment of administrative controls to prevent lifting trolleys from being left attached to the safety related load centers after the performance of maintenance. A modification to reinstall the lifting trolleys and rails in a seismically qualified configuration will be completed during the next refueling outage for each unit.
3131991010 | Arkansas 1, Arkansas 2 | 10/05/1991 | 03/27/1992 | 9204010013 | <strong>Offsite Power Source Potentially Unable to Maintain Adequate Voltage to Safety Loads During Specific Accident Conditions Due to Increased Offsite Grid Loading</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1991, an ANO Engineering evaluation identified specific conditions which could jeopardize the capability of an offsite power source to meet the requirements of General Design Criterion 17 for ANO-1 and ANO-2. It was determined that during peak summertime load conditions the 161KV offsite power source (Startup Transformer 2) might not be able to maintain adequate voltage to ANO loads during accident conditions with both units off line and the 500KV power source (autotransformer) unavailable. The impact of increased 161KV grid loading with time was not identified due to the failure to incorporate Millstone Degraded Grid Voltage requirements into Entergy transmission system review criteria. Short term corrective actions included placing the feeder breakers from Startup Transformer 2 in the "Pull to Lock" position, which prevents it from automatically picking up ANO loads due to loss of power to the 6.9KV or 4.16KV buses. Procedural guidance was also implemented to restrict the loading of Startup Transformer 2 when the 500KV source is unavailable to ensure its capability to supply adequate voltage to safety loads. Long term corrective actions will include the installation of capacitor banks near ANO and voltage tap changes on transmission system and ANO transformers. This report is also intended to meet the special reporting requirements of ANO-1 Technical Specification 3.7.2.H.
3131991011 | Arkansas 1 | 10/10/1991 | 11/11/1991 | 9111180104 | <strong>Inadequate Procedures For Setting Lube Oil Pressure Control Valves Results In Oil Leakage And Potential Common Mode Failure Of High Pressure Injection Pumps</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1991, following an overhaul of High Pressure Injection (HPI) pump P36A, simultaneous operation of P36A and its auxiliary oil pump P64A was requested for post-maintenance testing of repairs to the lube oil system pressure control valve. During this test run, System Engineering personnel observed that approximately one cup of oil per minute was flowing from the outboard pump bearing area. A similar condition was later found to exist on pump P36C. On October 10, 1991, it was determined that this condition represented a potential problem that could have resulted in the HPI pumps becoming inoperable during an ESAS actuation. The cause of this condition was lack of procedures for adjustment of the lube oil control valves on the HPI pumps. Adjustments were made on the lube oil system for P36A and P36C to stop the oil leakage. A night order was issued to Operations personnel advising them to be alert to any oil leakage and to initiate prompt corrective actions if leakage is detected. In addition, the lube oil system design is being evaluated to determine if long term use of the currently installed type of pressure control valves is appropriate.
3131991012 | Arkansas 1, Arkansas 2 | 11/11/1991 | 12/11/1991 | 9112170504 | <strong>Automatic Actuation of the Control Room Emergency Ventilation System During Ventilation System Maintenance Caused by High Airborne Activity Which Resulted From an Inadequate Pre-job Evaluation</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1991 an actuation of the Control Room Emergency Ventilation System (CREVS) occurred during the performance of maintenance to change the filters on the Radwaste Area Exhaust Ventilation System. On November 11, 1991 at 2035, workers entered the ventilation system air handler to begin changing the prefilters. Approximately 20 seconds after opening the door to the air handler, the Continuous Air Monitor began to alarm. At 2059, replacement of the prefilters was stopped and the door to the air handler was closed. The Control Room isolation occurred at 2100 hours when the count rate on the Control Room ventilation radiation monitor exceeded its alarm setpoint of 160 counts per minute (cpm). The Control Room radiation monitor indication quickly returned to approximately 60 cpm after the isolation. The high activity in the air handler was most likely caused by back leakage through the air handler inlet damper of fission gases introduced into the system by the Condenser Vacuum System. The fission gases were then drawn into the Control Room ductwork through existing pitot tube traverse access ports, seams or joints in ductwork and/or leaking gaskets in equipment, thus causing the Control Room isolation. Procedures were revised to ensure that the condenser vacuum pumps are aligned to draw from the separator tank during isolation of the Radwaste Area Exhaust Ventilation System fans.
3131991013 | Arkansas 1, Arkansas 2 | 11/13/1991 | 12/13/1991 | 9104170276 | <strong>Automatic Actuation of the Control Room Emergency Ventilation System Due to a Valid Radiation Signal Which Resulted From Leakage From a Letdown Filter Drain Valve</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1991 at 1307, an automatic actuation of the Control Room Emergency Ventilation System was initiated by 2RE-8750-1, which is a radiation monitor located in the Control Room ventilation intake ductwork. At the time of the actuation, the Control Room Ventilation System was lined up in the recirculation mode with the supply isolation damper manually closed. The supply and exhaust fans, which are normally secured when the Control Room is automatically isolated, were in service supplying ventilation to the Computer Room. At 1022, the Reactor Coolant System (RCS) developed a small leak from a filter drain valve. This leak was stopped at 1034. At 1253, the Penetration Room Exhaust System, which draws from the filter room where the leak was located, was placed in service. This system exhausts downward through a U-shaped ventilation exhaust pipe (gooseneck) located on the side of the containment building that is oriented toward the Control Room normal ventilation intake duct. The most likely cause of this event was the entry of high airborne activity from the letdown filter drain valve through the gooseneck into the intake ductwork. The back pressure on the Control Room ventilation supply damper created by the ventilation system lineup caused the damper to leak and created a flowpath for the high activity to the radiation monitor.
3151991001 | Cook 1 | 01/12/1991 | 02/04/1991 | 9102120111 | <strong>TS 3.7.9.5 Required Fire Hose Station Inoperable without Required Backup Fire Suppression Hose Due to Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1991, at 2115, it was identified that a fire hose station (FHC) being used as compensatory backup fire suppression was isolated by a red tag clearance. On December 30, 1990, the FHC for the pressurizer (PZR) heater (HTR) transformer (XFMR) room was isolated by a clearance and a backup fire suppression hose was routed from FHC-30. On January 12, a request to remove an additional section of the fire protection water system from service, which included FHC-30, was approved. The red tag clearance for this additional work was placed at about 0400 on January 12. It was identified at about 2115 on January 12 that FHC-30 had been isolated while it was serving as a backup fire suppression. A second fire hose was routed from an operable FHC to the PZR HTR XFMR room at about 2130. <br /><br /> This event was caused by inadequate administrative controls to assure fire impairment reviews were based on the current status of the fire protection system. A memo was issued on January 18 to address the lessons learned from this event. The administrative controls will be revised by February 15, 1991, to add assurance that fire impairment reviews will be based on the current status of the fire protection system.
3151991002 | Cook 1 | 01/28/1991 | 02/27/1991 | 9103060108 | <strong>Emergency Diesel Generator Declared Inoperable for Maintenance without Required Technical Specification Surveillance Being Completed due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 1-28-91, the Unit one CD Emergency Diesel Generator (EDG) was removed from service for maintenance and declared inoperable. With the U-1 CD EDG inoperable, Technical Specification (TS) 3.8.1.1 (Electrical Power Systems, A.C. Sources) required the operators to demonstrate the operability of the circuits between the offsite transmission network and the onsite Class 1E distribution system by performing TS surveillance 4.8.1.1.1.a within one hour. When the EDG was declared inoperable, the TS surveillance requirements were not completed within the one hour limit. The cause for the missed surveillance was personnel error. Neither the involved Senior Reactor Operator assigned to supervise the Unit 1 CD EDG removal from service nor the Unit Supervisor recalled the TS surveillance requirement at the time the EDG was declared inoperable. The lessons learned by the missed surveillance were thoroughly reviewed with the involved operators by their Shift Supervisor.
3151991003 | Cook 1, Cook 2 | 03/08/1991 | 04/08/1991 | 9104120346 | <strong>Liquid Release To Unrestricted Area In Violation Of Technical Specification 3/4.3.3</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1991 at approximately 0245 hours, a sampled but unmonitored liquid release occurred when a liquid waste release was restarted and completed while the liquid waste discharge monitor (RRS-1000) was inoperable. This is a violation of Technical Specification 3/4.3.3, Radiation Monitoring Instrumentation, LCO 3.3.3.9, Radiation Liquid Effluent Instrumentation. Review of the radioanalytical results of the monitor tank contents indicate that while the maximum permissible concentration (MPC) was at 3.58E+0 MPC (including Tritium), the actual concentration discharged to Lake Michigan was 3.70E-4 MPC when considering monitor tank flow rate (1.24E+2 gpm) and dilution water flow rate (1.20E+6 gpm). Therefore, 10CFR20 limits were not challenged. <br /><br /> The primary factor of this event is the failure of the monitor to actuate the discharge isolation valve, RRV-285, while the radiation monitoring device (RRS-1001) was in a Hi Fail status. The root cause although not conclusive, is attributed to a shorted interrupt logic line which kept the monitor from alarm checking while in the High Fail status. A secondary factor is attributed to the failure of the operator to recognize the significance of a "Hi Fail" status.
3151991004 | Cook 1 | 05/12/1991 | 06/11/1991 | 9106180298 | <strong>Reactor Protection System Actuation Due to Reactor Coolant Pump Bus Undervoltage Caused by Main Generator Voltage Regulator Failure</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1991 at 0826 hours while performing a main generator "maximum reactive capability" test, a Reactor Protection System actuation (reactor trip sequence) occurred.<br /><br /> The reactor trip was due to an undervoltage condition sensed on the reactor coolant pump (4KV) busses. An investigation concluded that the bus undervoltage condition was due to a decrease in main generator output voltage. This decrease resulted from a transfer from automatic to manual control of the main generator voltage, which was initiated by the malfunction of a protective "exciter field current limiter" device. <br /><br /> The main generator voltage regulation system "exciter field current limiter panel" has been determined to be defective. This component will be replaced. Changes have been made to appropriate operating procedures requiring the matching of manual and automatic main generator voltage regulator setpoints. This will avoid large deviations between setpoints and will enhance electrical distribution system stability during any future transfers of main generator voltage regulation from automatic to manual control.
3151991005 | Cook 1, Cook 2 | 07/18/1991 | 10/31/1991 | 9111060331 | <strong>Design Documents Could Be Located That Would Demonstrate the Capability of the Diesel Generators Ventilation and Exhaust Structures to Withstand the Effects of a Tornado</strong><br /><i>Abstract:&nbsp;</i>This revision is being submitted to provide preventive actions. During an Engineering Review, design documents could not be located that would demonstrate the capability of the Emergency Diesel Generator (EDG) combustion air engine exhaust, and room ventilation systems to withstand the effects of a tornado. Components found to be potentially vulnerable included the combustion air intake filter and silencer, the EDG exhaust stack and silencers, and the duct work associated with the room ventilation supply of the Plant's four EDGs. Upon recognition of this condition, actions were taken to provide a pressure equalization path to protect the ventilation duct work and the intake air silencer from the postulated differential pressure loads. The NRR granted a 30 day exemption of the Tornado Design Criterion to allow modification of the specific components mentioned. Modifications to the outside structures were completed on August 16, 1991. An additional damper will be installed on the EDG Room ventilation supply to isolate the Internal duct work from tornado effects. This damper is expected to be installed by December 31, 1991.
3151991006 | Cook 1 | 11/29/1990 | 08/23/1991 | 9108270163 | <strong>Personnel Error During The Design Change Process Resulted In Being Outside The Design Basis For Separation Of Safety Related And Non-Safety Related Circuits</strong><br /><i>Abstract:&nbsp;</i>The design of an electrical distribution circuit associated with Unit 1 CD Emergency Diesel Generator (EDG) was discovered to be in non-conformance with 10CFR50 Appendix A, General Design Criteria 17 and 22, from November 29, 1990 through July 24, 1991. This resulted from a design change which, through the removal of a circuit breaker, caused a safety related Essential Safety System (ESS) power supply circuit to be directly connected to a non-safety related Balance of Plant (BOP) circuit. Had a fault on the BOP circuit occurred simultaneously with a condition requiring the diesel generator to operate, the loss of power to the DG1CD auxiliaries could have affected extended EDG operation. A design change was completed on July 24, 1991, which reinstalled the breaker and restored the required isolation point. <br /><br /> The design change which caused the breaker to be removed was based on an electrical breaker coordination study conducted in 1988 which incorrectly identified the BOP Motor Control Center as a safety related component. To prevent a recurrence of this type of error, design procedures were revised and extensive training of design personnel was completed.
3151991007 | Cook 1 | 08/19/1991 | 11/15/1991 | 9112020127 | <strong>Shutdown Rods Mispositioned During Attempt To Move Control Rods Due To Malfunction Of Multiplexing Relay In The Rod Control System</strong><br /><i>Abstract:&nbsp;</i>This revision provides information on the results of the root cause analysis and corrects the Failed Component Identification information. On August 19, 1991, during routine surveillance testing of the full length rods, Control Bank A was ordered into the core by the Rod Control System but appeared not to move into the core by observation of the Analog Rod Position Indication. Further positioning of Control Bank A resulted in an Urgent Alarm being received. Initial troubleshooting of the Rod Control System found no reason for the Urgent Alarm and it was reset. The rods were moved per the test requirements and the surveillance completed. <br /><br /> At approximately 1200, a rod misalignment in Shutdown Bank A, Group 2 was suspected due to additional small amount of dilution required to keep thermal power at the pre-surveillance level and a decrease in the Analog Rod Position Indication for Shutdown Bank A, Group 2 in relation to pre-surveillance readings. At 1305 hours the flux mapping system was used to determine that the 4 rods of Shutdown Bank A, Group 2 were inserted approximately 6 steps into the core. Further troubleshooting of the Rod Control System discovered a failure of the 2AC Power Cabinet Multiplexing Relay, MXR-1. It was replaced and proper operation of the Rod Control System was verified. The misaligned rods of Shutdown Bank A were brought out to the top of the core and normal operation resumed at 1605 hours.
3151991008 | Cook 1, Cook 2 | 09/24/1991 | 10/24/1991 | 9110300308 | <strong>Four Radioactive Sealed Sources Not Leak Tested In Accordance with Technical Specification Due to Misclassification</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1991 it was determined that four radioactive calibration sources had not been leak tested in accordance with Technical Specifications 3/4.7.7 (Unit 1) and 3/4.7.8 (Unit 2). <br /><br /> The tests had not been performed since the sources were received on site in April of 1987. The reason for the tests not being performed is that they had been misclassified as unsealed sources due to inadequate procedural detail. When it was determined that the sources were actually sealed, leak tests were performed. The results of the tests were satisfactory, less than 0.005 microcuries of removable contamination, In addition, all sources were evaluated for the appropriate classifications. <br /><br /> To prevent recurrence an improper example has been removed from the procedure. Further, additional enhancements to the procedure and technician training are planned.
3151991009 | Cook 1 | 09/27/1991 | 10/25/1991 | 9111010200 | <strong>Inoperable Fire Damper Not Properly Compensated for Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1991, while conducting testing of the Unit One Reactor Cable Tunnel (RCT) CO sub 2 system, a Performance Technician discovered that the CO sub 2 pop-off chain for a fire damper had been wired to the CO sub 2 piping, thus rendering the fire damper inoperable and in non-compliance with Technical Specifications. <br /><br /> It was determined that a fire would not propagate due to the inoperable damper because: 1) the combustible loading in the fire zone is low; 2) any fire in these areas would be detected by available ionization type detectors while the fire is in an incipient stage; 3) manual fire fighting equipment is readily available for use by the fire brigade; 4) the subject fire damper would perform as designed provided the CO sub 2 pop-off was removed, which could have been done either manually by the fire brigade, if conditions permitted, or by the melting of a fusible link in the chain; 5) the low pressure CO sub 2 Systems protection zones have the capability of providing multiple dumps of CO sub 2 if the fire brigade deemed it necessary; 6) the low combustible loadings in subject zones, coupled with the location of all combustibles would make ignition of combustibles located in the adjacent fire zone by heat convection and/or radiation unlikely. <br /><br /> The wiring open of the fire damper was determined to be an isolated incident. The pop-off was immediately installed correctly. The fire damper was then tested and declared operable. Based on a Plant survey, retraining will be conducted to applicable personnel on appropriate response to inoperable fire dampers.
3151991010 | Cook 1, Cook 2 | 10/16/1991 | 11/12/1993 | 9311170232 | <strong>Liquid Release to Unrestricted Area in Violation Of Technical Specification Due to Poor Human Factors in the Design and Operation of the Release Monitor</strong><br /><i>Abstract:&nbsp;</i>This revision is being submitted to update corrective action. <br /><br /> On October 16, 1991, at approximately 1300 hours, a sampled but unmonitored liquid release occurred when the liquid radwaste effluent header sample gamma radiation detector RRS-1000 went into an external fail status change alarm. At that time the alarm was acknowledged by depressing the acknowledge button. This action also bypasses the trip functions which allows opening of the waste release isolation valve to initiate sample flow to above the low flow trip setpoint of 3.1 gpm. To re-arm the trip function the sample flow must be increased to 5.5 gpm. During this release the re-arming flow rate was never reached. <br /><br /> Enhancements were made to the liquid waste release procedure to require increasing the sample flow rate to the level required for arming the trip setpoint. In addition, to aid the operators in identifying the alarm condition the duration of the audible alarm was increased to approximately 8 seconds. A distinctive audible tone was installed to distinguish this alarm from other control room alarms. Actions have been taken to address a trip logic concern by a design change to suppress transient loading on alarm relay contacts.
3151991011 | Cook 1 | 06/10/1991 | 05/07/1992 | 9205130192 | <strong>Emergency Diesel Generator Not Placed On Increased Surveillance Frequency When Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1991, unit one AB emergency diesel generator (EDG) was not placed on increased surveillance frequency as required by Technical Specification (TS) 3.8.1.1 (Electrical Power Systems, A.C. Sources), Table 4.8-1, which requires the EDG to be placed on increased surveillance frequency if the number of start failures are two or more in the last 20 start attempts. Unit one AB EDG failed to start during a normal surveillance run on June 3, 1991. Due to inadequate documentation of a valid start failure in December 1990, the June 1991 failure was not recognized as the second failure within the last twenty starts. The December 1990 failure was identified by the Diesel System Engineer as a valid failure; however, Operations Department records did not reflect this. <br /><br /> Operations staff have added a review by the cognizant Production Supervisor of all EDG start failures to ensure all Technical Specification requirements have been met. In addition, the Diesel System Engineer is currently logging and tracking all EDG start attempts independent of Operations Department records.
3161991001 | Cook 2 | 01/07/1991 | 02/11/1991 | 9102150161 | <strong>A Roving Firewatch (FW) was Posted Instead of the Required Continuous FW Due to Misinterpretation of the TS. 3.7.9.2 Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1991, at 0856, the fire protection sprinkler system for the turbine-driven auxiliary feedwater pump (TDAFP) room and the auxiliary feedwater (AFW) pump corridor was removed from service and a roving firewatch (FW) was established in the TDAFP room instead of the required continuous FW. The Unit Supervisor (senior reactor operator SRO! licensed) reviewed Technical Specification (TS) 3.7.9.2 and TS table 3.7-5B to determine the FW requirements. The TS table describes the AFW pump corridor and the TDAFP room in the same line item entry. The TS 3.7.9.2 action statement allows establishing a roving FW if there is operable fire detection in the area. The Unit Supervisor interpreted the TDAFP room and AFW pump corridor as being one area and that the operable fire detection in AFW pump corridor allowed establishing a roving FW. The fact that the TDAFP room doors to the AFW corridor are administratively controlled in the open position seemed to support this interpretation. A second SRO reviewed and concurred with the Unit Supervisor's interpretation. The sprinkler system was restored to operable status at 1625 on January 8, 1991. On January 23, 1991, it was identified that a continuous FW should have been established in the TDAFP room. This event was reviewed with the involved individuals and a lessons learned memo was issued to Operations Department personnel.
3161991002 | Cook 2 | 02/20/1991 | 03/22/1991 | 9103280137 | <strong>Missed Surveillance of a Single Fire Damper Due to Inadvertent Omission of Damper from Procedure During Procedure Revision</strong><br /><i>Abstract:&nbsp;</i>On 2-20-91, while revising the inspection procedure for fire dampers protecting safety-related areas, it was discovered that a previous procedure revision had inadvertently omitted a fire damper from the inspection list. Due to the omission, subsequent surveillance performance using the procedure did not include the omitted damper. The Plant's Technical Specifications require the performance of a visual inspection of each fire damper and its associated hardware at least once per 18 months. Prior to the omission, the damper was part of the procedure and had been properly surveilled. <br /><br /> At the time of discovery, the omitted damper was visually and functionally inspected and accepted. The damper showed no adverse effects due to the extended time interval and remained within specification during the unsurveyed period. Current Administrative Controls governing procedure revision review requirements will reduce the probability of similar events.
3161991003 | Cook 2 | 03/13/1991 | 04/12/1991 | 9104180156 | <strong>Condenser Air Ejector Noble Gas Not Sampled And Analyzed In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1991 at 1857, SRA-2905, the Condenser Evacuation System Noble Gas Monitor was declared out of service. From March 13, 1991 at 1948 hours to March 14, 1991 at 1550 hours compensatory sampling in accordance with Technical Specification 3.3.3.10, Table 3.3-13, Item 2a was not conducted due to difficulties in obtaining a sample at the normal sampling point. The cause of this event was personnel error. <br /><br /> No radioactivity has been detected in the Unit 2 secondary system since the Steam Generator Repair Project. In addition, the Steam Generator Blowdown Radiation Monitors were operable and would have indicated a radioactivity transient in the secondary system. Therefore, we believe this event did not pose a threat to the health and safety of the public.<br /><br /> After discovery of an appropriate sampling point the eight hour sampling frequency was resumed. 12 THP 6020 LAB.038, Techniques of Gaseous Sampling, was revised to allow sampling of the Condenser Air Ejector at an alternate sample point. In addition, Chemical Section Supervisory personnel were counselled concerning the significance of Technical Specification required sampling.
3161991004 | Cook 2 | 03/13/1991 | 04/12/1991 | 9104180309 | <strong>Reactor Protection System Actuation Due to Ice and Snow Damaging Off-Site Electrical Transmission Lines</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1991 at 0651 hours, the Unit 2 reactor tripped as a result of a turbine trip generated by a moisture separator-reheater (MSR) high water level trip. The turbine-generator trip and reactor trip were a result of off-site electrical transmission system disturbances. Ice and snow damaged 765 KV transmission lines which caused a significant load rejection on the main turbine. The closing of the main turbine control valves in response to the load rejection created a MSR pressure transient which actuated the MSR high water level trip and tripped the main turbine and reactor. The plant was stabilized in Mode 3. <br /><br /> Abnormalities noted during the event included the electronic overspeed trip of the turbine driven auxiliary feedwater pump, closure of one of the four main steam isolation valves, and apparent slow closure of the #4 combined intercept valve. All equipment malfunctions were reviewed with no unreviewed safety questions and the reactor bus returned critical on March 15, 1991 at 1113 hours.
3161991005 | Cook 2 | 06/14/1991 | 07/15/1991 | 9107220223 | <strong>Bolts Removed from Pressurized Essential Service Water Line Expansion Joint Due to Reversed Component Labels</strong><br /><i>Abstract:&nbsp;</i>The west ('W') essential service water (ESW) train was made inoperable at 2146 on 6/13/91 in preparation for replacement of an 8-inch expansion joint labelled as 2-XJ-54W. At 0600 on 6/14/91, Maintenance personnel began to remove the flange bolts from the expansion joint. All of the flange bolts were removed at about 0700. The expansion joint remained lodged in place and water sprayed from the flanges. The water was initially believed to be either from trapped water or isolation point leakby. At 1240, however, it was identified that the expansion jointed labelled as being on the 'W' ESW train was actually on the east ('E') ESW train and the bolts were reinstalled at 1317. The Engineering review of this event determined that the water lossed out the flange was insignificant and that the expansion joint would have remained in place during a design basis earthquake. This event is being voluntarily reported as the analysis indicates the 'E' ESW train remained operable.<br /><br /> The cause of the labelling problem could not be determined. The labeling problem with the 2-XJ-54 expansion joints was corrected on 6/14/91. A walkdown was performed on similar expansion joints in unit 1 and 2. One additional problem was found and corrected in unit 2 on 6/19/91. The labelling process was reviewed and determined to be adequate with this event being caused by a unique combination of circumstances. A lessons learned memo was issued 7/9/91 to Operations and Maintenance personnel on this event.
3161991006 | Cook 2 | 08/01/1991 | 08/30/1991 | 9109040343 | <strong>Reactor Trip-Turbine Trip from Main Generator Protective Relay Operation During Failure of a Main Generator Output Breaker Current Transformer</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1991, at 1931 hours, the Unit 2 reactor tripped as a result of a turbine trip generated by the generator differential protective relays operating caused by a fault/explosion of the phase three current transformer (CT) of the main generator output breaker. The CT was disassembled and inspected. The inspection revealed that the CT had an internal failure, possibly arising from past stresses on the CT. The American Electrical Power Nuclear Organization will be taking responsibility for future scheduling of the predictive and preventive maintenance activities related to switchyard CT internal deterioration detection, an activity which had not been prudently applied to this particular CT prior to the event. <br /><br /> Abnormalities noted during the event included the electronic overspeed trip of the turbine-driven auxiliary feed pump as the operator was removing it from service, and closure of one of the four main steam isolation valves, which should have stayed open. The turbine-driven auxiliary feedwater pump was immediately reset and placed in standby, and the closed main steam isolation valve was promptly reopened.
3161991007 | Cook 2, Cook 1 | 08/02/1991 | 12/30/1996 | 9701060104 | <strong>Simulator Scenario Identified Flowpath That Diverted ECCS Flow, Caused by Plant Design/Emergency Response Guidelines</strong><br /><i>Abstract:&nbsp;</i>This LER revision is being submitted to update the dose rate and leakage assumptions associated with this event, to revise the corrective actions, and to reflect additional information discovered as part of the Design Basis Documentation Program.<br /><br /> On 8-2-91, a 'small break loss of coolant accident' run on the Plant simulator identified a flowpath which may be established by plant conditions and the Emergency Operating Procedures (EOPs) with the potential to divert water away from the emergency core cooling system and the containment building. The flowpath was from the Centrifugal Charging Pump discharge through an emergency leakoff valve, through the seal return line safety valve to the volume control tank (VCT), and through the VCT safety valve to the chemical and volume control system holdup tanks. <br /><br /> A review of the finding concluded that the amount of water which could be diverted did not significantly affect core cooling. However, the diverted water would be discharged from the containment building. Analysis of the potential dose rate from the diverted water to the whole body at the site boundary was calculated to be insignificant compared to the 10 CFR 100 accident dose limit and even within the 10 CFR 20.105 dose limits for unrestricted areas during normal operations for 1% failed fuel. Additional calculations assuming 50% of the core iodines were present in the leaking fluid demonstrated that total LOCA doses at the site boundary and the low population zone are also within the 10 CFR 100 limits. Control room doses are within 10 CFR 50 Appendix A Criterion 19 limits. The condition identified has the potential to be a generic issue for Westinghouse-designed plants. The appropriate EOP was revised to address the simulator finding.
3161991008 | Cook 2 | 11/05/1991 | 11/27/1991 | 9112060241 | <strong>Containment Pressure Relief Performed with the Radiation Monitor Trip Function Blocked Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991 at 1906 hours, the containment pressure relief valves were opened to perform a containment pressure relief while the valve's associated radiation monitoring system trip/block switches were in the BLOCK position. The pressure relief valves are allowed to be opened by Technical Specification 3.6.3.1, Containment Isolation Valves, on an intermittent basis under administrative control. The opening of these valves with the radiation monitoring system switches in BLOCK was not the proper administrative control for the conditions that existed at the time. Due to a misinterpretation of a procedure step, a Reactor Operator (RO) trainee signed off the step in the containment pressure relief procedure while the switches were in the BLOCK position; however, the switches should have been in the NORMAL position. This error was not identified by the Unit Supervisor (US) or the RO until the containment pressure relief was completed. The cause of this event was improper trainee control. Neither the US nor the RO were in direct contact with the RO trainee when the procedural error occurred. The Operations Department Superintendent issued letters to all licensed operators, RO trainees and shift supervisors emphasizing individual responsibility for controlling trainee activities in the control room. This event did not adversely impact the public health and safety.
3161991009 | Cook 2, Cook 1 | 11/12/1991 | 12/12/1991 | 9112170536 | <strong>Inoperable Ice Condenser Due To Incorrect Flow Passage Inspections</strong><br /><i>Abstract:&nbsp;</i>An Engineering Evaluation revealed that the Ice Condenser Flow Passage Inspection, to satisfy Ice condenser Technical Specification Surveillance requirement, did not include the entire flow area assumed in the short term containment integrity analyses presented in the Updated Final Safety Analysis Report (UFSAR). Since the flow area assumed in the containment integrity analysis was not fully inspected, the potential existed for an unacceptable degradation of the flow area. <br /><br /> The deficiency was determined to be reportable on November 12, 1991, and both Unit 1 and 2 Ice Condensers were declared inoperable. The Surveillance Test Procedure was revised to include the new inspection areas. The Ice Condenser Flow Passages in both units were inspected, in accordance with the revised procedure, and found to be operable prior to expiration of the Technical Specification Limiting Condition for operation time limit.
3161991010 | Cook 2 | 11/15/1991 | 12/16/1991 | 9112260303 | <strong>Reactor Protection System Actuation Due to Low-Low Steam Generator Level When Steam Pressure Increased from Main Turbine Control Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1991 at 1113 hours, the Unit 2 reactor tripped as a result of a low-low Steam Generator (SG) water level in SG #21. Prior to the reactor trip, instrumentation was being installed on the main turbine control fluid circuit. The purpose of this instrument was to investigate oscillations of control valve A which was scheduled to be tested later that evening. A pressure indicator which measures the output of the turbine operating device was to be isolated and another transmitter was to be installed in parallel to it. However, unknown to personnel involved, worn threads on the stem of the manual isolation valve prevented the pressure indicator from being completely isolated. As a drain plug was removed to vent pressure from the instrument isolation valve, pressure on the output of the operating device was also decreased. This effectively lowered the setpoint supplied to the speed governor, which compares actual turbine speed to the operating device setpoint, and fully closed the high pressure and low pressure turbine control valves. With the steam supply isolated, SG pressure rapidly increased and caused SG level to decrease below the reactor trip setpoint. <br /><br /> The root valve's bonnet was replaced and damaged stem threads were repaired. During the outage, repairs were also completed to reduce the turbine load swings experienced during valve testing. A review of the work control process will be performed to identify any enhancements that can be added to reduce the probability of an unplanned actuation occurring from similar activities in the future. Any change indicated by the review will be implemented by March 30, 1992.
3171991001 | Calvert Cliffs 1, Calvert Cliffs 2 | 01/29/1991 | 02/28/1991 | 9103050463 | <strong>Design Error In The Emergency Diesel Generator Air Start System Results In Administratively Inoperable Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1991, it was identified that a small portion of Non-Safety Related tubing in the Air Start System for Emergency Diesel Generator No. 21 (EDG) was not seismically qualified. Failure of this 1/4 inch tubing would create a potential leak path from both of the independent Safety Related EDG air start headers and potentially none of the three EDGs could be started. At the time of discovery, Unit 1 was at 100 percent power and Unit 2 was in Cold Shutdown (MODE 5) at a temperature of 113 degrees Fahrenheit and atmospheric pressure. <br /><br /> The cause of the event was an error in the design of the EDG Air Start System. <br /><br /> Tubing for two of the three EDGs were subsequently determined to be capable of withstanding a seismic event. If a seismic event occurred simultaneously or after an event requiring the EDGs start, the EDGs would most likely have started before the air headers lost enough air to prevent a start. This condition resulted in an event of low safety significance.<br /><br /> Corrective actions include declaring the EDGs inoperable, entering appropriate Technical Specification ACTION Statements, isolating the tubing and restoring OPERABILITY of the EDGs, initiating a temporary modification to restore normal charging of the EDG Air Start System, and initiating a permanent modification to correct the non-seismically qualified tubing.
3171991002 | Calvert Cliffs 1, Calvert Cliffs 2 | 04/19/1991 | 05/28/1991 | 9106050270 | <strong>Emergency Diesel Generator Slow Start Times Allowed Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1991 a system engineer reviewing Surveillance Test Procedure (STP) O-8C noted that it did not meet the requirements of Technical Specification (TS) Surveillance 4.8.1.1.2.c. The TS Surveillance requires that at least once every 184 days, each Emergency Diesel Generator (EDG) start from an ambient condition and accelerate to at least 900 rpm in 10 seconds or less. The STP incorrectly verified that the EDG reached 810 rpm in the required time. <br /><br /> Upon further review, he found several instances where the 21 EDG probably did not reach 900 rpm in less than 10 seconds but was declared OPERABLE by the STP in violation of the TS. <br /><br /> The root cause of this event was inadequate procedural change management when revised TSs were implemented in 1977. <br /><br /> The affected STPs have been revised to require that the EDGs reach 900 rpm in 10 seconds or less as required by the TS. This is done by relating rpm to measured electrical output frequency. <br /><br /> A review of all TS Surveillance requirements for technical adequacy is currently underway. This review is structured to identify errors of this type.
3171991003 | Calvert Cliffs 1 | 10/01/1991 | 10/31/1991 | 9111070117 | <strong>Reactor Protection System Actuation and Plant Trip Due to Low Steam Generator Water Levels Caused by Loose Electrical Fuse</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1991 Calvert Cliffs Unit 1 tripped from 93 percent power due to low Steam Generator (SG) water levels. The low SG water levels resulted from a loose fuse in the power supply to 12 Feedwater Regulating Valve (FRV) differential pressure (dp) controller and 12 Steam Generator Feed Pump (SGFP) turbine speed controller. A bent fuse clip caused an electrical discontinuity. The fuse holder has been replaced and personnel whose duties involve fuse manipulation will be trained on proper fuse installation and removal.
3171991004 | Calvert Cliffs 1 | 04/07/1990 | 08/09/1991 | 9108130153 | <strong>Missed Surveillance Due to Scheduling Error</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1991, the Operations Functional Surveillance Test Coordinator discovered that Calvert Cliffs Unit 1 had been in a condition prohibited by the plant's Technical Specifications in that MODE 3 was entered on April 7, 1990 without completion of all applicable Surveillance Requirements (SR). Specifically, SR 4.3.2.1.1(1.d) had not been completed prior to entering MODE 3. The surveillance has a frequency of 18 months and had been last completed on April 10, 1988. The cause for the prohibited condition was personnel error coupled with insufficient reference documentation and inadequate review in preparing the surveillance test schedule. The appropriate surveillance frequency has been corrected and an approved reference document has been approved. Additionally, procedural control of surveillance frequency changes has been implemented to prevent recurrence.
3171991005 | Calvert Cliffs 1 | 07/30/1991 | 08/29/1991 | 9109050234 | <strong>Surveillance Test Not Performed Within Technical Specification Prescribed Time Interval Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1130, July 30, 1991, it was determined that a surveillance test required by Technical Specifications was not performed within the required time interval. The circuitry for smoke detectors in the Unit-1 Purge Air Supply Room was not tested every six months as required. At the time, Unit-1 was in MODE 1 at 100 percent power.<br /><br /> The causes of this event were personnel error by the procedure writer and inadequate technical review. This event did not result in any safety significant consequences. <br /><br /> The smoke detectors were tested and performed satisfactorily. <br /><br /> The Surveillance Test Procedure (STP) has been corrected to include the required tests every six months. A program is in progress to review the technical adequacy of STPs at Calvert Cliffs. Personnel action was taken with the procedure writer and technical reviewer. Expectations on STP accuracy will be reiterated to STP writers and technical reviewers.
3171991006 | Calvert Cliffs 1 | 07/24/1991 | 08/30/1991 | 9109100389 | <strong>Failure to Follow Technical Specification Action Statement Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1991, a non-conforming condition existed at Calvert Cliffs with respect to Technical Specification 3.3.1.1 ACTION Statement 2 for Unit 1 in that the Reactor Protection System channel B trip unit 1 was taken out of bypass without declaring the channel OPERABLE or placing it in a tripped condition. The cause of this prohibited condition was personnel error. The Shift Supervisor involved has been counselled and all licensed operators have been educated on this event.
3171991007 | Calvert Cliffs 1 | 12/24/1991 | 01/23/1992 | 9201290139 | <strong>Emergency Air Lock Inner and Outer Doors Open Simultaneously Due to Mechanical Malfunction</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1991, maintenance personnel, unaware that the Unit 1 Containment Emergency Air Lock inner door was open, opened the exterior door, briefly breaching containment. Containment integrity was restored within one minute. The interior door remote position indication did not indicate that the door was open and an interlock mechanism that normally prevents both doors from being open simultaneously, did not function properly. <br /><br /> The cause is attributed to mechanical malfunction which includes a slipped chain and misaligned cam in the interlock mechanism and inaccurate interior door position indication. <br /><br /> The chain and cam were realigned and the mechanism verified OPERABLE. A sign has been placed next to the exterior door warning personnel of the loose chain and cautioning them to open the door carefully. Appropriate personnel are being briefed on the details of this incident and cautioned against opening the door before pressure is equalized across it.<br /><br /> Additional testing to confirm the cause of the mechanical malfunction will be conducted when ALARA conditions and Technical Specification OPERABILITY requirements permit. Should it become necessary to use the Emergency Air Lock prior to implementation of final corrective actions, we will implement additional controls to ensure personnel entering the air lock are aware of the status of both air lock doors.
3171991008 | Calvert Cliffs 1 | 12/29/1991 | 01/28/1992 | 9201310246 | <strong>Inadvertent Actuation of the Auxiliary Feedwater Actuation System due to Circuit Design</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1991, an inadvertent actuation of the Auxiliary Feedwater Actuation System (AFAS) occurred at Calvert Cliffs Unit 1. At the time of the event, Unit 1 was in MODE 3 (HOT STANDBY) with the Reactor Coolant System at 523 degrees Fahrenheit and 2250 psia. Preparations were underway to enter MODE 2 (STARTUP). <br /><br /> The cause of the event is the sensitivity of the original AFAS START logic circuit design to induced noise pulses. This sensitivity was masked by the time delay in the circuit. The modification to the logic circuit relocated the time delay and revealed the unexpected susceptibility of this circuit to noise induced pulses such as electro static discharge. The actuation is attributed to an electro static discharge on the AFAs cabinet while a licensed utility operator was shutting an adjacent AFAS sensor cabinet door. <br /><br /> The vendor has been requested to design and provide hardware for a corrective modification. To prevent recurrence the AFAS cabinet area is roped off and access to the area requires Shift Supervisor permission. Caution tags are in place to warn plant personnel of the potential for spurious actuation of the AFAS cabinets due to static charge. Previously established electro static discharge countermeasures were expanded for work in and around all AFAS cabinets.
3171991009 | Calvert Cliffs 1 | 11/26/1991 | 12/26/1991 | 9201060275 | <strong>Loss of OPERABLE HPSI Train Due to Inoperable Pump Breaker</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1991 while operating at 100 percent rated thermal power, Calvert Cliffs Unit 1 entered plant Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 when all High Pressure Safety Injection (HPSI) trains became inoperable. The plant remained in LCO 3.0.3 for approximately 35 minutes. While operating with one OPERABLE HPSI train, that train's pump breaker failed to align for starting. The cause of this event was a mispositioned fiber spacer that interfered with an operating-mechanism-solenoid plunger. Investigative efforts are continuing with the possibility of manufacturing or design defect being evaluated. If shown to have existed, Baltimore Gas and Electric shall supplement this report, documenting the cause and additional corrective action. Corrective action included replacing the breaker with a suitable replacement to restore operability and repairing the non-aligning breaker. Corrective action that continues includes inspecting 16 of 60 safety-related breakers in the field and including an operating- mechanism inspection in scheduled PMS to accommodate inspection of all remaining safety-related breakers.
3181991001 | Calvert Cliffs 2 | 03/12/1991 | 04/26/1991 | 9105020163 | <strong>Reactor Coolant Inadvertently Drained Through Containment Spray Header Due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1991 at 12:48 a.m., plant operators inadvertently drained approximately 1900 gallons of Reactor Coolant System water through the Calvert Cliffs Unit 2 containment spray ring and a drain line. This incident occurred while operators were lining up to fill the Unit 2 Safety Injection Tanks. <br /><br /> The root cause of this event was personnel error in that the Plant Watch Supervisor misinterpreted procedures, inappropriately performed procedure steps concurrently, and failed to verify the position of an isolation valve. Verbal communication by the operators in the field was deficient.<br /><br /> Appropriate personnel actions were taken. <br /><br /> All shift crews were instructed on management expectations concerning correct procedure interpretation, verbal communications, and appropriate lines of authority. <br /><br /> We are revising the procedural controls for performing steps concurrently.<br /><br /> We are enhancing continuing training coverage of important control processes in the operations area where deviations in the field could reduce the defense-in-depth intended by these controls.
3181991002 | Calvert Cliffs 2 | 03/27/1991 | 04/26/1991 | 9105010203 | <strong>Engineered Safety Features Actuation System (ESFAS) Initiation Due to Operator Error While Restoring ESFAS Logic Cabinet</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1991, at 11:51 a.m., an inadvertent Safety Injection Actuation Signal (SIAS) was initiated on Calvert Cliffs Unit 2. The incident occurred while utility licensed operators were attempting to re-energize the Engineered Safety Features Actuation System AL Actuation Logic Cabinet. At the time of the event Unit 2 was in Cold Shutdown (MODE 5) with a Reactor Coolant System (RCS) temperature of 140 degrees Fahrenheit and a pressure of 220 psi. Unit 1 was operating at 100 percent power. <br /><br /> The root cause of the event was personnel error by the Senior Reactor Operator (SRO) who was directing the evolution. The SRO failed to fully comprehend two CAUTION statements contained within the procedure he was using and directed a Control Room Operator to perform steps out of order. <br /><br /> The inadvertent SIAS caused the closure of the Chemical and Volume Control System isolation valves and the start of a second charging pump. Shutdown Cooling was in-service maintaining RCS temperature and the High Pressure Safety Injection system was lined up for Low Temperature Over Pressure Protection. Both of these systems were unaffected by the SIAS activation.<br /><br /> Immediate corrective actions included counseling the operators and informing other personnel of the event. Continuing actions focus on improving procedure usage, pre-evolution briefings, involvement of supervisory personnel, and the content of procedures.
3181991003 | Calvert Cliffs 2 | 04/09/1991 | 05/07/1991 | 9105090363 | <strong>Inadvertent Actuation of Reactor Protection System While Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1991 at 0137, an inadvertent Reactor Protection System (RPS) actuation occurred at Calvert Cliffs Unit 2 while the plant was conducting Control Element Assembly testing. The plant was in Hot Shutdown, at a Reactor Coolant System Pressure of 2250 psia and temperature of 532 degrees Fahrenheit. The incident occurred when personnel who intended to key a portable radio and observe for RPS trip actuations (in the performance of troubleshooting Radio Frequency Interference problems) accidentally keyed the radio out of sequence. <br /><br /> The root cause of the event was personnel error complicated by a combination of the portable radio's design and standard controls for minimizing contamination.<br /><br /> Immediate corrective actions included an entry on the Shift Supervisor's log informing personnel not to take portable radios in the vicinity of the flow transmitters and a similar entry made on the Shift Turnover Sheet. Actions to prevent recurrence include permanent signs outside of containments accesses, changes to site procedures, informing all site portable radio users of the restrictions inside the containments, and reassessing industry experiences to ensure current plant controls are adequate.
3181991004 | Calvert Cliffs 2 | 05/04/1991 | 05/31/1991 | 9106050278 | <strong>Inadvertent Actuation of Auxiliary Feedwater System During Main Turbine Overspeed Test</strong><br /><i>Abstract:&nbsp;</i>At 2122 on May 4, 1991 at Calvert Cliffs Unit 2, an Auxiliary Feedwater Actuation System (AFAS) actuation signal was received during a Main Turbine overspeed test. A steam transient resulted in an erroneous Steam Generator (SG) level signal which actuated AFAS. At the time of this event, Unit 2 was in MODE 1 (Power Operation) at a power level of 10 percent.<br /><br /> The cause of this event was a design deficiency in that the Wide Range SG Level instrument was not designed to provide accurate level indications during extreme pressure and steaming transients. Interaction of high speed AFAS circuitry with the level instrument resulted in an inadvertent AFAS actuation. <br /><br /> Corrective Action for this event includes implementing a facility modification to prevent SC pressure and steaming transients from causing unwanted AFAS actuations. In the meantime, a procedure change will be utilized to prevent similar AFAS actuations from occurring.
3181991005 | Calvert Cliffs 2 | 05/02/1991 | 05/31/1991 | 9106050263 | <strong>Reactor Protective System Actuation and Plant Trip Due to a Loss of Feed Caused by Component Failure</strong><br /><i>Abstract:&nbsp;</i>At 1050 on May 2, 1991, a Low Steam Generator (SG) Level Reactor Protective System Trip occurred at Calvert Cliffs Unit 2 while attempting to control SG level oscillations at low power level. At the time of the trip, Unit 2 was operating in MODE 1 (Power Operation) at 8 percent power. The low SG level was caused by a loss of feedwater event when the operating SG Feed Pump (SGFP) was lost due to a speed controller failure. <br /><br /> The initiating loss of feed event was caused by a failed circuit board edge connector which prevented the operator from resetting the SGFP speed controller and restoring feed.<br /><br /> Immediate corrective actions included replacing the circuit board and connector, and inspecting like SGFP speed controllers for similar problems. A SGFP speed controller alignment procedure including functional test will be written, and this event will be included in the next cycle of Instrument Maintenance continuing training.
3181991006 | Calvert Cliffs 2 | 06/15/1991 | 07/15/1991 | 9107190077 | <strong>Unit 2 Shutdown Required by Plant Technical Specifications Due to Loss of Control Room Air Conditioning Operability</strong><br /><i>Abstract:&nbsp;</i>At 1400 on June 15, 1991 at Calvert Cliffs Unit 2, a plant shutdown as required by the plant Technical Specifications was conducted following a loss of Control Room Emergency Ventilation System operability. At the time of the event, Unit 2 was operating at 100 percent power. <br /><br /> The root cause of the loss of Emergency Ventilation operability was the lack of adequate procedural guidance in both maintenance and post-maintenance activities associated with the Control Room Air Conditioning (CR HVAC) System. This allowed the presence of non-condensible gases to be introduced to the operable train of CR HVAC when the alternate train was secured for maintenance. <br /><br /> Corrective actions included placing the plant in a mode of operation not requiring system operability, purging the No. 12 air conditioning system, improving existing procedures and guidance, and establishing a task force to identify problems and improve system availability.
3181991007 | Calvert Cliffs 2 | 07/11/1991 | 08/12/1991 | 9108140211 | <strong>Loss of Operable Boration Flowpath Due to a Failed Fuse</strong><br /><i>Abstract:&nbsp;</i>At approximately 2030 on July 11, 1991 at Calvert Cliffs Unit 2, it was determined that a B train failure of the No. 22 Boric Acid Storage Tank (BAST) heater circuit while the No. 12 Emergency Diesel Generator was out-of-service had administratively reduced the number of operable heat traced flowpaths from three to none. This reduction is not addressed in Limiting Condition for Operation (LCO) 3.1.2.2 which requires at least one flowpath. At the time of the occurrence, Unit 2 was operating at 100 percent power. Operating outside of LCO 3.1.2.2 required entry into LCO 3.0.3 which required restoration of the flowpath within one hour or action must be taken to shut the plant down. <br /><br /> The probable cause of this event is component failure of the control power fuse for the B train BAST tank heater. <br /><br /> Corrective actions included replacing the fuses and verifying the integrity and function of the control power circuit. Additional steps were taken to heighten sensitivity to equipment malfunctions during periods of reduced equipment availability.
3181991008 | Calvert Cliffs 2 | 10/30/1991 | 11/27/1991 | 9112020235 | <strong>Steam Generator Effluent Flow Rate Not Estimated Every Four Hours Per TS ACTION Statement Due to Operator Error and Insufficient Procedure Clarity</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1991, at approximately 0810, a condition prohibited by Technical Specifications (TS) was identified at Calvert Cliffs Unit 2. While draining Steam Generator (SG) No. 21, flow rate was not estimated every 4 hours when the discharge flow rate measuring device was not OPERABLE as required by TS 3.3.3.10. At the time, Unit 2 was in Cold Shutdown (MODE 5) at a temperature of 102 degrees Fahrenheit and a reactor coolant pressure of 100 psia. <br /><br /> The causes of the event were insufficient operator attention to detail and insufficient clarity of the applicable operating instruction. <br /><br /> There were no safety consequences associated with this event. <br /><br /> Corrective actions include personnel action, reemphasizing to the operators the importance of attention to detail, evaluating SG draining related procedures and clarifying them as necessary, instructing personnel to identify similar problems in other procedures for clarification, establishing a operations policy requiring a backup for Senior Reactor Operator reviews of TSs referenced by procedures, and providing the details of this event to all licensed operators.
3201991001 | Three Mile Island 2 | 01/21/1991 | 02/20/1991 | 9102270194 | <strong>Incorrect Containment Isolation Verification</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1991, during a review of the in-progress Containment Isolation Verification surveillance (4210-SUR-3244.01), it was determined that quarterly checks were not being performed on penetration isolation valve SGC-FV-2 as required. <br /><br /> Valve SGC-FV-2 had been inappropriately deleted from containment isolation valve surveillance procedure 4210-SUR-3244.01 during a revision. As a result, SGC-FV-2 was not verified closed for the period from April 18, 1990 to January 21, 1991. <br /><br /> The event was the result of personnel error. Insufficient action was taken to assure the comprehensiveness of the valve listing used for verifying containment isolation.<br /><br /> Immediate corrective action was taken to verify SGC-FV-2 closed. At the same time, a temporary change notice (TCN) was initiated to correct the inadvertent deletion of containment isolation valve SGC-FV-2 from the containment isolation verification surveillance. Two independent reviews were completed to assure the comprehensiveness of the containment isolation valve listing in the surveillance procedure. <br /><br /> The event is reportable per 10CFR50.73(a)(2)(i)(B).
3201991002 | Three Mile Island 2 | 03/08/1991 | 04/05/1991 | 9104080333 | <strong>Inadvertent Vaporization Of Accident Generated Water</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1991, the TMI-2 Processed Water Disposal System (PWDS) was operating in the "coupled mode" (i.e., evaporator coupled to the vaporizer) when a recirculation valve was found partially open. This condition permitted a portion of the accident generated water (AGW) feed to bypass the evaporator and mix with the evaporator effluent. The result was that approximately 120 gallons of AGW was vaporized and released to the atmosphere without being processed by the evaporator. <br /><br /> The event was the result of a design deficiency in that the location of the recirculation valve (i.e., floor level, in the middle of an equipment access path) requires the operators to routinely step over the valve to access equipment required for system operation. Apparently, an operator inadvertently kicked the valve/valve handwheel without realizing he had caused the valve to be repositioned. Upon discovery of the mispositioned valve, it was immediately closed. Other corrective actions taken were to terminate operations pending an assessment of the event, install a latchable valve handle on the valve at issue, and lower the alert level on the vaporizer influent radiation monitor to provide earlier warning of an off-normal condition. A long-term corrective action under consideration is to relocate the valve to eliminate the tripping hazard problem. <br /><br /> TMI-2 Tech. Spec. 3.9.13 states, "ACCIDENT GENERATED WATER shall be disposed of in accordance with NRC-approved procedures." Per the NRC-approved PWDS operating procedure, the recirculation valve was required to be shut during coupled mode operations. Therefore, PWDS operation in this manner, although inadvertent, was prohibited by the plant's Tech. Specs. and the event is reportable per 10 CFR 50.73(a)(2)(i)(B).
3201991003 | Three Mile Island 2 | 04/03/1991 | 05/03/1991 | 9105090340 | <strong>Processed Water Disposal System Valve Misalignment</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1991, the TMI-2 Processed Water Disposal System (PWDS) was operating in the "coupled mode" (i.e., evaporator coupled to the vaporizer) when a vaporizer blow-down valve was found closed. The purpose of this flow pathway is to draw-off solids from the vaporizer flash tank and recycle them to the evaporator for solidification and disposal. The closure of the blow-down valve has the potential to adversely impact the system decontamination factor (DF) of the PWDS; however, no impact was observed.<br /><br /> The event was a result of personnel error in that the evaporator operator did not follow the operating procedure. A contributing factor was an unwieldy procedure that did not lend itself to ease of use. Upon discovery of the mispositioned valve, the immediate corrective action taken was to open the valve and notify the TMI-2 Control Room. Longer term corrective actions include additional training for the evaporator operators and a revision to the PWDS operating procedure. <br /><br /> TMI-2 Tech. Spec. 3.9.13 states, "ACCIDENT GENERATED WATER shall be disposed of in accordance with NRC-approved procedures." Per the NRC-approved PWDS operating procedure, the blow-down valve was required to be open during coupled mode operations. Therefore, PWDS operation in this manner, although inadvertent, was prohibited by the plant's Tech. Specs. and the event is reportable per 10 CFR 50.73(a)(2)(i)(B). <br /><br /> This event is similar in nature to LER 91-02.
3201991004 | Three Mile Island 2 | 04/12/1991 | 05/10/1991 | 9105210057 | <strong>Processed Water Disposal System Sample Valve Misalignment</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, the TMI-2 Processed Water Disposal System (PWDS) was operating in the "coupled mode" (i.e., evaporator coupled to the vaporizer) when a vaporizer exhaust sample valve was found closed. A sample of the vaporizer exhaust is routinely analyzed to calculate the system decontamination factor (DF); it is not used to determine radionuclide release. <br /><br /> This event was a result of personnel error in that the evaporator operator did not follow the operating procedure. Contributing factors were the unwieldy nature of the relevant procedure (i.e., it does not lend itself to ease of use) and the decision to have the TMI-2 Control Room sign-off on a separate copy of the procedure. Upon discovery of the mispositioned valve, the immediate corrective actions taken were to open the valve and initiate an investigation into the cause of the mispositioning. The PWDS was subsequently shut down. Longer term corrective actions include additional training for the evaporator operators and a revision to the PWDS operating procedure. <br /><br /> TMI-2 Tech. Spec. 3.9.13 states, "ACCIDENT GENERATED WATER shall be disposed of in accordance with NRC-approved procedures." Per the NRC-approved PWDS operating procedure, the vaporizer exhaust sample valve was required to be open during coupled mode operations. Therefore, PWDS operation in this manner, although inadvertent, was prohibited by the plant's Tech. Specs. and the event is reportable per 10 CFR 50.73(a)(2)(i)(B). <br /><br /> This event is similar in nature to LERs 91-02 and 91-03.
3201991005 | Three Mile Island 2 | 06/26/1991 | 07/24/1991 | 9107290270 | <strong>Processed Water Disposal System Sample Valve Misalignment</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1991, the TMI-2 Processed Water Disposal System (PWDS) was operating in the "coupled mode" (i.e., evaporator coupled to the vaporizer) when a vaporizer exhaust sample valve was found closed. A sample of the vaporizer exhaust is routinely analyzed to calculate the system decontamination factor (DF); it is not used to determine radio- nuclide release. <br /><br /> This event was a result of either personnel error in that the evaporator operator did not follow the operating procedure or a design deficiency in that the valve must be "cracked" open to provide the required drip flow. Various contributing factors make the root cause of this event indeterminate. Upon discovery of the mispositioned valve, the immediate corrective actions taken were to open the valve and initiate an investigation into the cause of the mispositioning. The PWDS was subsequently shut down. Longer term corrective actions include a revision to the PWDS operating procedure and an engineering review of the sampling system. <br /><br /> TMI-2 Tech. Spec. 3.9.13 states, "ACCIDENT GENERATED WATER shall be disposed of in accordance with NRC-approved procedures." Per the NRC-approved PWDS operating procedure, the vaporizer exhaust sample valve was required to be open during coupled mode operations. Therefore, PWDS operation in this manner, although inadvertent, was prohibited by the plant's Tech. Specs. and the event is reportable per 10 CFR 50.73(a)(2)(i)(B). <br /><br /> This event is similar in nature to LERs 91-02, 91-03, and 91-04.
3211991001 | Hatch 1, Hatch 2 | 01/18/1991 | 02/11/1991 | 9102150132 | <strong>Remote Transmission Line Failure Coupled With Switchyard Breaker Failure Causes Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 01/18/91, at approximately 1500 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, a remote power transmission line failed at its attachment point to the supporting electrical tower. In addition, a breaker in the Plant Hatch 230 kV switchyard failed to fully open in response to the sensed electrical fault conditions resulting in the trip of the Unit 1 main transformer auxiliary lockout relay. This resulted in main generator and main turbine trips, which, in turn, resulted in a reactor scram. This also resulted in a loss of power to the Unit 1 nonessential electrical busses and the prevention of the normal automatic transfer to the alternate supply due to the transfer logic. Power was manually restored to nonessential loads within approximately 2 to 3 minutes allowing for the initiation of operator actions to restore feedwater flow. In the interim, to recover reactor water level, the High Pressure Coolant Injection system (HPCI) automatically initiated. Although it exhibited erratic behavior in the automatic mode, it was successfully controlled manually and water level was restored and maintained with HPCI until feedwater flow was restored. Reactor pressure was controlled by the turbine bypass valves.<br /><br /> The root causes of the scram were the failure of the high tension power line and the failure of the main breaker to fully open. The root cause of the erratic HPCI operation was component failure in the HPCI speed controller. <br /><br /> Corrective actions included repairing the failed power line, repairing the failed breaker, and replacing the failed HPCI speed controller.
3211991002 | Hatch 1, Hatch 2 | 02/03/1991 | 03/05/1991 | 9103050342 | <strong>Component Failure And Personnel Error Result In Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2/3/91 at approximately 0420 CST, Unit 1 and Unit 2 were in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, a partial, outboard Group 2 Primary Containment Isolation System (PCIS, EIIS Code JM) isolation signal was generated resulting in closure of some outboard Group 2 Primary Containment Isolation Valves (PCIVs, EIIS Code JM). This, in turn, resulted in the isolation of the Unit 2 Hydrogen and Oxygen Analyzer (EIIS Code IK) and Fission Products Monitoring (FPM, EIIS Code IK) systems. The isolation signal occurred due to a failed relay. A second ESF actuation occurred during the replacement of the failed relay. A relay apparently was bumped resulting in actuation of the "B" trains of the Unit 1 and Unit 2 Standby Gas Treatment (SBGT, EIIS Code BH) systems, isolation of the Unit 1 and Unit 2 Secondary Containments, and isolation of additional outboard Group 2 PCIVs. <br /><br /> The cause of the first event was component failure. The coil in relay 1C61-K24 failed, actuating the isolation logic for some of the outboard Group 2 PCIVs per design. The cause of the second event was personnel error. A plant electrician, while replacing relay 1C61-K24, apparently bumped nearby relay 1C61-K79. This actuated the initiation logic for the "B" trains of both units' SBGT systems, and the isolation logic for both units' Secondary Containments and additional outboard Group 2 PCIVs. <br /><br /> Corrective actions for this event included replacing the failed relay and counseling involved personnel.
3211991003 | Hatch 1, Hatch 2 | 02/10/1991 | 03/08/1991 | 9103140391 | <strong>Component Failure Results In ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2/10/91 at approximately 1537 CST, Units 1 and 2 were in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, the Main Control Room Environmental Control (MCREC, EIIS Code VI) system automatically transferred from the normal mode to the pressurization mode. The transfer occurred as designed when refueling floor Area Radiation Monitors (ARM, EIIS Code IL) 1D21-K601B and 1D21-K601D tripped on a high radiation signal. After the actuation occurred, licensed Operations personnel verified proper operation of the MCREC system and that an actual high radiation condition did not exist on the refueling floor. An investigation determined that the signal was the result of an upscale spike caused by loss of one of the power supplies to these ARMs. It was determined that a fuse internal to the power supply had failed. ARMs 1D21-K601B and D provide an input to the MCREC pressurization mode logic. The failed fuse was replaced and the MCREC system was returned to its normal mode of operation at approximately 1751 CST on 2/10/91. <br /><br /> The cause of the event is component failure. A fuse internal to one of the ARM power supplies failed. The fuse failure was investigated and appears to be a random failure. <br /><br /> Corrective actions for this event included replacing the fuse and returning the MCREC system to its normal mode of operation.
3211991004 | Hatch 1 | 02/12/1991 | 03/14/1991 | 9103200225 | <strong>Component Failure Causes Turbine Trip And Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 2/12/91 at approximately 0911 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, the unit scrammed on Turbine Stop Valve (TSV) closure. The main turbine tripped on a low Electrohydraulic Control (EHC) system hydraulic fluid pressure signal. Reactor water level decreased to approximately 3 inches above instrument zero and was restored to normal using the Reactor Feedwater Pumps (RFPs). Reactor vessel steam dome pressure briefly peaked at approximately 1111 psig and the Bypass Valves (BPVs) successfully controlled pressure. No Safety Relief Valves (SRVs) lifted. The pressure experienced in the main steam lines was transitory and apparently less than reactor vessel steam dome pressure. However, using steam dome pressure, the SRVs were possibly not in compliance with their 1% Technical Specifications tolerance requirement. The valves were removed and tested in accordance with code requirements. The actual drift experienced was within the bounds of a previous analysis demonstrating adequate overpressure protection. <br /><br /> The cause of this scram was vibration-induced component failure of Hydraulic Fluid Pressure Switch 1N32-N300. The cause of the SRV setpoint drift was corrosion-induced bonding of the surface between the pilot valve disc and seat. <br /><br /> Corrective actions for this event included replacing the pressure switch and moving it away from the source of vibration. The SRVs were tested and refurbished. Georgia Power Company (GPC) will continue to participate in the BWR Owners' Group action plan to resolve setpoint drift.
3211991005 | Hatch 1 | 02/17/1991 | 03/18/1991 | 9103210276 | <strong>Reactor Water Level Instrument Perturbation Results In Reactor Scram While In Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 2/17/91, at approximately 1840 CST, Unit 1 was in Cold Shutdown with reactor coolant temperature at approximately 118 degrees F and an indicated reactor water level of approximately 50 inches above instrument zero (approximately 214 inches above top of active fuel). At that time, instrumentation and control (I&C) technicians were attempting to rectify a mismatch between redundant reactor water level indications. While they were returning reactor water level instrument 1C32-N004B to service, a pressure spike was experienced on the instrument sensing line. The same sensing line also feeds two other reactor water level instruments, 1B21-N680C/D. The latter two instruments sensed the spike and actuated the Reactor Protection System (RPS, EIIS Code JE), resulting in a scram signal due to sensed low reactor water level. The low reactor water level signal also resulted in an automatic isolation of the Shutdown Cooling (SDC) system (RHR, EIIS Code BO). The false low reactor water level signal cleared immediately. The scram signal was reset within approximately 3 minutes, and shutdown cooling was restored by approximately 1900 CST. Reactor water temperature reached a maximum of approximately 138 degrees F per control room indications. <br /><br /> The root cause of the event could not be conclusively determined, but it is believed that an air bubble trapped in the instrument sensing line either moved or collapsed causing the instrument spike.<br /><br /> Corrective actions for the event included completing the maintenance activity on reactor water level instrumentation and returning SDC to service.
3211991006 | Hatch 1 | 02/25/1991 | 03/25/1991 | 9103290039 | <strong>Personnel Error Results In An Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2/25/91 at approximately 1420 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, a monthly scheduled surveillance was being performed on Reactor Core Isolation Cooling (RCIC, EIIS Code BN) Steam Line Low Pressure trip unit 1E51-N658A. While performing this procedure, an isolation of Group 4 Primary Containment Isolation System (PCIS, EIIS Code JM) valve 1E51-F008 occurred. An investigation later determined that a link in the valve closure logic was apparently not fully opened. This link was required to be opened by the procedure and would have prevented the ESF actuation during the surveillance. After the actuation occurred, licensed Operations personnel verified that a valid automatic isolation signal was not present. By approximately 1540 CST on 2/25/91, the Group 4 isolation signal had been reset, valve 1E51-F008 had been reopened, and the RCIC system had been returned to an operable status.<br /><br /> The cause of the event is personnel error. Instrument and Control (I&C) personnel performing the surveillance apparently failed to fully open the correct link. <br /><br /> Corrective actions include counseling of involved personnel, performing the surveillance procedure, and verifying that the surveillance results were satisfactory.
3211991007 | Hatch 1 | 02/27/1991 | 03/27/1991 | 9104010330 | <strong>Personnel Error Results In Main Turbine Trip And Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 2/27/91 at approximately 1247 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, both Recirculation Pumps tripped while plant Instrument and Controls (I&C) technicians were performing the quarterly surveillance on the turbine first stage pressure permissive input to the Reactor Protection System and the End-of-Cycle (EOC) Recirculation Pump trip logic. Loss of recirculation system flow caused a rapid increase in reactor water level and the Main Turbine and both Reactor Feedwater Pump Turbines tripped on high reactor water level. The Main Turbine trip resulted in a full scram per design. Reactor water level decreased such that the Group 2 Primary Containment Isolation System valves isolated. Reactor water level was recovered using the High Pressure Coolant Injection system and "A" Reactor Feedwater Pump. Reactor pressure was controlled with the Main Turbine Bypass Valves. <br /><br /> The cause of this event was personnel error. I&C technicians had inadvertently left in place a jumper following performance of a different surveillance on 2/22/91. This jumper, in conjunction with the surveillance on the turbine first stage pressure permissive instruments, was sufficient to actuate enough of the EOC Recirculation Pump trip logic to cause a trip of both pumps. <br /><br /> Corrective actions for this event include counseling the involved personnel, performing an inspection of both units' Main Control Room panels, and revising procedures.
3211991008 | Hatch 1, Hatch 2 | 03/21/1991 | 04/19/1991 | 9104240219 | <strong>Inadequate Procedure Results In Missed Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 3/21/91 at approximately 1300 CST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power) and Unit 2 was in the Cold Shutdown mode. At that time, plant personnel performing a review of Chemistry department Technical Specifications surveillances determined that some daily channel checks had not been performed at the frequency required by the Unit 1 and Unit 2 Technical Specifications. Specifically, the daily channel checks of the Unit 1 Recombiner Building Ventilation noble gas activity monitor and sample flowrate measuring device and the Main Stack sample flowrate measuring device were performed on 1/26/91 at a time of day which exceeded the required frequency of performance. This was contrary to the requirements of Unit 1 Technical Specifications Table 4.14.2-1 and Unit 2 Technical Specifications Table 4.3.6.10-1. <br /><br /> The cause of this event is a less than adequate procedure. Procedure 62EV-SAM-003-0S, "Gaseous Waste Discharge Monitor Checks," did not contain adequate guidance to ensure the daily checks were performed during the same time period each day such that the required frequency plus grace period was not exceeded. <br /><br /> Corrective actions for this event include issuing daily channel check guidance to Chemistry personnel and revising procedures 62EV-SAM-003-0S and 64CH-ADM-001-0S, "Chemistry Program."
3211991009 | Hatch 1, Hatch 2 | 07/12/1991 | 04/29/1992 | 9205040219 | <strong>Single Failure Vulnerabilities Discovered In The Main Control Room Environmental Control System</strong><br /><i>Abstract:&nbsp;</i>On 7/12/91, at approximately 1205 CDT, Units 1 and 2 were in the Run mode at 2436 CMWT (100 percent of rated thermal power). At that time, nonlicensed personnel determined that the Main Control Room Environmental Control (MCREC) system did not comply with the single failure design criterion as required by the plant's Final Safety Analysis Report. Specifically, the air conditioning subsystem of the MCREC system could not sustain a single failure to the system's class 1E power supply and still maintain the Main Control Room temperature within the Technical Specifications limit. Consequently, only one of two independent, redundant MCREC systems could be assumed to be operable contrary to the plant's Technical Specifications which require that both systems be operable. A limiting condition for operation (LCO) was entered per the Technical Specifications. The design review performed per the commitment made in revision 0 of this report and subsequent testing revealed additional single failure concerns. <br /><br /> The causes of the single failure vulnerabilities were less than adequate design and failure to fully understand the design of the system. <br /><br /> Corrective actions include implementing design changes to the system and revising the system operating procedure.
3211991010 | Hatch 1 | 05/16/1991 | 06/14/1991 | 9106180299 | <strong>Improper Installation On Relay Results In Engineered Safety Features Actuation</strong><br /><i>Abstract:&nbsp;</i>On 5/16/91, at 2155 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% of rated thermal power). At that time, an isolation signal was received by Reactor Core Isolation Cooling (RCIC, EIIS Code BN) system valve 1E51-F105. The valve subsequently closed per design. The valve is designed to close on high drywell pressure in conjunction with low RCIC steam line pressure. This condition did not exist at the time of the event. Investigation revealed the plastic cover on relay 1E51-K48 was wedged on such that the relay fingers were pressed against the contacts as though the relay were in an energized state. (The relay energizes to generate an isolation signal to valve 1E51-F105.) Further investigation disclosed that at the time the isolation was received, a plant operator had been performing a surveillance in Control Room panel 1H11-P623 where relay 1E51-K48 is located. It was concluded that he had inadvertently bumped the relay, wedging its plastic cover against the contact fingers. At 2230 CDT, the cover was loosened. The isolation signal was cleared, and the valve was reopened. No other actuations occurred as a result of this event. <br /><br /> The cause of this event was personnel error in that the wiring on relay 1E51-K48 was improperly routed. This led to improper installation of the cover of relay 1E51-K48, making the relay susceptible to an inadvertent actuation resulting from being bumped. <br /><br /> Corrective actions for this event include repairing this and similarly affected relays, and training personnel.
3211991011 | Hatch 1, Hatch 2 | 06/12/1991 | 07/09/1991 | 9107160246 | <strong>Inadequate Procedure Results In Missed Technical Specifications Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 06/12/91, at 1500 CDT, Unit 1 and Unit 2 were in the Run mode at a power level of 2436 CMWT (100% rated thermal power in both units). At that time, plant chemistry personnel reviewing the surveillance history of diesel fuel oil sampling and analysis discovered that laboratory results of analyses were not being reported to the plant in a timely manner. These analyses are required once every 92 days per both units' Technical Specifications and the Fire Hazards Analysis. Additionally, it was found that one set of samples had been lost while in shipment to a test laboratory, and therefore was not analyzed at all. This is a condition prohibited by the Technical Specifications, but is also reportable per Technical Specifications section 6.9.2. When the condition was discovered, the results of past analyses were reviewed and it was determined that operability of diesel engines had not been impacted by the event. <br /><br /> The cause of the event is an inadequate procedure. Specifically, surveillance procedure 64CH-SAM-002-OS, "DIESEL FUEL OIL: SAMPLING," did not contain steps to assure the results of laboratory analyses were reported to the plant within the required time frame. <br /><br /> Corrective actions for this event will include revising the affected procedure to require verification of receipt of samples and timely reporting and evaluation of analyses. This action will be complete by 8/15/91.
3211991012 | Hatch 1 | 06/19/1991 | 07/17/1991 | 9107230362 | <strong>Procedural Deficiency Results In Violation Of Technical Specifications Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On 6/19/91, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, based on a question raised by a task force review of the Chemistry Technical Specifications, it was determined that an instrument calibration of the Post Loss of Coolant Accident (LOCA) Radiation Monitoring system's radiation detectors 1D11-N022A-D was not being performed at the required frequency. Procedure 62CI-CAL-012-0S, "Post LOCA Radiation Monitor," requires these detectors to be calibrated once per 18 months instead of once per 6 months as required by Unit 1 Technical Specifications Table 4.2-11, Item 12. Previously, licensed Operations personnel had declared the Post LOCA Radiation Monitoring system inoperable and initiated a Limiting Condition for Operation on 6/7/91 at 1500 CDT. This was done as a conservative measure when the preliminary conclusion was reached that the Technical Specifications required the detectors to be included in the 6 month calibration of the Post LOCA Radiation Monitoring system. This requirement was confirmed in conversations held with NRC personnel on 6/19/91. Detectors 1D11-N022A-D were calibrated and the Post LOCA Radiation Monitoring system was returned to an operable status at 1410 CDT on 7/2/91. <br /><br /> The cause of this event was a less than adequate procedure. Procedure 62CI-CAL-012-0S required the detectors to be calibrated once per 18 months instead of once per 6 months. <br /><br /> Corrective actions include calibrating detectors 1D11-N022A-D and revising procedure 62CI-CAL-012-0S.
3211991013 | Hatch 1 | 08/09/1991 | 10/09/1991 | 9110180042 | <strong>Turbine Trip Generator Ground Fault Signal Causes Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 8/9/91 at 1523 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, Generator Field Ground Detecting Relay 1N51-K751 actuated causing a Main Turbine trip and reactor scram on Turbine Stop Valve (TSV) closure per design. Reactor vessel water level decreased as expected due to void collapse resulting in a Group 2 Primary Containment Isolation System signal on low water level. All Group 2 Primary Containment Isolation Valves closed per design except Drywell Equipment Drain Sump Outboard Isolation Valve 1G11-F020. This valve took 114 seconds to close; however, it is required to close within 15 seconds of the receipt of an isolation signal. Valve 1G11-F019, the inboard isolation valve for the Primary Containment penetration, closed in 11 seconds, effectively isolating the penetration in the required time frame. Reactor vessel pressure increased to about 1120 psig following closure of the TSVs. All the Safety Relief Valves (SRVs) except 1B21-F013J opened to decrease pressure. A review of post-scram data indicated SRV 1B21-F013J behaved properly during the event. The Main Turbine Bypass Valves operated to control pressure after the SRVs closed. <br /><br /> The cause of this event is believed to have been a short duration ground. Post-scram testing of the generator revealed no existing ground fault. Calibration of relay 1N51-K751 indicated its trip setpoint had drifted, but spurious actuation of the relay could not be proven. The reason valve 1G11-F020 was slow to close is still under investigation. <br /><br /> Corrective actions include testing the generator, replacing relay 1N51-K751, and timing and scheduling an inspection of valve 1G11-F020.
3211991014 | Hatch 1, Hatch 2 | 08/10/1991 | 12/17/1991 | 9112300058 | <strong>Component Failure Results In Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On 8/10/91, at 1011 CDT, Unit 1 was in the Hot Shutdown mode with the reactor vessel at 500 psig and reactor coolant temperature at 470 degrees Fahrenheit. Unit 2 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, the output breakers for the normal power supply to the Unit 1 Reactor Protection System (RPS, EIIS Code JC) bus 'B' tripped when an overvoltage relay failed. This caused a loss of power to the 'B' channel of the RPS, the Process Radiation Monitors (EIIS Code IL), the Neutron Monitoring System (NMS, EIIS Code IG), the Primary Containment Isolation System (PCIS, EIIS Code JM), and the Offgas Radiation Monitoring System (EIIS Code IL). The "fail-safe" design of these systems resulted in their assuming the tripped state when power was interrupted. These trips resulted in a half scram signal on Unit 1 RPS channel 'B', closure of various Unit 1 PCIS valves and initiation of the 'B' trains of both units' Standby Gas Treatment Systems (SGTS, EIIS Code BH). Two Unit 1 SGTS dampers were subsequently found to have incorrectly returned to their standby configuration following the restoration of power and the reset of the isolation logic. <br /><br /> The cause of the loss of power to the RPS bus was component failure. The cause of the dampers repositioning after reset of the isolation logic was a discrepancy in the installation of the damper wiring and less than adequate verification testing in response to IEB 80-06. <br /><br /> Corrective actions for this event include replacing the failed component, issuing an operating order, performing a design and field review of SGTS actuation logic, and restoring the damper wiring in accordance with design drawings.
3211991015 | Hatch 1, Hatch 2 | 08/23/1991 | 09/18/1991 | 9109240282 | <strong>Component Failure Results In ESF Actuations And Design Deficiency Results In Tech. Specs. Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On 8/23/91, at 0828 CDT, Units 1 and 2 were in the Run mode; both at a power level of 2436 CMWT (100 percent rated thermal power). At that time, Unit 1 experienced a loss of power to the 'B' Reactor Protection System (RPS) bus when the 'B' RPS Motor-Generator (MG) Set tripped. The MG Set tripped when a plant equipment operator attempted to replace a burned-out light bulb in the local MG Set control panel. As the operator attempted to unscrew the bulb, the glass portion of the bulb separated from the metal base and the two filament leads touched. The shorted leads caused the motor starter relay to drop out, tripping the MG Set and deenergizing the RPS bus. This caused a half scram signal on Unit 1 RPS channel 'B', closure of various Unit 1 PCIS valves and initiation of the 'B' trains of both units' Standby Gas Treatment System (SGTS). RPS bus 'B' was subsequently placed on its alternate power supply. At 0855 CDT, an expected power interruption while transferring the RPS bus back to its normal supply resulted in a Main Steam Line Radiation Monitor (MSLRM) being rendered inoperable. This condition was discovered at 2255 CDT, on 8/23/91. Operators subsequently took actions to initiate a trip signal in the RPS and PCIS logic associated with the monitor. <br /><br /> The cause of the loss of power to the RPS bus was component failure. The cause of the failure of the MSLRM was design inadequacy. <br /><br /> Corrective actions for this event include replacing the failed light bulb, sending bulbs to the vendor for a failure analysis, resetting the MSLRM, functionally testing the MSLRM and returning it to service, revising a procedure, conducting training, and reviewing the event for 10 CFR 21 reportability.
3211991016 | Hatch 1 | 09/05/1991 | 09/30/1991 | 9110080400 | <strong>Blown Fuse Results In Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 9/5/91, at 0655 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, licensed plant operators observed annunciation in the control room that a Reactor Water Cleanup (RWCU, EIIS Code CE) system failure had been detected at remote panel 1H21-P002. They also observed closure of the RWCU outboard Primary Containment Isolation Valve (PCIV, EIIS Code JM) 1G31-F004, and a trip of the RWCU pump, 1G31-C001A. Investigation into the event by Instrument and Control technicians revealed that fuse 1A71B-F18 located in control room panel 1H11-P623 had blown, disconnecting power from relay 1A71B-K27, resulting in closure of the PCIV. It was concluded that isolating the RWCU system had caused the RWCU system failure annunciation due to sensed low flow. No problems such as short circuits or failed relays were identified in the circuit which is fed by the fuse. The fuse was replaced and the RWCU system was returned to service by 0840 CDT without further incident. <br /><br /> The cause of this event is failure of fuse 1A71B-F18. Since no cause could be found for the failure of the fuse, the event is considered to be the result of a random failure of the fuse. <br /><br /> Corrective actions for the event included replacing the failed fuse and returning the RWCU system to service.
3211991017 | Hatch 1, Hatch 2 | 09/11/1991 | 10/09/1991 | 9110180039 | <strong>Personnel Error Results In A Main Turbine Trip And A Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 9/11/91, at approximately 0925 CDT, unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent of rated thermal power). At that time, the Reactor Feedwater Pumps and the Main Turbine tripped on a false high reactor water level signal. Subsequently, the reactor scrammed and the Recirculation pumps tripped on Turbine Stop Valve (TSV) closure. Reactor pressure immediately increased to 1102 psig resulting in ten of the eleven Main Steam System Safety Relief Valves opening as designed. Reactor water level decreased to the Low Level 3 and 2 setpoints initiating actuation signals to the Primary Containment Isolation System (PCIS), the Units 1 and 2 Standby Gas Treatment Systems (SGTS), the Reactor Protection System (RPS), the High Pressure Coolant Injection (HPCI) system, and the Reactor Core Isolation Cooling (RCIC) system. Level was restored using the HPCI and RCIC systems. Immediately following the scram, RPS bus 'A' de-energized due to an undervoltage condition being sensed on the bus. This is a possible occurrence when RPS is on alternate supply and the 4160 V buses transfer as designed following a Main Turbine trip. The loss of the RPS bus resulted in initiation signals being transmitted to PCIS, SGTS, and the Main Control Room Environmental Control System pressurization mode logic. The bus was re-energized six minutes following the scram.<br /><br /> The cause of the event was cognitive personnel error on the part of a nonlicensed, contract Health Physics technician. The technician inappropriately leaned a hand-held radiation detector against a scram-sensitive panel. The instrument fell, contacting instrumentation valving and ultimately causing the false high level signal. The technician was counseled. A plant-wide directive will be issued addressing the event.
3211991018 | Hatch 1, Hatch 2 | 09/17/1991 | 10/14/1991 | 9110230161 | <strong>Apparent Personnel Error Results In Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 09/17/91, at 0457 CDT, Unit 1 and Unit 2 were both in the Run mode at power levels of 2387 CMWT on Unit 1 (97 percent rated thermal power) and 2436 CMWT on Unit 2 (100 percent rated thermal power). At that time, an Instrument and Control technician performing surveillance procedure 57SV-D11-008-1S, "Reactor Building Exhaust Vent Instrument Functional Test," apparently removed two refueling floor ventilation system exhaust monitors (EIIS Code IL) from service instead of the two reactor building ventilation system exhaust monitors as required. This caused the 'B' train of both units' Standby Gas Treatment Systems (SGTS, EIIS Code BH) to start and the normal ventilation systems to trip/isolate as designed. The technician immediately realized his mistake and reset one of the monitors, clearing the trip signal. Plant operators secured the SGTS and returned the normal ventilation system to operation by 0502 CDT. The surveillance on the reactor building ventilation system radiation monitors was completed without further incident. <br /><br /> The cause of the event could not be conclusively determined. Although the technician could only recall having manipulated one piece of equipment incorrectly, it is believed that he actually removed two instruments from service during the course of the surveillance, causing the event. <br /><br /> Corrective actions for this event included counseling the technician and conducting a functional test of the involved instrumentation to ensure its operability.
3211991019 | Hatch 1 | 09/20/1991 | 10/18/1991 | 9110290005 | <strong>Group 5 Primary Containment System Isolation Occurred During Reactor Water Cleanup System Evolution</strong><br /><i>Abstract:&nbsp;</i>On 09/20/91, at 1312 CDT, Unit 1 was in Cold Shutdown with reactor pressure at atmospheric. Reactor water level was in the normal band at approximately 200 inches above the top of active fuel, and reactor water temperature was approximately 130 degrees Fahrenheit. At that time, licensed plant operators secured the operating pump in the Reactor Water Cleanup (RWCU, EIIS Code CE) system in preparation for starting the standby pump. Upon securing the operating pump, an RWCU Leak Detection System (LDS, EIIS Code IJ) alarm actuated, indicating a high differential flow in the RWCU system. When the 45-second time delay expired, both Group 5 Primary Containment Isolation System (PCIS, EIIS Code JM) valves automatically closed, isolating RWCU per design. No leakage from the RWCU system was observed. Plant operators performed a fill and vent on the RWCU system, and the LDS alarm cleared. Instrument and Control technicians subsequently demonstrated the operability of involved flow instrumentation. The Group 5 PCIS valves were reopened by 1726 CDT and the RWCU system was returned to service by 2040 CDT. <br /><br /> The root cause of this event was most probably due to two leaking valves in the RWCU system that permitted the system to drain slightly after the RWCU pump was secured. This drainage affected flow transmitter 1G31-N012, which tripped the LDS, resulting in the isolation. <br /><br /> Corrective actions for this event include verifying proper operation of the affected flow transmitter, returning RWCU to service, and repairing the two leaking valves in the RWCU system. The first two actions are complete. The last actions are scheduled for completion prior to unit startup on 11/24/91.
3211991020 | Hatch 1, Hatch 2 | 10/04/1991 | 11/01/1991 | 9111070078 | <strong>Area Radiation Monitors Trip Resulting In Engineered Safety Feature Automatic Actuation</strong><br /><i>Abstract:&nbsp;</i>On 10/4/91 at 2342 CDT, Unit 1 was in a refueling outage with the mode switch in Refuel and no fuel in the reactor vessel. Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time various area high radiation annunciators alarmed in the Main Control Room and the unit-common Main Control Room Environmental Control System (MCRECS) automatically transferred to the pressurization mode. All 38 Area Radiation Monitor (ARM) trip units, located on Main Control Room panel 1D21-P600, had tripped; however, the trip unit indicators were reading within their normal ranges. Two of the ARMs located on the Refueling Floor provide initiation signals for automatic actuation of the MCRECS pressurization mode when their design setpoints are exceeded. Since the ARM trip unit indicators showed that radiation levels were normal, the trip units were reset. MCRECS was then returned to its normal mode of operation at approximately 2355 CDT. <br /><br /> The most probable cause of this event was concluded to be a voltage perturbation in the common power supply of the ARMs. However, a review of outage activities in progress at the time of the event did not reveal any activities that would have resulted in such a perturbation. <br /><br /> Corrective actions for the event included resetting the ARM trip units and returning MCRECS to its normal mode of operation.
3211991021 | Hatch 1, Hatch 2 | 10/07/1991 | 10/25/1991 | 9110300177 | <strong>Personnel Error Causes Unplanned Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On 10/7/91 at 0438 CDT, Unit 1 was in a refueling outage with the core completely unloaded and Unit 2 was in the Run mode at a power level of 2436 CMWT (100%) rated thermal power). At that time, a fuse blew in the Unit 1 Reactor Protection System (RPS) bus "B" Equipment Protection Panel 1C71-P003D. This resulted in the RPS bus "B" protection circuit sensing abnormal condition and opening one od the RPS bus "B" power supply breakers per design. This in turn, caused a loss of power to the "B" channel of the RPS, the Process Radiation Monitors, the Neutron Monitoring System. The "fail-safe" design of these systems resulted in their assuming the tripped state when power was interrupted. These trips resulted in a scram signal on Unit 1 RPS channel "B", an isolation signal to various Unit 1 PCIS valves, initiation of the "B" trains of both unit' Standby Gas Treatment Systems, and swapping of the Main Control Room Environmental Control Systems to the pressurization mode. By 0445 CDT. the blown fuse had been replaced, the RPS bus "B" breaker reset, and the actuated system returned to normal. <br /><br /> The cause of this event is personnel error. Plant Electricians replacing fuses per Maintenance Work Order 1-91-4868 inadvertently grounded a jumper while working in panel 1C71-P003D. This caused a short circuit current which blew a five ampere fuse in the RPS bus "B" protection circuit.<br /><br /> Corrective actions for this event include counseling involved personnel and discussing the event at tool-box meetings.
3211991022 | Hatch 1 | 10/09/1991 | 11/06/1991 | 9111140087 | <strong>Safety Relief Valve Setpoints Remain Within In-Service Testing Tolerance Requirements</strong><br /><i>Abstract:&nbsp;</i>On 10/9/91, at 1430 CDT, Unit 1 was in its thirteenth refueling outage with the mode switch in Refuel and fuel removed from the reactor vessel. All eleven Main Steam System (EIIS Code SB) Safety Relief Valves (SRVs) had been sent offsite for testing of their mechanical lift setpoints as required by American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code, Section XI, IWV-3512. At that time, engineering personnel were notified by the offsite testing agency that tests showed the mechanical lift setpoints for all eleven SRVs were within the Section XI tolerance requirement of +/- 3 percent. <br /><br /> This report is being submitted voluntarily due to the potential industry interest in view of the ongoing Boiling Water Reactor Owners Group (BWROG) activities to address SRV mechanical lift setpoint drift. The cause of the setpoint drift is corrosion-induced bonding of the SRV pilot valve disc and seat. In this event, the SRV's all lifted within their setpoint tolerance of +/- 3 percent; however, this report is being submitted to apprise the industry of the results.
3211991023 | Hatch 1, Hatch 2 | 10/14/1991 | 11/12/1991 | 9111180279 | <strong>Blown Fuse Results In Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 10/14/91, at 1135 CDT, Unit 1 was in the Refuel mode with the reactor vessel disassembled. No fuel was in the vessel, and the reactor cavity was flooded. Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, control room operators observed that the "B" train of each unit's Standby Gas Treatment System (SGTS, EIIS Code BH) had started. Licensed operations personnel then verified proper operation of the SGTS and that an actual condition requiring SGTS operation did not exist. Since conditions that would have indicated the start was valid did not occur, operators attempted to reset the system and restore normal ventilation. However, the SGTSs could not be tripped. Electricians troubleshooting the systems discovered fuse 1C61-F20 had blown. The blown fuse was replaced, and the SGTSs were returned to service by 1432 CDT. <br /><br /> The cause of this event was a blown fuse. The fuse application was reviewed and determined to be correct. The blown fuse occurrence is believed to be random. <br /><br /> Corrective actions for this event include: 1) replacing the blown fuse, 2) securing SGTS, 3) returning normal ventilation systems to service, reviewing the fuse application, and 4) testing the efficiency of the filter train carbon adsorbers.
3211991024 | Hatch 1 | 10/16/1991 | 11/12/1991 | 9111180270 | <strong>Technical Specifications Surveillance Not Performed At Required Periodicity</strong><br /><i>Abstract:&nbsp;</i>On 10/16/91 at 1130 CDT, Unit 1 was in a refueling outage with the core completely unloaded. At that time, it was determined that the requirements of Unit 1 Technical Specifications section 4.7.A.5 had not been met. Specifically, procedure 34SV-SUV-019-1S, "Surveillance Checks," required the Unit 1 Torus oxygen concentration to be verified to be less than 4% once per week instead of once per day as required by the Technical Specifications. The procedure did require the Unit 1 Drywell oxygen concentration to be verified to be less than 4% once per day as required. With the unit in a refueling outage and the core unloaded, Unit 1 Technical Specifications section 4.7.A.5 was not applicable because the oxygen check requirement applies only when the unit is in power operation. Therefore, no Limiting Conditions for Operation existed at the time of discovery of this missed surveillance.<br /><br /> The cause of this event was a misinterpretation of the requirements of section 4.7.A.5. This specification requires that "the primary containment oxygen concentration" be measured daily. It appears that primary containment has been interpreted to mean the Drywell. In fact, the Torus is also part of the primary containment and, because the Torus atmosphere is not in constant communication with the Drywell atmosphere, its oxygen concentration must be checked as well. <br /><br /> Corrective action for this event included revising procedure 34SV-SUV-019-1S to require a daily check of Torus oxygen concentration.
3211991025 | Hatch 1, Hatch 2 | 10/24/1991 | 11/22/1991 | 9112040059 | <strong>Less Than Adequate Procedure Results In Technical Specifications Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On 10/24/91, at 1300 CDT, Unit 1 was in a scheduled maintenance and refueling outage with the vessel disassembled and with no fuel in the vessel. Unit 2 was in the Run mode at approximately 2436 CMWT (approximately 100 percent of rated thermal power). At that time, nonlicensed personnel determined that the automatic function of Main Control Room Environmental Control System (MCRECS) exhaust damper 1Z41-F018B was not being tested as required by the plant's Technical Specifications. Unit 1 Technical Specifications Table 4.2-8 and Unit 2 Technical Specifications Section 4.7.2.e.3 require a logic system functional test of the pressurization mode function of MCRECS to be performed at least once per 18 months. Damper 1Z41-F018B automatically closes as part of the automatic transfer of MCRECS to the pressurization mode. However, its automatic function was not being checked during the associated logic system functional testing. Licensed personnel were notified of the deficiency. At 1500 CDT, a clearance was issued to isolate the motive force (the actuator's air supply ) from the damper actuator to ensure that the damper was maintained in the closed position until it could be properly tested. <br /><br /> The cause of the event was a less than adequate procedure. Procedure 42SV-Z41-001-0S, "Main Control Room Pressurization LSFT" did not include verification of the damper closing following an automatic transfer of MCRECS to the pressurization mode. <br /><br /> Corrective actions include securing the damper in the closed position, reviewing the procedure for similar problems, and revising and performing procedure 42SV-Z41-001-0S.
3211991026 | Hatch 1 | 11/06/1991 | 12/04/1991 | 9112100265 | <strong>Pressure Perturbation Causes False Low Reactor Water Level Signal And ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On 11/6/91 at 0441 CST, Unit 1 was in the Refuel mode with the core completely loaded and Reactor Pressure Vessel reassembly in progress. At that time, a full reactor scram signal occurred from a false low water level signal caused by a pressure perturbation on a common sensing line. This occurred when a new instrument isolation valve was opened during routine valve lineups. All controls rods were fully inserted; thus, no rod motion resulted. Several Group 2 Primary Containment Isolation System valves also received an isolation signal on low water level and valves 1E11-F008, Shutdown Cooling Suction Outboard Isolation Valve, and 1E11-F015B, Residual Heat Removal Inboard Injection Valve, closed per design. This resulted in interruption of the normal shutdown cooling flow path. The trip signal cleared 12 seconds after its receipt. Licensed operations personnel then reset the scram and isolation signals and, at 0517 CST, restored shutdown cooling flow. During the 36 minutes shutdown cooling was out of service, reactor water temperature increased from 105 to only 109 degrees F.<br /><br /> The cause of this event was a lack of adequate controls governing the position of the new instrument isolation valve during instrument venting activities. The valve was not opened prior to instrument venting activities as it should have been. As a result, part of a water level sensing line was inadvertently drained. When the isolation valve was later opened, the drained line rapidly filled causing a pressure perturbation on the common sensing line.<br /><br /> Corrective actions for this event include resetting the scram and isolation signals, restoring shutdown cooling to service, and issuing a Departmental Directive.
3211991027 | Hatch 1 | 11/08/1991 | 12/04/1991 | 9112100178 | <strong>Improper Sensing Line Installation Results In ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 11/08/91, Unit 1 was in the Refuel mode with vessel reassembly in progress. A flow controller for a Reactor Water Cleanup (RWCU) system flow control valve, 1G31-F033, had been repaired. At 0020 CST, the valve was being opened for testing purposes when the RWCU Leak Detection System (LDS) annunciator alarm was received followed by the automatic closure of Group 5 Primary Containment Isolation System (PCIS) valves 1G31-F001 and 1G31-F004. The operating RWCU pump tripped as designed. A second event occurred on 11/15/91 with Unit 1 in the Refuel mode and the vessel fully assembled. A restricting orifice was to be installed in the RWCU system piping near valve 1G31-F033. The valve was required to be opened in order to establish the clearance boundary. When the valve was opened at 1341 CST, an isolation of the Group 5 PCIS valves occurred along with a trip of the operating RWCU pump. No immediate operator actions were required in either event. <br /><br /> The cause of this event was concluded to be an improper installation of the instrument sensing lines for differential pressure transmitter 1G31-N012. This routing results in the instrument tubing partially draining whenever the RWCU system piping at the instrument line taps is drained. The partially drained tubing produced a differential pressure across the transmitter resulting in a false RWCU high differential flow signal. <br /><br /> Corrective actions for this event include performing an engineering review to assess the feasibility of rerouting the instrument sensing lines.
3211991028 | Hatch 1, Hatch 2 | 11/16/1991 | 12/16/1991 | 9112260323 | <strong>Personnel Error Results In An Unplanned Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 11/16/91, at 1630 CST, Unit 1 was in the Refuel mode with the vessel assembled and Unit 2 was in the Run mode at 2436 CMWT (100 percent of rated thermal power). At that time, the Main Control Room Environmental Control System (MCRECS), shared by the Unit 1 and 2 Main Control Rooms (MCR), automatically transferred to the pressurization mode. No plant conditions existed that would necessitate the actuation. Coincident with the MCRECS transfer to the pressurization mode, the MCR lights flickered, indicating a possible power supply problem. The licensed Unit 1 Shift Supervisor, aware that electrical equipment line-ups were in progress per procedure 42SV-R43-027-1S, "Diesel Generator 1C LOCA/LOSP Testing," contacted the nonlicensed plant equipment operator (PEO) performing the activity. The PEO informed him that he had inadvertently tripped the wrong breaker in performing the procedure, realized his mistake, immediately closed the breaker back using the local control switch, and was attempting to contact him. Investigations showed that the momentary loss of power resulting from the breaker being cycled caused the automatic transfer of MCRECS. Subsequently, MCRECS was transferred back to its normal mode of operation and, at 1735 CST, the NRC was notified of the event pursuant to 10 CFR 50.72. <br /><br /> The cause of the event was cognitive personnel error on the part of a nonlicensed individual. While reaching for a particular breaker control switch, the PEO inadvertently grasped the switch adjacent to it. When he placed the control switch to the trip position, the associated breaker tripped resulting in the generation of an automatic Engineered Safety Features (ESF) actuation signal. The PEO was counseled regarding the event.
3211991029 | Hatch 1 | 11/26/1991 | 03/30/1992 | 9204030134 | <strong>Malfunctioning Motor Operated Valve Results In Group 1 Isolation During Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 11/26/91, Unit 1 was in the Startup mode at approximately 4% rated thermal power and was starting up from a refueling outage when system leaks in the drywell led to a decision to shut down the unit and perform repairs. At 1539 CST, the reactor was shut down by manual scram per procedure. Since the core had been critical for only 109 hours, the decay heat level was relatively low, and the reactor began to cool down rapidly. Therefore, licensed personnel closed the inboard Main Steamline Isolation Valves, intending to retard cooldown rate by throttling a non-safety related motor operated valve in the main steamline drain, 1B21-F020. However, this valve did not respond to the control switch, so the main steamline drain had to be isolated. This isolated all steam loads from the reactor and required the Main Condenser vacuum breakers to be opened since steam seal pressure was not available. At 1620 CST, when condenser vacuum decreased to the set point of the Group 1 Primary Containment Isolation System trip on low condenser vacuum, an automatic isolation signal was received. Group 1 valves which went closed were the 3/4-inch Reactor Water Sample valves and redundant valves in penetrations which had already been isolated including the outboard Main Steamline Isolation Valves. All affected valves functioned as designed. Although the automatic actuation could have been prevented by bypassing the low condenser vacuum trip, licensed operators properly focused their attention on the higher priority of controlling cooldown rate. <br /><br /> The root cause of this event was the inability of valve 1B21-F020 to throttle on demand. <br /><br /> The torque switch on valve 1B21-F020 was adjusted. .
3211991030 | Hatch 1, Hatch 2 | 12/02/1991 | 12/23/1991 | 9201020114 | <strong>Instrument Drift Causes Area Radiation Monitor Trips Resulting In ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On 12/02/91 at 1055 CST and 1133 CST, and on 12/07/91 at 0545 CST, Units 1 and 2 were in the Run mode at an approximate power level of 2436 CMWT (100 percent rated thermal power). At those times, the unit-common Main Control Room Environmental Control (MCREC, EIIS Code VI) system automatically transferred from the normal mode to the pressurization mode. The events occurred as designed when refueling floor Area Radiation Monitors (ARMs, EIIS Code IL) tripped on false high radiation signals. After each actuation, licensed Operations personnel verified proper operation of the MCREC system and verified that an actual high radiation condition did not exist in the affected areas. The ARM trip units were reset and the MCREC system was returned to its normal mode of operation after each event.<br /><br /> The cause of these events was instrument setpoint drift. An investigation later determined that the events occurred when the high radiation trip setpoint for the affected ARMs drifted, causing the ARM to trip on a false high radiation signal. The cause for the setpoint drift was investigated and a trip unit was replaced. <br /><br /> Corrective actions for these events included returning the MCREC system to its normal mode of operation, adjusting the high radiation trip setpoints to their proper values, functionally testing four of the refueling floor ARM trip units, and replacing a trip unit.
3211991031 | Hatch 1 | 12/04/1991 | 12/23/1991 | 9201020108 | <strong>Inadequate Procedure Results In ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 12/04/91 at 0455 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (100% rated thermal power). At that time, Group 5 Primary Containment Isolation System valves 1G31-F001 and F004 closed on a Reactor Water Cleanup (RWCU) system high differential flow isolation signal. The isolation signal occurred as the "A" RWCU pump was being placed into service per procedure 42SP-101791-RZ-1-1N, "FT for RWCU Sealless Pump." The system had been isolated for several hours and as a result, system temperature and pressure had decreased causing voids to form in the system piping. When the "A" pump suction isolation valve was opened to place the pump into service, the system was unisolated and the partially voided piping rapidly filled. A high differential flow condition (system influent with no effluent) resulted. Isolation valves 1G31-F001 and F004 closed on an RWCU system high differential flow isolation signal per design. This terminated flow into the system and the isolation signal cleared.<br /><br /> The cause of this event was an inadequate procedure. Special purpose procedure 42SP-101791-RZ-1-1N did not contain adequate instructions and cautions to ensure an isolation did not occur when the "A", pump was placed into service. <br /><br /> The procedure will not be used again. It was intended only as a functional test for the "A" RWCU pump (the sealless pump) and the functional test of the pump has been completed satisfactorily.
3211991032 | Hatch 1 | 12/28/1991 | 01/27/1992 | 9201310300 | <strong>Personnel Error Results In Missed Technical Specifications Required Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 12/28/91 at 2230 CST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, it was determined from a routine review of completed surveillance procedure data packages that a daily check of the Unit 1 Torus oxygen concentration had not been performed the previous day as required by Unit 1 Technical Specifications section 4.7.A.5. The check had been performed on 12/26/91 at 2245 CST, but was not performed again until 12/28/91 at 1136 CST. The time between these two consecutive Torus oxygen concentration checks was about 37 hours, exceeding the time allowed by the Unit 1 Technical Specifications (24 hours plus a 25% grace period). When this event was discovered, the required surveillance was current; therefore, no Limiting Conditions for Operation had to be entered. <br /><br /> The cause of this event was personnel error. Licensed Operations personnel performing surveillance procedure 34SV-SUV-019-1S, "Surveillance Checks," on 12/27/91 incorrectly marked the Torus oxygen concentration check as "not required." This error was not caught until after the grace period for performing the surveillance had expired. A review of the complete data package from procedure 34SV-SUV-019-1S for 12/27/91 revealed no other missed surveillances. <br /><br /> Involved personnel were counseled. Additionally, this event will be included in beginning of shift training for Operations shifts.
3211991033 | Hatch 1 | 12/30/1991 | 01/27/1992 | 9201310234 | <strong>High Pressure Coolant Injection System Inoperable Due To Component Failure</strong><br /><i>Abstract:&nbsp;</i>On 12/30/91, at 1015 CST, and on 12/31/91, at 1800 CST, Unit 1 was in the Run mode at 2436 CMWT (100 percent of rated thermal power). At each of these times, the High Pressure Coolant Injection (HPCI) system experienced flow oscillations of approximately 2000 gallons per minute while being tested in accordance with procedure 34SV-E41-002-1S, "HPCI Pump Operability." The procedure was being performed in order to meet the surveillance requirement of Unit 1 Technical Specifications section 4.5.D.1.b.(1). In each case, the system was secured and declared inoperable. Appropriate Limiting Conditions for Operation (LCO) were initiated and the required Technical Specifications actions were implemented. Corrective maintenance was performed on the system following each incident and functional testing of the system was satisfactorily completed on 12/30/91, at 1900 CST, and on 1/1/92, at 0330 CST, respectively. In each case, the system was returned to standby and the LCO terminated. The cause of each event was intermittent failure of a transfer relay(s) internal to the HPCI system flow control unit, 1E41-K615. The relays function to transfer flow control between the manual and automatic modes. Failure of the relay(s) caused HPCI system flow to oscillate excessively in each of the events. Since the failure was intermittent, it was not identified during troubleshooting activities following the first failed surveillance test and did not show up during the subsequent functional test. Corrective actions for the event included replacing the transfer relays and functionally testing the system in accordance with procedure 34SV-E41-002-1S.
3221991001 | Shoreham | 03/24/1991 | 04/22/1991 | 9104260114 | <strong>Unplanned Actuation of Engineered Safety Feature Systems</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1991 at 1221, the reactor Building Normal Ventilation System (RBNVS) outboard exhaust valve (1T46*AOV-037B) closed for no apparent reason. With RBNVS operating in a recirculation mode, this isolation of the exhaust flow path caused the Reactor Building pressure to rise above -.30" (water gauge) which in turn caused the unplanned initiation of Engineered Safety Feature systems Reactor Building Standby Ventilation System "A" and Control Room Air Conditioning "A". These two systems were restored to their normal lineups at 1225. Plant management personnel were informed of this event and the NRC was notified at 1426 per 10CFR50.72(b)(2)(ii). A definite cause for the outboard exhaust valve closing could not be determined. The exhaust valve itself, its control circuit and the components that vent air off the valve to assist it in closing were all inspected or tested but nothing abnormal was found.
3231991001 | Diablo Canyon 2 | 07/15/1991 | 08/13/1991 | 9108220001 | <strong>Containment Ventilation Isolation Resulting From A Voltage Transient Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1991, at 1416 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 100 percent power, a spurious Containment Ventilation Isolation (CVI) actuation occurred. This constitutes an Engineered Safety Feature (ESF) actuation. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on July 15, 1991, at 1725 PDT. <br /><br /> An Instrumentation and Controls (I&C) technician inadvertently dropped a screw on the power switch for power supply NM51 while performing maintenance. This resulted in a voltage transient to the output relays of radiation monitors RM-11 and RM-12, which caused a solid state protection system (SSPS) Train B CVI actuation. <br /><br /> The root cause for the CVI was determined to be personnel error, inattention to detail, in that the I&C technician did not establish a temporary electrical barrier while working above the energized switch. <br /><br /> The corrective actions to prevent recurrence will include: (1) counseling of the technician involved regarding the necessity for establishing a temporary electrical barrier when working around energized equipment, when practical, and (2) issuance of a maintenance bulletin that describes this event and discusses current policies and procedures applicable to performing work on energized equipment.
3231991002 | Diablo Canyon 2 | 08/26/1991 | 12/20/1991 | 9201020006 | <strong>Potential Missetting Of Main Steam Line Code Safety Valve Due To Failure Of Test Equipment</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for informational purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On August 26, 1991, the setpoints for Main Steam Safety Valves (MSSVs) RV-60 and RV-225 on main steam line 2-4 were tested using Trevitest equipment. MSSV RV-60 was tested and required a normal adjustment to bring it into tolerance. Subsequently, MSSV RV-225 was tested and required an abnormally large adjustment to bring it into tolerance. Because this large adjustment was needed, a prompt post-calibration verification was performed on the Trevitest equipment. It was determined that the Trevitest equipment had failed during the adjustment of RV-225. RV-225 was then declared inoperable. RV-60 was not declared inoperable, since the Trevitest failure was judged to have occurred subsequent to adjusting RV-60 (because only normal, minor adjustments had been made to RV-60). On August 27, 1991, RV-60 was rechecked and lifted at 1105 psi (4 psi above its acceptance criteria of 1090 psi +/-1%). <br /><br /> The Trevitest equipment failure was due to a defective cell in the battery of the Trevitest test recorder. It could not be determined whether RV-60 lifting out of tolerance on August 27, 1991 was caused by adjusting the setpoint high due to failure of the Trevitest equipment, or by normal setpoint drift. <br /><br /> The corrective action to prevent recurrence was a revision to the applicable maintenance procedure to require a post-calibration check of the Trevitest equipment prior to testing another MSSV on the same steamline.
3231991003 | Diablo Canyon 2, Diablo Canyon 1 | 09/01/1991 | 10/01/1991 | 9110100146 | <strong>Inadvertent Entries Into Technical Specification 3.0.3 Due To Personnel Error And Inadequate Procedure Review</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1991, two events of inadvertent entry into Technical Specification (TS) 3.0.3 occurred: 1) at 0535 PDT, while in Mode 4 (Hot Shutdown) at 0 percent power, Unit 2 inadvertently entered TS 3.0.3 when the requirements of TS 3.5.3.d and TS 3.6.2.1 were determined to have not been met following removal of power from both Residual Heat Removal (RHR) pump suction valve operators before entry into Mode 5 (Cold Shutdown); and 2) at 1013 PDT with Unit 2 still in Mode 4, Unit 2 again entered TS 3.0.3 when TS 3.6.2.1 was not met because control power for both Containment Spray (CS) pumps was deenergized. Both events were identified on September 1, 1991, at 1130 PDT during a walkdown of the control room boards. By 1145 PDT, the RHR suction valves and the CS pumps were returned to an operable status. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(b) at 1409 PDT. Unit 2 entered Mode 5 on September 1, 1991, at 1435 PDT. <br /><br /> The root cause for the RHR pump suction valves having been deenergized in Mode 4 was inadequate procedure revision review. The root cause for the CS pumps being deenergized in Mode 4 was personnel error, inattention to detail by the licensed operator issuing clearances.<br /><br /> Corrective actions included revising Operating Procedure L-5 and reviewing all other "L" series procedures, preparation of an Operations Incident Summary, and sending memorandums to appropriate personnel to clarify when clearances will be approved and to emphasize responsibilities for thorough preparation and review of procedure revisions.
3231991004 | Diablo Canyon 2 | 08/13/1991 | 09/16/1991 | 9109250143 | <strong>Technical Specification 3.4.6.2, Action B. Not Performed On Time Due To Calculation Error In A Surveillance Test Result Caused By Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1991, at 1700 PDT, Technical Specification (TS) 3.4.6.2 was not met when the Unit 2 Reactor Coolant System (RCS) unidentified leakage exceeded one gpm. The required action, to reduce the unidentified leakage to the acceptable limit within four hours or be in Hot Standby within the next six hours, was not performed due to an error in a calculation in Surveillance Test Procedure (STP) R-10C, "Reactor Coolant System Water Inventory Balance." This STP had been completed 10 hours earlier and had incorrectly calculated the unidentified leakage as less than one gpm. <br /><br /> On August 13, 1991, at 1755 PDT, containment sump in-leakage was determined to be 1.2 gpm. STP R-10C was performed and RCS unidentified leakage was determined to be 1.9 gpm. An Unusual Event (UE) was declared. Investigation identified the area where the leakage was occurring. Isolation of that piping reduced the RCS unidentified leakage to 0.8 gpm. On August 14, 1991, at 0019 PDT, the UE was terminated. <br /><br /> On August 16, 1991 it was determined that a calculation error had occurred for STP R-10C performed on August 13, 1991, at 0700 PDT. As a result, unidentified leakage had been approximately 1.4 gpm versus the 0.8 gpm recorded.<br /><br /> The root cause of this event was personnel error. The personnel involved in this event have been counseled regarding the need for attention to detail and self verification.
3231991006 | Diablo Canyon 2 | 10/03/1991 | 11/01/1991 | 9111080113 | <strong>Momentary Loss Of Power To Radiation Monitor Rm-26 Causes Control Room Ventilation System Mode Shift (ESF Actuation) Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1991, at 1256 PDT, with Unit 2 in Mode 5 (Cold Shutdown) at 0 percent power, the Control Room Ventilation System (CRVS) shifted from normal mode to pressurization mode. This mode change constitutes an Engineered Safety Feature (ESF) actuation.<br /><br /> While removing instrument AC inverter IY-24 from service in accordance with procedure OP J-10:III, "Instrument AC System-Shutdown and Clearing," a senior licensed operator and a non-licensed operator inadvertently opened the output breaker for inverter IY-23 instead of the intended breaker for inverter IY-24. This resulted in a momentary loss of power to the control room ventilation intake radiation monitor RM-26, which caused the CRVS to shift from normal mode to pressurization mode.<br /><br /> On October 3, 1991, at 1427 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The root cause of this event was personnel error (inattention to detail). The operators involved failed to perform an adequate pre-job review of the operating procedure. They did not notice that specific attachments to the procedure had been provided. <br /><br /> To prevent recurrence, (1) the operators involved were counseled, (2) an Operations Incident Summary has been issued, (3) OP J-10:III will be revised, and (4) Operations Policy A-6 was revised.
3231991007 | Diablo Canyon 2 | 10/06/1991 | 11/01/1991 | 9111080157 | <strong>Inadvertent Safety Injection While In Mode 5 Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1991, at 0008 PDT, with Unit 2 in Mode 5 (Cold Shutdown) during the fourth refueling outage, two safety injection (SI) signals occurred due to technicians operating Solid State Protection System (SSPS) control switches out of sequence with the surveillance test procedure (STP) they were performing. A four-hour, non-emergency report required by 10 CFR 50.72(b)(2)(ii) was made on October 6, 1991, at 0218 PDT.<br /><br /> The cause of the SIs was personnel error. The technicians failed to utilize STP I-16D4, "Reconfiguring An SSPS Train In Modes 5 or 6," during the switch operating sequence. STP I-16D4 requires the SSPS Input Error Inhibit switch to be repositioned from "Normal" to "Inhibit" and the Mode Selector switch from "Test" to "Operate," in that order. The technicians repositioned the switches in reverse order on SSPS Trains A and B. Each train produced an SI signal.<br /><br /> All equipment performed as expected in Mode 5 during the SI. Unit 2 was returned to normal Mode 5 alignment on October 6, 1991, at 0015 PDT. Since emergency core cooling pumps were secured for maintenance, there was no water injection into the reactor coolant system.<br /><br /> The technicians involved in this event were counseled in accordance with PG&E's positive discipline program. A memorandum has been issued from the Vice President, Diablo Canyon Operations and Plant Manager, emphasizing the need for procedural compliance and verification.
3231991008 | Diablo Canyon 2 | 09/19/1991 | 10/18/1991 | 9110240155 | <strong>Contract Radiographers Overexposed Due To Equipment Failure And Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1991, at approximately 0300 PDT, two contract radiographers taking radiographs of piping welds in DCPP Unit 2 Residual Heat Removal Heat Exchanger Room 2-2 discovered that their low and high range pocket ion chambers (PICs) were off scale high. The radiography source was immediately placed in a safe condition. The radiation dose measured by their thermoluminescent dosimeters (TLDs) was approximately 3.1 rem for one individual and 11.5 rem for the other. <br /><br /> The overexposures occurred at the completion of a radiograph when the source (73 curies, Iridium-192) was not completely retracted. The radiographers are believed to have performed two or three additional radiographs before discovering their PICs to be off scale. Assessment of the whole body exposures later determined that they had received 3.0 rem and 15.2 rem, respectively, during the event. <br /><br /> The root causes of this event were the mechanical failure of the source to fully retract into the camera, and the failure of the radiographers to follow their written procedures. <br /><br /> PG&E procedures for DCPP will be revised to require: (1) verification that the radiographer has alarming dosimetry and that the radiographer's survey instrument responds to a radioactive source on each scale, and (2) the use of auto-locking cameras for Iridium sources as a contract requirement. In addition, Quality Assurance and Radiation Protection will review a potential contractor's past radiological safety performance prior to allowing that contractor on the Qualified Suppliers List.
3231991009 | Diablo Canyon 2 | 09/26/1991 | 04/24/1992 | 9205040024 | <strong>10 CFR 100 Dose Limits Potentially Exceeded In The Event Of A Design Basis Loss Of Coolant Accident Recovery As A Result Of Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On September 26, 1991, with Unit 2 defueled, leakage of approximately 1.3 gallons per minute (gpm) was identified from diaphragm valves CVCS-2-8471 and CVCS-2-548 in the charging pump suction line during the performance of a hydrostatic test. The diaphragms in both valves were replaced and the valves tested satisfactory. <br /><br /> On October 4, 1991, at 1645 PDT, an evaluation of the leakage discovered September 26, 1991, determined that the control room and exclusion area boundary 10 CFR 100 dose limits could be potentially exceeded during the design basis recirculation phase of loss of coolant accident (LOCA) recovery. On October 4, 1991, at 1800 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(i). <br /><br /> The root cause of body-to-bonnet leakage in valve CVCS-2-8471 was personnel error in that the valve was not included in the plant preventive maintenance program. The root cause of body-to-bonnet leakage from valve CVCS-2-548 could not be determined. <br /><br /> The preventive maintenance program will be revised to include diaphragm replacement frequency and bolt torquing for diaphragm valves.
3231991010 | Diablo Canyon 2 | 10/22/1991 | 04/20/1992 | 9204280067 | <strong>TS 3.3.3.6 Action Limit For An Inoperable Reactor Cavity Sump Wide Range Level Channel Was Exceeded Due To Inadequate Corrective Actions Following A 1990 Channel Failure</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1991, at 0958 PDT, with Unit 2 in Mode 2 (Startup) at 0 percent power, Action Statement a of Technical Specification (TS) 3.3.3.6 was exceeded due to reactor cavity sump wide range level channel 942A being inoperable for greater than seven days in Modes 1 (Power Operation), 2, or 3 (Hot Standby). <br /><br /> Troubleshooting did not identify any equipment problems. The channel was returned to service at approximately 1700 PDT. The channel was declared operable at 2115 PDT on October 22, 1991, because the channel parameters were determined to be within allowable tolerances. <br /><br /> The failure to meet the TS Action Statement was caused by inadequate corrective actions for a previous similar occurrence. During investigative actions performed following a March 15, 1992, channel 942A failure, I&C discovered that only the zero range had been affected by the failure. The channel was operable in all the ranges required for the performance of its intended safety functions. It is now believed that the previous failures were similar; therefore, this channel was operable during these previous events.<br /><br /> STP I-1B was revised to require that the CSF-5 display screen of the Safety Parameter Display System (SPDS) be reviewed to identify problems with reactor cavity sump wide range level channels. The transducer and the entire electronics package for channel 942A were replaced. No subsequent failures have occurred. Information plaques were installed on the SPDS display panels describing the SPDS signals for a channel problem. Additional training has been provided to operators to increase sensitivity to these failures.
3231991011 | Diablo Canyon 2 | 10/20/1991 | 11/20/1991 | 9111270131 | <strong>Technical Specification 3.5.2, 4.0.4, And 4.0.5 Violations Resulting From Failure To Test A Valve Following Maintenance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1991, at 1400 PDT, the 72-hour Limiting Condition for Operation (LCO) of Technical Specification (TS) 3.5.2, Action a. was exceeded when valve SI-2-8802B was not tested following corrective maintenance. TS 4.0.5 required surveillance was not performed. <br /><br /> On October 20, 1991, at 1724 PDT, TS 4.0.4 was not met when Unit 2 transitioned from Mode 3 (Hot Standby) to Mode 2 (Startup) with the required post-maintenance test (PMT) requirements of valve SI-2-8802B not completed. <br /><br /> On October 22, 1991, at 2100 PDT, the failure to conduct a PMT was identified by Plant Engineering while reviewing required actions for a second transition into Mode 2. The required surveillance test was revised to permit performance in Mode 3 and was successfully performed on October 22, 1991, at 2139 PDT.<br /><br /> The root cause of these events was personnel error due to a failure to recognize that maintenance performed on valve SI-2-8802B would require post-maintenance operability testing. Information supplied in the field copy of the work package was confusing and not sufficient to readily identify PMT requirements. <br /><br /> To prevent recurrence, (1) an Operations Event Report will be issued, (2) Work Planning will issue enhanced work policies, and (3) the Engineering Test Group will be trained on performing mode transition searches.
3231991012 | Diablo Canyon 2 | 10/12/1991 | 03/05/1992 | 9203090463 | <strong>Failure To Meet Technical Specification 4.5.2 When Visual Inspections Were Not Performed Due To A Programmatic Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1991, at 2340 PST with Unit 2 in Mode 4 (Hot Shutdown) at 0 percent power, following the Unit 2 fourth refueling outage (2R4), containment integrity was established. <br /><br /> From October 16, 1991 to February 4, 1992, numerous investigations were conducted to identify the cause of debris left in containment. These investigations consisted of a QC surveillance, an Engineering evaluation, personnel interviews, a review of containment entry records, and several meetings of the Technical Review Group (TRG). During these investigations, four individuals stated that they had not completed an STP M-45B, "Containment Inspection When Containment Integrity is Established," data sheet. Based on the results of these investigations, on February 4, 1992, the TRG conservatively determined that Technical Specification 4.5.2.c had not been met. <br /><br /> The root cause of this event was determined to be lack of a comprehensive program for control of materials after establishment of containment integrity. <br /><br /> To prevent recurrence, a procedure will be developed to establish a comprehensive program for control of material after containment integrity has been established. Appropriate personnel will be trained on this procedure.
3241991001 | Brunswick 2 | 01/25/1991 | 04/04/1991 | 9104100221 | <strong>Unit 2 Turbine Trip/Reactor SCRAM While Calibrating a Feedwater Computer Point</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1991, Unit 2 reactor scrammed from 100% power. The scram was due to a turbine trip on high reactor water level which resulted from the Feedwater Level Control System responding to a sensed loss of feed flow during performance of a Process Computer point calibration on the Feedwater flow logic system. Instrumentation and Control (I&C) technicians performing the calibration failed to recognize a procedure prerequisite step which stated that the unit must be in cold shutdown or refuel to perform the procedure. <br /><br /> The event was due to the failure of the work control process to prevent this activity from being performed, caused by inadequate reviews in the scheduling and implementation phases of the process and the failure of the technicians to ensure the prerequisites were met. In addition, the procedure Summary Sheet incorrectly stated that no special plant conditions were required for the performance of the procedure. <br /><br /> Corrective actions included stoppage of the computer point calibrations, suspension of use of the procedure Summary Sheets, communication of the event with plant personnel, development of a Recovery Action Plan, and initiation of a working level Task Force to investigate this and similar recent personnel errors.<br /><br /> The safety systems functioned as designed. Equipment response concerns were identified, but none posed a significant safety concern.
3241991002 | Brunswick 2 | 04/02/1991 | 05/02/1991 | 9105070201 | <strong>IRM D Spikes Upscale During DC Ground Isolation Procedures A Full RPS Trip</strong><br /><i>Abstract:&nbsp;</i>At approximately 0959 hours (EST) on April 2, 1991, an unexpected trip in Reactor Protection System (RPS) Trip System B coincident with an expected trip in RPS Trip System A, was incurred and a consequential full RPS trip was received. The expected trip was incurred when power to the automatic scram logic of RPS Trip System A was deenergized during dc ground isolation procedures. The full RPS trip was reset shortly thereafter. <br /><br /> The direct cause of the unexpected trip was Intermediate Range Neutron Monitoring (IRM) channel D spiking upscale. A signal noise, created by the RPS Trip System A scram relays deenergizing, was induced into the IRM D detector circuitry IRM channel D was declared inoperable and a Work Request/Job Order (WR/JO 91-AGPA1) was initiated to troubleshoot IRM D for incoming noise and repair as necessary. Metal Oxide Varistors (MOVs) have been installed across the coils of the associated scram relays on a temporary basis until permanent installation can be effected. MOVs have proven to be effective in suppressing high voltage spiking. Additional corrective action included initiating an Adverse Condition Report (ACR B91-177) to assess the performance of IRMs. <br /><br /> The safety significance of this event was minimal as control rods were fully inserted in the core prior to the full RPS trip. Previous similar occurrences have been reported in LERs 1-84-034, 1-85-031, 1-85-045, 2-86-014, 1-87-010, 2-88-009 and 1-89-002.
3241991003 | Brunswick 2 | 05/21/1991 | 06/20/1991 | 9106260235 | <strong>Component Failure In RCIC Steam Line Break Isolation Actuation Trip Unit Results In Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1991, at 1500 hours (EST), the Unit 2 reactor was at 100% power. The Reactor Core Isolation Cooling (RCIC) system was isolated for routine surveillance testing. At this time, a Primary Containment Isolation System (PCIS) Group 5 logic B isolation signal was generated. Investigation determined that an erroneous trip in the RCIC steam line break d/p high flow, channel B, trip unit was the cause of this Engineered Safety Feature (ESF) actuation. Per design, the RCIC steam supply outboard isolation valve, 2-E51-F008, received an isolation signal, but since both the inboard and outboard isolation valves were previously closed per procedure, no valve movement was experienced. This event was discovered on May 21, 1991, at approximately 1520 hours during an attempt to restore RCIC to standby readiness after completion of the surveillance testing. At this time, the control operator noticed that the "RCIC Steam Line Break D/P HI" annunciator was sealed in and would not reset. Subsequently, at approximately 1545 hours, the condition cleared without any corrective actions being performed. The cause of this event was component failure. A transistor anomaly, characterized by a gradual increase in the trip output voltage, caused the output of the Rosemount Model 510DU Analog Master Trip/Calibration Unit trip card to produce an erroneous trip output signal to the PCIS logic. The failed trip unit was removed and replaced with a new one from stock by 0324 hours, on May 22, 1991. Additional corrective action will include changing out the older Model 510DU Analog Trip Units with the newer Model 710DU Analog Trip Units on an as needed basis. The RCIC system was placed in standby at approximately 0435 hours on May 22, 1991. This event had no adverse impact on nuclear safety. Previous similar events involving Rosemount Model 510DU Analog Trip Units have been reported in LERs 2-89-001, 2-89-008 and 1-89-017.
3241991004 | Brunswick 2 | 06/25/1991 | 07/25/1991 | 9103270162 | <strong>Component Failure In RWCU High Ambient Temperature Switch Point Module Results In Unplanned Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1991, at 0639 hours (EDT), the unit 2 reactor vas at 100% power. The Reactor Water Cleanup (RWCU) System was isolated and routine Maintenance Surveillance Testing was in progress. At this time, a Primary Containment Isolation System (PCIS) Group 3 logic A2 isolation signal was generated due to an RWCU High Ambient Temperature Switch Point Module (Riley Model 86 PT-GF) failing upscale. Per design, the RWCU Inlet Inboard Isolation Valve received an isolation signal, but since both the inboard and outboard isolation valves were previously closed per procedure, no valve movement was experienced. The unit Control Operator became aware of this unplanned Engineered Safety Feature (ESF) actuation by Control Room annunciation. Subsequently, at 1030 hours the same point module again failed upscale with no associated maintenance activities in progress. Component failure was determined to be the cause of this event and the failed point module was removed and replaced with a new one from stock. The defective temperature switch point module is being shipped to General Electric (GE) for failure analysis. Current plans are to change out the existing Riley Model 86 Temperature Switches with more modern NUMAC hardware (reference LER 2-90-019). Testing was completed satisfactorily and the RWCU system was returned to service at approximately 1020 hours on June 26, 1991. This event had no adverse impact on nuclear safety. Previous similar events involving component failure of Riley Model 86 Temperature Switches have been reported in LERs 2-83-058, 2-84-017, 1-86-008, 1-86-014, 2-87-007 and 2-87-009.
3241991005 | Brunswick 2 | 06/30/1991 | 11/26/1991 | 9112020145 | <strong>ESF Actuations Caused By Voltage Regulator Transient With Failure Of Primary Containment Isolation Solenoid Operated Valves</strong><br /><i>Abstract:&nbsp;</i>A surveillance to check the operation of the Manual and Auto Main Generator Voltage Regulators was in progress. Following a step of the procedure which required the voltage regulator Mode Selector switch to be placed in the Manual position, the Transfer Voltmeter deflected significantly. Emergency Bus E4 was lost and the Reactor Protection System Motor-generator set 2B tripped. Emergency Diesel Generator #4 auto-started and a half SCRAM signal was received along with Primary Containment System Isolation signals; Group 3 (Reactor Water Cleanup), Group 6 (Containment Atmospheric Control), half Group 1 (Main Steam Line), Group 2-Division II (Transverse Incore Probe and Drywell Floor/Equipment Drains). Main Generator output voltage was raised using the Manual voltage regulator and the voltage regulator was transferred to the Automatic mode. ESF actuations occurred except for the outboard Drywell Floor Drain Isolation valve which failed to close on the Group 2-Division II signal. The Inboard Floor Drain Isolation valve was closed after four attempts and the line was isolated. The cause of this event is still under investigation. Due to the plant being at full power, the decision was made to allow the voltage regulator to remain in the Automatic mode until troubleshooting takes place during the September, 1991 scheduled shutdown for a refueling outage. Initial investigations indicate that the valve failures were due to a lubricant which gelled inside the ASCO solenoids causing the core to adhere to the top casing in its energized position. Scratches on the outboard valve solenoid internals may have contributed to the failure. As corrective action the solenoids on the two valves that failed were replaced. Valves with similar solenoids were tested and surveillance frequency increased. A task force has been established to investigate the ASCO solenoid issue. Under reasonable and credible alternative conditions this event would not have been more severe. Other similar ASCO events were LER 2-88-001 and Plant Incident Report 90-036; Voltage Regulator events LER 2-81-01, 1-86-024, 2-90-015.
3241991006 | Brunswick 2 | 08/21/1991 | 09/20/1991 | 9109260116 | <strong>Electrical Noise Induced During Routine RWCU Surveillance Testing Caused A Spurious Isolation Signal To Be Initiated In The RWCU Leak Detection Logic Resulting In An Unplanned Engineered Safety Feature Actuation.</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1991, at approximately 0930 hours (EDT), the Unit 2 reactor was operating at 100% power. At this time, a spurious trip of a 20-foot/50-foot Reactor Water Cleanup (RWCU) Piping General Area High Energy Line Break (HELB) leak detection temperature switch (2-G31-TSH-5932) was incurred during routine RWCU surveillance testing. When this Riley Model 86 Temperature Switch tripped, an unexpected isolation signal was initiated in Trip System B of the Primary Containment Isolation System (PCIS). Per design, the RWCU Inlet Outboard Isolation Valve received an isolation signal, but since both of the RWCU inlet isolation valves were previously closed, no valve movement was experienced. This spurious trip resulted from electrical noise induced during testing of a nearby RWCU Room Differential Temperature Switch (2-G31-N602F). The Instrument and Control (I&C) technicians performing the surveillance test notified licensed personnel of this unplanned ESF actuation. The susceptibility of these switches to spurious trips has been documented in General Electric Information Letters (SILs 416 and 443) and IE Information Notice (IEN) 86-69. Current plans are to changeout the existing Riley Model 86 Temperature Switches with more modern NUMAC hardware on Unit 1 in 1992, and Unit 2 in 1993. Short term corrective actions (such as adding one-second time delay relays to the isolation logics for the Unit 2 isolation valves) are being evaluated. This event had no adverse impact on nuclear safety. Previous similar events have been reported in LERs 2-88-020, 2-90-019, and 2-91-009.
3241991007 | Brunswick 2, Brunswick 1 | 04/07/1991 | 08/14/1991 | 9108220141 | <strong>Emergency Diesel Generator Monthly Load Testing Could Mask Early Detection Of A Potential Failure Of An Engine Driven Fuel Oil Pump</strong><br /><i>Abstract:&nbsp;</i>This Voluntary Report is being submitted to address concerns raised by the April 7, 1991, 18 month Emergency Diesel Generator (EDG) #3 Load Test (2MST-DG13R). The test results determined that the bus to bus time on #3 EDG, resulted in a 2A Core Spray (CS) response time of 28.08 seconds. This exceeded the required Technical Specification (TS) response time of less than or equal to 27 seconds. The required response time for 2A CS vas exceeded due to the slow pressurization of the fuel oil header by the positive displacement engine driven fuel oil pump, whose internal relief valve complete bypass setting was found low. The EDG engine driven fuel oil pump was replaced and 2MST-DG 13R performed satisfactorily. <br /><br /> This event raised a concern that during the EDG monthly load tests (PT-12.2A/B/C/D) the start of the electric driven fuel oil pump could mask a failure of the engine driven fuel oil pump. The EDG monthly load tests (PT-12.2A/B/C/D) were revised to include some starts (10 of 12 months) without allowing the start of the electric driven fuel oil pump to pressurize the fuel oil line prior to start-up. <br /><br /> This is not a significant safety concern as the SAFER/GESTER-LOCA Analysis, has shown that adequate core cooling would be provided given a response time of up to 40 seconds. Additionally, other EDG's and low pressure Emergency Core Cooling Systems (ECCS) would have been available in the event of an accident. <br /><br /> This is an isolated incident.
3241991008 | Brunswick 2 | 07/09/1991 | 08/08/1991 | 9108140231 | <strong>Inability To Control The RWCU Reject Flow Control Valve Caused Excessive Flow Through The Nonregenerative Heat Exchangers Resulting In RWCU Isolations On High Temperature</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1991, at approximately 2048 hours (EDT) and on July 24, 1991, at approximately 0402 hours, the Reactor Water Cleanup (RWCU) Inlet Outboard Isolation Valve received a nonregenerative heat exchanger discharge high temperature isolation signal and automatically closed. This is not a primary containment isolation signal (Engineered Safety Feature actuation); it protects the resin in the filter/demineralizer units from over temperature conditions. The unit was at 100% power during these events. Both isolations occurred while the RWCU was being placed into service. The unit control operator (CO) became aware of the isolations by Control Room annunciations. In each case, the high temperature condition resulted from too much reactor coolant flow passing through the nonregenerative heat exchangers while rejecting flow to the Main Condenser. On July 9, 1991, the CO had throttled open the RWCU Reject Flow Control Valve and stabilized the flow at approximately 50 gpm. About ten minutes later, the flow drifted up to approximately 100 gpm. A caution tag was placed on the manual control station for the Reject Flow Control Valve, and the RWCU system was placed back into service at approximately 2106 hours on July 9, 1991. Troubleshooting was performed on July 23, 1991, but no problems were noted at this time. Subsequently, on July 24, 1991, while the CO was transferring flow to the reactor vessel, RWCU isolated. Additional troubleshooting on the Reject Flow Control Valve was performed, and the feedback linkage was found loose on the Honeywell pneumatic valve positioner. The linkage was adjusted, and testing was performed satisfactorily. The RWCU system was returned to service at approximately 1730 hours on July 25, 1991. These events had no adverse impact on nuclear safety. Previous similar events have been reported in LERs 1-89-013 and 1-91-017.
3241991009 | Brunswick 2 | 07/09/1991 | 08/08/1991 | 9108140235 | <strong>Voltage Spike During Routine HPCI Surveillance Testing Causes Spurious Isolation Signal In The RWCU Leak Detection Logic Resulting In Unplanned Engineered Safety Feature Actuations.</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1991, at approximately 0923 hours (EDT), and on August 6, 1991, at approximately 1129 hours, the Unit 2 reactor was at 100% power. At these times, the Reactor Water Cleanup (RWCU) Inlet Inboard Isolation Valve received a spurious Primary Containment Isolation System (PCIS) Group 3 isolation signal in Trip System A and closed. Trip logic A closes the inboard isolation valve only. The unit control operator (CO) became aware of these unplanned Engineered Safety Feature (ESF) actuations by Control Room annunciation. Both events occurred during a routine High Pressure Coolant Injection (HPCI) steam leak detection channel functional test. A logic relay located in the associated Steam Leak Detection Cabinet de-energized producing a voltage spike sufficient to disturb the incoming AC power. This voltage spike caused a momentary change of state of a Riley Model 86 Temperature Switch (Riley SCAM Module) located in the same cabinet. The module affected was in the RWCU leak detection logic. The susceptibility of these switches to spurious trips has been documented in General Electric Information Letters (SILS 416 and 443) and IE Information Notice (IEN) 86-69. Current plans are to change out the existing Riley Model 86 Temperature Switches with more modern NUMAC hardware. As an interim measure, metal oxide varistors (MOVs) have been installed across the coils of the associated 120 VAC HPCI isolation logic relays on Unit 2. MOVs have proven to be effective in suppressing high voltage spiking. Testing before and after installation of the MOVs showed substantial reduction in spurious trip outputs of the Riley SCAM Modules. Plans are to install MOVs on Unit 1 also. These events had no adverse impact on nuclear safety. Previous similar events involving spurious isolations have been reported in LERs 1-88-002, 2-88-020, 1-89-004, 1-89-005 and 2-90-019.
3241991010 | Brunswick 2 | 08/06/1991 | 09/05/1991 | 9109110071 | <strong>RWCU Reject To Main Condenser Isolation Valve Seat Leakage Caused Spurious Isolation Signals To Be Incurred On High Differential Flow While Restoring The RWCU System To Service Resulting In Four Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1991, at approximately 2302 hours (EDT), and on August 21, 1991, at approximately 1714 hours, the Reactor Water Cleanup (RWCU) system automatically isolated on high differential flow (system leak detection) while being restored to service. The RWCU system also automatically isolated on high differential flow at 0620 hours, and again at approximately 1433 hours, on August 22, 1991, during subsequent attempts to restore the system to service. The Unit 2 reactor was operating at 100% power during these events. These high differential flow isolations stemmed from the RWCU Reject To Main Condenser Valve (2-G31-F034) leaking past the seat. When the RWCU system is out of service, leakage through this valve is sufficient to require refilling/repressurizing of the system. Although the RWCU Operating Procedure (2-OP-14) included alternate pressurization procedures for increased control, it did not provide sufficient guidance (which alternate procedure to use, when to use it, and how to use it) to allow the unit operators to pressurize the system using the optimum procedure. 2-OP-14 was revised on August 24, 1991, to ensure optimum procedures are used when the alternate method of system pressurization is used. The RWCU Reject To Main Condenser Valve, 2-G31-F034, is expected to be replaced during the upcoming Unit 2 Refueling Outage, currently scheduled to be completed by December 6, 1991. In these events, no actual pipe breaks existed. The isolations were incurred while placing the RWCU system into service due to differential flow perturbations. The ECCS, RCIC system, and EDGs were operable and in standby readiness during these events. Previous similar events have been reported in LERs 2-88-003, 2-88-010, 2-90-011, and 2-90-014.
3241991011 | Brunswick 2 | 08/24/1991 | 12/16/1991 | 9112240306 | <strong>Potential Leakage Past Reactor Water Cleanup System Primary Containment Inlet Isolation Valves May Have Resulted in a Primary Containment Penetration Not Being Completely Isolated</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1991, Operations personnel were attempting to place the Reactor Water Cleanup (RWCU) system in service. The light bulb on the motor control center for the RWCU inlet outboard isolation valve was burned out. During replacement, the bulb broke off in the socket, causing an electrical short and blowing the control power fuse. This rendered the valve inoperable. Per Technical Specifications for primary containment isolation purposes, the inlet inboard isolation valve was closed from the Reactor-Turbine Generator board. Operators noted that the process line downstream of the valve did not depressurize as expected. Several valves downstream were cycled which created sufficient differential pressure to cause the valve to seat. The control power fuse for the outboard isolation valve was replaced. A special test was developed and performed on August 25, 1991 to quantify leakage and assess the operability of the inboard isolation valve. The results indicated that both the inboard and outboard isolation valves were leaking by. When a sufficient differential pressure was placed on the valves, they both appeared to seat. On August 26, 1991, another similar test was performed to assess RWCU on line leakage and operability of the inboard and outboard isolation valves. This test conservatively confirmed that the outboard isolation valve was operable under the differential pressure test conditions; however, on August 24, 1991 when the outboard isolation valve was inoperable with the blown fuse and the inboard isolation valve was potentially leaking by, the line may not have been isolated. Both the inboard and outboard isolation valves were closed and placed under equipment clearance until the unit was shutdown for refueling on September 11, 1991. During the unit shutdown a local leak rate test will be performed to determine the amount of leakage past the inboard and outboard isolation valves. Any necessary repairs to the valves will be made during the refuel outage. The safety significance of this event was minimal. Previous similar events include: PCIS- LER 1-91-016, 2-87-001; 2-84-016 2-79-078, 2-91-005: MCC lights 2-90-020. This report is being provided as supplemental information.
3241991012 | Brunswick 2 | 09/14/1991 | 10/14/1991 | 9110240054 | <strong>Component Failure Of The Reactor Water Cleanup System Outlet Flow (Return To The Reactor) Differential Pressure Transmitter Resulted In A Cleanup Leak Hi-Hi Alarm And Subsequent Initiation Of An Engineered Safety Feature Isolation Signal.</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1991, at approximately 1913 hours (EDT), the Unit 2 reactor was in cold shutdown. Unit 2 was in day 3 of a scheduled 77 day refueling outage. At this time, the Reactor Water Cleanup (RWCU) system "Cleanup Leak HI-HI" alarm annunciated in the Main Control Room. The RWCU system had been on-line for approximately one and a half hours, and was rejecting reactor coolant to the Main Condenser Hotwell for reactor water level control, when this high differential flow (RWCU line break) alarm was received. Upon receipt of the "Cleanup Leak HI-HI" alarm, the unit Control Operator (CO) tripped the RWCU recirculation pump, and manually initiated closure of the RWCU system inlet inboard and outboard isolation valves to promptly isolate the system. Although the RWCU system was manually isolated, the isolation signal remained sealed in, and a Primary Containment Isolation System (PCIS) Valve Group 3 automatic isolation signal was received. The RWCU system was subsequently walked down and no leaks were located. The cause of this event was failure of the RWCU system outlet flow (Return To The Reactor) Rosemount 1153 differential pressure transmitter (2-G31-FT-N041). The failed transmitter was new and had been in service approximately two weeks when this event occurred. Since the RWCU system differential flow-high actuation instrumentation is not required to be operable in the cold shutdown mode, it was jumpered out to allow the RWCU system to be restored to service. On September 15, 1991, at approximately 0024 hours, the RWCU system was restored to service. 2-G31-FT-N041 is expected to be replaced by December 1, 1991. Plans are to ship the defective transmitter to Rosemount for failure analysis. This event had no adverse impact on nuclear safety.
3241991013 | Brunswick 2 | 09/14/1991 | 10/14/1991 | 9110240028 | <strong>During Residual Heat Removal Shutdown Cooling Loop Transfer The Reactor Coolant System Structural Integrity Temperature Limit Was Exceeded When The Unit's Senior Reactor Operator Failed To Recognize This Limitation</strong><br /><i>Abstract:&nbsp;</i>At 1730 on September 14, 1991, Unit 2 was In Cold Shutdown and the Residual Heat Removal (RHR) shutdown cooling was being transferred from the B to A loop. The Unit Senior Reactor Operator (SRO) had anticipated that the reactor coolant would heat up in a controlled manner during this transfer because both loops of RHR shutdown cooling would temporarily be out of service during the transfer and fuel was still in the reactor vessel. He applied the Technical Specification (TS) Mode change temperature limit for Cold Shutdown of 212 degrees F, as the most limiting reactor coolant temperature. Earlier that day, the same SRO had added temporary shielding permits for class 1 components (American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code) to the Reactor Coolant System Structural Integrity Limiting Condition for Operation (LCO). This restricted the reactor coolant temperature to the reactor vessel Nil-Ductility Transition (NDT) temperature + 50 degrees F (143 degrees F). When the SRO later approved the RHR shutdown cooling loop transfer he did not recognize the more restrictive limit until the loop transfer was partially complete and reactor coolant temperature had increased to approximately 130 degrees F. The Shift Supervisor was notified and since they were already into the loop transfer they decided to continue placing the A loop RHR in shutdown cooling as the fastest means of restoring shutdown cooling. The loop transfer was safely completed, but not before the reactor coolant temperature reached 155 degrees F. The reactor coolant temperature had been above the 143 degrees F limit for approximately 20 minutes before the RHR shutdown cooling loop brought the temperature back within specification. <br /><br /> This isolated event resulted from the SRO's failure to recognize the limiting temperature condition, but it resulted in no damage to the plant.
3241991014 | Brunswick 2 | 09/27/1991 | 10/28/1991 | 9111050129 | <strong>Unplanned RPS Actuation Resulted From Senior Control Operator Re- Aligning The Scram Discharge Volume Hi-Hi Level Trip Bypass Switch Without Informing The Duty Reactor Operators</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1991 at 0443 Unit 2 was in a refueling outage with the reactor core partially off loaded to the spent fuel pool. All control rods were fully inserted and the Control Rod Drive (CRD) system was secured except for a temporary mechanical jumper to supply cooling water while CRD system maintenance was being performed. Several hours earlier, as the CRD system was being prepared to return it to service, the Reactor Protection System (RPS) trip had been reset. The Unit's senior reactor operator (SRO) while touring the reactor control panels found the Scram Discharge Volume (SDV) Hi-Hi Level Trip Bypass Switch was still in the Bypass position with both SDV not drained annunciators cleared. As the reactor operators (RO) were busy, the SRO returned the switch to the Normal position himself, without informing the ROs. The SDV Hi-Hi Level RPS Trip, whose annunciator he had not verified, resulted in the full RPS trip. <br /><br /> There is no safety significance to this event, as the RPS responded as expected and no control rod motion occurred since all control rods were previously fully inserted. The longer reset times of the SDV electronic level switches does not affect their operability. <br /><br /> Previous related LERs are 1-88-031 and 1-87-010.
3241991015 | Brunswick 2 | 10/02/1991 | 05/28/1993 | 9306040086 | <strong>Unplanned ESF Actuation While Removing Reactor Low Level Instrumentation From Service For Lowering Of Reactor Vessel Level For Invessel Inspections And Decontamination.</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991, the reactor was defueled. A special procedure (SP) to coordinate the lowering of the vessel level for invessel inspections and chemical decontamination was in progress. Prerequisite steps which disable and place a clearance on the ECCS/PCIS and RPS automatic initiations on low reactor water level components were in progress. At 0216, a spurious low level (LL) trip signal was generated that resulted in closure of isolation valves to the drywell, automatic starting of the DG's and partial actuation of ECCS logic. This event was caused by lack of a caution requiring actions to be performed in the order specified in the SP. Typically, pre-requisites do not require actions and can be verified in any order; as opposed to procedure steps which must be performed sequentially. The SP was revised to incorporate the required caution statement and approved on 10/15/91. Subsequently, the SP has been revised to place the actions required by the prerequisite steps and the caution within the body of the procedure. Personnel involved with initiating, approving, hanging and pulling of clearances received real time training on this event. This was an isolated event and no generic implications regarding the interface between procedures and clearances were found. This event would not have been more severe under reasonable and credible alternative situations.
3241991016 | Brunswick 2 | 10/05/1991 | 11/04/1991 | 9111080143 | <strong>Severe Weather Induces A Voltage Drop On An Off-Site Distribution</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1991, at 0136, Unit 2 was in a refueling outage with all fuel removed from the reactor vessel. The Emergency Core Cooling Systems (ECCS) initiations had been defeated to support having the reactor vessel drained down for in-vessel maintenance. The #3 Emergency Diesel Generator (EDG) was out of service for scheduled maintenance. To Satisfy the Technical Specification surveillances required due to #3 EDG being inoperable, #4 EDG operability verification testing was in progress. #4 EDG was running but had not been electrically tied to the 4160 volt Emergency Bus E4. Prior to the auxiliary operators completing the electrical tie, an electrical storm caused a 230 kilo-volt off-site distribution line to trip on a phase to ground fault, and the master/slave breaker from the Balance of Plant (BOP) Bus 2C to the Emergency Bus E4 opened. This resulted in a momentary loss of voltage on Emergency Bus E4 during the automatic transfer to the #4 EDG. While the automatic transfer to the #4 EDG lasted only approximately 4 seconds, as designed, the Reactor Protection Bus B (RPS Bus B) was deenergized. The loss of RPS Bus B resulted in the closure of some Primary Containment Isolation System (PCIS) Division II valves and, an isolation signal for secondary containment with a Standby Gas Treatment System initiation signal. The response of the Emergency Safety Feature (ESF) systems was as expected considering the outage condition of the systems. At 0315 on October 5, 1991, the Emergency Bus #4 was reenergized from the BOP Bus 2C.<br /><br /> As designed the 230 kilo-volt line voltage drop was of sufficient magnitude to actuate the undervoltage relay, therefore no operability concerns were identified that would require corrective action. The safety significance is minimal as the required safety functions occurred and the loss of Emergency Bus #4 lasted approximately 4 seconds while transferring to the #4 EDG. Unit 1 was not affected by the transfer of the Emergency Bus E4 to the #4 EDG.
3241991017 | Brunswick 2 | 10/17/1991 | 11/16/1991 | 9111250111 | <strong>Safety Relief Valves Tested At Wyle Laboratories Exceeded Technical Specification Limit Due To Pilot Disc-To-Seat Bonding.</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was shutdown and in day 36 of a 77 day scheduled refueling outage. Eleven safety relief valve (SRV) pilot assemblies were removed from the unit and shipped to Wyle Laboratories for set pressure testing and recertification. 'As-received' testing was performed by Wyle Laboratories using Wyle Test Procedure No. 1025 with the following results: Two of the SRV pilots (G,L) had a setpoint drift of less than 1%, Five of the SRV pilots (C,D,E,F,K) had a setpoint drift of between 1.6% and 3.6%, One SRV pilot (J) had a setpoint drift of 8.6%. The remaining three SRV pilots (A,B,H) did not initially lift at steam test pressures of 1207, 1303 and 1260 psig respectively. Special diagnostic testing was performed on the three SRV pilot assemblies that did not initially lift. The average percent drift for all SRV's is 7.0%, with the highest drift for any SRV at 20.2%. <br /><br /> An engineering evaluation has determined that oxygen induced pilot-disc-to-seat bonding prevented the three pilots from initially actuating. The pilot discs have been replaced in SRV pilots A, B, C and J and all four of these pilots have been successfully recertified. SRV D's PH13-8Mo disc has been replaced with a Stellite 6b disc. Other SRV pilots sent to Wyle have also been recertified. <br /><br /> Carolina Power and Light (CP&L) Company will request a Technical Specification change to relax the setpoint tolerance for the SRVs from 1% to 3%. CP&L is investigating a pilot disc modification to mitigate the pilot-to-disc bonding problem. Several material deposition techniques are being analyzed to enhance the pilot disc surface. Although the Technical Specification limiting condition for operation was exceeded, the test results are bounded by GE analysis of the 1986 event. The GE analysis determined that the peak vessel pressure would have remained below the ASME code reactor vessel pressure limit of 1375 psig.
3241991018 | Brunswick 2 | 10/20/1991 | 11/19/1991 | 9111270070 | <strong>Reactor Building Ventilation Isolation and Standby Gas Train Start Due to Low Level #2 Actuation Caused by Reactor Level Instrumentation Reference Leg Perturbation Incurred During Technical Specification Testing</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in Refuel (Mode 5) with the reactor vessel defueled. At 1208 on 10/20/91, while returning to service an A loop reactor pressure indicator following Technical Specification required calibration testing, a hydraulic perturbation of a shared reference leg occurred. The perturbation resulted in isolation of the Unit 2 Reactor Building Ventilation System and automatic start of the 2A and 2B Standby Gas Trains (SBGT). <br /><br /> A special procedure was developed to support root cause determination. The results of the special procedure indicate that the perturbation was due to a lack of attention to detail while venting applied calibration pressure from a reactor pressure indicator. Immediate corrective action was implemented to ensure that the B loop reactor pressure indicator calibration process was monitored by the responsible maintenance supervisor. Additional corrective actions include counseling of the responsible Instrumentation and Control (I&C) technician and performance of a Human Performance Evaluation. A review of the event will be conducted with appropriate Maintenance personnel to strengthen their awareness of the potential for perturbation of reactor vessel level instrumentation during shutdown conditions. <br /><br /> This event poses minimal safety significance in that the affected systems functioned as designed and the Unit was in the refuel condition with the reactor vessel defueled. Other perturbations have been reported in LERs 1-90-006, 1-87-017, 2-90-006, 2-89-017 and 2-86-020.
3241991019 | Brunswick 2 | 11/12/1991 | 08/12/1993 | 9308170190 | <strong>LLRT Failure of Two Main Steam Lines' Inboard and Outboard Isolation Valves Resulting in a Condition Outside the Plant Design Basis.</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1991, the Unit 2 reactor was shutdown in refuel/maintenance outage. Local leak rate testing (LLRT) of the main steam isolation valves (MSIVs) had been performed. The results of testing indicated that MSIV leakage on main steam lines (MSLs) C and D had exceeded the Technical Specification (TS) limit of 11.5 standard cubic feet per hour (scfh), but the actual amount of leakage could not be determined. MSL C outboard MSIV leakage was caused by an indication across the in-body seat. It is believed the indication resulted from the disk closing on a piece of metal that had spalled off the body bore during a previous closure. MSL C inboard MSIV leakage resulted from poor disk to in-body seat contact caused by low spots. Low spots are generally the result of in-body seat deformation from thermal expansion and contraction. It was believed that MSL D outboard MSIV leakage resulted from the disk not seating completely against the in-body seat. The disk outside diameter was contacting a raised lip (tooling mark) on the in-body seat surface. It was believed that low spots also caused leakage of the MSL D inboard valve. MSLs C and D MSIVs repairs were completed and a repeat of the testing revealed zero leakage in both MSLs (ie; MSL C = 0.173 scfh and MSL D = 0.266 scfh). This event is considered potentially safety significant based on the inability to determine the amount of leakage. A previous failure of two MSIVs to meet the TS required 11.5 scfh leakage requirement has been reported in LER 1-88-025. That LER involved the outboard MSIV on two separate MSLs. On December 7, 1992, the results of testing indicated that MSIV leakage on MSL D had again exceeded Technical Specification limits (LER 2-92-010).
3241991020 | Brunswick 2 | 12/14/1991 | 01/13/1992 | 9201220184 | <strong>High Pressure Coolant Injection System Startup Routine Surveillance Testing Finds Loose Components After A Refueling Outage Rebuild</strong><br /><i>Abstract:&nbsp;</i>At 1400 on 12/14/91, Unit 2 Reactor was at 2% reactor power during the startup following a refueling outage. The High Pressure Coolant Injection (HPCI) turbine was uncoupled for routine overspeed trip mechanism testing. The overspeed trip mechanism had been adjusted after the initial test run showed that the turbine did not trip within the required speed range. During the second test run, the HPCI turbine steam supply valve (E41-F001) would not open from the control room. The E41-F001 valve actuator had been rebuilt during the outage but the limit switch assembly finger base which holds the individual limit switches was found loose. The E41-F001 limit switch assembly was tightened and adjusted. The other HPCI valve actuators that had been rebuilt by the same service vendor were checked and no problems were found with these limit switch assemblies. Based on discussions with the service vendor and the inspection results, this is considered an isolated event. <br /><br /> At 1436 on 12/15/91, the overspeed testing was recommenced but an erratic turbine speed feedback signal stopped the test. The erratic signal was due to the speed sensing gear having come loose from its shaft. No damage was found and the speed sensing gear set screws were tightened. The speed sensing gear had not been removed from the shaft that outage, but the possibility exists that the speed sensing gear impacted the magnetic pickup during one of several removals and installations of the turbine Woodward governor upper housing. <br /><br /> These isolated events have minimal safety significance. While the HPCI system itself was not available, the other Emergency Core Cooling Systems (ECCS) were operable during this period.
3241991021 | Brunswick 2 | 12/17/1991 | 01/13/1992 | 9201210288 | <strong>Voltmeter Internal Failure During Testing Results In An Inadvertent HPCI Injection And Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>At 09:42, on December 17, 1991, Unit 2 was at 5% Reactor power. A startup was in progress on completion of a refueling outage. The Emergency Core Cooling Systems were operable. The Reactor Scrammed when the High Pressure Coolant Injection (HPCI) system inadvertently started and injected relatively cold water into the reactor vessel. <br /><br /> Instrumentation and Controls (I&C) technicians were performing a routine surveillance (2MST-RHR23M) on the HPCI Reactor vessel Low Level 2 (118") initiation logic. Per the surveillance, an "A" channel level instrument was actuated and its relay contacts were verified closed by checking the voltage across the open "B" channel contacts. This voltage cheek was performed with a Fluke 860OA-01 digital voltmeter (DVM), which has since been verified to have an internal fault. The fault allowed sufficient current flow to actuate an initiation of the HPCI system. The relatively cold water injected by the HPCI system caused the Reactor power to exceed the 15% Average Power Range Monitor (APRM) Scram setpoints. Once the HPCI initiation was verified as invalid, the HPCI system was manually shut down. <br /><br /> After the cause of the Unit 2 Reactor Scram had been identified, startup was recommenced at 02:23 on 12/18/91. <br /><br /> This isolated event posed minimal safety significance in that plant systems responded as designed.
3251991001 | Brunswick 1 | 01/03/1991 | 02/28/1991 | 9103070003 | <strong>Dropped Fuel Bundle During Refuel Outage 7</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1991, during refueling reloading operations, fuel bundle LHG612 was dropped when a momentary loss of power to the refuel grapple occurred when the bundle encountered resistance with the adjacent control blade as it was being lowered into core position 09-16. The bundle fell approximately 127" into its core position against the fuel support piece. No releases occurred as a result of this event. The event investigation determined that a reversal of the grapple solenoid air lines and grapple control switch resulted in the grapple not being "fail-safe" on loss of power. The bundle dropped as a result of the refuel grapple opening when the bundle load was lost, concurrent with the loss of power to the grapple. The event investigation was unable to determine whether the as-found configuration of the grapple was from original delivery or the result of modification of the assembly during plant maintenance activities. <br /><br /> Only the Unit 1 refuel grapple configuration was involved. Unit 2 was determined to be properly configured with respect to loss of power. Corrective actions include correcting the configuration, testing of other refuel grapples on both units for correct fail-safe loss of power configuration, revising procedures to incorporate loss of power testing of the refuel grapple upon loss of load, inspection of the dropped bundle, the core position internals and related areas, and conducting design feature reviews of the Unit 1 and Unit 2 refuel bridges. The safety significance of the event was relative to the potential free fall of a fuel bundle on a loss of power concurrent with a loss of load. A resulting bundle fall would be restricted to the length of the fuel bundle; therefore, any resulting event would remain bounded by the current FSAR analysis for a Refuel Accident.
3251991002 | Brunswick 1 | 01/18/1991 | 02/19/1991 | 9102260210 | <strong>Safety Relief Valves Tested At Wyle Laboratories Exceed Technical Specification Limit Due To Pilot Disc-To-Seat Bonding.</strong><br /><i>Abstract:&nbsp;</i>Technical Specification limiting conditions for operation require that the safety valve function of all reactor coolant system safety/relief valves be operable with lift settings within 1% of their setpoints to prevent the system from being pressurized above the safety limit of 1325 psig. Eleven Target Rock Corporation model number 7567F two-stage safety relief valves are installed to perform this function. <br /><br /> As a result of Set Pressure Testing during the current Unit 1 Refueling Outage, it was determined that 7 of the 11 Safety Relief Valves (SRVS) lifted at greater than 1% of their setpoint. This setpoint drift (which is a generic concern with Target Rock two-stage SRVs at BWRs) is attributed to bonding of the pilot disc-to-seat surfaces. Corrective action included installing a different set of eleven certified pilot assemblies in Unit 1. The BWROG SRV Setpoint Drift Fix subcommittee is now pursuing activities to reduce oxygen concentrations in the pilot assemblies and CP&L is actively participating in these activities. <br /><br /> Although the setpoint limit was exceeded, the test results were bounded by previously analyzed test results (see LER 2-86-001). This analysis determined that the setpoint drift of the SRVs did not create a potential for exceeding the ASME code reactor pressure vessel limit of 1375 psig. Previous occurrences are reported in LERs 2-84-7, 1-85-033, 2-86-001, 1-87-011, 2-88-005, 1-88-030 and 2-89-18.
3251991003 | Brunswick 1, Brunswick 2 | 01/31/1991 | 02/05/1992 | 9202110308 | <strong>Fail As-Is Position Of CBEAF System Inlet And Outlet Dampers Not Evaluated With Respect To A Chlorine Event.</strong><br /><i>Abstract:&nbsp;</i>A condition that was discovered to be outside the design basis was reported on January 31, 1991 at 4:02 p.m. This condition involves the inlet and outlet dampers for the Control Building Emergency Air Filtration (CBEAF) trains which fail as-is on loss of power. When the CBEAF system is operating in the recirculating mode, a single electrical failure will cause the dampers to remain open. This will result in an airflow path to the Control Room environment that has not been previously evaluated for its effect on control room habitability relative to chlorine protection. <br /><br /> This condition resulted from a failure to evaluate the fail as-is position (in combination with a single failure) of the CBEAF dampers with respect to a chlorine event. On January 31, 1991, at approximately 6:11 p.m., the chlorine tank car was removed from the site pending an engineering evaluation of CBEAF single failures. The evaluation determined the chlorine tank car could be returned to the site provided the most limiting condition of operation (LCO) is entered when the CBEAF is in operation. A tracking LCO was established to ensure implementation of the LCO requirements and the chlorine tank car was returned to the site on February 10, 1991. A project (PCN G0187A) has been initiated to make the Inlet and Outlet dampers automatically close on loss of power. Additionally, the Nuclear Engineering Department (NED) has performed a validation of the chlorine isolation system functional design basis as well as reviewed the failure positions of safety related dampers against the design basis failure position. The safety significance of this condition is considered minimal. Previous occurrences are reported in LERs 2-82-24, 2-82-84, 2-82-099, 1-84-033, 1-86-033, 1-88-034 and 1-90-007.
3251991004 | Brunswick 1, Brunswick 2 | 02/18/1991 | 03/19/1991 | 9103270162 | <strong>Invalid First Interval Hydrostatic Test Boundary on Reactor Pressure Vessel Hydro.</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1991, it was determined that the surveillances required by Technical Specification 3.4.8 (Reactor coolant system structural integrity) had not been performed on all required components during the first 10 year interval hydrostatic pressure test performed on 6/1/83 (Unit 1) and 9/6/84 (Unit 2). The inboard manual isolation valves on small diameter test, drain and vent lines were closed; and therefore, the outboard valves were not subjected to hydrostatic test pressures, per ASME Section XI code requirements. The event safety significance is considered minimal as the inboard and outboard isolation valves are manual valves that are both shut during power operations. The valves are independently verified closed prior to start-up of the unit and remain so during normal power operation. Even if simultaneous passive failure of the first isolation valves, along with sections of the affected lines, is assumed, the consequences are bounded by the existing updated FSAR chapter 15 LOCA analysis, and the reactor can be shutdown in a safe and orderly manner. With the safety assessment presented to the NRC (NLS 91-052), Unit 1 was allowed to start-up, and Unit 2 remained at power, During the next refueling outage, the components identified as not having been hydrostatically tested will be tested.
3251991005 | Brunswick 1 | 02/27/1991 | 03/28/1991 | 9104020234 | <strong>Nonconservative Setpoint For High Steam Flow Isolation Instrument Results In Manual Isolation Of HPCI</strong><br /><i>Abstract:&nbsp;</i>At 2306 hours EST on February 27, 1991, the High Pressure Coolant Injection (HPCI) Steam Supply Inboard Isolation Valve (1-E41-F002) and the Suppression Pool Suction Valve (1-E41-F042) were manually closed. This action was required since the minimum number of operable channels was not satisfied for HPCI high steam flow trip system B. The HPCI system was declared inoperable at the time of isolation pursuant to the HPCI Technical Specification limiting Condition for Operation (LCO). <br /><br /> The HPCI system was manually isolated when the existing setpoint for Steam Line High Flow instrument, 1-E41-PDTS-N005-2, was determined to have been established in the nonconservative direction (equivalent to approximately 330% steam flow). Technical Specifications require that the HPCI steam line isolate at <br /><br /> The nonconservative setpoint was caused from less than adequate allowance in an interim setpoint (implemented by Plant Modification 89-055) to account for error induced by the formation of "loop seals". The subject differential pressure transmitter sensing line had been improperly routed causing the formation of loop seals. The routing problem was corrected during the recently completed refueling outage and a new isolation setpoint was calculated. 1-E41-PDTS-N005-2 was satisfactorily recalibrated by 0856 hours EST on February 28, 1991. HPCI was subsequently placed in standby at approximately 1136 hours EST on the same date. The safety significance of this event is considered minimal. A previous occurrence is reported in LER 1-88-014.
3251991006 | Brunswick 1 | 03/04/1991 | 04/03/1991 | 9104080238 | <strong>High Pressure Coolant Injection and Reactor Core Isolation Cooling low steam line isolation pressure switches (ASCO Tri- point pressure switches) exceeded the Technical Specification limit, when greater than expected setpoint shifts were experienced.</strong><br /><i>Abstract:&nbsp;</i>Unit 1 ASCO Tri-point pressure switches associated with the HPCI and RCIC low pressure PCIS group 4 or 5 isolations experienced a larger than expected shift in setpoints. This resulted in 4 of 4 RCIC low pressure switches (1-E51-PS-N019A-D) and 3 of 4 HPCI low pressure switches (1-E41-PS-N001A,B and D) exceeding the Technical Specification allowable values (>/= 50 psig for RCIC and >/= 100 psig for HPCI). Initially this event was determined to be not reportable, but further technical analysis of the event concluded at 1245 on March 4, 1991, that it was reportable. It was identified that the procedures used to calibrate these ASCO Tri-point pressure switches do not provide adequate directions for calibrating the instruments, when the unit is in a cold depressurized condition, therefore they may not remain within the Technical Specification Limit when the units are returned to a hot pressurized condition. This shift in setpoint for ASCO Tri-point pressure switches, between depressurized and pressurized conditions, had been previously identified in EER 88-0310, 88-0347, 88-0367, and 88-0406, but it is now felt that the shift was under estimated for situations where the instruments remained depressurized for long periods (i.e. a refueling outage). This was caused by a lack of available data for long term depressurized conditions, where the instruments were re-adjusted. The safety significance is considered minimal because the switches would function to isolate the lines at a slightly lower pressure.
3251991007 | Brunswick 1 | 03/05/1991 | 04/04/1991 | 9104090308 | <strong>Overcurrent Relay Setting Was Not Returned To Proper Configuration Following Calibration Resulting In Generator Trip/Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1991, the Unit 1 Reactor was at 100% power and 1005 psig. The Emergency Core Cooling Systems (ECCS) were operable, in standby readiness. The Control Operator (CO) had reduced generator voltage to bring MegaVars to +100. At 0937 hours EST, Unit 1 scrammed. The SCRAM was caused by a turbine generator trip resulting from tripping of the 51V-B main generator overcurrent relay from a sensed overcurrent condition. The variation in the amperage seen as a result of the CO lowering the bus voltage triggered the relay to sense and overcurrent condition; however, no actual overcurrent condition existed during this event.<br /><br /> Immediately following the SCRAM, one of the main generator overcurrent relays (51V-B) was observed to have different settings than the two adjacent relays. This relay had been removed from the plant and taken to the Transmission Substation Maintenance (TSM) shop for calibration during the recently completed refueling outage. It was determined this event resulted from personnel error, the failure of the individual(s) performing the calibration and installation of the relay to return the relay settings to the correct operating configuration following calibration. A Human Performance Enhancement System (HPES) evaluation is being performed. The 51V-B relay settings were corrected and the relay returned to service. Relays worked by the involved TSM crew were visually inspected for proper settings on both units 1 and 2. The safety significance of this event is minimal. During the transient, no unusual safety system performance was noted. No ECCS system initiations were seen nor expected. Other SCRAMS in the past two years that have been attributed to personnel error are reported in LERs 2-89-009, 2-90-009, and 2-91-001.
3251991008 | Brunswick 1 | 03/06/1991 | 04/05/1991 | 9104100029 | <strong>Mis-Interpretation Of Technical Specification Surveillance Requirements Led To Not Maintaining The Drywell Air Lock Interlock Surveillance Current As Required In Operating Guideline (OG-03).</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1991, the Unit 1 Primary Containment (Drywell) was accessed with the Reactor Pressure Vessel at nearly equal to 300 psig. The day shift continued to allow Drywell access, but the Unit 1 Senior Reactor Operator (SRO) incorrectly interpreted that multiple Drywell entries did not require performing the air lock door interlock surveillance for each entrance and exit, as required in Primary Containment Operating Guideline (OG-03). When the Operations Shift Foreman became aware of the interpretation he had the surveillance performed as required by OG-03. This event is considered to be an isolated case of personnel error. While the Drywell air lock interlock Technical Specification Surveillance was not maintained current, the safety significance was minimal as the interlock was found to be operable when surveillance testing was performed, and Primary Containment was maintained at all times.
3251991009 | Brunswick 1, Brunswick 2 | 03/28/1991 | 04/29/1991 | 9105060110 | <strong>Dual Unit Reactor Shutdown And Resulting Low Reactor Vessel Water Level Isolation Of The Unit 1 Primary Containment Isolation System Groups 2, 6, & 8 And Automatic Reactor Scram Signal, During The Manual Scram.</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1991, at 0530 #1 Emergency Diesel Generator (DG) was removed from service for repairs. By March 28, 1991, at 1823 preparations for a dual Unit Reactor shutdown were initiated because #1 DG's camshaft was damaged during the repairs to its camshaft bearings. The camshaft of #1 DG require repairs projected to take longer than the seven days allowed by the Technical Specification (ending March 29, 1991, at 0530). <br /><br /> It was planned to shutdown Unit 1 Reactor by manual Scram from 19% Reactor power due to the inoperable neutron monitoring, Intermediate Range Monitors (IRM) "A" & "C" which upon entering the Start-up Mode would have required a half Scram signal in the "A" Reactor Protection System (RPS). During the manual Scram the Reactor Vessel level momentarily shrank to below the Low Level 1 setpoint for Primary Containment Isolation System (PCIS) groups 2, 6, & 8 isolations and the automatic Reactor Scram setpoint.<br /><br /> The Unit 2 Reactor was also shutdown by manual Scram, when during the shutdown IRM "B" & "D" failed requiring a half Scram signal in the "B" Reactor Protection System (RPS).
3251991010 | Brunswick 1 | 04/15/1991 | 05/15/1991 | 9105280081 | <strong>ESF Actuation; Primary Containment Isolation System Group 1 Isolation of the Main Steam Line Isolation Valves When the Turbine Speed Control Logic Spuriously Selected the 1800 RPM Mode When Normally Closed Relay Contacts Failed to Remain Closed After the</strong><br /><i>Abstract:&nbsp;</i>The Unit 1 reactor was in cold shutdown. At 225853 on April 15, 1991, the main turbine was reset in accordance with the applicable steps of the Turbine System Operating Procedure. At 230055 the Main Steam Isolation Valves (MSIVs) closed when a Group 1, Primary Containment Isolation System (PCIS) isolation signal occurred (ie; low condenser vacuum coincident with the main turbine stop valves not fully closed). At that time it was noted that the electro-hydraulic control (EHC) logic had selected the 1800 rpm turbine speed mode. Instrumentation and Control personnel attached a brush recorder to the EHC circuitry. This monitoring revealed that the spurious selection of the 1800 rpm mode was caused by the normally closed contacts of a relay failing to maintain closure after the relay coil was de-energized. The relay card in the EHC circuitry was replaced. A work request has been initiated to investigate the corresponding Unit 2 relay during the next refueling outage. The MSIVs operated as designed and closed in response to the PCIS Group 1 isolation signal. The purpose of the PCIS signal which occurred during this event is to prevent a possible uncontrolled release of radioactive steam to the turbine building. The reactor was in cold shutdown, at atmospheric pressure, and being maintained at 144 degrees fahrenheit, therefore, no radioactive steam was present. This event had no nuclear safety significance.
3251991011 | Brunswick 1 | 04/24/1991 | 05/24/1991 | 9106030274 | <strong>Component Failure Of An RPS Electrical Protection Assembly (EPA) Breaker Logic Card Results In Unplanned ESF Actuations.</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1991, at approximately 1753 hours (EST), Unit 1 was in cold shutdown. Backup power was being supplied through the alternate power source to Reactor Protection System (RPS) electrical bus B. At that time, Engineered Safety Feature (ESF) actuations were incurred as designed when an unexpected trip on an electrical protection assembly (EPA) output breaker in the alternate power source caused a loss of power to RPS bus B. At approximately 2345 hours (EST) on April 24, 1991, after transferring RPS bus B back to its normal power source, all systems and isolations were restored to normal. Shutdown cooling was maintained throughout this event. <br /><br /> The cause of the event was determined to be component failure of the EPA printed circuit board (PCB) logic card. Corrective action included replacement of the PCB logic card. The safety significance of this event was minimal. Previous similar occurrences, involving failure of EPA logic cards, have been reported in LERs 1-87-009, 2-89-021 and 1-90-014.
3251991012 | Brunswick 1 | 05/03/1991 | 06/03/1991 | 9106100495 | <strong>Unexpected Engineered Safety Features Actuation While Hanging Clearance</strong><br /><i>Abstract:&nbsp;</i>On 5/3/91 with the Unit 1 reactor in cold shutdown, an extensive effort was in progress to identify and repair grounds on the 250/125 VDC Battery Buses. While hanging an electrical clearance in support of DC ground isolation activities, an unexpected closure of the Unit 1 outboard primary containment (drywell) floor and equipment drain isolation valves occurred. Subsequent reference drawing research identified the proper circuit response had been initiated. There was no nuclear safety significance.<br /><br /> The cause of the event was the personnel involved with the clearance research effort failed to perform a thorough review of plant drawings to determine clearance effects on plant equipment as required by Equipment Clearance Procedure AI-58. The problems associated with the clearance research effort resulted from the firm belief that the clearance was correct after researching the current reference drawings and the plant modification functional summary. <br /><br /> The affected valves were returned to the normal line-up position. Significant corrective actions to preclude recurrence include review of the event with appropriate clearance center personnel and enhancement to plant reference drawing revision priority. Similar events resulting from inadequate clearance research have been reported in LERs 1-85-030, 1-85-036, 1-88-029, 1-88-034, 1-89-004, 1-89-015, 2-89-016, 1-90-001 and 1-90-027.
3251991013 | Brunswick 1 | 05/07/1991 | 06/06/1991 | 9106100501 | <strong>Coincident HPCI/RCIC Inoperability Due To RCIC Instrumentation Sensing Line Leakage</strong><br /><i>Abstract:&nbsp;</i>On 5/7/91 with the Unit 1 reactor at 100% power, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 was entered when both the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems were inoperable. The coincidence of inoperable systems occurred as a result of in progress testing of the HPCI system and the inoperability of the RCIC High Steam Flow instrumentation. The capability of terminating HPCI testing in support of timely system restoration in conjunction with the ability to utilize operable reactor vessel depressurization and low pressure injection systems significantly reduced the impact to nuclear safety. <br /><br /> The cause of this event was due to the loss of the RCIC High Steam Flow transmitter 1-E51-PDT-N017 sensing line level. This condition was caused by a loose 1-E51-PS-N019A isolation valve fitting. The void created from the loss of level increased the volume of turbulent steam and gases within the 1-E51-PDT-N017 sensing line affected by the leak. The additional turbulence increased the transmitter's electronic noise signal to a level which caused the associated master trip unit indicator to fluctuate and the cycling of the master and slave trip unit trip indicating lights. The subject transmitter and analog trip units responded properly to the abnormal condition imposed by the loss of sensing line level. Consequently the cause of this event is not attributed to component failure. A review of past Maintenance work history and recent applicable plant modifications did not identify contributing factors for the loose condition of the valve fitting.<br /><br /> The loose sensing line fitting was tightened and the affected sensing line filled and vented. No further corrective action is being taken at this time. This is considered an isolated occurrence based on a review which did not reveal any similar events.
3251991014 | Brunswick 1 | 06/10/1991 | 07/10/1991 | 9107180055 | <strong>HPCI Inboard Steam Supply Isolation Valve Closure When Electrical Continuity To A Steam Leak Detection Module Was Interrupted.</strong><br /><i>Abstract:&nbsp;</i>The Emergency Core Cooling Systems were operable, and the monthly HPCI Steam Leak Detection (SLD) Channel Functional Test was in progress. The test realigns the system logic, removes it from the "test" status, and then verifies that associated annunciators have reset. In this case, an annunciator remained sealed in. A trip indication was not sealed in on the module and the associated relay was in its proper configuration. A terminal point associated with the last module tested has three wire connections and a good connection is sometimes difficult to achieve. Based on this knowledge, the technician re-checked this module connection; inadvertently breaking the electrical continuity at the SLD module input. This resulted in closure of the HPCI steam supply inboard isolation valve on a PCIS "B" channel isolation signal, as designed, at 1039. The HPCI system was returned to standby line up at 1048. The involved technician considered himself to be "evaluating" an unexpected condition. His evaluation focused on re-verification to determine if the steps he had performed in the MST had in some way resulted in the condition. The technician's actions should have been limited to a passive verification of the wiring. Further actions should have proceeded after contacting supervision. The technician was counselled and appropriate action was taken. The exact cause of the annunciation is indeterminate. Training on this event will be provided to appropriate maintenance personnel. As a result of past problems with the SLD system modules, they are scheduled to be replaced. This event would not have been more severe under reasonable and credible alternative conditions. Past events involving this instrumentation have been reported.
3251991015 | Brunswick 1 | 06/12/1991 | 07/12/1991 | 9107170206 | <strong>Two Inoperable Control Rod Accumulators Result In Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1991 at approximately 0451 hours (EDT), Unit 1 was operating at 100% power with one Control Rod Drive Hydraulic Control Unit inoperable due to maintenance, when the Control Room received a low nitrogen pressure alarm on another Hydraulic Control Unit making it inoperable. With two or more Control Rod Scram Accumulators inoperable, Technical Specifications 3.0.3 was invoked, placing the plant in a six hour to hot shutdown condition. An Auxiliary Operator was dispatched to recharge the accumulator with the low pressure. There was no intent to commence a unit shutdown unless problems were encountered during the recharging evolution. On June 12, 1991 at approximately 0531, the accumulator was successfully recharged and Technical Specification 3.0.3 was exited.<br /><br /> The cause of this event is attributed to the simultaneous inoperability of two hydraulic Control Units (HCU). Corrective actions included recharging the HCU Accumulator with the low nitrogen pressure, completing repairs on the HCU with the nitrogen leak. <br /><br /> The safety significance of this event is minimal. With the reactor vessel at full operating pressure and the scram discharge volume at atmospheric pressure, the accumulator is not needed to meet scram time requirements. Standby Liquid Control system was available as a backup to the Control Rod Drive Hydraulic Control Unit accumulators. <br /><br /> A review of records revealed no similar events.
3251991016 | Brunswick 1 | 06/19/1991 | 11/15/1991 | 9111210109 | <strong>Failure of both RCIC steam line isolation valves to seat</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1991, with Unit 1 at 100% power, the Reactor Core Isolation Cooling (RCIC) steam line was isolated to perform surveillance tests. During system restoration, after completion of the surveillance testing, it was discovered that with both the Primary Containment Isolation System (PCIS) valves (1-E51-F007/F008) closed, the downstream 3" diameter steam line was still pressurized to 1000 psig. This indicated that both the 1-E51-F007 and F008 valves were leaking by their seats, and a PCIS LCO 12-hour action statement was entered.<br /><br /> While quantifying the valve leakage, an isolation valve seated when a differential pressure (DP) was created across the closed isolation valves by opening the RCIC turbine steam supply valve (1-E51-F045). The 1-E51-F045 was then closed and the 1-E51-F008 opened to apply a DP across the 1-E51-F007. Additional stroking of the 1-E51-F007 and F008 with no initial differential pressure showed that each valve did in fact isolate the RCIC steam line. The valves seated as indicated by RCIC steam line pressure response and later by the decrease in steam line temperature. Evaluation determined that the RCIC steam line was now isolated and the 12-hour action statement was exited. An on-line Local Leak Rate Test (LLRT) was performed that established the leakage rates across the 1-E51-F007/F008 as within normal acceptable leakage criteria and RCIC was restored to service at 0215 on June 22, 1991. <br /><br /> A SUPPLEMENTAL INFORMATION section has been added to reflect the October 23, 1991 Technical Support investigation results, that supported the original cause of event.
3251991017 | Brunswick 1 | 07/06/1991 | 08/05/1991 | 9108090162 | <strong>RWCU Isolation on Failure of Nonregenerative Heat Exchanger Temperature Switch</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1991, with Unit 1 at 100% power, the Reactor Water Cleanup System (RWCU) Inlet Outboard Isolation Valve (1-G31-F004) auto closed when the Non Regenerative Heat Exchanger Outlet temperature was sensed to be 135 degrees F. The Control Operator shut the RWCU Inlet Inboard Isolation Valve (1-G31-F001), which does not receive an auto closure from this signal, to ensure the line was isolated. An Auxiliary Operator found the indicator for temperature switch/transmitter 1-G31-TS-N008 pegged upscale. <br /><br /> While this temperature switch/transmitter (1-G31-TS-N008) does not provide a Technical Specification Primary Containment Isolation System (PCIS) signal it does actuate one of the RWCU PCIS Group 3 isolation valves (1-G31-F004). <br /><br /> Investigation by Instrumentation and Control technicians determined that the temperature switch/transmitter had failed due to an internal fault. With 1-G31-TS-N008 replaced and calibrations completed, at 0450 on July 7, 1991 Operations unisolated RWCU to return it to service.
3251991018 | Brunswick 1 | 07/18/1991 | 08/16/1991 | 9108220114 | <strong>Reactor Scram Resulting From Common Instrument Header Pressure Perturbation</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1991, Unit 1 reactor was at 100% power when it scrammed as the result of a Main Steam Line Isolation signal, inadvertently generated during surveillance 1MST-RSDP-21Q for reactor water level transmitter B21-LT-N026B, which was being returned to service. After extensive investigation it is suspected that an instrument isolation valve leaked-by, resulting in a pressure transient on the common instrument header which has instruments feeding both reactor protection divisions. The resulting erroneous level signals caused the following system actuations: Isolations - Group 1 (Main Steamlines), Group 3B (1/2 Reactor Water Cleanup System), and Initiations - Reactor Core Isolation Cooling (RCIC), High Pressure Coolant Injection (HPCI), Standby Gas Treatment (SBGT), Core Spray (CS), Emergency Diesel Generators (EDG). <br /><br /> The Emergency Core Cooling Systems (ECCS) were operable. <br /><br /> The safety significance of this event is minimal as plant safety systems responded as required.
3251991019 | Brunswick 1, Brunswick 2 | 07/23/1991 | 08/22/1991 | 9108300089 | <strong>Word Processing Technique Used During Procedure Revisions Inadvertently Established Incorrect Setpoint Head Correction Values Resulting In A HPCI Low Steam Supply Pressure Switch Being Left Below The Technical Specification Allowable Limit.</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1991, at approximately 1410 hours (EDT), Unit 1 was in cold shutdown. The Unit 2 reactor was operating at 100% power. At this time, it was determined that the Maintenance Surveillance Test (MST) procedures utilized to calibrate the Units 1 and 2 High Pressure Coolant Injection (HPCI) low steam supply pressure switches (four per unit) had been revised incorrectly for approximately two months. Word processing techniques used when the procedures were revised had inadvertently established incorrect setpoint head correction values resulting in one of the Unit 1 pressure switches being left below the Technical Specification limit of >/= 100 psig by 0.5 psig on June 11, 1991, and by 0.1 psig on July 12, 1991. The Unit 2 procedure did not have error margins sufficient to allow settings below the Technical Specification limit. The affected Unit 1 instrument channel was declared inoperable at 1410 hours on July 23, 1991. The MST procedures were revised to correct the head correction values, and on July 24, 1991, at approximately 0613 hours, the Unit 1 pressure switches were recalibrated utilizing the corrected procedure. At this time, the affected pressure switch was found to be within the Technical Specification allowable limit. The procedure revision errors were identified during a system engineer review of recent HPCI steam line low pressure instrument calibration data. The cause of these procedural errors was that there was no formal process for ensuring the procedure technical reviewers knew which portions of a procedure had been electronically altered via word processing (cloning or copying sections for ease of typing the changes). Formal controls are expected to be established by September 30, 1991. Additional corrective actions include reviewing other Maintenance Surveillance Test procedures, by October 31, 1991, for possible cloning errors. The safety significance of this event is considered to be moderate.
3251991020 | Brunswick 1 | 07/25/1991 | 08/23/1991 | 9108280253 | <strong>HPCI System Low Pressure Isolation During Reactor Startup</strong><br /><i>Abstract:&nbsp;</i>During the Unit 1 Reactor startup on July 25, 1991, High Pressure Coolant Injection (HPCI) isolated on low reactor pressure as it was being placed in its standby lineup. <br /><br /> Reactor pressure was being held at 112 psig to allow Instrumentation and Control technicians to reset the HPCI low steamline pressure isolation switches. Special procedure 91-036, was required due to the isolation pressure switches narrow operating band not allowing reset prior to exceeding the 113 psig Technical Specification value that requires HPCI operability. When the HPCI isolation valves were opened to pressurize the HPCI steamlines, reactor pressure dropped sufficiently to pickup the 2 low pressure isolation switches that make-up the trip logic designed to close the HPCI Steam Supply Inboard Isolation Valve 1-E41-F002, and the HPCI Suppression Pool Suction Valve 1-E41-F042 which was already closed. While the reactor pressure was high enough to allow placing HPCI in its standby lineup, reactor power at 1% was too low to maintain the stable steam pressure required by the narrow operating band of the HPCI low steamline pressure isolation switches without dropping reactor pressure below the isolation setpoint.<br /><br /> The safety significance of this isolated event is minimal since the HPCI system was not required to be operable and the Primary Containment Isolation System functioned as designed.
3251991021 | Brunswick 1 | 07/28/1991 | 08/27/1991 | 9109040281 | <strong>Operation Outside Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. ON JULY 27, 1991, UNIT 1 HAD COMPLETED A POWER INCREASE TO FULL POWER. ON JULY 28, 1991 AT APPROXIMATELY 0600 HOURS (EDT), DURING ROUTINE SURVEILLANCE, THE SHIFT SUPERVISOR OBSERVED THAT THE GROSS MEGAWATT RECORDER WAS INDICATING HIGHER THAN EXPECTED (SLIGHTLY ABOVE 790 MWE) FOR 100% POWER OPERATION. THE SHIFT TECHNICAL ADVISOR PERFORMED A HAND HEAT BALANCE CALCULATION TO CHECK THE ACTUAL MEGAWATT THERMAL (MWT) OUTPUT WHICH REVEALED THAT ACTUAL POWER WAS 100.59% AND MEGAWATTS THERMAL (MWT) WERE 2450. (THE PLANT IS LICENSED FOR 2436 MWT.) REACTOR POWER WAS REDUCED TO APPROXIMATELY 2400 MWT. INVESTIGATIONS REVEALED THAT A FEEDWATER (FW) INLET TEMPERATURE POINT WAS INPUTTING A HIGH VALUE INTO THE PROCESS COMPUTER HEAT BALANCE CALCULATION INDICATING AN ERRONEOUS POWER CALCULATION (99.92% WITH ACTUAL POWER AT 100.59%) AN AVERAGE VALUE OF THE THREE OTHER FW INLET TEMPERATURE POINTS WAS SUBSTITUTED FOR HIGH POINT WHICH RESULTED IN AN ACCURATE POWER CALCULATION BY THE PROCESS COMPUTER. THE CAUSE OF THE EVENT WAS DUE TO A FAILED TEMPERATURE ELEMENT IN THE FIELD WHICH WILL BE REPLACED DURING A UNIT OUTAGE WHEN PARTS ARE AVAILABLE. PREVIOUS EVENTS INCLUDE NCR S-89-076 SAFETY SIGNIFICANCE WAS MINIMAL DUE TO THE FACT THAT THE UNIT DID NOT EXCEED 102% POWER.
3251991022 | Brunswick 1, Brunswick 2 | 08/07/1991 | 09/06/1991 | 9109110181 | <strong>Control Building Emergency Air Filtration Damper Malfunction</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1991 during periodic testing of the Control Building Emergency Air Filtration system, it was found that the normal air supply damper failed to close. Investigations revealed that the cause of the damper binding was due to mis-orientation of a portion of the actuator for vertical motion. A work order was initiated to have Maintenance rotate a portion of the actuator and align it to the operator linkage. The system was returned to service approximately 1600 hours on August 8, 1991. <br /><br /> Subsequent investigations revealed that the damper had been disconnected during plant modification work during June of 1990 by a maintenance work order. A second work order was initiated to have the damper restored to its design configuration by the system engineer's direction. During the evolution, the system engineer observed the damper operation from underside. The root cause of the improper installation of the damper is due to the system engineer relying on individuals skill of the craft to install and verify the installation rather than providing written steps and diagrams. <br /><br /> Corrective actions included inspection of other dampers on the same elevation for proper orientation. Outage Management and Modifications, Technical Support, Maintenance and Nuclear Engineering will provide training on this event. Per a memorandum from the Maintenance manager on March 30, 1991, work orders are now required to contain explicit step-by-step instructions for work on Q-list equipment. The safety significance of this event is minimal due to the fact that the damper tested satisfactorily since the modification work in June, 1990. Previous similar events include 1-90-007. Associated events include 1-91-003 and 1-88-034.
3251991023 | Brunswick 1 | 08/22/1991 | 09/23/1991 | 9109300145 | <strong>Preparations For Flushing The Reactor Water Cleanup System Inboard Isolation Valve Seat Resulted In A RWCU Isolation On High Temperature</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1991, at 1147, Unit 1 was at 100% power when the Reactor water Cleanup (RWCU) Inlet Outboard Isolation Valve G31-F004 received a RWCU nonregenerative heat exchanger discharge high temperature isolation signal. The G31-F004 valve was already closed at the time, therefore no valve movement was actually experienced, While this was not a primary containment isolation signal (Engineered Safety Feature actuation), it protects the resin in the filter/demineralizer units from over temperature conditions. The isolation occurred while the RWCU system was being aligned prior to the use of a special procedure that would flush the valve seat of the RWCU Inboard Isolation Valve G31-F001. The RWCU system was being aligned per RWCU Operating Procedure OP-14. The high temperature condition resulted when leakage by the RWCU Reject to the Main Condenser Valve G31-F034 drained the system down stream of the filter/demineralizer bypass valve, G31-F044. When the G31-F044 was opened, per procedure, the hot water upstream of the valve flowed faster than the ability of the nonregenerative heat exchanger to cool the water, The high temperatures sensed at the nonregenerative heat exchanger resulted in the RWCU isolation signal.<br /><br /> This event had no adverse impact on nuclear safety. Previous similar events have been reported in LERs 1-89-013, and 2-91-008.
3251991024 | Brunswick 1 | 09/14/1991 | 10/14/1991 | 9110240101 | <strong>Outside Technical Specifications - LPCI "B" Loop Inoperable Due To Seismic Considerations</strong><br /><i>Abstract:&nbsp;</i>The Unit 1 reactor was operating at 100% power and the Emergency Core Cooling Systems (ECCS) were operable in standby readiness on September 14, 1991. As-Built verification of supplementary steel was in progress. At 1315 (EDT) Engineering personnel informed Operations that the 1-E11-F015B (RHR/LPCI Inboard Injection valve) was inoperable because of seismic considerations resulting from support deficiencies. The involved supports affected conduit containing the power supply cable to the valve. Operations initiated a Limiting Condition for Operation (LCO) at that time. At 2335 (EDT) the repairs were completed and the LCO was canceled. The cause of the support deficiencies and the length of time this condition existed is indeterminate. The deficiencies have been corrected. This event was identified in accordance with plant work request procedures. Personnel performing the as-built verification of supplementary steel are cognizant of structural requirements and will continue to identify deficiencies. No further corrective actions are required. Previous similar events involving seismic qualification of equipment include LERs 1-88-06, 1-88-16, 1-88-35, 2-89-02.
3251991025 | Brunswick 1 | 10/03/1991 | 11/04/1991 | 9111080299 | <strong>High Pressure Coolant Injection Diaphragm Control Valve Diaphragm Failed Causing Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1991, at approximately 0230, Unit 1 was operating at 100% power. The Core Spray (CS) system, Low Pressure Coolant Injection (LPCI) system, Automatic Depressurization system (ADS) and Diesel Generators 1, 2 and 4 were operable and in standby. Diesel Generator 3 was inoperable for scheduled maintenance. The High Pressure Coolant Injection (HPCI) system was inoperable for scheduled maintenance surveillance testing. Prior to this time, on August 23, 1991, during weekly testing of the HPCI system, an Auxiliary Operator found that the diaphragm control valve for the low oil pressure trip leaked during stroking. On August 23, 1991, the Technical Support HPCI system engineer evaluated the leak. Due to the factors considered in the HPCI system engineer's evaluation, it was determined that the oil leak did not prevent HPCI from performing as required and was not an operability concern at that time. A work order was initiated to replace the failed diaphragm, but replacement parts could not be located in the materials warehouse on site. On October 2, 1991, at 1110, a 14 day Limiting Condition for Operation was initiated to remove the HPCI system from service for scheduled maintenance surveillance testing. On October 3, 1991, at approximately 0230, Operations personnel began periodic operability testing of the HPCI system. While the HPCI turbine was being started, an Auxiliary Operator (AO) in the field noted an oil leak. He notified the Control Room personnel and the HPCI turbine was secured. It was determined that this was the same leak identified on August 23, 1991. Further investigations located the parts on site and Maintenance personnel replaced the failed diaphragm. At 1818 on October 3, 1991, replacement of the diaphragm was completed. The HPCI system was placed back in standby on October 4, 1991, at 1020 hours after the scheduled testing was completed. During this event, CS, LPCI and ADS systems were available as backup systems for HPCI. If needed, they would have mitigated the consequences of an accident, thereby reducing the safety significance of this event.
3251991026 | Brunswick 1 | 10/15/1991 | 01/13/1992 | 9201210277 | <strong>Unit 1 Reactor Shutdown Required When Emergency Diesel Generator Maintenance Was Determined To Require More Time Than The Technical Specification Limiting Condition Of Operation Would Allow With A Unit At Power</strong><br /><i>Abstract:&nbsp;</i>At 0700 on October 1, 1991, #3 Emergency Diesel Generator (EDG) was declared inoperable to allow for scheduled maintenance as part of the Unit 2 refueling outage. By 0600 on 10/15/91, it was apparent that the #3 EDG would not be returned to service in time to avoid the Reactor shutdown required by the Limiting Condition for Operation (LCO) action statement of the Electrical Power Systems, A. C. Sources, Technical Specification. The time required to complete the original work scope had increased due to emergent work items, scheduling and coordination issues, and a procedural compliance issue. This made it impossible to return the #3 EDG to service prior to the LCO expiring. On 10/15/91 at 0600, Unit 1 was at 100% reactor power with the Emergency Core Cooling Systems (ECCS) operable. Unit 2 was defueled in a refueling outage. The decision was made to commence a Reactor shutdown beginning at 0630 on 10/15/91. Unit 1 entered Hot Shutdown at 1803 on 10/15/91, and Cold Shutdown at 1740 on 10/16/91. The #3 EDG was declared operable at 1850 on 10/20/91, upon completion of maintenance and testing. Unit 1 Reactor startup was commenced at 0048 on 10/21/91, and the Unit vas synchronized to the system grid at 1724 on 10/21/91.<br /><br /> This event was of minimal safety significance as the Technical Specification LCO actions were successfully complied with by shutting down Unit 1. <br /><br /> A previous similar event is LER 1-91-009. <br /><br /> This supplement adds more detailed information to the body of the original LER.
3251991027 | Brunswick 1 | 11/05/1991 | 11/27/1991 | 9112040071 | <strong>Two Inoperable Control Rod Accumulators Result In Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, Unit 1 was at 100% reactor power. At 0040 on November 5, 1991, as Control Rod Drive (CRD) Hydraulic Control Unit (HCU) 34-19 was being recharged with nitrogen, a second HCU accumulator 46-27 low nitrogen pressure caused a CRD Accumulator low Pressure/ High Level alarm in the Control Room. With two or more Control Rod Drive Scram Accumulators inoperable, Technical Specification 3.0.3 was invoked. This required placing the Unit in a six hour to Hot Shutdown condition. After verifying the second alarm was due to low nitrogen pressure, the Auxiliary Operator continued recharging the first HCU 34-19 with nitrogen. There was no intent to commence a Unit shutdown unless problems were encountered during the recharging evolution. At 0055, on November 5, 1991, the accumulator for HCU 34-19 was successfully recharged and Technical Specification 3.0.3 was exited. <br /><br /> The cause of this event is the simultaneous inoperability of two Control Rod Drive Hydraulic Control Units due to the drop in the Reactor Building ambient temperature. A cold front resulted in areas of the Reactor Building reaching new seasonal lows (as recorded building temperatures dropped approximately 7 degrees F over the previous 3 days). Corrective actions included recharging the HCU accumulators with nitrogen. <br /><br /> The safety significance of this event is minimal. When the reactor vessel is at operating pressure and the scram discharge volume is at atmospheric pressure, the scram accumulator is not needed to meet scram time requirements. The Standby Liquid Control system was available as a backup to the Control Rod Drive system. <br /><br /> A previous similar event was reported in LER 1-91-015.
3251991028 | Brunswick 1 | 11/05/1991 | 12/05/1991 | 9112110325 | <strong>Component Failure Of A Reactor Water Cleanup System Isolation Logic Relay Resulted In An Unplanned Engineered Safety Feature (ESF) Actuation.</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, at approximately 1518 hours (EST), the Unit 1 reactor was at 100% power. The Reactor Water Cleanup (RWCU) system was in service with both filter/demineralizers on-line. The Emergency Core Cooling Systems (ECCS), the Reactor Core Isolation Cooling (RCIC) system, and the Emergency Diesel Generators (EDGs) were operable and in standby readiness. At this time, the Primary Containment Isolation System (PCIS) received a spurious Valve Group 3 isolation signal resulting in the automatic closure of the RWCU system Inlet Inboard Isolation Valve (1-G31-F001). The unit Control Operator (CO) became aware of this unplanned ESF actuation by Control Room annunciation and indication. The spurious isolation signal was generated per design when a normally energized RWCU isolation logic relay (1-A71-K37) coil burned up causing failure in the deenergized position, which then actuated that portion of the RWCU leak detection logic that commands 1-G31-F001 to close. Inspection of the Control Room backpanel areas revealed a faint burning smell; however, there was no visible smoke or fire from the failed General Electric (GE) model No. CR120 relay. The relay failure was determined to be normal end of coil life failure due to aging. The coil for the failed relay was replaced with a new one from stock. Following satisfactory postmaintenance testing, the RWCU system was restored to service at approximately 1032 hours on November 6, 1991. No further corrective actions are planned. The GE CR120 relay was not considered to be a repetitive failure component that warranted a design change or periodic changeout. This event had no adverse impact on nuclear safety. A previous similar event involving a failed GE CR120 relay is reported in LER 1-90-029.
3271991001 | Sequoyah 1, Sequoyah 2 | 01/15/1991 | 02/14/1991 | 9102210154 | <strong>Electrical board room and main control room air handling unit sequence timers not calibrated within the required frequency because of nontechnical specification classification</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1991, at 0800 EST with Units 1 and 2 at 100 percent power, TVA determined that sequence timers for the electrical board room and main control room (MCR) air handling units (AHUs) had not been calibrated within the required frequency. During the 1987 and 1988 timeframe, the electrical board room and the MCR AHU sequence timers were classified as nontechnical specification (non-TS). Preventive maintenance (PM) procedures were written for the electrical board room AHU Sequence Timers 2A and 2B, but the performance of the PM for 2B was delayed while waiting for spare parts to be made available. The timers for the electric board room AHUs were subsequently calibrated and are currently within calibration. Calibration procedures for the MCR AHU sequence timers were not issued as a result of not closing the WP in a timely manner. The root cause of the timers not being calibrated within the TS required frequency was the initial failure to recognize these timers as being within the scope of the D/G sequence timer surveillance requirement. On January 15, 1991, the MCR AHU sequence timers were determined to be in calibration. Corrective actions include revising appropriate surveillance instructions to include the electrical board room ana MCR AHU sequence timers and reviewing unclosed workplans for procedure impact.
3271991002 | Sequoyah 1, Sequoyah 2 | 01/24/1991 | 10/18/1991 | 9110280214 | <strong>Voluntary Report of an Event Involving Lack of Response to an Annunciator Warning of Decreasing Pressure in the Diesel Generator Air Start System</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to document that it is being submitted as a voluntary report. On January 24, 1991, at 0945 Eastern standard time (EST) with Units 1 and 2 in Mode 1, Limiting Conditions for Operation (LCOs) 3.0.5 and 3.8.1.1 were entered. The "A" train emergency gas treatment system (EGTS) was out of service for a filter test when it was discovered that the "B" train diesel generator (D/G) automatic air start system was below the 180 pounds per square inch gauge limit used at the time of the event to determine operability. The air compressor for the D/G starting air system was manually started and the air pressure reestablished. This event resulted from the failure of operational personnel to identify and respond to an annunciator in the main control room, warning of decreasing pressure in the air start system. Troubleshooting revealed the failure of the air compressor to automatically start was caused by a blown fuse (Type NON 10). The blown fuse was replaced and the normal automatic function of the system was restored. As a result of further testing and evaluation, the D/G was determined to have been operable in the as-found condition. Additionally, expectations relative to operator attentiveness to annunciators have been clearly conveyed and the level of awareness of the shift crews has been significantly raised.
3271991003 | Sequoyah 1 | 02/18/1991 | 03/20/1991 | 9103270282 | <strong>Technical specification required shutdown because of the failure of the 1B-B centrifugal charging pump.</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991, at 1858 Eastern standard time (EST) with Unit 1 in Mode 1, the centrifugal charging pump (CCP) was declared inoperable and removed from service. The 1B-B pump had been in continuous operation for several months. The first indication of possible pump degradation was when Operations attempted several iterations to increase letdown flow. When CCP flow decreased and current increased, the pump was declared inoperable. ASME Section XI testing was performed and degradation of the pump was confirmed. Disassembly of the pump showed heavy wear on the impeller shoulders in the wear ring area as well as on the balance drum. The shaft was also found to have a crack that was determined to have existed for several months or even years. The root cause of the pump failure could not be conclusively determined. Potential contributing factors to the failure include long-term gas entrainment and/or the entrainment of gas and/or solid material through the pump associated with a return of the boric acid makeup system to service. The 1B-B CCP was repaired and tested, and subsequently declared operable at 1454 EST on February 23, 1991. Expanded vibration monitoring of the CCPs, in addition to the procedural controls for returning the boric acid makeup system to service, is being implemented to preclude rapid failures of the CCPs.
3271991004 | Sequoyah 1 | 03/06/1991 | 04/05/1991 | 9104080284 | <strong>LCO 3.0.3 entry resulting from multiple rod position indicators indicating greater than 12 steps from the group demand position counters and caused by a voltage regulating circuit board failure.</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1991, at 0422 Eastern standard time (EST), with Unit 1 operating in Mode 1, Limiting Condition for Operation (LCO) 3.0.3 was entered after actuation of multiple P250 plant computer Rod Position Indication (RPI) deviation alarms and the associated control board annunciator. All RPIs had dropped and approximately 25 of the RPIs were indicating low by more than the allowed 12 steps from the rod control system group demand step counters. This deviation was caused by a failure in the Solatron voltage regulator which provides the input power to the RPI instrument racks. Adjustments were made to the Solatron's output voltage, and the RPIs increased to within the acceptable range. LCO 3.0.3 was exited at 0635 EST. Although the RPI system was operable, the Solatron output voltage and associated RPI readings were not as stable as normal. Therefore, on March 7, 1991, at 1805 EST, the RPI system was removed from service and LCO 3.0.3 was again entered in order to replace the voltage regulating circuit board. The board replacement was successfully completed and the RPI stability problem was corrected. At 1855 EST, the RPI System was declared operable and LCO 3.0.3 was exited. Corrective actions include sending the failed board to Sola Electric for failure evaluation and instituting PMs for periodic inspections and replacements.
3271991005 | Sequoyah 1, Sequoyah 2 | 03/05/1991 | 04/04/1991 | 9104090313 | <strong>Diesel Generator room fire protection system inoperable because of an incorrectly terminated wire which was the result of inappropriate personnel actions.</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1991, at approximately 1315 Eastern standard time (EST), with Units 1 and 2 in Mode 1, while performing a regularly scheduled fire protection surveillance instruction, it was discovered that the interface wiring between panel 0-L-619 and the 1B-B diesel generator (D/G) room carbon dioxide (CO sub 2) system had been incorrectly terminated. This was the result of inappropriate personnel actions. At this time, the CO sub 2 and fire protection systems were inoperative (because of the on-going performance of surveillance testing) and compensatory measures were in place. Supervision and engineering were notified at this time. Their review concurred that a wiring discrepancy existed. The shift operations supervisor (SOS) was notified at approximately 1400 EST. The D/G building fire protection and suppression was placed back in-service, except the 1B-B D/G room CO sub 2 system where fire watches remained in-place until the problem was corrected. Work orders were also initiated to inspect the other diesel building and plant fire protection panels for similar situations. The problem on fire protection panel 0-L-619 was corrected and the system was declared operable at 1100 EST on March 6, 1991.
3271991006 | Sequoyah 1 | 04/03/1991 | 05/03/1991 | 9105070014 | <strong>The Reactor Building Annulus fire protection system was not properly verified as required by TS because of a failure to update the associated procedure as a result of a modification.</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1991, at 1430 Eastern daylight time with Unit 1 at 100 percent power, SQN entered Limiting Condition for Operation (LCO) 3.7.11.2 for Unit 1 when it was discovered that seven sprinkler heads in the Unit 1 Reactor Building Annulus had not been inspected, as required by TS. In June 1988, Work Plan (WP) 418-01 added seven sprinkler heads to the existing 45 in the annulus and relocated 10 existing sprinkler heads. The surveillance instruction (SI) that implements the surveillance requirement was not updated to indicate the additional sprinkler heads, and therefore, these sprinkler heads had not been verified since the implementation of the WP in 1988. Immediate corrective action for this event was to enter the LCO 3.7.11.2 and establish continuous fire watches in the Unit 1 annulus. The sprinkler system was walked down, the SI performed, and a pressure test was conducted as a post maintenance test. The SI was revised to reflect the current number of sprinkler heads. The LCO was exited at 2040 on April 4, 1991.
3271991007 | Sequoyah 1, Sequoyah 2 | 04/22/1991 | 05/22/1991 | 9105300349 | <strong>Limiting Conditions for Operation 3.0.3 entered when both trains of control room emergency ventilation were declared inoperable; when the 'A' train AHU failed and the 'B' train AHU was out-of- service for maintenance.</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1991, at 1848 Eastern light time (EDT) with Units 1 and Mode 1 (100 percent power), Limiting Condition for Operation (LCO) 3.0.3 was entered when both trains of control room emergency ventilation were declared inoperable. Train 'A' was declared inoperable when the shaft of the Train 'A' main control room (MCR) air handling unit (AHU) failed from fatigue. The Train 'B' MCR AHU had been previously declared inoperable to support maintenance activities. Train 'B' MCR AHU was returned to service at 2100 EDT on April 22, and LCO 3.0.3 was exited.
3271991008 | Sequoyah 1, Sequoyah 2 | 04/29/1991 | 07/31/1991 | 9108050180 | <strong>Inoperable penetration seals that were not inspected or identified as a result of a deficient procedure</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide an updated schedule for corrective actions. On April 29, 1991, with Units 1 and 2 operating in Mode 1, it was determined that fire barrier penetration seals had not been visually inspected as required by Technical Specification (TS) 4.7.12. Technical inadequacies in Surveillance Instruction (SI) 233.1E, "Mechanical Penetration Fire Barrier Visual Inspection," including inadequate acceptance criteria, were discovered during an investigation of fire barrier discrepancies. The SI inadequacies contributed to not identifying inoperable penetration seals during the Technical Specification 4.7.12 surveillance. The nonfunctional seals were identified during a walkdown in the area on May 31, 1990. A breaching permit was issued and closed within 7 days of identification based on a performance of a portion of SI-233.1E utilizing the deficient acceptance criteria to determine operability. The penetrations were sealed on June 8, 1990. The procedures implementing the TS SR will be revised and additional surveillance performed as deemed appropriate.
3271991009 | Sequoyah 1, Sequoyah 2 | 05/06/1991 | 09/18/1992 | 9209250084 | <strong>Operation with Inoperable Auxiliary Building Fire Suppression System Because of Inadequate Test Performance and Review</strong><br /><i>Abstract:&nbsp;</i>This LER provides details concerning the cause of the auxiliary building sprinkler system's reduced performance and also to report the corrective actions taken to return the system to operable status. On May 6, 1991, at 1600 EDT, with Units 1 and 2 operating in Mode 1, LCO 3.7.11.1 was entered when the fire suppression system for the auxiliary building was declared inoperable. Upon further review, it was determined that the system was not inoperable. This LER has appropriately been changed to a voluntary report. The original surveillance instruction techniques were overly conservative and the acceptance criteria basis was inadequately developed. Special testing and a computer hydraulic modeling were performed to verify the operability requirements of the HPFP system. The cause of the reduction in system performance has been determined to be internal piping corrosion deposits, incrustation, and a buildup of river sediment.
3271991010 | Sequoyah 1, Sequoyah 2 | 05/15/1991 | 09/06/1991 | 9109120209 | <strong>Failure to conduct visual inspection of expansion joint seals previously not considered to be fire barriers and discovery that seal material does not meet fire barrier requirements.</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to update the corrective actions associated with this event. On May 15, 1991, at 1800 Eastern daylight time (EDT), with Units 1 and 2 operating in Mode 1 it was determined that the expansion joint material between the reactor building shield walls and the auxiliary building did not meet Underwriters laboratory (UL) or Factory Mutual standards for a flame spread of less than 25 feet. Limiting Condition for Operation (LCO) 3.7.12 was entered on both units and appropriate fire watches established. The expansion joints between the auxiliary building and shield buildings at Elevations 669.0, 690.0, 706.0, 714.0, 734.0, and 759.0 contain a material for which specific documentation supporting fire resistiveness to an accepted UL or Factory Mutual standard is not available and therefore, the configuration cannot be considered a creditable fire barrier. Investigation determined that these seals have been in place since initial construction, the initial design did not consider these seals to be a fire barrier; and accordingly, they were not included in the surveillance and subsequent Appendix R analysis. A preliminary test of the fire resistance of the expansion joint material provided reasonable assurance that the material is certifiable as a fire barrier and qualification testing is being pursued. Testing of the material and evaluation of the test results are scheduled to be completed by February 7, 1992. This event is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B), Unit 2 License Condition 2.H and TS Limiting Condition for Operation 3.7.12 action a.
3271991011 | Sequoyah 1, Sequoyah 2 | 06/02/1991 | 07/05/1991 | 9107080111 | <strong>Limiting Condition for Operation 3.0.3 was entered when the control room emergency ventilation system was declared inoperable because a pressure boundary door was improperly breached open.</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1991, at 1705 Eastern daylight time (EDT) with Units 1 and 2 operating in Mode 1 at 100 percent power, Limiting Condition for Operation (LCO) 3.0.3 was entered when the control room emergency ventilation systems (CREVS) was determined to be inoperable. The CREVS was determined to be inoperable because a ventilation boundary door was improperly breached. Modifications was implementing a design change involving an asbestos abatement in the relay room on Elevation 732 of the control building and had breached a boundary door to facilitate traffic and removal of asbestos. The breach was improperly controlled as a result of inappropriate personnel actions. After determining the breach was inappropriate, the structure was dismantled in an orderly manner. LCO 3.0.3 was exited at 1735 EDT when the structure was removed and the door closed. Corrective actions include additional training, procedure and process revisions, and communication of expectations regarding performance.
3271991012 | Sequoyah 1, Sequoyah 2 | 06/12/1991 | 07/12/1991 | 9107170230 | <strong>Inadvertent breach of the main control room and cable spreading room fire barrier and pressurization boundary During the Unit 2 Cycle 4 refueling outage because of inappropriate personnel actions</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1991, at approximately 1250 Eastern daylight time (EDT) with Units 1 and 2 in Mode 1, a breach to the control room pressurization boundary was discovered during the routine performance of a surveillance instruction. Units 1 and 2 applied the action provisions of Limiting Condition for Operation (LCO) 3.7.12, and a work request was written to correct the problem. On June 13, 1991, at approximately 1331 EDT, the breach had been sealed and documented, and Action Statement a of LCO 3.7.12 was exited. Investigation of the event determined that the breach occurred on or about September 8, 1990, during the implementation of the Unit 2 Cycle 4 refueling outage Gamma Metrics modification. Modifications' craft were instructed to install a conduit in the bottom of Panel 2-M-13 Cabinet II, but through inappropriate personnel actions, mistakenly installed the conduit in Cabinet III. Part of the installation procedure required the fire barrier in the bottom of the panel to be breached. The incorrect installation was identified and corrected. However, the inadvertent breach through the fire barrier and pressurization boundary was not recognized, and corrective action was not initiated to repair the breach. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), LCO 3.7.12, Action Statement a, and Unit 2 License Condition 2.H.
3271991013 | Sequoyah 1, Sequoyah 2 | 06/13/1991 | 07/31/1991 | 9108050172 | <strong>Inoperable penetration seal that was not inspected or identified as a result of a deficient procedure</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide additional information resulting from further investigation. On June 13, 1991, with Units 1 and 2 operating in Mode 1, it was determined that a fire barrier penetration had not been properly sealed and visually inspected as required by Technical Specification (TS) 4.7.12. The deficient seals appear to have existed since initial construction and were not corrected by implementation of a 1987 design change intended to ensure fire compartmentation was adequately established relative to conduit penetrations. The cause could not conclusively be determined because of the extended duration of the condition, but appears to have resulted from inattention to detail. Technical inadequacies in Surveillance Instruction (SI) 233.1E, "Mechanical Penetration Fire Barrier Visual Inspection," including inadequate acceptance criteria, contributed to not identifying inoperable penetration seals during previous surveillances. The penetration was sealed on June 18, 1991. The procedures implementing the TS surveillance requirement will be revised, and additional surveillances will be performed. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) and Unit 2 License Condition 2.H.
3271991014 | Sequoyah 1, Sequoyah 2 | 06/10/1991 | 07/10/1991 | 9107170221 | <strong>Fire watch patrols were not performed because of radiological conditions and a failure of administrative controls</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1991, with Units 1 and 2 operating in Mode 1, fire watches required by Technical Specification LCOs 3.3.3.8 and 3.7.12 action statements were missed in the auxiliary building and the additional equipment building because of an airborne condition that occurred at 2017 EDT. Additionally, fire watch patrols in the ABGTS room in the auxiliary building, Elevation 714, and the UHI area in the additional equipment building required by Action Statement (a) of LCO 3.7.12 were not performed because of a failure in the administrative control of fire watch patrols. As corrective action, the detectors that were out of service were returned to operable status, the airborne condition was corrected, the fire watches were reestablished, and administrative control of fire watch patrols has been strengthened. These events are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation prohibited by technical specifications.
3271991015 | Sequoyah 1, Sequoyah 2 | 07/08/1991 | 08/07/1991 | 9108140044 | <strong>Fire Watch Patrol Was Not Performed Because of Inadequate Shift Turnover</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1991, with Units 1 and 2 operating in Mode 1, a fire watch required by Technical Specification 3.7.12, Action Statement (a), was not performed for approximately four hours. The fire watch was not performed because of inadequate shift turnover, which resulted from ineffective communication of the revised turnover process, staffing requirements to the fire watch, and the fire protection foreman. The fire watch was reestablished upon discovery. The requirements associated with shift turnover have been reviewed with all fire watches.
3271991016 | Sequoyah 1, Sequoyah 2 | 07/11/1991 | 02/07/1992 | 9202140203 | <strong>Operations with Unqualified Penetration Seals Caused by Thermal Movements</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1991, with both units operating in Mode 1, a condition was identified involving unqualified penetration sleeve seals because of piping thermal movements. The unqualified sleeve seals consist of Dow-Corning 3-6548 room temperature Vulcanizing (RTV) silicone foam. Piping through four Unit 1 and five Unit 2 penetrations exceeded the axial movement criteria of 15 percent of the minimum annular distance and three Unit 1 and three Unit 2 penetrations exceeded the 1/4-inch limit for radial movements. The cause of the existing unqualified penetrations is that original design requirements relative to RTV foam seals were inadequate. Corrective actions include maintaining required fire watch coverage in the interim, modifying the unqualified seals and establishing an action plan to address the remaining sleeve seal issues. This report is being submitted as required by 10 CFR 50.73(a)(2)(i)(B) and in follow-up to Special Report 91-11.
3271991017 | Sequoyah 1 | 07/15/1991 | 04/24/1992 | 9204290330 | <strong>Operation With an Inoperable Lower Containment Radiation Monitor Because of the Inlet Valve Being Isolated</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to reflect a schedule change to a corrective action. On July 15, 1991, at 0820 Eastern daylight time (EDT) with Unit 1 operating in Mode 1, and 100 percent power, Radiation Monitor (RM) 1-RM-90-106, which provides lower containment atmosphere particulate and gaseous monitoring, was declared inoperable because the inlet valve was found closed. This condition was discovered by radiochemical laboratory analysts (RLAs) replacing a filter on the RM. The valve had apparently been left closed following the filter replacement the previous day. The valve was immediately opened, but the RM was not considered operable until after a functional check was conducted. A low flow alarm, which should have alerted operators to the condition, had not actuated. The alternate RM (1-RM-90-112) was aligned to lower containment at 1239 EDT. Several personnel performance weaknesses and procedure inadequacies contributed to the event. Corrective action includes additional training and revision to the procedures involved.
3271991018 | Sequoyah 1, Sequoyah 2 | 08/12/1991 | 08/26/1991 | 9108290067 | <strong>Operation With Barriers That Did Not Comply with Underwriters Laboratories Configurations Resulting from Deterioration of Material, Inappropriate Personnel Actions or Initial Installations Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1991, with Unit 1 and Unit 2 operating in Mode 1, a condition was identified involving nonfunctional fire barriers. This condition was discovered during implementation of corrective actions associated with Special Report 91-03, Revision 1, dated June 7, 1991. As-found conditions in seven fire barrier walls did not comply with Underwriters Laboratories tested configurations. The duration and cause of these conditions could not conclusively be determined. They could have resulted from inappropriate personnel action, deterioration of material, or initial installation not conforming to compartmentation requirements. Corrective action includes repair of the subject deficiencies, inspecting the remaining fire barriers to provide a baseline of qualification, upgrading surveillance to ensure barriers are maintained, and raising personnel awareness through General Employee Training.
3271991019 | Sequoyah 1, Sequoyah 2 | 07/21/1991 | 08/16/1991 | 9108230232 | <strong>Emergency Diesel Generator Started When the Start-Stop Handswitch 0-HS-82-104 was Inadvertently Bumped</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1991, at 1955 Eastern daylight time with both units in M 100 percent power, 2,235 pounds per square inch gauge, and 578 degrees Fahrenheit), the 2B-B diesel generator (D/G) started when the main control room (MCR) Handswitch (HS) 0-HS-82-104 was bumped. A system engineer was in the MCR walking from the Unit 2 end to the Unit 1 end between the shift operations supervisor's (SOS's) desk and Panel 0-M-26. Movement of personnel conducting business with the SOS at the SOS's desk caused the system engineer to bump 0-HS-82-104 located on Panel 0-M-26, thus starting the 2B-B D/G. The cause of the accidental start of the 2B-B D/G was the system engineer walking too close to the panel on carpet color-designated for the purpose of disallowing normal personnel traffic. The system engineer was unfamiliar with the significance of the red-colored carpet. Immediate corrective action was to place the 2B-B D/G in standby. A site dispatch has been issued informing employees of the significance of the red carpet in the MCR, and a sign has been added in the MCR instructing personnel not to step on the red carpet.
3271991020 | Sequoyah 1, Sequoyah 2 | 07/22/1991 | 08/21/1991 | 9108270215 | <strong>Action Provisions of LCOs 3.7.11.2 and 3.7.11.4 Could Not Be Complied With Following the Loss of Fire Suppression Water System Pressure</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1991, at 2115 Eastern daylight time (EDT), with Units 1 and 2 operating in Mode 1, Limiting Conditions for Operation (LCOs) 3.7.11.2 and 3.7.11.4 were entered when all fire protection spray and sprinkler systems and hose stations were declared inoperable. The required action provisions to establish fire watches and route backup fire hoses within one hour could not be complied with because all plant areas were affected, constituting operations prohibited by technical specifications. These systems were declared inoperable as the result of a loss of pressure in all fire suppression water system headers. The loss of header pressure was the result of incorrectly positioned valves that were manipulated during fire pump testing on the afternoon of July 22. Upon discovery of the incorrectly positioned valves, actions were promptly implemented to restore system pressure in a controlled manner. System pressure was restored, system valve alignment was verified, and LCOs 3.7.11.2 and 3.7.11.4 were exited at 0129 EDT on July 23. The Operations personnel responsible for incorrectly positioning the valves were appropriately disciplined. This LER also supplements information provided in Special Report 91-12, dated August 5, 1991.
3271991021 | Sequoyah 1, Sequoyah 2 | 09/03/1991 | 10/03/1991 | 9110100029 | <strong>Failure to comply with technical specifications because of the deletion of a surveillance requirement During a procedure revision</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1991, at 1100 Eastern daylight time (EDT) with Units 1 and 2 operating in Mode 1, a problem was discovered involving failure to comply with plant technical specifications. The surveillance instruction implementing Surveillance Requirement (SR) 4.8.2.3.2.e, for battery performance discharge tests did not require a postmaintenance test (PMT) that ensured literal technical specification compliance; however, the PMT was fully adequate from a technical standpoint. Technical Specification SR 4.8.2.3.2.b.2 requires that connection resistance be verified following a battery discharge. This requirement appears to be intended to apply to inadvertent discharges rather than planned testing because a technical basis for this requirement does not exist following a discharge test. This requirement was deleted from the performance discharge test SI during a 1988 revision to the procedure because of an oversight. The requirement will be added to the SI before the next performance.
3271991022 | Sequoyah 1 | 09/04/1991 | 10/04/1991 | 9110110026 | <strong>Smoke Detectors in Duct Work of Clean Air Systems Inoperable Because of Misoriented Covers</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1991, at 1842 Eastern daylight time (EDT) with Units 1 and 2 operating in Mode 1, Limiting for Operation (LCO) 3.3.3.8 was entered because the smoke detectors in the emergency treatment system and the auxiliary building gas treatment system, were determined to be inoperable. An hourly fire watch was established for the affected ares. This condition was discovered during routine replacement of an inoperable detector when Operations personnel noticed potential leakage paths for airborne radioactivity from the duct work. Informal inspection of other duct detectors revealed additional problems with the detectors including, misorientation of the detector covers and missing sensitivity test jack lids. Misorientation of the detector cover reduces the air flow though the detectors causing the instrument to effectively become inoperable. A work request was initiated to correct the conditions, and LCO 3.3.3.8 was exited at 2118 EDT on September 6, 1991, except for four inaccessible detectors located in the Unit 1 lower containment cooler area. These duct detectors will be inspected and corrected during the Unit 1 Cycle 5 refueling outage. This report also fulfills the requirements of the special report required by Technical Specification 3.3.3.8, Action b.
3271991023 | Sequoyah 1, Sequoyah 2 | 08/30/1991 | 09/30/1991 | 9110040242 | <strong>Potential for loss of containment sump inventory to outside containment During a small break loss of coolant accident</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1991, at 1500 Eastern daylight time (EDT) with Units 1 and 2 operating in Mode 1, it was determined that a potential accident scenario identified by a D. C. Cook Nuclear Plant Nuclear Experience Review existed at SQN for a loss of postaccident containment sump inventory outside containment. The scenario involves a high suction pressure for the centrifugal charging pumps resulting in the seal water heat exchanger relief valve diverting containment sump inventory to the volume control tank during a small break loss of coolant accident (LOCA). SQN's personnel reviewed the identified scenario, performed a similar accident scenario on the SQN simulator, and concluded that a similar condition at SQN potentially existed. The root cause of the event has not yet been determined; the investigation into the event by Westinghouse Electric Corporation and TVA is ongoing. Operations' crews were briefed on the potential event and the appropriate mitigating actions. The emergency procedures were reviewed and determined to be adequate to mitigate small break LOCA scenarios without compromising core and nuclear safety. An emergency preparedness implementing procedure was revised to include this potential small break LOCA concern with various actions to address the scenario.
3271991024 | Sequoyah 1, Sequoyah 2 | 10/22/1991 | 11/21/1991 | 9111270115 | <strong>Inoperable fire detector circuit supervision due to inadequate understanding and review</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1991, with Unit 1 in Mode 5 and Unit 2 in Mode 1, it was discovered that an alarm condition on a fire detection panel "masks" trouble alarms on the panel. Because several alarms have been in continuously, the detector supervisory circuits required by Surveillance Requirement 4.3.3.8.2 have been functionally inoperable, without complying with the corresponding action provisions. This condition resulted from a lack of understanding of the specific fire detection system feature and a lack of sensitivity to fully evaluating continued operation with alarm conditions. The continuous alarm conditions have been disabled, and operators have been trained on the masking feature of alarm conditions. Additional corrective actions are being taken to institutionalize the awareness of the masking feature.
3271991025 | Sequoyah 1 | 12/14/1991 | 01/13/1992 | 9201210139 | <strong>Main steam isolation valves inoperable because jumpers had not been removed following maintenance</strong><br /><i>Abstract:&nbsp;</i>During the performance of a special test of the main steam isolation valves (MSIVs) on December 14, 1991, jumpers were discovered on the A train closure circuitry that had not been removed following outage maintenance activities. The jumpers would prevent manual or automatic closure of the MSIVs from the A train circuitry or protective signals. The MSIVs were declared inoperable, and the appropriate Limiting Conditions for Operations (LCOs) were entered. The jumpers were removed and the valves were subsequently stroke-time tested successfully. The Loop 4 valve was adjusted, retested, and declared operable. The other valves were tested successfully. Jumpers had been removed from the B train circuitry following outage maintenance activities. Jumpers were not removed from the A train circuitry because personnel did not properly use and follow procedures. Maintenance personnel will be briefed on the requirements and importance of prejob briefings, following procedures, and having work instruction in the field. Contributing causes were also identified and are being addressed.
3271991026 | Sequoyah 1, Sequoyah 2 | 11/07/1991 | 12/09/1991 | 9112130060 | <strong>Insufficient vendor information results in a lack of selective breaker coordination</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1991, at 0800 Eastern standard time (EST) with Unit 1 in a refueling outage and Unit 2 operating at approximately 100 percent power, it was determined that various 480-volt electrical boards did not have selective coordination between the feeder breakers and the load breakers on the board as a result of a breaker design feature. The design feature had not been recognized as a result of insufficient vendor information. To correct the coordination problem on safety-related boards, a modification was initiated to disable the design feature on selected breakers. On November 8, 1991, two electricians implementing the modification introduced a glowstick into a 1B2-B shutdown board compartment prior to checking for faults. The electrode assembly of the glowstick contacted the B and C phase buses and a fault occurred causing damage and loss of the shutdown board. The shutdown board was repaired and the modification completed for the selected breakers.
3271991027 | Sequoyah 1 | 12/13/1991 | 01/13/1992 | 9201210144 | <strong>Manual closure of the main steam isolation valves as a result of a malfunction of a steam dump valve controller resulting in a cooldown of the reactor coolant system</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1991, at 1459 Eastern standard time (EST), Unit 1 reactor coolant system (RCS) experienced an inadvertent cooldown event. Upon observing pressurizer level decreasing, Operations increased charging flow and manually isolated letdown in an attempt to stabilize the pressurizer level. Review of plant parameters determined that the event was due to a problem on the secondary side of the plant. Operations proceeded to manually close the main steam line isolation valves and manually closed the level control valves to limit the cooldown effect of auxiliary feedwater. In order to complete steam generator (S/G) isolation, the operators isolated S/G blowdown. After isolation of all four S/Gs, plant parameters stabilized. The root cause of this event was the intermittent failure of a steam dump valve controller resulting in the opening of two steam dump valves. The severity of the cooldown was caused by a steam dump valve failing to close after the controller malfunctioned. A work order was performed that replaced the pressure controller and controlling potentiometer.
3281991001 | Sequoyah 2 | 01/03/1991 | 02/01/1991 | 9102080167 | <strong>Automatic Feedwater Isolation and Subsequent Auxiliary System Start as the Result of a High-High Steam Generator Level and LCO 3.0.3 Entry for More Than on RPI per Bank Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1991, at 1516 Eastern standard time (EST) with Unit 2 in Mode 1, a feedwater isolation (FWI) and subsequent automatic start of auxiliary feedwater occurred. The FWI was the result of a high-high steam generator level signal from Loop No. 4. The high-high level setpoint was reached following the inadvertent closure of the main turbine governor valves. The governor valves closed during attempts to reset the turbine electrohydraulic control (EHC) system following an automatic turbine runback. The turbine EHC system was receiving an artificially high input for turbine impulse pressure, which was caused by a dampening valve that had vibrated closed in the impulse pressure transmitter sense line. Administrative controls have been initiated that prohibit the use of the turbine control circuitry, which utilized the turbine impulse pressure input. <br /><br /> On January 4, 1991, at 0512 EST with Unit 2 stabilized in Mode 2, Limiting Condition for Operation (LCO) 3.0.3 was entered when two rod position indicators in the same bank deviated from the demand position indicators by greater than 12 steps. The deviations were the result of temperature changes and rod movement following the turbine trip. Temperature was stabilized, the control rods were withdrawn slightly, and the RPIs returned to indicating within 12 steps of the demand indicators. LCO 3.0.3 was exited at 1002 EST. An evaluation will be conducted in an effort to prevent future entries into LCO 3.0.3 as a result of RPI drift.
3281991002 | Sequoyah 2 | 02/11/1991 | 05/02/1991 | 9105070337 | <strong>Failure to comply with Technical Specification Action Statement and establish the appropriate compensatory measures.</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1991, with Unit 2 in Mode 1, it was determined that on February 11, 1991, Unit 2 had operated in a condition prohibited by Technical Specification (TS) 3.3.3.8 Limiting Condition for Operation (LCO) action statement (a). Action statement (a) requires a fire watch to be established within an hour upon entering the LCO. On February 11, 1991, fire protection panel 0-L-630 was removed from service for maintenance, and Operations entered LCO 3.3.3.8. Because of the expected short duration, no fire watch was established. Operations ordered the work stopped and return of the panel to normal when all four fire pumps started unexpectedly. Operations prematurely exited the LCO when informed that the panel had been returned to normal. Communications between Operations personnel and Maintenance personnel was inadequate causing Operations to consider the panel to be operable. Troubleshooting later revealed the panel was inoperable and Operations was notified. LCO 3.3.3.8 was re-entered. Unit 2 operated approximately six hours without establishing a fire watch. Multiple causes and contributing factors have been identified, including an inadequate procedure, poor communication, inadequate training, and failure to follow procedures. Corrective actions are being taken to address these items..
3281991003 | Sequoyah 2 | 03/01/1991 | 04/10/1991 | 9104170202 | <strong>Power Not Removed From Cold Leg Accumulator Isolation Valve As A Result Of Inappropriate Personnel Actions.</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1991, at 0127 Eastern standard time (EST) with Unit 2 in Mode 1, it was discovered that the breaker for the operator for the No. 3 cold leg accumulator (CLA) isolation valve 2-FCV-63-80 was locked in the closed position. This was discovered during the performance of Surveillance Instruction (SI) 0-SI-OPS-063-013.0, "Cold Leg Accumulator Valves Power Removal Verification." The last documented manipulation of this breaker was on February 14, 1991, when an evolution was being performed in attempt to stop inleakage of reactor coolant into the CLA. This evolution was initiated at 2019 EST on February 14, 1991, and completed at 2032 EST with the components thought returned to their required conditions/positions. No independent verification of the breaker's restoration was performed. The cause of the event is attributed to inappropriate personnel actions. Immediate corrective action was to restore the breaker to its correct position. Additional corrective actions include discussions with Operations personnel to clarify requirements, disciplinary action, procedure clarifications, and further training.
3281991004 | Sequoyah 2 | 03/29/1991 | 05/29/1991 | 9106040367 | <strong>Computer point out of scan on the P-250 computer as a result of not maintaining configuration control</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to include additional corrective actions for this issue. On March 29, 1991, at 1142 Eastern standard time, with Unit 2 in Mode 1, TVA identified the plant process computer P-250 computer point C0019A (Control Bank C, Group 2, Position K-10) was out-of-scan. The computer point monitors a control rod cluster position, which provides input into the "Rod Deviation and Sequence/NIS Power Range Tilts" alarm. Surveillance Requirement (SR) 4.1.3.2 requires the comparison of the demand position and rod position indication systems at least once every four hours if this alarm is inoperable. The computer point was taken out of scan on March, 21, 1991, while troubleshooting the "Rod Deviation and Sequence/NIS Power Range Tilts" alarm, which came in during the performance of Periodic Instruction (PI) 0-PI-NXX-085-001.0, "Bimonthly Resetting of Control Rod Fully Withdrawn Position." The cause of the event is failure to return the point to scan; configuration control during troubleshooting of the alarm was not implemented. Immediate corrective action was to place the computer point back into scan. Additional corrective actions include discussions with personnel concerning the importance of configuration control and implementation of a method to maintain configuration control.
3281991005 | Sequoyah 2 | 07/18/1991 | 08/19/1991 | 9108300100 | <strong>Surveillance Requirement Time Interval Exceeded Because of Untimely Failure of P-250 Process Computer</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1991, at 1440 Eastern daylight time (EDT) with Unit 2 operating in Mode 1, SQN entered Limiting Condition for Operation (LCO) 4.0.3 for Unit 2 because Technical Specification (TS) Surveillance Instruction (SI) 0-SI-OPS-92-078.0, "Power Range Neutron Flux Channel Calibration by Heat Balance Comparison," had not been performed within the TS 24-hour specified timeframe and allowed 25 percent extension. The test is usually accomplished utilizing the P-250 process computer and requires only 30 minutes. When the P-250 is unavailable, a manual-type data gathering and calculation exercise is employed requiring approximately five hours to complete. When efforts for restoration of the P-250 computer were unsuccessful and personnel recognized a serious problem existed in restarting the computer, insufficient time remained to complete the SI using alternate means. At 1255 EDT Technical Instruction 2 was initiated to manually perform the SI. LCO 4.0.3 was entered at 1440 EDT, the SI was completed at 1700 EDT, and LCO 4.0.3 was exited at 1710 EDT. To prevent this event from occurring in the future, a computer software program will be evaluated, developed, and implemented to provide an increased frequency of the performance of 0-SI-OPS-92-078.0. This will provide a more reasonable timeframe to implement and accomplish performance of the surveillance requirement by alternate means, if required.
3281991006 | Sequoyah 2 | 11/07/1991 | 12/09/1991 | 9112120224 | <strong>Reactor trip on low-low steam generator level resulting from an inadvertent main steam isolation valve closure caused by a limit switch failure</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1991, at 1403 Eastern standard time, the Unit 2 reactor tripped on low-low steam generator level in Loop 4 during a routine performance of a main steam isolation valve (MSIV) partial stroke test in accordance with Surveillance Requirement 4.7.1.5. During the performance of the test, the MSIV fully closed because of the failure of a limit switch to actuate, which reopens the valve upon reaching the 90 percent open position. The control room staff responded as prescribed by emergency procedures. They promptly diagnosed the plant conditions and took actions necessary to stabilize the unit in a safe condition. Safety systems performed as expected with minor anomalies that did not affect the operators' capability to respond to the event. The 90 percent limit switch was replaced, and the MSIV was retested successfully.
3281991007 | Sequoyah 2 | 11/10/1991 | 12/10/1991 | 9112170462 | <strong>Essential raw cooling water test connection valves necessary for containment integrity were discovered to be partially open for an indeterminate reason</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1991, at approximately 1815 Eastern standard time (EST) with Unit 2 in Mode 5 and Unit 1 in a refueling outage, it was discovered while performing a verification of containment integrity surveillance that three Unit 2 one-half-inch essential raw cooling water (ERCW) test connection valves (normally closed) were partially open. This surveillance instruction requires these valves to be closed and secured to maintain containment integrity. The test personnel reported to the assistant shift operations supervisor that they closed and locked the valves and that the test connection caps were in place and not leaking. The reason for the valves being partially open cannot be determined. The last known manipulation of the valves documents the valves as being closed, locked, and verified. No evidence has been identified to indicate that the valves were opened for any reason since the last official manipulation. The locking devices were found to be loosely installed. The approved method for securing locked valves as delineated in operating procedures has been discussed, and the sensitivity of the personnel raised as to the proper method for ensuring valves are locked appropriately.
3281991008 | Sequoyah 2 | 12/02/1991 | 01/02/1992 | 9201090277 | <strong>Failure of the refueling water storage tank wide range level transmitters because of inadequate administrative controls</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1991, at 0050 Eastern standard time, Unit 2 entered the action statements of Limiting Conditions for Operation 3.0.3 and 3.3.3.7 because of the inoperability of the four wide range refueling water storage tank (RWST) level transmitters (LTs). The transmitter failures occurred when heavy rains resulted in the flooding of the basin surrounding the RWST. Subsequently, the LTs failed because of the partial submergence of the cabinets housing the transmitters resulting in a short between the electrical leads. The root cause of this event is considered to be ineffective administrative controls to compensate for a design deficiency. The RWST basin was pumped out, and the LTs and terminal strips were dried. The proper operation of the transmitters was verified, and they were returned to service. Corrective action is to strengthen the administrative controls.
3311991001 | Duane Arnold | 01/06/1991 | 01/30/1991 | ML11234040 | <strong>Manual Scram Shutdown of Plant Due to Steam Leak in the Heater Bay</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1991, with the plant operating at 95% power, a controlled reactor shutdown was initiated due to a steam leak in the heater bay. At 1107 operators rapidly reduced recirculation flow to minimum in preparation for insertion of a manual scram. The decision to manually scram was conservatively made to ensure heater bay temperatures would not challenge the Main Steam Line isolation setpoint of 200 degrees F. At 1113, with reactor power at approximately 60%, a manual scram was inserted. The intermediate cause of this event was a break in a two inch extraction steam drain line just below the welded joint which attaches the drain line to a twelve inch extraction steam line. The cause for the break in the pipe was cyclic fatigue due to the relative movement of the two inch and twelve inch pipe during plant operation. The section of to inch pipe, where the break occurred, was replaced with a new pipe. The new pipe was constructed with an expansion loop to compensate for relative movement between the twelve and two inch pipes. This event had no effect on the safe operation of the plant. Following the scram the plant was quickly brought to a stable condition.
3311991002 | Duane Arnold | 01/22/1991 | 02/14/1991 | ML11234040 | <strong>Reactor Coolant Heatup Rate Exceeds Technical Specification Limit Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1991, during a reactor startup, the heatup rate for the reactor coolant exceeded 100 degrees F/hour in violation of Technical Specification 3.6.A.1. The cause of the event was personnel error. Operators had initiated actions which were reducing heatup rate and successfully restored the heatup rate to within acceptable limits in a few minutes. An analysis of the thermally induced stresses which occurred during the event concluded these were well within acceptable values. <br /><br /> Corrective actions include discipline and counseling personnel involved and prompt dissemination of information relating to the event to all operating crews. Procedures for monitoring the heatup rate are being enhanced. Simulator training will incorporate lessons learned from this event.
3311991003 | Duane Arnold | 02/09/1991 | 03/06/1991 | ML11234040 | <strong>Reactor Scram Due to EHC Oil Fluctuations During Routine Turbine Testing</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1991 at 1659, a reactor scram from 100% power occurred due to a sensed low control oil pressure at the Main Turbine Control valves. Extensive troubleshooting following the event identified induced electrical noise in the Turbine Electro-Hydraulic Control (EHC) System which appeared to have ultimately caused the pressure fluctuation in EHC control oil. Corrective actions include shielding of appropriate cabling and additional, more frequent EHC system component preventive maintenance. All automatic actions occurred as designed as a result of the scram. Operator actions were appropriate and expeditiously returned the plant to a stable condition.
3311991004 | Duane Arnold | 05/08/1991 | 06/07/1991 | ML11234041 | <strong>Inadvertent Inboard High Pressure Coolant Injection System Steam Supply Isolation While Venting a High Steam Flow Differential Pressure Switch.</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1991, with the plant operating at 100% power, a Primary Containment Isolation System High Pressure Coolant Injection System inboard isolation occurred. The isolation occurred during venting of a HPCI Turbine High Flow differential pressure switch (PDIS2244). Venting of PDIS2244 was initiated when Operations identified that the instrument was not indicating as expected approximately three hours after its calibration. The root cause of this event was a combination of two factors. The discrepancy in instrument indication is suspected to have been caused by air being trapped in the instrument or its associated piping during the calibration process. The second factor was a lack of guidance for Operations personnel with respect to venting instruments to correct indication discrepancies. Corrective actions for this event will include review of the instrument calibration process/piping configuration and issuance of formal guidance for Operations personnel regarding the process to be followed when a discrepancy in instrument indication is identified. <br /><br /> This event had no effect on the safe operation of the plant. Although HPCI was technically inoperable during the thirteen minutes that the inboard steam supply isolation valve was closed, HPCI was completely functional and could have been placed in service immediately if required.
3311991005 | Duane Arnold | 06/22/1991 | 04/28/1992 | 9205050243 | <strong>Automatic Reactor Scram Following Main Steam Isolation Valve (MSIV) Closure and Subsequent Residual Heat Removal (RHR) Shutdown Cooling Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1991 with the reactor at approximately 100% power, a single outboard Main Steam Isolation Valve (MSIV) closed, resulting in a high flux automatic reactor scram. The root cause for this event was poor workmanship during original construction of a soldered copper joint in the non-safety related nitrogen supply piping to the outboard MSIVs. Corrective actions include replacement of the MSIV copper piping with stainless steel tubing and evaluation of the long term suitability of existing copper piping in systems related to plant safety or availability. <br /><br /> While proceeding to cold shutdown, on June 23, 1991, a partial Primary Containment Isolation System (PCIS) Group IV actuation isolated the Residual Heat Removal (RHR) system suction piping. This occurred while aligning RHR to enter shutdown cooling. When the RHR pump was started, a pressure surge, cause unknown, resulted in the PCIS actuation. Corrective actions include installation of instrument line snubbers, and testing and analysis of the RHR shutdown cooling system. <br /><br /> This report is submitted as a supplemental update on corrective actions taken and testing performed.
3311991006 | Duane Arnold | 07/11/1991 | 07/31/1991 | 9108060242 | <strong>Primary Containment Isolation System Half Group III Isolation Due to a Blown Fuse Associated with a Refuel Pool Exhaust Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1991, the plant was operating at 100% power when a primary containment isolation system group III ('A' side) isolation occurred along with the initiation of the 'A' standby gas treatment system and isolation of secondary containment. Investigation of the isolation determined that a fuse had blown in the circuit which supplies power to the 'A' refuel pool exhaust radiation monitor. Following replacement of the fuse, the isolation was reset.<br /><br /> The cause of the group III isolation was loss of power to the 'A' refuel pool exhaust radiation monitor. On a loss of power, the monitor defaults to the tripped condition. Investigation into the cause for the blown fuse did not identify any conditions which would have caused the fuse to blow. The blown fuse was replaced without further problems. <br /><br /> This event had no effect on the safe operation of the plant.
3311991007 | Duane Arnold | 08/06/1991 | 08/21/1991 | 9108270106 | <strong>Inadvertent Inboard High Pressure Coolant Injection Steamline Isolation Due to Personnel Error While Installing Relay Block</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1991, during routine surveillance testing, a primary containment isolation for the high pressure coolant injection system steamline was inadvertently actuated by a station technician while installing a relay block. Further surveillance testing resulted in discovery of a non-functioning steamline high flow sensor in the high pressure coolant injection isolation system. Subsequent required testing revealed a broken speed transmitter for the reactor core isolation cooling turbine. Corrective actions included repair of the non-functioning switch and the broken transmitter. Additionally, personnel were reminded that extreme care must be used when installing relay blocks due to the close tolerances associated with them.
3311991008 | Duane Arnold | 08/07/1991 | 08/21/1991 | 9108270101 | <strong>Automatic Emergency Diesel Generator Start Due to Momentary Emergency Bus Undervoltage During Electrical Storm</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1991, at 0733, with the plant operating at 100% power, the 'A' and 'B' Emergency Diesel Generators (EDG) automatically started but were not required to load.<br /><br /> The cause for automatic starting of the EDGs was a momentary under-voltage condition on both emergency buses which was sensed by bus under-voltage relays that feed the EDGs' start logic. The cause for the under-voltage condition was cycling of two switchyard circuit breakers which supply off-site loads. The breakers cycled automatically due to a momentary grid disturbance during an electrical storm. <br /><br /> Following verification that emergency bus voltages were at satisfactory levels, the EDGs were secured and returned to the standby mode. This event had no effect on the safe operation of the plant.
3311991009 | Duane Arnold | 08/15/1991 | 09/05/1991 | 9109130203 | <strong>Reactor Water Cleanup System Isolation Due to a Blown Fuse in the Power Supply Unit</strong><br /><i>Abstract:&nbsp;</i>On August 15, 19?1, at approximately 1851 hours with the reactor operating at 100% power, a primary containment isolation system (reactor water cleanup system) isolation occurred. The reactor water cleanup pump and heat exchanger rooms were inspected for signs of leakage following the isolation. No leaks were found. A blown fuse in the power supply to the high differential flow circuit caused a square root converter to lose power. The root cause of the blown fuse in the power supply is the positioning clip, located in the back of the square root converter instrument drawer, had bent upward slightly and contacted the square root converter cable connector. Corrective actions included repositioning the clip and fuse replacement. All automatic actions associated with the isolation occurred as designed.
3311991010 | Duane Arnold | 09/17/1991 | 10/17/1991 | 9110250025 | <strong>Monitoring Instrumentation not Installed to Meet Seismic Requirements</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1991, it was discovered that four Foxboro instrument nests located in the Control Room did not match their seismic test configuration. A nest is a mounting base with power connections that can house up to ten function modules. Function modules are solid-state electronic circuit cards that perform a specific function. These nests contain the instruments that monitor containment water level (wide range); torus water level, average torus water temperature; drywell pressure and air temperature; and reactor pressure (wide range). There are also instruments to control a Residual Heat Removal (RHR) interlock that disables containment spray permissive at a reactor low water level (2/3 core coverage). The nests were expeditiously brought to a qualified configuration on September eighteenth.
3311991011 | Duane Arnold | 10/17/1991 | 11/14/1991 | 9111260271 | <strong>Inadequate Incorporation of Technical Specification Surveillance Requirements During Design Change Review Causes Missed Verification of Flowpath to Fire Hose Stations</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1991, while operating at 100% reactor power, it was found that six valves in the flowpath to the safety related hose stations were not verified open under surveillance procedures as required by technical specifications. System walkdown and drawing reviews were completed to ensure all omitted valves were identified. In each case, the valve was found to be in the proper position. The monthly surveillance test has been modified, to include the six omitted valves. This event had no affect on the safe operation of the plant.
3311991012 | Duane Arnold | 12/07/1991 | 12/26/1991 | 9201020175 | <strong>Reactor Water Cleanup System Isolation Due to Deformed Connector Contacts</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1991, at 100% reactor power, a primary containment isolation system (reactor water cleanup system) isolation occurred. While taking logs, a control room operator noticed the systems flow summer module not fully flush with the front of the panel. When the operator attempted to fully insert the module, a reactor water cleanup differential flow alarm was received. Approximately 45 seconds later a reactor water cleanup system isolation was received. All automatic actions associated with the isolation occurred as designed and were verified. The cause of the isolation was deformed contacts on the connector at the rear of the summer module. The cause of the deformed contacts is not known although a bent alignment plate causing misalignment of the connector is suspected. The contacts were returned to their normal shape and continuity was verified during movement of the module.
3311991013 | Duane Arnold | 11/07/1991 | 12/26/1991 | 9201020169 | <strong>Lack of Backdraft Dampers in Standby Filter Units</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1991 during system maintenance, it was noted that backdraft dampers designed to be in place in the control building standby filter unit system were not installed. Manual adjustable dampers were found installed in their place. <br /><br /> Special testing proved the system remained operable under the failure mode conditions. The cause for the lack of installation of proper equipment was a failure by the contractor to follow design documents during construction. <br /><br /> This report is being voluntarily submitted for informational purposes.
3331991001 | FitzPatrick | 01/09/1991 | 02/07/1991 | 9102140074 | <strong>Spurious Partial Activation of Primary Containment Isolation System Due to Electrical Noise While Calibrating Adjacent Instrument</strong><br /><i>Abstract:&nbsp;</i>A false primary containment high radiation isolation JM! signal occurred at 1105 on 1/9/91 while the plant was operating at full power. The six primary containment isolation valves which are activated by this signal were already in the closed position. The trip was reset at 1109. Redundant instrumentation confirmed that radiation levels were normal. An electrical noise signal was generated when contacting a volt meter probe with the high voltage test connection during a calibration of an unrelated instrument. The unrelated instrument was physically located about one foot above the electronic drawer for the primary containment high radiation monitor which generated the false signal. Calibration procedures for radiation monitoring instruments will be revised to note that the possibility of spurious trip signal being transmitted to adjacent instruments exists. During the 1991 Refueling Outage the panel containing the radiation monitors will be thoroughly inspected and analyzed to determine if improvements in noise suppression are possible.
3331991002 | FitzPatrick | 03/04/1991 | 04/03/1991 | 9104100210 | <strong>New Three-Inch Telephone Cable Conduit Sleeve Fire Wall Penetration Opened and Left Unattended Due to Personnel Error and Deficient Procedures</strong><br /><i>Abstract:&nbsp;</i>On 3/4/91, an opening was made in a wall to install a 3-inch telephone cable conduit sleeve. The wall is a fire barrier in Appendix A to NRC Branch Technical Position 9.5-1. The plant was operating at full power. No fire watch was provided. The opening was left unattended when workers went to lunch at 1145. The opening was discovered unattended at 1226. A fire watch was established. The wall separated the telephone room from a stairwell and ultimately from steel conduit containing safety-related cable located more than 138 feet from the opening. A second for wall is in place between the opening and the safety-related cable. This second wall is not designated in the fire Protection Manual. The work request specified requirements to provide fire barriers in the conduit in accordance with a specific procedure. The procedure required posting of a fire watch for a list of specific areas, not including this penetration. The work permit request failed to provide instructions for a fire watch. The job supervisor was experienced in working on fire barrier penetrations. The cause is attributed to human error in not recognizing the need to establish a fires watch while the fire barrier penetration was open and unsealed and a deficient procedure. Corrective action will include retraining of the foreman, increased attention to pre-job preparation and briefing by the supervisors, and revision to the installation procedure.
3331991003 | FitzPatrick | 03/09/1991 | 04/09/1991 | 9104190336 | <strong>High Radiation Gate Left Unlocked And Unguarded Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1991 at 0100 hours, with the plant shutdown in the cold condition, a non-licensed operator (NLO) discovered the primary containment (drywell) entrance gate 272-11 unlocked and unguarded with the latch mechanism taped over. The NLO immediately untaped the latch, shut and locked the gate. A Radiological Technician had taped over the latch mechanism to facilitate moving equipment (HEPA hose) into the primary containment and forgot to remove the tape and lock the gate when he finished because he left the primary containment through a different access point. The gate was left in the unlocked and unguarded condition for a period of approximately four hours and twenty minutes. A check of the access log for the Reactor Building (RB) and a tour of the Primary Containment showed that no unauthorized personnel were in these areas. Corrective actions include a reaffirmation of high radiation area locked gate requirements with all plant radiation workers and disciplinary action.
3331991004 | FitzPatrick | 03/18/1991 | 04/17/1991 | 9104240274 | <strong>Radioactive Liquid Effluent Release in Excess of Two Times Maximum Permissible Concentration Due to Personnel Error, Deficiencies in Procedures, & Management of Eng.</strong><br /><i>Abstract:&nbsp;</i>An Unusual Event was declared at 1445 on 3/18/91 after the unmonitored release of radioactivity was detected outside the auxiliary boiler building. Contamination was detected on the ground, building walls, and roofs. Due to rain shower activity, rain water from contaminated building roofs drained to the storm drainage system, resulting in an unmonitored release into Lake Ontario. This event resulted from activities associated with the liquid radioactive waste concentrator [WD]. The concentrator waste line was plugged and operators were performing troubleshooting activities to clear the line. Steam from the auxiliary boiler [SA] provides process steam to the waste concentrator and the condensate is returned to the boiler. Due to inappropriate actions by the operators, the condensate return became contaminated with radioactive concentrated waste. The radioactive waste escaped with the venting steam via the atmospheric vent on the auxiliary boiler roof. At approximately 1315 the vent was closed, which terminated the source of unmonitored release. The storm drainage system was blocked at 1939, terminating the unmonitored release to Lake Ontario. Activities during and after the Unusual Event involved preventing continued release to the environment, clean-up, decontamination, root cause of the event, and an assessment and accounting of radioactivity released during the event.
3331991005 | FitzPatrick | 04/12/1991 | 05/13/1991 | 9105210193 | <strong>Torus Water Temperature Instrumentation Inoperable Due To 3.5 Degree Instrument Channel Uncertainty</strong><br /><i>Abstract:&nbsp;</i>The primary containment NH! suppression pool (torus) water temperature instrumentation was modified in 1981 to provide for one dual element resistance temperature detector (RTD) in each of the 16 bays of the torus. An evaluation of the system on 4/11/91 found that a maximum of one degree of non conservative error could be introduced during conditions of nonuniform addition of heat to the torus providing torus cooling mode of Residual Heat Removal System was in operation. This data was then included in an instrument channel uncertainty calculation performed on 4/12/91. A conservative maximum instrument channel uncertainty of 3.52 fahrenheit degrees was calculated. However, this is within a calculated 4 degree margin to the NUREG 0783 peak local temperature limit. Conservatively, the torus water temperature instrumentation is being reported as inoperable. The torus water temperature instrument software was reprogrammed to add a 4 degree bias so that the calculated bulk (average) temperature would be displayed at a value of 4 degrees above the water temperature actually sensed by the RTDs. Analysis shows that even if this maximum uncertainty had occurred in the non conservative (low) direction, the resulting indicated temperature would not have had an adverse effect on operator actions if events managed by the emergency operating procedures had occurred.
3331991006 | FitzPatrick | 05/07/1991 | 10/04/1991 | 9110110142 | <strong>Manual reactor shutdown due to inoperability of both Low Pressure Coolant Injection subsystems due to mechanical failure of on</strong><br /><i>Abstract:&nbsp;</i>Between 0400 and 0500 on 5/7/91 a monthly Technical Specification check found one of the two primary containment isolation valves in both residual heat removal BO! low pressure coolant injection (LPCI) BO) subsystems to be inoperable. One valve operator torque switch tripped in both directions preventing both full closure and full opening. The other valve had excessive seat leakage. The inoperability of both RHR/LPCI systems required a reactor shutdown within 24 hours which was initiated and an Unusual Event declared at 1237. The reactor was manually scrammed at 1820 achieving cold shutdown on 5/8/91 at 0330. The Unusual Event was terminated at 0400. In LPCI loop B the threads of the gate valve stem nut in the motor operator were worn and broken causing the valve to lock in a partially open position. The stem nut was replaced and LPCI loop B restored to service at 1410 on 5/12/91. The stem of an angle globe throttle valve in loop A was broken inside the valve body. The disc, disc guides, and seat were severely damaged. The valve was removed from the system and repaired. Analysis determined stem nut wear out may have been accelerated by mechanical overload caused by high differential pressure across the valve. The valve stem failed due to throttle flow induced vibration causing cyclic fatigue.
3331991007 | FitzPatrick | 06/21/1991 | 08/20/1992 | 9208260195 | <strong>Scram while Shutdown Caused by False Low Reactor Water Level Signal During Calibration of Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - PREVIOUS REPORT DATED JULY 22, 1991<br /> EIIS Codes are in ! <br /><br /> A false low reactor water level signal resulted in a reactor scram at 1418 hours on 6/21/91 while the plant was in the cold condition. Narrow range reactor feedwater control JB! level transmitter 06LT-52C had been replaced and calibrated. As it was being valved into service, the scram occurred. The instrument being restored to service shares common reference and variable legs with the instruments of the reactor protection system JC! level instruments which initiated the scram. <br /><br /> This is the third occurrence of an event of this type, under similar circumstances, within 18 months. A hydraulic transient occurred as reactor water level transmitter 06LT-52C was valved in service. A root cause investigation has been completed. Corrective action is in the process of being implemented. Related LERs: 90-026, 90-001, 87-020, and 85-012.
3331991008 | FitzPatrick | 06/25/1991 | 07/25/1991 | 9108050063 | <strong>Fire Barrier Manway Open Without Fire Watch Caused by Human Error</strong><br /><i>Abstract:&nbsp;</i>The plant had been shut down for approximately 7 weeks for maintenance. On 6/25/91 at 1330, a 17 by 21-inch rectangular opening was found between the cable tunnel containing safety-related cable and a concrete block pipe chase. The opening is normally closed by a 3-hour rated manway plug. The plug had been removed to perform a modification and was apparently not replaced due to personnel error at the end of the second shift (1530-2330) the previous night. <br /><br /> Modification installation personnel were aware of the existence of the fire barrier and the access plug. The need to keep the plug in place when modification work was not in progress was emphasized during pre-job briefings.<br /><br /> The lack of combustible material in the pipe chase, coupled with the location and the distance across a bare concrete floor to the nearest safety-related cable tray, supports a finding that no significant safety risk existed.<br /><br /> Corrective actions include counselling of personnel and labeling of removable fire barrier penetration seals.
3331991009 | FitzPatrick | 07/11/1991 | 08/15/1991 | 9108220219 | <strong>Residual Heat Removal Heat Exchanger Vent Piping Inoperable Due to Incorrect Piping Configuration and Pipe Support Discrepancies</strong><br /><i>Abstract:&nbsp;</i>A long-term pipe support inspection and repair program is being conducted. Inspection of the pipe supports on the Residual Heat Removal (RHR) BO! Heat Exchanger "B" Vent piping, one and two-inch diameter size, was conducted on December 7, 1989. Piping configuration deviations and support detail and location deviations were discovered during the inspection. Initial pipe support operability assessments by plant engineering personnel determined that the supports were operable for the design loading condition.<br /><br /> The pertinent inspection and discrepancy information was compiled and submitted to the design organization for detailed analysis. A detailed computer analysis of the existing piping and support conditions concluded on June 20, 1991 that piping stresses during certain design loading conditions would exceed the operability stress limits. <br /><br /> The piping and supports were restored to the original design code requirements on July 20, 1991. <br /><br /> The root cause of this condition was determined to be original design error. LER-87-007 reported a similar condition at this facility.
3331991010 | FitzPatrick | 07/09/1991 | 06/13/1994 | ML04105067 | <strong>Emergency Diesel Generators Potentially Inoperable Due to Fire Protection Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Supplementary Report: The plant had been shutdown for approximately seven weeks for maintenance. As the result of a review of the fire protection reference manual, a number of concerns were identified beginning on 6/6/91. Those determined to be reportable include: 1) Three postulated fire scenarios which could have resulted in loss of ventilation fans for spaces containing equipment required for safe shutdown. 2) Four carbon dioxide actuated fire dampers which had been intentionally closed that would have prevented ventilation of the EDG switchgear room if other supply fans were also disabled by a fire. 3) Five deficient electrical penetrations in a battery room. 4) 19 fire dampers either improperly installed or maintained which could have prevented their operation as designed. The deviations were caused by inadequate fire protection program implementation due to an insufficiently qualified staff, weak administrative controls and inadequate communication between functional work groups. Fire Protection program improvements were implemented through the JAF Results Improvement Program. These improvements included setting program goals and objectives, training, program monitoring and effectiveness evaluations. All hardware deficiencies were corrected through maintenance improvements or modifications.
3331991011 | FitzPatrick | 07/09/1991 | 08/14/1991 | 9108220221 | <strong>Five Control Room Back Panels Lack Adequate Seismic Anchorage Due to Missing Welds</strong><br /><i>Abstract:&nbsp;</i>The design process associated with replacement of a recorder in control room panel 25-09 req ired an evaluation be performed for panel anchorage to floor structure. A walkdown of the 25-09 panel anchorage and adjacent panels 09-18, 09-19, 09-21, and 09-38 performed on June 17, 1991 revealed a number of anchorage points in the base of the panels were not plug-welded to existing embedded floor steel as required by the plant drawings. This was determined to be a concern on July 10, 1991. <br /><br /> The condition was corrected by a plant modification that was designed and issued on July 12, 1991 to restore the anchorage in accordance with alternate design requirements. The modification work was completed on July 19, 1991. <br /><br /> An engineering analysis for the Design Basis Earthquake loading condition was performed concurrent with the restoration activity and completed on July 22, 1991 to evaluate the panels in their original as-built supported condition. The results of the analysis determined the panel anchorage could have failed. <br /><br /> The root cause of this condition was determined to be original construction error. There have been no similar LERs at this facility involving equipment anchorage.
3331991012 | FitzPatrick | 07/21/1991 | 08/20/1991 | 9108290135 | <strong>Fire Door Blocked Open Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1991, at approximately 2130 hours while the plant was shutdown for maintenance, the south cable tunnel to relay room NA! fire door was found blocked open. This door was noted to be closed at approximately 0600 by an operator performing rounds in the area and again by a fire watch in the area between 1300 and 1500. A fire watch was stationed in the immediate area in the relay room to monitor four ventilation system fire dampers, but this door was not included in their instructions. Investigation did not identify the individual(s) responsible for blocking this door open.<br /><br /> Description <br /><br /> The plant was shutdown for maintenance. On July 21, 1991 at approximately 2130 hours while responding to an open door alarm on the north cable tunnel fire door in the relay room NA!, the operator noted the south cable tunnel fire door in the relay room was blocked open and that it would not properly close. A fire watch person was in the area of the door monitoring four
3331991013 | FitzPatrick | 07/31/1991 | 08/27/1991 | 9109160203 | <strong>Both Standby Liquid Control Systems Made Inoperable Due to Loss of Pump Discharge Accumulator Precharge</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1991, at 0910 hours while the plant was shutdown for maintenance, both Standby Liquid Control (SLC) BR! systems were declared inoperable due to the-pump discharge accumulator nitrogen precharge being zero psig. <br /><br /> Both accumulators lost the nitrogen charge due to a slow leak in the charging connector spring loaded valves (Schrader fitting). Both accumulators were immediately recharged and placed on increased monitoring frequency.<br /><br /> Licensee Event Report 89-006 describes a similar incident at this facility.
3331991014 | FitzPatrick | 08/05/1991 | 09/04/1991 | 9109110138 | <strong>Bonnet Pressure Locking of Low Pressure ECCS Injection Valves</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1991 with the plant shutdown for maintenance while filling and venting the Residual Heat Removal (RHR) BO! system following repairs to the outboard Low Pressure Coolant Injection (LPCI) BO! valve, the inboard LPCI injection valve failed to open. The failure of the Limitorque SMB-4 actuator motor was due to sustained operation at locked-rotor current.<br /><br /> On August 5, 1991 the root cause of the actuator motor failure was determined to be hydraulic locking of the valve bonnet. Both LPCI and core spray inboard injection valves were determined to be susceptible to this failure mechanism. All four valves were modified to place a bonnet vent to the high pressure side of the valves.
3331991015 | FitzPatrick | 08/19/1991 | 11/25/1991 | 9112040105 | <strong>High Pressure Coolant Injection System Inoperable Due to Slow Response Time</strong><br /><i>Abstract:&nbsp;</i>Surveillance of the High Pressure Coolant Injection System (HPCI) BJ!, required during a reactor start-up, was performed on 8/19/91 in accordance with Technical Specification 4.5.C.1. Test data indicated that the full flow injection time of 30 seconds, specified in the Final Safety Analysis Report (FSAR) was exceeded by 0.84 seconds. The turbine stop valve opening time of 25.3 seconds specified by the Inservice Testing (IST) Program was exceeded by 2.46 seconds. Also, the main pump discharge inboard isolation valve (23MOV-19) calculated response time of 32.7 seconds exceeded the IST requirement by 2.7 seconds. RPCI was declared inoperable initiating a 7-day Limiting Condition for Operation (LCO). During the next 2 days, HPCI was subjected to 3 test runs. The extended time to full flow was caused by the excessive time period for the turbine stop valve (23HOV-1) to come off its fully shut seat. Oil pressure to open the stop valve was delayed due to air in the duplex filter housing. HPCI met the IST, ST, and FSAR criteria and was declared operable on 8/21/91. HPCI was inoperable for 45.75 hours. Corrective actions include adjusting oil system pressure and placing standby filter in service. LERs 87-010, 89-019, and 89-025 are related.
3331991016 | FitzPatrick | 09/11/1991 | 10/27/1992 | 9211030243 | <strong>Turbine Building Ventilation Exhaust Monitoring</strong><br /><i>Abstract:&nbsp;</i>ELLIS Codes are in !<br /><br /> The plant was operating normally at 100% rated power on 09/11/91 when it was discovered at 0100 hours that continuous Turbine Building (NM! ventilation exhaust iodine and particulate monitoring IL! had been out of service for approximately 16 hours. continuous monitoring is required by Radiological Effluent Technical specification (RETS) 3.1.b. The primary cause of the event was a communications error by the shift supervisor. <br /><br /> A Human Performance Enhancement System Evaluation of the event indicates that protective tagging errors, failure to properly self-check, procedure deficiencies, training deficiencies and the failure of the assistant shift supervisor to attend the shift briefing (planning meeting) were contributing causes. Corrective actions include procedure revision and training in self check techniques.
3331991017 | FitzPatrick | 08/22/1991 | 10/10/1991 | 9110240012 | <strong>Fire Doors Between Emergency Diesel Generator Rooms Left Open on Two Occasions Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1991, at approximately 1000 hours while the plant was operating at 100% power, a journeyman operator on rounds found two normally closed fire doors in an open position. One door, 76FDR-DG- 272-8, is between the B and C Emergency Diesel Generator (EDG) engine rooms; and the other door, 76FDR-DG-272-9, is between the EDG A and C engine rooms. On September 10, 1991, at approximately 1535 hours, while the plant was operating at 100% power, the normally closed fire door, 76FDR-DG-272-7, between the EDG B and D engine rooms was found in an open position by engineering personnel conducting a plant walk through. In both instances, the doors were unattended by plant personnel, and therefore, were without the required posted fire watch in accordance with Technical Specification 3.12.F.1. Only door 76FDR-DG-272-8 is an Appendix R to 10CFR50 three-hour fire barrier. All the doors are Appendix A to BTP 9.5-1 three-hour fire barriers. The fire doors were subsequently secured and the need to keep fire doors closed or post a fire watch was re-emphasized with the personnel involved.
3331991018 | FitzPatrick | 09/17/1991 | 10/16/1991 | 9110280283 | <strong>Primary containment vent and purge valves isolated by spurious high signal trip from containment high range radiation monitor</strong><br /><i>Abstract:&nbsp;</i>A spurious primary containment high radiation monitor JM! isolation signal occurred at 0920 on 9/17/91 while the plant was operating at full power. The primary containment vent and purge valves which are activated by this signal were already in the closed position. The logic circuitry was reset immediately. Redundant instrumentation confirmed that containment radiation levels were normal. The signal which generated the activation of the monitor trip was of a transient nature and could not be traced to a cause. During the 1992 Refueling Outage instrument panels containing the primary containment high range radiation monitors will be inspected and evaluated to determine if improvements are possible for reduction of random transient or spurious electric noise which can cause isolation signals. <br /><br /> Related LERs: 90-028 and 91-001
3331991019 | FitzPatrick | 09/17/1991 | 04/15/1992 | ML09142030 | <strong>High Coolant Injection Instrument Line Failure</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> During normal operation at 100 percent rated power, the quarterly flow rate surveillance of the High Pressure Coolant Injection System (HPCI) BJ! was performed on 09/17/91 in accordance with Technical Specification 4.5.C.1. The Local Leak Rate Test (LLRT) line on the HPCI turbine exhaust line check valve (23HPI-65) failed at a socket weld. Manual valve 23HPI-11 was shut in order to isolate the exhaust line from the primary containment NH! torus. HPCI was declared inoperable initiating a 7-day Limiting Condition for Operation (LCO). Root cause evaluation of this failure indicated poor weld quality as a result of paint contamination during installation. Corrective actions included modification of the piping to reduce the bending moment of the LLRT connection. HPCI was declared operable on 9/19/91. HPCI was inoperable for 64.3 hours.
3331991020 | FitzPatrick | 09/25/1991 | 10/25/1991 | 9111010249 | <strong>Fire Door 76FDR-RW-272-16 Inoperable Due to Tape on Latch Bolt as a Result of Human Error</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! <br /><br /> On 09/25/91 at 0100 hours fire door 76FDR-RW-272-16 in the Appendix R barrier between the turbine building NM! and radwaste building NE! was found with the latch mechanism taped thus preventing latching of the door. A firewatch was posted. The latch was taped as a personnel safety concern when it was found that the latch was inoperative. A firewatch was posted and the door was repaired and tested. The cause of this event was human error.
3331991021 | FitzPatrick | 09/04/1991 | 11/27/1991 | ML04105068 | <strong>Residual Heat Removal, Emergency Diesel Generators, and Fire Pumps Potentially Made Inoperable Due to Inadequate Modification Installation Activities</strong><br /><i>Abstract:&nbsp;</i>The exhaust ventilation fan for one of two safety-related pump rooms tripped on thermal overload at 1400 on 9/4/91 with the plant at full power. The fan trip was the result of a restricted ventilation air supply due to closure of 6 fire dampers to allow modification of the dampers. The restricted air supply resulted in overload during fan auto start while windmilling in reverse or due to low flow during operation. An engineering review formalized on 10/9/91 identified a fire scenario with potential for damage to the fan and fire damper controls and resulting loss of exhaust fans and closure of ventilation fire dampers. Ventilation loss during pump operation would degrade performance of the residual heat removal BO! residual heat removal service water BI!, emergency service water (ESW) BI!, and electric and diesel driven fire pumps KP!. Loss of the ESW flow would degrade the emergency diesel generators EK!. Inadequate ventilation following fire damper closure results from inadequate analysis of the NRC required 1980 fire damper installation. A fire watch in place prior to the event will remain until adequate ventilation is assured. Installation procedure review adequacy and alternate ventilation designs are being evaluated.
3331991022 | FitzPatrick | 10/15/1991 | 03/15/1994 | 9403300023 | <strong>Primary Containment Isolation System - Spurious Actuation</strong><br /><i>Abstract:&nbsp;</i>Update Report - Previous Report Date: 11/13/91<br /><br /> A spurious primary containment high radiation monitor A isolation signal occurred at 0201 on 10/15/91. The primary containment vent and purge valves which are isolated by this signal were already in the closed position. Redundant instrumentation confirmed that containment radiation levels were normal and logic circuitry reset immediately. The transient input signal which activated the monitor trip is believed to have been generated by the actuation of the off-gas vent line isolation delay timer which was initiated during the performance of surveillance testing. The exact nature of the interaction had not been identified at that time. A procedure was developed to closely examine the relationship of actuation to the noise transient during the 1992 refueling outage. The pathways for initiation of the monitor trips was found to be an added input filter assembly. The filters were removed from the monitor inputs before the plant was restored in January, 1993, to eliminate monitor trips by this pathway.
3331991023 | FitzPatrick | 10/09/1991 | 03/15/1994 | 9403230106 | <strong>Both Trains of Safe Shutdown Equipment Potentially Inoperable</strong><br /><i>Abstract:&nbsp;</i>During normal full power operation on 10/9/91, it was found that a Safety Division 1 motor control center ED! feeder cable was routed through a fire zone for which Division 1 equipment is relied on to meet safe shutdown requirements of 10 CFR 50, Appendix R, Section III.G. While the original Appendix R evaluation indicated the cable was within conduit embedded in concrete, it was discovered that a portion of the conduit is actually not embedded. A fire watch was posted immediately. The Division 2 cable was rerouted to meet Appendix R requirements. A root cause analysis indicated that there was a lack of commitment to the fire protection program. Weak written procedures, inadequate interface between engineering groups responsible for the program and inadequate staff qualifications contributed to this deviation. A Fire Protection Program improvement plan was developed from the root cause analysis. the plan was incorporated into the site Results Improvement Program. Actions completed through the improvement program will preclude recurrence of this type event.
3331991024 | FitzPatrick | 11/16/1991 | 03/15/1994 | 9403230046 | <strong>Unsatisfactory Penetration Seals Found During Inspection</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1991, at approximately 1730 hours while the plant was operating at 100 percent power, seven electrical penetration fire seals were found in an unsatisfactory condition during the performance of a penetration seal baseline inspection. As the inspection continued, it became evident that there were programmatic problems with the penetration seal program. Deviations from design were found in approximately 39 percent of the 7200 seals inspected. Minor repairs, cosmetic in nature, were initiated in an additional 15 percent of the seals inspected. All penetration seals were restored to design condition through rework or evaluation as an acceptable configuration. This final report describes the scope and nature of inspection findings. The root cause of the poor condition of the FitzPatrick fire penetration seal program was inadequate training and qualification of staff. Poor administrative controls was a contributing factor. Improved training has been implemented and administrative controls have been strengthened to ensure adequate management oversight of the program. <br /><br /> LER 89-007-01 describes similar weaknesses and deficiencies with the penetration fire seal program.
3331991025 | FitzPatrick | 11/14/1991 | 12/23/1991 | 9112270359 | <strong>Suppression Pool Bulk Temperature Monitor Inoperable Due to a Manufacturing Inadequate Soldered Termination and Incorrect Operation Instruction Program Inserted</strong><br /><i>Abstract:&nbsp;</i>On 11/14/91 at 1920, the primary containment NH! suppression pool water temperature monitoring system Channels A and B were declared inoperable, placing the plant in a 6-hour Limiting Condition for Operation (LCO) when a potential inadequate manufacturer's soldered wiring termination was discovered. On 11/15/91 at 1738, after Channel A had been returned to service and the 6-hour LCO exited an incorrect sensor failure deviation delta value was found to have been inserted into one of the Channel A summation/averaging computation modules. This action caused the plant not to be within the requirement of Technical Specification (TS) Table 3.2-6 LCO action for approximately 17 hours. The cause of the unsoldered wiring terminations was an inadequate manufacturing assembly process and the incorrect deviation delta value was lack of adminstrative controls for instrumentation computation component operating instructions (programs). Both had the potential for degraded plant operator response to postulated design basis accidents. Corrective action was soldering of the unsoldered wiring terminations and inserting the correct deviation delta value into the module. Administrative control of the program was strengthened by issuing access and usage instruction to staff.
3331991026 | FitzPatrick | 11/27/1991 | 12/23/1991 | 9112270363 | <strong>Inoperable Containment Isolation Valves in Both Core Spray Systems</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1991 at 10:05 A.M. with the plant at full power, the "A" and "B" train core spray BM! pump minimum flow valves (14MOV-5A/B) were declared inoperable due to their inability to meet their primary containment NH! isolation function. Technical Services discovered that the valves did not have remote manual operation capability as required by the plant's Final Safety Analysis Report and Technical Specifications.
3331991027 | FitzPatrick | 11/27/1991 | 12/27/1991 | 9201030264 | <strong>Low Pressure Coolant Injection Independent P WER Supply Potentially Inoperable Due To EQ Program Validation Problem</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1991, with the plant operating at 100% power, it was decided in a management meeting that an environmental qualification problem with the two independent power supplies ED! for the low pressure coolant injection (LPCI) BO! valves had the potential for placing the plant in a condition that is outside the design basis for the plant in the event of a LOCA. It was determined that the independent power supplies, under normal plant operating conditions, were operating within their design specification and were operable per the JAF Technical Specifications.<br /><br /> Due to a concurrent problem with the core spray, containment isolation valves, the plant was shut down and cooled down (see LER 91-026). The problem with the independent power supplies will be resolved with a plant modification which will be installed prior to restart of the plant.
3331991028 | FitzPatrick | 11/28/1991 | 12/30/1991 | 9201090145 | <strong>Reactor Shutdown and Cooldown Not Complete Within Time Required Due to Personnel Error and Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1991 while conducting a reactor shutdown and cooldown to meet the requirements of Technical Specification 3.7.D.3 as a result of inoperable primary containment NH! isolation valves (see LER-91-026), the reactor temperature was not reduced to less than 212 degrees F within 24 hours as required. Cooldown to less that 212 degrees F was achieved in 25 hours and 6 minutes. The event was caused by personnel errors and procedure deficiencies. Operating shift resource were diverted to tasks other than meeting the Technical Specification requirement and the shutdown/cooldown process was delayed during performance of surveillance that could have been deferred until after the Technical Specification actions were met. Corrective action includes procedure changes and training to reduce the probability of recurrence. No similar LERs have been written at this facility.
3331991029 | FitzPatrick | 11/30/1991 | 06/03/1993 | 9306100190 | <strong>Spurious Trips of Primary Containment Vent and Purge Isolation System</strong><br /><i>Abstract:&nbsp;</i>Update Report - Previous Report Date, January 2, 1992 <br /><br /> EIIS Codes are in ! <br /><br /> False primary containment NH! high radiation isolation system JM! signals occurred at 1431 and 1938 on November 30, 1991, and again at 1114 on December 13, 1991, while the reactor was shutdown in the cold condition. The 12 primary containment isolation valves which are activated by these signals were already closed or went closed in response. Before two of the actuations, a two-way radio was being keyed in the vicinity of the radiation monitors and at the time of the third, a cable penetration fire seal inspection was being conducted within the monitor cabinet and a Technical Specification surveillance test was being performed on main steam line radiation monitors located in adjacent cabinets. The pathways for initiation of the monitor trips was through a filter assembly. The filters were found attached to the input of the monitors during a root cause investigation. The filters were removed from the monitor inputs before the plant was restarted in January, 1993, to eliminate monitor trips by this pathway. The root cause investigation and analysis was completed during the 1992 Refueling Outage.
3331991030 | FitzPatrick | 12/03/1991 | 04/01/1992 | 9204080103 | <strong>Undocumented Assembly In Primary Containment High Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - PREVIOUS REPORT DATE, JANUARY 2, 1992<br /><br /> EIIS Codes are in !<br /><br /> During the week of 12/9/91, the high range primary containment radiation monitors (HRCMs) IL! installation and application was being evaluated to determine the reason for the history of abnormally high susceptibility to electromagnetic interference (EMI) (see LER 91-001 91-018, 91-022, 91-029, and 92-014). During the course of this evaluation, an undocumented assembly was found in the signal input path to each of the two radiation monitors. The vendor for the radiation monitors was contacted to determine the function of this assembly. The vendor indicated that this assembly may be diagnostic test equipment and that the assembly may have an adverse effect on the performance of the radiation monitors under high primary containment NH! drywell temperature conditions that could exist during a Loss of Coolant Accident (LOCA). A detailed analysis indicates that this assembly introduces a maximum non conservative error of 3.5% for actual radiation levels greater than 1.0E4 R/hr. This analysis concluded that the effect of this assembly cannot be determine conventional analysis techniques for radiation levels less than 1.0E4 R/hr.
3331991031 | FitzPatrick | 12/02/1991 | 01/19/1992 | 9201270259 | <strong>Design Deficiency of the Emergency Service Water System Return Piping from the Emergency Diesel Generator Jacket Water Coolers</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! <br /><br /> On 12/2/91, the plant was in the cold shutdown condition. The Design Basis Document reconstitution effort identified a potential design deficiency in the Emergency Service Water System (ESW) BI!. The common 12 inch ESW return piping from the four Emergency Diesel Generator (EDG) EK! jacket coolers (93WE-1A, 1B, 1C, 1D) is directed back into the A train ESW and Residual Heat Removal Service Water (RHRSW) BI! pump bay MK!. This condition results in heated water from the EDG jacket water coolers being recirculated to the ESW and RHRSW pump inlets. <br /><br /> No design documentation evaluating the effect of the ESW return line from the EDG jacket coolers was located. A conservative analysis was performed to determine the effect of the design configuration on ESW and RHRSW supply temperatures. Immediate corrective action was to limit plant operation to a maximum lake temperature of 65 degrees F and change procedures to require running an RHRSW pump while the ESW pumps are supplying cooling water to the EDGs during EDG operation. This action will prevent exceeding the currently analyzed ESW and RHRSW supply temperature of 82 degrees F. Long-term corrective actions will be a reanalysis of the effect of the ESW return flow from the EDG jacket coolers on ESW and RHRSW inlet temperature or a modification to reroute the ESW return piping from the EDGs.
3331991032 | FitzPatrick | 12/26/1991 | 05/01/1993 | 9305120026 | <strong>Intake Heaters Potentially Inoperable Due to Control Room Fire</strong><br /><i>Abstract:&nbsp;</i>FINAL REPORT - PREVIOUS REPORT DATE: JANUARY 27, 1992 EIIS Codes are in !<br /><br /> On 12/26/91, with the plant in a cold condition and undergoing routine maintenance, a Plant Operations Review Committee meeting was held and it was determined that during a postulated Control Room fire, the existing design of the circulating water system intake structure [NN] deicing heaters is outside the design bases of the plant. Engineering evaluations found that the loss of these deicing heaters due to a Control Room fire is possible and this type of event had not been analyzed as part of the Appendix R fire analysis. The design bases of the deicing heaters was reviewed and the investigation concluded that the heaters are not necessary to maintain safe shutdown and that the present QA category is appropriate.
3331991033 | FitzPatrick | 12/19/1991 | 11/05/1992 | 9211100275 | <strong>Voluntary Report Concerning Potential Torus Pressure Instrument Errors</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - PREVIOUS REPORT DATE: JANUARY 21, 1992 <br /><br /> EIIS Codes are in ! <br /><br /> The plant was in normal shutdown with the mode switch in the refuel position when it was postulated on 12/19/91 that under Loss of Coolant Accident conditions, water may accumulate in primary containment NH! pressure suppression chamber (torus) pressure sensing lines causing significant instrument error. The potentially effected instruments are for accident monitoring IP!, input to certain Safety Parameter Display System (SPDS) displays, and for control of reactor building-torus vacuum breaker isolation valves. On 4/29/92 Engineering provided the results of calculations, which show that the originally postulated errors due to water accumulation result in only approximately one-fourth of a drip leg being filled in 100 days at accident conditions. As a result, no errors are introduced and this LER is reclassified as a voluntary report.
3341991001 | Beaver Valley 1 | 01/07/1991 | 02/05/1991 | 9102110168 | <strong>Inoperable Delta Flux Alarm Without Alternate Monitoring</strong><br /><i>Abstract:&nbsp;</i>On 1/7/91, during routine monitoring of the plant computer log printouts, several anomalies were identified in the Power Range Excore Nuclear Instrumentation data. An investigation of the anomalies revealed that computer points for Power Range Detector N41 and Power Range N42 Top Detector had both been removed from computer scan on 12/30/90 in accordance with a surveillance procedure. These computer points were not returned to computer scan during the performance of maintenance surveillance procedures to restore the Power Range High Nuclear Flux Reactor Trip setpoints. The removal from scan of computer point N0043A caused an erroneous value for computer point Quadrant 2 Delta Flux (U0956). Quadrant 2 Delta Flux, U0956, is used for the Delta Flux Alarm program. The Delta Flux Alarm is considered to have been inoperable for Quadrant 2 from 12/30/90 at 1104 hours to 1/7/91. Both computer points were restored to scan on 1/7/91. There were no safety implications to the public as a result of this event. The Delta Flux Alarm was operable for Power Range Detectors N41, N43 and N44. Delta Flux was recorded on 12/31/90 and 1/06/90 as a normal weekly surveillance. No abnormalities were noted for these readings.
3341991002 | Beaver Valley 1 | 01/18/1991 | 02/19/1991 | 9102250136 | <strong>Reactor Coolant System Pressure Boundary Leakage Results in Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 1/16/91, with the Unit in Power Operation at 100% reactor power, a review of the operating logs showed an increased containment sump pumpout rate and increased "unidentified" leakage (from 0.1 gpm to 0.3 gpm) on a reactor coolant system (RCS) water inventory surveillance test. During the 1/16/91 afternoon shift and the 1/17/91 midnight shift, multiple containment entries were made to identify the source of the leakage. The area of leakage was reported to be near the Loop 1B Cold Leg Stop Valve. Since the installed insulation prevented positive identification of the exact location of the leak, a plant shutdown to Hot Standby was performed. An Unusual Event was declared in accordance with the Emergency Preparedness Plan Implementing Procedures due to apparent pressure boundary leakage. Following insulation removal, the leakage was confirmed to be on the piping to RC-67, the Loop 1B Cold Leg Vent Valve. This valve and piping was removed and the RCS pressure boundary penetration was plugged and capped. There were no safety implications to the public as a result of this event. No radioactive releases from containment occurred. The amount of leakage was within the capability of the normal charging system arrangement.
3341991003 | Beaver Valley 1 | 01/19/1991 | 02/19/1991 | 9102250144 | <strong>Feedwater Isolation due to "A" Steam Generator Level High</strong><br /><i>Abstract:&nbsp;</i>On 1/19/91 with the Unit in Cold Shutdown, reactor coolant temperature was being reduced by the Residual Heat Removal (RHR) system. To increase the cooldown rate of the secondary plant, two steam dump valves were opened to the condenser which was being maintained at vacuum. Steam generator levels began trending upward. At 1346 hours, level in the "A" steam generator reached 75 percent, causing a feedwater isolation signal and closing the main feedwater containment isolation valves. Following the ESF actuation, plant operators broke condenser vacuum and opened the steam generator atmospheric steam release valves which increased steam generator pressure to atmospheric. As pressure in the steam generators increased, levels decreased. Evaluation of this event determined that the subatmospheric pressure within the steam generators caused an addition of water from the Primary Plant Demineralized Water Storage Tank (WT-TK-10) due to a flowpath through the open auxiliary feedwater throttle valves. Additionally, some "swelling" occurred as saturation conditions existed in the steam generators. The operating procedure which allows drawing a vacuum in the steam generators for cooling purposes will be revised. There were no safety implications to the public as a result of this event. Unit 1 was in Cold Shutdown with the RHR system providing core cooling.
3341991004 | Beaver Valley 1 | 01/22/1991 | 02/19/1991 | 9102250139 | <strong>Containment Liner Test Channel Vents Found Unplugged</strong><br /><i>Abstract:&nbsp;</i>During a maintenance outage on 1/22/91, station personnel working in containment discovered a containment liner test channel vent line unplugged. Further inspections were initiated and found a total of 27 plugs missing. An additional 11 plugs, while in place, were found to be degraded due to corrosion. All the missing or degraded plugs were for test channels located on the liner floor. Twelve of the vent lines for these channels extended approximately two and a half feet above the floor, while the other 26 vent lines ended flush with the floor. All 26 of the channel vent lines that ended flush with the floor were sampled for liquid or corrosion products. Minor amounts of moisture (two to three drops) were found in two of the 26 channels. No indication of moisture was found in the other channels. Chemistry personnel verified that the two samples had neutral pH, but were unable to perform additional analysis due the limited sample quantity. No indications of liner corrosion or degradation were noted. All 38 vent lines were plugged with stainless steel plugs. An engineering analysis has been initiated to determine the potential for any effects to the containment liner due to this event.
3341991005 | Beaver Valley 1 | 01/31/1991 | 03/04/1991 | 9103060311 | <strong>ESF Actuation - Steam Generator Blowdown Isolation</strong><br /><i>Abstract:&nbsp;</i>On 1/31/91 at 0303 hours, blowdown from all steam generators isolated when blowdown containment isolation valves TV-BD-100A,B,C and blowdown sampling containment isolation valves TV-SS-117A,B,C closed. Steam, leaking past the seat of the normally closed steam supply trip valve, TV-MS-105A, to the steam-driven auxiliary feedwater pump caused the pump to develop a discharge pressure sufficient to cause automatic blowdown isolation. Steam supply to the pump was isolated by closing the upstream steam supply isolation valve (MOV-MS-105). The diaphragm of TV-MS-105A was replaced by Instrument & Control (I&C) technicians. The cause of this event was personnel error. The air supply to TV-MS-105A was set at 30 psi versus the required 50 psi. TV-MS-105A had insufficient air pressure to completely close against full secondary steam pressure. I&C personnel increased the air pressure to maintain the valve closed. This event will be reviewed by all I&C supervisors and technicians. There were no safety implications to the public as a result of this event. TV-BD-100A,B,C and TV-SS-117A,B,C are containment isolation valves which actuated to their required safety related positions.
3341991006 | Beaver Valley 1 | 02/11/1991 | 03/12/1991 | 9103150457 | <strong>ESF Actuation - Steam Driven Auxiliary Feed Pump Auto-Start and Blowdown Isolation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 2/11/91 at 1003 hours with the unit in Mode 1, Operating Surveillance Test (OST) 1.24.1 "Steam Generator Auxiliary Feedwater Pump Discharge Valves Exercise" was being performed when the Steam Driven Aux. Feed Pump (FW-P-2) Steam Supply Valve (TV-MS-105A) received an open signal. The Aux. Feedwater Pump Motor Operated Discharge Valves were being stroke tested from the Emergency Shutdown Panel when TV-MS-105A opened, initiating the start of FW-P-2 and Blowdown Isolation. Investigation revealed that the relay which transfers control of TV-MS-105A from the Control Room to the Emergency Shutdown Panel had spuriously actuated. Since the shutdown panel control switch for TV-MS-105A is maintained in the open position, TV-MS-105A immediately opened when the relay actuated. There were no safety concerns due to this event. Following actuation, the Auxiliary Feedwater System functioned as designed and was returned to normal system arrangement. The cause of the spurious relay actuation could not be determined.
3341991007 | Beaver Valley 1 | 02/28/1991 | 03/28/1991 | 9104010406 | <strong>Partial Loss of Battery Chargers Causing Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 2/28/91 at 1206 hours, numerous vertical board alarms indicated that the 480V emergency bus 1-8N was deenergized. Operators were dispatched to emergency switchgear to investigate the event. It was discovered that the 480V supply breaker 8N1 was open with a green target, indicating the breaker had been manually opened and had not tripped due to an electrical fault. The upstream 4kV supply breaker, 1E12, was found closed with no protective relays targeted. Breaker 8N1 was cycled satisfactorily in the test position to verify its correct operation and was racked onto the bus. The bus was reenergized and all loads were restored and independently verified by 1300 hours. Investigation into the event determined that the 8N1 breaker had been inadvertently tripped by a vendor procedure writer who was verifying alarm response procedures at the time. During the time from 1206 to 1221 hours, MCC1-E9 was deenergized, rendering Train A battery chargers 1-1 and 1-3 inoperable and causing entry into Technical Specification (TS) 3.0.3. There were no safety implications to the public as a result of this incident. The opposite train of safety systems was fully operable throughout the event.
3341991008 | Beaver Valley 1 | 03/11/1991 | 04/10/1991 | 9104150320 | <strong>Underrated Motor Termination Leads on Low Head Safety Injection Pump</strong><br /><i>Abstract:&nbsp;</i>On 3/11/91, during preventive maintenance, minor chaffing damage was found on the B train low head safety injection pump motor leads. Maintenance supervision also found an underrated motor termination installed. The underrated termination showed no signs of insulation breakdown but was rated for 1 KV as opposed to the required 4 KV. An appropriately rated termination was installed, the minor chaffing damage was repaired, and the motor was returned to service on 3/13/91. This underrated termination was apparently installed in June of 1986 when the motor was removed to repair a grease seal. The cause for this event was that the work request for this repair did not specify the use of procedures that addressed proper termination methods. A review of the maintenance history for all environmentally qualified motors was performed to identify any lead termination work. All termination work performed was satisfactory. There were no safety implications to the public as a result of this event. The A train low head safety injection pump motor terminations were inspected and found to be of the correct rating.
3341991009 | Beaver Valley 1 | 03/14/1991 | 04/10/1991 | 9104180185 | <strong>A Portion Of Chemical And Volume Control System Piping Not Hydrostatically Tested In Accordance With ASME XI</strong><br /><i>Abstract:&nbsp;</i>On 3/14/91, it was identified that full compliance to the American Society of Mechanical Engineers (ASME) section XI hydrostatic testing requirements during the First inspection Interval was not met. A portion of Class 3 piping in the Chemical and Volume Control System (CVCS) between the boric acid pumps and the charging pump suction line, was excluded from the site pressure testing program. The cause for this event was a program deficiency. The testing program was developed to address all safety related lines and piping using the Hydrostatic Testing (HAFA) Topical Report, Regulatory Guide 1.26 and the Final Safety Analysis Report (FSAR). A review of the completed Instrumented Inspection Technique (ITT) Program showed an inconsistency between the FSAR and Technical Specifications for the CVCS line, which resulted in this line being incorrectly classified and not included in the Testing Program. A reevaluation of all piping previously excluded from the ITT Testing Program is ongoing. An operability assessment of the excluded CVCS line was performed and the subject line was determined to be structurally sound and functionally operable. This line will be hydrostatically tested during the current inspection interval. There were no safety implications to the public as a result of this event. An evaluation of the subject line determined that the line is operable.
3341991010 | Beaver Valley 1 | 04/05/1991 | 09/11/1992 | 9209170032 | <strong>Inadvertent ESF Actuation of Safety Injection Valve During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 4/5191, operators were performing OST 1.1.12 (Safeguards Protection System Train B Test). At 1923 hours an unanticipated closure of Train B Low Head Safety Injection Pump minimum flow line isolation valve, MOV-SI-885B, occurred. Operators terminated the test at 2019 hours and manually opened MOV-SI-885B from the control board. Instrumentation and Control Technicians investigated this event and determined that contact pair 3-4 of Solid State Protection System relay K641B had failed, allowing current to pass while the contacts were supposed to be open. Failure of this contact pair caused valve MOV-SI-885B to close. Technicians then replaced contact pair 3-4 in relay K641B. This failure only affected Train B Low Head Safety Injection Pump recirculation capability. The pump would have been fully capable of performing its design function in the event of a large break LOCA where recirculation flow is not required. The Train A System was operable throughout the event. The failure of one train of safety injection is bounded by analysis in Beaver Valley's UFSAR Section 6.3.1.2, "ECCS Single Failure Criterion Compliance".
3341991011 | Beaver Valley 1 | 04/08/1991 | 05/08/1991 | 9105130368 | <strong>Failure of Safeguards Pit Ventilation Isolation Damper</strong><br /><i>Abstract:&nbsp;</i>On 4/8/91, Maintenance was inspecting the train A Safeguards Pit Ventilation Isolation Damper VS-D-4-11A (manufactured by Shan-Rod, model number 4320). The inspection was being performed in response to a previously identified potential failure of Shan-Rod damper spline adaptors. During this inspection, it was discovered that the spline adaptor keyed on the damper shaft had slipped out of position and moved along the damper shaft. This movement was sufficient to allow the adaptor to disengage from the motor operator drive gear. With the spline adaptor not engaged to the drive gear, the damper position could not be changed by the motor. The train B series damper was tested and verified to be functioning properly. maintenance reset the spline adaptor to its correct position. Operations tested the train A damper and verified it was operating properly on 4/9/91. An engineering modification is being developed to prevent future adaptor movement. There were no safety implications due to this event as the train B series isolation damper was fully functional throughout the event and capable of performing the necessary isolation function.
3341991012 | Beaver Valley 1 | 04/15/1991 | 05/15/1991 | 9105210470 | <strong>Excessive Maximum Operating Pressure Differential Selected Solenoid Operated Valves</strong><br /><i>Abstract:&nbsp;</i>On 4/15/91, with the Unit in Cold Shutdown at 150 counts per second, a solenoid valve (SOV) walkdown being performed in response to an information notice, identified a design deficiency with six air operated solenoid valves. The design deficiency involved the use of air operated solenoid valves in applications where the maximum operating differential pressure on the valves was exceeded. The six valves are located in the auxiliary feedwater systems, the primary grade water system and the condenser air ejector system. In each application, the incoming air supply pressure resulted in the maximum operating differential pressure across the air operator being exceeded. The solenoid valves are Automatic Switch Company (ASCO) Models NP8320A189E and FT8320A12. This event was caused by design deficiencies. An equipment modification to replace the solenoid valves with valves rated for operation at higher differential pressures is being performed during the eighth refueling outage. There were no safety implications as a result of this event. Although the valves were identified as being subjected to higher than designed differential pressures, there have not been any operational problems associated with these valves.
3341991013 | Beaver Valley 1 | 05/10/1991 | 06/07/1991 | 9106120117 | <strong>Pressurizer Code Safety Valve Lift Setting Less Than Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On 5/2/91, with the Unit in Refueling, the "C" Pressurizer Code Safety Valve (RV-RC-551C) was tested by Wyle Laboratories in accordance with Beaver Valley Test Procedure (BVT) 1.60.05 "IST - Safety and Relief Valve Tracking." In two of three lift tests, the valve actuated at pressures outside the Technical Specification lift setpoint of 2485 psig 3 percent (2509.8 psig/2410.5 psig). The "as-found" setpoints were: 2431, 2402 and 2373 psig. As a result of the lift test on RV-RC-551C, the "A" Pressurizer Code Safety Valve (RV-RC-551A) was tested on 5/10/91. In one of the three lift tests, this valve also actuated at a pressure outside the lift setpoint tolerance of 3 percent. The "as-found" setpoints were: 2409, 2429 and 2425 psig. The valves were left with Wyle Laboratories for repair and resetting of valve lift pressure to 2485 psig 1 percent. The apparent cause for the failure of the valves to meet the lift setpoint on three successive lifts was setpoint drift. The valves were reset to within 1 percent of the lift setpoint. There were no safety implications as a result of this event. The lift point for RV-RC-551C was found within specification on the first and conservatively low on the second and third lifts. The lift point on RV-RC-551A was found conservatively low on the first lift test and the two subsequent lifts were within specifications.
3341991014 | Beaver Valley 1 | 05/02/1991 | 05/31/1991 | 9106050225 | <strong>Technical Specification Surveillance Testing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 5/2/91, it was discovered that Operations Surveillance Test (OST) 1.44C.1, Containment Purge And Exhaust Isolation Test, did not direct the operators to verify that a containment purge and exhaust isolation would occur on manual initiation as required by Technical specification surveillance 4.9.9. This OST is required to be performed within 150 hours prior to the start of and at least once per seven days during core alterations. A review of the performance history of this OST revealed that on 10/14/89, during our seventh refueling outage, core alterations were performed without proper verification of containment purge and exhaust isolation on manual initiation. In the eighth refueling outage no core alterations were performed without verification of manual initiation. However, on several occasions during the seventh and eighth refueling outages the surveillance requirements were satisfied by means other than the performance of OST 1.44C.1. Although previous revisions of this procedure required the proper verifications, a procedure revision was put into effect on 8/16/89 which inadvertently deleted the requirement to verify manual initiation. From 8/16/89 until 5/3/91, only one core alteration was performed without verifying manual initiation of the purge and exhaust isolation. The automatic isolation function was verified operable on all applicable occasions.
3341991015 | Beaver Valley 1 | 05/17/1991 | 06/17/1991 | 9106210033 | <strong>Control Room Ventilation System Outside Air Exhaust Dampers Inadvertently Opened</strong><br /><i>Abstract:&nbsp;</i>On 5/17/91, an operator performing a walkdown of the Unit 1 Control Room Ventilation system found the two outside air series exhaust dampers open. These dampers had been closed during the Unit 1 refueling outage, but were required to be maintained closed to support continued power operation at Unit 2 since the two Units share a common control room ventilation envelope. The operator notified the Nuclear Shift Supervisor and immediately closed the dampers. Investigation determined that one of the dampers had been opened on 5/16/91 when it apparently was inadvertently energized momentarily after its motor control center was cleaned. The dampers are designed to open when energized without a closure signal present. The other damper was apparently opened due to the same cause between 5/4/91 and 5/17/91. The exact date for this damper opening could not be determined due to a failure of the computer point associated with its position indicating limit switches. An INPO Human Performance Enhancement System evaluation of this event was conducted. Station procedures have been revised to require locking the dampers' breakers off their bus. Repairs of the computer inputs from the damper's limit switches has been initiated. During the period from 5/16 to 5/17 when both these dampers were open, the joint Unit 1/Unit 2 control room envelope could not have been automatically isolated.
3341991017 | Beaver Valley 1 | 05/16/1991 | 06/17/1991 | 9106200281 | <strong>Incorrect Calibration of Vertical Movement Seismic Accelerometer</strong><br /><i>Abstract:&nbsp;</i>On 5/16/91, an Instrumentation and Control (I&C) engineer reviewing the calibration procedure for the seismic event Peak Recording Accelerometers, noted an apparent discrepancy in the calibration method for the vertical axis recorder. The vendor was contacted and confirmed that the method the station was using to calibrate the vertical axis was incorrect. Incorrect calibration methods caused the vertical axis recorder to be inoperable. The two horizontal axes, which use a different calibration method, were being calibrated correctly. The calibration method for the vertical axis was corrected. Investigation determined that the incorrect calibration method had been in use since initial plant operation. When writing the initial procedure, an apparent misunderstanding of the calibration requirements for the vertical axis resulted in an attempt to calibrate the vertical axis using a similar methodology used for the two horizontal axes. There were no safety implications due to this event. In addition to the Peak Recording Accelerometer seismic instrumentation, the station also has two other independent seismic instrumentation systems that are capable of recording motion on all three axes.
3341991018 | Beaver Valley 1 | 06/06/1991 | 07/08/1991 | 9107120147 | <strong>Auxiliary Feedwater Pump Flow Indicating Switches As-Found Configuration not Supported by Seismic Analysis</strong><br /><i>Abstract:&nbsp;</i>During the Eighth Refueling Outage, with the unit in cold shutdown (Mode 5), engineering performed a seismic qualification inspection of the auxiliary feedwater pump's recirculation valve flow switches (FIS-FW-151A, B, and 152). During the inspection, on 6/6/91, it was discovered that terminal boxes, weighing approximately two pounds, were directly attached to the switches. This was in disagreement with the manufacturer's seismic qualification reports which documented that the switches were tested with smaller terminal boxes (weighing approximately three-quarters of a pound) or with no terminal boxes attached. An investigation determined that the switches and terminal boxes were installed as part of a design change (DCP 130) in 1980. The auxiliary feedwater system is required to be operable in Modes 1, 2 and 3. The seismically unqualified flow switches may have caused misoperation of the recirculation flow control valves during a seismic event. Therefore the operation of the auxiliary feedwater system was potentially degraded since installation of the design change in 1980. A design change was immediately initiated, moving the terminal boxes from the switches and supporting them independently. This work was completed on 7/3/91, prior to the unit entering Mode 3.
3341991019 | Beaver Valley 1 | 06/18/1991 | 01/07/1993 | 9301130080 | <strong>Missed Weld Examinations Determined After Mode Escalations Resulting in Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 7/9/91 at 1230 hours, with the unit in Hot Shutdown, a cooldown to Cold Shutdown was initiated when it was determined that the surveillance frequency for the American Society of Mechanical Engineers Section XI Non Destructive Examination (NDE) (1978-1988) requirements during the First Ten Year Inspection Interval was exceeded. Several longitudinal welds on welded fittings in the Low Head Safety Injection System, the Residual Heat Removal System, and the High head Safety Injection System were inadvertently excluded from the First Ten Year Interval NDE inservice inspection program. The longitudinal welds were not included on the isometric drawings that were used to formulate the NDE inservice inspection program. An inadequate review of the piping spool piece drawings and associated Component Certified Mill Test Reports supplied during the original construction from the piping fabricator resulted in the development of incomplete isometric drawings. All required welds have been inspected with no indications found. A review of piping spool piece drawings from original fabrication was performed to verify that all required longitudinal welds in fittings are included in the NDE inservice inspection program. There were no safety implications to the public as the Unit was shutdown in accordance with Technical Specifications and all of the inspected welds are acceptable.
3341991020 | Beaver Valley 1 | 06/22/1991 | 07/22/1991 | 9107250262 | <strong>Inoperable Hydrogen Recombiner due to Incorrect Thermocouple/Control Circuit Wiring</strong><br /><i>Abstract:&nbsp;</i>At 1600 hours on 6/22/91 with the plant in mode 5, test data was taken on the A-train Hydrogen Recombiner. This data was taken for comparison purposes while troubleshooting an apparent temperature discrepancy that had occurred on the B-train recombiner. Thermocouple pairs TE-3A and 3B for the A-train recombiner detect process flow temperature at the heater outlet and TE-4A and 4B measure reaction chamber temperature. As the thermocouples are in redundant pairs, temperatures on thermocouples 3A and 3B should agree closely, as should those on 4A and 4B. However, TE-3A and 4B were in agreement, as were TE-3B and 4A. This indicated that thermocouple leads were reversed. Since the heater outlet temperature increases faster than reaction chamber temperature on system startup, it was confirmed that the leads for TE-3A and 4A were reversed. The miswiring was corrected by changing the leads at the recombiner control panel. With the leads in the as-found condition, the vendor indicated that operation of the recombiner might have been unstable and could have tripped prematurely. The "A" Hydrogen Recombiner was considered inoperable until the wiring was corrected. This degraded recombiner had existed at least since a design change was implemented in 1986 and most likely since original construction.
3341991021 | Beaver Valley 1 | 07/18/1991 | 09/06/1991 | 9109110025 | <strong>Manual Control Rod Insertion By Opening of Reactor Trip Breakers</strong><br /><i>Abstract:&nbsp;</i>On 7/18/91 the plant was critical in Mode 2 while the Testing and Plant Performance group was performing their Core Design Check Test procedure. Criticality had been achieved by the withdrawal of Control Bank D rods to 215 steps. Control Bank D rods were then moved in and out several times, per the procedure, in order to determine an Isothermal Temperature coefficient (ITC). At 0445 hours an ITC was determined and found to be within the acceptance criteria. In order to prepare for the next portion of the test procedure, Control Bank D was to be withdrawn to 228 steps and Control Bank B was to be inserted while maintaining the reactor critical. At 0450, Control Bank D was withdrawn, adding a small amount of positive reactivity, but when Control Bank B was selected and demanded to insert the Rod Control System Urgent Alarm came in. Only group two of Control Bank B began to move. The Reactor Operator then borated approximately 50 gallons to stop the power increase. This took the reactor subcritical and brought the plant into Mode 3. The test was suspended. An investigation revealed that a fuse and its fuse indicator were blown in the 1BD Power Cabinet. At 0723 all control rods were inserted by manually opening the Reactor Trip Breakers. There were no safety implications as a result of this event. The shutdown margin was verified and the control rods were able to be tripped.
3341991022 | Beaver Valley 1 | 07/20/1991 | 08/19/1991 | 9108220168 | <strong>Reactor Trip and Feedwater Isolation due to Steam Generator Level Control Malfunction</strong><br /><i>Abstract:&nbsp;</i>On 7/20/91, the station was at 21 percent power and preparing to increase load. The operators placed the Main Feedwater Regulating Valves (MFRV) in service using the Station Startup Procedure. When the C MFRV was placed in operation, it opened rapidly, causing C steam generator level to increase to the Hi-Hi Level/Feedwater Isolation (FWI) setpoint. The main turbine and feedpump tripped and the FWI valves closed. Level in the A steam generator decreased to the Lo-Lo Level/Reactor Trip setpoint. All control rods automatically fully inserted. Auxiliary feedwater initiated in response to the main feedpump trip and Lo-Lo steam generator levels. One auxiliary feed recirculation valve failed to open, but did not affect auxiliary feed operation. Investigation found the control circuit for the C MFRV had been mis-wired during a recent control loop calibration. The control circuit was rewired and the other MFRV circuits were checked and verified to be correctly wired. A Human Performance Enhancement System evaluation of this event has been initiated. This event will be covered in Instrumentation personnel training. There were no safety implications due to this event. A FWI due to Hi-Hi steam generator level and a reactor trip due to Lo-Lo steam generator level are bounded by Feedwater System Transient analyses in Beaver Valley's UFSAR sections 14.1.8 and 14.1.9.
3341991023 | Beaver Valley 1 | 07/27/1991 | 12/18/1991 | 9112260288 | <strong>Reactor Trip Due To Electro-Hydraulic Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>On 7/26/91 at 1930 hours in operating Mode 1 at 30 percent power, the unit began to experience turbine governor control oscillations from the turbine Electro-Hydraulic Control (EHC) system. Between 1930 hours 7/26/91 and 0655 hours 7/27/91, three load rejections of between 100 and 150 MWe were experienced. Operators stabilized the plant after each load rejection. EHC troubleshooting by plant personnel and contractor technicians began after the first occurrence. After the third occurrence, station management decided to remove the turbine from service in accordance with the Abnormal Operating Procedure for a load rejection. During preparations for shutdown, a fourth load rejection, accompanied by erratic turbine governor valve control, occurred. The reactor tripped at 0713 hours, due to a low level coincident with a low feedwater flow in the "B" steam generator. Control room personnel stabilized the plant in Operating Mode 3. The spurious governor valve signals were due to a faulty circuit card in the EHC system. There were no safety implications to the public as a result of this event. All shutdown and control rods inserted, and all plant systems responded as designed.
3341991024 | Beaver Valley 1 | 07/27/1991 | 08/26/1991 | 9108290075 | <strong>Generation of Feedwater Isolation and Letdown Isolation Signals</strong><br /><i>Abstract:&nbsp;</i>On 7/27/91, the station was in Mode 3 following a reactor trip due to turbine control problems (LER 1-91-23). Instrument and Control personnel were troubleshooting problems with the B loop Bypass Feedwater Regulating Valve. Troubleshooting was being performed using the control loop calibration procedure as a guide. The procedure directed the signal leads from the control loop to the valve be lifted. This removed the ability to remotely operate the valve and allowed I&C personnel to perform troubleshooting on the valve control circuit without causing valve movement. Due to a combination of poor communications and procedural deficiencies, when the leads were relanded to restore the control loop to service, an open demand signal was present. This caused the valve to open, resulting in an overfeed of the B Steam Generator. The control room operators noted the increasing water level and manually aligned all components to their feedwater isolation positions. in addition, the resultant Reactor Coolant System cooldown caused pressurizer level to decrease and the reactor operator manually isolated RCS letdown in response. After the manual alignments were accomplished, steam generator level and pressurizer level parameters were exceeded causing the Feedwater Isolation signal and Letdown Isolation signal to be generated.
3341991025 | Beaver Valley 1 | 09/08/1991 | 10/07/1991 | 9110110009 | <strong>Computer Failure Renders Axial Flux Difference Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 9/8/91 at 0459 hours, while operating at 100 percent power, a plant computer (P250) malfunction rendered the Axial Flux Difference (AFD) Monitor Alarm inoperable. Technical Specifications require logging AFD when this alarm is inoperable. Since the operations staff was unaware that the alarm was inoperable, they did not start logging AFD. Later that same day at 0945 hours, the P250 printer failed. The operations staff contacted the computer engineer for assistance in restoring the printer function. Following his advice, the P250 computer was restarted at 1011 hours. Although the printer could not be restored, the computer restart restored the AFD Monitor Alarm's operability. On 9/9/91 at 0800 hours, the computer engineer noted an error message describing the failure that rendered the AFD monitor inoperable on his programmers' console and informed Operations of this failure. It was determined that from 0459 to 1011 on 9/8/91, the plant operated in a condition prohibited by Technical Specifications.
3341991026 | Beaver Valley 1 | 09/09/1991 | 04/27/1992 | 9205010274 | <strong>Potentially Inoperable Charging Pump Due to Missing Nuts on High Speed Coupling</strong><br /><i>Abstract:&nbsp;</i>This revision is being submitted to reflect a second engineering evaluation of coupling performance during a seismic event and to revise the root cause of the event.<br /><br /> On 7/26/91, station mechanics were performing preventive maintenance on the "B" charging pump. When the coupling guard was removed, it was noticed that the nuts for the pump side spool piece coupling were not attached to the bolts but were lying in the bottom of the coupling guard. Maintenance had been performed on the pump on 6/28/90 and again on 7/05/90. A review of copies of the maintenance procedures used indicated that the coupling was most likely installed improperly following the first of these maintenance activities. The procedures will be revised to specifically address torquing bolts on both coupling halves. After completing the 7/26/91 maintenance, the nuts were installed on the bolts and torqued to specifications.<br /><br /> On 9/9/91, the initial engineering evaluation concluded, that if the charging pump were running during a seismic event, the coupling should remain intact during the event. If the pump were idle during the earthquake, afterward the coupling might not function if the pump were started. However, on 11/25/91 a subsequent analysis, taking the actual reassembly methods into account, concluded the coupling would remain intact during a seismic event in any operating condition.
3341991027 | Beaver Valley 1 | 09/26/1991 | 10/28/1991 | 9111040203 | <strong>Insufficient Diesel Generator Fuel Oil Supply</strong><br /><i>Abstract:&nbsp;</i>The unit was operating at 100 percent power when the Electrical Distribution System Functional Evaluation Team (EDSFE) identified a concern with the fuel oil supply to the emergency diesel generators. There are two underground fuel oil storage tanks, each with a capacity of 20,000 gallons. The capacity of both tanks together is adequate for more than seven days of full load operation of one diesel generator as required by the UFSAR. However, in the event of a loss of one emergency bus, the affected train of transfer pumps would not be available to supply fuel oil to the opposite train diesel generator. The train A pumps (EE-P-1A, 1B) take suction from the A storage tank (EE-TK-1A) and normally supply the train A diesel generator. The train B pumps (EE-P-1C, 1D) take suction from the B storage tank (EE-TK-1B) and normally supply the train B diesel generator. Thus, in the event of a loss of one emergency bus, only one half of the required supply of fuel oil would be available to the operable diesel generator (approximately three and one half days' worth).
3341991028 | Beaver Valley 1 | 10/02/1991 | 11/01/1991 | 9111070086 | <strong>Inoperable Overpressure Protection Due to Inadequate Seismic Qualification</strong><br /><i>Abstract:&nbsp;</i>On 10/2/91, with the unit at 100 percent power, the Overpressure Protection system (OPPS) was declared inoperable due to inadequate seismic qualification. Upon reviewing a vendor supplied 10CFR21 report, the station determined that relays associated with the OPPS, were installed in Auxiliary Relay Racks (ARRs) which are not seismically qualified. Since the OPPS, utilizing the power operated relief valves (PORV), is a seismic, Category I system, it was declared inoperable. This report is being submitted in accordance with 10CFR50.73.a.2.i.B, as a condition prohibited by Technical specifications. The OPPS had been assumed operable, during all applicable modes, since it's original installation. This resulted in several instances when the OPPS function supplied by the PORVs was potentially inoperable. The OPPS is required to be in service whenever the Reactor Coolant System (RCS) temperature is at or below 292 degrees Fahrenheit. On 10/23/91 the unit was shutdown to Cold shutdown for unrelated reasons. While in Cold Shutdown, a modification which utilized spare relays in adjacent, seismically qualified, Auxiliary Safeguards Cabinets was completed for the susceptible relays. On 10/26/91, following completion of the design change, the OPPS was declared operable.
3341991029 | Beaver Valley 1 | 11/06/1991 | 12/06/1991 | 9112100235 | <strong>Auxiliary Feedwater Pump Actuation Due to Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On 11/6/91 while in Mode 3, heat up of the Reactor Coolant System (RCS) was terminated and a plant cooldown to Mode 5 was commenced. Steam generator levels were being maintained with condensate pump flow through the bypass feedwater regulating valves. A main steam isolation valve bypass valve was opened to facilitate the RCS cooldown. Concurrently, steam generator blowdown system flow was increased to aid in steam generator chemistry control. Steam generator levels began to decrease. Operators took manual control of the bypass feedwater regulating valves but were unable to restore steam generator level. Generator level continued to decrease until the A steam generator reached the low-low level setpoint and started the steam driven auxiliary feedwater pump. Steam generator levels were restored to normal prior to securing the auxiliary feedwater pump. The cause of the event was due to a lack of secondary flow to the steam generators. Condensate flow was ineffective due to the steam generator pressure being near the shutoff head of the condensate pumps. At no time was the margin of safety to the general public reduced, as the auxiliary feedwater pump started as designed. The event will be reviewed in a future operator licence retraining session.
3341991030 | Beaver Valley 1 | 11/08/1991 | 12/09/1991 | 9112160079 | <strong>Inadequate Filter Bank Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 11/8/91 during a management reevaluation of Safety System Functional Examination (SSFE) audit findings, a reportable finding, concerning an unconservative test method for determining the Supplementary Leakage Collection and Release System (SLCRS) Filter removal efficiency was identified. The test method in place at that time only determined filter bank removal efficiency and excluded bypass damper leakage effects which would lower the systems' overall efficiency. Therefore, the systems' overall removal efficiency may not have met Technical specification requirements. Upon issuance of the SSFE finding, it was determined that if bypass damper leakage was less than 500 CFM then required limits would not have been exceeded. Actual leakage measurements verified that this leak rate was not exceeded. After revising the test method to account for bypass damper leakage, both trains of SLCRS filter banks were satisfactorily tested. The SSFE is an ongoing internal self-assessment process.
3341991031 | Beaver Valley 1 | 11/14/1991 | 12/12/1991 | 9112170303 | <strong>Engineered Safety Features Actuation - Auto Start of 1B River Water Pump During Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On 11/14/91, with the Unit in Operating Mode 5 (Cold Shutdown), electricians began performance of a preventive maintenance procedure (PMP) on Cubicle E14 on the 1AE 4160 Volt Emergency Bus. This cubicle is one of the breakers used for the 1C river water (RW) pump. During the performance of the PMP, a spring clip was observed lying on the cubicle floor near the cell switch linkage. While replacing the clip, the electricians inadvertently actuated the cell switch. Because of a mechanical interlock, this caused the running 1A RW pump to trip and the standby 1B RW pump to start on low header pressure. The cause for this event was personnel error. The 1A RW pump was restarted and the 1B RW pump was shutdown. This event will be reviewed by maintenance personnel. There were no safety implications as a result of this event. The standby RW pump immediately started upon loss of the running RW pump. River water cooling flow was maintained at all times.
3341991032 | Beaver Valley 1 | 12/03/1991 | 01/02/1992 | 9201070363 | <strong>Inadequate Ventilation Flow from High Head Safety Injection Pump Cubicles</strong><br /><i>Abstract:&nbsp;</i>On 12/3/91 with the unit in Power Operation at 100 percent power, ventilation concerns involving the High Head Safety Injection (HHSI) pumps led to the determination that the plant's safe shutdown capability was potentially degraded. The actual measured ventilation flow from each HHSI pump cubicle was found to be less than the flow-rate required by the calculations to maintain motor temperatures within required Environmental Qualification limits. An investigation determined that a manual isolation damper, common to all three HHSI pumps, was failed in a partially closed position. The damper was repaired and placed in the proper position to meet flow requirements. The Nuclear Regulatory Commission was notified in accordance with 10 CFR 50.72.b.2.iii.A and this report is being submitted in accordance with 10 CFR 73.a.2.v.A as a condition that potentially could alone have prevented safe reactor shutdown. There was no adverse impact to the safety of the public as a result of this event.
3351991001 | St. Lucie 1 | 01/28/1991 | 02/26/1991 | 9103050506 | <strong>Inadvertent Actuation Of Reactor Protection System During Mode 3 Testing Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1991, at 1136, with Unit 1 in mode 3 for scheduled Control Element Assembly testing, an inadvertent actuation of the Reactor Protection System occurred during Reactor Protection System testing. The actuation occurred on High Startup Rate, channels A and B. The Trip Circuit Breakers opened, and one Control Element Assembly inserted. The reactor was already subcritical, and the event had no effect on plant operation. <br /><br /> The root cause of the event was cognitive personnel error. A utility licensed operator inadvertently adjusted the wrong trip test potentiometer during Reactor Protection System Loss of Turbine testing. <br /><br /> Corrective actions: Utility licensed operators restored the incorrectly positioned potentiometer to its correct position and closed the Trip Circuit Breakers. Scheduled testing was resumed. An INPO Human Performance Enhancement System review was performed on this event. The operator was counseled. An Operator Self Verification program had recently been introduced in order to reduce personnel error. As this policy is fully implemented and all operators become familiar with it, the frequency of such errors should be reduced.
3351991002 | St. Lucie 1 | 02/19/1991 | 03/18/1991 | 9103260168 | <strong>Unplanned Actuation of Auxiliary Feedwater System Components Due to Personnel Error While Troubleshooting Problem Discovered During Monthly Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1991 with Unit 1 at 100% power, an unplanned actuation of the Auxiliary Feedwater System (AFW) occurred. While troubleshooting a problem uncovered during the monthly functional testing, the Steam Admission Valve from the 1B Steam Generator (S/G) and the Trip and Throttle Valve to the turbine of the 1C AFW Pump both showed "open" indication and the 1C AFW Pump started. Troubleshooting was suspended and the AFW System components were restored to their normal status. There was no injection of Auxiliary Feedwater into the Steam Generators.<br /><br /> The root cause of the event was personnel error on the part of Plant Instrument and Control (I&C) personnel. While troubleshooting the AFW System to determine the cause of a failed light on the Auxiliary Feedwater Actuation System (AFAS) Channel D Initiation Relay, the incorrect fuse was pulled, resulting in the inadvertent actuation of AFW System components. <br /><br /> The Corrective Actions implemented as a result of this event are: 1) Engineering will revise the vendor technical manual to clarify the fuse designations and provide separation on the circuit schematic to indicate they are not located in the same fuse box. 2) As part of the Engineering Request, fuse maps will be provided to facilitate the location of fuses within the confines of each channel bay. These will be incorporated into the AFAS technical manual. 3) Personnel involved were counselled on the importance of using required Sensitive System procedures when working on such designated systems. 4) A Human Performance Enhancement System (HPES) review of the event was performed.
3351991003 | St. Lucie 1 | 05/06/1991 | 06/04/1991 | 9106110130 | <strong>Manual Reactor Trip Following a Turbine Runback Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1991, St. Lucie Unit 1 was in Mode 1 and holding power at 96% to complete a Nuclear Delta-T Power Calibration before resuming full power operation following a scheduled shutdown. The 1A Heater Drain Pump tripped at 0508 and, four seconds later, the 1A Steam Generator Feedwater Pump tripped causing a turbine runback. The unit was manually tripped at 0509 at the direction of the Nuclear Plant Supervisor in anticipation of an automatic reactor trip and Standard Post Trip Actions were performed. The unit was then stabilized in Mode 3, Hot Standby. <br /><br /> The manual reactor trip was the result of a turbine runback initiated when both the 1A Heater Drain Pump and the 1A Steam Generator Feedwater Pump tripped. An investigation revealed a possible grounding of the 5A Feedwater Heater Hi-Hi level switch which, in turn, opened Circuit Breaker 27 on the 120 VAC Vital Static Uninterruptible Power Supply. This would have caused the normal drain valves to close on several secondary Feedwater Heaters and the alternate drain valves to open. It was also found that the pressure sensing element setpoint for the 1A SGFP had drifted high from the normal value of 275 psig to 291 psig. The end result was a low suction pressure condition on the Feedwater Pump suction line and the trip of the 1A Steam Generator Feedwater Pump on low suction pressure. <br /><br /> The immediate Corrective Actions implemented as a result of this event include: testing and replacing Circuit Breaker 27 as a precautionary measure, cleaning and testing the 5A Feedwater Heater Hi-Hi level switch, and lowering the setpoint of the 1A Steam Generator Feedwater Pump to its normal value of 275 psig.
3351991004 | St. Lucie 1 | 05/16/1991 | 06/14/1991 | 9106210300 | <strong>Late Technical Specification Required Fire Watch Patrol due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 16 May, 1991, while operating at 100% power, St. Lucie Unit 1 experienced a late fire watch patrol of the shield building annulus area. Due to modifications being performed to the Unit 1 Fire Detection system, the "B" side Fire Detection system was out of service, for which Technical Specification 3.3.3.7 requires an 8 hour fire watch inspection of the shield building annulus. A concurrent 10 hour surveillance run of a shield building exhaust fan created a differential pressure across the annulus door that made it impossible to open and gain access to perform the inspection. Upon notification of this condition, the control room senior reactor operator assumed that the fire watch was required shiftly rather than every 8 hours, and continued the exhaust fan surveillance. When the site Fire Protection department later notified the control room that the fire watch was late, operators secured the 6B Shield Building Exhaust fan to allow the fire watch to be performed. <br /><br /> The cause of this event was personnel error. The surveillance run of the shield building exhaust fan interfered with the scheduled fire watch, resulting in the fire watch time interval being exceeded. <br /><br /> Corrective actions for this event were to secure the shield building exhaust fan to allow access to the annulus, perform the required fire patrol, and deter the exhaust fan surveillance until the B side Fire Detection system was placed back in service. The Training Department will review this event for possible incorporation into the Licensed Operator Requalification Training program, and Control Room supervision will receive counselling on correct interpretation of Technical Specification fire watch requirements.
3351991005 | St. Lucie 1 | 07/01/1991 | 07/29/1991 | 9108070110 | <strong>Reactor Trip from 100% Power on Low Steam Generator Water Level caused by a De-energized Feedwater Regulating Valve due to a Deficient Procedure.</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1991, St. Lucie Unit 1 was operating in Mode 1 at 100% power. Utility Maintenance personnel were attempting to remove LIC-9013-B, the Channel B narrow range level indicator for the 1A Steam Generator. At 1137 FIC-9011, the 1A Feedwater Regulating Valve Digital Controller, lost all power. The 1A Steam Generator water level decreased, and the Reactor Control Operator opened the 100% Main Feedwater Bypass Valve in an attempt to regain level. At 1138 the reactor tripped automatically on low level in the 1A Steam Generator. Standard Post-Trip Actions were performed, and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause of this event was due to a deficient procedure which did not completely isolate electrical power to LIC-9013-B during maintenance. With this indicator controller unisolated, two leads were inadvertently shorted, resulting in an overload and blown power supply fuse. As transfer to the back up power supply occurred, that power supply's breaker tripped resulting in a complete loss of power to FIC-9011. This loss of power resulted in a close demand signal from the controller to the 1A Feedwater Regulating Valve. The Feedwater Regulating Valve went closed, and water level decreased in the 1A Steam Generator to the reactor trip setpoint. <br /><br /> Corrective actions as a result of this event: a revision of plant maintenance procedures to direct the isolation of power to the steam generator level indicators, and a procedure revision to require supervisory and department head review of proposed work on sensitive systems. Also, a plant modification for replacing the steam generator level indicators with a model which has pin type connectors is under consideration.
3351991006 | St. Lucie 1 | 09/18/1991 | 10/15/1991 | 9110250031 | <strong>Reactor Trip During Control Rod Drive Motor-Generator Set Synchronization Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 18 September, 1991, with Unit 1 in mode 1 at 100%, operators prepared to return the 1A Control Element Drive Mechanism (CEDM) Motor Generator (MG) set to service following maintenance on its flywheel bearing. At 1043, while a utility non-licensed operator was manually synchronizing the 1A MG set to the CEDM bus, the generator output breaker was closed out of phase with the running MG set. This resulted in an instantaneous overcurrent condition on the CEDM bus. The overcurrent condition opened 7 Trip Circuit Breakers (TCBs) and removed power to the CEDMs. All Control Element Assemblies (CEAs) then fully inserted. The main turbine automatically tripped upon sensing an undervoltage condition on the CEDM bus and the 2 remaining TCBs opened. The operators then implemented Standard Post Trip Actions, and the normal Reactor Trip Recovery procedure. <br /><br /> The root cause for the out of phase synchronization of the MG set was that a non-licensed operator made a personnel error while attempting to manually synchronize the 1A MG set to the CEDM bus. The non-licensed operator closed the generator output breaker out of phase while he was in an incorrect section of the procedure. Contributing factors to this event included: on the scene supervision of this load threatening activity was absent, a lack of specific technical knowledge by the operator, no pre-evolution brief between maintenance and operating personnel was held, and the procedure for MG set operation contained some human factor deficiencies. <br /><br /> Corrective actions were to: counsel the individuals involved on this event, emphasize the importance of on the scene supervision and pre-evolution briefings, provide additional training on MG set operation to non-licensed operators, revise the procedure for CEDM MG Set Operation, and verify the proper operation of the 1A MG set.
3351991007 | St. Lucie 1, St. Lucie 2 | 11/04/1991 | 12/02/1991 | 9112110066 | <strong>Diesel Generators Administratively Declared Out of Service Because of Particulate Contamination in the Diesel Fuel Oil Due to Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991 St. Lucie Nuclear Unit 1 was in Mode 6 (Refueling) and Unit 2 was in Mode 1 at 100% power when sample results telephoned from an off-site contract laboratory indicated out of specification particulate contamination in three of the four diesel fuel oil storage tanks (FOSTs) on site. Both the Unit 1 FOSTs and the 2B FOST contained greater than 10.0 milligrams per liter (mg/l) particulates. As a result of this, the 1A, 1B, and 2B Emergency Diesel Generators were administratively declared out of service. A mobile filtration system was brought in from a vendor to recirculate the fuel oil in the tanks and filter out the particulate contamination contained in the fuel oil. The FOSTs were cleaned and returned to service within the time limits of the applicable Technical Specification Action Statement on both units. <br /><br /> This event was caused by the use of a contaminated fuel oil tanker truck transfer pump and hose during the receipt of diesel fuel oil on October 10, 1991. The root cause of this event is procedural deficiencies in plant Chemistry procedures. The corrective actions undertaken as a result of this event are as follows: 1) The Chemistry procedures have been changed to eliminate the discrepancies discovered during this event, and make enhancements to ensure a similar event will not occur. 2) The first 100 gallons of all fuel oil shipments received will be flushed into drums. 3) A filtration unit is being purchased which will be installed on the fuel oil tanker discharge hose to trap any possible particulate contamination after flushing into the drums. 4) American Society of Testing and Materials (ASTM) Standard 2276-83 particulate testing will be performed on the fuel oil tanker for all shipments prior to transferring any fuel oil into the site FOSTs until the filtration unit is installed. 5) The Chemistry Department is having an outside vendor conduct a review of all other diesel fuel oil analytical techniques to ensure compliance with the ASTM Standard.
3351991008 | St. Lucie 1 | 11/10/1991 | 12/09/1991 | 9112170467 | <strong>Core Alterations Performed With Containment Integrity Not in Compliance With Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Between 1430 on November 10, 1991, and 0210 on November 11, containment integrity was not in compliance with Technical Specifications. St. Lucie Unit 1 was in Mode 6, Refueling, and fuel assemblies were being moved in the reactor core. Containment integrity is required for core alterations. <br /><br /> The cause of the incomplete containment integrity was personnel error by Mechanical Maintenance department personnel for failure to follow an approved procedure. Plant procedure requires that Nuclear Plant Work Orders be approved by the Nuclear Plant Supervisor prior to starting work. Without obtaining this prior approval, maintenance workers removed a relief valve on one side of a containment penetration while a drain valve was open on the other side. This created a direct flow path from containment to the Reactor Auxiliary Building. Permission to start work was requested after the relief valve had been removed by the previous shift. <br /><br /> Corrective actions were: containment integrity was re-established, the responsible maintenance supervisor was counseled on the need for strict adherence to procedures, and the event will be incorporated into Maintenance journeyman training. This event was also discussed with all maintenance crews and the importance of receiving proper authorization prior to beginning work on plant systems was stressed. An INPO Human Performance Enhancement review of this event was also performed.
3351991009 | St. Lucie 1 | 11/14/1991 | 12/09/1991 | 9112170472 | <strong>Removal of the Plant Vent Stack Monitors From Service Resulted in a Condition Prohibited by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1991 with St. Lucie Unit 1 in Mode 6 completing refueling requirements, a licensed utility operator noted that the Unit was in a condition prohibited by the Plant's Technical Specifications. The Plant Vent Stack Particulate Sampler, Iodine Sampler, and Noble Gas Activity monitor had been placed out of service and the Chemistry Department was not notified to sample for activity. Technical Specification 3.3.3.10 requires continuous sample collection with auxiliary sampling equipment to be performed if the plant vent is to be used as the effluent pathway. This condition existed for approximately twelve hours. During this time period there were no activities which could have resulted in an abnormal gaseous release. The root cause of this event was a cognitive personnel error by utility-licensed operators for referencing an inappropriate Technical Specification pertaining to Radiation Monitoring Instrumentation. <br /><br /> Corrective actions taken were: 1) Chemistry obtained a gas sample and analyzed it for abnormal activity; 2) Operations reviewed containment work for the period when the plant stack was unmonitored and found no activities which would have resulted in a release of airborne activity; 3) Operations Supervision counselled all licensed personnel to thoroughly review all the applicable Technical Specifications prior to taking a piece of equipment out of service; 4) Training Department incorporated this event into the Licensed Operator Requalification Training Program.
3361991001 | Millstone 2 | 01/10/1991 | 05/24/1991 | 9105310195 | <strong>Electro-Hydraulic Control System Failure Caused Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1991 at 1612 hours, with the unit operating at 92% power, the main turbine tripped on low Electro-Hydraulic Control (EHC) pressure. The Reactor Protection System initiated a Reactor trip following the turbine trip. Normal post-trip procedures were followed. There were no safety implications since the unit experienced a normal Reactor trip shutdown.
3361991002 | Millstone 2 | 01/18/1991 | 04/30/1993 | 9305140121 | <strong>Revised Interpretation of Electrical Distribution Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1991 at 1330 hours with the plant at 100% power and normal operation, the plant was notified of the results of an Engineering Evaluation On January 18, 1991 at 1330 hours with the plant at 100% power and normal operation, the plant was notified of the results of an Engineering Evaluation that had determined that operation of the four vital 120 volt Alternating Current (AC) buses on their alternate sources is unsatisfactory. The requirements for the four vital AC buses are described in Technical Specification Section 3.8.2.1. <br /><br /> This is being reported as an operation or condition prohibited by the plant's Technical Specification at this time because of a revised interpretation of Technical Specification requirements. Previous interpretation of the requirements of Section 3.8.2.1 was that it required the vital 120 volt buses be energized to be considered operable. Following the review of the Engineering Evaluation, the determination was made that since the alternate sources of power for the vital 120 volt AC buses are non-vital, then operation of the unit with these busses powered from alternate sources for a period of time longer than allowed by the action statement (8 hours) would make the busses inoperable. <br /><br /> To avoid a recurrence, specific written instructions have been issued to inform the plant operating staff of the revised interpretation of Section 3.8.2.1 and of the requirements to enter the action statement if any of the four vital 120 volt AC buses are powered from their alternate sources. <br /><br /> In addition, the potential for similar conditions in other sections was reviewed. The review determined that Section 3.8.2.3 which addresses Direct Current (DC) Distribution and operation of the vital DC Batteries, Busses and Battery Chargers, was also being interpreted non-conservatively. This was due to the potential for using the spare (swing) Battery Charger to power the vital facility 2 DC bus, even though this swing Charger is itself powered from a vital facility 1 480 volt AC bus. This specification does not address alternate sources, although the swing Charger can be aligned to power either facility DC bus. <br /><br /> Changes to Section 3.8.2.1 of the Technical Specifications, and modifications to the AC feed to the swing Charger are planned to provide the long term corrective action for both conditions identified.
3361991003 | Millstone 2 | 02/12/1991 | 03/13/1991 | 9103210046 | <strong>Design Inadequacy - Potential Loss of DC Switchgear Cooling During Loss of Instrument Air</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1991 at 1055 hours, while the plant was at 100% power, a reportability determination was made concerning a design inadequacy noted by a Unit 2 Probabilistic Safety Study. The study determined that a loss of Instrument Air could result in the eventual loss of both vital DC Switchgear trains, due to the loss of room cooling. The reportability evaluation determined that both DC Switchgear trains were inoperable and an Immediate Report was made (IRF# 91-19) pursuant to the requirements of 10CFR50.72(b)(2)(iii)(A). Prior to the completion of the reportability determination, when the problem was originally recognized, a procedure change was implemented to correct the deficiency. <br /><br /> Upon a loss of instrument air the normal chilled water flow to the DC Switchgear Coolers is isolated. However, unless there is a concurrent safety injection actuation signal, the vital chilled water pumps and chillers do not receive a start signal. The result would be the loss of ventilation cooling to both DC Switchgear Rooms, possibly followed by inverter and DC equipment failure. <br /><br /> The root cause was design inadequacy. The design did not adequately address the loss of instrument air failure mode of the normal chill water supply valves. Additionally, Abnormal Operating Procedure 2563, Loss of Instrument Air, was inadequate in that it did not recognize the loss of chill water to the DC Switchgear Coolers. <br /><br /> Corrective action included the revision of the procedure to include a note on this event and to provide direct operator actions that must be taken to ensure chill water flow to the DC Switchgear Room coolers. This procedure revision was effective January 30, 1991 and restored the affected systems to operable status.
3361991004 | Millstone 2 | 02/16/1991 | 03/18/1991 | 9103260216 | <strong>Unexpected Trip of 'B' S/G/ Feed Pump and Subsequent Manual Rx Trip</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1991, with the unit operating at 100% power, the 'B' Steam Generator Feed Pump (SGFP) unexpectedly tripped at 1731 hours. The pump was reset and the speed of the 'A' SGFP was raised from 4430 to 5100 RPM. As the 'B' SGFP was accelerated, it caused low suction pressure for both pumps. The 'B' SGFP tripped again, was reset, tripped and reset again. The 'A' and 'B' pump suction pressures again alarmed low. The 'A' SGFP then tripped. Low level alarms occurred in both steam generators. At 1733 hours, the reactor was manually tripped because of decreasing SG levels. The cause of the initial 'B' SGFP trip is unknown.
3361991005 | Millstone 2 | 01/24/1991 | 03/28/1991 | 9104080227 | <strong>Failure to Perform Some Required Inservice Examinations</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1991, with the plant at 100% power, the Millstone Unit 2 Inservice Inspection Coordinator identified that several ASME Class 2 piping non-destructive examinations had not been performed, as required, because they had never been included in the approved Unit 2 Inservice Inspection Program. This omission violates Millstone Unit 2 Technical Specification 4.05 which requires that inservice inspections "be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code .... except where specific written relief has been granted by the Commission ..." Eight weld examinations which should have been performed during the First Inspection Interval, which ended in December 1985, were not performed. Relief from performance of these examinations was not requested. Review of this omission showed that there was reasonable assurance that the affected piping had not been subjected to conditions that could result in degradation. Thus, failure to perform the required examinations did not have any impact on the operability or reliability of any safety related system. The missed examinations were scheduled for performance during the next cold shutdown. Changes to the Millstone Unit 2 ISI Program Plan were initiated to include the required examinations in the Program Plan. This omission was determined to be reportable under 10 CFR 50.73(a)(2)(i)(b) on February 28, 1991.
3361991006 | Millstone 2 | 03/30/1991 | 08/16/1991 | 9109030005 | <strong>Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1991, with the plant in Mode 1 at 100% power, it was determined that Surveillance Requirement Section 4.0.5 was not performed within the required 92 day time interval and that Surveillance Requirement 4.0.2.a, "the maximum allowable extension not to exceed 25% of the surveillance time interval," was not satisfied. The missed surveillance was performed immediately, met the acceptance criteria, but was 7 days past the maximum allowable extension. <br /><br /> Surveillance Requirement Section 4.0.5 states: "Inservice inspection of ASME Code Class 1, 2, and 3 components and inservice testing ASME Code Class 1, 2, and 3 pumps and valves shall be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code..." <br /><br /> The specific surveillance missed was the quarterly ISI stroke testing of the Facility II LPSI system procedure SP 21136. The valves were 2-SI-451, LPSI Pump B minimum flow check valve, 2-SI-635, and 2-SI-645, LPSI to Loop 2A and 2B stop valves, respectively. <br /><br /> There are no safety consequences as a result of this event because no modifications or maintenance activities were performed on the three valves since the last successful surveillance test on November 29, 1990.
3361991007 | Millstone 2 | 02/25/1991 | 03/27/1991 | 9104040182 | <strong>Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1991, with the plant in Mode 1 at 100% power; it was determined that Surveillance Requirement 4.9.16.1 was not performed within the required 72 hour time interval and that Surveillance Requirement 4.0.2.b, "the combined time interval for any 3 consecutive surveillance intervals not to exceed 3.25 times the specified surveillance interval", was not satisfied. The missed surveillance was performed approximately 96 hours after the previously completed surveillance.<br /><br /> Surveillance Requirement 4.9.16.1 states: "The decay time of all fuel within a distance "L" from the center of the spent fuel pool cask set-down area shall be determined to be >/=120 days within 24 hours prior to moving a shielded cask to the refueling floor and at least once per 72 hours thereafter." Distance "L" equals the major dimension of the shielded cask. <br /><br /> There are no safety consequences as a result of this event, since at the time of the missed surveillance there were no fuel assemblies in the spent fuel pool with a decay time of less than 120 days.
3361991008 | Millstone 2 | 05/25/1991 | 09/13/1991 | 9109240327 | <strong>Reactor Trip Due to Low Steam Generator Pressure</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1991, at 1732, with the reactor subcritical in MODE 3 (0% power, 511 degrees F, 2250 psig), the reactor automatically tripped while it was being manually shut-down. The reactor tripped on Low Steam Generator Pressure which was caused by excessive cooling of the Reactor Coolant System (RCS). The control room operating shift completed applicable portions of EOP 2525, "Standard Post Trip Actions" and EOP 2526, "Reactor Trip Recovery" without further incident. All equipment responded as expected and the reactor remained in a stable condition. The cause of the event was ineffective coordination between the reactor and turbine shutdown. Actions to address the coordination shortcomings have been implemented and procedure enhancements have been incorporated to eliminate the possibility of this specific scenario being repeated. This event is being reported pursuant to the requirements of paragraph 50.73 (a) (2) (iv), reporting any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature System. Similar LER's: None.
3361991010 | Millstone 2 | 10/18/1991 | 03/26/1993 | 9304050271 | <strong>Reanalysis of Main Steam Line Break Exceed Containment Design Limits</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1991, at 1305 hours, with the plant in Mode 1 at 100% power, a reportability determination was made concerning a reanalysis of the main steam line break event inside the containment. The reanalysis has confirmed that the assumptions made for the existing (1979) main steam line break analysis were non-conservative with respect to power level, break size, and single active failure. Using more restrictive assumptions, design limits for containment pressure and temperature could be exceeded. NNECo determined that this condition was reportable as a condition outside the design basis of the plant. An Immediate Report was made to the NRC, and the unit immediately commenced an orderly downpower to approximately 3% power (Mode 2). The existing main steam line break analysis is acceptable for Mode 2 operation. <br /><br /> A Justification for Continued Operation (JCO) was developed to allow the unit to return to power operation by stationing a dedicated reactor operator to close the main feedwater block valves following any reactor trip. This JCO documents the basis for reasonable assurance that, with the actions of a dedicated operator, containment pressure will remain below the design basis value for all postulated main steam line break events. The unit was returned to power operation on October 22, 1991. <br /><br /> Short term plant modifications to automatically close the main feedwater block valves given a Containment Isolation Actuation Signal (CIAS) were installed and tested in December 1991. As stated in the JCO, these modifications eliminate the necessity to station a dedicated reactor operator to close the main feedwater block valves following a reactor trip.<br /><br /> Plant modifications required to ensure an acceptable containment pressure response for a main steam line break inside the containment have been installed and tested. A revised response to I&E Bulletin 80-04 was submitted in January 1993 to update our previous submittal for containment response and return to power for MSLB events.
3361991012 | Millstone 2 | 11/06/1991 | 01/28/1993 | 9302110346 | <strong>Manual Reactor Trip Due to Plant Conditions Resulting From a Rupture in the Reheater Drain Tank to High Pressure Feedwater Heater Pipe</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1991, with the plant operating at 100% power, an eight inch diameter pipe ruptured at approximately 0643. The subject line contains pressurized, heated water and serves as a drain line from the first stage reheater drain tank no. 1B to the 1B high pressure feedwater heater. The water in this line is normally 470 psig at 463 degrees F. The leak released steam into the turbine building. The control room received a call that there was a "loud noise" in the turbine building. This initiated a review of control room instrumentation which indicated: Moisture separator reheater changes, slight cooldown, slight MWe output decrease and a 15 second calorimetric increase to 2722 MWth. A visual inspection of the turbine building confirmed the steam leak. At 0649 the SCO ordered a manual reactor trip based on alarms and indications. The reactor and turbine were tripped. The shift carried out EOP 2525, "Standard Post Trip Actions." Approximately one minute after the trip the SS ordered the main steam isolation valves shut and the opening of the condenser dump valves to depressurize the main steam header. After EOP 2525 was completed, and in-hand verified, the shift entered EOP 2536, "Excess Steam Demand." In order to assess the source of the leak, the remaining condensate pump was secured and condenser vacuum was broken. With the plant stable the operators exited EOP 2526 "Reactor Trip Recovery."
3381991001 | North Anna 1 | 02/24/1991 | 03/14/1991 | 9103220373 | <strong>Hot Leg Safety Injection Branch Flow Above Technical Specification Requirements Due To Inherent Errors In Flow Measurement Techniques</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1991 with Unit 1 in Mode 5 (Cold Shutdown), it was discovered during the performance of the High Head Safety Injection (HHSI) flow balance test that one Safety Injection (SI) pump's total flow rate exceeded the maximum Technical Specification (TS) requirement for pump runout. Technical Specification surveillance 4.5.2.h requires SI pump flow to be less than or equal to 650 gallons per minute (gpm). While flowing 1-CH-P-1A to the hot leg branch lines through the normal header, the total pump flow was 657.3 gpm. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> The cause of the event was inherent errors in measurement techniques used to initially set the SI throttle valves along with the method of repositioning the throttle valves. In addition, the TS acceptance band is very narrow with no stated tolerances. When the excessive flow was discovered, the throttle valves were adjusted so that the total flow from 1-CH-P-1A to the hot leg branch lines through the normal header is now 618.9 gpm as indicated by the permanent total flow indicator.<br /><br /> No significant safety consequences resulted from this event because a previous Nuclear Safety Analysis has determined that the actual runout value of a HHSI pump is 705 gpm. The highest total flow rate recorded for 1-CH-P-1A was 657.3 gpm which is significantly less than the pump runout value. Therefore, the health and safety of the public were not affected at any time during this event.
3381991002 | North Anna 1 | 01/25/1991 | 02/15/1991 | 9102250147 | <strong>Pressurizer And Main Steam Safety Valve Setpoints Out Of Tolerance Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>At 1017 hours on January 25, 1991, with Unit 1 in Mode 6 (Refueling), the "as found" set pressures for 2 Pressurizer Safety Valves and 7 of 15 Main Steam Safety Valves (MSSVs) were found to be outside the setpoint tolerances allowed by Technical Specifications 3.4.3 and 3.7.1.1, respectively. This event is reportable pursuant to 10CFR50.73 (a) (2) (i) (B) for conditions prohibited by Technical Specifications.<br /><br /> The safety valves were sent to Wyle Labs for testing. The "as found" set pressures for 2 pressurizer safety valves and 7 MSSVs were found to be outside the allowable Technical Specification tolerance. However, the "as found" set pressures were within the 3% tolerance specified in ASME Section XI. <br /><br /> The safety valves will be repaired and readjusted, as necessary to be within the correct setpoint tolerance allowed by Technical Specifications.<br /><br /> This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. In addition the "as found" set pressures were within the 3% tolerance specified in ASME Section XI. The health and safety of the public were not affected at any time during this event.
3381991003 | North Anna 1 | 01/30/1991 | 02/27/1991 | 9103060158 | <strong>Steam Generator Tube Defects</strong><br /><i>Abstract:&nbsp;</i>During the 1991 refueling outage on Unit 1, one hundred percent of the inservice tubes in the three Steam Generators (S/Gs) (both hot and cold legs) were inspected using the standard eddy current (E/C) bobbin probe. Additionally, augmented inspections were performed using a rotating pancake coil (RPC) probe and an 8X1 probe. As a result of these inspections, greater than 1% of the tubes in each of the three S/Gs were identified as having pluggable indications. These inspection results required the three S/Gs to be classified as Category C-3. All defective tubes are being removed from service. The defects identified in the three S/Gs are reportable pursuant to 10CFR50.73(a)(2)(v)(C) as required by Technical Specification 4.4.5.5.c. Four hour reports were made pursuant to 10CFR50.72(b)(2)(i). <br /><br /> No reactor core safety concerns exist since the number of tubes plugged in each S/G is less than the current Safety Analysis tube plugging limit. The health and safety of the general public were not affected during this event.
3381991004 | North Anna 1, North Anna 2 | 02/06/1991 | 02/22/1991 | 9102280186 | <strong>SEALED SOURCE MISSED SURVEILLANCE DUE TO INADEQUATE PROCEDURES</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. ON FEBRUARY 6, 1991, AT 1944 HOURS, WITH UNIT 1 IN A REFUELING OUTAGE (MODE 6) AND UNIT 2 OPERATING AT 100% POWER (MODE 1), PERSONNEL DISCOVERED THAT A SEALED RADIOACTIVE SOURCE IN STORAGE HAD NOT BEEN LEAK TESTED PRIOR TO USE AS REQUIRED BY THE SURVEILLANCE REQUIREMENTS OF TECHNICAL SPECIFICATION 3.7.11.1. THE SOURCE HAD BEEN TAKEN OUT OF STORAGE SEVERAL TIMES TO CALIBRATE THE CONTAINMENT HIGH RANGE RADIATION MONITORS AND WAS NOT LEAK TESTED. THIS EVENT IS REPORTABLE PURSUANT TO 10 CFR 50.73(A)(2)(I)(B) FOR A CONDITION THAT IS PROHIBITED BY THE TECHNICAL SPECIFICATIONS. THE CAUSE OF THE EVENT WAS INADEQUATE PROCEDURES FOR VERIFYING THE LEAK TESTING OF SOURCES IN STORAGE. AS AN IMMEDIATE CORRECTIVE ACTION, THE SOURCE WAS LEAK TESTED AND REMOVABLE CONTAMINATION LEVELS WERE VERIFIED TO BE LESS THAN TECHNICAL SPECIFICATION LIMITS. IN ADDITION, PROCEDURES WERE REVISED TO ENSURE SOURCES IN STORAGE ARE PROPERLY LEAK TESTED. ALSO, SOURCES IN STORAGE HAVE BEEN LABELLED WITH INFORMATION PROVIDING THE OPERABILITY AND LEAK TEST REQUIREMENTS. THIS EVENT DID NOT POSE ANY SIGNIFICANT SAFETY IMPLICATIONS BECAUSE WHEN THE SOURCE WAS TAKEN OUT OF STORAGE FOR CALIBRATING THE CONTAINMENT HIGH RANGE RADIATION MONITORS, THE SOURCE WAS SMEARED AND CHECKED FOR CONTAMINATION PRIOR TO BEING PLACED BACK IN STORAGE. LEAKAGE WAS NOT DETECTED WHEN THE SOURCE WAS SMEARED AND CHECKED FOR CONTAMINATION.
3381991005 | North Anna 1 | 02/09/1991 | 03/06/1991 | 9103130003 | <strong>Refueling Operations Containment Building Penetrations Breach</strong><br /><i>Abstract:&nbsp;</i>At 2200 hours on February 9, 1991, with Unit 1 in Mode 6 (refueling), it was discovered that containment building penetrations had been breached when penetrations through the equipment hatch were found with inadequate isolation devices. This is a violation of Technical Specification 3.9.4 and therefore is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). A four hour report was made pursuant to 10CFR50.72 (b)(2)(iii)(C) & (D). <br /><br /> The cause of the event was inadequate procedural controls to ensure full accountability of penetrations through the equipment hatch. Following completion of core on-load a Senior Reactor Operator was performing surveillance inspections of the equipment hatch penetrations. During this inspection two hoses were identified that appeared to breach the containment building penetrations. No core alterations were occurring at the time of discovery. Core mapping and reactor cavity pump down were secured as an additional conservative action. The containment penetrations were isolated and/or removed prior to resuming these activities. <br /><br /> This event posed no significant safety implications because the containment was under a negative pressure at the time thereby preventing any out leakage and the refueling was completed without a fuel handling incident. Also this event is bounded by the UFSAR dropped fuel assembly accident analysis. Therefore, the health and safety of the public were not affected at any time during this event.
3381991006 | North Anna 1 | 04/03/1991 | 04/18/1991 | 9104240428 | <strong>Missed A.C. Offsite Power Source Surveillance due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1440 hours, on April 3, 1991, with Unit 1 operating at 99.2% power (Mode 1), and 1J Diesel Generator tagged out for pre-planned maintenance, it was discovered that an 8 hour Technical Specification (TS) Surveillance had not been performed within the allowed interval. Technical Specification 3.8.1.1, Action Statement (b), requires that whenever one diesel generator is declared inoperable, the operability of the A.C. Off-site Power Sources must be verified within one hour, and at least once per 8 hours thereafter. This event is reportable, pursuant to 10 CFR 50.73 (a) (2) (i) (B) as a condition prohibited by Technical Specifications 4.0.3 and 3.8.1.1. <br /><br /> The cause of the event which resulted in the failure to perform the required surveillance was personnel error. Following discovery of the omission at 1440 hours, Operations immediately initiated the offsite A.C. Power Source verification and satisfactorily completed the surveillance at 1455 hours. <br /><br /> This event posed no significant safety implications since off-site power sources remained operable during the period, as evidenced by successful completion of the A.C. Off-site Power Sources surveillance procedure. Alarms and indication were available to Control Room personnel to provide status of Electrical Distribution System at all times. Therefore, the health and safety of the general public was not affected at any time during this event.
3381991007 | North Anna 1, North Anna 2 | 03/05/1991 | 03/26/1991 | 9104010323 | <strong>Waste Gas Decay Tank Maintained With Oxygen Concentration Greater Than 2% With Hydrogen Concentration Greater Than 4% For More Than 48 Hours</strong><br /><i>Abstract:&nbsp;</i>At 1235 hours on March 5, 1991 with Unit 1 in Cold Shutdown (Mode 5) and Unit 2 at 100% power (Mode 1), it was discovered that the oxygen concentration in the "A" Waste Gas Decay Tank (WGDT) was 2.4% with a hydrogen concentration of 11.0%. The Technical Specification (TS) Action Statement 3.11.2.5 "a" requires the oxygen concentration to be reduced to less than 2% within 48 hours when the hydrogen concentration is greater than 4%. The oxygen concentration was greater than 2% for approximately 63 hours; therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> The cause of the event was personnel error in the interpretation of the applicable TS action statement; therefore, the requirements of the action statement were not satisfied. A TS amendment which will provide better guidance is currently pending NRC approval. When the TS violation was discovered, the release of "A" WGDT was secured and nitrogen was added to bring the oxygen concentration to below 2%. <br /><br /> No significant safety consequences resulted from this event because the oxygen level was maintained below the concentration that would support combustion. Since the mixture of gas within the WGDT remained below flammable limits, the health and safety of the public were not affected at any time during this event.
3381991008 | North Anna 1 | 03/09/1991 | 04/01/1991 | 9104080260 | <strong>Momentary Breech Of Containment Integrity Due To Faulty Limit Switch On Personnel Air Lock</strong><br /><i>Abstract:&nbsp;</i>At 0050 hours on March 9, 1991, with Unit 1 at 3.5% power (Mode 2), it was determined that containment integrity was momentarily lost when the inner door equalizing valve was partially opened with the outer personnel hatch door already opened. Personnel were attempting to enter Unit 1 containment with the outer door open while another team was attempting to exit. This event is reportable pursuant to 10CFR50.73(a)(2)(v)(C). A four hour report was made pursuant to 10CFR50.72(b)(2)(iii)(C). <br /><br /> The cause of the event was a faulty Limit Switch (LS) on the outer door which normally provides a redundant interlock preventing simultaneous operation of the inner and outer personnel air locks. Both doors could not have been opened at the same time due to a differential pressure switch which would have prevented this. When the team inside containment began to equalize across the inner door with the outer door already open, the equalizing valve cycled partially open providing a breech of containment integrity. The event was immediately identified by the containment access teams, and the outer door was closed and secured to restore containment integrity. <br /><br /> No significant safety consequences resulted from this event because the containment breech was immediately identified and integrity restored. Also, a differential pressure switch was in place providing a redundant interlock to prevent both doors from being simultaneously opened. Therefore, the health and safety of the public were not affected at any time during this event.
3381991009 | North Anna 1, North Anna 2 | 04/11/1991 | 05/07/1991 | 9105130285 | <strong>Inservice Testing Missed Surveillances Due To Personnel Error In Program Implementation</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1991 with Unit 1 in Mode 1 (99.4 percent power) it was determined that a backseat surveillance test for three main steam check valves, located in the supply line to the steam driven auxiliary feedwater pump, was not satisfied. On April 18, 1991 with Unit 1 in Mode 1 (100 percent power) it was determined, through an Inservice Testing Program implementation assessment, that a surveillance for a safety injection trip valve, located in the vent line from the accumulator to the waste gas charcoal filters, was missed. On May 1, 1991 with Unit 1 in Mode 1 (100 percent power) and Unit 2 in Mode 1 (100 percent power) it was also determined that surveillances for the seal water supply isolation valves to the control room chillers, were missed. These incidents are a violation of Technical Specification 4.0.5 and therefore reportable pursuant to 10CFR50.73 (a)(2)(i)(B).<br /><br /> The cause of the event was personnel error resulting in the requirements of Generic Letter 89-04 not being adequately implemented. Upon determination that the surveillances were not met the affected valves were successfully tested. <br /><br /> These incidents posed no significant safety implications because the valves were capable of performing their intended safety function. Therefore, the health and safety of the public was not affected at any time during these events.
3381991010 | North Anna 1 | 04/23/1991 | 05/16/1991 | 9105280084 | <strong>Auto Start Of Emergency Diesel Generator 1J Due To Loss Of Power From "A" RSST And Subsequent Start Due To Inadvertent Bypass Of Air Start SOV</strong><br /><i>Abstract:&nbsp;</i>At 0920 hours on April 23, 1991, with Unit 1 operating at 100 percent power (Mode 1), the "A" Reserve Station Service Transformer (RSST) isolated because of an inadvertent overcurrent auxiliary relay trip. The cause of the "A" RSST isolation was personnel error associated with improper installation of an overcurrent trip auxiliary relay. The Unit 1 "J" Emergency Diesel Generator (EDG) auto-started and re-energized the Unit 1 "J" Emergency Bus. This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as an automatic actuation of an Engineered Safety Feature (ESF). A four-hour report was made in accordance with 10CFR50.72 (b)(2)(ii) at 1106 hours.<br /><br /> At 0726 hours on April 26, 1991, with Unit 1 at 100 percent power, the 1J EDG was inadvertently started due to plant personnel accidently bypassing the air start SOV via the manual override while performing a walkdown to plan a work order. This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as an automatic ESF actuation. A four-hour report was made in accordance with 10CFR50.72 (b)(2)(ii) at 0908 hours. <br /><br /> The 1J EDG functioned properly to restore power to the Unit 1 "J" Emergency Bus. All other automatic actuations also functioned properly. Therefore, the health and safety of the public was not affected at any time during these events.
3381991011 | North Anna 1 | 05/11/1991 | 06/06/1991 | 9106130316 | <strong>Unit Shutdown Due To Exceeding Technical Specification Limit For Reactor Coolant System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>At 0400 hours on May 11, 1991, with Unit 1 at 30 percent power, a containment entry team identified a source of leakage between the "B" cold leg loop stop valve and the isolation valve for the 3/4 inch (3/8 inch inside diameter) upper disc pressurization line, and the Action Statement of Technical Specification 3.4.6.2 was entered. A unit shutdown commenced at 0500 hours due to an unisolable Reactor Coolant System (RCS) pressure boundary leak. A Notification of Unusual Event (NOUE) was declared in accordance with the emergency plan, and all appropriate notifications were made in a timely manner. The unit was placed in cold shutdown (mode 5) at 1640 hours. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(A) as a completion of a plant shutdown required by TS. A one hour report was made pursuant to 10CFR50.72 (a)(i). <br /><br /> A visual inspection of the pipe crack indicated a probable high cycle fatigue failure mechanism. No significant safety consequences resulted from the pipe crack because the leak, approximately 0.7 gpm, was much less than the normal charging system make up capacity. In addition, there are no pipe whip or impingement concerns associated with the disc pressurization piping. The health and safety of the public was not affected at any time during this event because the leak was confined to the containment structure and no release was made to the environment.
3381991012 | North Anna 1 | 05/20/1991 | 06/11/1991 | 9106180209 | <strong>Auxiliary Feedwater Pump Auto-Start Signal Received</strong><br /><i>Abstract:&nbsp;</i>At 0603 hours on may 20,1991, with Unit 1 in Mode 4 (hot shutdown) and heating up in preparation for unit start-up, the Auxiliary Feedwater Pumps (AFWP) received an auto start signal when the circuit breakers for the "C" Main Feedwater Pump (FWP) opened due to a hi-hi level in the "C" Steam Generator (SG). The "C" SG hi-hi level was caused by opening the "C" Main Steam (MS) Non-Return Valve (NRV) with a sufficient differential pressure to induce a swell in SG water level. A four hour report was made in accordance with 10CFR50.72 (b)(2)(ii) at 0929 hours. This event is reportable pursuant to 10CFR50.73(a)(2)(iv) as an automatic actuation of an Engineered Safety Feature. <br /><br /> The event was caused by personnel error. Steam generator level returned to normal, feedwater (FW) isolation was reset, and the main feedwater pump breakers were re-closed to restore feed capability from the condensate system. <br /><br /> The AFWP's are not required until Mode 3 and were in "Pull-to-Lock". Therefore, an actual auto-start did not occur. Sufficient feedwater was available and all systems functioned as designed. The plant remained stable during the event. Therefore, the health and safety of the public was not affected at any time during this event.
3381991013 | North Anna 1, North Anna 2 | 05/22/1991 | 06/13/1991 | 9106180343 | <strong>Missed Surveillance On Quench Spray Pump Discharge Motor Operated Valves</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1991 with Unit 1 in Mode 2 at 3 percent power and Unit 2 in Mode 1 at 100 percent power it was determined during a review of the Inservice Testing (IST) Program implementation procedures that stroke time surveillance requirements for closed direction testing of four quench spray pump discharge motor operated valves had not been performed. This is a violation of Technical Specification 4.0.5 and therefore reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the event was personnel error resulting in the requirements of the IST Program not being adequately implemented. The current test procedure requires testing of the subject valves in the open direction only. Upon determination that the surveillances were not met, the affected valves were successfully tested. <br /><br /> These incidents posed no significant safety implications because the valves were capable of performing their intended safety function. Therefore, the health and safety of the public was not affected at any time during this events.
3381991014 | North Anna 1, North Anna 2 | 07/03/1991 | 07/26/1991 | 9107310154 | <strong>Failure To Measure Inlet Pressure For Boric Acid Transfer Pump Surveillance Tests</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1991 with Units 1 and 2 in Mode 1 at 100 percent power it was determined that ASME Section XI surveillance requirements for the four boric acid transfer pumps had not been adequately performed during the second quarter of 1991. The IST Program requires the pump inlet pressures to be directly measured; however, the implementing procedures required the inlet pressure to be calculated from tank level. This is a violation of Technical Specification 4.0.5 and therefore reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the event was personnel error resulting in the failure to obtain the appropriate relief from the test requirements when difficulty was encountered with installation of permanent pressure gages. Upon determination that the surveillances were not met, the inlet pressures for the affected pumps were successfully measured using temporary test equipment. <br /><br /> These incidents posed no significant safety implications because the pumps were capable of performing their intended safety function. Therefore, the health and safety of the public was not affected at any time during this event.
3381991015 | North Anna 1 | 07/14/1991 | 08/01/1991 | 9108070138 | <strong>Inadvertent Reactor Protection System Trip Signal Caused By Control Power Bus Short During Process Control Cabinet Maintenance</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1991, at 1048 hours Unit 1 was in mode 3 at 474 degrees F and heating up when an exposed control bus wire in a process control cabinet shorted which induced a voltage spike on a vital bus. The voltage spike resulted in high neutron flux alarms and the generation of a Reactor Protection System (RPS) signal. The control power bus short also caused a loss of control power to the charging header low pressure relay which caused an automatic start of a charging pump when low discharge header pressure was indicated. This event is reportable pursuant to 10CFR50.73 (a) (2) (iv) as an automatic actuation of the RPS. A four hour report was made pursuant to 10CFR50.72 (b) (2) (ii). <br /><br /> The cause of the event was personnel error during installation of a backup power supply on a process control cabinet. The insulation on a control bus wire was inadvertently cut and shorted to ground. The shorted wire resulted in a voltage spike on a vital bus which generated the high neutron flux RPS signal and subsequently caused a loss of control power to the charging header low pressure relay. <br /><br /> No significant safety consequences resulted from this event because the reactor protection system signal was inadvertent. Since the reactor trip breakers were already open and the unit was not actually in a high flux condition, the health and safety of the public was not affected at any time during this event.
3381991016 | North Anna 1, North Anna 2 | 07/22/1991 | 08/19/1991 | 9108230283 | <strong>Charging Pump Temporary Flow Meter Outside ASME XI Accuracy Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1991 with Unit 1 in mode 1 at 99.2 percent power and Unit 2 in Mode 1 at 100 percent power it was determined that ASME XI requirements for instrument accuracy had not been met with an ultrasonic flow indicator used for testing the six charging pumps. The code requires that the flow instrumentati n be accurate to within 2 percent of full scale for pump testing; however, the accuracy of the equipment may be worse than 3 percent in the case of charging pump testing. Since the instruments were not accurate to 2 percent, this is a violation of Technical Specification 4.0.5 and therefore reportable pursuant to 10CFR50.73 (a)(2)(i)(B).<br /><br /> The cause of the event was personnel error resulting in failure to maintain testing equipment within the ASME XI code requirements. Revision 6 of the IST program changed the charging pump quarterly test flow rate from recirculation flow to normal charging flow. In order to avoid having to isolate recirculation flow, the use of ultrasonic flow equipment was written into the implementing procedures. Subsequently, it was determined that the flow meters do not meet the ASME XI tolerance requirements in this application.<br /><br /> This incident posed no significant safety implications because the pumps were still capable of performing their intended safety functions. Therefore, the health and safety of the public were not affected at any time during this event.
3381991017 | North Anna 1 | 08/08/1991 | 10/10/1991 | 9110170118 | <strong>Spurious Closure Of "A" Main Steam Trip Valve Causing Reactor Trip And Safety Injection</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1991, at 0242 hours, with Unit 1 at 99.8 percent power (mode 1) "A" main steam trip valve shut causing a safety injection and reactor trip. The initiating signal for the safety injection was high steam flow coincident with low steam line pressure in two out of three main steam lines. At 0250 hours a Notification of Unusual Event was declared, and the safety injection signal was reset in accordance with Emergency Procedures. Heat removal was accomplished through the atmospheric main steam power operated relief valves due to closure of the main steam trip valves. This event is reportable pursuant to 10CFR50.73 (a)(2)(iv), and was the twelfth ECCS Actuation reportable pursuant to Technical Specification 6.9.2. A one hour report was made pursuant to 10CFR50.72 (a)(i). <br /><br /> The cause of the event was water entering the control relay junction box for the "A" main steam trip valve. The source of water was determined to be rainfall entering the quench spray pump house due to a defective rain gutter. Inspection of the junction box revealed corrosion on the relay contacts which closed the gap between the seal-in contacts making it possible for water to create a short across the contacts.<br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public was not affected at any time during this event..
3381991018 | North Anna 1, North Anna 2 | 08/14/1991 | 09/10/1991 | 9109180241 | <strong>Failure To Perform Response Time Testing On 72 % Undervoltage Relays And Time Delay Setpoints Found Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1991, at 1114 hours with Unit 1 operating at 99.1 percent power (Mode 1) and Unit 2 operating at 100 percent power (Mode 1) it was determined that Emergency Diesel Generator (EDG) time response testing had been performed on the 74% undervoltage (UV) relay circuitry instead of the 72% UV relay circuitry as required by Technical Specifications (TS). Subsequently, the 72% UV relays were found with time delay settings of 2.0 seconds rather than the TS required 2.2 0.03 seconds. Therefore, this event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B).<br /><br /> The cause of the event was personnel error associated with incorrect interpretations of the TS surveillance and setpoint requirements. Upon determination that test procedures and setpoints were incorrect, the relays were recalibrated to the TS limits and properly time response tested. <br /><br /> No significant safety consequences resulted from this event because the 74% undervoltage circuit which was time response tested is the primary circuit that starts the EDG. The 72% UV relay is required to function to load the EDG, and this circuitry is tested every other month during degraded voltage/loss of voltage functional tests. In addition, the 2.0 second time delay is a conservative value relative to the 2.2 second specification. Therefore, the health and safety of the public was not affected at any time due to this event.
3381991019 | North Anna 1, North Anna 2 | 09/04/1991 | 10/11/1993 | 9310180276 | <strong>Inadequate Procedure Causes An Improper LHSI Relief Valve Blowdown Ring Setting Resulting In Operability Issues</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1991 with Unit 1 in Mode 1 (100 percent power), it was discovered during testing of the "B" Low Head Safety Injection (LHSI) pump, 1-SI-P-1B, that discharge relief valve, 1-SI-RV-1845C, lifted and did not reseat until after the pump was secured. Following an engineering evaluation, it was determined that, previously documented and more severe relief valve misadjustments could have resulted in the failure of a relief valve to reseat. This relief valve leakage is assumed to be 20 gpm for 30 days which is greater than the UFSAR assumed leakage of 50 gpm for 10 minutes due to a LHSI pump seal failure. This is reportable pursuant to 10CFR50.73 (a)(2)(ii)(B) for a condition that was outside the design basis of the plant. <br /><br /> The cause of the event was an inadequate procedure. The maintenance procedure did not provide adequate instructions for adjusting the relief valve blowdown ring setting on the LHSI discharge line relief valves. The procedure has been subsequently revised, the blowdown ring on all relief valves have been properly set, and all relief valves have been successfully tested.<br /><br /> This incident posed no significant safety implications because procedural action could have been taken to reseat the relief valve thereby eliminating the postulated radioactive release. In addition, the LHSI system was not required to mitigate an accident during the timeframe in question. Therefore, the health and safety of the public was not affected at any time during the event.
3381991020 | North Anna 1, North Anna 2 | 10/31/1991 | 12/23/1991 | 9201030275 | <strong>Service Water System Configuration During Logic Testing - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>At 1117 hours on October 31, 1994, the Units 1 and 2 operating at 100 percent power (Mode 1), it was discovered that the shared Service Water (SW) system may not have been able to provide design flow to an accident unit's Recirculation Spray Heat Exchangers. This discovery was made during the performance of a periodic test which removed the automatic start function of the Unit 2 Emergency Diesel Generator which provides emergency power to the Unit 2 "B" SW pump during an accident. The test also removed the automatic start function of the Unit 1 "B" SW pump. Operating procedures require that the SW pump discharge pressure be adjusted to 258 psig by manually throttling Component Cooling Heat Exchanger CCHX valves when less than 4 pumps are operable; however, the system was not throttled as required. It was initially determined that sufficient SW flow may not have been available to mitigate the consequences of an accident, and a four hour report was made on October 31, 1991, pursuant to 10 CFR 50.72 (b) (2) (iii) (D).<br /><br /> On November 26, 1991, an engineering calculation was completed and reviewed by the Station Nuclear Safety and Operating Committee (SNSOC) which determined that sufficient SW flow was available to mitigate the consequences of an accident. Therefore, the health and safety of the public were not affected during the event. The NRC was notified of the change in reportability on November 26, 1991, at 1240 hours. This voluntary report is being submitted to discuss the event and the basis for reclassification to nonreportable status.
3381991021 | North Anna 1 | 11/26/1991 | 12/20/1991 | 9201020215 | <strong>Missed Surveillance Of Offsite AC Sources</strong><br /><i>Abstract:&nbsp;</i>At 1330 hours, on November 26, 1991, Unit 1 was operating at 100% power (Mode 1) when it was discovered that an Emergency Diesel Generator (EDG) battery had an individual cell voltage (ICV) which was less than the Technical Specification (TS) low limit. The discovery was made following the addition of water to cells which had low electrolyte levels. Engineering personnel determined the low ICV reading was invalid due to the recent addition of water. At 1630 hours, Management determined that the low reading was valid. TS 3.8.1.1, Action Statement (b), requires verification of the A.C. Off-site Power Sources within one hour when one EDG is declared inoperable. Since the surveillance was not performed within one hour, this event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B). <br /><br /> The cause of the event was personnel error due to a misunderstanding of the ICV reading resulting in a delayed report to the Operations shift. Following discovery of the missed surveillance, the Off-site A.C. Power Source verification was satisfactorily completed at 2015 hours. <br /><br /> This event posed no significant safety implications since off-site power sources remained operable during the period. Therefore, the health and safety of the public was not affected at any time during this event.
3381991022 | North Anna 1 | 12/23/1991 | 01/21/1992 | 9201270348 | <strong>Unit Shutdown Due To Indetermination Of Steam Generators Following Eddy Current Data Re-Review</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1991, at 1717 hours, a Unit 1 shutdown from 100 percent power (Mode 1) was initiated by management when the operability status of the Steam Generators was called into question. A re-review of the Steam Generator eddy current data taken during the last refueling outage was performed per NRC request to support Unit 1 operation until April 1992. During the review, several indications were identified which could possibly be defects in the tubes. The condition of several tubes could not be determined using the criteria of the re-review; therefore, the unit was shutdown. A Notification of Unusual Event was declared at 1632 hours on December 23, 1991, in accordance with Emergency Plan Implementing Procedures and was terminated on December 24, 1991, at 0730 hours when the unit safely reached cold shutdown. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (i) (A). <br /><br /> The cause of the event was the indeterminate status of the Unit 1 Steam Generators as a result of the eddy current re-review.<br /><br /> This event posed no significant safety implications because the Steam Generator tube integrity was maintained, there were no radiological releases associated with the normal shutdown, and the additional potential defects were bounded by the existing RG 1.121 safety analysis model. Therefore, the health and safety of the general public was not affected at any time during this event.
3381991023 | North Anna 1 | 12/27/1991 | 01/22/1992 | 9201290045 | <strong>Inadvertent Flow From LHSI System To RCS During Shutdown With RCS At Low Pressure</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1991, at 1545 hours, Unit 1 was at cold shutdown (Mode 5) with Reactor Coolant System (RCS) pressure at 30 psig and slowly decreasing when the pressurizer level increased from 60% to 82% cold calibrated level. Investigation revealed that the Low Head Safety Injection (LHSI) pump discharge valves had been left open after Type "C" testing. As RCS pressure slowly dropped, the Refueling Water Storage Tank (RWST) static head became sufficient to cause borated water to flow through the LHSI pumps into the RCS.<br /><br /> This event is reportable pursuant to 10 CFR 50.73 (a) (2) (iv), and a four hour report was made pursuant to 10 CFR 50.72 (b) (2) (ii). <br /><br /> This event posed no significant safety implications because there was no overpressure concern. In addition, the minimum shutdown margin required by TS TS 3.1.1.2 was maintained. Therefore, the health and safety of the public was not affected at any time during this event.
3391991001 | North Anna 2 | 03/18/1991 | 04/12/1991 | 9104230221 | <strong>PORV Control Circuitry Missed Surveillance Due To Incorrect Technical Specification Interpretation And Administrative Error</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1991, at 1714 hours, with Unit 2 operating at 100% power (Mode 1), it was determined that a set of contacts and associated wiring on the control room bench board switch for the Train A power operated relief valve (PORV) over pressure control circuitry had not been tested as required by Technical Specification surveillance requirement 4.4.3.2.1.b. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) for a condition that is prohibited by the Technical Specifications.<br /><br /> The cause of the event was the incorrect interpretation of Technical Specification 4.4.3.2.1.b. Previous interpretations did not require testing of the contacts and associated wiring for the PORV control circuitry. As an immediate corrective action, the action statement of Technical Specification 3.4.3.2 was entered and PCV-2455C was declared inoperable and its associated block valve was shut. The appropriate procedure was temporarily revised to functionally test the contacts and associated wiring and testing was satisfactorily performed. As an additional corrective action, appropriate procedures will be revised to ensure each contact and associated wiring in the PORV control circuitry is adequately tested.<br /><br /> This event did not pose any significant safety implications because subsequent testing of the contacts and associated wiring demonstrated that the PORV was capable of performing its intended function in the case of an overpressure event. The health and safety of the general public were not affected at any time during this event.
3391991002 | North Anna 2 | 05/14/1991 | 06/03/1991 | 9106100133 | <strong>Automatic Start Of The 2H Emergency Diesel Generator Caused By De-energization Of The 2H Emergency Bus Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>At 0000 hours on May 14, 1991, with Unit 2 at 97% power (Mode 1) and Unit 1 in cold shutdown (Mode 5) ; the Unit 2 emergency bus 2H was inadvertently de-energize(d due to isolation from the Reserve Station Service Transformer B. This caused an automatic actuation of the 2H EDG due to loss of voltage on the 2H bus. This event is reportable pursuant to 10CFR50.73(a)(2)(iv) as an automatic actuation of an Engineered Safety Feature (ESF). A four-hour report was made in accordance with 10CFR50.72(b)(2)(ii) at 0131 hours on May 14, 1991. <br /><br /> This event was caused by personnel error. The control room operator did not properly follow the operating procedure and accidently manipulated the wrong circuit breaker while transferring the Unit 1 B station service bus to the B Reserve Station Service Transformer.<br /><br /> No significant safety consequences occurred because the redundant emergency bus 2J remained available to supply power to required plant equipment. The 2H EDG functioned properly and re-energized the 2H Emergency Bus. All other automatically actuated equipment functioned as designed. The health and safety of the public were not affected at any, time during this event.
3391991003 | North Anna 2 | 05/22/1991 | 06/07/1991 | 9106130320 | <strong>Missed Surveillance On Safety Injection System Accumulator Nitrogen Supply And Vent Valves Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1991 with Unit 2 in Mode 1 (100 percent power) it was determined, through an Inservice Testing Program implementation assessment, that a surveillance test on four safety injection system accumulator nitrogen supply and vent valves was missed. This is a violation of Technical Specification 4.0.5 and therefore reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event was personnel error. The PTSS Coordinator, who is responsible for test scheduling, did not revise the performance modes for 2-PT-212.18 that were approved and documented on a procedure action request. Upon determination that the surveillance was not met, Technical Specification 4.0.2 was entered, and the affected valves were successfully tested. <br /><br /> This incident posed no significant safety implications because the valves were capable of performing their intended safety function as demonstrated during testing that was conducted on May 22, 1991. Therefore, the health and safety of the public was not affected at any time during these events.
3391991004 | North Anna 2 | 06/03/1991 | 06/27/1991 | 9107030245 | <strong>Failure To Verify Reactor Vessel Head Vent Valve Locked Open Following 1989 Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1991 with Unit 2 in Mode 1 at 100 percent power it was determined during a Quality Assurance audit of Technical Specification compliance that documented evidence could not be located which verified that the manual isolation valve upstream of the reactor vessel head vent path was verified locked in the open position following the 1989 refueling outage. This incident is a violation of Technical Specification 4.4.11.2.a and therefore reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the event was personnel error in that the acceptance criteria of a periodic test procedure was signed off as complete when the appropriate action had not been performed. The valve was verified open by observing flow through the reactor vessel head vent path. Following the 1990 refueling outage, the valve was verified locked open. <br /><br /> This incident posed no significant safety implications because the reactor vessel head vent path was demonstrated as fully capable of performing its intended function by verifying flow through the appropriate valves. Therefore, the health and safety of the public was not affected at any time during this event.
3391991005 | North Anna 2 | 08/14/1991 | 09/09/1991 | 9109180267 | <strong>Degraded Voltage Relay Time Delay Setpoint Outside Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1991, at 1114 hours with Unit 2 operating at 100 percent power (Mode 1) it was determined that a 90% degraded voltage relay for a Unit 2 emergency bus which is required by TS to have a 60 3 second time delay had a measured response time of 54.7 seconds. Since the degraded voltage (DV) relays were not set in accordance with the TS, this event is reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event was personnel error associated with inadequate procedures. It is station policy to include TS surveillance requirements in the procedure's acceptance criteria; however, the time delay requirement was not included in this case. Station personnel did not recognize that the setpoint was outside the requirement because it was not addressed in the acceptance criteria. Therefore, the cause of the event was personnel error.<br /><br /> No significant safety consequences resulted from this event because total response time for the 90% DV protection circuitry was significantly below the TS limits. Since the shorter response time settings were within the allowable band of the General Design Criteria - 17 analysis, the health and safety of the public was not affected at any time due to this event.
3391991006 | North Anna 2 | 09/05/1991 | 02/03/1994 | 9402150187 | <strong>Failure To Place Inoperable Degraded Voltage Relay In Trip Within One Hour</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, at 1114 hours with Unit 2 operating at 100 percent power (Mode 1) it was determined that one of three timer actuation relays used in the Emergency Bus 2J Degraded Voltage (DV) circuit had failed during testing. Technical Specifications (TS) allow power operation to continue if the inoperable relay is placed in trip within one hour; however, the amount of time required to research and install the necessary jumpers exceeded the one hour limit. The Action of TS 3.0.3 was entered which requires the unit to be shutdown. Prior to initiating the unit shutdown, the necessary electrical jumpers were installed and the failed relay was, in essence, placed in trip, and power operation continued. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> In the initial assessment, the relay failure was attributed to long term heating caused by continuous energization. Subsequently, the relay was replaced and the UV/DV functional test was successfully completed. <br /><br /> No significant safety consequences resulted from this event because the other two relays on Emergency Bus 2J remained capable of performing their intended function. Also, the redundant emergency bus was fully operable. Since the DV protection circuitry was maintained in a condition that was within the design basis of the plant, the health and safety of the public was not affected at any time during this event.
3391991008 | North Anna 2 | 09/05/1991 | 09/24/1991 | 9110010140 | <strong>Failure To Replace Fuses With Resistance Measurements Outside Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, at 1000 hours with Unit 2 operating at 100 percent power (Mode 1) it was discovered that five fuses which provide secondary protection for the pressurizer heater electrical containment penetrations failed to meet the acceptance criteria of a resistance test performed on August 29, 1990. The fuses with unacceptable resistance measurements were not replaced and retested prior to unit operation as required by Technical Specification (TS) 4.8.2.5.a.3; therefore, this event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). Immediate corrective actions were to retest the five fuses and replace those with unacceptable resistance values and review records to ensure the other pressurizer heater fuses installed had acceptable resistance readings. <br /><br /> The cause of the event was personnel error due to inattention to detail. The individuals performing the test failed to recognize that the resistance data was outside the acceptance criteria.<br /><br /> No significant safety consequences resulted from this event because the primary breakers had not tripped and resistance tests performed on the pressurizer heater cables revealed no faults which could have damaged the integrity of the penetration. This was verified by the satisfactory performance of routine monthly electrical penetration leakage tests. Therefore, the health and safety of the public was not affected at any time during this event.
3391991009 | North Anna 2 | 09/20/1991 | 10/10/1991 | 9110170115 | <strong>Reactor Trip Caused By MFRV Closure Upon Failure Of Driver Card And Subsequent Safety Injection Caused By Malfunction Of The Steam Dump Control System</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1991, at 0513 hours, with Unit 2 at 100 percent power, the "B" Main Feed Regulating Valve (MFRV) closed due to a driver card failure causing a reactor trip. The initiating signal for the reactor trip was "B" Steam Generator low level coincident with a steam flow greater than feed flow mismatch. After the reactor trip, an automatic Safety Injection (SI) was initiated. The SI was initially determined to be non-valid; however, a detailed investigation revealed that a malfunction in the steam dump control system resulting in a high steam flow with low-low Reactor Coolant System (RCS) average temperature generated the SI signal. This was the sixth SI to occur on Unit 2. This event is reportable pursuant to 10CFR50.73 (a) (2) (iv), and a four hour report was made pursuant to 10CFR50.72 (b) (2) (ii). A Notification of Unusual Event was declared upon determination that the SI signal was valid. <br /><br /> The "B" MFRV closure and subsequent reactor trip was caused by failure of the valve driver card. The SI signal was caused by a malfunction in the steam dump control system which prevented the valves from modulating closed. <br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public was not affected at any time during this event.
3391991010 | North Anna 2 | 10/06/1991 | 10/31/1991 | 9111070068 | <strong>Condenser Air Ejector Isolation And Subsequent Bypassing Of Flow To The Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1991, with Unit 2 operating at 100 percent power (Mode 1) inspections were in progress for possible condenser air inleakage sources. At 2000 hours both condenser air ejectors were observed to be aligned with flow to the turbine building atmosphere, bypassing the installed radiation monitor. With the radiation monitor bypassed, the capability for automatic diversion of air ejector flow to containment upon a high-high radiation monitor alarm was defeated. The event was discovered while investigating low background radiation levels on the air ejector radiation monitor. This event is reportable pursuant to 10CFR50.73(a)(2)(v)(C), and a four hour report was made pursuant to 10CFR50.72(b)(2)(iii)(C). <br /><br /> The cause of the event was failure to provide adequate supervisory controls over a non-routine evolution. The lack of detailed procedural guidance was a contributing factor. <br /><br /> No significant safety consequences resulted from this event because the calculated total gaseous release activity was a small fraction of the allowable effluent limit. Therefore, the health and safety of the public was not affected at any time during this event.
3391991011 | North Anna 2 | 11/03/1991 | 11/27/1991 | 9112050160 | <strong>Plant Shutdown Required By Technical Specifications Due To RHR Valve Packing Failure</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1991, at 0803 hours, with Unit 2 operating at 100 percent power, Operations Department personnel noticed increased makeup flow to the Reactor Coolant System (RCS) and an increased pumping frequency of the Primary Drains Transfer Tank (PDTT). At 0841 hours identified leakage was determined to be greater than the 10 gpm limit of Technical Specification (TS) 3.4.6.2, and the Action Statement was entered. A containment entry team identified the Residual Heat Removal (RHR) System inlet motor operated valve as having an elevated leak-off temperature. At 1456 hours the unit was placed in hot standby (Mode 3) in accordance with the Action Statement. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (i) (A). A one hour notification was made pursuant to 10 CFR 50.72 (B) (1) (i) (A). <br /><br /> The cause of the event was failure of the RHR System inlet isolation valve packing. After repairing the valve packing, the RCS leakage was determined to be within Technical Specification limits and the Action Statement was cleared. <br /><br /> No significant safety consequences resulted from this event because there was no release of radioactive material to the environment. Therefore, the health and safety of the public was not affected at any time during this event.
3411991001 | Fermi 2 | 01/16/1991 | 02/15/1991 | 9102220001 | <strong>Transistor Degradation in Trip Unit Causes High Pressure Coolant Injection System Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1991, at 1530 hours, the High Pressure Coolant Injection (HPCI) inboard steam supply valve, E41-F002, unexpectedly closed during surveillance 44.020.219, "NSSSS HPCI Turbine Exhaust Diaphragm Pressure Division I Functional Test." The surveillance was stopped, a Limiting Condition for Operation (LCO) was entered with the HPCI system and the associated containment isolation valves were declared inoperable.<br /><br /> The HPCI isolation resulted from a malfunction of transistor Q8 on a Rosemount 510DU trip unit. The trip unit supplies an isolation signal to valve E41-F002. <br /><br /> The failed Rosemount 510DU trip unit was replaced with a Rosemount 710DU trip unit, as recommended in General Electric Service Information Letter (SIL) 520, "Transistor Degradation in Rosemount 510DU Trip Units." The recommendations of the SIL were being evaluated at the time of this event. The HPCI system was declared operable, and the LCO was removed at 2312 hours, on January 16, 1991.
3411991002 | Fermi 2 | 02/15/1991 | 03/15/1991 | 9103190416 | <strong>Emergency Diesel Generators 11 and 13 Concurrently Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991, both divisions of on-site emergency A.C. electrical power were declared concurrently inoperable due to one of two Emergency Diesel Generators (EDGs) from each division being inoperable. The plant entered the applicable Limiting Condition for Operation.<br /><br /> The causes of the inoperable EDGs involved two separate problems on the Woodward Governor Motor Operated Potentiometers (MOP). On EDG 13, which is part of Division 2, the MOP problem was due to a shift in the reset frequency resistance setpoint. On EDG 11, which is part of Division 1, the MOP problem was due to clutch slippage caused by a slight misalignment of its motor. <br /><br /> After realignment of the MOP motor, EDG 11 was restarted and successfully completed its operability run. Division 1 on-site power was then declared operable. After replacement of the MOP, EDG 13 was restarted and successfully completed its surveillance test. Corrective action to prevent recurrence will include periodic inspection of the MOPs on all four EDGs to detect MOP degradation prior to it affecting EDG operability.
3411991003 | Fermi 2 | 02/28/1991 | 06/07/1991 | 9106120238 | <strong>Primary Containment Atmosphere Monitoring System Flow Switch Supplied with Unsuitable Wiring Insulation</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1991, Fermi 2 was notified by Whittaker Electronic Resources Division that a flow switch manufactured by Chem-Tec for the Exo-Sensor Hydrogen/Oxygen monitoring system could contain Teflon, rather than Tefzel, lead wire insulation. Teflon is not qualified for the postulated radiation environment encountered following a design basis Loss of Coolant Accident (LOCA). <br /><br /> An investigation determined that the Division II Primary Containment Atmosphere Monitoring System (PCAMS) contained a flow switch with Teflon lead wire insulation. The immediate corrective action was to add nuclear grade heat shrink sleeving (Raychem) over the Teflon insulated wire. Later visual inspection revealed the heat shrink sleeving did not cover the entire length of the Teflon lead wires. The flow switch was subsequently bypassed in the PCAMS pump control circuit. <br /><br /> The root cause of this condition is a breakdown in the procurement process between Whittaker Electronic Resources Division and their flow switch supplier, Chem-Tec, and inadequate work instructions for the Raychem repair of the flow switch. Whittaker filed a 10CFR21 report with the NRC against the flow switch. <br /><br /> The repaired flow switch in Division II PCAMS was replaced during the Second Refueling Outage with a flow switch containing Tefzel insulated lead wires.
3411991004 | Fermi 2 | 03/12/1991 | 04/11/1991 | 9104170157 | <strong>Manual Scram Due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1991, at 0509 hours, the Off-Gas system sand filter differential pressure high alarm annunciated. At 0615 hours, operations personnel found a broken Moisture Separator Reheater (MSR) relief valve manifold drain line to the condenser, common to both the east and west MSR relief valve manifolds. The drain line was failed at the heat affected zone of a weld. There is no isolation valve between the location of the break and the condenser. At 0623 hours, the reactor was manually scrammed due to an impending loss of condenser vacuum. At 0636 hours, reactor pressure and level stabilized and the scram was reset. <br /><br /> The piping system failure occurred at a socket-welded elbow and initiated at the toe of the weld in the heat affected zone. Two pipe supports, one on each side of the failure location, had broken U-bolts. Failure of the pipe support U-bolts allowed unacceptable cyclic pipe displacements which led to the pipe failure. The piping system and supports were repaired and additional temporary supports were added to the piping system to reduce line movement.
3411991005 | Fermi 2 | 03/31/1991 | 07/03/1991 | 9107100103 | <strong>Exceeded Tech Spec Allowable Limits for Local Leak Rate Testing</strong><br /><i>Abstract:&nbsp;</i>Periodic leak rate testing of primary containment isolation valves and penetrations was completed during the Second Refueling Outage in accordance with the requirements of Technical Specification 3.6.1.2 and 10 CFR 50, Appendix J. During the performance of Type C testing, a total of 27 of the 233 valves tested, including three Main Steam Isolation Valves, exceeded their administrative allowable leakage rate and their combined leakage exceeded the limits as defined in the subject Technical Specification Limiting Condition for Operation. Also, 3 Type B tests failed their leakage criteria. <br /><br /> As necessary, containment isolation valves that exceeded their individual administrative allowable leakage rate were repaired or reworked. These valves were successfully retested.
3411991006 | Fermi 2 | 04/10/1991 | 05/10/1991 | 9105210213 | <strong>Balance of Plant Breaker Opened Causing Reactor Building Heating Ventilation and Air Conditioning Isolation</strong><br /><i>Abstract:&nbsp;</i>At 0754 hours on April 10, 1991, a "Balance Of Plant" breaker which provides 120/208 VAC feed to distribution panel 72B-4C-1 opened. Division I of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system isolated, and Standby Gas Treatment System (SGTS) automatically started. The Control Center Heating Ventilation and Air Conditioning System (CCHVAC) received an isolation signal, however, it was already in the recirculation mode for surveillance testing. <br /><br /> The isolation/actuation signals were caused by component failure. Initial troubleshooting identified the main feed breaker in distribution panel 72B-4C-1 as the cause for the loss of power. The breaker was removed and electrically tested by simulating overload conditions; the X and Z phases tripped as expected. However, the Y phase indicated an open circuit. The breaker was opened for Inspection. Contact degradation was determined to be the apparent cause for the Y phase opening. The breaker 72B-4C-1 was replaced.
3411991007 | Fermi 2 | 04/14/1991 | 05/14/1991 | 9105220167 | <strong>Error During Performance of Radiation Monitor Calibration Results in Actuation of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1991, a Radiation Protection (RP) technician was performing a calibration procedure for the Reactor Building Ventilation Exhaust Radiation Monitor. After successfully completing the calibration, the technician reset the Trip 1 and Failure indicators at the module. One of the indicators, Trip 2, had a burned out light bulb. Therefore, because it was not lighted, it was not reset. <br /><br /> While performing steps to restore the radiation monitor configuration to normal, the Trip 2 actuation logic was completed. As a result, the reactor building and control center ventilation systems were challenged and properly functioned. <br /><br /> This event was due to personnel error since the technician did not reset all the activated trips. Contributing causes were a lack of clarity in the procedure step and the failure of the indicator bulb. <br /><br /> An evaluation of this event was performed using the Human Performance Evaluation System. The procedure being used has been revised to clearly state what indications should be received and to verify that the trips are properly reset.
3411991008 | Fermi 2 | 04/24/1991 | 09/06/1991 | 9109130231 | <strong>ESF Actuation During Performance of Reactor Pressure Vessel Level Transmitter Calibration</strong><br /><i>Abstract:&nbsp;</i>At 0440 hours on April 24, 1991, unexpected Engineered Safety Feature actuations took place during the performance of a surveillance test on the Division II, Channel B reactor pressure vessel level transmitter. The plant was in a refueling outage with the reactor defueled. <br /><br /> An investigation determined the cause of the ESF actuation was due to a trip output logic switch in the wrong position on a Division I, Rosemount 510 DU trip unit, C71N650A (Drywell Pressure High). The root cause of this event was personnel error. The trip output logic switch, located on a printed circuit board in the trip unit, was inadvertently mispositioned during rework of the board. <br /><br /> Immediate corrective action was to verify that Rosemount analog trip system switches were in the correct position. A Human Performance Enhancement System report was completed. Specified procedures will be reviewed and revised, as required, to provide enhanced control over surveillance performance.
3411991009 | Fermi 2 | 04/29/1991 | 05/29/1991 | 9106040278 | <strong>Loss of Power to Bus 65F Causes Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1991, surveillance test 42.302.06, "Calibration and Logic System Functional Test of Division II 4160 Volt Emergency Bus 65F and 14ED Undervoltage Circuits", was in progress. At 0910 hours, power was lost to bus 65F and its associated buses 72F, 14ED, and 72ED. Division I of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system isolated and Standby Gas Treatment System (SGTS) automatically started. The Control Center Heating Ventilation and Air Conditioning System (CCHVAC) received an isolation signal. However, it was already in the recirculation mode for other surveillance testing. <br /><br /> Initial investigation determined that, due to personnel error, knife switch 65F-F6 was not in the correct position prior to performing step 5.2.5.10.a of 42.302.06. Subsequently, the knife switch was correctly positioned. RBHVAC and SGTS were returned to normal at 1052 hours. An accountability meeting was held for this event. The event was discussed in detail and corrective actions were determined.
3411991010 | Fermi 2 | 05/19/1991 | 06/18/1991 | 9106240006 | <strong>Failure of Control Room Ventilation Charcoal Filter Surveillance</strong><br /><i>Abstract:&nbsp;</i>During an analysis of the Control Room Emergency Filtration System's emergency make-up unit charcoal sample, it was discovered that the sample no longer met the Technical Specification 4.7.2.c.2 Surveillance requirement criteria for methyl iodide penetration of less than 1%. As a result, the system was declared inoperable on May 19, 1991 at 1245 hours. <br /><br /> There are potential contributing factors to this failure. This was the charcoal filter installed at start up of the unit and, therefore, had provided several years of service. Charcoal efficiency will degrade over time. Fermi 2 established a more conservative testing condition this time. The test temperature was lowered which was reflected in a reduction in the methyl iodide removal efficiency. <br /><br /> The charcoal was replaced and the system was declared operable. Fermi 2 will continue to comply with Technical Specifications which are intended to detect this condition.
3411991011 | Fermi 2 | 05/23/1991 | 06/21/1991 | 9106260356 | <strong>Control Center Heating Ventilation and Air Conditioning Shifts to Recirculation Mode Due to Spurious Spike of Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>At 0009 hours, on May 23, 1991, the Control Center Heating Ventilation and Air Conditioning system (CCHVAC) shifted into the recirculation mode and annunciator 3D45, "Cont. Center Makeup Air Radn Monitor Upscale Trip", was received. In accordance with the Alarm Response Procedure (ARP) an operator was dispatched to investigate the 3D45 annunciator alarm. The operator observed the Division II Radiation Monitor (MON) Trip 2 and Trip 1 lights on. The radiation monitor was reading 100 counts per minute (cpm) and its trip point is 281 cpm. The monitor was reset at 0011 hours. Approximately 8 seconds later, the monitor spiked to 1000 cpm then slowly drifted back down to a normal reading of approximately 60 cpm.<br /><br /> The cause of the event has been determined to be a spurious spike of radiation monitor D11-K813. Trouble hooting was unable to determine the cause of the spike. Engineering personnel were contacted for concurrence and agreed with the assessment made by I&C maintenance. <br /><br /> CCHVAC was restored to normal operation at 0143 hours in accordance with the ARP and system operating procedure 23.413, "Control Center HVAC System".
3411991012 | Fermi 2 | 05/25/1991 | 06/21/1991 | 9106260412 | <strong>Intermediate Range Monitor Inoperative Trip Due To Damaged Fuse Holder</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1991, a half scram signal was received from Reactor Protection System (RPS) Division I. Since RPS Division II had a half scram signal inserted for relay work, a full scram signal occurred. The plant was in a refueling outage with all control rods already fully inserted.<br /><br /> An investigation determined the half scram signal from RPS Division I was due to an inoperative trip of an Intermediate Range Monitor (IRM). The cause of this event was a damaged fuse holder which did not allow proper seating of the fuse. <br /><br /> The damaged fuse holder was replaced and the fuse was properly seated. An inspection of other fuses in the IRM system was conducted. Required reading of this event has been issued to appropriate personnel.
3411991013 | Fermi 2 | 06/01/1991 | 07/01/1991 | 9107080118 | <strong>Safety Relief Valves Set Pressure Outside Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>The Main Steam System is equipped with fifteen Safety Relief Valves (SRVs). Technical Specifications require that half of the SRVs be proven operable at least once every eighteen months by performing a met pressure test. Fifteen SRVs were removed and sent to Wyle Laboratories to meet the surveillance requirement during the recent refueling outage. Wyle Laboratories has notified Detroit Edison that while all fifteen actuated during testing, twelve of the SRVs failed their set pressure test. <br /><br /> The cause of this event is currently under review by Detroit Edison in conjunction with the Boiling Water Reactor Owners Group (BWROG) SRV Set Point Drift Committee as a generic issue. An analysis was performed shows that the peak dome pressure that would be experienced in the event of a vessel over-pressurization would be within the safety limits.<br /><br /> All spare replacement SRVs were refurbished, cleaned, retested and certified to be within tolerance prior to their installation on the main steam lines. Detroit Edison is continuing to follow the BWROG recommendations to resolve this concern.
3411991014 | Fermi 2 | 06/01/1991 | 07/01/1991 | 9107080110 | <strong>Division I Fuel Pool Ventilation Exhaust Radiation Monitor Blew Fuse Causing Engineered Safety Feature Actuation Signals</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1991, Instrumentation and Controls surveillance procedure 44.020.111, "NSSSS Fuel Pool Ventilation Exhaust Radiation, Division I, Channel C Response Time Test', was being performed. At 0805 hours, the following Engineered Safety Features (ESF) actuated: the Reactor Building Heating Ventilation and Air Conditioning system (RBHVAC) isolated, Control Center Heating Ventilation and Air Conditioning system (CCHVAC) shifted to the recirculation mode, Standby Gas Treatment System (SGTS) automatically started, and the Drywell Inert/Purge System automatically isolated. <br /><br /> The Division 1 Fuel Pool Ventilation Exhaust Radiation Monitor, D11-K609C, was in the process of being removed from its rack to install a jumper when the ESF isolations/actuations occurred. Troubleshooting of the radiation monitor's circuits was performed and power fuse F1 was found opened. The fuse was replaced and the systems affected were restored by 0854 hours. The surveillance test was successfully completed at 1120 hours.
3411991015 | Fermi 2 | 06/27/1991 | 07/29/1991 | 9108050137 | <strong>Reactor Scram Due to Overheating at Main Transformer 2A</strong><br /><i>Abstract:&nbsp;</i>At 2115 hours on June 27, 1991, a pipe was discovered glowing red on one of two main unit transformers. The glowing pipe was located at the point of contact between the low voltage side isophase bus housing and an oil line which is connected to a pipe header from the conservator tanks (oil reservoirs). A controlled plant shutdown was ordered. Self-extinguishing flames were subsequently observed and an immediate plant shutdown was ordered. The main generator breakers were manually opened resulting in a reactor scram due to a turbine control valve fast closure. <br /><br /> An investigation determined the overheating was due to a vent pipe cap in direct contact with the low voltage side isophase bus housing. The root cause has several contributing factors. The primary one is the arrangement of the vent cap port relative to the isophase bus housing and another is the use of a larger size vent cap than needed which reduced the clearance between the vent cap and the housing. <br /><br /> A small part of the isophase bus housing was ground away to re-establish the physical separation between the vent pipe cap and the housing. An inspection of other pipe caps was conducted. The Preventive Maintenance events for both transformers will be revised to include a check of the physical separation between the pipe caps and the isophase bus housing. Required reading will be conducted for the off-site utility personnel and all involved supervision.
3411991016 | Fermi 2 | 07/02/1991 | 08/01/1991 | 9108060171 | <strong>Inadvertant Closure of HPCI Isolation Valve During Performance of A Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>At 1637 hours on July 2, 1991, the High Pressure Coolant Injection System (HPCI) turbine steam supply line bypass valve inadvertently closed during the performance of a surveillance test. The resultant valve isolation was an Engineered Safety Features actuation and HPCI was declared inoperable at that time. Subsequently, the surveillance was completed and HPCI was restored to operable status at 1655 hours. <br /><br /> The cause of this event involves three main factors. First, the valve breaker rotary switch failed due to a broken snap ring. Second, failures occurred on the part of Operations personnel and Instrument and Controls personnel to properly implement existing and acceptable operations policies and practices regarding responsibilities for control over surveillance activities and equipment operation controls. Third, the application of a NOTE in the surveillance procedure was not adequately defined. <br /><br /> The failed breaker rotary switch was replaced. An accountability meeting was held with the utility personnel involved in this event and an operations critique was issued which addresses the actions to be taken to prevent recurrence. Personnel involved have been counselled regarding their actions and responsibilities during the performance of surveillance activities and appropriate disciplinary action has been issued. In addition, required reading and training for appropriate personnel will be conducted. The affected surveillance procedure has been appropriately revised.
3411991017 | Fermi 2 | 08/13/1991 | 09/12/1991 | 9109180138 | <strong>Valve E51-F062 Closed Due to Personnel Error During Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 1738 hours, on August 13, 1991, during performance of surveillance procedure, 44.020.235, "NSSS - RCIC Steam Line Pressure, Division I Functional Test", valve E51F062 closed when the Group 9 Primary Containment Isolation logic for that valve was inadvertently energized. E51F062 is the Reactor Core Isolation Cooling Turbine Exhaust Line Vacuum Breaker Isolation Valve. The logic was energized when a test instrument lead made circuit continuity. The valve was immediately reopened and plant conditions remained stable throughout the event. <br /><br /> The root cause of the event was determined to be personnel error by the Instrumentation & Controls (I&C) repairman performing the surveillance. A contributing factor was the location of the relay being measured, which is in a difficult to reach position at the bottom of a deep and narrow panel. <br /><br /> Required reading will be given to I&C personnel, and this event will be covered in detail during I&C continuous training. A Potential Design Change has been initiated to evaluate installation of test jacks, which would enable measurements to be taken from the front of this panel. This PDC will be dispositioned and planned for implementation, if needed, within the Five-Year Operating Plan.
3411991018 | Fermi 2 | 10/02/1991 | 11/01/1991 | 9111050235 | <strong>APRM Weekly Calibration Requirement Not Performed per Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991, Detroit Edison discovered that an error had been made during implementation of Technical Specification Amendment 75. This error resulted in the failure to complete one of two weekly CHANNEL CALIBRATION requirements for the Average Power Range Monitoring (APRM) system channels. Procedures which implemented CHANNEL FUNCTIONAL TEST requirements for APRM's, whose surveillance interval had been modified from weekly to quarterly by Amendment 75, also implemented a weekly CHANNEL CALIBRATION requirement. These procedures were revised without accounting for this weekly CHANNEL CALIBRATION requirement. Upon recognition of the missed surveillance requirement, all APRM's were declared inoperable. Surveillances were performed successfully and the APRM's were restored to operable status. The primary root cause of this event can be attributed to a deficiency in the process utilized during implementation of Technical Specification Amendments. Changes to this process are being made. Personnel involved in implementing Amendment 75 should have prevented the error. A review of lessons learned from this event is being done by appropriate personnel. Additionally, a Human Performance Enhancement System (HPES) evaluation will be performed to confirm this assessment of root cause, contributing factors and corrective actions.
3411991019 | Fermi 2 | 11/20/1991 | 05/20/1992 | 9205260257 | <strong>Reactor Water Cleanup System Isolations Due to High Pump Room Differential Temperature and Personnel Error During System Restoration</strong><br /><i>Abstract:&nbsp;</i>This LER describes two Engineered Safety Features (ESF) actuations of the Reactor Water Cleanup System (RWCU) on November 20, 1991. The first isolation occurred at 1051 hours due to a high differential room temperature (inside to outside the room) in the B RWCU pump room. Detroit Edison believes the cause of the high temperature which resulted in this event, to be failure (loss of calibration) of a switch in the automatic control circuit for the B RWCU pump room cooler. This switch was recalibrated and monitored until a replacement switch was procured and installed. The second isolation occurred at 2231 hours while removing a jumper, utilized during restoration of the RWCU system from the first isolation, in accordance with the system operating procedure. The cause of this isolation is believed to be a personnel error when the jumper was inadvertently grounded during removal, which resulted in a blown fuse in the isolation circuitry for one RWCU isolation valve. An accountability meeting has been held regarding this error. A design change will be implemented to modify the control circuitry for automatic RWCU system isolation due to non-regenerative heat exchanger high temperature to eliminate the need to install jumpers during system restoration following an isolation. Additionally, this LER was issued as required reading for operators and appropriate systems engineering personnel.
3411991020 | Fermi 2 | 11/20/1991 | 07/06/1992 | 9207090158 | <strong>High Pressure Coolant Injection System Start Failure During Quarterly Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1991, at 1954 hours, the High Pressure Coolant Injection System (HPCI) failed to start during performance of surveillance, 24.202.01, "HPCI Pump Time Response and Operability Test at 1000 PSI". In compliance with the appropriate Limiting Condition for Operation, the HPCI system was declared inoperable and the Technical Specification Action Statement was entered.<br /><br /> The system failed to start when the governor control valve (E4100F068) failed to open and admit steam to the HPCI turbine. The initial investigation showed that the Hydraulic Actuator (EGR), E41-K203, was not functioning, thus keeping the governor valve closed. The EGR was replaced. Post maintenance surveillance testing demonstrated that the HPCI system operated properly. On November 22, at 0612 hours, the HPCI system was declared operable. <br /><br /> Detroit Edison believes the cause of the EGR failure to be corrosion from water intrusion into the HPCI oil system. Investigation following the initial failure, subsequent surveillance testing, and a scheduled system outage determined the cause of the water intrusion to be a degraded barometric condenser vacuum pump (which was replaced following the subject EGR failure), and degraded turbine gland seals and turbine lube oil system sealing mechanisms (which were replaced in May of 1992). Procedure changes have been made to enhance monitoring of HPCI turbine vacuum during surveillance testing which should provide early warning of degrading barometric condenser vacuum pump and/or turbine sealing mechanism (carbon rings and dust collar) performance.
3411991021 | Fermi 2 | 11/27/1991 | 12/27/1991 | 9201070034 | <strong>Control Center Heating Ventilation and Air Conditioning Shifts to the Recirculation Mode During Surveillance 24.413.05</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1991, Operations, and Instrumentation and Control (I&C) personnel were performing surveillance procedure 24.413.05, "Division II Control Room Emergency Filter Auto Transfer Test". At 1315 hours, during performance of the surveillance, the Division II Control Center Heating Ventilation and Air Conditioning (CCHVAC) shifted to the recirculation mode. This occurred during step 5.1.3 of the surveillance procedure as the I&C repairman was exiting Panel H21-P296D after installing test switch leads. Division II CCHVAC was returned to normal operation at 1325 hours.<br /><br /> There were two contributing factors to the root cause of this event. First, there was an inadequate evaluation of test methods for this surveillance. However, it should be noted that the surveillance had been performed successfully in the past. Second, the I&C repairman installing the switch leads on relay T41M105 made a personnel error. <br /><br /> Procedures 24.413.05 (Division II) and 24.413.04 "Division I Control Room Emergency Filter Auto Transfer Test", will be revised so that external test equipment is not used to time the CCHVAC shift to the recirculation mode. As a result of the personnel error element, the I&C Continuing Training (Lessons Learned) Program will discuss this event.
3411991022 | Fermi 2 | 12/11/1991 | 01/10/1992 | 9201150202 | <strong>Primary Containment Negative Pressure During Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1991, operations personnel were proceeding with the planned plant shutdown for replacement of the 2A main unit transformer. The shutdown plan included utilizing two mechanical vacuum pumps to maintain Main Condenser vacuum for locating a suspected tube leak in the condenser. At 1212 hours, Drywell pressure started decreasing from 15.2 psia to 14.4 psia. The Torus to Drywell and Reactor Building to Torus vacuum breakers began lifting at 1226 hours, as designed, to control the negative pressure. At 1553 hours, the third MSIVs were closed and the Primary Containment Vacuum Breakers stopped cycling. Primary Containment pressure began increasing due to addition of nitrogen which had been started two hours earlier. Drywell pressure was restored to normal and nitrogen addition was terminated at 1922 hours. <br /><br /> Investigation established that the cause of this pressure event was a reverse flow through the Safety Relief Valves (SRVs). The flowpath was from the Drywell through the SRV vacuum breakers, producing reverse flow through the SRVs into the Main Steam Line Drains and to the Condenser, which was at a vacuum condition created by operating two Mechanical Vacuum Pumps. Operations and Plant Support Personnel were not familiar with SRV operation in the abnormal condition of a vacuum environment. Operations, Maintenance and Technical Staff and Managers training will review this event. This training will be completed the first quarter of 1992.
3441991001 | Trojan | 01/09/1991 | 02/08/1991 | 9102120019 | <strong>Inadvertent Control Building Ventilation Isolation Due to Actuation of Sulfur Dioxide Detector Power Switch While Checking the Status of Its Power Indicating Lamp</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1991, the Trojan Nuclear Plant was operating at 100 percent Rated Thermal Power. A Control Room Ventilation System isolation occurred when an operator was checking the status of a power indicating lamp on a Sulfur Dioxide detector. The causes of this event were as follows. Improper design - The power indicating lamp is an integral part of the power switch. This combined design makes it difficult to replace the lamp without actuating the switch. Inadequate labeling - The labels on the detectors did not provide warning against actuating the switch during light bulb replacement, or the protective actuation which will occur if the switch is actuated. Inadequate previous corrective action - A similar event occurred during Sulfur Dioxide detector maintenance in 1990. The corrective actions focused on causing an actuation during detector maintenance, and did not consider whether other plant personnel might cause the same type of event. <br /><br /> Caution tags were placed on both detectors indicating that attempts to change the light bulbs may de-energize the detectors. New labels will be placed on the detectors which warn against changing the light bulbs and the possibility of causing an Engineered Safety Features actuation if the switch is operated. A modification to separate the indicating lamp from the power switch will be made.
3441991002 | Trojan | 01/22/1991 | 08/12/1991 | 9108220108 | <strong>Incore Instrumentation System Thimble Tube Leak During Power Operation</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1991, the Trojan Nuclear Plant was operating at 100 percent Rated Thermal Power. At 1605, an alarm was received indicating a leak at the incore instrumentation system seal table. The seal table area radiation monitor was checked and showed an activity increase. Other monitoring instrumentation also indicated the presence of a leak from the Reactor Coolant System. The Containment process radiation monitor indicated an increase in activity, and Containment humidity had increased approximately 2 percent over previous readings. Reactor Coolant System leak rate calculations showed leakage rates near 1 gpm. At 1822, a Containment entry was made to identify and attempt to isolate the leak. At 2023, the leak was isolated. The leakage originated from an incore instrument thimble tube. The cause of the leak was tube wear due to flow induced vibration. The leak was in a tube which had been replaced in 1990 and had been in service for approximately six months. The replacement tubes were larger in diameter than the originals. The larger diameter thimble tubes were isolated and remained so until the plant was shut down for the 1991 refueling outage. Thimble tube eddy current examinations were performed during the 1991 refueling outage. As a result of those examinations, 14 tubes were repositioned. The tube which leaked and one additional tube were removed and the positions were capped.
3441991003 | Trojan | 01/30/1991 | 03/01/1991 | 9103050420 | <strong>Dilution of Sample Stream During Venting of Containment Building Results in Improperly Monitored Release</strong><br /><i>Abstract:&nbsp;</i>At 2024 on January 30, 1991, with the Plant in Mode 1 (Power Operation), venting of air from the Containment Building was begun to reduce pressure in the building. On January 31, 1991, a Chemistry Effluent Analyst reviewing the previous day's Containment Monitor System data noticed that the noble gas count rate was approximately 1,500 counts per minute (cpm) before the evolution and approximately 400 cpm after the evolution was begun. Venting was stopped at 0708. Subsequent inspection of the filter adsorber cartridge holder of the iodine monitor revealed that the O-ring which provides a seal against air leakage into the system was out of its groove through approximately 90 degrees of arc. The O-ring was returned to its groove, and the holder was reinstalled. Expected count rates were then observed. Analysis of the noble gas effluent data showed that there was a sample dilution factor of approximately 5.9 introduced by the leakage into the sample stream. Thus, the dilution of the sample stream would have allowed actual concentrations of monitored effluents to be greater than the 2 times background allowed by Trojan Technical Specifications before automatic isolation of the Containment Building ventilation would have occurred. Had a radiological accident occurred in the Containment Building during the air pressure reduction evolution, automatic isolation of the Containment Building ventilation would still have occurred well before there was any significant effect on the health and safety of the public.
3441991004 | Trojan | 02/12/1991 | 03/14/1991 | 9103200191 | <strong>Inadequate Drawings Result in Development of Inadequate Work Instructions and Lead to Inappropriate Jumper Placement and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1991, the Trojan Nuclear Plant was operating at 100 percent Rated Thermal Power. At 1020, maintenance was in progress to repair a damaged electrical conduit associated with the plant lighting system. During the course of the repairs, a wiring jumper was incorrectly installed within a lighting contactor panel, and resulted in 120 Volt A.C. power being applied to the negative leg of a 125 Volt D.C. bus. The electrical noise on the D.C. bus resulted in actuation of the Electro-Hydraulic Control Master Trip Bus, tripping the turbine. The turbine trip initiated a Reactor trip. Following the Reactor trip, Auxiliary Feedwater was initiated on a low-low steam generator level signal and Main Feedwater was isolated on a Reactor trip combined with low Tave signal. The cause of this event was the lack of adequate drawings which resulted in the preparation of inadequate work instructions. This in turn led to installation of the jumper in an inappropriate location. An Engineering Evaluation and component walkdown were performed and determined that no damage to plant components occurred. Procedures have been revised to require specific instructions for the placement of electrical jumpers.
3441991005 | Trojan | 02/15/1991 | 03/18/1991 | 9103260048 | <strong>Inadequate Procedures and Failure to Specifically Identify Conditional Surveillances Results in Improper Performance of Reator Trip System Channel Functional Tests.</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991, the Trojan Nuclear Plant was in Mode 3 (Hot Standby) following a plant trip which occurred on February 12, 1991. Because of discussion during a training class on the Trojan Operating License and Technical Specifications, it was recognized that the Channel Functional Test for the Power Range Neutron Flux Low Setpoint Reactor Trip (Low Power Trip) might not have been being completed prior to a Reactor startup as required by the Technical Specifications. A review of the surveillance documentation was performed and it was concluded that in eleven of the 29 previous startups this surveillance had been missed. On February 18, 1991, during a further review of surveillances, it was determined that the Channel Functional Test for the Turbine Trip Functional Unit of the Reactor Trip System was not being performed prior to Reactor startup as required by the Technical Specifications. The Low Power Trip missed surveillance was caused by the failure to identify this requirement as a conditional surveillance and separate it from periodic surveillance requirements. Failure to test the Turbine Trip Functional Unit at the appropriate time was due to an inadequate procedure. Procedures will be revised to clearly indicate that these surveillances must be performed prior to a Reactor startup.
3441991006 | Trojan | 03/03/1991 | 04/02/1991 | 9104050277 | <strong>Failure of Inverter Which Supplies 120 VAC Preferred Instrument Panel Results in Plant Shutdown Per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1991, the Plant was in Mode 1 at 100 percent rated thermal power. At 0720, an inverter trouble alarm was received in the Control Room. It was found that one of the 125-V dc-backed inverters supplying a 120-V ac preferred instrument panel had automatically transferred the panel to the 120-V ac bypass source. The preferred instrument panel was declared inoperable and an eight-hour Technical Specification action statement was entered. The Plant was shut down to Mode 5 because investigation and correction of the cause of the automatic transfer and noted inverter circuit damage was not accomplished within the time requirements of the action statement. An investigation determined that the most probable scenario is that the automatic transfer of the inverter was initiated by a random component failure of an integrated circuit on a logic board in the inverter. It is postulated that the automatic transfer was accompanied by a current surge which damaged inverter circuit components that may have been stressed by transfers occurring at excessive phase angle differences. The inverter was investigated, repaired, tested, and returned to service. Synchronization checks were also performed on the three remaining inverters. An adjustment was made on one of the three inverters, and adjustments will be made on the other two inverters during the 1991 Refueling Outage. Additional sets of printed circuit boards will be acquired for each of the inverters, calibrated in situ, and stored as spares so that they are available to replace the sets in the inverters if future inverter circuit failures occur.
3441991007 | Trojan | 03/07/1991 | 04/08/1991 | 9104150260 | <strong>Failure to Perform Containment Air Lock Surveillance Testing as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1991, the Plant was in Mode 5 (Cold Shutdown). A review of Trojan Technical Specification (TTS) Surveillance 4.6.1.3, Containment Airlocks, indicated that the surveillance required by the footnote had not been performed as required. The surveillance requires that air locks opened during periods when Containment integrity is not required (e.g., Mode 5) shall be tested at the end of such periods at not less than Pa (60 psig). It was verified that other required surveillance testing had been successfully performed on the Containment air locks to demonstrate that they were operable, even though the overall air lock leakage test at 60 psig required by the TTS 4.6.1.3 footnote had not systematically been performed. The investigation of this event also identified three occurrences in which the specified time interval for performing the 6 month overall air lock leakage test at 60 psig (TTS 4.6.1.3.b) had been exceeded. The procedure will be revised to ensure precise instructions exist for accomplishing the Containment air lock surveillance testing in conformance with requirements. The causes of this event were the failure of personnel to recognize and properly implement a Technical Specification surveillance requirement.
3441991008 | Trojan | 03/12/1991 | 10/15/1991 | 9110250019 | <strong>Less Than Adequate Control of Analysis and Procedure Changes Result in Potential for Fire Induced Spurious Operations to Adversely Affect Ability to Safely Shut Down</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) At 1645 preliminary results indicated that potential, fire-induced spurious operations of the pressurizer auxiliary spray valve, steam generator power operated relief valves, and the Reactor Coolant System charging flow control valve could have adversely affected the ability to safely shut down the Plant in the event of a fire. Final analysis results have indicated that if the fire-induced spurious operations of these components had occurred, then the ability to safely shut down the Plant would not have been adversely affected. It appears that these potential spurious operations of concern were not completely addressed in the "Trojan Nuclear Plant 10 CFR 50 Appendix R Review" and its implementing procedures. The root cause of the event was inadequate control of changes to the spurious operation analysis and its implementing procedures. Analysis and procedure changes have been implemented to address the specific deficiencies. Long term corrective actions included changes to the administrative controls for analysis and procedure revisions and the establishment of a centralized Fire Protection Engineering group. PGE concluded in its evaluation of the event that the existence of the deficiencies had minimal safety significance.
3441991009 | Trojan | 03/15/1991 | 06/21/1991 | 9106260377 | <strong>Electrical Components Which Lack Sufficient Documentation to Demonstrate Operability Under Low Temperature Service Conditions Due to Design Weakness</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1991 while in Mode 5 (Cold Shutdown) during a review to address equipment operability concerns identified on March 7, 199.1, Portland General Electric Company (PGE) identified that ASCO Catalog No. NP-1 solenoid valves lacked sufficient documentation to demonstrate operability for low-temperature (-5 degrees F) service conditions. The cause of these deficiencies has been determined to be weaknesses in the establishment of low-temperature minimum temperature requirements in the Trojan design basis, in equipment procurement and installation specifications and a failure to document these weaknesses in the corrective action processes in use at Trojan. The assessment of these deficiencies, including safety significance during previous power operation, and the determination of the scope of these documentation weaknesses are complete. However, of the over 5,500 components reviewed, only 6 component types/locations have been identified as requiring further safety significance assessment. These devices would have most probably performed their required safety function(s), either because the device was not seriously affected by cold weather or administrative controls for cold weather would have assured an adequate environment; or sufficient time and instructions for operator actions existed to compensate for the deficiency or redundant equipment was available. Corrective action to support Plant operation at low temperatures will be completed prior to the onset of cold weather. The public health and safety were unaffected by this event.
3441991010 | Trojan | 03/14/1991 | 08/15/1991 | 9108190228 | <strong>Emergency Core Cooling System Inoperability Due to Uncertainties Associated With Orifice Plate Coefficients</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1991, the Plant was in Mode 5 (Cold Shutdown). Evaluations performed by Westinghouse and reviewed by Trojan indicated that the Centrifugal Charging Pumps (CCP) and the Safety Injection Pumps (SIP) could be operated at flow rates in excess of the maximum flow values specified in Trojan Technical Specification (TTS) 4.5.2.f, "Emergency Core Cooling Systems Surveillance Requirements". TTS 4.5.2.f.1.b specifies a CCP total flow rate of less than or equal to 560 gpm. The actual CCP total flow rate could be 580 gpm. TTS Surveillance Requirement 4.5.2.f.2.b specifies a SIP total flow rate of less than or equal to 650 gpm. The actual SIP total flow rate could be as high as 675 gpm. Based on the data, the cause of this event was the use of improper orifice plate flow coefficients for determination of the individual injection line flow rates. On March 14, 1991, at 1700 hours the CCPs and SIPs were declared inoperable for Emergency Core Cooling System (ECCS) (Modes 1-4) and Valves MO-8801A and M-8801B, "BIT Tank Outlet Isolation Valves.", were caution tagged to preclude the use of the Boron Injection Tank as a boration flow path. Corrective actions include: flow balancing the CCP and SIP flows using new flow limits obtained from analyses, performing new analyses to support revised flow and changes to TTS Surveillance Requirement 4.5.2.f, submitting a change request to TTS Surveillance Requirement 4.5.2.f, developing calculations that indicate the total uncertainty associated with flow orifices, and performing a review of orifice plates in pipe sizes under 2 inches nominal. Based on these evaluations, it was concluded that past operation of the Trojan Plant did not represent any undue risk to the public health and safety.
3441991011 | Trojan | 05/10/1991 | 12/22/1993 | 9401060376 | <strong>Inappropriate Material In Electrical Penetration Assembly Module Seals Cause Leakage and Potential Loss of Electrical Continuity</strong><br /><i>Abstract:&nbsp;</i>During local leak rate testing on March 30, 1991, excessive leakage was identified in one Containment Building electrical penetration assembly (EPA) due to a failed seal. Although the leakage quantified on April 6, 1991 was not sufficient to cause Overall Containment Integrated Leakage to exceed acceptable values, it was subsequently decided on May 10, 1991, that the condition of the Containment EPA seals may have caused the plant to be in an unanalyzed condition. The seals were made of a material that was inappropriate for the application, and therefore possible degradation of the seals made it indeterminate whether the seals would perform their design function of ensuring containment integrity. This issue was reported pursuant to 10 CFR 21 on June 24, 1991. <br /><br /> The purpose of the EPAs was to provide for electrical continuity of the contained conductors, while maintaining containment integrity. Nitrogen is applied between the inner and outer seals to ensure continuity by preventing moisture intrusion. Following a postulated loss of coolant accident, degradation of the seals combined with a poor design would allow moisture intrusion potentially resulting in degradation of electrical continuity. The seals have been replaced with seals of a more durable material. This supplement is being submitted to indicate additional applicable reporting criteria and to provide additional details on the design and safety functions of the EPAs.
3441991012 | Trojan | 05/13/1991 | 06/12/1991 | 9106190292 | <strong>Inadequate Procedure Allows Transfer Of Instrument Bus Power Supply Which Causes Momentary De-energization Of Chlorine Detectors Which Results In Isolation Of Control Room Ventilation</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1991 the Trojan Nuclear Plant was in Mode 6 (Refueling) with no fuel movement in progress. At approximately 1346 an isolation of the Control Room normal ventilation system occurred due to an outside air toxic gas isolation signal. The signal resulted from a momentary de-energization of a chlorine detector while transferring power supplies to its instrument bus. The root cause was concluded to be inadequate operating procedures which did not identify that the isolation could occur. Corrective actions include procedure changes. Because the detectors and ventilation system operated as designed, this event was not safety significant.
3441991013 | Trojan | 03/25/1991 | 06/25/1991 | 9107020263 | <strong>Rapid Cooldown of the Pressurizer During Mode 5 Operation Due to Procedure Weakness</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1991, while in Mode 5, during boration of the Reactor Coolant System (RCS) to refueling boron concentration, pressurizer liquid space temperature decreased from approximately 425 degrees F to 145 degrees F in less than one hour. This 280 degrees F cooldown of the pressurizer liquid exceeded the Trojan Technical Specification (TTS) Section 3.4.9.2.b, Limiting Condition for Operation (LCO) of 200 degrees F in any one-hour period and placed the Plant in the associated TTS action statement. The action statement requirement was already partially satisfied because the Plant was in cold shutdown, however, pressurizer liquid space temperature was not restored within the 200 degrees F in any one-hour period limit within 30 minutes. Therefore, this Licensee Event Report (LER) is being submitted as a condition prohibited by the Plant Technical Specifications. An analysis of this event has been performed by the Nuclear Steam Supply System (NSSS) vendor. The integrity of the pressurizer vessel was not compromised by this event and ample margin exists for future operation; therefore, this event has minimal safety significance.
3441991014 | Trojan | 04/08/1991 | 05/08/1991 | 9105150186 | <strong>Missed Surveillance Testing Of Service Water Seismic Category I/II Isolation Valve Due To Scheduling Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1991, while in Mode 6, with fuel movement in progress, an engineer in the Inservice Testing (IST) organization discovered that a Service Water System seismic boundary valve (CV-3714) had not been stroke-time tested at its new monthly frequency. The test frequency had recently been increased from quarterly to monthly pursuant to Article IWV-3417 of Section XI of the ASME code. The shift supervisor was notified and core alterations were suspended. Approximately 30 minutes later, the valve had been successfully retested and core alterations resumed. The cause of the missed surveillance was an error in the scheduling of this IST Program Alert List valve. The method being utilized to prepare the schedule was not formally proceduralized. This event has no safety significance due to the subsequent testing being acceptable and the small change in stroke time (three versus two seconds) with respect to the required stroke time of 13 seconds.
3441991015 | Trojan | 04/12/1991 | 08/30/1991 | 9109040452 | <strong>Incomplete Single Failure Analysis Of Safety-Related HVAC Systems Causes Potential For Exceeding Design Temperature For Redundant Equipment Located In Common Area</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, the Trojan Nuclear Plant was in Mode 6 (Refueling). At 1600, it was confirmed that, under certain postulated Plant accident or transient conditions, a single failure of a component cooling water (CCW) pump unit cooler could have occurred without the recognition of the operators and could have allowed temperatures in the Auxiliary Building open area (45-foot elevation) to exceed the existing design temperatures. A similar problem was confirmed to exist for the service water (SW) pump room in the Intake Structure. The root cause was concluded to be that the single failure criterion was not completely applied during the original design of safety-related heating, ventilating and air-conditioning (HVAC) systems. Corrective actions have included procedural requirements to compensate for the potential single failures not previously considered. An evaluation was completed and the results indicate that there is an extended length of time before the design temperature could be exceeded (for CCW pump area) and that the equipment is able to withstand the maximum calculated temperatures (for the SW pump room). Based on the results of the evaluation, this event is not considered to be safety significant.
3441991016 | Trojan | 04/19/1991 | 05/20/1991 | 9105290142 | <strong>Missed Technical Specification Surveillance While Defueled</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1991 the Plant was in a refueling outage and the reactor vessel was defueled. During a review of Periodic Operating Test POT 24-1, "Shift Operating Routines", it was determined that some Trojan Technical Specification (TTS) surveillances required while the Plant is defueled were not consistently being performed. <br /><br /> The cause of this event was the failure to adequately incorporate TTS applicability requirements into POT 24-1. Contributing causes were the failure to define a Plant mode for the defueled condition and the failure to provide surveillance procedure writing guidance for the undefined mode (defueled). <br /><br /> A temporary change was made to POT 24-1 and the surveillances in question were performed satisfactorily. Preventive actions will include reviewing TTS to identify surveillance requirements with applicability other than Modes 1-6, issuing a definition for the defueled mode, and revising the surveillance procedure writer's guide to include the defueled mode.
3441991017 | Trojan | 01/15/1990 | 05/08/1991 | 9105150300 | <strong>Inadequate Administrative Controls Over License Change Process Results in Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1990, the Trojan Nuclear Plant was operating at 100 percent Rated Thermal Power. During a review of Technical Specification surveillances, it was noted that the Channel Calibration for the containment sump inventory measuring instruments was not being performed within the required frequency. The cause was determined to be inadequate administrative controls over the Trojan license change process. It was found that the Technical Specification originally required performance of a "Calibration Test" for the containment sump inventory measuring instruments. In 1987, the Technical Specification was amended to require Channel Calibration of these instruments. The reason stated for making the change was to provide consistency within the Technical Specifications, since "Calibration Test" was not a defined term. Administrative controls for submittal of a License Change Application did not require identifying how the requirements of the requested amendment would be met if the License Change Application was approved. In addition, no review of the license change, once it was issued, was required to ensure that procedures adequately addressed the requirements of that change. Administrative controls for processing License Change Applications and License Amendments have been implemented.
3441991018 | Trojan | 07/02/1991 | 12/03/1991 | 9112090292 | <strong>Technical Specification Surveillance Missed Due to Sensors Not Being Included in the Calibration of the Reactor Vessel Level Instrumentation System</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1991 the Plant was in Mode 5 (Cold Shutdown), following core reload during the 1991 Refueling and Maintenance Outage. During an investigation of air inleakage into Reactor Vessel Level Indication System (RVLIS) sensing lines as a potential cause for inability to calibrate transmitters, it was determined that the RVLIS channel calibration had not included the sensor bellows located closest to the reactor vessel. The 1991 RVLIS Channel Calibration which included the sensor bellows led to the identification of air inleakage into the RVLIS sensing lines. Air inleakage in these sensing lines would cause the RVLIS water level indications to be inaccurate under reduced-pressure (accident) conditions. Corrective actions include: elimination of potential sources of air inleakage; purge, evacuation, fill, and complete channel calibration of the RVLIS; procedural clarification of the requirements for performing RVLIS channel calibrations; a review for similar occurrences in Technical Specification channel calibrations; and improved administrative control of Operational Assessment Reviews for thorough technical evaluation and targeted 90-day evaluation time.
3441991019 | Trojan | 04/08/1991 | 02/28/1992 | 9203030420 | <strong>Special Report Not Submitted and Waste Gas Decay Tank Release Made When Meteorological Monitoring Instruments Were Inoperable</strong><br /><i>Abstract:&nbsp;</i>Trojan Technical Specification 3.3.3.4 "Meteorological Instrumentation" requires the preparation and submittal of a Special Report if either or both of the wind direction instruments is inoperable for more than seven days. This specification also requires suspension of releases of gaseous material from the radwaste gas decay tanks when both of the wind direction sensors are inoperable. It has been determined that the Channel "A" wind direction sensor on the 33 foot meteorological tower was inoperable for a period in excess of seven days in 1989, and a Special Report was not submitted. It has subsequently been determined that the Channel "B" wind direction sensor was inoperable for a portion of the time that the Channel "A" sensor was inoperable and that Waste Gas Decay Tank releases occurred during this period. Failure to submit the Special Report was the result of an inadequate operability determination and miscommunication. Waste Gas Decay Tank releases were made during the period when both wind direction instruments were inoperable because this condition was not recognized. The wind direction instruments were inoperable because they were loose on the mount and did not maintain alignment with the reference direction (north). The wind direction sensors were realigned on May 2, 1989.
3441991020 | Trojan | 08/16/1991 | 09/12/1991 | 9109170123 | <strong>Auxiliary Feedwater Flow Channel Checks Not Performed In Accordance With Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1991 the Plant was in Mode 5 (Cold Shutdown). During the routine biennial technical review of Periodic Operating Test (POT)-24-5, "Monthly Operating Routines", it was determined that auxiliary feedwater (AFW) flow channel checks had not been performed in accordance with Trojan Technical Specification (TTS) Definition 1.10, "Channel Check". TTS Definition 1.10 states that a channel check shall include, where possible, comparison of the channel indication with other indications derived from independent instrument channels measuring the same parameter. As performed in accordance with the surveillance procedure (POT-24-5) AFW flow channel checks did not consistently compare indicators in independent channels measuring the same parameter, even though independent channels were available. A second problem identified was that the channel check did not include all of the required AFW flow indicators. <br /><br /> The cause of this event was the failure of personnel to adequately incorporate Technical Specification Surveillance Requirements into the appropriate surveillance procedure. <br /><br /> The appropriate surveillance procedure will be revised so that the AFW channel check includes observation of the required AFW flow indicators. Preventive actions that have been taken include: establishment of a Surveillance Compliance Improvement Program, and implementation of required training for personnel performing technical reviews. This event had no effect on the health and safety of the public.
3441991021 | Trojan | 05/24/1991 | 10/22/1991 | 9110290293 | <strong>Inadequate Analysis of Shutdown Methodology Results in Potential Inability to Depressurize and Cool Down the Plant in Accordance with 10CFR Part 50, Appendix R</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1991 the Trojan Nuclear Plant was in Mode 6, during the 1991 Refueling and Maintenance Outage. A validation of Emergency Fire Procedure (EFP)-1, "Alternative Shutdown for Control Room Evacuation Caused by Fire" was being performed, on the Trojan Plant Simulator, following procedure changes which were made to address NRC identified deficiencies. During the simulation it could not be verified that the plant could be cooled down and depressurized to Residual Heat Removal System conditions, using existing procedures and the plant components analyzed to be available following a postulated worst case fire. This condition was the result of a lack of coordination and integration of resources necessary to establish a properly based approach to Appendix R implementation. This resulted in performance of inadequate analyses and in the development of procedures which were not fully supported by analyses, as the Trojan Appendix R program developed. Personnel in the various engineering disciplines involved with fire protection activities have been organized into a dedicated Fire Protection Engineering Group reporting directly to a Fire Protection Supervisor. The pressurizer Power Operated Relief Valve (PORV) control systems have been modified to enable crediting at least one of the pressurizer PORVs for post-fire Reactor Coolant System depressurization.
3441991022 | Trojan | 06/12/1991 | 07/10/1991 | 9107180163 | <strong>IST Program Relief Misinterpretation Leads To Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1991, the Plant was in Mode 5. During a review of Inservice Testing (IST) data for the residual heat removal (RHR) pumps, it was confirmed that no pump bearing temperature readings were obtained prior to returning the 'B' RHR pump to service on May 18, 1991. Portland General Electric Company (PGE) personnel had considered the American Society of Mechanical Engineers (ASME) Code requirement to monitor pump bearing temperatures to have been deleted by NRC letter dated February 28, 1991. In the NRC Resident Inspector's Monthly Exit with the licensee on June 21, 1991, PGE management was informed that a Technical Specification violation had occurred because pump bearing temperature readings were not obtained prior to returning the 'B' RHR pump to service on May 18, 1991. This Licensee Event Report (LER) is being submitted to document a condition prohibited by the Plant's Technical Specifications Title 10 of the Code of Federal Regulations, Part 50.73(a)(2)(i)(B)!. <br /><br /> Plant procedures have been revised to ensure compliance with the ASME code requirements. Bearing vibration is a more meaningful indicator of pump performance than bearing temperature. Since vibration readings taken prior to returning the 'B' RHR pump to service were acceptable this event had no effect on the public health and safety.
3441991023 | Trojan | 06/26/1991 | 07/26/1991 | 9107310149 | <strong>Inadequate Administrative Procedure and Personnel Errors Result in Missed Surveillance of Diesel Fire Pump Battery</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1991 the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) when a maintenance unit supervisor discovered that the performance of the Diesel Fire Pump battery's surveillance inspection had exceeded its monthly interval by four days. The root causes were concluded to be an inadequate administrative procedure and personnel errors. Corrective actions include procedure changes and counseling of involved personnel. Subsequent completion of the surveillance inspection indicated that the Diesel Fire Pump would have been available to perform its design function. Because of this and because of the availability of the Electric Fire Pump, this event was concluded to not be safety significant.
3441991024 | Trojan | 04/25/1990 | 07/29/1991 | 9108020215 | <strong>Improper Technical Specification Interpretation Results in Failure to Perform Alternate Sampling and Analysis While Waste Gas Oxygen Concentration Alarm was Out</strong><br /><i>Abstract:&nbsp;</i>During the period April 25, 1990 to May 10, 1990, Control Room annunciation associated with the waste gas compressor discharge oxygen concentration was out of service to support annunciator system modifications. The plant was shut down in the 1990 refueling outage during this period. Trojan Technical Specifications require continuous monitoring of the waste gas compressor discharge oxygen concentration (or collection and analysis of grab samples) during waste gas compressor operation. The waste gas compressors are normally under automatic control and it is likely that they operated several times between April 25 and May 10, 1990. Collection and analysis of grab samples was not performed while the annunciator was out of service. This was caused by a failure to correctly interpret the requirements for continuous oxygen concentration monitoring as they were written in the Technical Specifications. The Technical Specifications were amended to specify that a single alarm be Operable in the Control Room to satisfy the continuous oxygen concentration monitoring requirement. An Operations procedure was developed in 1990 to provide guidance on use of the new annunciator system. The procedure includes requirements to notify the Shift Supervisor prior to disabling an alarm and precautions to consider Technical specification requirements and compensatory actions prior to disabling an alarm.
3441991025 | Trojan | 05/08/1991 | 08/12/1991 | 9108220014 | <strong>Inadequate Technical Specification Surveillance on the Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1991, the Plant was in Mode 6 (Refueling). During a review of Emergency Diesel Generator (EDG) load ratings, it was determined that the surveillance performed in accordance with the Trojan surveillance procedure did not adequately meet the intent of the Trojan Technical Specifications (TTS). The TTS requires that each EDG be demonstrated operable by verifying that the auto-connected loads to each diesel generator unit do not exceed the 2,000-hour rating of 4,752 kW. As performed by the surveillance procedure, the EDG loads were not representative of accident condition loads. For example, the Engineered Safety Features pumps were on recirculation in lieu of injecting into the Reactor Coolant System (RCS) at the higher accident flows and loads. The event resulted from the failure of personnel to adequately implement a TTS surveillance requirement. <br /><br /> An operability determination was performed which verified that the EDG loads were within the TTS limits. Other corrective and preventive actions include: establishment of a Surveillance Compliance Improvement Program, and training of personnel involved in procedure development and review. In addition, an engineering calculation which verifies that EDG TTS load requirements are not exceeded will be added to the surveillance program. This event had no effect on the health and safety of the public.
3441991026 | Trojan | 07/24/1991 | 08/21/1991 | 9108260241 | <strong>Lightning Strike Causes Distribution System Undervoltage and Results in Automatic Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 Refueling and Maintenance Outage. Plant electrical loads were being supplied from the Trojan switchyard via the Startup Transformers. The "B" Train Emergency Diesel Generator was out of service for maintenance. A lightning storm was in progress and was causing transmission system disturbances resulting in cycling of various system breakers. At 1054, a lightning strike resulted in a momentary undervoltage condition on the distribution system grid, which was sensed by relays on the secondary side of the plant startup transformers. The relays actuated and caused an automatic start of the "A" Emergency Diesel Generator. The undervoltage condition on the transmission system was caused by a lightning strike. The Emergency Diesel Generator start was initiated by a protective relay which sensed the undervoltage condition on the secondary (12.47 KV) side of one of the plant startup transformers. There are two levels of undervoltage protection provided at the 4.16 KV level which provide sufficient undervoltage protection for the plant. Portland General Electric Company is evaluating removal of the 12.47 KV undervoltage Emergency Diesel Generator start relay scheme to eliminate unnecessary Emergency Diesel Generator starts.
3441991027 | Trojan | 08/13/1991 | 04/27/1992 | 9205010227 | <strong>Steam Generator Inspections Result in C-3 Classification</strong><br /><i>Abstract:&nbsp;</i>During the 1991 Refueling and Maintenance outage at the Trojan Nuclear Plant, examination of the Steam Generators was conducted and resulted in each of the four Steam Generators being classified in Category C-3 per Trojan Technical Specification 4.4.5.2, Reactor Coolant System - Steam Generators. Analysis of eddy current examinations, using standard bobbin coil and motorized rotating pancake coil techniques, resulted in 1580 tubes plugged and 1017 tubes sleeved (some tubes have multiple sleeves) among the four Steam Generators. Eight Steam Generator tubes were removed for metallurgical analysis. The metallurgical analysis revealed that tube wall degradation had occurred at the tube support plates due to outer diameter stress corrosion cracking and intergranular attack (ODSCC/IGA). PGE applied for and was granted an amendment to the Trojan Plant Operating License which clarified Technical Specification Surveillance Requirement 4.4.5.4.a.6, "Repair Limit", for determining serviceability of tubes with ODSCC/IGA. The revised technical specification allows for a repair limit that addresses structural integrity. The plant chemistry program and other operating parameters are being evaluated to determine whether improvements can be made to slow the rate of, or arrest, further tube degradation.
3441991028 | Trojan | 08/08/1991 | 08/30/1991 | 9109100215 | <strong>Inadequate Procedure Which Did Not Completely Implement A Technical Specification Change Results In Missed Surveillances Of Seismic Gap Seal Fire Barriers</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1991 the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) when a determination was made that some fire barrier surveillances required by Trojan Technical Specification (TTS) 4.7.9, "Penetration Fire Barriers", had not been completed. The surveillances were not completed for penetration fire barriers numbered 3550 through 3557 which provide seals for the seismic gaps at the ceilings of the walls of the Diesel Auxiliary Feedwater Pump (DAFP) and Turbine AFP (TAFP) rooms, (Turbine Building, 45-foot elevation). The root cause for not having the seals in the surveillance program was concluded to be an inadequate procedure which did not completely implement a TTS change. A short term corrective action included a review of other seismic gaps which identified eight other seals that should have been included in the surveillance program and had not been. The seismic gap seals have subsequently been added to the penetration fire barrier surveillance program. The event was concluded to not be safety significant because, in the as-found condition, sufficient protection remained to prevent fire propagation.
3441991029 | Trojan | 08/15/1991 | 11/26/1991 | 9112040231 | <strong>Potential for Control Room Doses to Exceed Design Limits Following a Fuel Handling Accident Due to Incorrect Analysis</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 refueling outage. During a review of a Final Safety Analysis Report (FSAR) amendment regarding Control Room habitability systems, the Plant Review Board raised a question regarding the design of the Control Room Area Radiation Monitor (ARM-11). It was questioned whether ARM-11 must be safety related in order to fulfill its design function to isolate the Control Room upon detection of radiation associated with a fuel handling accident. ARM-11 is neither safety related, nor redundant, and it is not properly configured to provide automatic Control Room isolation as assumed in FSAR analyses. Therefore, maintenance of operator doses within the limits of General Design Criterion 19 following a fuel handling accident could not have been assured. This condition appears to be the result of an original plant design error. The original FSAR evaluation of a fuel handling accident was performed under the assumption that the Control Room was isolated. <br /><br /> However, there was no explanation of how the isolation was to be initiated, nor does the placement of the ARM-11 detector support this assumption. Installation of a safety-related radiation monitoring system for the Control Room ventilation system, which will assure that the Control Room is isolated if a fuel handling accident occurs, is now planned for the 1993 refueling outage.
3441991030 | Trojan | 08/26/1991 | 12/16/1991 | 9112260006 | <strong>Inadequate Administrative Controls For The High Energy Line Break Evaluation Program Results In Potential For Both Trains Of Safety Related System To Be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1991 the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) when a determination was made that if a high energy line break (HELB) were to occur in the Main Steam Support Structure (MSSS), it would have the potential to render the diesel auxiliary feedwater pump (DAFP) inoperable. A subsequent review identified the turbine auxiliary feedwater pump (TAFP) to have a similar problem for a different HELB. The root causes of the event were concluded to be: (1) a mismatch existed between the experience level of the personnel and the complexity of the analysis, and (2) there was a lack of dedicated organization and supporting procedures to assure that HELB documentation interfaces were understood, reviewed and maintained. Corrective actions include(d) modifications to eliminate operability concerns for the DAFP and the TAFP, organizational changes to address the shortcomings, a revision to the review methodology for HELB induced environmental effects and an assessment of the adequacy of previous HELB analyses. Each auxiliary feedwater pump provides a redundant capability to the other and neither would be rendered inoperable as a result of the same HELB. If the remaining pump was assumed to fail per the single failure criterion, then the non safety-related electric AFP could also have been available. Based on the availability of the redundant pump and the electric AFP, the event is considered to have minimal safety significance.
3441991031 | Trojan | 08/31/1991 | 09/30/1991 | 9110280288 | <strong>Inadequate Corrective Action and Personnel Errors Result in Late Surveillance Tests for Fire Protection Water Sprays Systems</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) for a refueling outage. Planning and Control Management had requested an investigation of completion histories on Fire Protection Water Spray Systems (EIIS Code KP) surveillances as part of routine preparations to verify required completion dates. Investigations concluded that Technical Specification surveillances had not been performed within their allowable interval. Root causes were concluded to be inadequate corrective action from a previous similar event, and personnel errors. Because of this repeat occurrence, a program review and evaluation of scheduling system upgrades, and an investigation for similar occurrences, will be conducted. Based on the acceptable completion of water spray system surveillances, the Water Spray Systems would have been available to perform their design function. Therefore, PGE has concluded that this event was not safety significant.
3441991032 | Trojan | 07/23/1991 | 09/29/1992 | 9210060122 | <strong>Inadequate Procedural Controls Result in Safety Valve Ring Settings not in Accordance with Vendor Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 refueling outage. The "A" and "B" Trains of the Component Cooling Water System (CCW) were cross connected with the "A" CCW Pump in operation. At 2125, the "B" CCW Pump was started. At 2152, an alarm indicating low level in the "B" CCW surge tank was received in the Control Room. The two CCW trains were isolated from each other and at 2158, the "B" CCW Pump was stopped. An operator was dispatched to the Containment to locate the source of the water loss. At 2215, the operator in the Containment reported that a relief valve in the "A" Train of the CCW System was leaking. The leak was stopped at 2230 after the "A" CCW pump was stopped and system isolation valves were hand tightened. <br /><br /> The valve lift setpoint was about 120 psig rather than 150 psig as required. The nozzle ring setting was also found to be substantially different from the required setting. It was determined that there was inadequate control over the setting of nozzle rings. It was reported in Revision 1 of this report that ring settings of 54 valves were set to the position specified by the vendor. On August 6, 1992, it was discovered that the ring setting for one of the 54 valves was not set to the vendor specification. The ring setting was correctly set to the vendor specification on August 7, 1992.
3441991033 | Trojan | 10/22/1991 | 11/21/1991 | 9111260233 | <strong>Inadequate Training and Administrative Controls Result in Incorrect Main Steam Safety Valve Control Ring Settings</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991 the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 refueling outage. An inspection of a Main Steam Safety Valve (MSSV) was being done to resolve discrepancies between procurement and design documents regarding the valve's orifice size. The orifice size was in accordance with plant design requirements, however, the valve control ring settings were incorrect. The remaining MSSV control ring settings were checked. On October 22, 1991 it was concluded that six of the MSSVs were inoperable during the 1990 operating cycle. This condition was determined to be the cumulative result of inadequate training, procedures, supervisory methods and evaluation of previous industry and plant specific events. Specific training was developed and the MSSV control rings were set to the specified values, by qualified personnel. The training program for relief and safety valves will be upgraded. Corrective Maintenance Procedures will be developed for the MSSVs and other safety/relief valves in use at Trojan. Maintenance and surveillance activities will be evaluated to identify areas where data trending or technical reviews should be done to ensure timely detection of problems. A structured root cause evaluation to determine actions necessary to improve the technical adequacy of reviews performed under the Operational Assessment Review Program will be done.
3441991034 | Trojan | 09/05/1991 | 10/07/1991 | 9110160175 | <strong>Personnel Error Causes Incomplete Performance of a Surveillance Test for Liquid Radwaste Automatic Isolation</strong><br /><i>Abstract:&nbsp;</i>During review of a Plant surveillance test procedure on September 5, 1991, it was determined that a channel functional test for a process radiation monitor in the liquid radwaste effluent line did not include an isolation function specified in Trojan Technical Specification Table 4.3-8 footnote (1). Investigation concluded that personnel error resulted in omitting the required verification of automatic isolation from channel functional test procedures. Since the time this requirement was issued (Amendment 99, December 1984), improved administrative controls have been implemented to translate Technical specification amendments into applicable Trojan procedures. The event was concluded to not be safety-significant because design function has been demonstrated by test and operating procedures stipulate manual isolation if necessary.
3441991035 | Trojan | 11/15/1991 | 06/24/1992 | 9208100314 | <strong>Technical Specification Surveillance for Fire Detectors was Missed and Found Not to Completely Implement Testing Requirements Due to Inadequate Procedures and a Personnel</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1991 the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) when it was discovered, during a Quality Assurance audit of fire protection activities, that a Control Building Switchgear Room Smoke Exhaust and Smoke Detection System surveillance had not been performed within its required surveillance interval. In addition, the surveillance test did not fully implement Technical Specification surveillance requirements for fire detector instrumentation. The root causes were determined to be an inadequate administrative procedure, an inadequate test procedure, and personnel error. Procedure changes will be implemented as the corrective actions for these events. In addition, the surveillance test was revised to incorporate fully the missing surveillance requirements. Subsequent completion of the surveillance test indicated that the Control Building Switchgear Room's smoke detectors would have been able to perform their design function. In addition, an hourly fire patrol was in effect for the area during the period of the exceeded surveillance interval. For these reasons these events were concluded to not be safety significant.
3441991036 | Trojan | 11/10/1991 | 12/10/1991 | 9112130062 | <strong>Radiation Monitor Control Switch Malfunction Results in Containment Ventilation</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 refueling outage. Containment purging was in progress. At 2242, the operators were adjusting the alarm and trip, setpoints of the gas channel of the Containment Process and Effluent Radiation Monitor (PERM 1C). After the adjustment, the setpoints were checked. When the high alarm setpoint was checked, a high radiation alarm was received, and a Containment Ventilation Isolation Signal was generated, resulting in closure of the Containment purge valves. This even was caused by a failure of the "High" alarm indicator/switch to operate as designed, probably due to age related wear. This switch is used when setting the high alarm setpoint. When the switch is depressed, it is supposed to disable the output relays and prevent the alarm and isolation from occurring. The switch was cleaned and reinstalled. During post-maintenance testing it was found that the switch was still not functioning correctly. The switch was then replaced and tested satisfactorily. The "High" alarm pushbutton switches on other plant PERM's which supply Engineered Safety Feature Actuation Signals will be replaced during the next regularly scheduled calibration on those monitors. This event did not affect plant safety. This event resulted in the generation of a spurious high radiation alarm. The Containment purge valves properly closed in response to the signal.
3441991037 | Trojan | 12/11/1991 | 01/30/1992 | 9202040056 | <strong>Failure to Comprehensively Test Manual Engineered Safety Features Actuation Functions, Process Radiation Monitor and Permissive and Block Functions due to Deficiencies in Surveillance Test Program</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1991, a review of Engineered Safety Features Actuation System instrumentation surveillance procedures was being done in response to previously identified surveillance deficiencies. The review identified that Surveillance Procedures did not adequately test the ESFAS functions associated with manual initiations. It was also found that Containment Process and Effluent Radioactivity Monitor sampling instruments were not being properly surveilled. It was further found that the ESFAS and Reactor Trip System interlock functions were not being tested properly. These conditions were the result of inadequate translation of Technical Specification Requirements into surveillance test processes. The root cause was judged to be a lack of detailed understanding of the extent and depth of the Technical Specification surveillance Requirements and past management expectations for compliance. Procedures are being developed and will be performed to address the specific surveillance deficiencies. Special training on the Technical Specifications has been provided to selected personnel and incorporated into the Technical Staff training program. Implementation of a Consolidated Program Plan for Trojan surveillance Program Improvement began in November of 1991. This plan addresses both the administrative (scheduling and work control) and technical deficiencies in the Trojan surveillance program.
3441991038 | Trojan | 11/27/1991 | 12/24/1991 | 9112300294 | <strong>Dropped Filter Results in High Airborne Particulate Activity Inside Containment and Generation of a Containment Ventilation Isolation Signal</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 refueling outage. At approximately 2243, Control Room personnel were notified that a contaminated air filter had been dropped, inside containment, while it was being moved in preparation for disposal. The filter had been used to collect particles generated during the honing of Steam Generator tubes. At 2302, the "High" alarm setpoint of the Containment Radiation Monitoring System, particulate channel (PERM-1A), was reached and a Containment Ventilation Isolation Signal was generated. The Containment purge and hydrogen vent valves were already closed so no component movement occurred. The filter was dropped when it was lifted over a railing using a long handled tool. A similar event occurred on September 19, 1991. Corrective actions following that event did not install sufficient barriers to prevent recurrence. An in depth failure analysis was performed from generation of a contaminated filter through placing it in a high integrity container for disposal. Based on the analysis, a number of corrective actions were generated, including: 1) specific work instructions were written, 2) the filter lifting tool and its use were modified, and 3) personnel were trained on the new requirements.
3441991039 | Trojan | 12/26/1991 | 03/30/1992 | 9204020173 | <strong>Spurious Chlorine Detector Alarm Causes Automatic Control Building Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1991, the Trojan Nuclear Plant was in Mode 5 (Cold Shutdown) during the 1991 refueling outage. At 1734, the control room received a "Toxic Gas Damper Isolation" alarm, indicating actuation of a toxic gas monitor. Upon receipt of the alarm, the operators entered Off-Normal Instruction 54 "High Toxic Gas Concentration" and verified that the control building ventilation systems had automatically shut down, as required. The operators also determined that the "B" chlorine monitor was the source of the alarm. At 1736, the Turbine Building watch reported that chlorine was not present. The operators reset the chlorine monitor and left it bypassed until the cause of the actuation was investigated. The cause of the chlorine monitor actuation could not be determined. On December 31, 1991, the sensor on the "B" train chlorine monitor was replaced and the monitor was returned to service. On January 18, 1992, the same monitor began to operate erratically. It was declared inoperable and placed in bypass continued investigation into the cause revealed that the actuation was the result of transmitter output signal fluctuations to the monitor corrective actions include detector component replacement, procedure changes and a setpoint change. The failed detector components will be returned to the vendor for additional analysis.
3461991001 | Davis-Besse | 03/11/1991 | 04/10/1991 | 9104180114 | <strong>Monthly Functional Test Of Reactor Trip Module Logic Did Not Verify All Combinations.</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1991, at 1409 hours, a system engineer discovered that the monthly functional test procedures for Reactor Protection System (RPS) trip module logics may not adequately satisfy the requirements of Technical Specification 4.3.1.1.1, Table 4.3-1, Item 13. The test verified proper operation of one contact from each of the four from output relays in the Reactor Trip Module. This contact provides a dim-bright operation of indicator lamps. However, the other contacts from these output relays, which are used in the two-out-of-four trip logic circuitry, were not verified to operate properly for all possible combinations. After further evaluation, it was confirmed that the surveillance requirement was not being completely satisfied. The inadequacy was due to a procedure revision in 1981. The cause was an inadequate technical review. <br /><br /> At 1930 hours on March 11, 1991, a test using the appropriate indications was satisfactorily completed. On March 22, 1991, test procedures, DB-MI-03011 through 03014, were revised to permanently incorporate these changes. <br /><br /> The current procedure change process requires a more extensive review and approval which helps prevent incorrect revisions to procedures.
3461991002 | Davis-Besse | 09/01/1991 | 10/01/1991 | 9110090129 | <strong>Failure to Perform Source Range Nuclear Instrument Surveillances</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1991 at 0251 the plant entered Mode 3, Hot Standby in preparation for a refueling outage. At approximately 1100 on September 1, 1991, it was determined that surveillance tests for the Source Range Neutron Flux and Rate instruments required by Technical Specification 4.3.1.1.1 had not been performed to assure operability prior to entry into Mode 3. The applicable action statement (Technical Specification 3.3.1.1, Table 3.3-1, Action 6) was immediately invoked. The required surveillances were satisfactorily completed at 1445 on September 1, 1991 and the action statement was exited.<br /><br /> The apparent cause of this event was inadequate administrative controls for scheduling required surveillance tests for mode changes during reactor shutdown. Additionally, procedures did not contain requirements for verifying that the Source Range Neutron Flux and Rate instrument surveillance tests were satisfactorily completed prior to entry into Mode 3. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B).
3461991003 | Davis-Besse | 09/08/1991 | 10/08/1991 | 9110150400 | <strong>Inadvertent Safety Features Actuation During Maintenance/Modification Activities</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1991 at 0635 hours with the plant in Mode 5 for the seventh refueling outage, the station experienced an inadvertent Safety Features Actuation System (SFAS) Level 1 actuation during the calibration of a Containment Radiation High Trip Bistable (RSHH2005). Channel 4 of SFAS had been previously de-energized for the installation of SFAS Shutdown Bypass Modification 90-0006. Channel 2 of SFAS was tripped during the channel calibration. These two conditions on complimentary SFAS channels resulted in an inadvertent SFAS Level 1 actuation. The ESF systems responded to the Level 1 actuation as designed. <br /><br /> The cause of the event was inattention to detail. The personnel involved failed to recognize the abnormal condition prior to testing one channel of SFAS while another channel was de-energized. The personnel involved in the incident were reminded that tripping a SFAS channel in Test Trip Bypass concurrent with a de-energized complimentary SFAS channel will cause an SFAS actuation. Additionally, maintenance procedures will be changed to provide additional caution and guidance when testing SFAS.
3461991004 | Davis-Besse | 10/12/1991 | 11/11/1991 | 9111190087 | <strong>Deficient Reactor Protection System Response Time Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1991, with the plant in Mode 5 for the seventh refueling outage (7RFO), Systems Engineering identified that Reactor Protection System (RPS) response time testing did not adequately satisfy the requirements of Technical Specification Surveillance Requirement 4.3.1.1.3. The delay time of an ITE relay in the Shunt Trip Device (STD) of the Reactor Trip Breakers (RTBs) was not measured or accounted for in overall RPS response time testing. Automatic actuation capability was provided to the STD under Facility Change Request (FCR) 84-026 based on Generic Letter 83-28 guidance. Testing showed the delay was bounded by the 14 msec specified by the relay vendor. A review of past data revealed that with the 14 msec delay considered, the High Flux/Number of Reactor Coolant Pumps On trip function would have exceeded its allowable response time limit from December 1986 to March 1988 by 7.5 msec. This test deficiency was a result of an inadequate technical review of the FCR package and its supplement.<br /><br /> On October 22, 1991, RPS overall response time calculation procedures were revised to account for the 14 msec delay and were performed. All functional units were within their respective allowable response time limits. <br /><br /> Current procedures involving plant modifications require more extensive review and approval which should ensure that changes such as this are thoroughly evaluated and documented.
3461991005 | Davis-Besse | 10/11/1991 | 11/11/1991 | 9111190075 | <strong>Inadvertent Safety Features Actuation Due to Spurious Spike on Containment Radiation Monitor RE2007</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1991 at 1417 hours with the plant in Mode 5 for the seventh refueling outage, the station experienced an inadvertent Safety Features Actuation System (SFAS) Level 1 actuation when SFAS Channel 4 containment radiation monitor (RE2007) spuriously spiked. The spike occurred after RE2007 was calibrated following movement from containment into the shield building annulus in preparation for entry into Mode 4. Channel 1 of SFAS had been previously de-energized for the installation of SFAS Shutdown Bypass Modification 90-0006. This condition allowed the spurious trip of a single channel to cause an SFAS actuation. <br /><br /> This event occurred because of the spurious spike on RE2007 and of the design of SFAS which does not allow SFAS to be de-energized without failing the output devices to their safety positions/status. <br /><br /> SFAS Shutdown Bypass Modification 90-0006 is being installed to protect against unnecessary Engineered Safety Feature actuations.
3461991006 | Davis-Besse | 11/05/1991 | 02/05/1993 | 9302170140 | <strong>Analysis of Post Large Break LOCA Boron Concentration was Potentially Nonconservative</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, with the plant in Mode 2, Toledo Edison determined that analysis of boron concentration in the core after a large break LOCA of a cold leg was potentially non-conservative. A preliminary safety concern (PSC 2-91) was initially evaluated by Babcock and Wilcox Nuclear Services Company (NSSS vendor). The evaluation concluded that the boron dilution flow path through the reactor vessel vent valves would not carry two phase flow path for the forty day period previously predicted. The NSSS vendor had not accounted for the effect of the plenum cylinder in the reactor vessel when modeling the boiling in the plenum region. <br /><br /> Subsequent analysis takes credit for flow through passive gaps which exist between the core support shield and the hot leg nozzles. This flow path, by itself, is adequate to prevent boron precipitation. Active boron dilution flow paths, while unnecessary from an anlytical standpoint, provide added assurance. The preferred active boron dilution flow path will establish forward flow through the core via the decay heat drop line and will prevent boron precipitation even without credit for gap flow. A procedure change to the Davis-Besse operating procedures has been made which assures use of this flow path. A second active flow path, which induces reverse flow through the core using the pressurizer auxiliary spray line, also is available for long term use.
3461991007 | Davis-Besse | 12/06/1991 | 03/30/1992 | 9204060192 | <strong>Shutdown Required by Technical Specifications due to Emergency Diesel Generator Problems</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1991, at 0500 hours, Emergency Diesel Generator (EDG) 1-2 was taken out of service for routine maintenance. Post maintenance testing was unsuccessful. The symptoms of the failure indicated a defective speed switch. The 72 hour action statement of TS 3.8.1.1(a) expired on December 6, 1991, at 0500 hours and a plant shutdown was commenced. Hot Standby (Mode 3) was reached at 1054 hours on December 6, 1991. Toledo Edison's request for a temporary waiver of compliance to allow the plant to remain in Hot Standby for up to seven days while performing troubleshooting was granted on December 6, 1991. <br /><br /> Troubleshooting identified a defective speed switch. Upon replacement of the speed switch, EDG 1-2 was successfully tested and restored to operable status at 0205 hours on December 11, 1991. The plant commenced startup and MODE 1 was achieved at 1117 hours on December 11, 1991. <br /><br /> The initiation of the plant shutdown required by TS was reported to the NRC via Emergency Notification System (ENS) at 0834 hours on December 6, 1991 under 10 CFR 50.72 (b)(1)(i)(A). <br /><br /> The completion of a plant shutdown required by TS is being reported as an LER under 10 CFR 50.73(a)(2)(i)(A).
3461991008 | Davis-Besse | 12/10/1991 | 04/28/1992 | 9205050235 | <strong>Reactor Trip Due to Blown Fuse During Maintenance on Non- Essential 4160V AC Bus D2</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1991 at 0906, with the plant in Mode 3, work was being performed on non-essential 4160V AC Bus D2 which resulted in a blown fuse. This caused the reverse phase sequence undervoltage relay for Bus D2 (relay 47/D2) to actuate. Although no actual undervoltage condition existed, actuation of relay 47/D2 caused select Bus D2 load breakers to trip including the Motor Driven Feedwater Pump (MDFP) feeder breaker. The loss of the MDFP resulted in a loss of feedwater to the Once Through Steam Generators (OTSGs), and the subsequent actuation of the Steam and Feedwater Rupture Control System (SFRCS). The SFRCS initiated Auxiliary Feedwater, isolated Main Feedwater, and isolated Main Steam, as designed. In addition, the SFRCS actuation initiated the Anticipatory Reactor Trip System (ARTS) which tripped open the Control Rod Drive (CRD) trip breakers. The group one rods, which were 100% withdrawn, properly inserted into the reactor core. Automatic plant response was satisfactory and operator actions were appropriate. The blown fuse was replaced and feedwater was restored by restarting the MDFP approximately 15 minutes after it tripped. <br /><br /> Based on the results of a multi-disciplinary review team, the following corrective actions will be implemented to prevent similar events: development of a checklist for work affecting 4160V or 13.8KV PT fuses; enhanced pre-evolution briefings; and additional training for Electrical Maintenance Relay Technicians.
3461991009 | Davis-Besse | 12/08/1991 | 01/09/1992 | 9201150023 | <strong>Seal Test Not Performed on Emergency Air Lock</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1991, with the plant in Mode 1, the Containment Emergency Air Lock (CEAL) inner door was cycled by Radiological Control (RC) personnel during the performance of DB-HP-01101, Containment Entry, to verify that the strong backs were removed from the CEAL inner door. On December 10, 1991, at 1130, with the plant in Mode 3, the Shift Supervisor discovered the time limit for performance of Technical Specification (TS) Surveillance Requirement 4.6.1.3.a had expired and declared the CEAL inoperable. Due to a miscommunication and conflicting information regarding CEAL alarm function, the CEAL outer door was tested and the CEAL was declared operable at 2355, on December 10, 1991. Plant startup commenced and proceeded to Mode 1. Subsequent to Mode 1 entry, the Shift Supervisor was informed that the CEAL inner door had been cycled on December 5, 1991. The CEAL was again declared inoperable. Both the inner and outer CEAL doors were satisfactorily tested and the CEAL was declared operable at 1604, on December 11, 1991. This event was caused by a deficiency in DB-HP-01101 and a miscommunication between RC and Operations personnel. <br /><br /> The strong backs are currently being stored outside the CEAL outer door in the CEAL block house. DB-HP-01101 has been changed to reflect the new storage location and to require notification of the Shift Supervisor in the event either CEAL door is opened. Troubleshooting of the CEAL inner door limit switch will be completed prior to the end of the Eighth Refueling Outage. DB-OP-02004, Reactor Coolant Alarm Panel 4 Annunciators, will be revised by January 31, 1992, to indicate the current alarm function of the CEAL..
3481991001 | Farley 1 | 01/23/1991 | 02/15/1991 | 9102190139 | <strong>Missed Fire Watch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1440 on 01-23-91, it was recognized that an hourly fire watch patrol required by Technical Specification 3.3.3.9 was not being performed. A fire watch was required because a control room alarm had been disabled due to recurring spurious alarms. The Shift Foreman Operating who established the fire watch patrol inadvertently established the fire watch in the wrong area of the Auxiliary Building. The required firewatch was established at 1445 on 01-23-91. <br /><br /> This event was caused by cognitive personnel error. <br /><br /> The Shift Foreman Operating involved has been counseled.
3481991002 | Farley 1 | 04/08/1991 | 07/10/1991 | 9107160373 | <strong>Temporary Strainers Found In The Suction Piping Of The 1B And 1C Charging Pumps</strong><br /><i>Abstract:&nbsp;</i>While repairing a leaking flange on the suction of the 1C charging pump, a temporary strainer was found installed in the pump suction piping. This strainer was not in accordance with plant design and should not have been installed. All charging pumps on both units were inspected and a similar strainer was found installed in the suction piping of the 1B charging pump. <br /><br /> The strainers have been removed from the suctions of the 1B and 1C charging pumps. <br /><br /> An evaluation of the effect of these strainers was performed. This evaluation determined that there is no evidence that the temporary strainers would have prevented the fulfillment of the safety function of the charging pumps.
3481991003 | Farley 1 | 04/30/1991 | 05/13/1991 | 9105220255 | <strong>Steam Generator Tube Degradation</strong><br /><i>Abstract:&nbsp;</i>The following report is being submitted in accordance with Technical Specification 4.4.6.5.a and c. <br /><br /> During the Unit 1 Tenth Refueling Outage (U1RF10), eddy current inspections were performed on 100% of the available tubes in all three steam generators (SGs). As a result of this inspection a total of 214 tubes previously in service (2.13% of the total number of tubes inspected) were found to be defective which requires inspection results to be classified as Category C-3. Plugs were removed from a total of 228 previously plugged tubes in three SGs and these tubes were returned to service. Following these actions, the percentage of tubes plugged in each SG is 4.22%, 2.27% and 3.10% in SGs 1A, 1B and 1C, respectively. <br /><br /> In addition to the required tube plugging, several ongoing programs have been established to reduce the probability of future tube degradation.
3481991004 | Farley 1 | 04/23/1991 | 05/28/1991 | 9106040343 | <strong>RWST Water Inadvertently Drained To Containment</strong><br /><i>Abstract:&nbsp;</i>At 2030 on 4-23-91, approximately 5000 gallons of water from the refueling water storage tank (RWST) were drained to the containment floor. This occurred when maintenance personnel partially opened motor operated valves (MOVs) in the containment spray system and created a flowpath from the RWST to the containment spray pump sump suctions. <br /><br /> Maintenance personnel had obtained permission from the Shift Supervisor (SS) to partially open five valves using the manual operators. This was part of the test and restoration following work on the valves. The SS released all the valves for work assuming that one valve would be tested at a time. The maintenance personnel partially opened all the valves prior to stroking them electrically thus creating the flowpath. <br /><br /> This event was caused by cognitive personnel error. The SS failed to adequately control test and restoration of the valves. <br /><br /> When notified of the spill, plant operators closed the valves. No plant equipment was damaged. All outage work was stopped except for activities associated with the steam generators. During the 4-23-91 night shift and the 4-24-91 day shift, the General Manager - Nuclear Plant (GMNP) met with supervisory personnel to discuss prevention of errors.<br /><br /> The SS involved in this event has been disciplined. All SSs were reinstructed on the importance of controlling work activities.
3481991005 | Farley 1 | 05/18/1991 | 09/11/1991 | 9109170128 | <strong>Mode Changes Performed While A Valve In the TDAFWP Flow Path Was Misaligned</strong><br /><i>Abstract:&nbsp;</i>At 0445 on 05-18-91 and at 1510 on 05-19-91, the unit changed operational modes while a valve in the flow path for the turbine driven auxiliary feedwater pump (TDAFWP) was not in its correct position. On 05-17-91, Maintenance personnel had performed a time response test on the TDAFWP per procedure FNP-1-STP-256.18. This test required the recirculation bypass valve on the TDAFWP, Q1N23V008, to be unlocked and opened, which rendered the TDAFWP flow path inoperable. The valve was not closed prior to entering Modes 2 and 1. <br /><br /> This event was caused by procedural inadequacy. The procedure step restoring the valve to the closed and locked condition was signed off by Maintenance as being complete even though the valve was not closed. This occurred since the Maintenance procedure did not require an Operations sign-off for an Operations task. <br /><br /> Upon discovery, Q1N23V008 was closed and locked. FNP-1-STP-256.18 has been revised to require Operations personnel to sign off the step documenting the valve to be closed and locked. In addition, all plant procedures will be reviewed for cases where a group other than the primary performing group is required to perform a procedure step. Any procedures found in this posture will be evaluated as to the need for a specific sign-off from the group completing the task. This review and necessary revisions will be completed by September 15, 1991.
3481991006 | Farley 1 | 05/24/1991 | 06/20/1991 | 9106260361 | <strong>Inadvertent OTDT Reactor Trip During Testing</strong><br /><i>Abstract:&nbsp;</i>At 0050 on 05-24-91, with the unit operating at approximately 78 percent power, a reactor trip occurred when the two-out-of-three coincidence was satisfied for over-temperature-delta-temperature (OTDT). Work in progress on pressurizer pressure instrument PT456 required channel II of OTDT to be placed in the tripped condition. During the same time period, a portable instrument was attached to what was believed to be a spare resistance temperature detector (RTD) in channel I to support an unrelated test. However, the RTD was actually the one used by the OTDT channel. Attaching the test instrument to the RTD caused the second channel of OTDT to enter the tripped condition and the coincidence for a reactor trip was satisfied. <br /><br /> This event was caused by failure to request a drawing revision when a spare RTD was placed in service in 1977. Therefore, drawings used by the designer in the development of the 1991 RTD bypass removal design change did not show that a spare RTD had been placed in service. The post-modification test of the new RTD installation was not sufficiently thorough to detect this condition. <br /><br /> All the associated wiring has been verified to be in agreement with the current RTD bypass removal design change. The appropriate Maintenance and Plant Modifications personnel will be trained on this event.
3481991007 | Farley 1 | 06/29/1991 | 05/11/1993 | 9305170262 | <strong>Reactor Trip Following Actuation Of Protective Relays On The 1B Unit Auxiliary Transformer</strong><br /><i>Abstract:&nbsp;</i>At 2045 on 6-29-91, a Unit one reactor trip occurred. Two of the neutral overcurrent relays on the 1B unit auxiliary transformer (UAT) actuated resulting in a generator trip. By design, the generator trip caused the turbine to trip and the turbine trip caused the reactor to trip. <br /><br /> The low and high setpoint neutral overcurrent relays on the 1B UAT actuated as a result of an electrical fault. The fault was caused by a broken strand of a multiple stranded conductor coming into contact with the grounded core frame structure of the transformer. The multiple stranded conductor is located in the transformer oil box and connects the transformer winding to the transformer output bushing. <br /><br /> The conductor was repaired by removing the loose strand and reinsulating the conductor. The integrity of the conductor and crimp connection was verified prior to reinstallation of the insulation. <br /><br /> The 1B UAT was returned to service on 3-16-93 at 0227.
3481991008 | Farley 1 | 08/02/1991 | 08/28/1991 | 9109050104 | <strong>Reactor Trip Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0001 on 8-2-91, with the unit operating at 100 percent power, an automatic reactor trip was initiated due to loss of power to reactor coolant pump (RCP) breaker position indication for 1C RCP breaker. This occurred when a systems operator (SO) reset a breaker which appeared to be tripped. This breaker supplies power to 120 volt regulated panel 1E which in turn provides power to the 1C RCP breaker position contact. Above 35 percent power a reactor trip is generated when an RCP breaker opens. Loss of power to the breaker position contact causes solid state protection to generate an RCP breaker reactor trip. The breaker supplying power to the 1C RCP breaker did not actually open. <br /><br /> This event was caused by cognitive personnel error. The control room plant operator granted permission to reset the breaker which provides power to 1C RCP breaker position indication contact without verifying the function of the breaker or determining the cause of the apparent tripped condition. <br /><br /> The personnel involved have been counseled. Also, this event will be included in the next cycle of licensed and nonlicensed operator retraining. <br /><br /> A caution label which reads "Opening this breaker may cause a reactor trip" has been placed on the four associated breakers in Unit 1 and the four associated breakers in Unit 2.
3481991009 | Farley 1, Farley 2 | 08/19/1991 | 09/17/1991 | 9109200228 | <strong>Reactor Trip Caused By Lightning Induced Deenergization Of 1B Startup Transformer</strong><br /><i>Abstract:&nbsp;</i>At 1720 on 08-19-91, while operating at approximately 100 percent power, a reactor trip occurred. A lightning induced deenergization of the 1B startup transformer (SUT) caused the loss of 1B and 1C reactor coolant pumps (RCPs). The reactor tripped due to RCP breakers opening while at 100 percent power. <br /><br /> A lightning strike in the 230KV switchyard caused an instantaneous overcurrent trip on phase 2 of the 1B SUT. The deenergization of the 1B SUT caused a loss of power at 4160V buses B and C which deenergized 1B and 1C RCP. The plant responded to the loss of B train offsite power as designed with the automatic start and tie-on of the 1B and 2C Diesel Generators (DG) to the B train Engineered Safety Feature (ESF) 4160V buses G and J. This restored power to the B train ESF equipment. A train offsite power was not lost during this event. <br /><br /> Inspection and testing of 1B SUT, the oil static cables and the associated switchyard breakers revealed a damaged phase 2 lightning arrestor located at the 1B SUT 230KV terminal. The damaged lightning arrestor was replaced, and the 1B SUT returned to service. <br /><br /> An engineering study to investigate possible methods of preventing lightning induced reactor trips has been initiated. <br /><br /> The unit returned to power operation at 0921 on 08-21-91.
3481991010 | Farley 1 | 10/03/1991 | 11/01/1991 | 9111070008 | <strong>Manual Reactor Trip Due To Unexpected Governor Valve Closure</strong><br /><i>Abstract:&nbsp;</i>At 0606 on 10-03-91, while operating at 100 percent power, the operators manually tripped the reactor in accordance with FNP-1-AOP-13, "Loss of Main Feedwater." <br /><br /> The sequence of events resulting in the manual reactor trip began with the main turbine control system's unexpected automatic closure of the main turbine governor valves. The operators responded by placing the main turbine digital electro-hydraulic control system (DEHC) in "Turbine Manual" which stopped the governor valves' closure at 15 percent open. The ensuing plant transient resulted in both steam generator feed pumps (SGFPs) tripping on low suction pressure. <br /><br /> This event was caused by a degraded DC voltage output from the primary Operator Auto Controller (OAC) power supply in the main turbine DEHC system and a failure of the circuitry which should have transferred the power supply. This degraded voltage resulted in a change of several control parameter values within the primary OAC prior to its complete failure. These degraded control parameters were passed to the back-up OAC which resulted in continued governor valve closure until the system was placed in manual by the operators. <br /><br /> The degraded power supply was replaced and the primary OAC programming was reloaded. A DEH Task Force is continuing the investigation of this failure and will evaluate corrective action to prevent recurrence.
3481991011 | Farley 1, Farley 2 | 10/23/1991 | 11/22/1991 | 9111270165 | <strong>Inadequate Test of CCW Sample Cooling Supply Check Valves</strong><br /><i>Abstract:&nbsp;</i>On 10-23-91, during a procedure review, it was discovered that FNP-2-STP-23.8, "Component Cooling Water Valve Inservice Test" contained an inadequate system lineup for determining if component cooling water (CCW) check valve Q2P17V288 would seat against reverse flow as required. FNP-1-STP-23.8 was found to have the same deficiency. As a result of this review it was determined that check valves Q1P17V288 and Q2P17V288 had not been adequately tested per Technical Specification 4.0.5. Both check valves were declared inoperable and manually isolated. Each Unit initiated a 72 hour Limiting Condition for Operation (LCO) for the on-service train of CCW at 1630 on 10-23-91. These check valves are located in the CCW return line from the Gross Failed Fuel Detector (GFFD) and sample coolers for their respective Unit. <br /><br /> This event was caused by procedural inadequacy.<br /><br /> FNP-1-STP-23.8 and FNP-2-STP-23.8 were revised on 10-23-91 to provide a correct system alignment for the determination that check valve Q1(2)P17V288 prevents CCW flow in the reverse direction. A test of the Unit 1 valve using the revised procedure was performed satisfactorily, and the corresponding LCO was cleared at 2340 on 10-23-91. The Unit 2 valve, however, did not pass the revised procedure criteria. A Maintenance Work Request (MWR) was written, and corrective maintenance was performed. Post maintenance testing of Q2P17V288 was satisfactorily completed using the revised procedure, and the Unit 2 LCO was cleared at 1205 on 10-25-91.
3481991012 | Farley 1, Farley 2 | 12/29/1991 | 01/27/1992 | 9202030167 | <strong>Procedural Inadequacies for Verifying the Interlock Action of the RHR System From the RCS</strong><br /><i>Abstract:&nbsp;</i>On 12-29-91, during a procedure review, it was discovered that FNP-2-STP-11.5, "RHR Suction Valve Automatic Isolation Test", did not include a verification that the Reactor Coolant System (RCS) loop to Residual Heat Removal (RHR) pump suction valves Q2E11MOV8701A, Q2E11MOV8701B, Q2E11MOV8702A and Q2E11MOV8702B could not be opened from the main control board (MCB) when RCS pressure is above the automatic closure setpoint (700 psig). The verification of this interlock is part of the required surveillance testing associated with Technical Specification 4.5.2. In addition, prior to 3-1-88 this requirement had not been incorporated into FNP-1-STP-11.5 for the corresponding system in Unit 1 and therefore the surveillance had not been performed. <br /><br /> This event was caused by procedural inadequacy. <br /><br /> FNP-2-STP-11.5 has been revised to provide verification of the interlock and to include this as an acceptance criterion. Unit 1 procedure FNP-1-STP-11.5 previously contained a step to verify the interlock but not as part of the acceptance criteria. The Unit 1 procedure has also been revised to include verification of the interlock as an acceptance criterion.
3521991001 | Limerick 1 | 01/08/1991 | 02/06/1991 | 9102120181 | <strong>Loss of Reactor Enclosure Secondary Containment Integrity due to a Reactor Enclosure Overpressurization Transient causing a Blowout Panel to Actuate.</strong><br /><i>Abstract:&nbsp;</i>On 01/07/91, at 1545 hours, while placing the normal Reactor Enclosure (RE) Heating, Ventilation, and Air Conditioning (HVAC) system in operation, three of the four operating RE HVAC supply and exhaust air fans tripped. However, the 'A' RE HVAC supply air fan continued to operate, resulting in a RE high positive air pressure condition. The power supply breaker for the 'A' RE HVAC supply air fan was manually tripped and the fan then shutdown. At 1630 hours, operations personnel restarted the RE HVAC system, however, the system experienced difficulty in maintaining the RE negative differential pressure. The third RE HVAC exhaust air fan was placed in operation and RE negative differential pressure was reestablished. At 1900 hours, an open RE blowout panel was discovered. The Technical Specifications (TS) ACTION for loss of RE Secondary Containment Integrity (SCI) was entered and required restoring RE SCI or to complete a plant shutdown by 1100 hours on 01/08/91. On 01/08/91, at 0920 hours, reinstallation of the blowout panel was complete and RE SCI was restored. Following this event on 01/08/91, plant personnel determined that RE SCI actually became inoperable at 1545 hours and not at 1900 hours, which required the plant to be in Hot Shutdown by 0745 hours on 01/08/91. Therefore, the TS ACTION had not been met within the required time period. There was no radioactive release as a result of this event. The cause of the RE HVAC system problems was due to equipment failures. The equipment failures are being evaluated and this event will be discussed at operator training.
3521991002 | Limerick 1, Limerick 2 | 01/09/1991 | 01/18/1991 | 9101280008 | <strong>Inoperability of the Seismic Monitoring System for More Than 30 Days due to the Mechanical Failure of the Magnetic Tape Playback System</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1990 at approximately 0900 hours, the Limerick Generating Station (LGS) common Seismic Monitoring System (SMS) was determined to be inoperable when Surveillance Test (ST) procedure ST-2-036-606-0, "Seismic Monitoring - Triaxial Time-History Accelerometer/Recorder Functional Test (XRSH VA-107)," could not be completed satisfactorily. The SMS engineer initiated a purchase requisition for the replacement of the cassette drive unit of XRSH-VA-107. On January 9, 1991, at 0900 hours, the replacement cassette drive unit and associated printed circuit boards had not been received despite being expedited. Therefore, the SMS became inoperable for more than 30 days requiring the submission of a Special Report in accordance with Technical Specifications (TS) Section 3.3.7.2. No seismic events occurred while the SMS was declared inoperable. The actual and potential consequences of this event were minimal. The cause of the malfunction was noise being transposed onto the recorded signal on the cassette tape. XRSH-VA-107 was repaired and returned to service on January 10, 1991. The SMS was declared operable at 1530 hours on January 10, following satisfactory completion of ST-2-036-606-0. A comprehensive review to determine if there are adequate stock levels of spare parts for all the SMS is being performed, and is expected to be completed by January 31, 1991.
3521991003 | Limerick 1 | 01/13/1991 | 01/23/1991 | 9101280209 | <strong>Inoperability of the Loose-Part Monitoring System for more than 30 days due to a faulty electrical component in one system.</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1991, the Limerick Generating Station (LGS) Unit 1 Loose-Part Monitoring System (LPMS) was inoperable for more than 30 days requiring submittal of a Special Report in accordance with the requirements of Technical Specifications (TS) Section 6.9.2. On December 5, 1990, during an independent verification of a Surveillance Test (ST) procedure, ST-2-036-640-1, "Loose Part Monitoring System Channel Functional Test," the system engineer identified that the Digital Loose Part Locator (DLPL) circuit of the LPMS was in a "lockup" condition and could not be reset. It was then concluded that the LPMS was incapable of responding to a potential loose part event. The LPMS had entered a 30 day action requirement as required by TS Section 3.3.7.10 on December 14, 1990, when the Unit 1 Operational Condition (OPCON) was changed from OPCON 4 (Cold Shutdown) to OPCON 2 (Startup). As a result, on January 13, 1991, the 30 day time limit for returning the LPMS to operable status expired requiring the submittal of a Special Report in accordance with TS Sections 3.3.7.10 and 6.9.2. The cause of the malfunction has not yet been determined with certainty beyond recognizing that a faulty component in one of the DLPL printed circuit boards is the probable cause. A purchase requisition has been initiated to replace all the boards in the DLPL circuit. The new DLPL circuit boards are expected to be replaced by March 1, 1991, which will enable the LPMS to be returned to an operable condition.
3521991004 | Limerick 1, Limerick 2 | 01/23/1991 | 02/22/1991 | 9103040099 | <strong>Missed Technical Specifications Surveillance Requirements on fuel zone and neutron flux instrumentation.</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1991, we determined that Technical Specifications (TS) Surveillance Requirements (SR) had not been satisfied for TS Section 3.3.7.5, "Accident Monitoring Instrumentation," for Reactor Pressure Vessel (RPV) level and neutron flux monitoring instrumentation, without the associated TS ACTIONs being taken. Review of previous Surveillance Test (ST) procedures and Preventive Maintenance (PM) work, combined with satisfactory performance of required channel checks upon discovery of the condition, led us to conclude that the associated RPV level and neutron flux instrumentation would have performed as designed in the event of an accident. The cause of this event was personnel error resulting in procedural deficiencies. The cause was related to misinterpretation of the requirements of TS. The result of these misinterpretations was that procedures did not require monthly channel checks of the Source Range Monitors (SRMs) and Intermediate Range Monitors (IRMs) in Operational Condition (OPCON) 1, or 18-month channel calibration and monthly channel checks for fuel zone level indication instrumentation in OPCONs 1 and 2. Channel calibration Surveillance Test (ST) procedures have been written to ensure performance of the 18-month calibration TS SRs on fuel zone level indication instrumentation. System Engineers are revising procedures to ensure performance of monthly channel checks TS SRs on SRMs and IRMs in OPCONs 1 and 2, and the fuel zone level instrumentation in OPCONs 1 and 2.
3521991005 | Limerick 1 | 01/30/1991 | 02/27/1991 | 9103040323 | <strong>Incorrect Restoration of a Pressure Differential Switch Initiates a Spurious High Drywell Pressure Signal Causing an Engineered Safety Feature Actuation.</strong><br /><i>Abstract:&nbsp;</i>On 1/30/91, during performance of a Surveillance Test (ST) procedure, an Instrumentation and Controls (I&C) technician incorrectly restored a pressure differential switch (PDS) to operation causing a spurious Division 1 High Drywell Pressure (HDP) signal. The spurious Division I HDP signal initiated an Engineered Safety Feature (ESF) actuation, and various partial logic actuations. The ESF actuation and the partial logic actuations were immediately reset by Operations personnel. The actual consequences of this event were minimal. Had this event occurred during an operational condition in which the Reactor Pressure Vessel (RPV) pressure was below 455 psig, the potential for an unexpected Emergency Core Cooling System (ECCS) injection existed. The primary cause of this event was procedural non-compliance by an I&C technician. A significant contributing factor to the cause of this event was that the valving sequence for restoring the PDS is unusual and is reversed from the normal method in which other PDSs in the plant are restored. The I&C technicians involved in this event were counseled regarding the requirement for strict procedural compliance. To prevent the recurrence of a similar event, the equalizing valves for four (4) subject PDSs will be closed and their respective valve handles will be removed. The associated ST procedures for these PDSs will be revised to reflect this change. Until this corrective action is completed, warning labels have been installed on the PDSs.
3521991006 | Limerick 1, Limerick 2 | 02/18/1991 | 03/18/1991 | 9103220302 | <strong>This LER reports the actuation of the Primary Containment and Reactor Vessel Isolation Comtrol System due to a personnel error.</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1991, while the Shift Technical Advisor (STA) was instructing an STA trainee on the Radiological Meteorological Monitoring System (RMMS), an 'undefined' Wide Range Accident Monitor (WRAM) channel item number was selected at the Safety-Related Data Access Panel (RM-23) located in the Main Control Room. This caused an actuation of the Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature (ESF), resulting in the generation of a radiation isolation signal for the Drywell and Suppression Pool Purge Supply and Exhaust valves. However, no valve movement occurred since these valves were in the closed position during this event. The consequences of this event were minimal in that all associated plant systems and equipment performed as designed and there was no radioactive material released. The cause of this event was due to personnel error when the STA and STA trainee exceeded the direction provided by a system procedure while interrogating the RMMS. The STA and STA trainee used a RM-23 channel item number that is not listed in Procedure RMMS-301, "Operation of the Main Control Room Panel 00C691." The STA and STA trainee were counseled on the importance of performing a thorough review of procedures prior to their performance and on operating systems within procedural bounds. However, to reinforce procedure compliance, this LER will be incorporated into the continuing training program for appropriate operations personnel.
3521991007 | Limerick 1 | 02/26/1991 | 07/26/1991 | 9107300086 | <strong>Condition Prohibited by Technical Specifications in that Surveillance Requirements were not performed for a Fire Rated Barrier due to Procedural Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1991, we determined that a Technical Specifications (TS) Surveillance Requirement (SR) had not been satisfied for TS Section 3.7.7, "Fire Rated Assemblies," without the associated TS ACTIONs being taken in the specified time period. This condition has existed since the April, 1989 performance of Surveillance Test (ST) procedure ST-7-022-920-1, "Unit 1 Refuel Fire Rated Assembly Inspection," when an inappropriate Temporary Procedure Change was implemented. Upon discovery of the condition, fire protection personnel verified operability of the fire detection equipment, and posted the appropriate firewatch. Upon visual inspection of the involved fire rated barrier, we determined that no degradation of the barrier existed and therefore, it was capable of performing its intended function during the period in question. This, combined with the existing automatic detection and suppression capability on the opposite side of the fire rated barrier, and the low combustible loading, lead us to conclude that the potential consequences of this event were minimal. The cause of this event was personnel error leading to a procedural deficiency. On March 25, 1991, the missed TS SR was completed satisfactorily. A comprehensive review of the ST procedure was performed to ensure that all other fire rated assembly TS SRs were met. Deficiencies identified during this review were described in Unit 1 LER 91-014 submitted on July 1, 1991.
3521991008 | Limerick 1, Limerick 2 | 03/08/1991 | 12/11/1991 | 9112170551 | <strong>This LER reports a condition prohibited by TS in that eight Primary Containment isolation valves were inoperable due to inadequate torque switch settings.</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1991, Limerick Generating Station maintenance personnel performed diagnostic testing to support the design basis engineering review for Generic Letter 89-10, "Safety-Related Motor-Operated Valve Testing and Surveillance." This testing was performed on a Unit 2 Primary Containment (PC) motor-operated butterfly valve (MOBV) associated with the PC Purge and Exhaust system. However, maintenance personnel discovered that this valve and seven other similar type valves had torque switch settings that would result in the MOBV tripping on high torque before the valve could adequately close and seat in the event these valves were required to close during a differential pressure condition. These eight MOBVs were declared inoperable and the applicable Unit 1 and Unit 2 PC penetrations were isolated by deactivating and securing the redundant PC isolation valves in the closed position. The actual consequences of this condition were minimal and there was no release of radioactive material to the environment. The cause of this, event is the result of an inadequate industry testing method used for torque seated MOBVs installed during the Unit 1 and Unit 2 construction and startup testing programs. The investigation into the cause of this event concluded that generic implications are limited to torque seated MOBVs. The torque switch settings for the eight affected MOBVs have been adjusted after application of the Valve Operator Test and Evaluation System.
3521991009 | Limerick 1 | 04/12/1991 | 05/13/1991 | 9105240194 | <strong>Reactor SCRAM resulting from a Spurious Loss of the DC Electrical Power Supply to the Main Turbine Electrohydraulic Control System.</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, a Unit 1 reactor SCRAM and a partial Group VIC Primary Containment and Reactor Vessel Isolation Control System actuation occurred following a Main Turbine trip. The Main Turbine trip resulted from a spurious loss of the 125 volt DC electrical power supply to the Electrohydraulic Control (EHC) system. Following the SCRAM, all control rods fully inserted, reactor pressure increased to 1103 psig, and level decreased to approximately -20 inches instrument level. The Reactor Core Isolation Cooling (RCIC) system was manually operated to maintain reactor level when a loss of normal feedwater injection occurred. All systems operated as designed except for the normal feedwater system in which operator interaction occurred. Operations personnel successfully controlled the plant shutdown using the appropriate plant procedures. The cause of the loss of the 125 volt DC electrical power supply to the EHC system was due to a loose copper link inside a switch cabinet. The cause of the loss of normal feedwater injection was due to a personnel error resulting from a misinterpretation of the indications for the Condensate Filter Demineralizer system. The copper links were replaced with hard wire connectors, and an evaluation of other similar switch cabinets with copper links will be performed. Operator training will be implemented to address this specific loss of normal feedwater injection incident.
3521991010 | Limerick 1, Limerick 2 | 04/18/1991 | 07/25/1991 | 9107290271 | <strong>This LER reports the inadvertent isolation of the Refuel Floor Secondary Containment and initiation of the 'B' Standby Gas Treatment system due to a suspected valve leak.</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1991, during surveillance testing, an isolation of the Refuel Floor Secondary Containment (RFSC) occurred, an Engineered Safety Feature (ESF) actuation. This was due to a low negative differential pressure signal (i.e., a negative differential pressure approaching zero) between the RFSC and the outside environment. The 'B' train of the standby Gas Treatment System also started, an ESF actuation. There were no adverse consequences and no radioactive material was released to the environment as a result of this event. The RFSC was not required to be operable since there were no core alterations, movement of irradiated fuel, or, operations with a potential for draining the reactor vessel prior to, or during this event. The cause of this event was the generation of a false differential pressure signal resulting from a suspected small leak across a manifold equalizing valve for a Refuel Floor differential pressure transmitter (PDT). Instrumentation and Control personnel performed a leak check of tubing and valves and re-performed the surveillance test with satisfactory results. No leaks were identified and the pressure transient could not be reproduced. Surveillance tests were revised to require only one outside air header isolation valve to be closed during performance of this procedure. This will allow the PDT associated with the Refuel Floor to sense normal outside air volume pressure while redundant pressure instrumentation is being calibrated thus eliminating any effect from a minor leak in an equalizing valve.
3521991011 | Limerick 1, Limerick 2 | 04/25/1991 | 05/30/1991 | 9106050277 | <strong>This LER reports a condition prohibited by Technical Specifications where the 'B' loop of ESW was inoperable due to personnel errors resulting from deficient instructions.</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1991, plant personnel discovered that a condition prohibited by Technical Specifications (TS) had existed for approximately 10 hours on April 25, 1991. A TS Surveillance Requirement (SR) had not been met for two safeguard bus undervoltage relays coincident with the 'B' Emergency Service Water (ESW) system pump being out of service. This resulted in the 'B' loop of ESW being inoperable and the TS Action to shutdown the plant was not taken within the required time. The actual consequences of this event were minimal in that there was no accident requiring ESW to perform its design function and no radioactive material was released to the environment. This event was the result of personnel errors resulting from deficient written instructions for notifications when TS SR are not met and for the planning of system outages. An immediate corrective action was placed into effect to provide written notification to shift Operations personnel of TS required Surveillance Test procedures that are approaching or past their overdue dates. The guideline for communicating impending out-of-surveillance conditions due to expiration of the SR time interval will be revised to clarify the expectation of the communications between the work groups and Shift Supervision. The guideline for the performance of system outages will also be enhanced to clarify the impact on component and system operability when electrical distribution systems are declared inoperable.
3521991012 | Limerick 1 | 05/08/1991 | 06/07/1991 | 9106140068 | <strong>Loss of Reactor Enclosure Secondary Containment Integrity due to a Reactor Enclosure Overpressurization Transient causing a Blowout panel to open.</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1991, at 1220 hours, the normal Reactor Enclosure (RE) Heating, Ventilation, and Air Conditioning (HVAC) system was secured for performance of the Standby Gas Treatment System (SGTS) and Reactor Enclosure Recirculation System (RERS) flow verification Surveillance Test (ST), and the RE high differential pressure (dp) annunciator alarmed. The status lights for the RE HVAC Supply air fans were checked and indicated that no supply air fans were operating. Performance of the ST continued, but the SGTS experienced difficulty in maintaining the required RE negative dp. At 1249 hours, a RE blowout panel was discovered open causing a loss of RE Secondary Containment Integrity (SCI). The opening of the blowout panel was caused by the 'C' RE HVAC supply air fan over-pressurizing the RE, after the RE HVAC system was secured. The necessary actions and repairs were implemented, and the RE SCI was restored at 1326 hours on May 8, 1991. The radioactive release as a result of this event was limited to less than 0.01 percent of the Offsite Dose Calculation Manual Limits. The cause of the malfunctioning 'C' RE HVAC supply air fan was due to a burned out power supply breaker trip coil. An investigation of the trip coil failure identified no apparent cause. The Preventive Maintenance (PM) procedures for the 480 volt power supply breakers will be revised to inspect for evidence of trip coil degradation. A routine PM task will be initiated to inspect frequently operated 480 volt breakers every six months.
3521991013 | Limerick 1, Limerick 2 | 05/08/1991 | 06/06/1991 | 9106140078 | <strong>Both trains of the Standby Gas Treatment System were inoperable as a result of cognitive personnel error.</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1991, during the performance of Surveillance Test (ST) Procedure ST-6-076-250-11 "SGTS and RERS Flow Test," the 'A' trains of the Standby Gas Treatment System (SGTS) and Reactor Enclosure Recirculation System inadvertently shutdown and the manual Unit 1 Reactor Enclosure (RE) Secondary Containment isolation signal, which was present for the test, cleared. Licensed Main Control Room (MCR) personnel manually initiated the redundant Unit 1 'B' RE Secondary Containment isolation signal in an attempt to start the 'B' train of the SGTS. However, the 'B' train of SGTS did not initiate. With both the 'A' and 'B' trains of SGTS inoperable, Technical Specifications (TS) Action 3.0.3 was entered. An operator found Slide Gate Damper SGD-076-206-1 in the closed position which had been closed during application of a blocking permit. The closed SGD-076-206-1 which caused the Unit 1 RE Secondary Containment isolation signal to be bypassed was then opened. Both trains of the SATS were declared operable and TS Action 3.0.3 was exited. The actual consequences of the event were minimal, however, SATS could not have controlled the release of radioactive material in the event of an accident. The cause of this event is cognitive personnel error, less than adequate communication, and a failure to comply with a procedure. Corrective actions include a review of open blocking permits, counseling of operations personnel, tagging of devices, development of a case study for training use, and a review of existing guidance.
3521991014 | Limerick 1, Limerick 2 | 05/30/1991 | 07/09/1991 | 9107120132 | <strong>Failure to perform Technical Specifications Surveillance Requirements as a result of procedural deficiencies caused by personnel error.</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1991, following review of Unit 1 and Unit 2 Fire Rated Assembly Surveillance Test (ST) procedures, we determined that Technical Specifications (TS) Surveillance Requirements (SRs) for both Units 1 and 2 had not been satisfied for TS Section 3.7.7, "Fire Rated Assemblies," thereby rendering the affected assemblies inoperable and the associated TS ACTIONs were not taken in the specified time period. These conditions have existed since issuance of the fuel loading licenses for each unit. Upon discovery of the conditions, fire protection personnel verified operability of fire detection equipment, and posted the appropriate firewatches. Upon visual inspection of the involved accessible fire rated assemblies, we determined that no degradation of the assemblies existed and therefore, they were capable of performing their intended function. Firewatches have been established appropriately to satisfy TS ACTIONs for the inaccessible assemblies. The procedure writer was not thorough in identifying all TS fire rated assemblies in the original revision of the ST procedure. The cause of this event was personnel error resulting in procedural deficiencies. The ST procedures will be revised prior to their next performance to ensure completion of all TS SRs. To address generic concerns, review of fire damper and penetration seal ST procedures was conducted, which revealed one deficiency which will be corrected by revision of the ST procedure.
3521991015 | Limerick 1 | 05/28/1991 | 07/05/1991 | 9107110095 | <strong>This LER Reports Pressure Setpoint Drift of the Main Steam Safety Relief Valves due to Corrosion Induced Bonding within the valves which has been a Repetitive problem</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1991, Limerick Generating Station personnel identified that pressure setpoint testing of the fourteen reactor Main Steam System Target Rock Corp., Model 7567 F, pilot operated two-stage safety relief valves (SRVs) revealed that only three SRVs lifted within the Technical Specifications (TS) required limit of 1% of the nameplate setpoint as specified in TS Section 3.4.2. The root cause for the setpoint drift of the eleven SRVs was primarily corrosion induced bonding between the pilot disc made of either stellite or stainless steel (SS) and the stellite seat. The fourteen SRVs were all refurbished using stellite pilot discs, pressure tested, and recertified prior to being reinstalled during the first Unit 2 refuel outage. There were no actual adverse consequences or release of radioactive material as a result of this condition. This condition was determined as reportable on June 6, 1991, since this condition resulted in more than two independent trains becoming inoperable in a single safety system due to a single cause. Therefore, this report is being submitted in accordance with the requirements of 10CFR 50.73(a)(2)(vii).
3521991016 | Limerick 1 | 06/10/1991 | 07/10/1991 | 9107160279 | <strong>This LER reports a condition prohibited by Technical Specifications where reactor pressure was increased above 150 psig with the RCIC system inoperable.</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1991, during a Unit 1 reactor startup, reactor pressure was increased above 150 psig with the Reactor Core Isolation Cooling (RCIC) system not operable as required by Technical Specification (TS) Section 3.7.3. The plant entered a TS specified condition (reactor pressure greater than 150 psig) when the requirements of the TS Limiting Condition for Operation were not met and the associated TS Action required a shutdown. Therefore, this resulted in a condition prohibited by TS Section 3.0.4. The actual consequences of this event were minimal in that there was no accident requiring the RCIC system to perform its design function. The primary cause of this event was a cognitive personnel error in that a licensed Shift Supervisor failed to comply with the normal plant startup procedure and did not ensure compliance with the requirements of TS Sections 3.0.4 and 3.7.3. Immediately upon discovery of violation of TS Section 3.0.4, the procedure to align the RCIC system for automatic operation was started. The Shift Supervisor has been counseled on the importance of procedure compliance and the use of proper communications methods. Corrective actions for the contributing factors include: the LER will be included in licensed operator required reading and an evaluation will be made to determine whether the Electro-Hydraulic Control system can be used to accurately control reactor pressure below 150 psig during startups.
3521991017 | Limerick 1, Limerick 2 | 06/13/1991 | 08/25/1992 | 9209010011 | <strong>Operation in a condition prohibited by Technical Specifications due to inoperability of an off-site AC source caused by personnel error in performing blocking.</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1991, while performing work to correct setpoints on the 101 and 201 Safeguard Transformer Automatic Voltage Controllers (AVCs), the system engineer discovered that fuse FU-10 was missing from the potential transformer circuit that feeds the 201 Safeguard Transformer AVC. The fuse had been removed on April 17, 1989, as part of a blocking permit to allow replacement of a terminal board in the 201 Safeguard Transformer, and was not replaced. Following review of the effect of the missing fuse in the 201 Safeguard Transformer, on June 13, 1991, plant staff determined that Unit 1 and 2 had operated in d condition prohibited by Technical Specifications (TS) section 3.8.1.1, "A.C. SOURCES." The second off-site, source was not fully capable of fulfilling its design requirement of supplying power to the safeguard buses. Therefore, the plant operated in a condition prohibited by TS in that the TS Action was not taken in the required time. The actual consequences of this event were minimal in that no Loss of Coolant Accident (LOCA) or LOCA with Loss of Off-site Power transients were experienced while the plant operated with the fuse missing from the 201 safeguard transformer. The cause of the missing fuse was several personnel errors during preparation, application, removal, and closure of a blocking permit during April of 1989. The fuse was replaced upon discovery of the condition. In response to other blocking permit concerns which have been identified since this event, the plant has implemented corrective actions that address the cause of this event.
3521991018 | Limerick 1, Limerick 2 | 06/18/1991 | 03/26/1992 | 9203310219 | <strong>Primary Containment and Reactor Vessel isolation Control system actuations resulting from a Reactor Protection System/Uninterruptible Power Supply inverter inductor failure</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1991, an unexpected gross failure of an inductor in the Unit 1 '1B' Reactor Protection System (RPS)/Uninterruptible Power Supply (UPS) inverter caused a loss of power to the '1B' RPS/UPS power distribution panel (1BY160). This loss of power resulted in automatic actuations of the Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) (EIIS:JM), an Engineered Safety Feature (ESF). All systems responded as designed and power was restored to the panel within 18 minutes. An investigation conducted with the vendor of previous inductor failures determined the failure to be due to an inadequate design by the vendor, but was thought to be limited to newer inductors. Preventive maintenance tasks which were written following previous inductor failures to replace the newer inductors for all inverters on site on an annual frequency have been expanded to include the older inductors unless past thermographic inspections reveal temperatures well within the maximum temperature for the inductor. Thermographic inspections will continue to be performed on all inverter inductors on a quarterly frequency. If any indications of hot spots or significant temperature differences are detected, the inductor will be replaced. A modification had been initiated due to the previous inverter problems to replace the currently installed inverters with more reliable equipment. This modification is projected to be completed by the end of the next refueling outage for each unit.
3521991019 | Limerick 1, Limerick 2 | 07/16/1991 | 08/14/1991 | 9108220077 | <strong>ESF actuations due to a loss of power to an RPS/UPS power distribution panel caused by the spurious actuation of an underfrequency relay</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1991, at 0919 hours, a spurious actuation of an underfrequency relay resulted in a trip of the '1A' Reactor Protection System (RPS) inverter output circuit breaker which caused a loss of power to the '1A' RPS/Uninterruptible Power Supply power distribution panel (1AY160). This loss of power resulted in automatic actuations of the Primary Containment and Reactor Vessel Isolation Control System, an Engineered Safety Feature. Operations personnel reset the underfrequency relay and reclosed the breaker thereby restoring power to panel 1AY160 3 minutes later. All remaining isolations were reset 28 minutes after the trip. The isolations were bypassed or reset in accordance with plant procedures and the systems were restored expeditiously by operators, preventing any adverse impacts on plant systems. The cause of this event was the spurious actuation of an underfrequency relay. The relay was replaced on July 16, 1991. An evaluation is being performed by the off-site engineering organization to investigate possible revisions to the breaker trip logic to increase the reliability of this power supply.
3521991020 | Limerick 1 | 08/13/1991 | 09/05/1991 | 9109100342 | <strong>Two similar ESF actuation events occurred after a reactor water level indicating switch tripped twice within the same day, as the result of an unknown cause and a personnel error.</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1991, two events occurred where the Channel D reactor water level indicating switch, LIS-42-1N681D, tripped resulting in partial Group VIC Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations. The partial Group VIC PCRVICS actuations which occurred as a result of both events initiated as designed, and were immediately reset by Operations personnel. There was no release of radioactive material to the environment as a result of either event. The cause of the first event involving a non-valid trip of LIS-42-1N681D is unknown. The integrity of LIS-42-1N681D including its associated wiring and relays was tested and inspected, and no deficiencies were identified. The cause of the first event will be further investigated by the use of recording equipment to monitor the operation of LIS-42-1N681D. The cause of the second event, which also involved a trip of LIS-42-1N681D, was due to a personnel error. While assessing the cause of the first event, a technician incorrectly installed a test lead into the test equipment, causing an inadvertent trip of LIS-42-1N681D. The technician involved in the second event was counseled regarding attention to detail and the need to perform a self-check. The technician also presented "Lessons Learned" from the second event at a series of Foreman Team Meetings with emphasis placed on the need to perform a self-check.
3521991021 | Limerick 1, Limerick 2 | 08/29/1991 | 09/27/1991 | 9110090159 | <strong>Main Control Room Ventilation System isolation due to high toxic gas alarm caused by Freon released During Drywell Chiller Maintenance.</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1991 at 0918 hours, the High Toxic Chemical Concentration alarm was received in the Main Control Room (MCR). MCR personnel immediately implemented Special Event Procedure SE-2, "Toxic Gas," including donning self-contained breathing apparatus (SCBA). MCR personnel manually initiated a MCR ventilation system chlorine isolation, an Engineered Safety Feature (ESF). The 'A' train of the Control Room Emergency Fresh Air Supply (CREFAS) System, also an ESF, Initiated as designed and provided total recirculation of the MCR air without any intake from the outside atmosphere. The MCR Toxic Gas Analyzers read a vinyl chloride concentration as high as 31.60 ppm. Chemistry personnel obtained and analyzed a sample of the MCR air. The sample showed no detectable vinyl chloride so MCR personnel removed SCBA per procedure. After the air sample from the outside air intake plenum showed no detectable vinyl chloride, MCR operators reset the chlorine isolation at 1131 hours. The cause of the event was inadequate procedural guidance for performance of maintenance work on the Drywell Chillers. A procedure for the transfer of refrigerant on the Drywell Chillers will be written and approved by November 1, 1991. This procedure will include specific guidance for MCR operators to manually initiate a MCR ventilation isolation during periods of potential Freon release.
3521991022 | Limerick 1 | 09/17/1991 | 10/08/1991 | 9110160027 | <strong>Condition prohibited by Technical Specifications in that the 'IC' LPCI subsystem was removed from service while the HPCI system was out of service due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1991, while the Unit 1 High Pressure Coolant Injection (HPCI) system was out of service, a plant operator began to remove the '1A' Control Rod Drive (CRD) pump from service for planned maintenance activities. At 0258 hours, the plant operator inadvertently removed the '1C' Residual Heat Removal (RHR) pump power supply breaker from its cubicle, rather than the breaker for the '1A' CRD pump. The plant operator immediately reinstalled the breaker for the '1C' RHR pump. The removal of the incorrect breaker caused the '1C' Low Pressure Coolant Injection (LPCI) subsystem of the RHR system to be inoperable. At 0300 hours, operations personnel momentarily operated the '1C' RHR pump and then declared the '1C' LPCI subsystem operable. The '1C' LPCI subsystem was inoperable for two minutes. Technical Specifications (TS) Section 3.5.1, "ECCS Operating," ACTION "c" requires that all four LPCI subsystems of the RHR system be operable when the HPCI system is inoperable. This ACTION was not met during the two minutes and resulted in a condition prohibited by TS. The actual consequences of this event were minimal. An accident condition did not occur during the two minute period of time in which the '1C' LPCI subsystem was inoperable. The cause of this event was cognitive personnel error when the individual failed to perform a self-check. The plant operator involved in this event was disciplined, and this event will be communicated to the appropriate operations personnel to reinforce the importance of attention to detail.
3521991023 | Limerick 1, Limerick 2 | 10/07/1991 | 11/04/1991 | 9111120156 | <strong>ESF actuations due to a loss of power to an RPS/UPS power distribution panel caused by the inadvertent actuation of an underfrequency relay.</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, an inadvertent actuation of an underfrequency relay resulted in a trip of the '1A' Reactor Protection System (RPS) inverter output circuit breaker which caused a loss of power to the '1A' RPS/Uninterruptible Power Supply power distribution panel. This loss of power resulted in automatic actuations of the Primary Containment and Reactor Vessel Isolation Control System, and other various Engineered Safety Features. Operations personnel reset the underfrequency relay and reclosed the breaker thereby restoring power to panel 1AY160. All remaining isolations were reset 36 minutes after the trip. The isolations were bypassed or reset in accordance with plant procedures and the systems were restored expeditiously by operators, preventing any adverse impacts on plant systems. The cause of this event was the inadvertent actuation of an underfrequency relay during performance of a Surveillance Test (ST) procedure. A new test methodology is being developed for the performance of the ST procedure, to minimize the possibility of actuation of the underfrequency relay. Additionally, an evaluation is being performed by the off-site engineering organization to investigate possible revisions to the breaker trip logic to increase the reliability of this power supply.
3521991024 | Limerick 1, Limerick 2 | 10/25/1991 | 02/08/1993 | 9302170305 | <strong>'A' Loop of the Emergency Service Water system was inoperable as a result of an equipment failure and personnel errors.</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1991, an Emergency Service Water (ESW) system Surveillance Test (ST) procedure was performed for its normally scheduled quarterly performance by a non-licensed operator. The non-licensed operator observed pressurized flow through a check valve and noted this in the ST procedure. Main Control Room operations personnel reviewed the test and determined it was unsatisfactory due to the noted ST procedure step, but failed to declare equipment inoperable. On October 29, 1991, an evaluation of the ST procedure by the plant staff determined that the ESW system check valve failed to perform as designed and was therefore inoperable. The plant staff also determined that a condition prohibited by Technical Specifications existed. Corrective actions were immediately taken by operations personnel to address this condition. The actual consequences of this event were minimal in that no accident or operating transient occurred requiring operation of the affected safety systems. The causes of this event were an equipment failure and a failure to follow procedures due to 1) less than adequate training, 2) a misleading ST procedure note, and 3) a failure to initiate corrective actions. Corrective actions included repair of the ESW system check valve on November 19, 1991, letters from the plant manager to licensed operations personnel and senior plant staff members providing management expectations for when similar conditions occur, review and discussion at an operations shift supervision meeting, and training.
3521991025 | Limerick 1, Limerick 2 | 11/03/1991 | 12/03/1991 | 9112160121 | <strong>Main Control Room Isolations in response to a high toxic chemical concentration alarm of an indeterminate nature.</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1991, and again on November 18, 1991, Main Control Room (MCR) personnel received a MCR annunciator alarm indicating high toxic gas concentration in the MCR fresh air intake. In each instance, MCR personnel then entered Special Event procedure SE-2, "Toxic Gas," donned self-contained breathing apparatus, and manually initiated a MCR ventilation system isolation, an Engineered Safety Feature (ESF). In conjunction with the MCR ventilation system isolation, the Control Room Emergency Fresh Air Supply (CREFAS) system, also an ESF, initiated as designed, and provided total recirculation of the MCR air without any fresh air intake from the outside atmosphere. Chemistry personnel were notified and air samples from the MCR were obtained. No toxic gas concentrations were detected. The consequences of these events were minimal in that no toxic gas actually existed. The cause of these events was momentary high toxic chemical concentration indication of an indeterminate nature. Subsequent troubleshooting failed to clarify the exact cause of the high indications. We are investigating several options to decrease the vulnerability of the toxic gas detection system to a single failure or spurious signal to minimize the required MCR isolations.
3521991026 | Limerick 1 | 11/12/1991 | 12/11/1991 | 9112170251 | <strong>An Engineered Safety Feature actuation due to an inadequate review of a blocking permit for an isolation valve associated with a Primary Containment H2/O2 Combustible Gas Analyzer.</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1991, an electrical lead from a Primary Containment Isolation Valve (PCIV) in one of the sample lines to the H2/O2 Combustible Gas Analyzer (CGA) 10S206 was inadvertently grounded during maintenance activities, causing an actuation of the Primary Containment and Reactor Vessel Isolation Control System, an Engineered Safety Feature. The inadvertent grounding resulted in a loss of indication on the Main Control Room (MCR) panel 10C601 for other PCIVs associated with the sample lines to the CGA 10S206. A loss of valve position indication on several related valves is an indicator of a loss of electrical. power to the valves. Since the PCIVs fail closed with a loss of electrical power, MCR personnel removed the CGA 10S206 from operation, and later discovered that a fuse had blown in panel 10C601 as a result of the inadvertent grounding. Within 23 minutes, the CGA 10S206 was returned to operable status. The actual consequences of this event were minimal. The cause of this event was personnel error resulting from an inadequate understanding of the full scope of the maintenance activities to be performed on the PCIV for the CGA 10S206. The personnel involved in this event were counseled regarding the proper development and review of a blocking permit. A Management Directive addressing this event and the proper development and review of blocking permits will be issued to plant personnel. A discussion of this event and its causes will be included in the next cycle of Licensed Operator Requalification Training.
3521991027 | Limerick 1 | 11/12/1991 | 12/11/1991 | 9112170484 | <strong>An Engineered Safety Feature actuation due to an unknown cause for an isolation valve associated with a Primary Containment H2/O2 Combustible Gas Analyzer.</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1991, Main Control Room operators observed the initiation of a spurious actuation of the Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature. The initiation resulted in closure of the Primary Containment H2/O2 Combustible Gas Analyzer sample lines to the drywell, and an isolation signal to the normally closed Hydrogen Recombiner Inboard Isolation Valves and the Low Flow Nitrogen Makeup isolation valve. The actual consequences of the event were minimal and there was no release of radioactive material to the environment as a result of this event. The proximate cause of the actuation was a relay intermittently changing state; however, the cause of the spurious relay operation could not be determined. The defective relay was replaced. The new relay was tested and the affected equipment was declared operable on November 14, 1991. Bench testing and monitoring of the energized defective relay following replacement identified no problems. Since the testing of the relay revealed no equipment problems and no similar failures have occurred, the failure is considered an isolated event and no further corrective actions are planned.
3521991028 | Limerick 1 | 12/18/1991 | 01/17/1992 | 9201280119 | <strong>Inoperability of the High Pressure Coolant Injection system due to failure of the inboard steam supply isolation valve in the closed position.</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1991, following completion of maintenance on the High Pressure Coolant Injection (HPCI) system steam supply outboard isolation valve, HV-55-1F003, operations personnel attempted, unsuccessfully, to open the inboard isolation valve, HV-55-1F002. Subsequent investigation by maintenance personnel led to the determination that the valve motor failed upon closure of the valve on December 10, 1991. A Unit 1 shutdown was initiated on December 18, 1991, at 1800 hours, to facilitate repair of the valve. The inability to open HV-55-1F002 constituted a condition which alone could have prevented the fulfillment of the safety function of the HPCI system. The actual consequences of this event were minimal in that an accident condition did not occur during the time in which the HPCI system was inoperable. The cause of this event was the failure of the HPCI steam supply inboard isolation valve motor. Investigation by maintenance personnel led to the conclusion that the HV-55-1F002 motor failed due to the spring pack belleville washers binding on the bearing cartridge stem. The washers prevented the torque switch from interrupting electrical power to the motor and resulted in electrical power being continuously supplied to the stalled motor until the motor windings failed. The valve motor and spring pack were replaced on December 20, 1991. The original spring pack will be sent to the manufacturer for further examination and analysis.
3521991029 | Limerick 1, Limerick 2 | 12/23/1991 | 01/21/1992 | 9201290062 | <strong>Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations resulting from the failure of a PCRVICS fuse.</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1991, various actuations of the Unit 1 and 2 Primary Containment and Reactor Vessel Isolation Control Systems (PCRVICS), and a Unit 2 Reactor Enclosure Secondary Containment isolation occurred due to a blown fuse on Unit 2. These are Engineered Safety Feature actuations. The fuse was replaced and all isolations were reset within 30 minutes. The actual consequences of this event were minimal. All systems responded as designed and there was no release of radioactive material to the environment as a result of this event. The cause of the isolations was the failure of Unit 2 PCRVICS fuse B21H-F15A. The root cause of the fuse failure is unknown. The blown fuse will be sent to the manufacturer for failure analysis. A revision to this LER will be provided if anything significant is discovered during the failure analysis.
3521991030 | Limerick 1 | 12/30/1991 | 01/29/1992 | 9202030245 | <strong>Technical Specification Limiting Condition for Operation and Surveillance Requirement for temperature and time exceeded During reactor recirculation pump start.</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1991, at 1023 hours, operations personnel started the '1A' reactor recirculation pump in conjunction with the performance of Surveillance Test (ST) procedure ST-6-043-390-1, "Reactor Recirculation Pump Idle Loop Startup Temperature and Flow Check." ST-6-043-390-1 satisfies Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.1.4 and TS Surveillance Requirement (SR) 4.4.1.4. On December 30, 1991, at approximately 1300 hours plant personnel discovered that inaccurate temperature and time readings were recorded into the ST, causing the 50 degrees Fahrenheit (F) temperature differential limit of TS LCO 3.4.1.4 and the 15 minute time limit of TS SR 4.4.1.4 to be exceeded by 2 degrees F and 4 minutes respectively; conditions prohibited by TS. The '1A' recirculation pump was left in operation since these TS violations were discovered approximately 3 hours after the pump was placed in service, and it was determined that securing the pump and a subsequent restart would only result in further unnecessary thermal transients. The primary cause of this event was personnel error. The actual consequences of this event were minimal. The individual involved in this event was counseled, and specific plant procedures and the Licensed Operator Training Program will be evaluated to prevent recurrence of a similar event.
3531991001 | Limerick 2 | 01/07/1991 | 02/06/1991 | 9102120133 | <strong>A condition prohibited by TSs due to an inoperable overcurrent protective device and the required TS ACTION was not performed within the required time period.</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1991, Instrumentation & Controls (I&C) personnel identified d condition which was prohibited by Technical Specifications (TS). A Unit 2 Primary Containment penetration conductor overcurrent protective device was not calibrated to the TS (Section 3.8.4.1) required tolerance when it was installed as a replacement for a defective overcurrent protective device on December 3, 1990 and the required TS ACTIONs were not taken. The overcurrent protective device is an instantaneous magnetic circuit breaker (D234-R-E-10) that is aligned to the Unit 2 A2 drywell unit cooler fan and protects the electrical penetration in the primary containment wall. The replacement breaker for the A2 drywell unit cooler fan was incorrectly calibrated on December 3, 1990 in accordance with procedure PMQ-093-007, "Preventive Maintenance Procedure for Testing and Calibration of 480V Molded Case Circuit Breakers." This procedure did not differentiate between TS and non-TS required circuit breakers which have different allowable tolerances. In addition, maintenance personnel and operations personnel failed to perform the Surveillance Test (ST) which requires the operability of the circuit breaker. The PMQ-093-007 procedure will be revised to include a note specifying that ST procedure ST-8-093-320-1 or 2 shall be performed for the TS required circuit breakers. A review of the remaining PMQ procedures will be conducted to identify if any other similar problems exist. This event will be reviewed with the maintenance planners and operations personnel.
3531991002 | Limerick 2, Limerick 1 | 03/24/1991 | 09/04/1992 | 9209110189 | <strong>Inadvertent isolation, of the Unit 2 Primary and Secondary Containments due to a blown fuse During testing of a battery changer.</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1991, while Unit 2 was shutdown, various actuations of the Unit 2 Primary Containment and Reactor Vessel Isolation Control System and a Unit 2 Reactor Enclosure Secondary Containment isolation occurred. These are Engineered Safety Feature actuations. The actuations are suspected to be the result of d blown 300 amp fuse in the Division III 125 VDC circuitry during load testing of the Division III Safeguard Battery Charger. This blown fuse caused a transient condition in the DC control power to the second of two sets of undervoltage and overvoltage relays for the 2A Reactor Protection System/Uninterruptible Power Supply (RPS/UPS) distribution panel power supply breakers. The loss of control power is suspected of causing one of the protective relays to trip resulting in a trip of the associated RPS/UPS distribution panel power supply breaker. The power supply breaker was reclosed and the 2B loop of Shutdown Cooling was returned to service within 24 minutes. All systems responded as designed during the loss of power. The primary cause of the blown fuse was a lack of information from the manufacturer of a battery capacity test system used to test battery chargers. The appropriate battery charger test procedures now require testing to be performed with the test equipment in the proper mode. The 2A RPS/UPS power supply breaker with the relays was sent to the manufacturer for performance of a failure analysis. No problem was found with the relays and breaker and it was concluded that they will operate as designed.
3531991003 | Limerick 2 | 03/24/1991 | 04/22/1991 | 9104250285 | <strong>Inadvertent actuation of the Unit 2 Reactor Protection System due to a personnel error During the application of a Temporary Circuit Alteration.</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1991, an inadvertent Redundant Reactivity Control System (RRCS) Alternate Rod Insertion (ARI) actuation was initiated from Division I Logic during the application of a Temporary Circuit Alteration (TCA) to support Unit 2 outage work on Division I and III instrumentation. The ARI initiation caused the SCRAM inlet and outlet valves to open, and caused the SCRAM Discharge Volume (SDV) vent and drain valves to close. Repositioning of these valves caused level in the SDV to increase to its high level trip setpoint, causing a Reactor Protection System (RPS) full SCRAM actuation. There was no control rod motion during this event since all control rods were fully inserted prior to the event. The ARI and the RPS actuated as designed during this event. The cause of this event was personnel error resulting in less than adequate communication during installation of the TCA; an RRCS reset was requested when both RRCS and ARI resets were required. Procedural guidance will be developed to ensure both RRCS and ARI resets are performed for these routine Divisional TCAs that are applied during outages. The Licensed Operator Requalification training module for RRCS will be revised to include more detailed information on RRCS and ARI logic resets.
3531991004 | Limerick 2, Limerick 1 | 03/27/1991 | 04/26/1991 | 9105020218 | <strong>The inadvertent start of an Emergency Diesel Generator and an Emergency Service Water pump due to a spurious LOCA signal as a result of personnel error</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1991, an inadvertent LOCA signal was generated while System Engineers (SEs) were performing the Division III Loss of Coolant Accident (LOCA) - Loss of Offsite Power (LOOP) logic system functional Surveillance Test (ST) procedure associated with the D23 Emergency Diesel Generator (EDG). This LOCA signal caused the Unit 2 D23 EDG to Start, an Engineered Safety Feature (ESF) actuation. Additionally, the associated Division III AC Safeguard bus shed non-essential loads. After the D23 EDG start, the common 'C' Emergency Service Water (ESW) pump started automatically, also an ESF actuation. The actual consequences of this event were minimal in that no actual LOCA signal occurred and no adverse conditions resulted from the spurious signal. The cause of this event was personnel error in that the SE functioning as the test director in the Main Control Room (MCR) did not complete two substeps of a multiple part procedural step due to a lack of attention to detail. The SEs involved were counseled on the need for attention to details and the need to adequately communicate. A letter from the Limerick Generating Station Vice President to all site personnel was issued addressing this event and other incidents involving personnel error that have occurred during the current Unit 2 refueling outage. Additionally, the ST procedure and other similar ST procedures associated with the remaining Unit 1 and Unit 2 EDGs will be revised prior to their next performance to make the specific step into two steps.
3531991005 | Limerick 2 | 04/01/1991 | 05/01/1991 | 9105060226 | <strong>Special Report for Diesel Generator Test Failure</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1991, with Unit 2 in a refueling condition, plant personnel were performing Surveillance Test (ST) procedure ST-1-092-111-2. "D21 Diesel Generator 4 KV SFGD Loss of Power LSF/SAA and Outage Testing." The D21 Emergency Diesel Generator (EDG) had been declared inoperable to perform this procedure. The D21 EDG successfully rejected the 2A Residual Heat Removal (RHR) system pump motor load of 992KW. In accordance with the procedure, the 2A RHR pump was restarted; however, the D21 EDG output voltage increased above the acceptance criteria value to approximately 5200 volts. The test was then terminated. The cause of this event was an improperly installed potential transformer primary fuse that may have been due to personnel error. This resulted in a loss of generator output voltage feedback to the automatic voltage regulator. This event is classified as a valid failure. In the event of an actual loss of offsite power, the D22 EDG and D24 EDG were operable to provide adequate power to maintain the reactor in a safe shutdown condition as required by Technical Specifications. All other EDG potential transformer primary fuses were verified to be properly installed. An operator aid will be added onto each EDG cabinet door to caution operators to ensure all fuses are firmly seated in their fuse clips. Because this is the first failure for the D21 EDG, the test interval remains unchanged at 31 days.
3531991006 | Limerick 2 | 04/04/1991 | 05/06/1991 | 9105090360 | <strong>Inadvertent Emergency Diesel Generator start as a result of personnel error.</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1991, during performance of a Unit 2 Surveillance Test (ST) procedure, the D22 Emergency Diesel Generator (EDG), an Engineered Safety Feature (ESF), was inadvertently started. This occurred as a result of a plant operator depressing the wrong pushbutton while performing the ST procedure. The inadvertent start of the EDG constituted an unplanned actuation of an ESF. The EDG ran for less than ten (10) seconds before being secured by operations personnel. The inadvertent start did not impact the operability of the EDG. All remaining EDGs were operable and available for service. The cause of this event was personnel error in that the plant operator depressed the wrong pushbutton while performing the ST procedure due to a lack of both self-checking and attention to detail. The ST procedure did not contain certain barriers that could have assisted the operator in properly identifying equipment. The involved operator was counseled on the importance of attention to detail while performing work in the plant. Enhancements are being implemented in various EDG procedures which will create barriers to help prevent this type of personnel error in the future. There is a continuing effort through training and management involvement to heighten operator awareness of the need for attention to detail and self-checking.
3531991007 | Limerick 2 | 04/10/1991 | 05/10/1991 | 9105210239 | <strong>Handling of a control rod prohibited by Technical Specifications Surveillance Requirements 4.9.6.3b due to procedure deficiencies.</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1991, a Fuel Handling Supervisor observed the uptravel mechanical stop on the refueling platform monorail mounted auxiliary hoist to be mispositioned outside the limits of Surveillance Test procedure ST-6-107-633-2, "Core Alteration Testing." During the previous shift the uptravel mechanical stop was moved 24 inches to permit movement of a control rod blade from the spent fuel pool to the reactor. On April 12, 1991, during investigation into the event, it was determined that the top of a control rod blade was 1.5 inches less than the required 6 feet 6 inches below the normal fuel storage pool water level; a condition prohibited by Technical Specifications (TS) Surveillance Requirement (SR) 4.9.6.3b. TS SR 4.9.6.3b was amended on August 16, 1990. Prior to August 16, 1990, the interpretation of TS SR 4.9.6.3b did not limit control rod blade movement. The cause of this event was an inadequate maintenance procedure M-041-061 and an inadequate procedure ST-6-107-633-2. A contributing cause to the event was inadequate training of the Fuel Handling Supervisors on invessel maintenance activities following the change to TS SR 4.9.6.3b. The maintenance procedure has been changed to delete the provision to reposition the mechanical stop. Procedure ST-6-107-633-2 has also been revised. Additionally, the appropriate requalification training programs will be revised, the TS amendment control procedure will be revised and previously issued TS amendments will be reviewed to determine if a similar problem occurred.
3531991008 | Limerick 2 | 04/01/1991 | 06/12/1991 | 9106190264 | <strong>Voluntary Report for Potential Condition of Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1991, with Unit 2 in a refueling condition, plant personnel were performing Surveillance Test procedure ST-1-092-111-2, "D21 Diesel Generator 4KV SFGD Loss of Power LSF/SAA and Outage Testing." The D21 Emergency Diesel Generator (EDG) successfully rejected the 2A Residual Heat Removal (RHR) system pump motor load of 992 KW. In accordance with the procedure, the 2A RHR pump was restarted; however, the D21 EDG output voltage increased above the acceptance criteria value to approximately 5200 volts. The cause of this event was an improperly installed potential transformer primary fuse that may have been due to personnel error. This resulted in a loss of generator output voltage feedback to the automatic voltage regulator. The D21 EDG fuse may have been improperly installed since February 2, 1991. In this condition the operability of the D21 EDG was not assured, if a design basis event had occurred, such as a safe shutdown earthquake. If the D21 EDG was inoperable on February 2, 1991, a Technical Specifications (TS) violation of TS section 3.8.1.1b occurred because the associated TS Actions were not taken within the required time period. As a result, this voluntary LER is being submitted to report a condition that may have been a condition prohibited by TS. On May 31, 1991, an operator aid was added onto each of the sixteen EDG control panels. The operator aid references a system procedure that was revised to provide caution and direction for fuse installation and verification.
3531991009 | Limerick 2 | 05/21/1991 | 06/20/1991 | 9106260318 | <strong>Voluntary LER and Special Report for a loose wire in the potential transformer sensing network of an Emergency Diesel Generator.</strong><br /><i>Abstract:&nbsp;</i>On 5/21/91, with Unit 2 in a refueling condition, plant personnel were performing Surveillance Test (ST) procedure ST-1-092-114-2, "D24 Diesel Generator 4KV SFGD Loss of Power LSF/SAA and Outage Testing." While performing this procedure, the D24 Emergency Diesel Generator (EDG) output voltage increased above the acceptance criterion value. The cause of this event was a loose wire in the potential transformer sensing network which resulted in a loss of generator output voltage feedback to the automatic voltage regulator. The cause or time that the wire became loose cannot be determined. In this condition the operability of the D24 EDG was not assured if a design basis event had occurred, such as a safe shutdown earthquake. This situation represents a potential condition prohibited by Technical Specifications (TS) since the D24 EDG may have been inoperable since 7/05/89, and the associated TS Actions were not taken within the required time period. This voluntary LER is being submitted to report a condition that may have been prohibited by TS in addition to the requirements of TS Section 6.9.2 as required by TS Surveillance Requirement 4.8.1.1.3 due to an EDG test failure. On 5/22/91, the loose wire was corrected. The remaining connections on the D24 EDG as well as all other Unit 2 EDGs were inspected and no abnormalities in the wiring of the potential transformer sensing network were found. Because this is the first failure for the D24 EDG, the ST procedure frequency remained unchanged at 31 days.
3531991010 | Limerick 2 | 05/25/1991 | 06/24/1991 | 9107020303 | <strong>Special Report for a Nonvalid Diesel Generator Start Failure During a Valid Test</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1991, plant personnel were performing Surveillance Test (ST) procedure ST-6-092-311-2, "D21 Diesel Generator Operability Test Run." At 2016 hours, after the D21 Emergency Diesel Generator (EDG) had been running for approximately 3 hours its output increased to 3500 KW. The D21 EDG was declared inoperable at 2017 hours. The cause of this event was an improperly operating Auxiliary Test Start Relay which converted the 21 EDG control circuit to isochronous mode. The D21 EDG Auxiliary Test Start Relay was replaced and the test start circuit was instrumented. The D21 EDG was started and loaded to 2000 KW for 1 hour. The special test start circuit instrumentation detected no abnormalities. Procedure ST-6-092-311-2 was successfully performed and on May 29, 1991, the D21 EDG was declared operable at 2030 hours. The D21 EDG failure was classified as a nonvalid failure using the guidance of Regulatory Guide 1.108, "Periodic Testing of Diesel Generator Units Used as Onsite Electric Power System at Nuclear Power Plants". In the event of an actual loss of offsite power, the two operable Unit 2 EDGs would have provided adequate power to maintain the cold shutdown condition of the reactor.
3531991011 | Limerick 2 | 06/04/1991 | 07/26/1991 | 9107300303 | <strong>This LER reports a condition prohibited by Technical Specifications (TS) in that a TS Surveillance Requirement for the Average Power Range Monitor flow units was not performed.</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1991, plant personnel discovered the daily Jet PUMP and APRM flow unit operability verification Surveillance Test (ST) procedure was not performed on June 4, 1991. Technical Specifications (TS) Table 4.3.1.1-1 requires that an Average Power Range Monitor (APRM) flow unit channel check be performed once per 24 hours in Operational Condition (OPCON) 1, Power Operation, to ensure that the total core flow is greater than or equal to the APRM percent flow. TS Surveillance Requirement (SR) 4.0.4 requires that this SR be performed within 24 hours prior to entry into OPCON 1. Because the ST procedure was not performed on June 4, 1991, within the applicable surveillance interval, the APRM flow units were not in surveillance when the Reactor Mode Switch was placed in OPCON 1 at 0525 hours on June 5, 1991. This resulted in a condition prohibited by TS SR 4.0.4. Readings from the Daily Surveillance Log ST procedure were subsequently utilized to determine that total core flow was greater than the APRM percent flow on June 4, 1991 and therefore the actual APRM Trip setpoints were conservative which is what the SR was intended to verify. The cause of this event was personnel error resulting in procedural non-compliance. Contributing factors were procedural ambiguity and lack of attention to detail. The Unit 1 and 2 ST procedures will be revised to remove the identified ambiguities. Corrective actions for the procedure non-compliance and the lack of attention to detail are being addressed by a comprehensive review program.
3531991012 | Limerick 2 | 06/24/1991 | 11/27/1991 | 9112090445 | <strong>This LER reports the removal of two floor drain plugs associated with Reactor Enclosure (RE) Secondary Containment (SC), rendering RE SC inoperable due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1991, the Radwaste System Engineer (SE) recognized that two normally locked in place floor drain plugs associated with maintaining Unit 2 Reactor Enclosure (RE) Secondary Containment (SC) integrity had been removed by maintenance personnel on June 24, 1991, at approximately 1300 hours. The SE immediately instructed maintenance personnel to re-install and lock in place the two Unit 2 floor drain plugs. The two Unit 2 floor drain plugs were re-installed and locked in place at 1000 hours, on June 27, 1991, thereby restoring Unit 2 RE SC integrity. This event resulted in a condition prohibited by Technical Specifications. The actual consequences of the event were minimal in that no radioactive release occurred due to the Unit 2 RE being maintained at the required negative differential pressure for the duration of this event. The cause of this event is personnel error involving the following causal factors: less than adequate job planning as a result of inadequate floor drain system design drawings, inadequate communication, a sense of urgency for job completion, failure to comply with Administrative (A) procedure A-8, "Procedure for Control of Locked Valves and Devices," due to a lack of training, less than adequate attention to detail, and a lack of a questioning attitude by maintenance personnel. Corrective actions include a study on floor drain system drawings, counseling, and training of maintenance personnel on Administrative procedure A-8.
3531991013 | Limerick 2 | 07/17/1991 | 08/14/1991 | 9108220215 | <strong>A condition prohibited by Technical Specifications where a Surveillance Requirement was not met and Primary Containment Integrity was not verified due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1991, the Local Leak Rate Test (LLRT) Coordinator and a vendor performing an independent review of all LLRT procedures, discovered that the Surveillance Requirements (SR) for Technical Specifications (TS) Sections 3.6.1.1 and 3.6.1.2 were not met and the associated TS Actions had not been taken resulting in a condition prohibited by TS. The valve packing gland leakage tests on two Primary Containment Isolation Valves (Drywell Spray Valves) had not been included in Rev. 0 of the LLRT Surveillance Test (ST) procedures. These tests were required to be performed by March, 1991. Temporary Procedure Changes (TPCs) were then prepared for the LLRT ST procedures to include testing of the valve packing glands. The tests were satisfactorily completed on July 17 and the leakage rates through both of the valve packing glands were minimal. The cause of this event is a personnel error resulting in deficient LLRT ST procedures. The valve packing gland leakage tests were identified as missing from the startup phase LLRT procedures and were temporarily added to the startup LLRT procedures to allow performance. However, the changes were not permanently incorporated into the operating phase LLRT procedures by the startup LLRT coordinator following addition of the test taps and prior to transfer to plant staff. The current TPC and modification processes ensure proper permanent procedure revision and all LLRT procedures have been reviewed and found to contain adequate testing requirements.
3531991014 | Limerick 2 | 08/01/1991 | 08/23/1991 | 9109040445 | <strong>Inadvertent start of an Emergency Diesel Generator due to a personnel error in that a non-licenses operator failed to follow a Surveillance Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1991, during performance of a Unit 2 Surveillance Test (ST) procedure, the D24 Emergency Diesel Generator (EDG) was inadvertently started. The inadvertent start of the EDG resulted in an unplanned actuation of an Engineered Safety Feature. The D24 EDG ran for less than three seconds when it was secured by the non-licensed plant operator. This inadvertent start did not impact the operability of the D24 EDG. All remaining Unit 2 EDGs were operable and available for service. Therefore, the actual and potential consequences of this event were minimal. This unplanned start of the D24 EDG occurred as a result of a non-licensed plant operator failing to follow the ST procedure. The operator was disciplined for failing to follow the ST procedure. Additionally, a Shift Training Bulletin was issued to reiterate the need for procedure compliance and make all operators aware of this event.
3531991015 | Limerick 2 | 09/12/1991 | 07/30/1993 | 9308040301 | <strong>HPCI discovered in a degraded condition when the HPCI turbine stream supply valve failed to open fully due to an increase in the duration of valve unseating loads</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1991, the Unit 2 High Pressure Coolant Injection (HPCI) system was discovered to be in a degraded condition when the HPCI turbine steam supply valve failed to open fully. Since the HPCI system is a single train safety system, this degraded condition alone could have prevented the fulfillment of its safety function needed to maintain the reactor in a safe shutdown condition and mitigate the consequences of an accident. The actual consequences of this event were minimal since an accident condition did not occur during the time in which the HPCI system was degraded. The proximate cause of the failure of the steam supply valve to open was an increase in the duration of the valve unseating forces. Subsequent testing revealed that an additional minor force peak immediately after valve disc unwedging and a variation in the valve stem lubrication contributed to the increased valve opening resistance. The valve stem threaded portion was lubricated and the torque switch bypass limit switch was adjusted to remain in effect for the first 3.5 seconds of valve open cycle. Valve performance will be monitored quarterly and the valve will be replaced during the next scheduled Unit 2 refueling outage. The lubricant variation concern has been addressed by implementation of recommendations of the Electric Power Research Institute Improved Motor Operated Valve Lubricant Program.
3531991016 | Limerick 2 | 10/07/1991 | 11/04/1991 | 9111120152 | <strong>This LER reports a High Pressure Coolant Injection System Isolation caused by an I&C Technician selecting and testing the incorrect trip unit.</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, during performance of a Surveillance Test (ST) procedure, an Instrumentation and Controls (I&C) technician was switching electronically between trip units and inadvertently placed the selector switch to the next numbered trip unit. The technician then depressed the switch to begin the functional test which resulted in a Primary Containment and Reactor Vessel Isolation Control System actuation, an Engineered Safety Feature actuation, which closed the Unit 2 High Pressure Coolant Injection (HPCI) system steam supply line outboard isolation valve. This was an event which alone could have prevented the fulfillment of the safety function of a system. The HPCI system was restored to normal system alignment within 21 minutes. The actual consequences of this event were minimal in that an accident condition did not occur while the HPCI system was isolated, and the system was not called upon to perform its intended safety function. The cause of this event was a personnel error by the I&C technician performing the ST procedure in that insufficient attention to detail was applied to the performance of the ST procedure. The technician involved was admonished by the Maintenance and I&C Superintendent for failure to apply the principles of self-check and attention to detail while performing the ST procedure. The technician presented the causal factors involved in his inattentiveness and the necessity to apply the principle of self-check at an I&C technician All-Hands Meeting.
3531991017 | Limerick 2 | 11/15/1991 | 04/10/1992 | 9204210167 | <strong>High Pressure Coolant Injection system discovered in a degraded condition because of leak in an oil line to the future stop valve.</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1991, the High Pressure Coolant Injection (HPCI) system engineer discovered an oil leak, during a routine system walkdown, that alone could have prevented the HPCI system from fulfilling its safety function needed to maintain the reactor in a safe shutdown condition and mitigate the consequences of an accident. The actual consequences of this event were minimal because an accident condition did not occur during the time in which the HPCI system was inoperable or could have been degraded and because sufficient Emergency Core Cooling Systems were available. The period of time in which the HPCI system may have been degraded due to the oil leak is limited to the time between November 13, 1991, when the HPCI system was verified to be operable and November 15, 1991, when the oil leak was discovered by the HPCI system engineer. The leak was caused by a local defect in a section of the tube placed in tension by the manufacturing process. Based on a review of Limerick Generating Station maintenance history, as well as industry databases, this failure has been determined to be an isolated occurrence. The line was replaced with a hard pipe line similar to the lines on the Unit 1 HPCI system. The two remaining braided stainless steel hose lines in the Unit 2 HPCI system were inspected and confirmed to not be leaking oil. The HPCI system was declared operable on November 18, 1991.
3541991001 | Hope Creek | 01/10/1991 | 02/06/1991 | 9102120128 | <strong>Engineered Safety Features Actuation- Primary Containment Isolation During Performance Of Surveillance Test Due To Multiple Causes</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1991 at 0125, an actuation of the Channel "B" Primary Containment Isolation System (PCIS) occurred during the performance of a monthly functional test of Channel "B" Emergency Core Cooling System (ECCS) reactor vessel level instrumentation. Followup investigation determined that a Channel "B" PCIS actuation signal was input during the surveillance at the same time that a sealed in isolation from the Nuclear Steam Supply Shutoff System (NS4) existed due to a previous RPS bus transfer from alternate to normal power. The concurrent existence of both signals satisfied the Channel "B" PCIS logic, and the required system actuations occurred. It was determined that the prerequisites of the ECCS functional Lest procedure did not require resetting of potentially sealed in isolation signals from the NS4 prior to initiating a PCIS signal. Additionally, a Nuclear Control Operator (NCO, RO licensed) did not reset the NS4 circuit as required by the RPS operating procedure following the RPS bus transfer and no indications exist to alert control room personnel when a single channel NS4 isolation signal is present. Corrective actions included modifying the ECCS functional test procedure to require the resetting of potentially sealed in NS4 isolation signals, counseling for the NCO who failed to reset the NS4 isolation per procedure, and evaluating the NS4 circuitry for a potential design change to add NS4 isolation signal indication.
3541991002 | Hope Creek | 01/22/1991 | 02/21/1991 | 9102260192 | <strong>Steam Leak Detection System Thermocouples Wired Incorrectly - Installation Deficiency Results In Undetected Inoperability Of High Pressure Coolant Injection (HPCI) System Isolation Capability</strong><br /><i>Abstract:&nbsp;</i>On 1/22/91 at 1400, personnel performing a design change in the Steam Leak Detection (SLD) system determined that three room temperature monitoring thermocouples providing input to SLD were incorrectly wired. The configuration of the wiring was such that signals input to SLD temperature switches would respond in the direction opposite to actual temperature trends in the monitored rooms. Two of the thermocouples monitor High Pressure Coolant Injection (HPCI) pump room temperature, and provide inputs to the Channel "A" and "C" HPCI system isolation circuitry in the event of a HPCI steam supply line break. The third thermocouple is utilized as a spare, and does not provide isolation capability. <br /><br /> Subsequent investigation determined that the subject thermocouples had been wired incorrectly since original plant startup, and were not discovered during the testing process following installation. Corrective actions included wiring the subject thermocouples correctly, and verifying the wiring on all other thermocouples associated with the Steam Leak Detection system.
3541991003 | Hope Creek | 01/25/1991 | 02/25/1991 | 9102270278 | <strong>Engineered Safety Features Actuation - Primary Containment Isolation During Performance Of Surveillance Test Due To Design Deficiencies In The Steam Leak Detection System</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1991 at 2145, an actuation of the Channel "C" Primary Containment Isolation System (PCIS) occurred during the performance of a monthly functional test of Channel "C" Emergency Core Cooling System (ECCS) high drywell pressure instrumentation. Followup investigation determined that a Channel "C" PCIS actuation signal (input during the surveillance) existed at the time that a fuse blew in the Nuclear Steam Supply Shutoff System (NS4) logic during implementation of a design change to enhance testability and maintainability in the Steam Leak Detection (SLD) cabinets. The concurrent existence of both signals satisfied the Channel "C" PCIS logic, and the required system actuations occurred. The NS4 logic fuse had blown during implementation of a design change in the Steam Leak Detection (SLD) system when test equipment leads were inadvertently grounded in the associated SLD cabinet. The primary cause of this occurrence was a design deficiency in the SLD cabinets, in that limited internal cabinet accessibility serves as a setup to technicians performing testing and maintenance inside the cabinets. Corrective actions included replacing the blown fuse, resetting the PCIS logic, completing the surveillance in a satisfactory manner, and completing implementation of the subject design change.
3541991004 | Hope Creek | 02/03/1991 | 03/14/1991 | 9103190392 | <strong>Engineered Safety Features Actuation: Channel "A" Primary Containment Isolation System (PCIS) Actuation While Manipulating Vessel Level Instrument Valves</strong><br /><i>Abstract:&nbsp;</i>On 2/3/91, a Channel "A" PCIS actuation occurred while a Controls Technician was valving in a reactor vessel level instrument following completion of an Environmental Qualification seal design change on the instrument. On 2/13/91, a Channel "A" PCIS actuation occurred while a Controls Technician was verifying instrument valves to be in the open position. In both cases, after verifying that all expected actuations had taken place, the Senior Nuclear Shift Supervisor (SNSS, SRO licensed) directed that the isolation signal be reset, and that all affected equipment be returned to a normal configuration. Subsequent investigation determined that the primary cause of the PCIS initiations is the inherent sensitivity of reactor vessel instrument reference leg instrumentation to minor hydraulic transients on the reference legs. Additionally, it was determined that removal from service and restoration of vessel reference leg instrumentation may require placing associated trip units in a "test" condition to preclude actuation. This requirement is not proceduralized. Corrective actions include providing additional procedural guidance, completing a design change to install calibration volume chambers on selected reference leg instrumentation, and discussing these incidents with Controls Technicians and Supervisors during Maintenance Department Continuing Training.
3541991005 | Hope Creek | 02/19/1991 | 03/21/1991 | 9103260438 | <strong>Reactor Scram - Relay Malfunction Results In Startup Level Control Valve Failing Closed And Subsequent Low Water Level Scram During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On 2/19/91 at 1010, while in the process of power ascension during restart following the stations third refueling outage, a reactor scram on low reactor pressure vessel (RPV) level occurred. Prior to the scram, the Nuclear Control Operator (NCO, RO licensed) controlling the reactor feedwater (RFW) system was in the process of swapping RFW control from startup level control (single element) to master level control (three element). When RFW was placed in master level control, the NCO experienced difficulty in maintaining normal vessel level (+35"), and swapped back to startup level control. A relay failure in the control circuit associated with one of the two startup level control valves (the RFW system utilizes one 3" and one 12" valve for system startup) resulted in the 12" startup level control valve driving closed during the swap. Feedwater flow through the 3" valve was not sufficient to compensate for the loss of flow through the 12" valve, and the reactor scrammed on low RPV level (+12.5"). Subsequent investigation determined that the primary cause of this event was a relay failure in the circuit controlling the 12" startup level control valve. Immediate corrective actions included relay replacement and reviewing feedwater system startup procedures for possible enhancements with respect to the RPV level transient normally experienced during the transition from single element to three element RFW control. Longer term corrective actions include reviewing operating characteristics of the feedwater system during startup evolutions to determine if hardware enhancements are necessary and reviewing the preventive maintenance program for non-safety related solid state relays.
3541991006 | Hope Creek | 04/05/1991 | 05/01/1991 | 9105070120 | <strong>Engineered Safety Features Actuation: Reactor Water Cleanup Isolation When Venting Flow Transmitters Due To A Deficient System Operating Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1991 at 1113, control room personnel received indication of a Reactor Water Cleanup (RWCU) System isolation during the course of venting system differential flow transmitters. After ascertaining the initiating cause of the isolation, the Nuclear Shift Supervisor (NSS, SRO licensed) directed that the system be restored to a normal alignment. Subsequent investigation determined that the primary cause of this incident was a procedural deficiency, in that the RWCU procedure does not take into account the need for defeating the system isolation logic when venting the differential flow transmitters. Corrective actions consist of implementing a procedure change to require defeating the RWCU system isolation logic when venting system differential flow transmitters, and reviewing this event during licensed operator requalification training.
3541991007 | Hope Creek | 05/05/1991 | 08/28/1991 | 9109040133 | <strong>Filtration, Recirculation, and Ventilation System (FRVS) Units discovered Inoperable During Surveillance Test due to blown Heater Control Fuses - Entry into Technical Specification 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On 5/5/91, and twice on 7/6/91, during the course of performing a monthly operations department surveillance procedure on the Filtration, Recirculation, and Ventilation System (FRVS), three of the FRVS recirculation units were found to be inoperable due to blown fuses in the heater control circuits. The A, C, and D FRVS recirculation units each had one heater coil that was not energized, as such, the heater banks could not meet the kilowatt rating required by Technical Specifications and the subject units were declared inoperable. On 7/6/91, the A, D, and E units were determined to be inoperable for the same reasons. In each case Technical Specification 3.0.3 was entered. The fuses were replaced, the heaters verified operational and the affected FRVS units were returned to operability, and Technical Specification 3.0.3 was exited prior to the requirement to initiate plant shutdown. The initiating causes of these events was the blown heater control fuses in the affected FRVS recirculation units. Engineering assessment of both events has determined the primary cause for the fuses blowing to be excessive heat buildup in the heater control cabinets. The excessive heat resulted in the derating of the fuses, and blowing of the fuse at lower than rated current levels. In each case, immediate corrective actions consisted of replacing the blown fuses, verifying the heaters operational, and returning the units to operable status. Followup corrective actions have included test method revision, design changes to the panels to allow heat to dissipate without affecting unit operability. Engineering is continuing to review the environmental requirements for the heater control circuits and will implement additional design changes to enhance heater performance and reliability.
3541991008 | Hope Creek | 05/07/1991 | 06/06/1991 | 9106110274 | <strong>Reactor Scram On Low Water Level Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 5/7/91, at 2102, a Reactor Scram occurred due to a low Reactor Vessel water level. Conditions leading to the Scram were the 'A' Channel Feedwater Level Control indication alarming with a high level, causing the feedpumps to back down. This was followed by the 'C' Channel alarming at 30" and a subsequent Reactor Scram. All control rods were verified to be inserted and plant systems responded as expected, with minor exceptions as noted in the text of this report. Follow-up investigation determined that the most probable cause of the event was personnel error when a Controls Technician inadvertently connected a current source to the wrong transmitter while performing a surveillance test. Although the most probable root cause was personnel error, a less than adequate cabinet design also contributed to the event. Immediate corrective actions included counseling the Controls Technician with respect to self-verification and attention to detail and implementing a design change to install test switches with input jacks and to label the input jacks with a channel designator. The surveillance procedure was revised in accordance with the design change and is being reviewed for additional enhancements.
3541991009 | Hope Creek | 05/08/1991 | 06/06/1991 | 9106100469 | <strong>Full Initiation Of The Reactor Protection System Due To Spiking Of The "G" Intermediate Range Monitor - Equipment Malfunction</strong><br /><i>Abstract:&nbsp;</i>On 5/8/91 at 0758, with the reactor in Hot Shutdown (Operational Condition 3), a full Reactor Protection System (RPS) actuation occurred due to electronic spiking of the "G" Intermediate Range Monitor (IRM) (RPS Channel "A"). A 1/2 scram signal had been manually inserted to the "B" RPS channel on the previous shift due to the inoperability of various IRMs during maintenance and testing activities. When the "G" IRM spiked, both halves of the RPS logic were satisfied, and the full RPS initiation occurred. The spiking of the "G" IRM has been attributed to equipment malfunction, as a work request had been previously written (4/26/91) against IRM "G" due to intermittent electronic spiking (the IRM was scheduled to be repaired at the next forced or planned outage). Corrective actions consisted of performing repairs to the "G" IRM, as planned, prior to returning to power operation, and continuing an internal study regarding IRM reliability to identify potential future system enhancements.
3541991010 | Hope Creek | 05/15/1991 | 11/15/1992 | 9211230229 | <strong>Engineered Safety Feature Actuation - Automatic closure of Reactor Core Isolation Cooling Torus Vacuum Breaker inboard isolation valve During functional testing due to undetermined causes.</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1990, during the performance of a monthly functional test on Division 2 Drywell Pressure instrumentation, an automatic closure of the inboard Reactor Core Isolation Cooling (RCIC) torus vacuum breaker isolation valve (FC-HV-F062) occurred. After verifying that the isolation had not occurred from a valid condition, the Senior Nuclear Shift Supervisor (SNSS, SRO licensed) directed that the isolation be reset and the valve reopened. The monthly functional test was then performed again successfully. The results of investigation of the event have been inconclusive in determining a cause of the isolation; further testing and inspection of the valve logic control circuitry will be conducted at the next forced or planned unit outage. This additional testing has verified proper operation of the valve and circuitry.
3541991011 | Hope Creek | 05/22/1991 | 06/19/1991 | 9106240330 | <strong>Both Control Room Ventilation System Trains Inoperable Due To Separate And Unrelated Equipment Malfunctions Resulting In Entering Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 5/22/91 at 1320, Technical Specification 3.0.3 was entered due to the inoperability of both Control Room Ventilation (CRV) system units. At 1252, the "B" CRV chilled water system tripped. The "A" CRV chilled water system automatically started, as designed, but tripped 22 seconds later. Efforts to restart the "A" CRV chilled water system were unsuccessful and an attempt was made to restart the "B" CRV chilled water system, with the compressor vane control in "automatic" (normal startup alignment). The "B" CRV chilled water system compressor started, however, failed to load and was ordered stopped. At 1320, both units were declared inoperable, and after allowing the "B" system to cool, the "B" CRV chilled water unit was successfully restarted with the compressor vane control in "manual". At 1348, compressor vane control was placed in automatic, proper operation was verified, and the unit was declared operable. Technical Specification 3.0.3 was exited at this time. The cause of this event was unrelated equipment malfunctions - the "B" CRV chilled water system tripping due to an apparently spurious trip signal, and the "A" system tripping due to a broken terminal on the compressor impeller shaft displacement trip circuit. Corrective actions consisted of performing a temporary repair to the broken terminal on CRV compressor, and troubleshooting / investigation of the "B" CRV chilled water system trip. Permanent repairs to the "A" compressor are scheduled to be completed at the next scheduled system outage for this equipment.
3541991012 | Hope Creek | 06/04/1991 | 07/02/1991 | 9107120116 | <strong>Entry Into Technical Specification 3.0.3 Due To Concurrent Inoperability Of High Pressure Coolant Injection System For Surveillance And "B" Low Pressure Coolant Injection System For Maintenance</strong><br /><i>Abstract:&nbsp;</i>On 6/4/91 at 1914, the Senior Nuclear shift Supervisor (SNSS, SRO licensed) determined that Hope Creek had been in a condition requiring entry into Technical Specification 3.0.3 for a period of 6 minutes between 1901 and 1907. The condition requiring entry was due to the concurrent inoperability of the High Pressure Coolant Injection (HPCI) system and "B" loop of the Low Pressure Coolant Injection (LPCI) mode of the Residual Heat Removal (RHR) system. A surveillance was being conducted on HPCI at the same time that RHR was being returned to service following a scheduled system outage, however, overlap between the time the surveillance was actually started and LPCI was declared operable exceeded one hour. The primary causes of this occurrence were personnel errors on the part of the a Nuclear Shift Supervisor (NSS, SRO licensed) and Controls Department senior supervisor. The NSS failed to recognize the Technical Specification conflict between the HPCI surveillance and the RHR system outage. The Controls Department Senior Supervisor did not give an adequate RHR system status turnover because he erroneously assumed the RHR system outage was completed. Corrective actions included reviewing this event with the NSS and Controls Department Senior Supervisor involved in this event, enhancing the surveillance scheduling process, reviewing this event with all Operations Department and Controls Department supervisors, and reviewing Controls Department HPCI system surveillances to enhance precautions to preclude concurrent inoperability of multiple ECCS systems.
3541991013 | Hope Creek | 06/05/1991 | 07/02/1991 | 9107120298 | <strong>Both Trains Of Standby Liquid Control Inoperable During Performance Of Inservice Testing - Procedural Deficiency - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>On 6/5/91, during a review of an industry operating experience document for applicability to Hope Creek, a Safety Review Engineer determined that, during quarterly Inservice Testing (IST) of the Standby Liquid Control (SLC) system pumps, both SLC loops would be inoperable for a short period of time during the testing. The system valve alignments required by the quarterly SLC IST procedures could, for a brief period, establish a system flowpath such that the operable SLC loop would not inject to the reactor vessel if a valid injection signal occurred concurrent with performing the first portion of the IST procedure. These findings were communicated to the Senior Nuclear Shift Supervisor (SNSS, SRO licensed), and a change request was immediately initiated to modify the affected quarterly SLC IST procedures.
3541991014 | Hope Creek | 06/19/1991 | 07/17/1991 | 9107240203 | <strong>Engineered Safety Features Actuation: Various Channel "B" Emergency Core Cooling System Actuations/Initiations During Design Change Implementation Due To Relay Cabinet Design Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On 6/19/91 at 2025, during implementation of a design change in a Emergency Core Cooling System (ECCS) relay cabinet by Controls Department technicians, while loosening a termination screw, a wire retaining ring attached to the screw was inadvertently rotated such that it came in contact with an adjacent terminal post. The resultant short circuit caused a momentary loss of power to trip units in the relay cabinet, actuating various channel "B" Loss of Coolant Accident (LOCA) systems and components. After confirming the cause of the event and verifying all system responses had occurred as expected, the Senior Nuclear Shift Supervisor directed that the channel "B" ECCS actuation signals be reset, and all systems and components were returned to a normal (standby) status. No ECCS injection to the reactor vessel occurred. The primary cause of this occurrence was a design deficiency in the subject ECCS relay cabinet, in that limited internal cabinet accessibility inhibits testability and maintenance of components inside the cabinet. The subject design change was being implemented to prevent occurrences such as noted in this report. Corrective actions consist of completing the design change in the relay cabinet, reviewing the event with all Controls Department technicians involved in the continuing implementation of the subject design change, and incorporating lessons learned from this event into Controls Department technician training.
3541991015 | Hope Creek | 06/26/1991 | 07/24/1991 | 9107260184 | <strong>Engineered Safety Features (ESF) Actuation (Reactor Water Cleanup Isolation) Due To Tripping Of Reactor Protection System Channel "A" Electrical Protection Assembly</strong><br /><i>Abstract:&nbsp;</i>On 6/26/91 at 0921, the control room received indication of a half scram, and isolations of the inboard Reactor Water Cleanup (RWCU) isolation valve, Reactor Recirculation Sample Valve, and Main Steam Line Inboard Drain valve. The above actions occurred as a result of a loss of the power supply to the Channel "A" Reactor Protection S stem (RPS) electrical bus when the alternate power supply Electrical Protection Assembly (EPA) experienced a spurious trip (the bus was being fed by its alternate power supply due to a preventive maintenance outage of the Channel "A" RPS motor generator set). The Channel "A" RPS bus was re-powered from its normal power source, and the half scram and RWCU isolation were reset. Followup troubleshooting by the Maintenance Department and Systems Engineering could not determine a definitive reason for the trip of the EPA, however, it is suspected that the trip resulted from an EPA performance problem similar to those noted in General Electric Service Information Letter (SIL) 496. Immediate corrective actions consisted of troubleshooting the subject EPA, performing a functional test of the EPA, and adjusting the RPS bus alternate power supply transformer voltage to a higher value. Longer term corrective actions consist of implementing a modification to all RPS EPAs, as described in SIL-496, when EPA logic card upgrade kits are received from the vendor.
3541991016 | Hope Creek | 07/24/1991 | 08/21/1991 | 9108290111 | <strong>Engineered Safety Features Actuation (ESF) - Reactor Core Isolation Cooling System isolation due to Instrument failure.</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1991 at 1900 Hrs, a RCIC Steam Line Isolation and RCIC Turbine Trip occurred when a NUMAC temperature sensor associated with the Inboard RCIC steam line Isolation System failed. All plant Systems responded normally to this event and all appropriate Control Room Annunciators alarmed. After Control Room Personnel verified the isolation was not valid, repairs to the NUMAC module were initiated. when repairs were completed RCIC was placed in standby lineup and declared Operable. This report is being submitted pursuant to 10CFR50.73 (a) (2) (iv) Engineered Safety Feature Actuation.
3541991017 | Hope Creek | 08/15/1991 | 09/12/1991 | 9109200202 | <strong>Engineered Safety Feature Initiation (ESF) - High Pressure Coolant Injection System initiation due to equipment malfunction.</strong><br /><i>Abstract:&nbsp;</i>On 8/15/91 at 0109 hours Instrument and Control Technicians were in the process of performing a Channel Calibration of the Division 1 Hi Drywell Pressure transmitter. When the technician performed the gross fail portion of the test, the Drywell pressure Hi Hi Annunciator was received in the Control Room and indications of a subsequent High Pressure Coolant Injection System start (HPCI) occurred. After verifying no valid initiation signals were present, HPCI was secured prior to injecting into the Reactor Pressure Vessel. The Technicians performing the test were ordered to terminate the test until a preliminary investigation was completed. Initially, it was believed that the cause of the initiation was a faulty logic tester used in the performance of the surveillance. A different logic tester was employed in the second running of the surveillance which was completed satisfactorily later in the shift. All Control Room Annunciators and plant systems responded normally to this event. The most probable cause of the event was subsequently determined to be an intermittent spike on the output of a optic isolator card.
3541991018 | Hope Creek | 09/14/1991 | 10/09/1991 | 9110220150 | <strong>Engineered Safety System Action - "F" Filtration Recirculation Ventilation System Fan start.</strong><br /><i>Abstract:&nbsp;</i>On 9/14/91 at 0640 hours, during shift turnover, Control Room Operators (RO licensed) discovered that the "F" Filtration Recirculation Ventilation (FRVS) fan was running. After verifying no valid start signals were present the fan was secured. Operators could not determine the cause of the fan start and requested Instrument and Control Technicians to investigate. A review of the alarm chronolog did indicate a pressure perturbation in reactor building pressure at 0607 indicative of the fan starting. The I&C technician found water accumulated in the low flow switch associated with the out of service "C" FRVS recirculation fan. This switch provides an auto start signal to the standby fan in the event the running fan trips or develops a low flow condition. The technician drained the instrument tubing and the F FRVs recirculation fan was returned to a standby lineup.
3541991019 | Hope Creek | 11/23/1991 | 03/11/1992 | 9203190173 | <strong>Engineered Safety System Action - "E" Filtration Recirculation Ventilation System Recirc Fan Start</strong><br /><i>Abstract:&nbsp;</i>On 11/23/91 at 0500 hours, Control Room Operators (RO licensed) discovered that the "E" Filtration Recirculation Ventilation (FRVS) fan was running. After verifying no valid start signals were present the fan was secured. At 0638 hours during shift turnover the "E" FRVS fan started a second time. Operators noticed the fan start during panel walk down. They again verified no valid start signals were present and secured the fan. Operators could not determine the cause of the fan start and requested Instrument and Control Technicians to investigate. On 12/13/91 the E FRVS was instrumented and the FRVS System (A,B,C and D FRVS Recirc fans) was placed in service to determine the root cause of the spurious fan starts in conjunction with DOP/Halide testing. The FRVS System was in service for 6.5 hours with no auto fan starts occurring. The fans were secured at 1222 hours at the completion of the DOP/Halide test. At 1557 hours the E FRVS Recirc fan spuriously started and was subsequently secured by operations personnel. Subsequent investigation has revealed an accumulation of water in the low flow switch sensing lines as the most probable cause of the spurious fan starts. The testing did result in additional fan starts, on 12/23/91 the standby "E" FRVS Recirc unit, on 1/2/92 the standby "F" FRVS Recirc unit auto started and on 1/14/92 "E" FRVS Recirc unit auto started. An additional start of the "E" FRVS Recirc unit occurred on 2/16/92 following a surveillance test run. Previous corrective actions to ensure the accumulated water is drained periodically has improved operation of the system; however, subsequent investigation has revealed the need for more frequent draining and the possibility of rerouting the instrument tubing to eliminate collection points.
3541991020 | Hope Creek | 12/07/1991 | 01/06/1992 | 9201090021 | <strong>Engineered Safety Feature Actuation (ESF) - High Pressure Coolant Injection System isolation due to improper</strong><br /><i>Abstract:&nbsp;</i>On 12/07/91 at 1900 Hrs Control Room Personnel received indication of a High Pressure Coolant Injection System (HPCI) isolation during steam line warmup following a HPCI outage. After verifying no valid signals were present, control room personnel requested Instrument and Controls technicians to investigate the cause of the isolation. The technicians determined the isolation had occurred due to an intermittent error in the subtraction circuit of the "A" channel NUMAC drawer. The drawer was checked and a self test was initiated. The drawer tested satisfactory and the equipment was returned to service. During subsequent warm-up of the HPCI steam line, operators continued to monitor the NUMAC drawer with no abnormal conditions noted. HPCI was then placed in a standby lineup and declared operable. On 12/19/91 technicians performing a root cause investigation into the isolation noted that the field wiring of the thermocouples in the "A" channel isolation system were mis-wired. The System was declared inoperable and the field wiring was returned to proper configuration. Preliminary results of subsequent investigations have indicated the thermocouple leads may have been landed incorrectly during implementation of a design change package during refuel outage three. The redundant "C" channel isolation module has been verified to be wired correctly and operable. The system has been tested satisfactorily and HPCI was returned to a standby lineup.
3611991001 | San Onofre 2 | 01/19/1991 | 03/04/1991 | 9103080341 | <strong>Fuel Movements Performed Within The Spent Fuel Storage Pool Without Concurrent Operation Of Post Accident Cleanup Unit As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 1/25/91, with Unit 2 at 100% power, during the performance of the Train "B" fuel handling building Post Accident Clean-up Unit (PACU) (E-371) monthly surveillance, the, PACU inlet duct heater (E-465) was found to be "off", contrary to the surveillance requirements. Investigation revealed that the local pilot switch for E-465 was in the "off" position, de-energizing the heater. The pilot switch was turned "on", and the surveillance was re-initiated and completed satisfactorily. <br /><br /> Subsequently, it was determined that a previous E-371 monthly surveillance performed on 1/15/91 was incorrectly accepted as satisfactory since the completed surveillance procedure indicates that the heater was "off", contrary to procedural and Technical Specification (TS) requirements during the conduct of the test. Consequently, the operability requirements for PACU E-371 were not satisfied when movement of irradiated fuel in the Unit 2 Spent Fuel Pool occurred during the period of January 19 through 22, 1991 which resulted in violating the requirements of TS 3.9.12. <br /><br /> We have been unable to definitively determine the mechanism which resulted in mispositioning the heater pilot switch. The erroneous acceptance of the E-371 monthly surveillance performed on 1/15/91 is attributed to procedural deficiencies, inadequate knowledge level of PACU heater operation, and inadequate review of the surveillance test results by the personnel involved. Corrective actions include enhancing the PACU monthly surveillance procedure and reviewing this event with appropriate personnel.
3611991003 | San Onofre 2 | 03/10/1991 | 04/09/1991 | 9104150330 | <strong>Unit 2 Automatic Reactor Trip Due To Failed Control Element Drive Mechanism Control System (CEDMCS) Motor Generator (MG) Over/Underexcitation Protection Relay</strong><br /><i>Abstract:&nbsp;</i>At 1206 on March 10, 1991, with Unit 2 at 77% power and CEDMCS #1 MG set out of service for maintenance, the output contactor for the redundant MG set opened, causing de-energization of the CEDMCS bus and an automatic reactor trip. During recovery from the trip, both main feedwater bypass valves (MFBVs) opened unexpectedly. Control room operators attempted to throttle closed both MFBVs, but MFBV 2HV-1105 failed to respond to demand. As a result, steam generator (SG) E-089 level increased above that anticipated. Control room operators closed the associated main feedwater isolation valve to stop main feedwater flow to E-089. The plant was stabilized in Mode 3 at approximately 1230. During the post trip review, it was noted that SG level Channel C responded more slowly than the other three channels. <br /><br /> Failure of the CEDMCS #2 MG set ammeter (AMR) relay underexcitation contact caused the #2 MG set output contactor to open. The AMR relay was sent to an offsite laboratory for failure analysis. A low proportional band setting of the Feedwater Control System controller caused the MFBVs to open unexpectedly during recovery following the trip, causing the excursion in SG level. The investigation is continuing into the cause for 2HV-1105 anomalous operation. The slow response of the SG level Channel C was attributed to sediment in the transmitter sensing lines; evaluation of the SG level channel sluggish response is continuing. <br /><br /> The AMR relay for the CEDMCS #2 MG set was replaced. The proportional band of the FWCS controller was increased, and a minimum value determined. MFBV 2HV-1105 was stroke tested satisfactorily, demonstrating its proper operation. SG E-089 level Channel C sensing lines were blown down, and the instrument returned to within tolerance of the other three channels. Corrective actions will be implemented as necessary based on the results of the continuing cause investigations into the AMR relay failure, 2HV-1105 response failure, and the SG level Channel C sluggish response.
3611991004 | San Onofre 2, San Onofre 3 | 02/27/1991 | 03/29/1991 | 9104020396 | <strong>Fire Watches Not Established Within One Hour Contrary To Technical Specification 3.3.3.7</strong><br /><i>Abstract:&nbsp;</i>At 1535 on February 27, 1991, with Units 2 and 3 operating in Mode 1 at 100% power, based upon information received in the Control Room including; a ground alarm, a report of water near non-Technical Specification (TS) Pyrotronics Control Panel 2/3L-201-3 (it was raining heavily at the time), and the inability to reset spurious supervisory and fire alarms from the panel, Operators appropriately opened power supply breaker 2L-414-13 to de-energize the panel. Opening the breaker also caused the de-energization of a related TS Pyrotronics Control Panel 2/3L-201-1. As a result, 31 hourly fire watches in the Unit 2/3 Auxiliary Radwaste Building were required to be established. The establishment of fire watches was not completed within the 1 hour required by TS 3.3.3.7. Appropriate fire watches were in place by 1800.<br /><br /> The cause of this event was that the work process associated with the establishment of the fire watches required by the de-energization of TS Pyrotronics Control Panel 2/3L-201-1 was unwieldy and could not be accomplished within the 1 hour TS Action requirement.<br /><br /> An investigation into the cause of the spurious supervisory and fire alarms from panel 2/3L-201-3 is currently ongoing. Contingency plans for similar scenarios are being developed. Fire watch supervision will be relocated to the same area as the Emergency Services Officers (ESOs) to facilitate more rapid deployment of fire watches. A list of SONGS Units 2 and 3 power supply breakers associated with fire detection instrumentation will be made more readily available to the ESOs and Operations personnel which will aid in the identification of affected fire area/zones and attendant compensatory action requirements.
3611991005 | San Onofre 2, San Onofre 3 | 03/01/1991 | 04/01/1991 | 9104080207 | <strong>Missed Technical Specification Surveillance Concerning Explosive Gas Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1991 at 0515, the Oxygen (O sub 2) analyzer for the Waste Gas Surge Tank (WGST) was declared inoperable due to continuous spiking. Technical Specification (TS) 3.3.3.9 Action b was entered, and action was initiated to realign the alternate Hydrogen/Oxygen (H sub 2/O sub 2) analyzer to the WGST. At 0925, the operable H sub 2/O sub 2 analyzer was aligned and in service on the WGST. Since this realignment took approximately 4 hours, 10 minutes, the requirement of the TS to, within 4 hours, either restore monitoring capability to the WGST or obtain a grab sample of its contents was not fully satisfied. <br /><br /> This event was caused by an inadequate operating instruction. The operating instruction did not specify the need to complete the transfer within 4 hours or take the grab sample. In addition, the TS action statement does not provide clear direction for this action. <br /><br /> The Operating Instruction will be revised to clearly and fully address the operability requirements of the analyzers such that the time limits of the TS action statement are satisfied. The TS will be clarified as part of SCE's submittal in connection with the Technical Specification Improvement Program. Training will be provided to Operations personnel on the TS requirements.<br /><br /> There was no safety significance to this event. The H sub 2/O sub 2 concentrations in the WGST, both prior to the failure of the WGST analyzer and following the realignment of the remaining operable H sub 2/O sub 2 analyzer to the WGST, were below their respective alarm setpoints.
3611991006 | San Onofre 2, San Onofre 3 | 03/25/1991 | 04/24/1991 | 9104290234 | <strong>Inadvertent Toxic Gas Isolation System (TGIS) Actuation During The Performance Of Maintenance Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>At 1530 on March 25, 1991, with Unit 2 at 60% power and Unit 3 at 100% power, Toxic Gas Isolation System (TGIS) Train "A" actuated on high ammonia gas level. All TGIS Train "A" components were verified to have actuated as required. <br /><br /> The actuation occurred while troubleshooting was being performed on the Train "A" ammonia channel, which had failed on March 24, 1991. A Maintenance technician inadvertently bumped the jumper used to bypass the TGIS actuation circuitry, resulting in the jumper being momentarily dislodged. Since the ammonia level had been increased above the actuation setpoint to perform the troubleshooting, an actuation on high ammonia occurred. <br /><br /> The root cause of this event is that the location of the jumper used for bypassing the TGIS actuation circuitry was adjacent to the area requiring access during maintenance activities. Therefore, a potential existed for disturbance of the jumper during these activities.<br /><br /> For corrective actions: 1) appropriate disciplinary action has been administered to the technician involved in this event, 2) this event has been reviewed with appropriate Maintenance personnel, and 3) the bypass jumper, when installed in the future, will be relocated to an area less likely to be affected by maintenance activities.
3611991007 | San Onofre 2 | 04/10/1991 | 07/01/1993 | 9307060296 | <strong>Unit 2 Manual Reactor Trip Due To Loss Of Reactor Coolant Pump P004 Controlled Bleedoff Flow</strong><br /><i>Abstract:&nbsp;</i>This revision provides an amended cause assessment and corrective action section based on completion of our root cause evaluation. <br /><br /> At 1606 on April 10, 1991, the Unit 2 reactor was manually tripped on indication of a complete loss of controlled bleedoff (CBO) flow from reactor coolant pump (RCP) P004. P004 was stopped following the trip, and the plant was stabilized in Mode 3 at 1621. Emergency feedwater actuation system (EFAS) signals were generated for both steam generators (SGs) due to the expected SG level "shrink" following the trip.<br /><br /> CBO flow ensures long term integrity of the RCP seals during RCP operation. The loss of CBO flow was due to a shift in position of the P004 rotating baffle, whose fastening bolts were found to have fractured. The root cause of the failure of the baffle bolts was loss of preload due to thread embedment. Embedment is the plastic deformation of local high spots on the mating portions of threads. When this deformation takes place, the fasteners lose preload and are subject to cyclic stresses that can lead to fatigue failure. The P004 baffle was inspected, repaired, and re-installed with new bolts. <br /><br /> The P004 seal assembly was replaced with an in-kind part. The other three RCP baffles were inspected for similar deficiencies. Three (of six) baffle bolts on RCP P001 were found to have slightly loosened; no loose bolts were identified on the other two RCPs. The baffle bolts for these three RCPs were also replaced with new bolts.
3611991008 | San Onofre 2, San Onofre 3 | 06/22/1991 | 07/22/1991 | 9107260138 | <strong>Units 2/3 Spurious Toxic Gas Isolation System (TGIS) Actuation due to Train "A" Ammonia Analyzer Failure</strong><br /><i>Abstract:&nbsp;</i>At 0738 on 6/22/91, with Units 2 and 3 at 100% power, a Toxic Gas Isolation System (TGIS) actuation occurred in response to an apparent high ammonia signal as detected by the train "A" analyzer. All TGIS Train "A" components were verified to have actuated as required. TGIS Train "A" was reset at 1406. <br /><br /> Subsequent investigation by Operations found the TGIS Train "A" ammonia analyzer local indication to be spiking, indicative of an analyzer failure. The spiking was found to be due to erratic rotation of the ammonia analyzer chopper motor, which was later determined to be caused by corrosion of the motor internals. <br /><br /> The ammonia analyzer chopper motor was replaced and the analyzer re-calibrated. The failed chopper motor was sent to an offsite laboratory for failure analysis, which concluded that the observed corrosion of the chopper motor internals occurred prior to installation. The corrosion of the chopper motor internals has been attributed to either: 1) moisture introduced during storage for the five year period since SCE received the motor, or 2) moisture introduced during manufacture of the chopper motor resulting in corrosion, with the latter cause considered more likely. Inspection of other analyzers has shown no evidence of corrosion. TGIS analyzer chopper motors will be inspected for evidence of corrosion prior to installation until compelling evidence exists that the observed corrosion was an isolated occurrence.
3611991009 | San Onofre 2 | 07/02/1991 | 07/30/1991 | 9108050294 | <strong>Control Room Isolation System Spurious Actuation Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1337 on July 2, 1991, with Units 2 and 3 at 100% power, a Control Room Isolation System (CRIS) Train B spurious actuation occurred when, during the performance of on-the-job training, a radiation monitoring technician accidentally contacted the CRIS radiation monitor module power on/off pushbutton. This action de-energized the module, causing the actuation. All CRIS Train B components were verified to have actuated as required. CRIS was reset and the ventilation lineup returned to normal at 1400. <br /><br /> This event was discussed with the radiation monitoring technician who accidentally caused the CRIS module to de-energize, emphasizing the need to exercise care around operating equipment. This event will be reviewed with appropriate radiation monitoring technicians, emphasizing the need to exercise care while performing their assigned tasks. <br /><br /> There is no safety significance to this event since radiation levels remained normal and all CRIS Train B components actuated as required.
3611991010 | San Onofre 2 | 08/03/1991 | 09/03/1991 | 9109100314 | <strong>Control Room Isolation System Spurious Actuations (2) Due To Instrument Failures</strong><br /><i>Abstract:&nbsp;</i>At 0422 on August 3, 1991, and at 1731 on August 18, a Control Room Isolation System (CRIS) Train B spurious actuation occurred when sensed background count rate on CRIS Train B radiation monitor RT-7825 noble gas channel decreased below the instrument failure setpoint. There is no safety significance to these events since radiation levels remained normal and all CRIS Train B components actuated as required.<br /><br /> Inspections were performed on RT-7825 noble gas channel following both actuations. The inspections, which included verification that the detector connections were tight and that all front panel switches functioned properly, did not identify a cause for the instrument failures. The CRIS Train B detector and control room module were removed from the plant and replaced with in-kind parts. The monitor was returned to service at 0550 on August 24. Testing will be performed on the removed components in an effort to identify the root cause of the actuations. Appropriate corrective actions will be determined and implemented as necessary based on the results of the investigation.
3611991011 | San Onofre 2, San Onofre 3 | 08/30/1991 | 09/27/1991 | 9110020262 | <strong>Control Room Isolation System Train B Spurious Actuation</strong><br /><i>Abstract:&nbsp;</i>At 1253 on August 30, 1991, with Unit 2 in a refueling outage and Unit 3 at 100% power, a Control Room Isolation System (CRIS) Train B spurious actuation occurred. At 2115, CRIS Train B was placed in bypass, and at 2205, the control room ventilation lineup was returned to normal. There is no safety significance to this event since radiation levels remained normal and all required components actuated as designed. <br /><br /> At the time of the actuation, no maintenance or testing was being performed on the CRIS circuitry. Only the alarm associated with the CRIS Train B actuation relay annunciated. None of the other CRIS alarms which indicate causes of the actuation, such as high radiation or instrument trouble, were received. The most likely cause of the actuation was electronic noise associated with either the CRIS radiation monitor power supply or the signal path from the monitor. Extensive testing could not determine the specific cause of the actuation. <br /><br /> A design change to reduce the CRIS radiation monitor susceptibility to noise is being prepared. Monitoring equipment will be installed on the suspect circuitry for the next 90 days to enable the cause of any similar CRIS actuation to be more positively determined. If this monitoring identifies the cause for this actuation, appropriate corrective actions will be implemented.
3611991012 | San Onofre 2, San Onofre 3 | 08/29/1991 | 09/30/1991 | 9110080346 | <strong>Environmental Qualification Deficiencies of Containment High Range Area Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>With Unit 2 shutdown for a refueling outage, a validation effort of environmentally qualified (EQ) equipment in Unit 2 containment was performed as a corrective action to LER 89-012-01 (Docket No. 50-361). During this effort it was determined, on 8/29/91, that the coaxial connectors for the Containment High Range Area Radiation Monitors (2RE-7820-1 and 2RE-7820-2) inboard penetration enclosures were not provided with Raychem heat shrink sleeve kits. These kits are required for operability of the monitors in the postulated post-accident environment. Prompted by the findings at Unit 2, on 9/16/91, with Unit 3 at approximately 100% power, the coaxial connectors to the Unit 3 Containment High Range Radiation Monitors were inspected. This inspection revealed that Raychem heat shrink sleeve kits had not been installed. Raychem heat shrink sleeve kits for 3RE-7820-1 and 3RE-7820-2 were installed on 9/17/91 and 9/18/91, respectively. <br /><br /> This event has been attributed to discrepancies in the Environmental Qualification Documentation Packages (EQDP) associated with the Containment High Range Area Radiation Monitors. The causes of these discrepancies are similar to those reported in LER 89-012 (Docket No. 50-361), which described weaknesses in the implementation and administration of the EQ program. <br /><br /> Prior to returning Unit 2 to service, Raychem heat shrink sleeve kits will be installed on the Unit 2 penetration coaxial connectors. The EQDPs and the configuration drawings associated with the Units 2 and 3 Containment High Range Area Radiation Monitors will be revised to incorporate references to the installation of EQ qualified Raychem heat shrink sleeve kits. Any additional EQ discrepancies identified during implementation of corrective actions associated with LER 89-012-01 (Docket No. 50-361) will be reported in a supplement to this LER.
3611991013 | San Onofre 2, San Onofre 3 | 09/05/1991 | 10/02/1991 | 9110090323 | <strong>Spurious Train "A" Toxic Gas Isolation System (TGIS) Actuation due to Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0718 on 9/5/91, with Unit 2 in Mode 6 and Unit 3 at 100% power, the Train "A" Toxic Gas Isolation System (TGIS) VI! actuated. Control room alarms and indications alerted control room operators (utility, licensed) of the actuation. Operators responded properly to the Train "A" TGIS actuation by promptly: 1) verifying proper system operation, and 2) determining that the actuation was spurious due to a momentary loss of power. At 0815 the NRC was notified via red phone of both a TGIS and a Control Room Isolation System (CRIS) actuation. Subsequent investigation has determined that only a TGIS actuation occurred. Train "A" TGIS was reset and normal control room ventilation restored at 0822. <br /><br /> Preparations were being made for a Unit 2 Train "A" electrical Bus outage at the time of the actuation, with Unit 3 supplying power to the Train "A" TGIS. An operator was reading Circuit Breaker (CB) 52! numbers and required CB positions from a checklist while another operator (both utility, non-licensed) was tagging and positioning the CBs. While positioning the CBs, the second operator inadvertently opened the CB which supplies power from Unit 3 to the Train "A" TGIS sample pump and analyzers. The operator immediately re-closed the CB. <br /><br /> This event was caused by inattention to detail (cognitive error) by the operator positioning the CBs. The operator involved in this event has received appropriate disciplinary action. In addition, the circumstances of this event have been reviewed with appropriate Operations personnel. There was no safety significance to this event since all Train "A" TGIS components functioned as designed.
3611991014 | San Onofre 2 | 09/10/1991 | 11/13/1991 | 9111220208 | <strong>Inoperable Steam Supply Check Valve For The Auxiliary Feedwater</strong><br /><i>Abstract:&nbsp;</i>On 9/10/91, with Unit 2 in Mode 6 and defueled, turbine-driven Auxiliary Feedwater Pump (AFWP) P-140 steam-supply-check valve MU-005 was found to be damaged. The damage was discovered during an inservice testing (IST) activity in which the valve was disassembled to demonstrate full stroke capability. The check valve hinge pins were found to be damaged such that the valve disc was separated from the pins and lodged in the valve outlet body. The observed damage was indicative of the disc having been subjected to a large impact force. Our root cause evaluation indicates that the impact force was caused by a mass of water entrained in steam flowing through P-140 steam supply piping. Although the time of the event cannot be definitively determined, the damage is hypothesized to have occurred following the return to service of P-140 after the completion of maintenance activities, a time when the system is most vulnerable to the accumulation of condensation in the piping. <br /><br /> Air flow testing was performed on MU-005 in the as-found condition to evaluate the capability of the valve to perform it's design function. For the majority of accidents crediting AFW, we determined that the valve would not have prevented P-140 from performing it's design function. However, for a narrow range of postulated events, back flow of steam through the failed check valve could result in inadequate steam flow to the P-140 turbine, preventing P-140 from fulfilling it's design function. Thus, P-140 is considered not to have satisfied all of the necessary operability requirements of the Technical Specifications. <br /><br /> Corrective actions include installing a replacement check valve and modifying appropriate Operations procedures to ensure that the AFW steam supply lines are properly drained prior to placing P-140 in service. The Unit 3 turbine-driven AFWP steam-supply-check valves MU-003 and MU-005 were radiographed, and verified to be operating normally.<br /><br /> It has been determined that the safety consequences of the observed damage to MU-005 are minimal.
3611991015 | San Onofre 2 | 10/01/1991 | 10/30/1991 | 9111060259 | <strong>Containment Purge Isolation System Train "A" Actuation While Performing Radiography</strong><br /><i>Abstract:&nbsp;</i>On 10/1/91, at 0323, with Unit 2 in Mode 6 and containment purge in progress, a Containment Purge Isolation System (CPIS) JM! Train "A" actuation occurred during radiography in the vicinity of Containment Area Radiation Monitor 2RT-7856 MON!. Control room operators (utility, licensed) were alerted to the Train "A" CPIS actuation by control room annunciators ANN!. Operators responded properly to the actuation by 1) verifying that all CPIS Train "A" components operated in accordance with design and 2) verifying that the actuation was spurious before resetting CPIS and restoring containment purge at 0357. <br /><br /> At approximately 0240, prior to the performance of radiography and in accordance with procedure, Health Physics (HP) technicians notified the Control Operator (CO) that radiography was to be performed in containment and that radiation monitors may be affected. The discussion that took place between the HP technicians and the CO was not sufficiently clear for the CO to recognize that the proposed radiography could cause a CPIS actuation. The control operator did not anticipate that the radiography would cause a CPIS actuation; the actuation is therefore not considered preplanned. <br /><br /> To prevent recurrence of unplanned Engineered Safety Feature (ESF) actuations during radiography: 1) appropriate HP procedures have been modified to provide specific guidance regarding control room notification when radiography is performed in the vicinity of radiation monitors having ESF actuating functions, 2) appropriate Operations procedures will be modified to provide guidance for Operations personnel regarding the potential for ESF actuations during radiography activities, and 3) training relating to the procedure changes will be conducted for appropriate HP and Operations personnel. There was no safety significance to this event since all Train "A" CPIS components functioned as designed.
3611991016 | San Onofre 2, San Onofre 3 | 10/10/1991 | 11/08/1991 | 9111150011 | <strong>Control Room Installation System Train B Spurious Actuation Due To Instrument Failure</strong><br /><i>Abstract:&nbsp;</i>At 1238 on October 10, 1991, with Unit 2 in a refueling outage and Unit 3 at 100% power, a Control Room Isolation System (CRIS) Train B actuation occurred. The actuation was verified to be spurious, and all required components were verified to have actuated as designed. The CRIS Train B radiation monitor was placed in bypass, and at 1340, the control room ventilation lineup was returned to normal. There is no safety significance to this event since radiation levels remained normal and all CRIS Train B components actuated as required by the design. <br /><br /> The cause of the actuation was determined. to be a momentary (approximately 48 msec) instrument failure of the CRIS Train B particulate/iodine channel. The instrument failure was caused by a spurious noise signal either on the power input to the CRIS particulate/iodine channel module or on the signal path from the detector. <br /><br /> A design change to reduce the CRIS radiation monitor susceptibility to noise is being prepared. As an interim corrective action to reduce the susceptibility of the module to noise, a temporary modification has been installed which (1) adds a filtering circuit to the (AC) input to the radiation monitor module, and (2) enhances the filtering of the internal (DC) power supply regulators. Monitoring instrumentation previously attached to the CRIS Train B radiation monitor module (refer to LER 91-011, Docket No. 50-361) will remain installed for the balance of the initially planned 90-day period. This instrumentation will allow the cause of any similar CRIS actuation which occurs during this period to be more positively determined.
3611991017 | San Onofre 2, San Onofre 3 | 11/12/1991 | 12/12/1991 | 9112190015 | <strong>Delinquent Reactor Coolant System Surveillance Sample</strong><br /><i>Abstract:&nbsp;</i>On 11/13/91, it was determined that the Unit 2 and Unit 3 Reactor Coolant System samples obtained on 11/11/91, had not been analyzed for fluoride within the time required by Technical Specification (TS) 3/4.4.6, "Reactor Coolant System Chemistry." The analyses were required to be completed on 11/12/91 at 0223 and 0250 for Unit 2 and Unit 3, respectively. The fluoride analyses were subsequently completed at approximately 1100 on 11/12/91. <br /><br /> The root cause of this event was determined to be a cognitive personnel error. A Nuclear Chemistry Technician foreman (utility, non-licensed) had incorrectly deferred completion of the analysis without recognizing that the surveillance interval (including the extension allowed by TS 4.0.2) would be exceeded. In addition, difficulties were encountered in the use of the fluoride analysis equipment which contributed to the delay. <br /><br /> Corrective actions include 1) reviewing this event with appropriate Chemistry personnel, and 2) providing refresher training with respect to TS sampling and analysis requirements to appropriate Chemistry personnel. <br /><br /> There was no safety significance to this event since subsequent sample results were within the TS limits.
3611991018 | San Onofre 2 | 10/15/1991 | 02/25/1992 | 9203040201 | <strong>Safety Related Instrumentation Not Installed in a Seismically Qualified Configuration</strong><br /><i>Abstract:&nbsp;</i>On 10/15/91, while Unit 2 was in Mode 5 during a refueling outage, an inspection of the safety related Foxboro Spec 200 Process Instrumentation cabinets CAB! determined that several instrument modules were missing the upper and/or lower guide rails and/or vibration dampening material (bumpers). Without the guide rails and bumpers installed, this equipment would not conform to the vendor's generic seismic design requirements and was therefore considered inoperable, causing the applicable Technical Specification Limiting Condition for Operation for affected instrument loops to have been exceeded during previous periods of operation in Modes 1, 2, 3, and 4. Subsequent seismic testing demonstrated that without bumpers installed, the affected instrument modules would have functioned properly during and after the SONGS design basis seismic events. By 11/4/91, all missing guide rails were installed, and the affected instrumentation was returned to an operable condition. <br /><br /> The primary cause of this deficiency was determined to be inadequate vendor installation information. Additionally, although the information provided in the vendor qualification report presented an opportunity for SCE to identify the installation deficiency, this subtlety was not detected. To prevent recurrence, vendor technical manuals will be updated to include the latest revision of Foxboro MI 2AN-105 which clearly identifies these installation requirements. Lesson plans for in-house training courses will be updated to include a discussion on the seismic installation requirements. Although testing demonstrated that bumpers were not required, in order to maintain conservative margins, all missing bumpers will be replaced during the next scheduled refueling outage for SONGS 1, 2, and 3.<br /><br /> The safety significance was evaluated and determined to be inconsequential.
3611991019 | San Onofre 2 | 11/16/1991 | 09/29/1994 | 9410050256 | <strong>Inoperable Containment Pressure Instrumentation Due To Misconfigured Wiring From Instrument Line Isolation Valve Solenoid Actuator</strong><br /><i>Abstract:&nbsp;</i>At 2030 on 11/25/91, with Unit 2 at 100 power, it was determined that containment pressure instrument line isolation valve 2HV0352C had been closed (although indicating open) since the valve operating solenoids and position indication assembly had been replaced on 11/9/91, during the previous refueling outage. As a result, the channel "C" containment pressure transmitters had been isolated from containment, and inoperable, since that time. Technical Specification (TS) 3.3.2, "Engineered Safety Feature Actuation System Instrumentation," requires that in Modes 1-3, an inoperable containment pressure channel must be bypassed within one hour. Mode 3 was entered at 2329 on 11/15/91. Therefore, operation in Modes 1- 3 after 0029 on 11/16/91, with PPS channel "C" not bypassed, represented an operation prohibited by TSs. There is minimal safety significance to this event since the remaining channels of containment pressure instrumentation remained capable of initiating associated plant protection system actuations. <br /><br /> While performing maintenance on valve 2HV0352C solenoid actuator assembly internals, the intended polarities of both the opening coil and the closing coil were inadvertently reversed. As a result, the valve actuator was installed such that both operation and control room indication of the valve were reversed. The valve's position cannot be locally, visually ascertained; therefore, the restoration and maintenance verification testing of the valve relied solely on control room indication to verify proper valve operation and indication. A more rigorous test would have identified the reverse operation of the valve prior to its return to service. <br /><br /> After the valve solenoid actuator assembly internals were corrected, Edison performed a more rigorous restoration and maintenance verification test to verify proper valve operation. This event has been included in the applicable training programs for personnel who determine valve restoration and maintenance verification testing requirements. Additionally, Edison will enhance the Restoration and Maintenance Verification Testing procedure, for this and similar valves, to require a means to verify proper valve operation and indication.
3611991020 | San Onofre 2, San Onofre 3 | 12/26/1991 | 10/12/1994 | 9410190068 | <strong>Delinquent Weekly Surveillance On Class 1E 125 VDC Batteries Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 9/15/94, during a routine audit of Technical Specification (TS) 3/4.8.2, "D.C. Sources," Edison identified that the required weekly surveillance of the eight Class 1E 125 VDC batteries EJ, BTRY! for Units 2 and 3 in December 1991 was delinquent by approximately 3 to 6 hours. The batteries were surveilled on 12/17/91 at 1130 and 0930 for Units 2 and 3, respectively. With the allowed 25% extension, the next weekly surveillance was due on 12/26/91 at 0530 for Unit 2 and at 0330 for Unit 3. The surveillance was completed for Unit 2 on 12/26/91 at 0900 (3-1/2 hours late) and completed for Unit 3 at 0900 (5-1/2 hours late). At that time, Units 2 and 3 were in Mode 1 at 98% and 100% power, respectively. Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> This event was caused by individual inattention to detail. The maintenance individual (utility, maintenance) responsible for completing the surveillance failed to complete the surveillance as scheduled (cognitive error). When it was noted on 12/26/91 that the surveillance was not performed, Maintenance personnel apparently misunderstood TS 4.0.3 requirements and did not realize that reporting was required and the event was not reported as delinquent. The delinquent surveillance, when performed, indicated that the batteries remained within their operating parameters and therefore were capable of performing their safety function. Therefore, there was no safety significance to this event.<br /><br /> On 2/3/92, Edison submitted LER 3-91-009 to report a missed 12/21/91 quarterly surveillance for two of the batteries. Due to the misunderstanding noted above, the delinquent weekly surveillance was not included in that LER. The corrective action for LER 3-91-009 (to proceduralize the TS surveillances performed by Maintenance) has been completed and will ensure timely completion of the weekly battery surveillances. Edison will also review this event with appropriate personnel to ensure proper understanding of TS 4.0.3.
3621991001 | San Onofre 3 | 03/15/1991 | 04/15/1991 | 9104220351 | <strong>Unit 3 Automatic Reactor Trip Due To Non-1e Uninterruptible Power System Failure</strong><br /><i>Abstract:&nbsp;</i>At 0938 on March 15, 1991, Unit 3 automatically tripped from 100% power on a reactor protection system loss of load (LOL) signal. The LOL signal was caused by a turbine trip, which occurred as the result of a momentary interruption in power from the non-1E uninterruptible power system (UPS), de-energizing bus 3Q069. Emergency Feedwater Actuation System (EFAS) 1 and EFAS 2 actuations properly occurred. One non-1E 4.16 kV (3A03) bus did not automatically transfer from its normal power source to its alternate power source, resulting in the loss of the alternate power supply (3B012) to the non-1E bus 3Q069. One main steam safety valve lifted for a short time and properly reseated. At 1000, when 3A03 was manually reenergized, power was restored to 3Q069. Appropriate actions were taken in accordance with procedures to compensate for the operation of control systems which were affected by the loss of power to the non-1E UPS. Post-trip plant recovery otherwise proceeded normally. <br /><br /> An output capacitor in the constant voltage transformer (CVT) section of the non-1E UPS inverter failed causing the momentary interruption in power from the non-1E UPS. <br /><br /> All capacitors in the Units 2 and 3 non-1E UPS were replaced with an upgraded model. The Unit 3 instrument busses powered by the non-1E UPS were modified such that power will be maintained to critical component systems (i.e., feedwater, turbine governor, and control element drive mechanism control systems) in the event of similar failures.
3621991002 | San Onofre 3 | 04/12/1991 | 05/13/1991 | 9105210153 | <strong>Inadvertent Opening Of A Containment Purge System Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, at 1959, an outer containment mini-purge isolation valve, 3HV-9821, was discovered open in violation of the requirements of Technical Specification (TS) 3.6.1.7.b, "Containment Ventilation System Limiting Condition for Operation." The valve was promptly closed by Control Room (CR) personnel. Subsequent investigation determined that 3HV-9821 had been inadvertently opened at approximately 2339 on April 11, 1991 by a Control Operator (CO) (utility, licensed) during reset of the actuation circuitry for 3HV-9821. The actuation circuitry had been armed earlier in the day during surveillance testing of 3RE-7865-1 which had begun at 1030 on April 8, 1991. <br /><br /> 3HV-9821 was opened and remained open as the result of a number of deficiencies in the areas of operator performance, surveillance procedures, plant status monitoring systems, and switch labeling. <br /><br /> Corrective actions include: 1) the operator received appropriate guidance concerning performance in the area of problem solving and plant manipulation; 2) the surveillance procedure will be revised prior to its next use to prevent a similar inadvertent valve opening during testing; 3) a review of the radiation monitor and containment purge valve logic circuitry is being performed; and 4) the plant status monitoring systems are being evaluated for possible enhancements. <br /><br /> There was no safety significance to this event since the inner containment isolation mini-purge valve remained closed at all times. Also, 3HV-9821 would have closed on receipt of an ESFAS signal or a high radiation signal from the containment purge vent stack radiation monitor.
3621991003 | San Onofre 3 | 09/02/1991 | 10/04/1991 | 9110100181 | <strong>Technical Specification Action Requirement Exceeded Due To Core Operating Limit Supervisory System Backup Computer Failure</strong><br /><i>Abstract:&nbsp;</i>At 1242 on 9/2/91, with Unit 3 at 100% power, the reactor Core Operating Limit Supervisory System (COLSS) function was re-aligned from the Plant Monitoring computer! System (PMS), which was removed from service, to the COLSS Backup Computer System (CBCS). On 9/2, an undetected CBCS failure corrupted certain COLSS sub-programs, thereby stopping execution of some reactor power and power distribution calculations which are used by control room operators to monitor reactor operation. Since the CBCS appeared to be operating normally and a computer failure alarm was not received, the failure was not detected. On 9/4, this condition was detected and CBCS was determined to be inoperable. During this period, CBCS was relied upon to satisfy Technical Specification (TS) requirements for approximately eight hours. <br /><br /> With COLSS in service, the TSs permit the plant to be operated with a less restrictive DNBR than would be required with COLSS unavailable. Since the CBCS failure was undetected, action was not taken to restore DNBR to that required when COLSS is unavailable within the time limits required by TS 3.2.4.c. Additionally, the requirements of TS 4.2.4.2 and 4.2.1.2 to verify that when COLSS is unavailable, DNBR and linear heat rate, respectively, are within limits at least every two hours were not performed. <br /><br /> The mode of computer failure experienced in this event was not previously postulated or experienced; consequently, barriers to identify and mitigate the failure were not in place. Corrective actions include CBCS computer repairs and incorporation of a diagnostic check into the CBCS COLSS program. The event was of no safety significance.
3621991004 | San Onofre 3 | 09/30/1991 | 10/29/1991 | 9111060166 | <strong>Delinquent Technical Specification Surveillances Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 0815 on 9/30/91, with Unit 3 in Mode 1 at 100% power, it was discovered that Technical Specification (TS) surveillances required to be performed at least once per 24-hours had exceeded their surveillance interval by 40 minutes. <br /><br /> At 2225 on 9/28/91, Surveillance Operating Instruction SO23-3-3.26, "Once A Day Surveillance (Modes 1 - 4)," was performed. The surveillance was subsequently performed at 0505 on 9/30/91. The interval between completed surveillances was 40 minutes greater than the TS surveillance interval plus the allowable extension permitted by TS 4.0.2. <br /><br /> The cause of this event was a cognitive error by control room personnel. At the beginning of their shift, the control room operator and the control room supervisor reviewed the list of surveillances required to be performed on their shift. Although SO23-3-3.26 was specified to be performed prior to 2400 hours, due to a lack of attention to detail, this time requirement was not identified by either the control room operator or the control room supervisor.<br /><br /> As corrective action, appropriate disciplinary action has been administered to the personnel involved in this event. In addition, this event has been reviewed by appropriate Operations personnel. <br /><br /> There was no safety significance to this event since the delinquent performance of SO23-3-3.26 demonstrated that applicable TS components met their associated TS requirements and therefore remained operable.
3621991005 | San Onofre 3 | 11/04/1991 | 12/04/1991 | 9112100316 | <strong>Delinquent Core Protection Calculator Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>At approximately 1940 on 11/4/91, with Unit 3 in Mode 1 at 100% power, it was discovered that the once per 12-hour Core Protection Calculator (CPC) auto-restart Technical Specification (TS) surveillance had exceeded the surveillance interval by 1 hour and 5 minutes. <br /><br /> Units 2/3 Operations department recently changed their shift schedule from 8-hour shifts to 12-hour shifts. As a consequence, the times at which various surveillances are performed were changed to accommodate the new shift schedule. In this case, the time that the once per 12-hour CPC auto-restart surveillance was to be performed was changed on 10/31/91, from 0000 and 1200 hours to 0800 and 2000 hours. When the surveillance instruction change delineating the revised schedule became effective, the computer generated TS surveillance schedule used by the operators to control TS surveillances was not promptly updated to reflect the schedule change. Additionally, the operators were not required to read the surveillance operating instruction change notice prior to assuming shift responsibilities. Consequently, on 11/4/91, a new oncoming day-shift crew (who had been off the previous 3 days) performed the surveillance in accordance with the out of date computer generated schedule, resulting in the surveillance interval being exceeded. <br /><br /> Corrective actions include enhancing administrative controls and reviewing this event with appropriate Operations personnel. <br /><br /> There was no safety significance associated with the delinquent surveillance since the CPC surveillance, when performed, demonstrated that the CPCs met their associated TS requirements and therefore remained operable.
3621991007 | San Onofre 3 | 11/07/1991 | 12/06/1991 | 9112100039 | <strong>Fuel Handling Isolation System (FHIS) Train "A" Spurious Actuation During Radiation Monitor Return To Service</strong><br /><i>Abstract:&nbsp;</i>At 2255 on 11/7/91, with Unit 3 at 100% reactor power, FHIS Train "A" spuriously actuated as radiation monitor 3RI-7822 was being returned to service following a filter change-out for the particulate/iodine channel. There was no indication of increased radiation levels in the Fuel Handling Building (FHB). At 2314, after the airborne activity levels in the FHB were confirmed to be normal, FHIS Train "A" was reset and the FHB ventilation system was returned to normal. <br /><br /> The cause of the FHIS Train "A" actuation was an intermittent failure internal to the normal/bypass switch associated with the FHIS circuitry. <br /><br /> The planned corrective actions include: 1) replacement of the FHIS normal/bypass handswitch; and 2) performance of a failure analysis on the replaced handswitch to determine the root cause of the failure. A supplement to this LER will be submitted to update the cause and corrective action if the root cause is determined to be other than an isolated failure.<br /><br /> There is no safety significance to this event since FHB airborne activity levels remained normal and all FHIS Train "A" components operated in accordance with design.
3621991008 | San Onofre 3 | 11/29/1991 | 12/23/1991 | 9201030307 | <strong>Missed Firewatch Due To Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1603 on 11/29/91) with Unit 3 in Mode 1 at 100% power, a firewatch supervisor (contractor, non-licensed) conducting an inspection discovered that the required hourly firewatch patrol for the two Unit 3 Emergency Diesel Generator (DG) DG, EK! (3G002 and 3G003) rooms had been missed between 1500 and 1600. The hourly firewatch patrol had been established as required by Technical Specifications 3.7.8.2, "Spray and/or Sprinkler Systems," and 3.3.3.7, "Fire Detection Instrumentation," for inoperable fire protection equipment KP!. <br /><br /> The cause of this event was cognitive personnel error by the firewatch (contractor, non-licensed) when he missed the DG rooms during his assigned patrol. <br /><br /> The firewatch involved in this event has received appropriate disciplinary action. This event has been reviewed by appropriate firewatch personnel. As additional corrective action, firewatch supervisors have increased their monitoring of roving firewatch personnel. <br /><br /> There was no safety significance associated with this event since: 1) three early warning smoke detectors located in each DG room were operable and would have alerted appropriate personnel of a fire, 2) manual fire fighting equipment was available in the DG rooms to extinguish a fire, and 3) a continuously manned fire station is maintained on-site to immediately respond to a fire. In addition, fire barriers between the two DG rooms ensure that no single fire would have resulted in a loss of redundant safe shutdown equipment.
3621991009 | San Onofre 3 | 12/21/1991 | 02/03/1992 | 9202100176 | <strong>Delinquent Technical Specification Quarterly Surveillance Class 1E 125 Volt DC Batteries Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 1/2/92 with Unit 3 at 100 power, during a review of maintenance orders that required scheduling, it was identified that the quarterly surveillance on the class 1E 125 volt DC (VDC) "C" and "D" batteries, as required by Technical Specification (TS) 3/4.8.2, "DC Sources," was delinquent. The surveillance had last been completed on 8/28/91 and was overdue on 12/21/91. There is no safety significance to this event since the delinquent battery surveillance was completed with satisfactory results on 1/2/91, indicating that the batteries had remained capable of performing their safety function.<br /><br /> Personnel involved with ensuring that TS surveillances are completed within specified time intervals failed to adequately perform their assigned tasks as intended by established maintenance practices due to personnel error, including: 1) the surveillance planner and scheduler failed to adequately review the weekly surveillance status report, which clearly identified the battery surveillance to be delinquent; and 2) the planner's supervision failed to adequately perform their oversight responsibilities. <br /><br /> Appropriate disciplinary action has been administered to the personnel involved with the delinquent surveillance. This event was reviewed with the surveillance planner, scheduler, their supervision, and other appropriate personnel and supervisors, emphasizing the importance of performing proper, weekly independent reviews of the surveillance status report as necessary to ensure the timely performance of TS surveillances. Established maintenance practices regarding the scheduling and review of TS surveillances performed by Maintenance are being formalized into procedures to provide greater assurance that surveillances are performed as required.
3641991001 | Farley 2 | 04/01/1991 | 04/23/1991 | 9104260217 | <strong>Dropped Control Rod Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 1055 on 4-1-91, while operating at approximately 100 percent power, a reactor trip occurred when rod H-10 dropped into the core. The reactor trip occurred due to a high negative flux rate as detected by the power range nuclear detectors. The operator was performing FNP-2-STP-5.0 (Full Length Control Rod Operability Test). When control rod group C was tested, rod H-10 dropped into the core. <br /><br /> This event was caused by defective circuit card(s) in the rod control system. The suspect cards were replaced and the unit returned to power operation at 1208 on 4-09-91.
3641991002 | Farley 2 | 04/09/1991 | 05/02/1991 | 9105070238 | <strong>Reactor Manually Tripped Following Loss of Steam Generator Feed Pump</strong><br /><i>Abstract:&nbsp;</i>At 2040 on 4-9-91, the Unit 2 reactor was manually tripped following the loss of the operating (2A) steam generator feedwater pump (SGFP). The loss of the SGFP was caused by a failed electro-hydraulic (EH) fluid supply line coupling and subsequent loss of EH fluid. The failure was in the heat affected zone of a tubing-to-fitting socket weld on the EH supply to the high pressure governor valve to the 2A SGFP. Examination of the failed tubing revealed that the failure resulted from cyclic fatigue. <br /><br /> The EH tubing was repaired and all accessible welds on the EH systems on Units 1 and 2 SGFPs were inspected. Vibration readings were taken on the EH tubing connections in the vicinity of the Unit 2 SGFP turbines. Vibration was found on the EH tubing in the vicinity of the failure. The highest vibration occurred during low power plant operation. An investigation is continuing to determine if additional corrective action is necessary. <br /><br /> The unit returned to power operation at 1648 on 4-10-91.
3641991003 | Farley 2 | 04/16/1991 | 05/13/1991 | 9105240166 | <strong>Both Trains Of Ctl Rm Emer Air Cleanup Sys Inoperable Due To Both Trains Of U1 SW Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1747 on 4-16-91, Technical Specification 3.0.3 was entered because both trains of the shared control room emergency air cleanup system were inoperable. Both trains were inoperable because the respective Unit 1 service water trains supplying the air conditioners were inoperable.<br /><br /> The control room air conditioning units can obtain service water from Unit 1 only, which was in a refueling outage. The Unit 1 "B" train service water system had been removed from service for maintenance and modifications. Personnel working on motor-operated valves mistakenly closed the valve supplying Unit 1 "A" train service water to the Auxiliary Building. With both trains of Unit 1 Auxiliary Building service water inoperable, both trains of the shared control room emergency air cleanup system were inoperable. <br /><br /> Upon investigation, control room personnel determined the cause and the Unit 1 "A" train service water valve was opened. The "A" train emergency air cleanup system was returned to service at 1824 on 4-16-91, at which time Technical Specification 3.0.3 was no longer in effect.
3641991004 | Farley 2 | 04/20/1991 | 05/13/1991 | 9105220289 | <strong>Reactor Trip Due to Turbine Trip Caused by Reduction of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>At 1617 on 4-20-91, the reactor tripped due to a turbine trip. The turbine trip was caused by a reduction of condenser vacuum. The valve which supplies instrument air to the air operated steam admission valve for the 2A steam jet air ejector (SJAE) was inadvertently closed by personnel working in the area. This caused the steam supply valve to close and resulted in the loss of condenser vacuum. <br /><br /> The turbine building system operator immediately restored air to the steam admission valve upon finding the air supply isolated. Vacuum recovered shortly after the trip occurred and no further problems were identified. The unit returned to power operation at 0426 on 4-21-91.
3641991005 | Farley 2 | 08/06/1991 | 08/30/1991 | 9109050135 | <strong>Reactor Trip Caused By Lightning Induced Transient In the Rod Control System</strong><br /><i>Abstract:&nbsp;</i>At 1704 on 8-6-91, while operating at approximately 100 percent power, a reactor trip occurred. Apparently, a lightning induced transient in the rod control system caused some of the control rods to drop which resulted in a negative flux rate reactor trip. <br /><br /> Testing and inspection of the rod control system revealed no damage. It is postulated that a lightning strike induced voltage on the control rod drive mechanism cables which momentarily de-energized the power supply to one or more rod control cabinets and caused the rods associated with that cabinet or cabinets to drop. <br /><br /> An engineering study has been initiated to determine how to prevent further lightning induced reactor trips. <br /><br /> The unit returned to power operation at 2049 on 8-7-91.
3661991001 | Hatch 2 | 01/29/1991 | 06/14/1991 | 9106240011 | <strong>Instrument Trip Setpoints Determined To Be Outside Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 1/29/91 at approximately 0915 CST, Unit 2 was in the Run mode at an approximate power level of 2436. At that time, it was determined the setpoints for Unit 2 Condensate Storage Tank (CST, EIIS Code KA) level switches 2E41-N002 and 2E41-N003 were not in compliance with the requirements of Unit 2 Technical Specifications (TS) Table 3.3.3-2, item 3.c. The switches, which cause High Pressure Coolant Injection (HPCI, EIIS Code BJ) system suction source transfer from the CST to the Suppression Pool (EIIS Code BT) on low CST water level, were not set to initiate the transfer when 10,000 useable gallons of water were available to the HPCI system as intended by the Unit 2 TS. At the time of event discovery, the HPCI system was aligned to take suction from the Suppression Pool and remained in this alignment until the CST water level switch setpoints could be raised.<br /><br /> The cause of this event was less-than-adequate design documentation. Although the level switch setpoints were designed such that 10,000 gallons of water remained in the CST at the time of the suction source transfer, design documents did not require 10,000 gallons of water to be available to the HPCI system. <br /><br /> Corrective actions include raising the CST level switch setpoints and initiating revisions to appropriate portions of the Unit 2 Technical Specifications and Final Safety Analysis Report. All setpoint changes covered under DCR 84-138 have been reviewed, and no unmodified setpoints were found to present any safety concerns.
3661991002 | Hatch 2, Hatch 1 | 01/30/1991 | 02/18/1991 | 9102220105 | <strong>Component Failure Causes Unplanned Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On 1/30/91 at approximately 0015 CST, Unit 2 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power) and Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, the "A" trains of both units' Standby Gas Treatment (SBGT) systems automatically started, both units' Refueling Floor and Reactor Building ventilation systems (secondary containments) isolated, and the Unit 2 Hydrogen and Oxygen Analyzer and Fission Products Monitoring systems isolated. Additionally, a Group 2 Primary Containment Isolation System (PCIS) isolation signal to some of the Unit 2 inboard, Group 2 Primary Containment Isolation Valves (PCIVs) was generated. All systems functioned per design and unit operation was unaffected.<br /><br /> The cause of this event was component failure. The coil in relay 2C61-K50A failed causing a current surge which blew fuse 2C61-F19. This fuse is in the power supply to the initiation/isolation logic for the above systems. When the fuse failed, these logic systems lost power and their associated systems initiated/isolated per design. <br /><br /> Corrective actions for this event included replacing the failed relay and the blown fuse.
3661991003 | Hatch 2, Hatch 1 | 02/13/1991 | 03/08/1991 | 9103140368 | <strong>Component Failure Results In ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2/13/91 at approximately 1635 CST, Unit 1 was in Cold Shutdown and Unit 2 was in the Run mode at an approximate power level of 2397 CMWT (approximately 98% rated thermal power). At that time, the Main Control Room Environmental Control (MCREC, EIIS Code VI) system automatically transferred from the normal mode to the pressurization mode. This occurred as designed when refueling floor Area Radiation Monitors (ARM, EIIS Code IL) 2D21-K601A and 2D21-K601M tripped on a high radiation signal. After the actuation occurred, licensed Operations personnel verified proper operation of the MCREC system and that an actual high radiation condition did not exist on the refueling floor. An investigation later determined that the signal was the result of an upscale spike caused by loss of power to these ARMs. It was determined that a fuse internal to their power supply had failed. ARMs 2D21-K601A and M provide an input to the MCREC pressurization mode logic. The failed fuse was replaced and the MCREC system was returned to its normal mode of operation at approximately 2025 CST on 2/13/91. <br /><br /> The cause of the event is component failure. A fuse internal to the ARM power supply failed. The fuse failure was investigated and appears to be a random failure. <br /><br /> Corrective actions for this event included replacing the blown fuse and returning the MCREC system to its normal mode of operation.
3661991004 | Hatch 2 | 02/14/1991 | 03/15/1991 | 9103200205 | <strong>Component Failure In Generator Exciter Causes Turbine Trip And Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 2/14/91, at approximately 1854 CST, Unit 2 was in the Run mode at an approximate power level of 2388 CMWT (approximately 97.5% rated thermal power). At that time, a voltage regulator card in the exciter system for the main generator failed, resulting in main generator and main turbine trips. The unit scrammed on turbine stop valve closure. Reactor water level decreased to approximately 2 inches below instrument zero and was restored to normal by the Reactor Feedwater Pumps and the Reactor Core Isolation Cooling system. Reactor vessel steam dome pressure briefly peaked at approximately 1116 psig and the Bypass valves successfully controlled pressure. No Safety Relief Valves opened. The pressure experienced in the main steam lines was transitory and apparently less than reactor vessel steam dome pressure. However, using steam dome pressure, the SRVs were possibly not in compliance with their +/-1% Technical Specifications tolerance requirement. The valves were removed and tested in accordance with code requirements. The actual drift experienced was within the bounds of a previous analysis demonstrating adequate overpressure protection. <br /><br /> The root cause of the scram was component failure. The cause of the SRV setpoint drift was corrosion-induced bonding of the surface between the pilot valve disc and seat.<br /><br /> Corrective actions for this event included replacing the failed component in the generator exciter system and removing and refurbishing the SRVs. Georgia Power Company (GPC) will continue to participate in the BWR Owners' Group action plan to resolve setpoint drift.
3661991005 | Hatch 2 | 02/24/1991 | 03/15/1991 | 9103200157 | <strong>Personnel Error Results In Reactor Scram On APRM High Flux</strong><br /><i>Abstract:&nbsp;</i>On 2/24/91 at approximately 2013 CST, Unit 2 was in the Startup mode with the reactor critical at less than 1% rated thermal power. Reactor pressure was approximately 280 psig, and reactor coolant temperature was approximately 416 degrees F. A nuclear heatup to rated pressure and temperature (approximately 1000 psig and 545 degrees F, respectively) was in progress per procedure 34GO-OPS-001-2S, "Plant Startup." At that time, the reactor scrammed on Average Power Range Monitor (APRM, EIIS Code IG) high flux. Neutron flux increased to the scram setpoint of about 12% rated thermal power when feedwater was rapidly injected into the reactor vessel in response to decreasing reactor water level. Water level had begun to decrease when a Bypass Valve (BPV, EIIS Code SO) opened to control reactor pressure. The BPV opened during heatup, because licensed Operations personnel failed to maintain the BPV's pressure control setpoint above reactor pressure as required by procedure 34GO-OPS-001-2S. <br /><br /> The cause of this event was personnel error. Licensed Operations personnel failed to maintain the BPV's pressure control setpoint above reactor pressure as required by procedure, As a result, the BPV opened at its pressure setpoint of approximately 280 psig, allowing reactor vessel water inventory in the form of saturated steam to flow to the Condenser (EIIS Code SQ) and thereby causing reactor water level to decrease. Operations personnel failed to recognize the BPV was open. To control water level with the BPV open, feedwater was injected into the vessel, resulting in a power increase and scram on APRM high flux. <br /><br /> Corrective action for this event consisted of counseling the involved personnel.
3661991006 | Hatch 2, Hatch 1 | 03/17/1991 | 04/16/1991 | 9104180246 | <strong>Trip Of Area Radiation Monitor Causes Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 3/17/91 at approximately 1610 CST, Unit 1 was in the Run mode at 2436 CMWT; Unit 2 was also in Run, coasting down at 2276 CMWT (approximately 100-percent rated thermal power and 93-percent rated thermal power, respectively). Pre-outage activities were in progress on the Refueling Floor. At that time, the Main Control Room Environmental Control System automatically transferred from its normal mode of operation to the pressurization mode. This occurred as designed when Area Radiation Monitor 2D21-K601M, located near the Spent Fuel Shipping Cask Storage Pit, tripped when an underwater vacuum cleaner head was moved near it. The vacuum cleaner head was reading approximately 700 mR/hour on contact. The cleaner head was placed under the water in the Cask Storage Pit and the ARM reading returned to normal. No personnel received an unexpectedly high dose during the event, nor did anyone become contaminated. The Main Control Room Environmental Control System was returned to normal operation. <br /><br /> The cause of this event was personnel error by the involved personnel on the Refueling Floor. They failed to notify personnel in the Main Control Room of the anticipated actuation of an Engineered Safety Feature (ESF). Thus it could not be properly documented, prior to the actual ESF actuation, as part of a planned operational sequence of events. <br /><br /> Corrective actions include planned issuance of a departmental directive emphasizing the need to notify the Main Control Room to assure proper documentation of an anticipated ESF actuation.
3661991007 | Hatch 2 | 03/26/1991 | 04/25/1991 | 9104250220 | <strong>Unknown Inadequacy In Jumper Connection Results In Scram Signal During Surveillance In Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 3/26/91, at approximately 1155 CST, Unit 2 was in Cold Shutdown with reactor coolant temperature at approximately 100 degrees Fahrenheit, reactor pressure at atmospheric, and all control rods fully inserted. At that time, licensed plant operators observed indications that a full scram signal had been received. In accordance with Technical Specifications requirements prior to entering Refuel mode, surveillance procedure 34SV-C51-001-2S was being performed to test the Neutron Monitoring System (NMS, EIIS Code IG) noncoincident scram logic. This required the placement of electrical jumpers in the Reactor Protection System (RPS, EIIS Code JE) logic to ensure a full scram was not generated while testing NMS trip functions. In this event, it appears that at least one jumper failed to maintain contact resulting in a full scram signal when NMS signals were induced per the surveillance procedure. <br /><br /> The cause of this event could not be conclusively determined. However, it appears to be an isolated event resulting from an unknown inadequacy in a jumper connection. <br /><br /> Corrective actions for this event include completing the functional test which verified operability of the NMS noncoincident scram logic and revising the surveillance procedure to reduce the probability of recurrence.
3661991008 | Hatch 2 | 03/27/1991 | 04/24/1991 | 9104290165 | <strong>Main Steam Isolation Valve Local Leak Rate Test Failures</strong><br /><i>Abstract:&nbsp;</i>On 3/27/91, at approximately 1200 CST, Unit 2 was in the Refuel mode with the reactor vessel flooded. Fuel removal was in progress with fuel partially removed from the core. At that time, Local Leak Rate Testing (LLRT) of Main Steam Line Isolation valves (MSIVs, EIIS Code SB) 2B21-F022B and 2B21-F028B was completed, confirming that one pair of MSIV's in the same main steam line (MSL) leaked in excess of the Technical Specifications leakage limit. The other 6 MSIVs passed their LLRT, meeting the Technical Specifications requirement. The leakage of 92 SCFH through the one MSL was well within the capacity of the MSIV Leakage Control System to handle in the unlikely event of a Loss-of-Coolant Accident with the as-found MSIV leakage rates. <br /><br /> The root cause of this event is attributed to normal equipment wear resulting in slight degradation of the valve seating surfaces. <br /><br /> Corrective actions for this event include repairing and re-testing the valves.
3661991009 | Hatch 2 | 04/10/1991 | 05/08/1991 | 9105140134 | <strong>Safety Relief Valves Experience Setpoint Drift Due To Corrosion Induced Bonding</strong><br /><i>Abstract:&nbsp;</i>On 4/10/91, at approximately 0800 CDT, Unit 2 was in the Refuel mode with all fuel having been removed from the vessel. At that time plant engineering personnel received written notification of the results of off-site testing of pressure vessel safety relief valves (SRVs, EIIS Code RV). Three of the eleven SRVs exhibited drift in the mechanical lift setpoints in excess of the +/-3% tolerance specified by in-service testing (IST) requirements. Four SRVs experienced setpoint drift greater than the +/-1% Unit 2 Technical Specifications tolerance requirement in section 3.4.2.1. This voluntary report is being submitted due to the potential industry interest in this event in view of the ongoing efforts of the Boiling Water Reactor Owners' Group (BWROG) to reduce setpoint drift. The setpoint drift experienced was well within the analytical limits existing for reactor vessel over-pressure protection. <br /><br /> The root cause of the SRV drift in excess of +/-3% is corrosion-induced bonding of the surface between the pilot valve disc and seat. One additional SRV experienced negative drift in excess of -1%. <br /><br /> Corrective actions for this event include refurbishing the valves and continuing to participate in the BWROG efforts to resolve the SRV setpoint drift issue. The BWROG program direction has been concurred with by the NRC.
3661991010 | Hatch 2, Hatch 1 | 04/16/1991 | 05/13/1991 | 9105240163 | <strong>Blown Fuse Results In Engineered Safety Features Actuation</strong><br /><i>Abstract:&nbsp;</i>On 4/16/91, at approximately 2140 CDT, Unit 2 was in a refueling outage with the reactor vessel flooded, and all fuel removed from the vessel. At that time, Instrument and Control (I&C) technicians were performing surveillance procedure 57SV-D11-008-2S, "REACTOR BUI DING EXHAUST VENT RADIATION MONITOR CHANNEL FUNCTIONAL TEST." This procedure requires the installation of a jumper in Control Room panel 2H11-P606A. As the technician was installing the jumper, he inadvertently brought one end of the jumper into contact with a grounded steel enclosure inside the panel. This resulted in a current surge which blew fuse 2C61-F20. This fuse supplies logic power to the Primary Containment Isolation System (PCIS, EIIS Code JM) which provides initiation signals to the "B" trains of the Unit 1 and Unit 2 Standby Gas Treatment Systems (SGTS, EIIS Code BH), isolation signals to both units' Secondary Containment dampers (EIIS Code JM) and to various PCIS valves. All systems responded as designed.<br /><br /> The root causes of this event were personnel error coupled with poor working conditions in the Control Room panel. The technician did not take sufficient steps to assure success, and the equipment involved added to the difficulty of the task. <br /><br /> Corrective actions for this event will include discussing the event in I&C Tool Box meetings which will stress the need for adequately preparing work areas and re-evaluating the task for potential changes in the kind of jumpers that are used in this surveillance application.
3661991011 | Hatch 2, Hatch 1 | 04/20/1991 | 05/15/1991 | 9105220183 | <strong>Component Failure Results In Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 4/20/91, at approximately 1442 CDT, Unit 2 was undergoing a refueling outage with all fuel unloaded from the vessel and Unit 1 was in the Run mode maintaining 100% rated thermal power. At that time, the Main Control Room Environmental Control (MCREC, EIIS Code VI) system automatically transferred to the Pressurization mode. It was determined that the transfer was caused by a fuse blowing in the "A" channel of a Pressurization mode initiation circuit. The system transferred to the Pressurization mode and operated per design. A four-hour notification was made per 10 CFR 50.72(b)(2)(ii) at approximately 1603 CDT. The fuse was subsequently replaced and the MCREC system was returned to its normal mode of operation by approximately 2116 CDT. <br /><br /> The cause of the event was component failure in that fuse 2A71-F07A opened in the absence of a short-circuit condition. It is noted that electricians were performing corrective maintenance on the initiation circuit at the time of the event. However, based on an inspection of the circuit panels, interviews with the electricians, and testing on a mock-up of the initiation circuit, it was concluded that the electricians' work activity did not result in the fuse opening. <br /><br /> Corrective actions for this event included replacing the fuse and returning the MCREC system to its normal mode of operation.
3661991012 | Hatch 2 | 04/22/1991 | 05/21/1991 | 9105290087 | <strong>Less Than Adequate Procedure Results In ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On 4/22/91 at 1645 CDT, Unit 2 was in a refueling outage with the core completely unloaded and the reactor vessel flooded. At that time, a false Loss of Coolant Accident (LOCA) signal on low reactor water level was received. Diesel Generators 2R43-S001A, 2R43-S001C, and 1R43-S001B automatically started, the Main Control Room Environmental Control System automatically transferred from the normal mode to the pressurization mode, Turbine Building Plant Service Water isolation valves 2P41-F316A through D automatically closed, and Core Spray system injection valve 2E21-F005A and Residual Heat Removal (RHR) system injection valves 2E11-F015A and 2E11-F017A automatically opened. The Core Spray system and RHR system pumps did not start because they had been removed from service per approved plant procedures as part of refueling outage activities. Similarly, Core Spray system injection valve 2E21-F005B and RHR ystem injection valves 2E11-F015B and 2E11-F017B did not open because they had been removed from service. The LOCA signal was generated when new Analog Transmitter Trip System (ATTS) trip cards were installed in Main Control Room ATTS panels. Due to incorrect positioning of switches on the ATTS cards, a trip signal was generated when the cards should have been in an untripped condition. <br /><br /> The cause of this event is a less than adequate procedure. The procedure used to set the switches on the new trip cards was incorrect. The procedure's writer and sponsor failed to ensure the procedure provided correct guidance to properly set up the subject cards. <br /><br /> Corrective actions include counseling involved personnel, revising the procedure, and changing the trip card configuration.
3661991013 | Hatch 2 | 05/06/1991 | 06/03/1991 | 9106070102 | <strong>Spurious Electrical Spiking In Neutron Monitoring System Results In Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 5/6/91, at 0333 CDT, Unit 2 was in a refueling outage with the vessel flooded and the core partially reloaded with fuel. At that time, a spurious electrical spike in the Neutron Monitoring System (NMS, EIIS Code IG) resulted in an actuation of the Reactor Protection System (RPS, EIIS Code JE). All control rods were fully inserted into the core at the time the signal was received. Therefore, no control rod motion occurred as a result of the signal, No other nuclear instrumentation showed unusual activity. Therefore, the affected instrument was bypassed and the scram was reset by licensed plant operations personnel. No other automatic actuations resulted from this event. <br /><br /> The cause of the event was spurious electrical spiking of a neutron monitoring instrument. Given the plant configuration at the time of the event, any NMS trip signal would have caused, per design, an actuation of the RPS. The cause of the spurious electrical spiking could not be determined. No testing on this instrument was in progress. <br /><br /> Corrective actions for this event included bypassing the affected neutron monitoring instrument, resetting the scram, and returning the affected instrument to service after its erratic operation had subsided.
3661991014 | Hatch 2, Hatch 1 | 05/08/1991 | 06/05/1991 | 9106100335 | <strong>Less Than Adequate Storage Rack Design Evaluation Results In Technical Specifications Non-Compliance</strong><br /><i>Abstract:&nbsp;</i>On 5/8/91 at 0930 CDT, Unit 2 was in the Refueling mode with the core completely loaded when a discrepancy between Unit 2 Technical Specification (TS) 3.9.10 and the design of the High Density Fuel Storage System (HDFSS) (EIIS Code DB) racks in the Unit 2 Spent Fuel Pool was identified. TS 3.9.10 requires at least 23 ft of water be maintained over the top of irradiated fuel assemblies seated in the storage racks. However, rack design is such that 23 ft of water can be maintained only above the top of the active fuel region of assemblies seated in the racks. The top of each fuel assembly, i.e., top of the upper tie plate, is approximately 12.125 in. above the top of the active fuel (TAF). <br /><br /> GE was contacted to assess the safety significance of the discrepancy and provide a basis for the 23-ft requirement. GE indicated the discrepancy was not a safety concern, but was unable to document the 23-ft depth was intended to be measured with respect to TAF. Plant Hatch Corporate Support personnel analyzed the impact of this discrepancy and concluded that a safety concern did not exist. <br /><br /> The cause of this event is a less-than-adequate design change safety evaluation (SE) in that the SE for the HDFSS design change developed in the early 1980s did not address compliance with TS 3.9.10. On 5/20/91, LCO 2-91-424 was initiated to ensure compliance with Action Statement 3.9.10 until the TS are revised. That is, all movement of fuel assemblies and crane operations have been suspended. Proposed changes to TS 3.9.10, as well as Unit 1 TS 3.10.D, and the associated Bases will be submitted to the NRC.
3661991015 | Hatch 2 | 05/26/1991 | 06/24/1991 | 9107020146 | <strong>Component Failure Results In An Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 5/26/91 at 0742 CDT, Unit 2 was in the Cold Shutdown mode with preparations in progress for startup following a refueling outage. At that time, a full Group 1 Primary Containment Isolation System (PCIS, EIIS Code JM) isolation signal was received when the four Main Turbine Stop Valves unexpectedly opened when the control input logic board for Stop Valve no. 2 was pulled during set-up and check-out of the Electrohydraulic Control System (EHC, EIIS Code TG). The Stop Valves in the open position, in conjunction with low condenser vacuum, result in a Group 1 PCIS isolation signal. Because the unit was in a refueling outage, there was no vacuum in the condenser; therefore, when the Stop Valves opened, the logic for a Group 1 isolation was satisfied and a full Group 1 isolation signal was received. The PCIS functioned as designed. Group 1 Primary Containment Isolation Valve (PCIV) 2B31-F020, Reactor Water Sample Line Isolation Valve, closed. Other Group 1 PCIVs were already closed. <br /><br /> The cause of this event was component failure. The servo valve for Turbine Stop Valve no. 2 failed in such a manner as to cause the Stop Valve to open. Per design, the other three Turbine Stop Valves opened when Turbine Stop Valve no. 2 opened. <br /><br /> Corrective actions for this event included replacing the failed servo valve and verifying the servo valves for the Main Turbine Control Valves were functioning properly.
3661991016 | Hatch 2 | 05/30/1991 | 06/28/1991 | 9107030199 | <strong>Personnel Error Results In Missed Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 5/30/91 at 0800 CDT, Unit 2 was in the Cold Shutdown condition with reactor coolant temperature at 170 degrees Fahrenheit and reactor pressure at atmospheric. At that time, a plant engineer reviewing Primary Containment (PC, EIIS Code NH) isolation response time testing data discovered that not all the data had been collected as required by Unit 2 Technical Specification (TS) 4.3.2.3. Specifically, response time data were omitted for the PC isolation function initiated from a high PC pressure signal. This signal results in closure of the vacuum breaker isolation valves in the High Pressure Coolant Injection (HPCI, EIIS Code BJ) system and the Reactor Core Isolation Cooling (RCIC, EIIS Code BN) system. The data should have been collected during the 1989 and 1991 refueling outages but was missed due to a procedural error. All instruments and logic that were required to be tested were successfully surveilled prior to unit startup. Therefore, only one surveillance was performed after the required time interval had expired. This surveillance pertained to pressure sensor 2E11-N094D which should have been tested in the 1989 refueling outage. <br /><br /> The root cause of this event is personnel error. The procedure writers neglected to account for differences in the number of logic channels which could affect the testing frequency. The technical reviewers did not identify the oversight; therefore, the error was not corrected. <br /><br /> The corrective action for this event included performing the missed surveillance and revising the affected procedures.
3661991017 | Hatch 2 | 05/30/1991 | 06/28/1991 | 9107030207 | <strong>Fuse Failure Results In Primary Containment Isolation Valve Failing To Automatically Close</strong><br /><i>Abstract:&nbsp;</i>On 5/30/91 at approximately 2330 CDT, Unit 2 was in the Cold Shutdown condition with preparations in progress for unit startup following a refueling outage. At that time, Primary Containment Isolation System (PCIS, EIIS Code JM) valve 2B31-F019 failed to close upon receipt of a Group I PCIS signal which was an expected result of testing of the Main Turbine Stop Valves (TSVs, EIIS Code TA). The PCIS valve redundant to 2B31-F019 closed automatically as designed. All other Group I PCIS valves were already closed at the time of this event. Investigations revealed a blown fuse prevented 2B31-F019 from closing. The fuse was replaced at approximately 0120 CDT on 5/31/91, at which time the valve automatically closed. <br /><br /> The cause of this event was a blown fuse. Specifically, blown fuse 2C71-F10F, associated with a PCIS logic circuit input, prevented an isolation signal from being transmitted to the valve's control circuit. The cause of the blown fuse is unknown. <br /><br /> Corrective actions for this event included replacing the fuse and verifying operability of the associated isolation logic circuit.
3661991018 | Hatch 2 | 06/04/1991 | 07/03/1991 | 9107110154 | <strong>Error In The FSAR Results In Missed Technical Specifications Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 6/4/91 at approximately 1330 CDT, Unit 2 was in the Run mode at a power level of 1218 CMWT (50% rated thermal power). At that time, it was determined a local leak rate test of Primary Containment Penetration X-228B had not been performed as required by Unit 2 Technical Specifications section 4.6.1.2.d. Limiting Condition for Operation (LCO) 2-91-468 was initiated at 1330 CDT per the requirements of Unit 2 Technical Specifications section 3.6.1.1. A local leak rate test of Penetration X-228B was performed satisfactorily on 6/4/91. LCO 2-91-468 was terminated at 1745 CDT following successful performance of the test. On 6/10/91 at approximately 0930 CDT, during a followup investigation of the above event, it was determined Penetration X-228B had not been verified to be closed at least once every 31 days as required by Unit 2 Technical Specifications section 4.6.1.1. Since the penetration had been verified to be closed on 6/4/91 when the leak rate test had been performed, the required surveillance was current and an LCO did not have to be entered. <br /><br /> The cause of these events is an error in the Unit 2 Final Safety Analysis Report (FSAR). The Unit 2 FSAR incorrectly identified Penetration X-228B as not requiring a local leak rate test. This error also led personnel to believe the requirements of Unit 2 Technical Specifications section 4.6.1.1 did not apply. <br /><br /> Corrective actions include performing a local leak rate test of the penetration, revising applicable surveillance procedures to include checks of the penetration, correcting the Unit 2 FSAR, and reviewing Unit 1 and Unit 2 penetrations.
3661991019 | Hatch 2 | 09/12/1991 | 10/09/1991 | 9110180023 | <strong>Inadequate Design Results In Failure Of PCIV's To Close</strong><br /><i>Abstract:&nbsp;</i>On 9/6/91 at 1640 CDT, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, Primary Containment Isolation Valves 2G11-F004 and F019 failed to close during routine quarterly stroke time testing because their solenoid operated valves failed to operate. On 9/12/91 at 1500 CDT, with Unit 2 still operating at 2436 CMWT, personnel were inspecting the solenoid operated valves from 2G11-F003, F004, F019, and F020 when it was discovered that some of the failed valves' internals were coated with an oily, sticky substance. The substance was found on the disc, the solenoid core, the insert containing the internal valve orifices, and the bottom of the valve body. Additional investigation revealed their ethylene propylene discs had swollen, apparently from exposure to a petroleum based oil. The swelling of the discs, in conjunction with the sticky oil, caused the disc to stick to the valve body, This resulted in 2G11-F004 and F019 failing to close during testing. <br /><br /> The cause of this event is an inadequate design. A lubricator is installed upstream of the solenoid operated valves and inputs a petroleum based oil into the air supply. Therefore, the solenoid operated valves are exposed to air containing oil. However, these valves are designed to be used with oil-free air, because oil degrades ethylene propylene materials. <br /><br /> Corrective actions for this event include replacing the four solenoid operated valves, increasing the cycling of the affected valves, and changing the existing design and/or solenoid valves.
3661991020 | Hatch 2, Hatch 1 | 11/05/1991 | 12/02/1991 | 9112100049 | <strong>Spurious Breaker Trip Results In Engineered Safety Features Actuation</strong><br /><i>Abstract:&nbsp;</i>On 11/05/91 at 0350 CST, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, protective breaker 2C71-52-3D on the output of the 'B' motor-generator set in the Reactor Protection System (RPS, EIIS Code JE) power supply tripped. This caused a loss of power to the 'B' channels of the RPS, Process Radiation Monitors (EIIS Code IL), Neutron Monitoring System (NMS, EIIS Code IG), Primary Containment Isolation System (PCIS, EIIS Code JM), and Offgas Radiation Monitoring System (EIIS Code IL). The "fail-safe" design of these systems results in their assuming the 'tripped' state when power is interrupted. Therefore, these trips also resulted in closure of various PCIS valves and in the Main Control Room Environmental Control System (MCREC, EIIS Code VI) entering the pressurization mode. Licensed shift personnel restored power to RPS bus 'B' via its alternate supply by 0355 CST per procedure 34AB-OPS-066-2S, "LOSS OF RPS BUS," and all affected equipment was subsequently restored to its normal configuration. RPS bus 'B' was restored to its normal power supply by 1148 CST. <br /><br /> The cause of this event was a spurious trip of RPS protective circuit breaker 2C71-52-3D. Investigation indicated that no system condition existed which would have resulted in a valid trip. <br /><br /> Corrective actions for this event included adjusting the RPS output voltage as a precaution. This action is complete. In addition, a design review of the breaker application will be performed by 02/28/92.
3661991021 | Hatch 2 | 11/05/1991 | 12/04/1991 | 9112100273 | <strong>Personnel Error Results In Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On 11/5/91, at 2230 CST, Unit 2 was in the Run mode at 2436 CMWT (approximately 100 percent of rated thermal power). At that time, the Unit 2 licensed Shift Supervisor determined that the plant had not been in compliance with Action a. of Unit 2 Technical Specifications Section 3.3.6.4. Specifically, Post-Accident Monitoring System recorder 2T48-R608 had been inoperable for greater than 30 days. Since the condition was not identified, the required Technical Specifications action was not taken. Recorder 2T48-R608 provides post-accident monitoring capability of the Drywell and Suppression Pool pressures. The Shift Supervisor initiated a deficiency card to ensure that the event was properly investigated. By then the recorder had already been returned to service; therefore, no Limiting Conditions for Operation were entered.<br /><br /> The cause of the event was cognitive personnel error on the part of Control Room personnel. It was concluded from an investigation that the recorder was most likely turned off on 9/26/91 in order to replace one of the recorder pens and was inadvertently not turned back on. Subsequently, operators noted that the chart paper was not advancing but they believed the pens were tracking properly. The operators considered the recorder operable and initiated a deficiency card on the chart paper not advancing. The problem was not investigated and, thus, the recorder not found switched off until 11/5/91. <br /><br /> Corrective actions include requiring that recorders addressed in the Technical Specifications be considered inoperable when experiencing chart advancing problems and issuing a directive to licensed operators emphasizing the importance of performing adequate recorder checks.
3681991001 | Arkansas 2 | 01/14/1991 | 02/13/1991 | 9102220164 | <strong>Degraded Plant Fire Barriers Which Were Not Properly Identified During Routine Inspections Due To Inadequate Communications Between Different Plant Departments</strong><br /><i>Abstract:&nbsp;</i>In January 1991, while performing additional inspections of plant fire barriers following the recent completion of a routine eighteen month surveillance of the barriers, fire protection personnel discovered several deficiencies which had not been identified during performance of the surveillance activity. Based on evaluations of the deficiencies, it was determined that three fire barriers separating safety related areas were inoperable. Upon discovery of the conditions roving fire watches were established in the affected areas. The root cause of the failure to identify the deficiencies during the surveillance activity was attributed to inadequate communication between Fire Protection personnel and electrical maintenance during a prejob briefing conducted prior to performing the surveillance. Appropriate actions have been initiated to improve the procedures used for inspections and to provide additional training of inspection personnel. Based on the availability of fire detection and fire suppression systems for the affected plant areas and fire brigade personnel, there was no safety significance to these conditions.
3681991002 | Arkansas 2 | 01/18/1991 | 02/19/1991 | 9102250232 | <strong>Design Deficiency Results In Potential For Failure Of Emergency Diesel Generators Due To Inoperability Of Room Exhaust Fans</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1991, while performing inspections of vital, 480 volt AC, Motor Control Center breakers, the control power transformers (CPTs) in the breakers for the emergency diesel generator (EDG) rooms exhaust fans were found to be undersized. Evaluation of the design deficiency concluded that proper operation of the exhaust fans could not be assured under certain conditions of degraded offsite power voltage. Since the exhaust fans are needed to ensure proper operation of the EDGs, both ANO-2 EDGs were declared to be inoperable. Operating handswitches in the Control Room for one exhaust fan in each EDG room were placed in the 'off' position to prevent automatic starting of the fans. It was determined that the fans could be started manually if required and would not be susceptible to failure if the EDGs were supplying power to the vital electrical busses. Based on this action, both EDGs were declared operable. The undersized CPTs were replaced. The cause of this event appears to be the failure to identify the incorrect CPT size during previous design reviews due to an incorrect vendor drawing for the equipment. A plant electrical design drawing has been revised to indicate the correct CPT size for each applicable breaker.
3681991003 | Arkansas 2 | 01/18/1991 | 02/19/1991 | 9102250229 | <strong>Procedural Inadequacy Results In A Failure To Adhere To The Reduced Power Requirements Of Technical Specifications During Recovery From A Dropped Control Element Assembly</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1991 at 1415, while performing Control Element Assembly (CEA) current traces, Group 6 CEA 46 dropped to its fully inserted position. Operations personnel reduced power to 97.5 percent in accordance with the "CEA Misalignment" procedure (AOP 2203.03). At 1429, after determining that the cause of the dropped rod had been the inadvertent opening of its circuit breaker, the operators commenced withdrawing CEA 46 to realign it with the rest of the Group 6 CEAs. Reactor power was held constant (97.5 percent) during the recovery effort, as directed by AOP 2203.03. At 1443, CEA 46 reached realignment with Group 6. A subsequent evaluation determined that the time dependent reduced power requirements of Technical Specifications (TS) regarding dropped CEAs was not adhered to during the recovery. TS required that during the period of recovery, power should have been reduced by 5.8 percent. The root cause of this event was determined to be inadequate procedural guidance. AOP 2203.03 was ambiguous with respect to reduced power requirements. This event was discussed with the operations crews. A procedure change was implemented to remove the ambiguities regarding reduced power requirements.
3681991004 | Arkansas 2, Arkansas 1 | 01/25/1991 | 02/27/1991 | 9103050474 | <strong>Failure To Maintain Control Ventilation System Radiation Monitor Alarm/Trip Setpoint Value Within Technical Specifications Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1991 it was discovered that the Unit 2 control room radiation monitor had an alarm/trip setpoint greater than two times background and the control room emergency ventilation system had not been placed in the recirculation mode as required by Technical Specifications. On January 25, 1991 the average background was determined to be 83 counts per minute (CPM) and the alarm/trip setpoint at that time was set to 200 CPM. A job request was initiated to have the setpoint adjusted. It was not recognized until January 28, 1991 that Technical Specification 3.3.3.1 required the setpoint be adjusted within 4 hours. The control room ventilation system was placed in the recirculation mode, and subsequently, the setpoint was adjusted to 150 CPM. The event had no adverse impact on control room habitability; the capability of the monitor to perform its intended function was maintained. The root cause of this event was personnel error. The Operations Manager has issued a night order to remind operations personnel of the requirements of Technical Specification 3.3.3.1, and this event will be discussed during the training cycle following the 2R8 refueling outage.
3681991005 | Arkansas 2 | 02/01/1991 | 03/04/1991 | 9103080324 | <strong>Inadvertent Actuation Of Protective Relay Due To Vibration Results In Trip Of Reactor Coolant Pump Motor Breaker And Subsequent Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1991 at 1722 hours, while operating at 88 percent power an automatic reactor trip was initiated by the Core Protection Calculators (CPCs) due to a loss of power to reactor coolant pump 2P-32B. The emergency feedwater system actuated automatically due to post trip steam generator water level response (shrink) and was used to restore water levels to normal. Other plant system responded as designed to the transient and no significant malfunctions of equipment occurred. Investigations revealed that the RCP motor power supply feeder breaker had tripped due to inadvertent actuation of a motor phase differential relay for the breaker. The relay is mounted in a hinged door on the front of the breaker cubicle and was actuated due to vibration of the door. A faulty racking motor being used to rack up a breaker adjacent to the RCP breaker caused the excessive vibration. The faulty racking motor was removed from service. An engineering evaluation is being conducted to determine the feasibility of using a different type of protective relay to enhance the system design. The CPCs functioned properly to initiate an automatic reactor trip upon loss of an operating RCP. There was no actual safety significance to this event.
3681991006 | Arkansas 2 | 02/22/1991 | 03/22/1991 | 9103270237 | <strong>Core Protection Calculator Reactor Coolant System Flow Channels Not Calibrated As Required By Technical Specifications Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1991, at approximately 0940, it was determined by Operations personnel that a violation of the ANO-2 Technical Specifications had occurred in that a calibration of the Core Protection Calculators (CPCs) had not been performed, as required, when CPC indicated Reactor Coolant System (RCS) flow was observed to be greater than Core Operating Limit Supervisory System (COLSS) indicated RCS flow. Operations personnel record the indicated RCS flow of each CPC channel and the calculated COLSS RCS flow every 8 hours and compare the two readings to ensure that CPC RCS flow is less than COLSS indicated flow. It was determined that CPC indicated flow had been slightly greater than COLSS calculated RCS flow for 4 consecutive 8 hour checks. The CPCs were declared inoperable and Technical Specification (TS) 3.0.3 was entered at 0940. New flow coefficient constants were calculated and entered into the CPCs, lowering CPC indicated flow to less than COLSS indicated RCS flow. TS 3.0.3 was exited at 1039. The root cause of this event was determined to be personnel error. The Operations Manager counseled the operators involved in this event. Additionally, the Operations Manager will discuss this event with Operations personnel in his weekly meetings during the next requalification cycle. Management expectations regarding operations log taking will be emphasized.
3681991007 | Arkansas 2 | 02/23/1991 | 03/22/1991 | 9103270254 | <strong>Fire In Vital Engineered Safety Features 480 Volt Motor Control Center Caused By Incomplete Contact Between Bus Bars And Circuit Breaker Power Stabs</strong><br /><i>Abstract:&nbsp;</i>At 0050 on February 23, 1991, with the plant at hot standby conditions, a fire occurred in 480 volt Engineered Safety Features (ESF) Motor Control Center (MCC) 2B64. The fire occurred following starting of the main turbine turning gear motor and was caused by incomplete contact between the power stabs and bus bars for the turning gear breaker. A significant amount of ESF equipment for one redundant train was made inoperable when the MCC was de-energized by its feeder breaker tripping. The fire was extinguished in seven minutes. Restoration of power to the switchgear required approximately six hours. Throughout the event redundant safety related equipment was available to maintain the plant in a safe shutdown condition and remove residual heat. The root cause of the breaker fire was attributed to the design of the breaker cubicle that allowed misalignment when installing the breaker without providing a method of verifying proper breaker position. System Engineering will evaluate the feasibility of a design change to install guide brackets at the top of the MCC cubicle for the turning gear motor circuit breaker and other cubicles with a similar configuration. There have been no similar events reported in Licensee Event Reports from Arkansas Nuclear One.
3681991008 | Arkansas 2 | 03/09/1991 | 04/05/1991 | 9104090306 | <strong>Control Room Ventilation Isolation Caused By Emergency Diesel Generator Exhaust Fumes In the Intake Air Duct</strong><br /><i>Abstract:&nbsp;</i>At 0918 hours on March 9, 1991, with the plant in a refueling mode, ventilation isolation dampers to the Unit 2 control room automatically shut due to actuation of a smoke detector in the supply air duct. The source of the smoke was from the exhaust of an emergency diesel generator undergoing a test run. The root cause of the ventilation isolation was attributed to the design and location of the diesel generator exhaust in close proximity to the outside air intake for the control room normal ventilation system. Contributing factors included the design configuration of the exhaust hood for the diesel generator, existing plant conditions associated with both normal and emergency control room ventilation system components and an incorrect air balance in a portion of the ventilation system. Evaluation of the root cause has indicated that no further corrective actions are warranted. A manual balancing damper was readjusted to provide proper design air flow in the ventilation system. There have been no similar events reported in Licensee Event Reports from Arkansas Nuclear One.
3681991009 | Arkansas 2 | 03/11/1991 | 04/08/1991 | 9104120299 | <strong>Personnel Error Results In The Containment Ventilation System Effluent Pathway Not Being Monitored For Particulate And Iodine Activity As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1991, at approximately 1940, plant Chemistry personnel identified that a violation of the ANO-2 Technical Specifications had occurred in that the Containment Ventilation System effluent had not been adequately monitored for particulate and iodine activity for a period of approximately 5 hours and 39 minutes. The normal radiation monitor for the system was out of service for maintenance from 1322 until 1901 on March 11. An auxiliary sample pump was installed, as required by Technical Specifications, to collect samples to be analyzed for particulate and iodine activity. However, at approximately 1930, after the normal monitor had been returned to service, the technician that was removing the auxiliary pump discovered that its sample holder did not contain either a particulate or a charcoal filter. Therefore, that effluent pathway had not been monitored for particulates and iodine while the normal monitor was out of service. The process monitor for the Containment Purge System showed no adverse trends during the time that the effluent pathway was unmonitored. The root cause of this event was personnel error. The technician that installed the auxiliary pump had the filters in the area, but forgot to install them. Disciplinary action was taken against the responsible individual.
3681991010 | Arkansas 2 | 04/07/1991 | 05/03/1991 | 9105080321 | <strong>Inadequate Vendor Information Results In Containment Purge Isolation Valves Not Having Been Adequately Tested For Leakage Thereby Violating Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>During an inspection originated by Nuclear Regulatory Commission Information Notice 88-73, "Direction - Dependent Characteristics of Containment Purge Valves", ANO discovered that both the containment purge supply and exhaust inside isolation valves were installed such that they were less likely to seat when pressurized from the containment side. The purge system design does not provide for testing these valves from the containment side during local leak rate tests. The valves were tested for seat leakage during a containment integrated leak rate test performed in April 1991. The purge supply inside isolation valve leaked excessively. Leakage from the purge exhaust inside isolation valve was satisfactory. Two isolation valves in each line outside containment were tested and demonstrated satisfactory leak rates. A Technical Specification waiver of compliance was requested and approved to allow operating mode changes with existing conditions until an amendment can be approved. The two outside isolation valves in each line were deactivated in the shut position. A Technical Specification amendment is being evaluated to eliminate requirements for testing the inside containment valves. The feasibility of replacing or rotating the existing inside containment valves will be evaluated. There have been no similar events reported as Licensee Event Reports.
3681991011 | Arkansas 2 | 04/15/1991 | 05/14/1991 | 9105230111 | <strong>Subcritical Reactor Trip During Surveillance Testing Of the Reactor Protective System Due to A Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1991 at 0837 hours, with the reactor subcritical and control element assemblies inserted , an automatic Reactor Protective System trip occurred. Surveillance testing was being performed to determine the response time of the core protection calculator generated trip associated with Departure from Nucleate Boiling following reactor coolant pump flow coast down. Due to a procedural deficiency, trip signals were not bypassed as part of the test preparation. When the core protection calculator was reinitialized, trip signals were generated as a normal consequence of the process. These trip signals caused the trip circuit breakers to open before anticipated by the procedure. Testing was stopped and the procedure was corrected. Similar procedures for the surveillance testing of the other channels will be revised. The event is being reviewed with appropriate maintenance department personnel to take advantage of the lessons learned.
3681991012 | Arkansas 2 | 04/16/1991 | 05/15/1991 | 9105280174 | <strong>Both Service Water Loops Declared Inoperable Due To Clogging Of Pump Discharge Strainers Caused By a Breakdown In The Implementation Of Procedural Controls</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1991 both loops of the service water system were declared inoperable for approximately three minutes when a breakdown occurred in the implementation of procedural controls that resulted in debris bypassing screens at the pump suctions and clogging discharge strainers. The traveling screens were being rotated for inspection and lubrication. Sections of the procedure for this activity were performed out of sequence thereby allowing screen rotation without wash water flow. A contributing factor was ineffective communications. Throughout the event cooling water was supplied to both loops but at a reduced capacity. Restoration of one loop to normal pressure and flow conditions was accomplished in approximately three minutes by aligning the standby pump to the emergency cooling pond. Cleaning of debris from the pump discharge strainers restored both loops to an operable status in approximately two hours. The requirement to perform procedures in the proper sequence, unless specifically authorized otherwise, has been emphasized to appropriate maintenance personnel. Other corrective actions involve training of personnel concerning procedural compliance and effective communications.
3681991013 | Arkansas 2 | 05/12/1991 | 06/07/1991 | 9106120256 | <strong>Fire Watches Released From Inoperable Fire Barriers Due To Inadequate Documentation Concerning Posting Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1991, the Operations shift supervisor authorized release of fire watches that had been posted as required by a Technical Specification action statement at certain inoperable fire barriers. These fire barriers were located in the lube oil tank room, lube oil reservoir room, both battery rooms, and the control room. Work required to restore the barriers to an operable status had not been completed. Premature release of the fire watches was caused by inadequate documentation on the fire watch request forms concerning posting requirements. During the period without fire watch coverage, smoke or sprinkler pressure switch alarms were available in the control room for the affected areas. Fire watch posting was reestablished after the error was discovered. The total time without fire watch coverage was approximately thirty-four hours. The fire watch request forms for the affected barriers were revised to prevent recurrence of this event by specifically stating that the barriers have been inspected and are inoperable. Approval by Fire Protection personnel will be required before future release of fire watches at these barriers.
3681991014 | Arkansas 2 | 06/13/1991 | 07/12/1991 | 9107170063 | <strong>Inadequate Licensing Basis Document Information Resulted In Operation With 4160 Volt Engineered Safety Features Circuit Breakers In A Configuration For WHich Seismic Qualification Was Not Evaluated.</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1991, during an internal Electrical Distribution System Functional Inspection, it was discovered that four circuit breakers in 4160 volt Engineered Safety Features switchgear had been routinely positioned in a racked-down configuration. Seismic qualification for the breakers in this position was never performed. This allowed the possibility of damage to equipment in the switchgear rooms if a seismic event were to have occurred without the breakers being adequately restrained. The breakers involved were the two bus tie breakers and the two breakers for the "swing" High Pressure Safety Injection pump. This practice existed since before commercial operation of the plant. Unit 1 does not operate in this configuration. The root cause is inadequate licensing basis documentation that contributed to an inadequate procedure change in 1979 which approved the racked-down configuration as a normal method of operation. The breakers were removed from the switchgear rooms until the electrical system operating procedure could be revised to require their being racked-up. A change has been initiated to add information concerning lack of seismic qualification of the breakers in the racked-down configuration to the Safety Analysis Report.
3681991015 | Arkansas 2 | 09/12/1991 | 10/11/1991 | 9110170102 | <strong>Inadequate Vendor Analysis Of Coolant Cross Flow Resulted In The Potential For Emergency Diesel Generators Having Been Unable To Provide Design Electrical Output For Worst Case Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1991, COLTEC Industries, the vendor for ANO-2 emergency diesel generators, provided revised information that identified a problem with the generators' ability to provide design electrical load under worst case accident conditions. This information was provided to address an inquiry by ANO as part of an internal Electrical Distribution System Functional Inspection. A cross flow path between the cooling water systems for combustion inlet air and engine jacket cooling had been provided as part of the initial design. This cross flow path added additional heat burden to the air cooler resulting in reduced generator capacity. The reduced capacity would only have resulted in a problem during a large break loss of coolant accident with concurrent worst case (hottest) ambient conditions and coincident loss of normal cooling water supply requiring shifting to the emergency cooling pond and one diesel being unavailable. Corrective action was to shut an isolation valve in the cross flow path of each engine. This condition resulted in the plant having operated outside its design basis by potentially not having been able to ensure a safe shutdown during all design accident conditions.
3681991016 | Arkansas 2 | 09/24/1991 | 10/18/1991 | 9110250001 | <strong>Degraded Fire Barrier Caused By Unsealed Penetration Resulted From Inadequate Administrative Controls During Plant Construction</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1991, while performing a corrective maintenance activity identified during the previous Technical Specification surveillance inspection, Plant Modifications personnel identified a fire barrier penetration which was not properly sealed. The penetration between the floor of the South Emergency Diesel Generator Room and the overhead of a corridor outside of the Sample Room was filled with rags instead of grout. The root cause for this event was determined to be inadequate administrative controls during plant construction to ensure that rags used for damming material when applying an epoxy coating to the floor were removed when no longer required. The penetration being painted at the top caused it to appear like the rest of the floor slab and made the condition difficult to detect. Upon discovery, a fire watch was posted. The penetration has been properly sealed with grout. Current administrative controls have been evaluated to be sufficient to prevent recurrence of this condition. Although the fire barrier was degraded, no significant safety concern existed since adequate fire detection, suppression equipment, and the availability of Fire Brigade personnel provided significant protection against the spread of a fire.
3681991017 | Arkansas 2 | 10/11/1991 | 11/08/1991 | 9111150107 | <strong>Weekly Station Battery Surveillance Test Not Performed Within The Required Interval Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0810 on October 11, 1991, it was discovered that the Technical Specification surveillance test for the Arkansas Nuclear One Unit 2 station batteries had not been performed within the maximum allowable time interval. Both batteries were declared inoperable and Technical Specification 3.0.3 was entered. The tests for both batteries were completed satisfactorily by 0838, three hours and eight minutes after the end of the allowable interval. The root cause of this event was attributed to personnel errors by Electrical Maintenance personnel that resulted in a lack of oversight of the scheduled surveillance activity. A contributing factor was a failure of the Surveillance Coordinator to communicate to appropriate personnel the late completion status of the test. Actions have been taken to highlight surveillance tests on the shop schedule, standardize assignment of the battery surveillance to one crew, and improve communication between the Surveillance Coordinator and groups performing surveillances. A "lessons learned" training is being conducted with the Maintenance staff of both units. The surveillance program was reviewed and determined to be adequate. This event i-s reportable as an operation prohibited by Technical Specifications because of the entry into specification 3.0.3.
3681991018 | Arkansas 2 | 12/30/1991 | 01/24/1992 | 9201310321 | <strong>Service Water Valve Stuck In Intermediate Position Causes Service Water Loop To Be Inoperable Resulting In Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1991, a Service Water motor-operated valve stuck in an intermediate position during system realignment from supplying cooling tower basin makeup. This valve is a boundary between the seismic Loop 1 Service Water return header and the non-seismic Auxiliary Cooling Water (ACW) system. Service Water Loop 1 was inoperable because isolation from a piping break in ACW could not be assured if a seismic event were to have occurred. Since routine maintenance was in progress on one Emergency Feedwater pump and one containment hydrogen analyzer whose operability depended upon Service Water supplied from Loop 2, Loop 1 being inoperable resulted in both Emergency Feedwate pumps and both hydrogen analyzers being inoperable and therefore required entry into Technical Specification 3.0.3. One hydrogen analyzer was restored to operability within twenty five minutes. One Emergency Feedwater pump was operable within forty two minutes to allow exit from Technical Specification 3.0.3. The stuck valve was manually shut after approximately sixteen hours to allow exit from other Technical Specification action statements without any time limits having been exceeded. The root cause of the valve having stuck will be determined after plant conditions allow removal, inspection, and repair.
3691991001 | McGuire 1 | 02/11/1991 | 03/13/1991 | 9103210199 | <strong>A Unit 1 Reactor Trip Occurred Due To A Loss Of Offsite Power Caused By An Inappropriate Action, A Management Deficiency, And An Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1991, A Unit 1 Reactor Trip occurred at 1355:13. Prior to the event, Unit 1 was operating in Mode 1 (Power Operation) at 100% power. The Reactor was tripped by a Nuclear Instrumentation (NI) Power Range Hi Flux Rate signal. The trip signal was initiated when offsite power to the unit was lost because a blackout occurred in the 230KV switchyard. The blackout as a result of a failed relay in conjunction with a post modification test being performed on a newly added relay circuit in the switchyard. Subsequent depressurization of the Main Steam (SM) system resulted in a Safety Injection (SI). An Unusual Event was declared at 1420 due to Loss of Power and SI. The Technical Support Center (TSC) was activated as a conservative measure and TSC personnel made the required notification to the NRC. A thorough technical review was performed on the event and, consequently, a decision was made by Station Management (with concurrence of the NRC) to restart the Reactor. Unit 1 was returned to Mode 2 (Startup) operation on February 13, 1991, at approximately 0345. This event is assigned causes of Inappropriate Action, Management Deficiency, and an Equipment Failure..
3691991002 | McGuire 1 | 02/13/1991 | 03/15/1991 | 9103210250 | <strong>Trains A and B Of The Control Area Ventilation System Were Unable</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1991, while performing a periodic pressurization test of the Control Area Ventilation (VC) system, Performance (PERF) personnel discovered that the Technical Specification (TS) required positive pressure of 0.125 inches water gauge (w.g.) could not be maintained in the Control Room. PERF personnel advised Operations (OPS) personnel of their finding and OPS personnel declared Train B of the VC/YC system inoperable. Train A of the VC/YC system was also inoperable as a result of a flow balance test in progress on Train A of the Nuclear Service Water (RN) system; therefore, OPS personnel found it necessary to enter T.S. 3.0.3. The flow balance test was exited on Train A of RN, OPS personnel swapped to Train A of VC/YC and T.S. 3.0.3 was exited. During the course of this incident, Units 1 and 2 were in Mode 1 (Power Operation). This event has been classified as an Unknown because it could not be determined what caused the pressure decrease in the Control Room over the previous 3 months. PERF, Maintenance Engineering Services (MES) and Design Engineering (DE) personnel are evaluating long term options to alleviate the air leakage problems associated with the Control Room.
3691991003 | McGuire 1, McGuire 2 | 02/19/1991 | 03/21/1991 | 9103260441 | <strong>Both Trains Of The Control Room Ventilation System Were Inoperable Because Of A Design Deficiency And Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1991, Design Engineering (DE) personnel were performing a review of Nuclear Station Modification (NSM) MG-52065 to examine recommended additions to the NSM package. During the course of the review, DE personnel reevaluated the fact that loss of non-essential electrical power to chlorine detectors and radiation monitors associated with the Control Area Ventilation (VC) system would cause the Outside Air Intake Isolation valves for the VC system to close and that they could not be reopened from the Control Room. It was then determined that compensatory actions in place could not be achieved within the timing requirements for the assumptions of the Control Room dose analysis. Subsequently, at 2140, on February 19, 1991, both trains of the VC system were declared inoperable and Technical Specification (TS) Action statement 3.0.3 was entered for both units. A temporary modification was initiated to remove the automatic closure function from the radiation monitors and chlorine detectors. Also, changes to the procedures for responses to high chlorine or radiation alarms were initiated. At 0245, on February 20, the modification and procedure changes were completed and TS Action Statement 3.0.3 was exited. Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power at the time the event occurred. This event is assigned a cause of Design Oversight and a contributing cause of Management Deficiency. Appropriate modifications and procedure changes will be implemented to resolve the problem.
3691991004 | McGuire 1 | 02/19/1991 | 03/21/1991 | 9103270089 | <strong>A Unit 1 Reactor Trip Occurred Due To The Manual Opening Of A Reactor Trip Breaker Because Of A Management Deficiency And A Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1991, at 2142, Unit 1 experienced a Reactor/Turbine Trip. Unit 1 was in Mode 1 (Power Operation), at 100 percent power prior to this event. Prior to the Reactor Trip, Operations (OPS) management personnel were attempting to close the door on Reactor Trip Breaker (RTB) cubicle 1B. When the cubicle door was pushed closed, RTB 1B opened, tripping the Reactor. The Control Rods dropped into the Reactor core, thereby, generating a "NIS Hi Flux Rate Power Range Reactor Trip" trip signal. The only Safety System Actuation was the manual start of the Motor Driven Auxiliary Feedwater Pumps at 2143:58. OPS personnel implemented the Reactor Trip Or Safety Injection procedure and then entered the Reactor Trip procedure. OPS personnel returned Unit 1 to Mode 1 on February 21, 1991, at 1815. This event has been assigned causes of a Management Deficiency and a Possible Inappropriate Action.
3691991005 | McGuire 1 | 05/15/1991 | 06/14/1991 | 9107220309 | <strong>Both Trains Of The Annulus Ventilation System Were Inoperable Due To An Inappropriate Action Caused By Management Deficiencies and Deficient Communication</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1991, at 1130, Integrated Scheduling personnel were informed by Security personnel that both Unit 1 lower Annulus doors were open. The Integrated Scheduling person then checked with Operations (OPS) personnel to determine if they were aware of the doors being open. Consequently, since it could not be immediately verified whether the doors were still held open or not, OPS personnel entered Technical Specification (TS) Action Statement 3.0.3 for Unit 1 due to both trains of the Annulus Ventilation (VE) system being inoperable. Upon investigation by OPS personnel, it was found that the doors had been held open for painting of the doors and door frames on May 14, 1991, from 1500 to 1630, and on May 15, 1991, from 0800 to 0930 and 1020 to 1140. OPS personnel had not been aware that the doors were held open during these times and appropriate compensatory actions had not been established. <br /><br /> Therefore, both trains of the VE system were technically inoperable during the times when the doors were held open. The doors were verified to be closed and OPS personnel exited TS Action Statement 3.0.3 for Unit 1. Unit 1 was in Mode 1 (Power Operation) at 30 percent power at the time of the event discovery. This incident is assigned causes of Management Deficiency resulting from inadequate work control and management interface, and Inappropriate Action. Appropriate guidelines for control of painting station equipment will be re-emphasized to prevent recurrence of similar events.
3691991006 | McGuire 1 | 02/15/1991 | 03/28/1991 | 9104080212 | <strong>Technical Specification 3.0.3 Was Entered On Units 1 and 2 When The Containment Air Return And Hydrogen Skimmer System Was Declared Inoperable Due To A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991, Problem Investigation Report (PIR) 0-M91-0032 was initiated as a result of a concern expressed by a McGuire Nuclear Production Engineer during requalification training. The Containment Spray (NS) system pumps and the Containment Air Return (CAR) and Hydrogen Skimmer System (VX) fans had the potential to dead head due to the Containment Pressure and Control System (CPCS) permissive logic. The possibility also existed for the NS system pumps and VX system fan motors and damper motors to exceed their cycle duty. As a result of the Operability Evaluation (OE) performed by Design Engineering (DE) personnel, the VX system was declared inoperable on Units 1 and 2. Subsequently, Technical Specification (TS) 3.0.3 was entered on Units 1 and 2 on February 26, 1991 at 2057. Units 1 and 2 were in Mode 1 (Power Operation) at the time of this event. This event has been assigned a cause of Design Deficiency. To prevent this event from recurring, DE, Projects, and Compliance personnel are currently working on a comprehensive resolution to ensure long term reliability of the NS system pumps and VX system fans and dampers, thus eliminating pump dead heading and fan and damper cycling.
3691991007 | McGuire 1 | 05/20/1991 | 06/18/1991 | 9207200189 | <strong>Train B Of The Residual Heat Removal System Was Inoperable Due To Inappropriate Actions And An Unknown Possible Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1991 at approximately 1100, while Unit 1 was in Mode 1 (100 percent power), the action statement of Technical Specification 3/4.5.2 was exceeded without appropriate compensatory action. Valve 1ND-67B (Residual Heat Removal System Pump 1B and Heat Exchanger 1B Miniflow) had been inoperable for more than 72 hours without the knowledge of Operations (OPS) Control Room personnel. A work request was written on May 16, 1991 due to wires being pulled out of pressure switch 1NDPG5050 (Residual Heat Removal Pump 1B Miniflow) while test equipment was removed at the conclusion of periodic test PT/1/A/4204/01B (Residual Heat Removal Pump 1B Performance Test). It was not recognized by Performance (PRF) personnel at the time that this affected the operation of valve 1ND-67B. Valve 1ND-67B would not automatically open as required when ND Pump 1B was manually started on May 21, 1991. The separated wires were subsequently repaired under work request 144977OPS. The Residual Heat Removal (ND) system was returned to operable status on May 21, 1991 at 0550. This event is assigned causes of Inappropriate Actions, and an Unknown.
3691991008 | McGuire 1, McGuire 2 | 05/14/1991 | 08/15/1991 | 9108230152 | <strong>Under Certain Postulated Conditions, The Diesel Generators Could Be Rendered Inoperable Because Of A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1991, Design Engineering (DE) personnel issued Problem Investigation Report (PIR) 0-M91-0088. The PIR addressed a concern regarding non-seismically qualified piping in the vicinity of the Diesel Generator (D/G) air intakes. The concern was raised during an NRC audit. The piping in question was the 2 inch Main Steam drain lines and the 4 inch Condensate Feedwater tempering flow lines. On May 17, 1991, DE personnel issued an Operability Evaluation stating the D/Gs on Units 1 and 2 were conditionally operable. On May 22, 1991, PIR 0-M91-0100 was issued to address the concern regarding the same Main Steam and Condensate Feedwater lines when subjected to tornado wind loadings and tornado generated missiles. After evaluating the PIRs, DE personnel determined it would be necessary to upgrade the Main Steam drain line piping to withstand a seismic event and wind loads of 180 miles per hour (mph). The upgrades were implemented under Nuclear Station Modifications (NSMs) MG-12391 and MG-22391. DE personnel determined the Condensate Feedwater tempering flow lines were seismically rugged and would withstand wind loads of 300 mph. Unit 1 was in Mode 2 (Startup) and Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time the initial concern was addressed. The event has been assigned a cause of Design Deficiency because of an unanticipated environmental interaction between the steam which could potentially be released and the D/Gs. DE personnel are evaluating long term corrective actions for the piping in question under NSMs MG -12393 and MG-22393.
3691991009 | McGuire 1, McGuire 2 | 07/08/1991 | 08/22/1991 | 9110250071 | <strong>The Hardware Limits For Certain Process Control Equipment In The Reactor Protection System Were Exceeded Because Of A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>During the week of July 8, 1991, Maintenance Engineering Services (MES) were performing scaling calculations in preparation for the upcoming Unit 1 refueling outage. The calculations included determining the Westinghouse 7300 Process Control equipment gain settings for the revised Overtemperature Delta T (OTDT) setpoint. MES personnel discovered that the gain setting corresponding to the average Reactor Coolant (NC) temperature (Tave) input, for the new OTDT setpoint value, would cause the process control equipment to reach the hardware limit of the equipment prior to reaching the 100 percent power Tave value. The discovery prompted the MES personnel to investigate the existing Tave gain setting. They discovered the hardware limit was reached at 597 degrees Fahrenheit. Further investigation by Duke Power personnel revealed the same problem existed at Catawba Nuclear Station (CNS). Subsequently, changes were made to the process control equipment hardware at McGuire Nuclear Station (MNS) and CNS. The changes allowed the Tave gain setting to be reduced, bringing the process control equipment to within the hardware limits. During the time of this discovery, Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power. This event has been assigned a cause of Design Deficiency. Corrective actions include checking Reactor Protection System and Engineered Safety Features Actuations settings within the Westinghouse 7300 Process Control equipment to ensure hardware limits have not been exceeded.
3691991010 | McGuire 1, McGuire 2 | 07/24/1991 | 08/23/1991 | 9109040321 | <strong>Control Rod Deviation Monitor Inoperability Due To A Defective Procedure And A Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1991, at 1657, Operation Control Room personnel were informed the operability of Units 1 and 2 Rod Deviation Monitors was questionable. Prior to this event, Licensee Event Report 370/91-05 documented a Manual Reactor Trip on Unit 2. The investigation of the Unit 2 Reactor Trip revealed that Groups 1 and 2 of Control Rod Bank D had become misaligned by greater than 12 steps and no rod deviation alarms were received. Operations personnel declared Units 1 and 2 Rod Deviation Monitors inoperable and issued a work request to investigate and repair the Rod Deviation Monitor problem. During the investigation of the Rod Deviation Monitor problem, Production Support personnel discovered Units 1 and 2 Rod Deviation Monitors had been inoperable since December 7, 1983. Production Support personnel corrected the computer program procedure and verified the Rod Deviation Monitors operated properly. This event is assigned a cause of Defective Procedure because the procedure used to program the Rod Deviation Monitor was in error. This event is also being assigned a cause of management Deficiency because a procedure was not in place that required Operator Aid Computer programs to be functionally verified when installed or modified. A procedure to functionally verify Operator Aid Computer program installation and modifications had been developed and implemented prior to the discovery of this event. Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power at the time the event was discovered.
3691991011 | McGuire 1 | 07/24/1991 | 08/23/1991 | 9108290071 | <strong>Fuel Was Moved In The Fuel Pool While The Fuel Handling Exhaust System Was Inoperable Due To Inappropriate Actions</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1991, at 1000, while Unit 1 was in Mode 1 (Power Operation) at 100% power, Operations (OPS) Control Room personnel were informed by Performance (PRF) personnel that the Fuel Handling Exhaust (VF) system had been technically inoperable since May 27, 1991. Additionally, fuel had been moved, and crane loads had been moved over the Fuel Pool on July 11, 1991, July 18, 1991, and July 22,1991 through July 24,1991 while the VF system was technically inoperable. The VF system was subsequently declared inoperable and activity in the Fuel Pool was terminated. Appropriate notification was made to the NRC at 1324, on July 24, 1991. This event is assigned causes of Inappropriate Actions. OPS Control Room personnel were subsequently directed to declare the VF system inoperable if either the supply or exhaust equipment is out of service.
3691991012 | McGuire 1, McGuire 2 | 08/26/1991 | 09/25/1991 | 9110010124 | <strong>The Seven Day Technical Specification Surveillance For Vital Battery EVCA Was Missed Because Of Inappropriate Actions</strong><br /><i>Abstract:&nbsp;</i>On Friday, August 23, 1991, Instrumentation And Electrical (IAE) personnel were scheduled to perform a 7 day Technical Specification surveillance Preventative Maintenance/Periodic Test (PM/PT) on vital battery EVCA. The surveillance is normally performed by IAE shift personnel; however, shift personnel are not trained to perform the surveillance on the newly installed vital batteries. Therefore, the surveillance is performed by the IAE day crew personnel. However, due to Inappropriate Actions, the vital battery surveillance was missed. The surveillance was satisfactorily performed on August 26, 1991. Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power at the time of this event. This event was covered with IAE personnel responsible for the maintenance of the vital batteries. IAE shift personnel will receive training over the next 6 weeks so they can resume performance of the vital battery surveillance. IAE Planning and IAE personnel will also evaluate changing the day of the week the surveillance is performed to ensure appropriate interaction between IAE Planning and IAE personnel is maintained during the four day, ten hour work week.
3691991013 | McGuire 1 | 09/20/1991 | 10/21/1991 | 9110290459 | <strong>Both Trains Of The Annulus Ventilation System Were Inoperable Due To Management Deficiency And Inappropriate Actions</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1991, at 0815, Operations (OPS) Control Room personnel were informed by Security personnel that door AD 3311, Annulus Ventilation Bypass Door, was found open. The door was discovered to be open by a Security Officer posted in the area. This door is a Selected Licensee Commitment (SLC) Fire Door and serves as a pressure boundary for the Annulus ventilation (VE) system. The door must be posted with a fire barrier tag, and adequate compensatory measures must be implemented if the door is opened for periods longer than normal access during Modes 1 (Power Operation), 2 (Startup), 3 (Hot Standby), and 4 (Hot Shutdown). OPS personnel were not aware of the door being open and no tags or compensatory measures were in effect. Therefore, both trains of the VE system were inoperable. Security personnel immediately closed the door. Further investigation revealed that the door had been pushed closed but not latched for prolonged periods of time from 0904, on September 20, 1991 until 0834 on September 21, 1991. Since no compensatory actions had been established during these time periods, both trains of the VE system were inoperable during these times. OPS personnel made appropriate notification to the NRC at 1010, on September 21, 1991. Unit 1 was in Mode 4 at the time of the event discovery. This event is assigned causes of Management Deficiency and inappropriate Actions. Appropriate guidelines for control of the VE system doors will be developed to prevent recurrence of similar events.
3691991014 | McGuire 1 | 10/04/1991 | 12/11/1991 | 9112190186 | <strong>Train A Of The Containment Spray System Was Inoperable Due To A Mispositioned Valve As A Result Of An Unknown</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1991, valve 1RN-951, Containment Spray (NS) system Pump 1A Air Handling Unit (AHU) Outlet Control, was found mispositioned in the closed position during maintenance activities. Unit 1 was in Mode 6 (Refueling), in day 10 of a projected 71 day outage at the time of discovery. The misposition of valve 1RN-951 was brought to the attention of Operations (OPS) control Room personnel during discussion by OPS and Maintenance (MNT) personnel of valve 1RN-949, Residual Heat Removal (ND) System Pump 1A AHU Outlet Control, which was discovered mispositioned on October 4, 1991. During investigation of the event, it was determined that valve 1RN-949 was in the correct position during the time that the ND system was required to be operable. Valve 1RN-951 had been in the incorrect position for an unknown period of time after September 4, 1991. This resulted in Train 1A of the NS system being inoperable for an unknown period between September 4, 1991, and October 4, 1991. The NS system had been required to be operable September 4, 1991, through September 21, 1991, until Unit 1 entered Mode 5 (Cold Shutdown). Valves 1RN-949 and 1RN-951 were subsequently returned to the correct throttled position. This event is assigned a cause of Unknown because valve 1RN-951 was found in the closed position and no definite or probable cause could be determined.
3691991015 | McGuire 1, McGuire 2 | 10/13/1991 | 11/12/1991 | 9111190178 | <strong>An Inadvertent Unit 1 Train A Engineered Safety Features Actuation Occurred Because Of An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1991, at 0411, Operations (OPS) personnel were de-energizing Unit 1 Train A 4160 Volt Bus 1ETA for maintenance activity. Unit 1 was in No Mode and Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Upon opening breaker 1EPC BK 1ETA2, Standby Feeder Breaker For 1ETA Switchgear, a Blackout signal was sent to Diesel Load Sequencer 1A. Consequently, an Engineered Safety Features Actuation (ESFA) occurred on Train A causing associated valves and equipment to be moved or actuated as required for a Blackout configuration. This event is assigned a cause of Inappropriate Action because control power was not isolated to Diesel Generator Load Sequencer 1A prior to de-energizing Unit 1 Train A 4160 Bus 1ETA. OPS Management will review this event with appropriate OPS personnel.
3691991016 | McGuire 1 | 10/24/1991 | 11/25/1991 | 9112040028 | <strong>Qualified Fuel Assemblies Were Stored Improperly In The Unit 1 Spent Fuel Pool Due to A Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>While reviewing Technical Specification Section 3.9.12, McGuire Reactor unit personnel identified 11 fuel assemblies that had been stored in the Unit 1 Spent Fuel Pool in a manner contrary to the requirements of Technical Specification 3.9.12. This Limiting Condition For Operation requires, in part, that fuel stored in Region 2 of the Spent Fuel Pool shall undergo 16 days of decay, and if a checkerboard pattern is employed for unqualified fuel, one row between normal storage locations and checkerboard storage locations will be vacant. The vacant row provision of the specification was not satisfied from March 23, 1990 through October 23, 1991. At the time of discovery at 0900 on October 24, 1991, Unit 1 was defueled, and Unit 2 was in Mode 1 (Power Operation) at 100 percent power. This event has been assigned a cause of Defective Procedure. The fuel assemblies in question were immediately moved to positions to establish the required vacant row.
3691991017 | McGuire 1 | 10/16/1991 | 12/02/1991 | 9112060218 | <strong>The Control Area Ventilation System Was Inoperable Due To A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1991, McGuire Nuclear Station System Engineering personnel conducted a self training review of the Control Area Ventilation system. During the review, System Engineering personnel discovered the Smoke Purge Exhaust Fan would not receive a trip signal on a Diesel Generator sequencer actuation. System Engineering personnel suspected the operation of the Smoke Purge Exhaust Fan could adversely affect the ability of the Control Area Ventilation to function as designed during an emergency situation. Operations Management was notified by System Engineering personnel of the potential problem. Subsequent testing confirmed the Control Area Ventilation system would not maintain a positive pressure in the Control Room as designed with the Smoke Purge Exhaust Fan in operation. This event is assigned a cause of Design Deficiency due to an unanticipated component interaction. Operations personnel placed a safety tag on the control switch for the Smoke Purge Exhaust Fan to prevent operation of the fan. Unit 1 was defueled and Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time of discovery of the event.
3691991018 | McGuire 1, McGuire 2 | 12/18/1991 | 01/17/1992 | 9201270344 | <strong>Both Trains Of The Annulus Ventilation System Were Inoperable Due To Management Deficiency And Deficient Communication</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1991, Instrumentation and Electrical personnel were performing the semi-annual calibration on loop 2IAE-9060, Lower Personnel Air Lock Leak Rate Monitor. During this calibration, door AD 3321, Annulus Ventilation Bypass Door, was latched open to allow for communication between personnel working on the pneumatic module and remote control unit associated with the loop. This door is a Selected Licensee Commitment Fire Door and serves as a pressure boundary for the Annulus Ventilation (VE) system. The door must be posted with a fire barrier tag, and adequate compensatory measures must be implemented to ensure operability of the VE system if the door is opened for periods longer than normal access during Modes 1 (Power Operation), 2 (Startup), 3 (Hot Standby), and 4 (Hot shutdown). During the calibration no fire tags or VE system compensatory measures were in effect. Therefore, both trains of the VE system were inoperable while the door was open. Unit 2 was in Mode 1 at 100 percent power at the time of the event discovery. Further investigation has revealed that door AD 3321 on Unit 2 and door AD 3311, Annulus Ventilation Bypass Door, on Unit 1 have been latched open whenever the semi-annual calibration of the respective Lower Personnel Air Lock Leak Rate monitor has been performed. Since no compensatory actions had been established during those time periods, both trains of the VE system were inoperable during those times. This event is assigned causes of Management Deficiency and Deficient Communication. Appropriate measures for control of the VE system doors have been implemented.
3701991001 | McGuire 2 | 03/11/1991 | 04/10/1991 | 9104300088 | <strong>Failure To Comply With Engineered Safety Features Actuation System Instrumentation Technical Specifications Because of An Inappropriate Action And Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1991, at approximately 1400, Instrument And Electrical (IAE) personnel were performing procedure PT/2/A/4201/05B, Unit 2 Containment Pressure Control Analog Channel Operational Test (Train B). While performing this test, Containment Pressure Control System (CPCS) channel 2NSPT5490 was found to be faulty. At 1430, the Operations Senior Reactor Operator (OPS SRO) declared channel 2NSPT5490 inoperable and logged channel 2NSPT5490 in the Technical Specification Action Item Log (TSAIL) book. IAE personnel were directed to place channel 2NSPT5490 in the start permissive mode within one hour to comply with Technical Specification (TS) 3.3.2. After consultation with IAE Supervision, IAE personnel decided to use procedure PT/2/A/4201/05B to place channel 2NSPT5490 in the start permissive mode as required by TS 3.3.2. IAE personnel proceeded to Containment Pressure Control Cabinet (CPCC) 4 and performed procedure PT/2/A/4201/05B, section 12.1 through step 12.4.8. This action had IAE personnel place the key-operated control switch for channel 2NSPT5490 in the test position. They thought this action placed the channel in the start permissive mode, satisfying TS 3.3.2. While troubleshooting channel 2NSPT5490, IAE personnel discovered the channel was not in the start permissive mode. At 2150, IAE personnel took the appropriate actions to place channel 2NSPT5490 in the start permissive mode. This event is assigned a cause of Inappropriate Action because IAE personnel improperly followed the correct procedure. A cause of Defective Procedure is also assigned because steps that would have prevented this event were not located within the body of procedure PT/2/A/4201/05B.
3701991002 | McGuire 2 | 05/15/1991 | 06/14/1991 | 9106180383 | <strong>The Unit 2 Turbine Driven Auxiliary Feedwater Pump Was Inoperable Because Of A Mispositioned Sliding Link Due To A Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1991, while preparing to perform preventive maintenance on Unit 2 Turbine Driven Auxiliary Feedwater Pump suction pressure switch 2MCAPS5390, Instrument And Electrical personnel discovered sliding link C-8 in cabinet 2AFP2B was open. This open link would have prevented valve 2CA-116B (Turbine Driven Auxiliary Feedwater Pump Supply From Train B Nuclear Service Water), from opening if a low suction pressure signal had been received. This rendered the pump inoperable and left the Standby Shutdown Facility (SSF) in a degraded condition. The link was subsequently restored to the closed position by Instrument And Electrical personnel and valve 2CA-116B was stroked by Operations Control Room personnel. Sliding links for Units 1 and 2 Auxiliary Feedwater suction pressure switches were subsequently inspected per work requests 601113 and 601114 with no further problems noted. The event is assigned a cause of Possible Inappropriate Action because no definite cause could be determined. Unit 2 was in Mode 1 (Power Operation), operating between 95 and 100 percent power during the time period from April 22, 1991 through May 15, 1991. This event will be reviewed with Instrument And Electrical personnel and Quality Assurance personnel as applicable .
3701991003 | McGuire 2 | 06/06/1991 | 07/08/1991 | 9107150174 | <strong>An Inadvertent Unit 2 Train B Engineered Safety Features Actuation Occurred Because Of An Inappropriate Action And Management Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1991, at 1515, Performance (PRF) personnel were performing procedure PT/2/A/4200/28B, Train B Slave Relay Test on Unit 2. The PRF person coordinating the procedure mistakenly communicated to Operations (OPS) personnel to rack out the breaker for Motor Driven Auxiliary Feedwater (CA) Pump 2A instead of the breaker for Motor Driven CA Pump 2B as specified by the procedure. Consequently, when Train 2B Slave Relay was actuated in a later procedure step, Motor Driven CA Pump 2B started and pumped water into Steam Generators (SGs) 2C and 2D. The OPS personnel involved did not have specific written directions or a reference copy of the PRF procedure when racking out the breaker. When CA Pump 2B started OPS and PRF personnel recognized that an error had been made. PRF personnel reset the slave relay. OPS personnel then stopped the pump and took appropriate measures to stabilize SG level. Unit 2 was in Mode 1 (Power Operation) at 100 percent power when this event occurred. This event is assigned causes of Inappropriate Action and Management Deficiencies. Appropriate procedure changes will be implemented to ensure that Station personnel performing support activities for procedures will have a reference copy of the procedure or will have the procedure step(s) read to them verbatim prior to performing them.
3701991004 | McGuire 2 | 04/22/1991 | 09/05/1991 | 9109100367 | <strong>The Auxiliar Feedwater System Turbine Driven Pump Was Past Inoperable Due To Erroneous Calibration Of Suction Pressure Switches Due To A Management And A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1991 at approximately 2021, while Unit 2 was in Mode 1 (Power operation) at 100 percent power, the Auxiliary Feedwater (CA) Turbine Driven (TD) Pump was declared inoperable due to erroneous calibration of CA TD Pump suction pressure switches 2CAPS5380, 5381, and 5390. These pressure switches monitor CA TD Pump suction pressure and automatically open assured water source isolation valves 2CA-162C (TD CA Pump Suction Header from Nuclear Service Water Supply Isolation), 2RN-162B (Engineered Safety Function CA Assured Supply From B Train Nuclear Service Water System), and 2CA-116B (Engineered Safety Function TD CA Pump Suction From TD Feedwater Condensate Storage Tank), when CA TD Pump suction pressure falls below 2 psig for more than 2-3 seconds. It was subsequently determined that the CA TD Pump had been technically inoperable since initial startup because the assured suction source isolation valves would not have automatically opened as required. The associated pressure switches were subsequently calibrated under work request 601014IAE. The CA TD Pump was returned to operable status on April 22, 1991 at 2332. This event is assigned causes of Management Deficiency and Design Deficiency.
3701991005 | McGuire 2 | 06/28/1991 | 07/29/1991 | 9107310256 | <strong>Inadvertant Engineered Safety Features Actuation Because Diesel Generator 2B Automatically Started Due to An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1991, at 0836, Operations (OPS) Periodic Test (PT) group personnel were performing procedure PT/2/B/4350/01B, Bus Lines Protection Relay System Test, on Unit 2. The OPS PT group person performing the Control Room (CR) portion of the procedure mistakenly placed the "BUS 2B TRANS TRIP CHANNEL 2 RCVR TEST" key switch in the "TEST" position instead of the "BUS 2B TRANS TRIP CHANNEL 1 RCVR TEST" key switch as specified by procedure step 12.4.9. When the OPS PT group person in the switchyard placed "BUS 2B TRANS TRIP CHANNEL 1 TRANS TEST" key switch in test and depressed the "TEST" pushbutton as directed by procedure step 12.4.10, a trip signal was sent to "BUS 2B TRANS TRIP CHANNEL 1". The trip signal caused Bus 2B Generator Breaker to open and 6900 Volt Bus 2TB and 2TD to swap to their alternate power source as designed. An Engineered safety Features Actuation (ESFA) occurred when Diesel Generator (D/G) 2B automatically started, due to a momentary undervoltage spike, when buses 2TB and 2TD swapped to their alternate power source. This event was caused by an Inappropriate Action due to a lack of attention to detail. OPS management will review this event with appropriate OPS personnel. Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time of the event.
3701991006 | McGuire 2 | 07/08/1991 | 08/07/1991 | 9108130342 | <strong>The Unit 2 Emergency Personnel Hatch Was Discovered Unlatched Due To An Unknown And A Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1991, the Unit 2 Emergency Personnel Hatch between upper and Lower Containment was discovered unlatched, with the lead/wire tamper seals intact. This discovery was made by General Office Maintenance personnel. They were investigating the possibility that a similar problem which was identified at Catawba Nuclear Station (LER 413/91-03) could also exist at McGuire Nuclear Station. Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time of this event. The Emergency Personnel Hatch was subsequently inspected, relatched, and sealed per work request 04604D. The Unit 1 Emergency Personnel Hatch was also inspected and was found to be latched with the tamper seals intact and tightly installed per work request 09139C. This event is assigned a cause of Unknown since it could not be determined how or when the Unit 2 Emergency Personnel Hatch became unlatched. A cause of Management Deficiency is also assigned because of inadequate maintenance practices.
3701991007 | McGuire 2 | 07/14/1991 | 08/13/1991 | 9108190093 | <strong>A Manual Unit 2 Reactor Trip Was Initiated Due To A Control Rod Failure Caused By An Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1991, operations (OPS) personnel and Instrumentation and Electrical (IAE) personnel were performing the quarterly calibration on Power Range Neutron Flux Channels for Unit 2 to correspond with current Incore/Excore Correlation values. During this calibration, a Quadrant Power Tilt Ratio (QPTR) alarm was received after the first Neutron Flux Channel was returned to service. To comply with Technical Specifications (TSs), a load reduction to 91 percent power was required. During the subsequent power reduction, Group 1 of Control Rod Bank D failed to move properly causing a Control Rod misalignment greater than TS limits. To comply with TSs, Boron was added and the Control Rods were realigned. An Axial Flux Difference (AFD) oscillation resulted from the movement of the Control Rods and power reduction. Since the Control Rods would not move properly they were unavailable to dampen the oscillation. IAE personnel attempted to repair the Control Rod problem during the next day, but were unable to do so. At 0658, on July 14, 1991, OPS personnel initiated a manual Reactor Trip prior to exceeding Ts limits for AFD. OPS personnel implemented the Reactor Trip recovery procedure to recover from the transient. Unit 2 was in Mode 1 (Power Operation) at 90.5 percent power at the time of the Reactor Trip. This event is assigned a cause of Equipment Failure because the Control Rods would not properly insert into the core. Subsequent repairs were made to correct the problem and the Unit returned to Power Operation on July 16, 1991, at 0608.
3701991008 | McGuire 2 | 08/14/1991 | 09/13/1991 | 9109170294 | <strong>Both Trains Of The Annulus Ventilation System Were Inoperable Because Of An Inappropriate Action And A Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1991, at 2250, the Security Force Officer serving as Compensatory Officer for Control Access Door (CAD) 322 and posting a continuous fire barrier watch for Civil Door 713, noticed that Fire Door (FD) 713A was open. This door is a Selected Licensee Commitment (SLC)) Fire Door and serves as a pressure boundary for the Annulus Ventilation System. The door must be posted with a fire barrier tag, and adequate compensatory measures must be implemented if the door is opened. No tags were evident. The Security Force Officer contacted the Secondary Alarm Station personnel who in turn contacted the Unit 2 Operations (OPS) Control Room (CR) personnel. OPS CR personnel were unaware that FD 713A was open. The door was immediately secured at the direction of the Senior Reactor Operator (SRO). Because the door was left open with no compensatory measures in place and without the knowledge of CR personnel, both trains of the Annulus Ventilation System were inoperable from 1630 until 2250 on August 14, 1991. The four hour notification was made to the NRC at 0042, August 15,1991. Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time of event discovery. This incident is assigned causes of Inappropriate Action and Management Deficiency. To prevent recurrence, the importance of attention to detail has been reemphasized to all station personnel. Changes are planned to modify the fire tagging program to clearly state what actions are being verified by the individual's signature when fire barriers are returned to service. Independent Verification of Fire Penetrations upon return to operable status will be implemented.
3701991009 | McGuire 2 | 09/16/1991 | 10/16/1991 | 9110250058 | <strong>Missed Technical Specification Surveillance Due To A Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1991, Operations Periodic Test Group personnel were performing procedure PT/2/A/4400/02C, Nuclear Service Water Valve Verification. During the performance of the procedure, operations Periodic Test Group personnel noticed valve 2RN-279B, Auxiliary Building Ventilation Return Isolation, was not listed in the procedure. Further investigation also revealed that valve 2RN-299A, Auxiliary Building Ventilation Return Isolation, had not been listed in procedure PT/2/A/4400/02C from December 16, 1985 until May 31, 1988. The omission of valves 2RN-299A and 2RN-279B from procedure PT/2/A/4400/02C resulted in a missed Technical Specification surveillance. This event is assigned a cause of a Possible Inappropriate Action. The actual cause could not be determined from the available information. Operations Periodic Test Group personnel initiated a procedure change to add valve 2RN-279B to procedure PT/2/A/4400/02C. Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time of discovery.
3701991010 | McGuire 2 | 09/25/1991 | 10/25/1991 | 9208310318 | <strong>Unit 2 Manual Reactor Trip resulting From Possible Design, Manufacturing, Construction/Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>A Unit 2 Reactor T rip was manually initiated at 1450:50 on September 25, 1991. Prior to the event, Unit 2 was operating in Mode 1 (Power Operation) at 100 percent power. The trip was manually initiated by Operations Control Room personnel upon receipt of alarm panel 2AD-4, annunciator C-4 (Steam Generator D flow mismatch low CF flow). The annunciation resulted from Main Feedwater valve 2CF-26, Steam Generator D Containment Isolation Valve, movement to its fail-safe (closed) position upon loss of power to the controlling solenoid. The loss of power was caused by a voltage surge that blew fuse BA 11-12 in Terminal Board (TB) 1209. The voltage surge was caused by grounding both legs of Vital Battery EVCD as a result of the replacement of the control board indicator lamp for valve 2VX-33B, Containment Sample Supply Inside Isolation. This event has been assigned a cause of Possible Design, Manufacturing, Construction/Installation Deficiency because of damaged insulation resulting in a positive leg ground on the solenoid associated with valve 2CF-26. Corrective actions include inspection of surplus solenoids to ensure serviceable condition of the insulation.
3701991011 | McGuire 2 | 10/04/1991 | 11/04/1991 | 9111120255 | <strong>Unit 2 Experienced An Engineered Safeguards Features Actuation When Operations Personnel Manually Started The Auxiliary Feedwater Pumps Because Of A Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1991, at 1202, Operations (OPS) Control Room (CR) personnel manually started the Unit 2 motor Driven Auxiliary Feedwater (CA) pumps. This was considered an Engineered Safeguards Features (ESF) actuation. Unit 2 was in Mode 3 (Hot Standby) at the time of this event. CR instrumentation indicated decreasing auxiliary steam header pressure. Subsequently, a decrease in condenser vacuum, and a decrease in the steam seal pressure on the Main Turbine and Main Feedwater (CF) pumps occurred. OPS CR personnel tripped CF pump B and gradually removed CF pump A from the feedwater header. Once the auxiliary steam header pressure returned to normal, OPS CR personnel placed CF pump A back into the feedwater header and secured the CA pumps thirty minutes later. This event has been assigned a cause of Defective Procedure because no procedural guidance is provided to allow OPS personnel to use the CA system as an option during normal unit shutdown when the CF system is unavailable. As a corrective action, OPS Management will revise the Unit 1 and 2 unit shutdown procedure to reflect this option.
3701991012 | McGuire 2 | 11/08/1991 | 12/09/1991 | 9206050141 | <strong>An Automatic Reactor Trip Was Initiated Due To A Control Rod Failure Caused By An Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1991, at approximately 1142, Operations (OPS) Control Room personnel were performing the monthly procedure PT/2/A/4600/01, Rod Cluster Control Assembly Movement Test. Shutdown Banks A and B moved properly. However, Shutdown Bank C dropped into the core as the Reactor Operator at the controls attempted to step this bank in. The Solid State Protection system subsequently generated a Negative Flux Rate Trip signal which automatically tripped the Reactor. OPS Control Room personnel also initiated a Manual Reactor Trip as required by the Reactor Trip procedure. Diesel Generator 2B was running at the time and the emergency breaker for Diesel Generator 2B opened due to an overload when a low-low level in Steam Generator A caused the Auxiliary Feedwater and Nuclear Service Water Pumps to start. Unit 2 was in Mode 1 (Power Operation) at 100 percent power prior to the trip. The Unit performed as expected during the transient and there were no nuclear safety significant problems. An investigation was performed and it was determined that an electronic equipment failure within the Shutdown Bank C input logic circuit had caused the stationary rod gripper coils to stay de-energized too long. An independent safety review was performed and it was determined that it was safe and prudent to restart the Reactor. Unit 2 was returned to Mode 1 on November 9, 1991, at 0510. This event is assigned a cause of Equipment Failure due to an electronic failure in the Rod Control system circuitry.
3731991001 | LaSalle 1 | 01/23/1991 | 02/19/1991 | 9102260341 | <strong>Reactor Building Ventilation System Isolation Damper Closing Due To Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1991, at 1108 hours, with Unit 1 in Run Mode at 100% power, control power was lost to the Division 2 isolation dampers of the Reactor Building ventilation system (VR) [VA]. This was detected by an alarm and loss of damper position indication in the Control Room. The Division 2 isolation dampers closed as designed but the VR supply and exhaust fans continued running, and had to be manually secured. <br /><br /> A temporary system change was installed, which bypassed a failed relay. The control power was restored, and VR was restarted at approximately 1200 hours. On January 28, 1991, the temporary system change was cleared after the failed relay was replaced. <br /><br /> The event was caused by the failure of relay 1VR001AX, which functions in the starting circuit of the VR exhaust fans. The relay failure tripped the circuit breaker supplying the relay coil. The circuit also provides power to the isolation damper solenoids and coils in the VR fan trip logic. The cause of the relay failure is unknown.<br /><br /> There was no impact on the safe operation of the plant. The Division 2 VR dampers isolated as designed under loss of power. The loss of fan trips had no safety impact. Once the isolation dampers closed, the fans were outside the boundary of secondary containment. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Featured system.
3731991002 | LaSalle 1, LaSalle 2 | 03/26/1991 | 04/25/1991 | 9104300026 | <strong>Control Room Ventilation Isolation During Return To Service Due To Cognitive Error</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991, at approximately 2024 hours with Unit 1 defueled and Unit 2 in Operational Condition 1 (Run) at 99 percent power, a Division 1, Group 4 Primary Containment (PC) Isolation occurred. This isolation caused Unit 2 Reactor Building Ventilation (VR) Inboard Dampers 2VR05YA and 2VR04YB to close and the VR Fans to trip off. It also caused the Standby Gas Treatment System (VG) on both Units to auto start. <br /><br /> The cause of this event was a momentary loss of continuity in the Reactor Building Ventilation and Fuel Pool Cooling Exhaust Radiation Monitor Trip Logic. The loss of continuity occurred when a Technician loosened an electrical connection in the trip circuitry to remove a previously installed jumper. The location of the interrupted circuit path is such that the power to the contacts forming the combinational logic was lost, resulting in the complete isolation signal from the single open circuit. The root cause of this event was a cognitive error on the part of the Shift Engineer and IM Supervisor approving the removal of the Temporary System Changes. The possibility of disturbing the continuity of PCIS logic circuits during the removal process should have been recognized, and the need of temporary alligator clips specified to the Technician. <br /><br /> The Temporary System Change procedure will be revised and the departments involved in the event will be retrained on the procedure. This event was reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
3731991003 | LaSalle 1 | 03/19/1991 | 04/18/1991 | 9104230164 | <strong>Loss Of Engineered Safety Feature Bus 143 During Surveillance Testing Caused By Deficient Procedure & Personal Error</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1991 at 1323 hours, with Unit 1 defueled, Operational Analysis Department (OAD) personnel were performing 1B Diesel Generator (DG) protective relay calibrations in accordance with an approved station procedure when the normal feedbreaker to Engineered Safety Feature (ESF) bus 143 tripped. The 1B DG, which provides emergency power to ESF bus 143, was out of service at the time of this event and did not start; consequently ESF bus 143 remained deenergized. Review of the breaker tripping scheme indicated that the relay that OAD personnel had just tested (1B DG overcurrent with voltage restraint relay K35A) would trip the breaker. <br /><br /> The causes of this event were an inadequate procedure, and personnel error in identifying all trips to be defeated. Although the procedure used identifies the need for disabling trips, the procedure does not give any specific direction on which trips are required to be disabled.<br /><br /> The safety consequences of this event were minimal. Unit 1 was in cold shutdown and defueled during this event. The High Pressure Core Spray (HPCS) system was already inoperable due to scheduled maintenance at the time of this event. No Emergency Core Cooling Systems (ECCS) are required operable with the unit defueled. Once the cause for the trip was determined, ESF bus 143 was reenergized at 1352 hours on March 19, 1991. <br /><br /> Short term corrective actions will be to train all OAD personnel on this event. Long term corrective actions are to implement new procedures which identify all isolation points and required actions prior to performing the necessary calibrations or functional checks. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an ESF system logic.
3731991004 | LaSalle 1 | 04/01/1991 | 04/30/1991 | 9105060081 | <strong>Partial Group II Primary Containment Isolation Due To Blown Fuses</strong><br /><i>Abstract:&nbsp;</i>On April 01, 1991 at approximately 1416 hours with Unit 1 defueled at 0 percent power, the "B" Reactor Recirculation (RR) Hydraulic Power Unit (HPU) inboard isolation valves 1B33-F338B, 1B33-F340B, 1B33-F342B, and 1B33-F344B closed. The only related work in progress at the time was the installation of banana jacks by the Instrument Maintenance Department in accordance with work request L94823. <br /><br /> Upon investigation it was determined that fuse 1B21H-FU1B in panel 1PA14J had blown causing several isolation relays to de-energize, resulting in the partial Primary Containment Isolation System (PC) Group II and X isolation signal which caused the valves to close. All of the other Group II and X valves and actuations were already closed, out-of-service, or powered from another fuse. The cause of the blown fuse could not be identified. It is believed that current surges during the lifting and relanding of an energized relay's power lead may have weakened the fuse such that it blew some short time later with only normal current flow. <br /><br /> The fuse was replaced. The isolation logic was reset. <br /><br /> The Instrument Maintenance Department practice of installing banana jacks on energized circuits was halted. The work instructions were rewritten to de-energize the circuit prior to installing banana jacks to minimize the possibility of causing an actuation. <br /><br /> Engineering calculations were performed which verified that the type and size of fuse installed were correct to provide both reliable circuit operation and circuit protection. <br /><br /> This event is reportable to the NRC pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature (ESF) System.
3731991005 | LaSalle 1, LaSalle 2 | 04/10/1991 | 05/10/1991 | 9105160068 | <strong>Missed Technical Specification Surveillance On Containment Monitoring Due To Inadequate Pre-License Review</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1991 at 1230 hours with Unit 1 in Mode 5 (Refuel) and Unit 2 in Mode 1 (Run) at 0%/100% power respectively, it was determined that LaSalle Station had not performed a Technical Specification surveillance requirement on suppression chamber oxygen sampling. Technical Specification 3.6.6.2. was changed from taking an oxygen sample from Primary Containment to taking the oxygen sample from the Drywell and Suppression Chamber during pre-licensing (1981). LaSalle Operating Surveillance LOS-AA-W1, "Technical Specification Weekly Surveillances" performs sampling of the drywell on a weekly basis but did not get revised to include sampling of the suppression chamber.<br /><br /> The apparent cause of the event was due to an inadequate review of the Technical Specification change to determine procedures that required revisions. The consequences of this event are minimal since the drywell and suppression chamber are inerted in parallel and the drywell free air space is larger than the suppression chambers free air space, therefore making it highly likely that a non-combustible mixture has been maintained in the suppression chamber. <br /><br /> LaSalle Operation Surveillance LOS-AA-W1, was revised and performed satisfactorily on April 10, 1991 and found the drywell and suppression chamber at 2.4% and 3.2% oxygen concentration respectively. <br /><br /> This event is reportable to the NRC pursuant to the requirements of 10CFR50.73(a)(2)(i) due to a condition prohibited by the plant Technical Specifications.
3731991006 | LaSalle 1 | 05/19/1991 | 06/17/1991 | 9106200189 | <strong>Reactor Scram On Low Reactor Vessel Water Level Due To Loss Of 'A' Turbine Driven Reactor Feedwater Pump Caused By Control Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1991 at 0423 hours, with Unit 1 in Operational Condition 1 (Run) at 80% power (steady-state) and both Turbine Driven Reactor Feed Pumps (TDRFP) in three-element automatic control, the "A" TDRFP discharge flow decreased from 5.5 MLB/hr to 0.1 MLB/hr initiating a decrease in reactor water level. <br /><br /> Approximately three seconds after the loss of the "A" TDRFP flow, a reactor low level alarm annunciated. The licensed unit Reactor Operator (RO) immediately responded to the alarm and diagnosed the problem as loss of "A" TDRFP flow. The Operator placed the "A" TDRFP controller under manual control and attempted to manually increase flow. The "A" TDRFP failed to respond and since the "B" TDRFP could not turn the level decrease by itself the reactor scrammed at Level 3 (+12.5" reactor water level). All Reactor Protection actuations occurred as expected. There were no Emergency Core Cooling System (ECCS) or Primary Containment Isolation System actuations. The unit was placed in Hot Shutdown following the scram. <br /><br /> The cause of this event was the "A" TDRFP control valve spontaneously closing, effectively disabling the "A" feedwater turbine and pump flow control. The root cause for this closure is not known. After extensive "A" TDRFP testing, Unit 1 was restarted on May 21, 1991 and no problems have occurred since that time. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
3731991007 | LaSalle 1 | 05/28/1991 | 06/27/1991 | 9107020381 | <strong>Reactor Water Cleanup Isolation Due To Leaky Filter/Demineralizer Valve</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1991, at 1326 hours, with Unit 1 in the Operating Condition 1 (Run) mode at 100% power, the Reactor Water Cleanup (RWCU) System isolated on a Leak Detection (LD) High Differential Flow Isolation Signal causing both the RWCU Inboard and Outboard Isolation Valves to automatically close, followed by automatic trips of the RWCU pumps. <br /><br /> At the time of this event, LaSalle Special Procedure LLP-91-014, "Keeping the Precoat and Hold Pumps on Simultaneously", was being performed on the "B" Filter/Demineralizer. After this filter was de-isolated, the filter inlet valve 1G33-Z001-06B leaked by, allowing high pressure water to flow through the Filter Vessel and back to the low pressure piping, causing low pressure relief valve 1G33-Z001-063 to lift, causing the differential flow isolation logic to initiate. <br /><br /> Prior to the event, the Reactor Recirculation/Reactor Conductivity Monitor was inoperable. When RWCU isolated, the Reactor Water Cleanup/Reactor Conductivity monitor now became inoperable, and Chemistry was notified to monitor Reactor Chemistry in accordance with Technical Specification 3/4.4.4. <br /><br /> The RWCU lines were walked down to verify piping integrity, the isolation was then reset and the RWCU system was restarted at approximately 2120 hours on May 28, 1991. <br /><br /> Work request L08224 was written to repair valve 1G33-Z001-06B, which leaked past its seat. <br /><br /> This event is reportable to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineering Safety Feature System.
3731991008 | LaSalle 1, LaSalle 2 | 06/13/1991 | 07/12/1991 | 9107170113 | <strong>Spurious Auto Start Of Control Room Ventilation Emergency Makeup Train</strong><br /><i>Abstract:&nbsp;</i>At 0045 hours on June 13, 1991, with Unit 1 in Operational Condition 1 (Run) at 99 percent power, the "A" Control Room Ventilation Emergency Make-up Train auto started on a spurious trip from the Control Room Air Intake Radiation Monitor (1D18-K751B). No work was in progress at the time of the event which could be identified as a potential source of the high radiation signal. The Radiation Monitor was immediately reset, proper damper position was verified, and Control Room Ventilation returned to normal. <br /><br /> The cause of this event is unknown, but it is believed that random noise, of an unknown origin, in the electronics may have induced the spurious trip. <br /><br /> The consequences of this event were minimal since the auto starting of the Control Room Ventilation Emergency Make-up train was the correct Emergency Safety Feature (ESF) response for this situation. <br /><br /> To correct this problem a Modification will be performed to change to the Control Room Ventilation Process Radiation Monitoring logic to initiate when 2 out of the 4 detectors have High Radiation signals, instead of the present 1 out of 4 logic. <br /><br /> This event is being reported pursuant to requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature system.
3731991009 | LaSalle 1 | 09/20/1991 | 10/11/1991 | 9110220191 | <strong>Inadvertent Division II Reactor Water Cleanup Isolation Due to Poor Electrical Connection on Switch</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1991, at 1800 hours with Unit 1 in Operating Condition 1 and at 100% power, a Group 5 Division 2 isolation was received during the performance of LaSalle Instrument Surveillance LIS-MS-307A "Unit 1 Reactor Vessel Low Water Level 1 and 2 Isolation Instrument Channels A & C Monthly Functional Test". During the procedure, as an Operator placed the "C" channel in the test position, the isolation was received. This isolation caused the closing of the Reactor Water Cleanup (RT) Inboard Isolation Valve and tripped the running RT Pump.<br /><br /> Upon further investigation it became evident that the test switch for the "D" channel was not making contact. The "C" and the "D" channels provide the Division 2 isolation. When the "C" channel was taken to the test position the logic was completed and the isolation occurred. <br /><br /> The "D" channel test switch was cycled and verified that it was working properly. A work request has been written to inspect and clean the contacts or replace the switch. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature (ESF).
3731991010 | LaSalle 1 | 07/19/1991 | 05/07/1993 | 9305140255 | <strong>Spurious Auto Start Of Control Room Ventilation Emergency Makeup Train Due To High Radiation Spike</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1991 at approximately 0520 hours with Unit 1 in Operational Condition 1 (Run) at 100 percent power, the 'A' Control Room Ventilation Emergency Make-Up (VC) [VI] Fan OVC03CA auto started on a spurious trip of the control room air intake Process Radiation (PR) [IL] Monitor 1018-K751B. <br /><br /> On August 5, 1991 at approximately 0742 hours with Unit 1 in Operational Condition 1 (Run) at 98 percent power, the 'A' Control Room Ventilation Emergency Make-Up (VC) [VI] Fan OVC03CA auto started on a spurious trip of the Control Room air intake Process Radiation (PR) [IL] Monitor 1D18-K7518. <br /><br /> The apparent cause of the first event was random spikes from the power supply board of the Radiation Monitor 1D18-K751B. The observations of the power supply signal indicated that random spikes were taking place and that this could be a cause of the high radiation spikes. The apparent cause of the second event was determined to be from normal variations in background radiation readings. <br /><br /> The safety consequences of both of these events were minimal because the system worked as designed according to the high radiation indication. Also the fact that only one out of the four detectors registered high radiation readings, indicated that the initiation was not due to radiation. <br /><br /> To correct the problem of the first event the power supply board was replaced and the rad monitor electronic signals were observed again. The action of replacing the power supply board appears not to have worked because the event reoccurred on August 5, 1991. The work had been completed three days prior to this most recent occurrence. The corrective action for the High Radiation Spike is to modify the Radiation Monitor Circuit. The modified circuit gives the monitor a smoother wave form and a more stable response.
3731991011 | LaSalle 1 | 10/02/1991 | 11/01/1991 | 9111060239 | <strong>Missed Technical Specification Surveillance During Primary Containment Purge Due To Missed Prerequisite In Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991 at 0820 hours with Unit 1 in Operational Condition 1 (Run) at 100% power, a purge of the Unit 1 Drywell was initiated in accordance with LaSalle Operating Procedure LOP-VQ-11, "Nitrogen Inerting of Primary Containment with the Primary Containment Vent/Purge System", without the samples for Principal Gamma Emitters and Tritium as required by the Procedure and Technical Specification Table 4.11.2-1 being taken. <br /><br /> There were no safety consequences as a result of this event. At the time of the event the Primary Containment Continuous Air Monitor System showed normal levels of Noble Gas and Particulate activity, the Drywell Floor Drain and Equipment Drain Sump Flowrates were normal with no increasing trends. A Unit One Primary Containment sample for Noble Gases was already in progress at the time of the event. No gaseous effluent release limits were exceeded during the event. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) any operation or condition prohibited by the Plant's Technical Specification.
3731991012 | LaSalle 1 | 07/29/1991 | 08/23/1991 | 9108270168 | <strong>Reactor Core Isolation Cooling Overspeed Trip Due To Governor Valve Sticking Open</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1991, at 0920 hours, the Reactor Core Isolation Cooling (RCIC) Turbine tripped on mechanical overspeed. This event occurred while the operating department was performing LaSalle Operating Surveillance, LOS-RI-Q4, "Reactor Core Isolation Cooling System Cold Quick Start." Unit 1 was in operational condition 1 (Run) at 100% power level. <br /><br /> The mechanical overspeed assembly trips the RCIC Turbine at 125 percent of the rated speed, 5625 50 rpm. During the performance of the surveillance the RCIC system overspeed trip occurred at 5650 rpm. The mechanical overspeed assembly actuated as designed. <br /><br /> The cause for the actuation of the mechanical overspeed trip assembly during the performance of the surveillance was determined to be from the Governor Valve sticking in the open position during startup of the system. <br /><br /> The apparent cause was due to the short time that the system was in operation during a RCIC spurious injection that occurred on July 24, 1991, when RCIC started automatically due to low level signal spike and was shutdown in 28 seconds.<br /><br /> The RCIC system was declared inoperable, and work request L09337 and L09338 were initiated to investigate and repair the problem. The High Pressure Core Spray was fully operable throughout the event. <br /><br /> The Electric Governor EG-R Actuator and Remote Servo for the governor was replaced. Dresser Rand (formerly Terry Turbine) was contacted to determine if any similar situation with the Governor Valve had occurred. There were no indications of any similar condition.
3731991013 | LaSalle 1, LaSalle 2 | 08/07/1991 | 09/06/1991 | 9108270170 | <strong>Actuation Of "B" VE Charcoal Absorber Due To Defective Ionization Detector</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1991 with Units 1 and 2 in Operational Condition 1 (Run) at 100% power, a "B" Auxiliary Electric Equipment Room Ventilation (VE) return air fire alarm was received in the Control Room Fire Protection Panel. Concurrent with receipt of the alarm the "B" VE Charcoal Adsorber Dampers automatically realigned to place the normally bypassed unit in operation (unbypassed) mode. An operator who was immediately dispatched to survey the suspect areas verified that there was no fire. The defective detector was then identified and a work request written to repair it. Due to the defective Ionization Detector an hourly fire watch was also established in accordance with Technical Specification 3.3.7.9. During troubleshooting Electrical Maintenance personnel attempted to reset the detector but were unable to clear the fire alarm. As a result, the existing detector was removed and a new one installed. Upon replacement of the detector the fire alarm cleared and the "B" VE Charcoal Adsorber Dampers realigned to place the unit in its normally bypassed mode. At this time the hourly fire watch was terminated.<br /><br /> This event did not impact the safe operation of the plant because a fire did not actually occur. The automatic actuation of the Charcoal Adsorber Dampers due to the failure of the Ionization Detector was per design. Furthermore, an hourly fire watch was maintained until the defective detector was replaced. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
3731991014 | LaSalle 1 | 10/15/1991 | 08/31/1994 | 9409120068 | <strong>Lost Station Vent Stack Particulate Composite Sample (July 1991) by Offsite Vendor</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1991, the Chemistry Services Department at LaSalle County Station received a telephone call from a representative of TMA/Norcal, (a vendor that provides radioanalytical analyses service to the station) informing the station that they could not find the monthly Station Vent Stack particulate composite sample for July, 1991. Due to the loss of this sample, the surveillance requirements in Technical Specification Table 4.11.2-1, for a monthly gross alpha analysis and a quarterly Strontium 89/90 analysis on composite particulate samples could not be performed. <br /><br /> The exact cause of the lost sample is not known. The Chemistry Services Department believes that the sample was in the shipping container when it left the site. The vendor cannot determine if the sample was lost before receipt, or whether it was lost at their facility. <br /><br /> Gamma isotopic and tritium analyses of the samples obtained from the Station Vent Stack were reviewed for the months of June, July and August 1991 and showed a normal release trend. Therefore, it is believed that the lost data would also be normal. <br /><br /> A revision to Chemistry Procedure, LCP-410-9, has been made requiring the Station Quality Control Department to review the shipment of monthly Technical Specification composites prior to leaving the station to ensure all the samples are in the shipment when it leaves the site. <br /><br /> Continued on Attached Page
3731991015 | LaSalle 1, LaSalle 2 | 11/07/1991 | 03/06/1992 | 9203090414 | <strong>Inadequate Testing of Diesel Generators Due To Inadequate Procedures/Technical Specification Misinterpretation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. ON 11/7/91 AT APPROX. 1500 HOURS, WITH UNIT 1 AND UNIT 2 IN OPERATONAL CONDITION 1 (RUN) AT 100% POWER, DURING A NUCLEAR REGULATORY COMMISSION (NRC) ELECTRICAL DISTRIBUTION SYSTEM FUNCTIONAL INSPECTION (EDSFI) IT WAS DETERMINED, THAT CERTAIN EMERGENCY SAFETY FEATURE (ESF) BUS UNDERVOLTAGE RELAY CONTACTS WERE NOT FUNCTIONALLY TESTED AS REQUIRED BY PLANT TECH SPEC 4.8.1.1.2.D.4. THE STATION WAS PLACED ON A 24 HOUR TIMECLOCK AND THE REQUIRED CONTACT TESTING WAS COMMENCED TO FULFILL THE TECH SPEC SURVEILLANCE REQUIREMENTS. ON 11/8/91, AT 0900 HOURS IT WAS DETERMINED THAT THE ALLOWANCE OF THE 24 HOUR PERIOD TO PERFORM THE REQUIRED SURVEILLANCES WAS INAPPROPRIATE AND A LATE NOTIFICATION WAS MADE. TECHNICAL SPECIFICATION 3.0.5 WAS ENTERED. ALL TESTING WAS COMPLETED AT 1030 HOURS ON 11/8/91. THE ROOT CAUSE OF THIS EVENT WAS INADEQUATE TESTING PROCEDURES. THE SAFETY CONSEQUENCES OF THIS EVENT WERE MINIMAL. THE O, 1A, 2A, 1B, AND 2B DIESEL GENERATORS WERE INOPERABLE SOLELY DUE TO THE MISSED SURVEILLANCE AND WERE FULLY FUNCTIONAL THROUGHOUT THE EVENT, EXCEPT WHILE EACH WAS UNDERGOING TESTING IN ACCORDANCE WITH STATION CORRECTIVE ACTIONS. THIS EVENT IS BEING REPORTED PURSUANT TO 10CFR50.73(A)(2)(I) DUE TO A DEVIATION FROM PLANT TECH SPECS.
3731991016 | LaSalle 1 | 10/24/1991 | 11/22/1991 | 9112020346 | <strong>Division 3 125 VDC Battery Inoperable Due to a Loose Connection</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1991, with Unit 1 in Operational Condition 1 (Run) at 98% power, the Division 3 125 Volt DC battery was declared inoperable at 1045 hours when a loose cable connection on cell #1 was reported. Since the Division 3 battery is the emergency DC power supply for the High Pressure Core Spray (HPS, HP)BG! system, the HPCS system was declared inoperable. The Reactor Core Isolation Cooling (RCIC, RI)BN! system was already inoperable due to a failed operability surveillance. The battery cable connection was quickly retorqued to the proper value and resistance measurements verified acceptable. The Division 3 battery was declared operable at 1143 hours on October 24, 1991. The cause of this event is unknown. The consequences of this event were minimal, since Division 1 and Division 2 Emergency Core Cooling Systems were fully operable during this event. The Unit 1 and Unit 2 Division 3 batteries were inspected to verify the battery connections were tight. Technical Specifications require the Unit to be shutdown with both HPS and RCIC systems inoperable.<br /><br /> This event is reportable to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v)(A) due to a decrease in safe shutdown capability.
3731991017 | LaSalle 1 | 10/23/1991 | 11/21/1991 | 9112020335 | <strong>Reactor Core Isolation Cooling Overspeed Trip Due To Governor Valve Sticking Open</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1991, at 1031 hours, while Unit 1 was in Operational Condition 1 (Run), at 100% power, the Reactor Core Isolation Cooling (RCIC) BN! Turbine tripped on mechanical overspeed. This event occurred while the Operating Department was performing the quarterly surveillance that demonstrates the cold quick start capability of the RCIC system, LaSalle Operating Surveillance, LOS-RI-Q4, Reactor Core Isolation Cooling System Cold Quick Start." <br /><br /> The cause for the mechanical overspeed during the surveillance was failure of the Governor Valve to close during the start of the system. In an attempt to identify the root cause of the problem, the valve was disassembled, and inspected. Following inspection of the mechanical valve, the governor vendor, Woodward Governor Company, inspected the electronic controls and the electronic governor actuator for the system.<br /><br /> At the time of this incident the High Pressure Core Spray (HPCS) System, and the other Emergency Core Cooling Systems were fully operable. The RCIC System was declared inoperable and Work Requests were written to investigate and repair the problem.<br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3741991001 | LaSalle 2 | 01/10/1991 | 06/04/1991 | 9106110225 | <strong>High Pressure Core Spray Pump Room And Turbine Building Fire Rated Barrier Found Degraded During Inspection</strong><br /><i>Abstract:&nbsp;</i>Station Technical Staff was performing LaSalle Technical Surveillance LTS-1000-42 "Fire Assembly Integrity Inspections" and found open penetration in Technical Specification related fire rated walls. <br /><br /> At 0830 hours on January 10, 1991 with Unit 2 in operational condition 1 (Run) at 100% power, three open penetrations were found in the High Pressure Core Spray Room (HPCS). A one hour fire watch was initiated in accordance with LaSalle Technical Specification 3.7.6 action requirement a. A work request was initiated to seal the penetration and was completed on January 15, 1991. <br /><br /> At 1400 hours on April 10, 1991 with Unit 2 in operational condition (Run) at 100% power and Unit 1 in the refuel mode, openings were found between the metal decking and steel beam separating the Turbine Building and the Auxiliary Building. A one hour fire watch was established between columns 13-15 and a continuous fire watch was established for columns 15-17 in accordance with LaSalle Technical Specification 3.7.6 Action Requirement a. A work request was initiated to seal the penetration and was completed on April 16, 1991. <br /><br /> Because the degradation of the fire barrier would not have impaired safe shutdown of Unit 2, the safety significance of this is considered to be minimal. The root cause of this event is the failure to install these required fire barriers during initial construction and annotate them on the design drawings, as appropriate. An additional cause is the location of the openings, being approximately 17 to 20 feet above the floor, which contributed to them not being identified during past performances of LTS-1000-42. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i) due to a deviation from plant Technical Specifications.
3741991002 | LaSalle 2 | 03/18/1991 | 04/17/1991 | 9104230005 | <strong>Division 1 Reactor Building Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1991, at approximately 2044 hours with Unit 1 defueled, and Unit 2 running at 100 percent power, a Division 1, Group 4 Primary Containment Isolation occurred. This caused the Unit 2 Reactor Building Ventilation (VR) Outboard Dampers 2VR05YB and 2VR04YA to close and the VR fans to trip off. It also caused the Standby Gas Treatment System on both Units to auto start. <br /><br /> The apparent cause of this event is uncertain, but at the time of the event the Instrument Maintenance Department was performing LaSalle Instrument Surveillance LIS-VR-102, "Unit 1 Reactor Building Fuel Pool Exhaust Radiation Monitor Calibration" on the "A" channel. Due to this surveillance on the Fuel Pool Exhaust Process Radiation Monitor, there was a one-half isolation signal being given by the "A" channel and a signal from the "B" channel is all that would have to be received to cause the Group 4 Isolation. There were no indications of an isolation signal being received by the "B" channel, and it was tested satisfactorily when the calibration was performed. <br /><br /> The Instrument Maintenance Department looked for loose connections and found none. The surveillance on the "A" channel was reperformed, and tested satisfactorily, and the isolation problem did not reoccur. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
3741991003 | LaSalle 2 | 03/28/1991 | 04/26/1991 | 9104290295 | <strong>Reactor Building Ventilation Isolation Due To Personnel Error During Return To Service</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1991, with Unit 2 in Operational Condition 1 (Run) at 100% power, and Unit 1 defueled, the Operating Department was to transfer the Reactor Protection System bus. The Nuclear Station Operator reviewed the procedure and transferred a part of it to a separate piece of paper where he wrote incorrectly the terminal points to be jumpered out by the Equipment Operator. The Equipment Operator followed the instructions on the piece of paper for jumpering out the terminal points, therefore the wrong terminal points were jumpered out. (The Unit 2 Isolation logic from Unit 1 should have been jumpered out but instead Unit 1 Isolation logic from Unit 1 was jumpered out.) When the Reactor Protection System bus was transferred to the alternate power supply, the Division 1, Unit 2 Reactor Building Ventilation Isolation dampers isolated and the Unit 1 Standby Gas Treatment System auto started. <br /><br /> By using LaSalle Operating Abnormal Procedure, LOA-VR-01, "Recovery from a Group IV Isolation or Spurious Trip of Reactor Building Vent", the system was un-isolated. The involved personnel were tailgated in the importance of following procedure and the use of "in-hand" procedures. <br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety System.
3741991004 | LaSalle 2 | 06/17/1991 | 07/17/1991 | 9107230150 | <strong>Reactor Building Ventilation Due To Inadvertent Mechanical Shock To Control Switch Cabinet</strong><br /><i>Abstract:&nbsp;</i>At 0616 hours on June 17, 1991, with Unit 2 in Run mode at 94% power, the Unit 2 Reactor Building Ventilation system (VR) inboard isolation dampers closed without an apparent valid isolation signal. Investigation of plant activities at the time of the occurrence of the event yielded only one probable cause. Just prior to the isolation, a maintenance mechanic erecting scaffolding lost his balance, and stepped sharply onto the control panel of the inboard isolation dampers. The resulting shock caused the contacts of a control relay in the panel to momentarily lose contact, resulting in the isolation. There was no apparent defect in the relay. <br /><br /> At 0645 hours on June 17, 1991, the Unit 2 VR system was restored to service. The Mechanical Maintenance staff will be tailgated on precautions to be observed when erecting scaffolding near control panels, per General Information Notice 91-046. <br /><br /> This incident was reportable pursuant to the requirements of 10CFR73(a)(2)(iv), due to an actuation of an Emergency Safety Feature system.
3741991006 | LaSalle 2 | 03/21/1991 | 07/26/1991 | 9110010112 | <strong>Breach of Primary Containment During Surveillance Testing Due To Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1991 at 1110 hours, Unit 2 Primary Containment integrity was declared inoperable during a test run of Unit 1 Hydrogen Recombiner. The recombiner blower cover had been removed for preventative maintenance creating an opening to the Reactor Building such that when the Unit 2 containment valves were open, Primary Containment integrity became inoperable. The test run was a planned 10 minute evolution and the Unit 2 valves were closed from the Control Room following the test. One of the redundant isolation valves had a dual indication, and an operator was dispatched to investigate. The operator determined the cause of the dual indication and the valve closure was completed. He also recognized the Primary Containment integrity concern and notified the Control Room. Primary Containment integrity had been restored at 1150 hours by the Control Room Operator's remote closure of the valves, which was within the 1 hour timeclock of the Technical Specification 3.6.1.1 Limiting Condition For Operation (LCO). Personnel were in attendance at the recombiner during the condition. Because the LCO time limit was not exceeded, the condition was erroneously determined to not be an ENS call or LER. <br /><br /> On July 3 at 0850 hours, after subsequent review and discussions initiated by the NRC, LaSalle Station concluded that this event required notification under 10CFR50.72(b)(2)(iii)(C) and is reportable as an LER in accordance with 10CFR50.73(a)(2)(v). ENS notification was made at 1010 hours on July 3, 1991.
3741991007 | LaSalle 2, LaSalle 1 | 06/26/1991 | 07/26/1991 | 9107310250 | <strong>Control Room Ventilation Charcoal Adsorber Actuation Due To Inadvertent Bumping During Nearby Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1991, at 2045 hours, with Units 1 and 2 in Operational Condition 1 (Run) at 97% power and 100% power respectively, an Instrument Maintenance technician was replacing a differential pressure switch located inside the "A" Control Room Ventilation (VC) system local panel. As he was tightening a screw he inadvertently bumped an adjacent relay. This action sealed in the outside air smoke detection circuit which caused a fire alarm to be received in the Control Room and the normally bypassed charcoal absorber to be placed in line with the air flowpath. <br /><br /> This event did not impact the safe operation of the plant because the charcoal absorber actuated to its safety mode as designed. The individual involved in the incident received a minor shock and was transported to a nearby hospital for examination as a precautionary measure. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
3741991008 | LaSalle 2 | 08/11/1991 | 09/11/1991 | 9109170105 | <strong>Turbine Driven Reactor Feed Pump Insulation Fire Due To Lube Oil Leakage Through a Pinched Flange Gasket</strong><br /><i>Abstract:&nbsp;</i>At 0855 hours on August 11, 1991 with Unit 2 in Operational Condition 1 (RUN) at 91% power (1020 Mwe), smoke detectors alarmed and investigators reported a fire in the 2B Turbine-Driven Reactor Feed Pump (TDRFP) Room. The fire brigade responded and the fire was extinguished using carbon dioxide and water. The fire apparently originated from oil-soaked insulation resulting from a lubricating oil leak. Unit load was reduced to 87% (965 Mwe) to allow removal of the 2B TDRFP from service and placing the Motor-Driven Reactor Feed Pump (MDRFP) on-line. After the TDRFP was tripped, a fire watch was established until all insulation could be removed and the potential of re-flash eliminated. <br /><br /> The fire was extinguished within approximately eleven minutes of the arrival of the fire brigade at the scene. This exceeded the ten minute maximum time limit and a Generating Station Emergency Plan (GSEP) Unusual Event was declared at 0913 hours. The GSEP remained in effect until the potential for a re-flash was eliminated at 1725 hours. Work Request L09573 was generated to repair the oil leak.<br /><br /> This report is being reported pursuant to 10CFR50.73(a)(2)(x); a fire of greater than ten minutes which could have hampered site personnel in the performance of their duties. <br /><br /> The root cause of this event was turbine bearing lube oil leaking from the flange gasket of the ground brush assembly. This saturated the surrounding insulation with oil which fueled the fire once ignited. <br /><br /> A fire in this zone will have no impact on safe shutdown of the unit since the zone does not contain safety-related equipment. The ground brush assembly was removed and inspected, revealing a pinched flange gasket as the root cause of the oil leak. A replacement gasket was obtained and special care was taken during reassembly to avoid pinching the new gasket. Post maintenance testing indicated the flange was no longer leaking and the 2B TDRFP was returned to service at 0400 hours on August 16, 1991.
3741991009 | LaSalle 2 | 09/05/1991 | 10/03/1991 | 9110090327 | <strong>Inadvertent Residual Heat Removal and Steam Condensing Isolation Due to Broken Lead During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, at approximately 1056 hours, during the performance of LaSalle Instrument Surveillance LIS-MS-205, "Unit 2 Main Steam Tunnel High Area Vent Differential Temperature MSIV Isolation Calibration", an inadvertent Division 1 Group VI and Group VIII isolation occurred. This isolation was caused when an Instrument Mechanic working on the surveillance unintentionally broke a wire leading to 2E31-N614A, the Riley Temperature Module that performs Residual Heat Removal (RHR) Area High Differential Temperature Isolation.<br /><br /> The function of the broken wire was to provide the temperature module with a reference input temperature. Breaking the wire actually caused the module to experience a low differential temperature signal. However the resulting spurious signal oscillations were sufficient to trip the relay. <br /><br /> The wire was replaced on the Riley module, and the instrument and system were returned to normal. Since all of the affected isolation valves were closed no valves changed position.<br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73 (a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
3741991010 | LaSalle 2 | 09/06/1991 | 09/30/1991 | 9110030152 | <strong>Manual Scram Due to Electro-Hydraulic Control Leak</strong><br /><i>Abstract:&nbsp;</i>At 0415 hours, on September 6, 1991, with Unit 2 in Operational Condition One (RUN) at 85% power (965 MWe), the Electro-Hydraulic Control (EHC, EH)TG! Fluid Tank Hi/Lo level alarm annunciated after all four Main Turbine Control Valves had been cycled for required monthly Reactor Protection Surveillances.<br /><br /> A local investigation found that the EHC tank level was low. Also an EHC hydraulic oil leak was discovered at the #2 Main Turbine Control Valve. At 0525 hours, when it became apparent that the leak could not be controlled, a Unit shutdown was initiated. The reactor was manually scrammed at 0615 hours, from 32% power (361 MWe). Following the manual Scram, the turbine automatically tripped, on Main Generator reverse power. The leak stopped when the turbine tripped. <br /><br /> One leak was found at the half inch stainless steel tubing which supplies 1600 psig Relayed Emergency Trip System (RETS) hydraulic fluid to the #2 Control Valve. The cause of the leak has been attributed to broken and damaged piping supports that allowed the EHC lines to vibrate excessively. The damaged supports, allowed the RETS line and the 1 inch stainless steel tubing that supplies the 1600 psig Fluid Actuation Supply (FAS) to the #2 Main Turbine Control Valve to rub together, resulting in the failure of the RETS line. It was also identified that the RETS and FAS lines for the #4 Main Turbine Control Valve were also rubbing together. This had resulted in outer diameter wall thinning on the RETS line, however, no leakage occurred. <br /><br /> The hydraulic lines of #2 and #4 Control Valves were repaired. Four mechanical snubbers sprayed with fluid were replaced. All fluid soaked steam line insulation was replaced. All electrical cable jackets affected as well as the general area were cleaned. Repairs to the pipe supports recommended by the Nuclear Engineering Department were completed. <br /><br /> During the course of the event, 12 barrels of EHC fluid were added to restore the EHC reservoir to its normal level. The Mark I EHC system was supplied by General Electric. This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to a manual actuation of the Reactor Protection System.
3741991011 | LaSalle 2 | 09/07/1991 | 10/18/1991 | 9110240191 | <strong>Missed Surveillance Due to Incorrect Change in General Surveillance Program (DW Personnel Airlock Door Interlock Test)</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1991, it was determined that the Drywell Personnel Access Hatch Interlock surveillance had not been performed since December 15, 1990. This is contrary to Technical Specification 4.6.1.3.c which requires this surveillance be performed every six months. <br /><br /> The direct cause of this missed surveillance was that the due date, and subsequent critical date, were changed to January 5, 1992, to coincide with the Unit 2 Refueling Outage. Misinterpretation of the applicable Technical Specification requirement which apparently resulted in the surveillance due date and subsequent critical date being changed is a probable root cause for this missed surveillance. Other probable root causes are an error in the assignment of the applicable Plant Condition for this surveillance entry in the General Surveillance Program, and failure to use the General Surveillance Request Form when the previous due and critical dates were changed. <br /><br /> The missed surveillance was performed acceptably on September 6, 1991, and the surveillance is now current. <br /><br /> A revision to the General Surveillance Procedure, LAP-100-11, will be made requiring the General Surveillance Request Form be used for all changes to existing surveillances. An evaluation will be made to amend the Technical Specification requirements 4.6.1.3.b and 4.6.1.3.c to help ensure adequate understanding of the surveillance. <br /><br /> A General Surveillance Request Form was initiated to correct the applicable Plant Condition when this surveillance is to be performed. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) any operation or condition prohibited by the Plant's Technical Specification.
3741991012 | LaSalle 2 | 09/24/1991 | 10/18/1991 | 9110290249 | <strong>Unit 2 Reactor Scram Due to Turbine Valve Closure</strong><br /><i>Abstract:&nbsp;</i>At 0015 hours, on September 24, 1991, with Unit 2 in Operational Condition One (Run) at 100% power (1112 MWe), the reactor scrammed on Neutron Monitoring (NR) IG! upscale trips as a result of a pressure/power transient induced by the Main Turbine Valves (EH) TG! closing. No testing or maintenance was being performed at the time of the event. All other equipment responded as designed. All Reactor Control Rods inserted, the Main Turbine Bypass Valves opened, the Motor Driven Reactor Feed Pump maintained reactor level and Safety Relief Valves (SRV's) S, U, K, and E (NB) SB! cycled and then reseated. <br /><br /> The root cause of the scram has not been determined. An analysis of the sequence of events by Commonwealth Edison and the General Electric Company indicates that a spurious signal in the Electro-Hydraulic Control (EHC) system either falsely signaled a Main Turbine overspeed condition or created a sudden demand signal to be at zero load. <br /><br /> The speed circuits of EHC System were replaced and calibrated. This was also the corrective actions to a similar event which occurred at the James A. Fitzpatrick Plant, New York Power Authority, on November 5, 1989. Also, the circuits associated with the #1 3KHz oscillator were replaced and calibrated. <br /><br /> The speed circuits will be continuously monitored until the next refueling outage. The Mark I EHC system was supplied by General Electric. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to an automatic actuation of the Reactor Protection System.
3741991013 | LaSalle 2 | 10/07/1991 | 11/01/1991 | 9202100061 | <strong>Loss of Auxiliary Electric Equipment Room Ventilation Supply Fan Due to Overheating of Starting Coil for the Breaker</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 085%. ON 10/7/91, AT 0400 HOURS WITH UNIT 1 AND 2 IN OPERATIONAL CONDITION 1 (RUN) AT 95% AND 85% POWER RESPECTIVELY, A SEVEN DAY TIMECLOCK WAS ENTERED PER TECH SPEC 3.7.2 DUE TO THE VE(VI) SUPPLY FAN BREAKER TRIPPING. AT THIS TIME THE 'A' VC/VE(VI) TRAIN OUT OF SERVICE FOR SCHEDULED MAINTENANCE AND A ONE HOUR TIMECLOCK WAS ENTERED AT THIS TIME PER TECH SPEC 3.0.3, SINCE BOTH VC/VE(VI) EMERGENCY MAKE-UP TRAINS WERE INOPERABLE AT THE SAME TIME. THE 'A' TRAIN WAS RETURNED TO SERVICE AT 0450 NOTIFICATION WAS MADE AT 0755 HOURS ON 10/7/91, ON THE BASIS OF A LOSS OF A SAFETY SYSTEM FUNCTION, SINCE BOTH AUXILIARY ELECTRIC ROOM VENTILATION SYSTEMS WERE UNAVAILABLE FOR SERVICE. WORK REQUEST L10621 WAS INITIATED AT THIS TIME FOR THE ELECTRICAL MAINTENANCE DEPARTMENT TO INVESTIGATE AND CORRECT THE PROBLEM. THE CAUSE OF THE PROBLEM. THIS RELAY WAS REPLACED AND ON 10/7/91, AT 2030 HOURS THE VE(VI) SUPPLY FAN, OVE01CB, WAS SUCCESSFULLY RUN. ON 10/7/91, AT 2120 HOURS THE TIMECLOCK WAS EXITED. THIS EVENT IS REPORTABLE PURSUANT TO THE REQUIREMENTS OF 10CFR50.73(A)92)(V)(C) DUE TO THE LOSS OF A SAFETY SYSTEM FUNCTION.
3741991014 | LaSalle 2 | 10/29/1991 | 11/27/1991 | 9111270101 | <strong>Unit 2 Reactor Scram Due To A False High Vibration Trip Signal</strong><br /><i>Abstract:&nbsp;</i>At 0725 hours, on October 29, 1991, with Unit 2 in Operational Condition One (Run) at 100% power (1122 MWe), the reactor scrammed on Turbine Stop Valve closure due to the Main Turbine tripping on high #6 bearing vibration. At the time of this event, no related testing or maintenance was being performed.<br /><br /> All other equipment responded as designed. All Control Rods inserted, the Main Turbine Bypass Valves opened as required, the Motor Driven Reactor Feedwater Pump started and maintained reactor water level, and Main Steam Safety Relief Valves K, E, D, C, S and V cycled to control pressure and then reseated. <br /><br /> The root cause of the scram was a spurious trip from a Turbine Supervisory System Vibration Amplifier Circuit Card. The card has been replaced and its trip temporarily defeated. Administrative controls are in place to manually trip the turbine should actual high vibration be experienced on this bearing. The Turbine Supervisory System was supplied by General Electric. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to an automatic actuation of the Reactor Protection System.
3821991001 | Waterford 3 | 02/03/1991 | 03/04/1991 | 9103070218 | <strong>Failure to Place Plant Protection Channel in Bypass During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1991, during the performance of Operating Procedure OP-903-107 "Plant Protection System Channel B Functional Test," Steam Generator 2 low pressure setpoint was determined to be out of tolerance. Contrary to Technical Specification 3.3.1 Action Statement 2, channel B was not placed in the bypassed or tripped condition within 1 hour. This event is reportable as a condition prohibited by Technical Specifications. <br /><br /> This event was caused by an inappropriate action resulting from a failure to recognize that the channel was required to be placed in bypass during the surveillance test. The inoperable channel bistables were placed in bypass when the error was realized. Since the other three Steam Generator 2 low pressure channels were within specification, this event did not result in an increased risk to the health and safety of the public or plant personnel.
3821991002 | Waterford 3 | 02/21/1991 | 03/25/1991 | 9103270321 | <strong>Inadvertent Control Room Outside Air Isolation due to Equipment Malfunction</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1991, Waterford Steam Electric Station Unit 3 experienced an unplanned actuation of the Engineered Safety Feature (ESF) portion of the control room ventilation system. The actuation was initiated by a high alarm from one of the four normal Control Room Outside Air Intake (CROAI) radiation monitors, resulting in a control room isolation. Due to the ongoing performance of Operating Procedure 903-051, Control Room Emergency Filtration Unit Operability Check, a Control Room Emergency Filtration Unit was already in service. All other CROAI radiation monitors were indicating normal radiation levels and air samples taken in the area of the alarming radiation monitor showed no detectable activity. This event is reportable as an unplanned ESF actuation. <br /><br /> The root cause of this actuation was equipment malfunction of the CROAI radiation monitor caused by a perforation in the beta radiation window light shield. The beta radiation window light shield was replaced and the CROAI was returned to service. A unit availability investigation will be conducted to evaluate beta radiation light shield failures. In this event, the Control Room Emergency Filtration System functioned as designed and there was no actual release of radioactive material; therefore, this event did not result in an increased risk to the health and safety of the public or plant personnel.
3821991003 | Waterford 3 | 03/14/1991 | 04/15/1991 | 9104180176 | <strong>Improper Testing of the Main Steam Safety Valves due to Incorrect Vendor Supplied Data and Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1991, Waterford Steam Electric Station Unit 3 was operating at 96% power when a review of vendor supplied technical data used for Surveillance Testing of the main steam safety valves (MSSVs) revealed that incorrect data had been used to test the valve setpoints on previously performed tests. The error in data reduced the valve setpoints by approximately 11 pounds per square inch and could have possibly exceeded the Technical Specification (TS) required setpoint tolerance of +/- 1% of the valve setpoint pressure on some of the valves. <br /><br /> The review also revealed that prior to Refuel 2, the number of MSSVs were not tested in accordance with TS Surveillance requirements. Both events are reportable as operation prohibited by plant TS. <br /><br /> All 12 MSSVs were tested properly prior to Refuel 4 and currently have the proper setpoint. The design basis of the MSSVs to provide over pressure protection was maintained throughout these events; therefore, these events did not result in an increased risk to the health and safety of the public or plant personnel.
3821991004 | Waterford 3 | 04/04/1991 | 05/03/1991 | 9105070198 | <strong>Failure to Complete Technical Specification Surveillance due to Inadequate Attention to Detail</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1991, Waterford Steam Electric Station Unit 3 was in Mode 6, Refuel 4, when the Technical Specification Surveillance OP-903-099, Spent Fuel Handling Machine Operability, was not performed satisfactorily. The acceptance criteria for the surveillance was not completed within 72 hours prior to the start of fuel movement. Technical Specification 3.9.7, Surveillance Requirement 4.9.7.1 states that the fuel handling machine shall be demonstrated operable within 72 hours prior to the start of fuel assembly movement. Fuel movement began before the supervisor reviewed and approved the surveillance results. Therefore, the plant operated in a condition prohibited by Technical Specifications. <br /><br /> The root cause of this event is inadequate attention to details. Technical Specification Requirement 4.9.7.1, to perform the surveillance within 72 hours prior to the start of fuel assembly movement, was not properly completed. To prevent recurrence, the individual who performed the surveillance was counseled on the requirements of procedure OP-903-099 and Technical Specification 3.9.7. Because the fuel handling machine was subsequently tested satisfactory and demonstrated operable, this event did not threaten the health and safety of the general public or plant personnel.
3821991005 | Waterford 3 | 05/05/1991 | 06/04/1991 | 9106070238 | <strong>Shutdown Cooling Malfunction due to Ineffective Work Controls</strong><br /><i>Abstract:&nbsp;</i>At 1656 hours on May 5, 1991, Waterford Steam Electric Station Unit 3 was in Mode 5, when a Shutdown Cooling System (SDC) malfunction occurred on the operating 'B' train. Operating Procedure OP-901-046, Shutdown Cooling Malfunction, was entered. Low Pressure Safety Injection (LPSI) pump 'B', which provides flow for the SDC 'B' train, was discovered to be air bound. SDC flow was restored on the SDC 'A' train at 1715 hours. This event is reportable as a single cause or condition which caused an independent train to become inoperable for a system designed to remove residual heat. <br /><br /> The loss of SDC occurred when the bonnet from SI 512A (high pressure safety injection to reactor coolant loop 1 hot leg check valve) was removed as part of planned maintenance. The root cause of this event is that a collective decision was made to repair SI 512A without technical basis. The potential to disrupt the loop seal between the reactor and the LPSI pump 'B' was not realized in the decision to repair SI 512A.<br /><br /> Operator action quickly identified the SDC malfunction and restored SDC capability within 19 minutes of the event initiation, limiting the change in core exit thermocouple temperature to 10 degrees Fahrenheit (F) with a maximum temperature of 110 degrees F. Therefore, this event did not result in any increased risk to the health and safety of the public or plant personnel.
3821991007 | Waterford 3 | 05/10/1991 | 06/10/1991 | 9106120214 | <strong>Incorrect Electronic Current Sensor Rating on a 480 V Safety Related Bus due to Improper Architect Engineer Review</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1991, Waterford Steam Electric Station Unit 3 was shutdown in Mode 5, when a review of calculation EC-E89-007, Relay Settings and Coordination Curves for 6.9 KV, 4.16 KV and 480 V Busses, revealed that the electronic current sensor (ECS) current transformer (CT) rating installed on Motor Control Center Bus (MCC) 3AB311-S was 300 amps vice the required 600 amps. <br /><br /> MCC 3AB311-S supplies power to equipment necessary to run the "AB" essential services chiller. The potential for MCC 3AB311-S to exceed 300 amps existed in the event of a loss of off-site power with the main turbine tripped. The subsequent automatic restoration of electrical loads could have resulted in the MCC 3AB311-S breaker opening due to an overcurrent condition. This event is reportable as a condition which could have caused one train to become inoperable for systems designed to remove residual heat or shutdown the reactor and maintain it in a safe shutdown condition.<br /><br /> The root cause of this event was a failure of the architect engineer to properly verify CT amperage ratings, in accordance with design calculations, when the CTs were ordered for initial installation. Corrective action included installing the proper rated CT and verifying safety related buses for correct CT rating. Since another train would have been available during the scenario discussed above, this event would not have threatened the health and safety of the general public or plant personnel.
3821991008 | Waterford 3 | 05/17/1991 | 01/20/1992 | 9201230248 | <strong>Reactor Coolant System Leakage in Excess of Technical Specifications due to Check Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>At 1335 hours on May 17, 1991, with Waterford Steam Electric Station Unit 3 in Hot Shutdown (Mode 4), an Unusual Event was declared due to Reactor Coolant System (RCS) leakage from Pressurizer Spray Check Valve RC-303, in excess of Technical Specification (TS) requirements. TS 3.4.5.2(d) requires RCS leakage to be less than 10 gallon per minute (gpm). The leakage from RC-303 was calculated to be approximately 20 (gpm), requiring plant shutdown to Cold Shutdown (Mode 5) per TS's. During this event, TS 3.0.3 was entered due to closing the Safety Injection Tank (SIT) outlet isolation valves. <br /><br /> The root cause of this event is underdeveloped training on pressure seal valve installation. Corrective actions are to train Mechanical Maintenance personnel on pressure seal valve installation and to revise the pressure seal valve technical manual to include more detailed information on pressure seal gaskets. After RC-303 began to leak, RCS pressure and temperature was reduced, containment was evacuated, and RC-303 was repaired; therefore, the health and safety of the public was not jeopardized.
3821991009 | Waterford 3 | 05/21/1991 | 06/25/1992 | 9207070328 | <strong>Safety Injection Tank 1A and 1B Inoperable due to Relief Valve Malfunction</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1991, the plant was shutdown in Mode 3 at a Reactor Coolant System (RCS) pressure and temperature of 2250 psia and 540 degrees Fahrenheit, respectively. Safety Injection Tank (SIT) 1A was out of service due to an inoperable nitrogen relief valve. At 1411 hours the relief valve for SIT 1B lifted, lowering SIT 1B pressure below 600 psig. The resulting condition of two SITs inoperable under the existing plant conditions is reportable under 10CFR50.73 (a) (2) (i) as a condition prohibited by technical specifications (TSs) (entry into TS 3.0.3). <br /><br /> RCS pressure was lowered to less than 1750 psia, SIT 1A and 1B were declared operable, and Technical Specification 3.0.3 was exited. The relief valves for SIT 1A and 1B were later removed, tested, and returned to service. <br /><br /> The most likely root causes of this event were equipment malfunction due to abnormal vibration of the relief valve or valve tailpiece when agitated by scaffolding movement, and Equipment Design due to the installed SIT relief valves did not meet the specified blowdown criteria. <br /><br /> This agitation resulted in the spurious opening of the SIT 1A and 1B relief valves at a pressure lower than the required setpoint. Due to the prompt actions of operations personnel to place the plant in a stable condition in which the SITs were all operable, there was no danger to the health and safety of the general public or site personnel.
3821991010 | Waterford 3 | 05/26/1991 | 06/25/1991 | 9106270365 | <strong>Reactor Trip due to Plant Protection System Actuation During Annunciator Ground Isolation</strong><br /><i>Abstract:&nbsp;</i>At 0102 hours on May 26, 1991, an automatic reactor trip of Waterford Steam Electric Station Unit 3 occurred while in Start-up (Mode 2) at 0% power. The trip was initiated by the Plant Protection System in response to high log power on channels C and D. This event is reportable as a unplanned actuation of an Engineered Safety Feature under 10 CFR 50.73(a)(2)(iv). <br /><br /> The root cause of this event was the isolation of grounds on the main annunciator system during low power operation, which introduced electrical noise into the excore log power circuitry. Just prior to the reactor trip, Electrical Maintenance Technicians were troubleshooting the main annunciator system by isolating grounds to various power supplies. Upon isolating the grounds, a spurious signal was introduced into the log power circuitry, and the plant tripped on high log power. <br /><br /> Immediate corrective actions were taken to caution tag the annunciator cabinets to prohibit isolation of grounds while at a power level below the log power trip setpoint of .257% Long term action to prevent recurrence involves revising ME-004-455 to include a caution to prevent isolation of grounds below the log power trip setpoint. Because the plant protective features functioned as designed, the health and safety of the general public and plant personnel were not affected by this event.
3821991011 | Waterford 3 | 05/28/1991 | 08/08/1991 | 9108140164 | <strong>Reactor Trip Due to Faulty Relay</strong><br /><i>Abstract:&nbsp;</i>At 0809 hours on May 28, 1991, the Waterford Steam Electric Station Unit 3 main turbine was manually tripped due to a loss of governor control. After the turbine trip, an automatic reactor trip occurred when the electrical bus powering two reactor coolant pumps failed to transfer from the unit auxiliary transformers to the startup transformers upon loss of the main turbine. During the subsequent transient, a Main Steam Isolation Signal actuation occurred. This event is being reported as unplanned actuations of engineered safety features. <br /><br /> The root cause of this event was a faulty relay that prevented the electrical bus transfer. A contributing cause to this event was an inadequate procedure that, during troubleshooting of the main turbine digital electro hydraulic system, caused the loss of governor control. Another contributing cause to this event was a ground in a maintenance cabinet that caused main turbine load fluctuations. The faulty relay was replaced, the procedure revised and the cause of the ground removed. Plant protective features functioned as designed; therefore, this event did not threaten the health or safety of the general public or plant personnel.
3821991012 | Waterford 3 | 06/21/1991 | 07/22/1991 | 9107240144 | <strong>Failure to Perform Emergency Diesel Generator Surveillance due to Inadequate Attention to Detail</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1991, Waterford Steam Electric Station Unit 3 was operating at 100% power with the 'A' Emergency Diesel Generator (EDG) inoperable. The 'A' EDG had been declared inoperable due to Essential Service Chiller 'A' being secured for maintenance at 1638 hours on June 21, 1991. Technical Specification (TS) 3.8.1.1 was entered, requiring verification of offsite AC power availability within one hour of declaring the 'A' EDG inoperable and every eight hours thereafter. A review of the control room logs revealed that the one hour requirement was not complied with until 2223 hours on June 21, 1991. Similar conditions existed on June 20, 1991, from 0855 hours to 1122 hours, and from 1306 hours to 2101 hours. Therefore, the plant operated in a condition prohibited by TSs. <br /><br /> The root cause of this event is inadequate attention to detail. The Control Room Supervisor (CRS) failed to perform the action requirements of TS 3.8.1.1, resulting in a failure to perform the required surveillance. The CBS involved was debriefed on this event and a procedure will be issued to provide additional guidance on TS compliance. <br /><br /> Because offsite AC electrical power was verified available at 2223 hours on June 21, 1991, and existed throughout the event, no threat to the health & safety of the public or plant personnel existed.
3821991013 | Waterford 3 | 06/24/1991 | 11/15/1991 | 9111200183 | <strong>Manual Reactor Trip in Response to High Steam Generator Water Level Due to a Failed Startup Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>At 1315 hours on June 24, 1991, the reactor at Waterford Steam Electric Station Unit 3 was manually tripped due to high water level in Steam Generator (SG) #2. Four SG #2 high level reactor pre-trip alarms were received prior to manually initiating a reactor trip. A main steam isolation signal was manually actuated subsequent to the reactor trip as a result of excessive cool down rate. This event is reportable as an unplanned reactor protection system actuation. <br /><br /> The root cause of this event is SG #2 startup feedwater regulating valve failing open while at approximately 25 percent reactor power. A process analog control (PAC) card in the valve control circuitry failed, resulting in a constant open signal to SG #2 startup feedwater regulating valve. The PAC card was replaced and PAC card performance will be trended as part of the Long Term Reliability Program. Plant protective features functioned as designed; therefore, this event did not threaten the health or safety of the general public or plant personnel.
3821991014 | Waterford 3 | 06/27/1991 | 07/29/1991 | 9107310344 | <strong>Main Feed Isolation Valve Inoperable due to Accumulator Leak</strong><br /><i>Abstract:&nbsp;</i>At 0540 hours on June 27, 1991, Operations personnel identified a low nitrogen (N2) pressure indication on Main Feedwater Isolation Valve (MFIV) 184B, accumulator(ACC) 'B'. Instrumentation and Control Maintenance performed a N2 precharge pressure check and found the N2 pressure on ACC 'B' to be 40 psig. A subsequent check of ACC 'A' indicated a N2 precharge pressure reading of 2200 psig. Both N2 ACC for MFIV 184B were less than 2500 psig precharge, therefore, MFIV 184B was inoperable greater than 4 hours exceeding the action requirement of Technical Specification (TS) 3.6.3. The plant operated in a condition prohibited by TS. <br /><br /> The root cause of this event was N2 leakage from both MFIV 184B ACC. A contributing cause was the difficulty of accurately indicating low N2 precharge pressure. Corrective action taken was to recharge the MFIV 184B ACC. Long term corrective actions include an investigation of modifications to allow more accurate N2 ACC precharge pressure readings and the issuance of a standing instruction change for monitoring MFIV's hydraulic fluid level and N2 precharge pressure. Added protection of a Main Feed Regulating Valve and a Start-Up Regulating Valve, which both receive a Main Steam Isolation Signal to close, and a check valve in the main feedwater piping, isolation of the steam generators would be accomplished, if necessary, therefore; this event did not threaten the health and safety of the public or plant personnel.
3821991015 | Waterford 3 | 07/16/1991 | 08/05/1991 | 9108090165 | <strong>Failure to Stroke BD-103B When Restoring to Service due to a lack of Procedural Compliance</strong><br /><i>Abstract:&nbsp;</i>At 0800 hours on July 16, 1991, Waterford Steam Electric Station Unit 3 was operating at 100% power. Work had commenced to adjust the packing on Steam Generator Blowdown Containment Isolation Valve BD-103B. Limiting Condition for Operation 3.6.3 was in effect since the valve was inoperable, requiring the inoperable valve to be returned to operable status or the affected penetration isolated within 4 hours. Technical Specification (TS) 3.6.3 requires that each affected valve be stroked and timed prior to returning the valve to service. BD-103B was not tested prior to placing the valve in service and TS 3.6.3 requirements were not satisfied until 2146 on July 16, 1991 when the Operations Procedure 903-032 retest was completed. <br /><br /> The root cause of this event was a lack of procedural compliance. Upon granting permission for maintenance workers to adjust packing on BD-103B, the shift supervisor failed to enter BD-103B in the equipment out of service log and enter TS 3.6.3 to properly track the TS requirements for returning BD-103B to operable status. Since BD-103B was later tested satisfactorily, the valve would have performed its required function; therefore, this event did not threaten the health or safety of the public or plant personnel.
3821991016 | Waterford 3 | 07/20/1991 | 08/19/1991 | 9108230106 | <strong>Incore Detection System Inoperable due to Multiplexer Update Inadequacy</strong><br /><i>Abstract:&nbsp;</i>At 0755 hours on July 20, 1991, Operations personnel identified that inaccurate data was transmitted from Auxiliary Protection Cabinet Multiplexer (APCMUX) C to the Plant Monitoring Computer (PMC) from 0157 to 0730 hours, resulting in a total of 30% incore detectors (IDs) being inoperable. The data involved inputs from various IDs to the APCMUX C. Technical Specification (TS) 3.3.3.2 requires at least 75% of IDs to be operable for the incore detection system to be operable. <br /><br /> Because the PMC used data from the IDs for monitoring functions for the Core Operating Limit Supervisory System (COLSS) when the APCMUX C was malfunctioning, contrary to the action requirement a. of TS 3.3.3.2, the plant operated in a condition prohibited by TS. <br /><br /> The root cause of this event was the inability of the PMC to identify non-updated data being transmitted from the APCMUX. Corrective actions include an hourly verification of inputs to the PMC to ensure that updated data is transmitted to the PMC. An alarm to notify the control room of APCMUX information not being updated will be installed. Although COLSS was inaccurate, the Core Protection Calculators, which provide input to the plant protection system, were functioning properly; therefore, this event did not threaten the health and safety of the public or plant personnel.
3821991017 | Waterford 3 | 08/08/1991 | 09/09/1991 | 9109110152 | <strong>Operation in Technical Specification 3.0.3 for Inaccurate Safety Injection Tank Pressure Indication due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1354 hours August 8, 1991, Waterford Steam Electric Station Unit 3 was operating at 100% power while investigating abnormal readings associated with Safety Injection Tank (SIT) 2B pressure transmitter. While draining the sensing line for SIT 2B pressure transmitter, approximately 0.31 gallons of water was found. SIT 2B pressure had dropped to between 590 and 600 psig upon draining the water so Technical Specification (TS) 3.5.1 was entered and SIT 2B pressure was restored to within acceptable limits. Shortly thereafter, a similar sequence of events occurred on SIT IA pressure transmitter. The minimum pressure reached during the SIT 1A evolution was between 590 and 600 psig with approximately 0.33 gallons of water drained. During the described evolution, the plant was discovered to be operating in a TS 3.0.3 condition. In addition, it is possible that the plant has operated in a similar condition at various times since Refueling Outage 4.<br /><br /> The root cause of the water in the pressure transmitter sensing lines is an inadequate procedure. Operating Procedure (OP)-009-008 did not properly require draining of SIT pressure transmitter sensing lines after draining SIT's from a 100% filled condition. OP-009-008 will be revised to require sensing lines to be drained when draining SIT's from 100%. All other SIT pressure transmitters have been checked free of water and restored to normal operation.
3821991018 | Waterford 3 | 11/02/1989 | 09/13/1991 | 9109180145 | <strong>Outside Design Basis Due to An Inadequate Procedure Concerning ASME Section XI Class Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1991, during the ASME Section XI closure review of a work authorization an ASME Class 3 wafer disc was discovered to have been inadvertently installed in containment isolation valve CC-710. The wafer disc for this valve is required to meet ASME Class 2 qualification criteria. The inadequately qualified wafer disc was installed on November 2, 1989. This event is reportable as operation in a condition that was outside the design basis of the plant. <br /><br /> The root cause of this event is an inadequate maintenance procedure. Administrative Procedure MD-01-022, "Section XI Repairs and Replacements," does not adequately address pre-implementation work package review for ASME Section XI Class requirements for replacement parts. MD-01-022 will be revised and an ASME Class 2 wafer disc will be installed in CC-710.
3821991019 | Waterford 3 | 08/25/1991 | 09/24/1991 | 9109270191 | <strong>Inadvertent Multiple Engineered Safety Feature Actuation due to Test Circuit Malfunction</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1991, at 0214 hours while performing OP-903-107, Plant Protection System Functional Test, the plant received a Safety Injection Actuation Signal (SIAS), Containment Isolation Actuation Signal (CIAS), and Main Steam Isolation Signal (MSIS). Subsequently, a Reactor Trip occurred on loss of power to the Control Element Drive Mechanism motor generator sets due to the SIAS. Operations Control Room personnel entered the Emergency Operating Procedures and carried out the immediate operator actions. Recovery was performed in accordance with OP-902-006, Loss of Main Feedwater Procedure. The root cause of the event was an unforseen design problem. When the Matrix Relay Hold pushbutton (Cutler-Hammer Model #10250T506) was pushed, the speed of insertion was rapid enough such that the energization of the test coils occurred before the energization of the hold coils, resulting in an actuation of the SIAS, CIAS, and MSIS functions under test. A modification is being considered by System Engineering to replace the pushbutton with a three 3) position spring return handswitch.
3821991021 | Waterford 3 | 10/16/1991 | 11/15/1991 | 9111200186 | <strong>Safety Injection Tank Level Below Technical Specifications due to Low Reference Leg Level</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1991, Safety Injection Tank (SIT) 1A narrow range instrument SI ILT 0313 indicated a lower SIT level than the other two SIT level detectors and was placed out of service at 1106 hours. On October 17, 1991, after a review of SIT level trend data, Instrumentation & Control informed Operations that SI ILT 0313 may have displayed the correct SIT 1A level and that the other SIT 1A level detectors, SI ILT 0311 and SI ILT 0312, may indicate erroneously high SIT levels. While SI ILT 0313 was out of service, SIT 1A level fell below Technical Specification (TS) limits. <br /><br /> The root cause of this event was leakage of the common reference leg for SI ILT 0311 and SI ILT 0312. Since the plant was operated in a condition outside the design basis of the plant, at 1319 hours on October 17, 1991 operators made a 1-hour non-emergency event notification. This event is reportable under 10 CFR 50.73, operation or condition prohibited by plant TSs and condition outside the design basis of the plant. SIT 1A level was increased, reference legs filled and instrument valves inspected. Since the difference between the minimum required SIT level and lowest SIT level was slight, Peak Clad Temperatures would be expected to remain within the acceptable bounds of existing analysis; therefore, this event did not threaten the health and safety of the public or plant personnel.
3821991022 | Waterford 3 | 11/17/1991 | 12/17/1991 | 9112230239 | <strong>Inadvertent Engineered Safety Feature Actuations due to Plant Protection System Test Circuit Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 0324 hours on November 17, 1991, while performing OP-903-107, Plant Protection System Functional Test, the plant received a Safety Injection Actuation Signal (SIAS), Containment Isolation Actuation Signal (CIAS), and Main Steam Isolation Signal (MSIS). Subsequently, a reactor trip occurred on loss of power to the Control Element Drive Mechanism motor generator sets due to the SIAS. Operations Control Room personnel entered the Emergency Operating Procedures and carried out the immediate operator actions. Recovery was performed in accordance with OP-902-006, Loss of Main Feedwater Procedure. Inspection of the test cabinet revealed a loose wire connection in the CD matrix test circuitry. The loose wire connection was tightened and a system retest was performed satisfactorily. <br /><br /> The cause of this event was a test circuit malfunction which was caused by a loose connection on TB701 Terminal 2. The cause of the loose connection could not be positively determined and may have existed for some time. Waterford 3 is implementing a design change to install test circuit enhancements.
3821991023 | Waterford 3 | 12/20/1991 | 01/20/1992 | 9201270007 | <strong>Valve out of Position due to Inadequate Position Indication Labeling</strong><br /><i>Abstract:&nbsp;</i>At 2203 hours on December 20, 1991, Waterford Steam Electric Station Unit 3 was operating at 100% power when a Nuclear Auxiliary Operator (NAO) discovered component cooling valve CC-304 A, cross connect inlet to AB chiller, open. This valve misposition was identified while verifying positions of accessible locked valves per OP-100-009, Control of Valves and Breakers. Investigation determined that the valve was operated on December 1, 1991, at 1528 hours while replacing the B chiller with the AB chiller, requiring CC-304 B open and CC-304 A closed. With CC-304 A and B open, Component Cooling Water (CCW) loops A and B were cross connected at the inlet of the chillers. This cross connection defeats the two redundant, separate train design and results in operation of the system outside design basis. <br /><br /> The root cause of the event was inadequate position indication labeling of CC-304 A. The inadequate labeling caused a misinterpretation of the valve actual position, allowing the valve to be mispositioned. Contributing to the event was the inappropriate action taken by three operators who intended on two separate occasions to correctly position or check the position of CC-304 A.
3871991001 | Susquehanna 1 | 02/08/1991 | 03/07/1991 | 9103110269 | <strong>Isolation Pressure Switch Operation Prohibited by Tech Spec During Retest</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1991, with Unit 1 operating at 100% power, a surveillance test was being performed on isolation actuation instrumentation. (EIIS Code: I). During the calibration, it was observed that contacts in a pressure switch (PS) exhibited chattering just before the trip signal sealed in. The PS setpoint was within the acceptance criteria of the procedure but it was decided that replacement of the switch was required. <br /><br /> The switch was declared inoperable and the associated channel was placed in the trip condition as required by Technical Specifications. In order to perform a post-replacement surveillance, the affected channel had to be reset. With the channel taken out of the tripped condition, the ACTION statement was no longer met and because Tech Specs do not recognize or allow this action, LCO 3.0.3 action was entered. This entry into 3.0.3 constitutes an operation prohibited by Tech Specs. The affected channel was successfully retested and LCO 3.0.3 action was cleared in one half hour. The cause of the relay chattering could not be determined. The replacement switch will be monitored for similar behavior during the next surveillance. This action is considered adequate since the condition does not seem to detrimentally affect the function of the PS. This event was determined to be reportable per 10CFR50.73 (a)(2)(i)(B), in that a condition prohibited by Tech Specs existed while the channel was removed from the tripped condition. The Tech Specs contain no provision for allowing a trip signal, imposed by action requirements, to be reset for performance of surveillance tests necessary to restore operability. Such provisions are considered necessary and are being pursued.
3871991002 | Susquehanna 1 | 02/07/1991 | 03/11/1991 | 9103150241 | <strong>HPCI System Declared Inoperable Due to Failure of Outboard Steam Supply Line Isolation Valve to Stroke Open</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1991 with Unit 1 operating in Condition 1 at 100% power, the HPCI Outboard Steam Supply Line Isolation Valve failed to open during a routine valve exercising surveillance test. After further attempts to open the valve were unsuccessful, HPCI was declared INOPERABLE. The event has been determined to be reportable per 10CFR50.73(a)(2)(v) in that the inoperability of HPCI is a loss of a single train safety system. A few hours later the valve was successfully opened even though no corrective maintenance had been performed. The cause of this event was unable to be determined although there was an apparent intermittent malfunction in the valve open control circuit which has not repeated. Extensive inspections of the control circuit wiring, relays, and terminations were completed and no discrepancies were found that could explain the event. The valve has been stroked successfully a number of times since the event. However, the frequency for the valve exercising surveillance test for this valve will be increased to monthly for the next quarter to ensure proper operation.
3871991003 | Susquehanna 1, Susquehanna 2 | 02/14/1991 | 05/02/1991 | 9105070218 | <strong>Fire Damper Not Installed in Fire Rated Barrier</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1991 with Unit 1 and Unit 2 operating in Condition 1 at 100% and 99% power respectively, it was identified that a fire rated damper was not found in a fire rated barrier which is required to meet Technical Specification 3.7.7, and since it cannot be confirmed that a continuous firewatch was in place to meet the action statement for this Technical Specification during the entire time the damper was missing, it was determined that the condition constituted an operation prohibited by the Technical Specifications. A continuous firewatch was established. This condition is being evaluated to determine the requirement for this fire barrier. The initial evaluation appeared to indicate that this fire barrier was not required. Further evaluation has verified that this fire barrier does not separate redundant safe shutdown equipment or cables, has no effect on the safe shutdown analysis, and does not protect safety related equipment. Based upon this analysis, no operation prohibited by the Technical Specifications existed.
3871991004 | Susquehanna 1 | 03/21/1991 | 04/22/1991 | 9104250400 | <strong>ESF Actuations Due to RPS EPA Breakers Spurious Trip</strong><br /><i>Abstract:&nbsp;</i>At 1415 hours on March 21, 1991 with Unit 1 operating at 100% power, the primary power supply to the "A" Reactor Protection System (RPS) power distribution panel was lost when its Electrical Protection Assembly (EPA) breakers tripped. This interruption of power to "A" RPS, per design, caused Reactor Building HVAC Zones I and III, the Reactor Water Cleanup System, and various other Primary Containment Isolation System components to isolate and the Standby Gas Treatment System and Control Room Emergency Outside Air Supply System to auto initiate. All plant systems and components functioned properly and as expected in response to the event. No reactor parameters were affected and no Emergency Core Cooling Systems were actuated. The EPA breakers were reset at 1420 hours with no indication of abnormalities and all isolation signals were reset by 1502 hours. Full power operation of the unit continued without interruption. <br /><br /> The cause of the breaker trip will be investigated during the next unit outage. An EPA study prepared by GE - Nuclear Energy for the BWR Owners Group is currently under PP&L review to assess any operational or design changes that may be warranted. LER 90-007 (Docket No. 50-388/License No. NPF-22) will be updated to provide the results of this assessment. <br /><br /> Since all Engineered Safety Feature (ESF) systems and components functioned properly and per design, there were no safety consequences or compromises to the health or safety of the public.
3871991006 | Susquehanna 1 | 06/08/1991 | 07/05/1991 | 9107100328 | <strong>ESF Actuations Due to RPS EPA Breakers Spurious Trip</strong><br /><i>Abstract:&nbsp;</i>At 2331 hours on June 8, 1991 with Unit 1 operating at 100% power, the primary power supply to the "A" Reactor Protection System (RPS) power distribution panel was lost when its Electrical Protection Assembly (EPA) breakers tripped. RPS as well as other Plant systems and components functioned properly and as expected in response to the event. No reactor parameters were affected and no Emergency Core Cooling Systems were actuated. The 'A' distribution panel was swapped to alternate power until the primary power supply was restored. There was no indication of abnormalities and all isolation signals were reset by 0042 hours on 6/9/91. The primary power source EPA breakers were reset at 1430 hours on 6/9/91. Full power operation of the unit continued without interruption. While the exact cause of the trip was not definitively determined, the most probable cause for the trip was attributed to a faulty power supply on the EPA logic card. A task team has been organized to enhance the reliability of the Reactor Protection System. In addition, an EPA study prepared by GE - Nuclear Energy for the BWR Owners Group is also under PP&L review to assess any operational or design changes that may be warranted. LER 90-007 (Docket No. 50-388/License No. NPF-22) will be updated to provide the results of the efforts to enhance RPS reliability. Since all Engineered Safety Feature (ESF) systems and components functioned properly and per design, there were no safety consequences or compromises to the health or safety of the public.
3871991007 | Susquehanna 1, Susquehanna 2 | 06/19/1991 | 07/19/1991 | 9107230404 | <strong>'C' Emergency Diesel Start Time Exceeded Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>At 1458 hours on June 1991, with both Unit 1 and Unit 2 in Condition 1 at 100% power, the 'C' Emergency Diesel Generator (EDG) failed to reach Technical Specification required speed, frequency and voltage within the required time of 10 seconds or less during its monthly operability test per Technical Specification surveillance requirement 4.8.1.1.2.a. Measured start time was 24 seconds. The 'C' EDG was declared inoperable and a root cause investigation was commenced. The most probable cause of the slow start was attributed to air entrapment in the fuel supply header which led to slower engine acceleration on fuel oil. The cause of the fuel header air entrapment was attributed to a fuel system flowing vent modification implemented on EDGs 'A' through 'D' in 1990. The modified fuel piping design can potentially result in partial draining of the fuel supply header when the EDG is only run once every 31 days for its monthly operability test. An effective means to vent the air upon startup was not provided by the modification. Since this problem was a potential contributor to a 'D' EDG slow start during a troubleshooting run on 3/25/91, the flowing vents had been re-modified on that engine and were to be implemented as a precautionary measure on 'A', 'B' and 'C' EDGs at their next inspection outage. These re-modifications have been completed on 'A' and 'C' and will be implemented on the 'B' EDG by August 16, 1991. Until implementation, the 'B' EDG is being tested once every 15 days as a prudent measure. The 'C' EDG is being tested once every 7 days per Tech Spec Table 4.8.1.1.2-1. There were no safety consequences or compromise to public health or safety since three EDGs remained OPERABLE as required by the SSES Safety Analysis.
3871991008 | Susquehanna 1, Susquehanna 2 | 07/31/1991 | 08/30/1991 | 9109040364 | <strong>Loss of Offsite AC Circuit Caused Unit Scram and MSIV Isolation</strong><br /><i>Abstract:&nbsp;</i>At 1034 hours on July 31, 1991, with Unit 1 and Unit 2 operating at 100% power, a RPS SCRAM and MSIV isolation occurred on Unit 1 when a switchyard fault detection relay mis-operated resulting in de-energization of one of Susquehanna's offsite AC circuits coincident with a pre-existing half-scram/half MSIV isolation signal condition. Unit 2 experienced a half-scram as a result of the loss of the offsite AC circuit. Both Units automatically responded to the transient as designed including an ECCS injection by the HPCI system and SRV actuations on Unit 1. Subsequent Unit 1 ESF actuations occurred: RPS logic actuations during control of reactor level and pressure by Operators; RWCU isolation during restoration; and automatic swap of HPCI suction supply on high suppression pool level. The following conditions prohibited by the plant's Technical Specifications occurred on Unit 1: A reactor level indicating switch was determined to have been inoperable in excess of the required LCO Action time; a reactor coolant sample could not be obtained in the required time period; shutdown cooling was not established within 1 hour of meeting the pressure permissive; and COLD SHUTDOWN was not achieved within 24 hours after entering Tech Spec 3.4.6.1 Action. Unit 1 was stabilized in accordance with the Emergency Operating procedures and brought to COLD SHUTDOWN. The half-scram condition on Unit 2 was reset. An Event Review Team performed root cause investigations for all transient and recovery related issues. Corrective actions include hardware replacement, procedure revisions, personnel training and a review of offsite power switchyard operation and communications relative to effects on Susquehanna operation. At no time were there any safety consequences or compromise to public health or safety.
3871991009 | Susquehanna 1 | 07/31/1991 | 08/28/1991 | 9109040328 | <strong>Operation Prohibited by Technical Specification During Radiation Monitor Retest</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1991 with Unit 1 operating at 100% power, the 'B' Main Steam Line Radiation Monitor failed resulting in actuation of the 'B' Division of the Reactor Protection and Main Steam Isolation Systems. Investigation revealed that a capacitor in the monitor power supply had failed causing the loss of the monitor and the associated trips. The defective capacitor was replaced and the power supply for the monitor was restored. In order to perform the post-maintenance required surveillance, the affected channel had to be reset (i.e. - taken out of the tripped condition). With the channel taken out of the tripped condition, the ACTION Statement was no longer met and as a result, Technical Specification 3.0.3 was entered. The surveillance test was then successfully completed. The entry into Technical Specification 3.0.3. constituted operation prohibited by the Technical Specification since they do not recognize or allow this action of removing Technical Specification imposed trips from the tripped condition for performance of post-maintenance surveillance testing. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications. There were no safety consequences or compromises since only one channel of one division of the trip system was affected and since it failed to the safe (tripped) condition. The defective radiation monitor was repaired and the logic channel was tested satisfactorily. The power supply failure was attributed to a capacitor failed in a power supply card. We are pursuing a change to our Technical Specification to allow resetting trip signals in order to perform required surveillance testing following maintenance.
3871991010 | Susquehanna 1 | 08/05/1991 | 09/03/1991 | 9109090261 | <strong>ESF Actuations Resulted When Reactor Mode Switch was Inadvertently Placed in Run Rather Than Startup/Hot Standby</strong><br /><i>Abstract:&nbsp;</i>At 1520 hours on August 5, 1991 Unit 1 was in Condition 4, Cold Shutdown, and was preparing to enter Condition 2, Startup. When the Plant Control Operator attempted to place the reactor mode switch in Startup, the switch was inadvertently placed in Run. This resulted in the generation of a Main Steam Isolation Valve (MSIV) isolation signal due to low steam line pressure coincident with the mode switch in Run. This in turn caused a Reactor Protection System (RPS) actuation. No control rod or valve motion resulted. All rods were fully inserted prior to the event and all valves expected to close on the MSIV isolation signal were in the closed position. The root cause of this event is cognitive personnel error. Contributing to the error was the indication provided by the reactor mode switch key. The key indicated that the mode switch was in Startup/Hot Shutdown when it was actually in Run due to a bend in the key. This event was determined to be reportable per 10CFR50.73(a)(2)(iv), in that generation of a MSIV isolation signal and actuation of RPS constituted unplanned ESF actuations. There were no safety consequences or compromise to the public health or safety as a result of this event. The reactor mode switch key has been reworked and is indicating properly. The key will be replaced upon receipt of new mode switch keys from the vendor. In addition, this event will be reviewed by all Licensed personnel.
3871991011 | Susquehanna 1, Susquehanna 2 | 08/19/1991 | 09/18/1991 | 9109200160 | <strong>Unsealed Openings In Fire Rated Barriers</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1991 with Unit 1 and Unit 2 operating in Condition 1 at 100% power, it was identified that openings existed in fire rated barriers in the Control Structure which are required to meet Technical Specification 3.7.7, and since it cannot be confirmed that appropriate compensatory measures were in place to meet the action statement for this Technical Specification at all times, it was determined that the condition constituted an operation prohibited by the Technical Specifications. Operability of the fire detection on at least one side of the fire barrier was confirmed and an hourly firewatch was established. All similar locations were inspected for this condition. These openings will be sealed to assure integrity of the fire rated barrier.
3871991012 | Susquehanna 1, Susquehanna 2 | 10/07/1991 | 11/06/1991 | 9111140048 | <strong>Valves Not Surveillance Tested - Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, with both Units 1 & 2 at 100%, it was discovered that certain manual containment boundary valves were not included in required surveillance procedures. This condition was discovered during a periodic review of the procedure. The subject valves are normally locked closed test connection valves and were in fact in this configuration. Several causes were determined for this event. The first was personnel error during the initial preparation of the procedure for the valves in the RHR System. Concerning the valves in the CRM System, one cause was attributed to not including all applicable disciplines in the installation and/or closeout review process of the modification. Another cause was the methods utilized by operations during the modification closeout review process. The event was determined to be reportable per 10CFR50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specification in that surveillances were not performed as required by Technical Specification 4.6.1.1.b. There were no safety consequences or compromises as a result of this condition since the valves remained in the required locked closed position. Necessary surveillance procedure changes have been completed and the Operations section and Systems Engineering group are reviewing their present procedural guidance for enhancements to prevent recurrence of this type of event.
3871991013 | Susquehanna 1, Susquehanna 2 | 10/18/1991 | 11/18/1991 | 9111250036 | <strong>Pottnt.al For Pressure - Locking of RHR LPCI and Core Spray System Injection Valves</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1991, with both Unit 1 and Unit 2 in Condition 1 at 100% power, PP&L Engineering determined that a susceptibility to a motor-operated valve pressure-locking phenomenon exists for the Residual Heat Removal - Low Pressure Coolant Injection System (RHR-LPCI) and Core Spray System injection valves. Based on PP&L's operability evaluation, this deficiency has no impact on the continued safe operation of the Susquehanna units since the injection valve response times remain well within those required by the accident analyses contained in the FSAR. Although the overall system response time limits are not affected, the margin of safety is reduced. Per a prior agreement between PP&L and NRC NRR for conditions of this nature, this event is being reported pursuant to 10CFR50.73(a)(2)(ii)(B). PP&L has implemented precautions to provide additional assurance against the potential pressure locking scenarios and is evaluating modifications to resolve the pressure locking concern as well as a schedule for implementation.
3871991014 | Susquehanna 1, Susquehanna 2 | 11/07/1991 | 12/09/1991 | 9112130374 | <strong>RPS Alternate Power Supply EPA Breaker Overvoltage Setpoints Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1900 hours on November 7, 1991 all station alternate Reactor Protection System (RPS) power supply Electrical Protection Assemblies (EPA) were declared inoperable. The cause of the event was due to a "shift" of the EPA overvoltage trip setpoints above Technical Specification limits. The condition was discovered while investigating an EPA breaker trip. During the investigation, a test method not previously employeed was used to check the EPA setpoints. A setpoint "shift" was observed when this method was employeed. The "shift" was the result of using a test source with a near perfect output AC voltage sine wave to calibrate the setpoints then powering the EPAs with supply transformers which produced an output AC voltage sine wave with a slight distortion. The undervoltage and underfrequency setpoints of the alternate EPAs remained within Technical Specification limits,. The normal RPS power supply EPA breakers were not affected by this condition. <br /><br /> All RPS distribution panels remained in service and powered by the normal supplies while the alternate EPA overvoltage setpoints were adjusted to within Technical Specification limits using transformer output as the calibration source. The EPA calibration procedure will be revised to account for the "shift" of the alternate EPA setpoints. No safety consequences or compromises to the health or safety of the public were attributed to the event.
3871991015 | Susquehanna 1 | 11/07/1991 | 08/03/1995 | 9508080351 | <strong>High Pressure Coolant Injection System Inoperable Due to Broken Steam Control Valve Pilot</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1991, with Unit 1 at 100% power, it was determined that the High Pressure Coolant Injection System (HPCI) was inoperable in that the pressure and flow requirements of the Quarterly Flow Surveillance could not be met. Inspection of the turbine steam chest revealed that the head of the #1 poppet (Pilot valve) had broken off. The cause of the broken poppet could not be determined, since it was inadvertently discarded. This event was determined to be reportable per 10CFR50.73(a)(2)(V)(D) as a condition that alone could have prevented the fulfillment of the safety function of the system. However, sufficient safety margin exists in the design such that HPCI could have performed its intended function. The broken poppet was replaced and the other poppets were inspected. The surveillance test was then satisfactorily completed.
3871991016 | Susquehanna 1, Susquehanna 2 | 11/20/1991 | 03/24/1993 | 9303300215 | <strong>Postulated Appendix R Fire Could Place the Plant Outside Its Analyzed Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1991 with both units operating at 100% power, it was determined that a postulated Appendix R fire in the Control Room could place the plant in a condition outside of its analyzed design basis. This condition has been determined to be reportable per 10CFR50.73(a)(2)(ii)(B). The fire could result in a hot short in the control circuit of one of a number of components required to shut down the unit from the Remote Shutdown Panel. Damage to the component could occur. The scenario is applicable to both units. Thirty-nine valves on Unit 1 and forty valves on Unit 2 are affected from the RHR, ESW, RHRSW and RCIC Systems. The postulated condition relates to an oversight in the Appendix R analysis in which the possibility of a malfunction of Path 2 safe shutdown components during a postulated Control Room Appendix R fire was not analyzed. The safety significance is considered minimal because of the low probability of occurrence as well as the fact that backup systems exist that are able to bring the plant to a successful safe shutdown, fire detection and suppression systems are operable in the Control Room, Operations Control Room personnel have been briefed on the scenario and are qualified fire watch/fire brigade personnel having access to portable fire fighting equipment in the Control Room. PP&L has begun a detailed analysis to justify a deviation from the Appendix R requirements for this postulated condition. Upon completion, the request for deviation will be submitted to the NRC for approval. This has previously been stated in a letter to the NRC, PLA-3918, dated February 24, 1993.
3871991017 | Susquehanna 1, Susquehanna 2 | 11/25/1991 | 12/19/1991 | 9112300017 | <strong>Unplanned ESF Actuation When radiation Monitor Power Interrupted</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1991 with Unit 1 at 100% power and Unit 2 at 92% power an unplanned ESF actuation occurred when a fuse blew in the power supply to radiation monitors serving the Zone III ventilation, Standby Gas Treatment, and Control Room Emergency Outside Air Supply systems. The loss of power caused a Zone III isolation and auto-start of the SGTS & CREOASS systems. The blown fuse was replaced and all systems were returned to normal operation. The cause of the blown fuse was attributed to random failure. This event was determined to be reportable per 10CFR50.73(a)(2)(iv), as an unplanned ESF actuation. There were no safety consequences or compromises as a result of this event. All appropriate electrical parameters were checked following fuse replacement.
3881991001 | Susquehanna 2 | 01/08/1991 | 02/07/1991 | 9102130032 | <strong>Inadvertent Isolation of Shutdown Cooling Mode of Residual Heat Removal System</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1991 with Unit 1 in Cold Shutdown, the Residual Heat Removal System, operating in the Shutdown Cooling Mode, automatically isolated while technicians were performing instrument maintenance. Pressure switches were being replaced due to problems with setpoint drift. The cause of the isolation was improper work instructions which required opening links and when these links were opened, the isolation circuitry actuated. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) as an unplanned ESF actuation. There were no safety consequences or compromises to the health or safety of the public or plant personnel. Personnel performing the work immediately restored from the work activity and shutdown cooling was restored to operation. Contributing to the improper work instruction was the failure to use all available drawings. PP&L is developing a work planning guide for Instrument & Controls personnel and appropriate training will be performed on this guide.
3881991002 | Susquehanna 2 | 08/01/1990 | 02/08/1991 | 9102140192 | <strong>HPCI Outboard Steam Supply Containment Isolation Valve Declared Inoperable Due to Incorrect Torque Switch Setting</strong><br /><i>Abstract:&nbsp;</i>At 1715 hours on August 1, 1990, with Unit 2 operating in Condition 1 at 100% power, the High Pressure Coolant Injection (HPCI) steam supply outboard containment isolation valve, HV-255-F003, was declared inoperable due to the closing torque switch being improperly set. As such, Limiting Condition for Operation 3.6.3 Action a was entered. Actions were immediately taken to correct the torque switch setting and the valve was declared operable at 1935 hours. The root cause of the event is cognitive personnel error. During maintenance activities on HV-255-F003, in September 1986, the minimum torque switch setting was changed from 2 1/2 to 2 7/8 as a result of NRC Generic Letter 85-03, however, the calibration chart, located in the valve, was not changed to reflect the new range. During April 1988, the actuator for HV-255-F003 was overhauled. As part of the work plan, direction was given to return the torque switch settings to the minimum setting. With the incorrect calibration chart the torque switch was returned to 2-1/2. The condition is being reported under the provisions of 10CFR50.73 (a) (2) (i) (B) in that containment isolation valve HV-255-F003 was inoperable from April 9, 1988 until August 1, 1990. This determination was made on January 10, 1991 following re-evaluation of an earlier operability/reportability determination. Corrective actions consisted of resetting the torque switch within the required range and replacing the calibration chart. The new procedure governing torque switch settings provides the necessary additional controls to prevent recurrence of this type of event. There were no safety consequences or compromise to the public health and safety as a result of this event.
3881991003 | Susquehanna 2 | 02/26/1991 | 11/12/1992 | 9211200161 | <strong>Isolation Logic Relay - Operation Prohibited by Technical Specification During Retest</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1991 with Unit 2 operating at 95% power, the "Main Steam Isolation Valve Logic A/C Initiated" alarm was received in the Control Room. Investigation revealed the cause to be chattering contacts in a relay in the isolation logic. The affected channel was placed in the tripped condition as required by Technical Specification. The relay was reworked in place but tested unsatisfactorily followed by relay replacement and satisfactory test. In both cases (rework and replacement), the affected channel had to be taken out of the tripped condition to allow surveillance testing. With the channel taken out of the tripped condition, the ACTION Statement was no longer being met and thus Technical Specification 3.0.3 was entered which constituted operation prohibited by Technical Specifications since they do not recognize or allow this action (i.e. resetting Technical Specification imposed trips for performance of post-maintenance required surveillance testing). The relay was found to be out of adjustment which was the cause of the contact chattering. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications. There were no safety consequences or compromise since only one channel of one division of the isolation logic was affected. All other isolation functions remained operable throughout the time period. Evaluating our preventive maintenance program as to the need for improvement of relay preventive maintenance will be pursued as an enhancement to the program. Changes with respect to Technical Specification 3.0.3 will be pursued as part of the NRC generic Technical Specification Improvement Program rather than on an individual plant basis.
3881991004 | Susquehanna 2 | 03/15/1991 | 04/15/1991 | 9104220349 | <strong>Technical Specification Noncompliance During Refueling Bridge Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 1200 hours on March 15, 1991, with Unit 2 in Condition 5, Refueling, Operations personnel completed surveillance SO-281-002, Refueling Platform Main and Auxiliary Hoists Operability. The surveillance requires a control rod to be withdrawn one notch to test OPERABILITY of the Refueling Bridge interlock. Per Tech Spec Limiting Condition of Operation (LCO) 3.1.5, SLC is required to be OPERABLE in Conditions 1, 2, and 5* (* - with any control rod withdrawn). A control rod may be withdrawn with SLC INOPERABLE if the required actions of LCO 3.9.10.1 or 3.9.10.2 are met. When the surveillance was performed the SLC system was out-of-service for maintenance and the requirements for LCO 3.9.10.1 were not satisfied. This condition was determined reportable as an operation prohibited by Tech Specs. A historical review determined that a similar event occurred on March 14, 1991. The root cause of these events is attributed to personnel error, in conjunction with several contributing factors. The Reactor Manual Control System withdraw pushbutton had a yellow caution tag attached stating not to withdraw any control rods with SLC INOPERABLE. The Control Room Operators incorrectly evaluated that the restrictions on the caution tag did not apply and the surveillance could be performed. There were no safety consequences or compromise to the public health or safety as a result of this event. Actions to prevent recurrence include: re-emphasizing to all licensed operators the importance of compliance with controls on tagged devices and revising the surveillances to include confirmation steps that all applicable LCO requirements are satisfied prior to performance.
3881991005 | Susquehanna 2 | 03/09/1991 | 04/08/1991 | 9104120186 | <strong>Standby Gas Treatment Fan - Unexpected Start</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1991 with Unit 2 in Condition 3 (Hot Shutdown), the 'A' Standby Gas Treatment System (SGTS) fan started unexpectedly while securing the system following purging the primary containment in preparation for the refueling outage. The fan started due to actuation of the filter train high outlet temperature sensor. The cause of the actuation could not be determined with certainty but the most likely cause was an inaccurate signal from the temperature sensing element to the temperature switch while warm containment air was being introduced into the system. The accuracy of the temperature elements is questionable due to lack of data as to their length. In addition, the temperature sensors exhibit a wide tolerance band and discrepancies in the calibration procedures for the sensors were discovered during the investigation. The temperature condition cleared itself and the system was returned to normal standby alignment. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned ESF actuation occurred when the 'A' SGTS fan started due to actuation of the filter train outlet temperature switch. There were no safety consequences or compromises to the public health or safety. A review of the system design revealed that the setpoints for the filter inlet and outlet temperature switches were reversed which affected the order in which the cooling mode logic initiated. However, this condition would not have prevented the system from performing its intended function. The setpoints have been corrected and calibration procedures will be revised appropriately. An inspection of the temperature elements will be performed to determine if any physical changes to the elements is necessary.
3881991006 | Susquehanna 2, Susquehanna 1 | 04/22/1991 | 05/22/1991 | 9105300318 | <strong>Emergency Diesel 'A' Failure During 18 Month Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At 0040 hours on April 22, 1991, with Unit 2 in Condition 5 at 0% power and Unit 1 in Condition 1 at 100% power, the 'A' Emergency Diesel Generator (EDG) failed to reach rated speed and pick up load during 18 month LOCA - LOOP surveillance testing. The 'A' EDG did receive an automatic start signal and did start, but was manually shut down when it failed to reach rated speed and pick up its emergency bus loads. Investigations were unable to determine the exact cause of the failure to reach rated speed. A subsequent troubleshooting start attempt was successful. The EDG emergency start logic and operability surveillance tests were successfully performed. The 18 month LOCA - LOOP surveillance test was successfully reperformed in its entirety. There were no safety consequences or compromise to public health or safety since three EDGs remained OPERABLE as required by the Susquehanna Safety Analysis. Since there are two failures in the last 20 valid tests, the 'A' EDG test interval is one start at least once per 7 days per the Technical Specifications.
3881991007 | Susquehanna 2 | 05/15/1991 | 07/30/1991 | 9108050153 | <strong>ESF Actuations Due to an RPS EPA Breaker Spurious Trip</strong><br /><i>Abstract:&nbsp;</i>At 1820 hours on May 15, 1991 with Unit 2 operating at 100% power, the primary power supply to the "A" Reactor Protection System (RPS) power distribution panel was lost when one of its Electrical Protection Assembly (EPA) breakers tripped. RPS as well as other Plant systems and components functioned properly and as expected in response to the event. No reactor parameters were affected and no Emergency Core Cooling Systems were actuated. The 'A' distribution panel was swapped to alternate power until the primary power supply was restored. There was no indication of abnormalities and all isolation signals were reset by 1830 hours. The primary power source EPA breaker was reset at 0100 hours on 5/16/91. Full power operation of the unit continued without interruption. At the time of the initial report, the exact cause of the trip was not definitively determined. Subsequent investigations showed the cause for the trip was a faulty capacitor in the EPA logic card. A task team has been organized to enhance the reliability of the Reactor Protection System. In addition, an EPA study prepared by GE - Nuclear Energy for the BWR Owners Group is also under PP&L review to assess any operational or design changes that may be warranted. LER 90-007 (Docket No. 50-388/License No. NPF-22) will be updated to provide the results of the efforts to enhance RPS reliability. Since all Engineered Safety Feature (ESF) systems and components functioned properly and per design, there were no safety consequences or compromises to the health or safety of the public.
3881991008 | Susquehanna 2 | 05/30/1991 | 06/27/1991 | 9107030328 | <strong>ESF Actuations Due to RPS EPA Breakers Spurious Trip</strong><br /><i>Abstract:&nbsp;</i>At 0925 hours on May 30, 1991 with Unit 2 operating at 100% power, the primary power supply to the "A" Reactor Protection System (RPS) power distribution panel was lost when its Electrical Protection Assembly (EPA) breakers tripped. RPS as well as other Plant systems and components functioned properly and as expected in response to the event. No reactor parameters were affected and no Emergency Core Cooling Systems were actuated. The 'A' distribution panel was swapped to alternate power until the primary power supply was restored. There was no indication of abnormalities and all isolation signals were reset by 1015 hours. The primary power source EPA breakers were reset at 2150 hours on 6/1/91. Full power operation of the unit continued without interruption. While the exact cause of the trip was not definitively determined, the most probable cause for the trip was attributed to oscillator output shift on the EPA logic card. A task team has been organized to enhance the reliability of the Reactor Protection System. In addition, an EPA study prepared by GE - Nuclear Energy for the BWR Owners Group is also under PP&L review to assess any operational or design changes that may be warranted. LER 90-007 (Docket No. 50-388/License No. NPF-22) will be updated to provide the results of the efforts to enhance RPS reliability. Since all Engineered Safety Feature (ESF) systems and components functioned properly and per design, there were no safety consequences or compromises to the health or safety of the public.
3881991009 | Susquehanna 2 | 06/24/1991 | 07/23/1991 | 9107290157 | <strong>Reactor Water Cleanup System Isolation Due to Less Than Adequate Communication During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At 2200 hours on June 24, 1991 with Unit 2 operating in Condition 1 at 100% power the Reactor Water Cleanup (RWCU) steam leak detection instrumentation was inadvertently actuated during a routine functional test. This action resulted in the closure of the RWCU inboard primary containment isolation valve, HV-244-F001, and subsequent system isolation. During the functional test of the Main Steam Line Tunnel delta-temperature instrumentation I&C technicians inadvertently connected test equipment to the RWCU steam leak detection instrumentation. This resulted in the generation of a high delta-temperature signal for the RWCU pump room instead of the planned MSLT signal. The error was immediately recognized and corrected. The system responded as designed to the isolation signal and was returned to service at 2211 hours. The root cause of the event was less than adequate verbal communications. <br /><br /> The event was determined to be reportable per 10CFR50.73(a)(2)(iv), in that closure of HV-244-F001 constituted an unplanned ESF actuation. There were no safety consequences or compromise to public health or safety as a result of this event. Actions to prevent recurrence will include briefing all I&C technicians on this event, with emphasis on the importance of clear, concise communications and revising the applicable surveillances to remove any confusion factors which may have led to the event.
3881991010 | Susquehanna 2 | 06/28/1991 | 12/04/1992 | 9212140021 | <strong>RWCU System Isolated on Two Occassions Due to Actuation of Steam Leak Detection Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1991, with Unit 2 operating in Condition 1 at 100% power, the Reactor Water Cleanup (RWCU) system isolated on two separate occasions due to actuations of the system's steam leak detection instrumentation. At 1450 hours the first isolation occurred when the Riley temperature module meter switch for RWCU penetration room temperature was positioned to 'read' room temperature and the system isolated. At 1838 hours a second isolation occurred due to an actual Division II RWCU Penetration Room high ambient temperature signal. The system responded properly to both isolation signals. The root cause of the first RWCU isolation has, been attributed to a design deficiency with the Riley temperature modules. The root cause of the second RWCU isolation has been attributed to elevated ambient penetration room temperatures due to unusually hot weather conditions. This also contributed to the first event. The two events described were determined to be reportable per 10CFR50.73(a)(2)(iv), in that, in each case, an unplanned ESF actuation occurred. On July 12, 1991 a Waiver of Compliance was granted by the NRC allowing the RWCU high ambient room temperature trip setpoints to be increased from 118.3 degrees F to 131 degrees F to prevent any future spurious isolations during the hot weather months. Subsequently the RWCU area ambient steam leak detection modules were replaced. Operations personnel were trained on the design and use of the Riley modules. There were no safety consequences or compromise to public health or safety as a result of these events.
3881991011 | Susquehanna 2 | 06/25/1991 | 08/12/1991 | 9108150097 | <strong>High Radiation Area Door Found Unsecured</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1991 two plant Engineers and a Health Physics Technician discovered a high radiation area door in the closed position with the locking mechanism not properly seated in the striker plate. An event review team evaluated the event and determined the condition was prohibited by Technical Specification 6.12.2 and was reportable per 10CFR50.73 (a)(2)(i)(c). The event was caused by both personnel error and less than adequate physical condition of the door. Use of the high radiation area door in question was inadvertently omitted from a station key usage log. This omission prevented the required independent verification of the door being closed and secured. Additionally, physical inadequacies of the door assembly could have given a false sense of a secured door when it was checked closed after it was used. Immediate corrective actions included closing and independently verifying the door to be locked. All remaining high radiation area doors were then verified to be locked and latched. Maintenance was performed on the high radiation area door in question. Long term corrective actions include inspecting, and repairing as necessary, all Technical Specification 6.12.2 doors and providing Health Physics Technicians with training emphasizing self-verification and reporting of damaged doors. There were no safety consequences or compromises to the health and safety of the public.
3881991012 | Susquehanna 2 | 08/06/1991 | 09/05/1991 | 9109100207 | <strong>Automatic Unit SCRAM From Full Power</strong><br /><i>Abstract:&nbsp;</i>At 0727 hours on August 6, 1991 Unit 2 received simultaneous SCRAM and dual recirculation pump trip signals causing an automatic unit shutdown. All plant systems responded as expected in response to the transient. All reactor parameters were stabilized and the SCRAM was reset by 0740. The event was initiated when three of four main turbine stop valves (EIIS code: SB) unexpectedly closed far enough to produce Reactor Protection System (RPS) and End of Cycle-Recirculation Pump Trip (EOC-RPT) signals that the stop valves had closed. The stop valve closure signal was due to water intrusion into an electrical junction box causing a short-circuit in the Unit 2 turbine stop valve (TSV) control logic. The source of the water was a sealing steam leak from the #2 stop valve. The water-damaged components were replaced and post maintenance testing was performed. A temporary deflection shield was installed to inhibit water intrusion of the panel. Further modifications to prevent recurrence were implemented during a subsequent non related Unit shutdown on 8/22/91 (non reportable). Maintenance was performed on the #2 stop valve during the shutdown. On 8/28/91, during Unit startup, the #2 TSV was inspected and no leakage was found. Since all plant systems responded per design in response to the transient, there were no safety consequences or compromises to health or safety of the public.
3881991013 | Susquehanna 2 | 10/14/1991 | 11/13/1991 | 9111200047 | <strong>ESF Actuations Due to RPS M-G Set Output Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>At 1159 hours on October 14, 1991 with Unit 2 operating at 100% power, the primary power supply to the "A" Reactor Protection System (RPS) power distribution panel was lost when its Motor-Generator (MG) set output breaker tripped. RPS as well as other Plant systems and components functioned properly and as expected in response to the event. No reactor parameters were affected and no Emergency Core Cooling Systems were actuated. The 'A' RPS distribution panel was swapped to the alternate power supply until the primary power supply was restored. All isolation signals were reset by 1420 hours. The primary RPS power source was reset at 0955 hours on 10/16/91. Full power operation of the unit continued without interruption. The cause was determined to be abnormal behavior of the MG set output regulator mechanical relays. These relays were reworked and returned to service. The remaining MG set regulators of both units will be inspected for relay abnormalities and loose connections during the next respective planned equipment outage. In addition, periodic maintenance activities for RPS MG sets will be reviewed and incorporate maintenance of relays and security of connections. Since all Engineered Safety Feature (ESF) systems and components functioned properly per design, there were no safety consequences or compromises to the health or safety of the public.
3881991014 | Susquehanna 2 | 12/12/1991 | 01/10/1992 | 9203170278 | <strong>MSIV Closure Response Time Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 1400 hours on December 12, 1991, after reviewing an industry event report, an Instrumentation and Control Engineer discovered that a Main Steam Isolation Valve (MSIV) Closure Channel Response Time had exceeded the Technical Specification required value of 60 milli-seconds (msec) by 2 msec. The Unit 2 "B1" channel was 2 msec over Technical Specification limits from the Fall of 1989 until the Spring of 1991. The cause of the event was that Response Time Testing procedures did not account for the Trip Channel Sensor (limit switch contact) Response time of 10 msec as identified in General Electric Design Data sheets. Therefore the measured Response Time of 52 msec was actually 62 msec. The remaining Closure Response Channels were within Technical Specification limits and the system would have performed its intended function. Changes were initiated for I&C Response Time Testing procedures to ensure that 10 msec for Channel Sensor Response is included in the overall RPS Response Time for MSIV Closure and Turbine Stop Valve Closure. The reason why the Sensor Response Time allotment was not accounted for could not be determined. A review of Response Time procedures of both Units was performed to ensure no other Response Time tests were affected by the General Electric Design Data Sheets. No safety consequences or compromises to the health or safety of the public were attributed to the event.
3881991015 | Susquehanna 2 | 12/16/1991 | 01/14/1992 | 9201210226 | <strong>High Pressure Coolant Injection System Inoperable When Steam Supply Isolated Due to Leak</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1991, with Unit 2 in Condition 1 at 100% power, a small leak was discovered in a drain line for the HPCI system steam supply line. The leak was isolated by closing two drain valves upstream of a steam trap which is upstream of the leakage location. In addition, the steam supply isolation valve was closed due to the possibility of condensation build-up. Closing the steam supply valve caused the HPCI to be inoperable. The cause of the event was determined to be erosion/corrosion of the carbon steel HPCI drain line piping. This event was determined to reportable per 10CFR50.73(a)(2)(v)(D), as a condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. The drain piping was repaired at the leakage location. The piping is included in the erosion/corrosion control program and had been identified as experiencing some degradation. Documents were already in place to replace the subject piping with upgraded material during the next refueling outage in each Unit.
3891991001 | St. Lucie 2 | 03/04/1991 | 04/01/1991 | 9104080008 | <strong>Inadvertent Actuation of Auxiliary Feedwater Components While Performing Monthly Auxiliary Feedwater Actuation System Test due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1991 at 1440, an inadvertent actuation of the Auxiliary Feedwater Actuation System (AFAS) Channel A occurred. Auxiliary Feedwater (AFW) pump 2A started, The steam admission valve from the 2B Steam Generator to the turbine-driven 2C AFW pump opened, starting the 2C AFW pump. A main feedwater isolation valve received a signal to close, but only moved from its full open position before the signal cleared. Operators returned all components to their normal position. The initiating event was a momentary loss of auctioneered power supplies to Channel A AFAS actuation relays. The actuation occurred while Instrument and Control (I&C) technicians were performing a routine surveillance and had just finished balancing and adjusting power supplies 301A and 302B. <br /><br /> The root cause of this event is equipment failure. One power supply was momentarily unable to pick up load from the other. Power supply 302B was found to be faulty and replaced. <br /><br /> Other corrective actions include: checking other AFAS power supplies; replacing AFAS power supplies with an improved model; remove balancing and adjusting from the monthly surveillance to 18 month (performed when the unit is shut down). These actions will be taken on both units.
3891991002 | St. Lucie 2 | 04/15/1991 | 05/14/1991 | 9105220106 | <strong>Missed Technical Specification Surveillance Due to Procedural Error</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1991, following a review of a Surveillance Procedure, a utility Instrumentation and Controls supervisor found that four component relays that feed the Boric Acid Gravity Feed Valves and the Reactor Cavity Cooling Fans had not been tested. Further investigation into this missed surveillance revealed that these equipment relays had been tested every eighteen months during the Integrated Safeguards Test, but not during the semi-annual Channel Functional Test required for Safety Injection Actuation Signal Automatic Actuation Logic as per Technical Specification Surveillance 4.3.2.1. This has been the practice since Unit 2 began commercial operation in September of 1983. <br /><br /> The root cause of the missed surveillance has been attributed to procedural error. The relays concerned were inadvertently deleted during initial development of the surveillance procedure. The Corrective Actions implemented as a result of this event include revising the Surveillance Procedure to require testing the equipment relays for the Boric Acid Gravity Feed Valves and Reactor Cavity Cooling Fans with a Digital-Multi-Meter during power operations and verifying that the balance of the procedure is in compliance with Technical Specification Surveillance requirements and as described in the Final Updated Safety Analysis Report Tables 7.3-9 and 7.3-9a.
3891991003 | St. Lucie 2 | 04/26/1991 | 05/28/1991 | 9106040063 | <strong>2A Shutdown Cooling Heat Exchanger Out of Service Due to Mispositioned Component Cooling Water Valve Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This is a supplemental report to LER 389-91-003.<br /><br /> At 0110 on April 26, 1991, with Unit 2 at 100% power, Operations personnel began searching for a DC ground. At 0400, per plant procedure, Operations cycled HCV-14-3A, Component Cooling Water (CCW) outlet from the 2A Shutdown Cooling (SDC) Heat Exchanger (HX) to de-energize its solenoid operator in an effort to locate the DC ground. After the valve opened, no flow through the heat exchanger was indicated. Approximately 4000 gallons per minute (gpm) of CCW flow was expected through the HX. Upon investigation, the 2A SDC HX CCW return isolation valve SB-14365 was found to be locked closed. This valve is required to be Locked Open. It had been entered into the Valve Switch Deviation Log on October 23, 1990 as Locked Throttled and restored November 29, 1990. As this is the most recent documented manipulation date, it is assumed to have been mispositioned at this time. The valve position pointer was broken and indicated open. The cause of the mispositioning is a personnel error by a non-licensed utility operator. The root cause of the failure to detect the mispositioning is cognitive personnel error by utility non-licensed operators and a deficiency in implementation of plant management's policy on valve position verification. <br /><br /> Corrective actions included: correctly realigning the valve; Operators on both units performed a full Valve Status Check; Senior FPL and Plant management re-emphasized the requirements for valve position verification in meetings with operating crews; and unannounced Quality Control and Operations Supervision monitoring of valve position verification has been implemented.
3891991004 | St. Lucie 2 | 05/03/1991 | 05/24/1991 | 9105300325 | <strong>Two Containment Fan Coolers Inoperable Based on Low Component Cooling Water Flow Due to a Design Error Causing Low Flow Alarm Limit Less Than Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1991, with Unit 2 at 100% power, a non-licensed utility operator physically verified the Locked Throttled position of SB-14530, the common header isolation valve for Component Cooling Water (CCW) from the 2A and 2B Containment Fan Coolers, in accordance with Administrative Procedure #2-0010125A, Data Sheet #36, Weekly Valve Status Check. A functional check of the system flows was not conducted after performance of Data Sheet #36, and it is surmised slightly less than normal CCW flow to the Containment Fan Coolers was the resultant effect.<br /><br /> At 0800 on May 3, 1991, with Unit 2 at 100% power, a non-licensed utility operator discovered the Component Cooling Water flows from the 2A and 2B Containment Fan Coolers were reading approximately 1170 gallons per minute (gpm), below the Technical Specification required minimum of 1200 gpm. The CCW Return from the 2A and 2B Containment Fan Coolers, Valve SB-14530, was found to be in the Locked Throttled position, as required. The proper flows were then re-established on the 2A and 2B Containment Fan Coolers and they were declared operable again. The cause of this event was a design error in that the CCW Low Flow to each Containment Fan Cooler alarm limits were found to be set non-conservatively with respect to the Technical Specifications. A contributing factor was the lack of guidance for position verification of throttled valves. <br /><br /> The significant Corrective Actions taken as a result of this event: 1) The flows on the 2A and 2B Containment Fan Coolers were returned to their normal values; the flows on the 2C and 2D Containment Fan Coolers were verified to be above the Technical Specification limits. 2) The CCW Low Flow Containment Fan Cooler alarms were raised to above 1200 gallons per minute on both units. 3) Procedural guidance will be implemented to provide a definitive position verification method for Locked Throttled valves.
3891991005 | St. Lucie 2 | 09/20/1991 | 10/21/1991 | 9110300224 | <strong>Missed Surveillance for Safety Injection Tank Water Level and Pressure Channel Functional Test Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1991, it was discovered that the September surveillance for the Safety Injection Tank (SIT) water level and pressure monthly channel functional test was not performed when scheduled. Using the 25% maximum allowable extension permitted by Specification 4.0.2, the latest date for the monthly surveillance to be performed on time was September 20, 1991. <br /><br /> The root cause of the event was personnel error by the responsible Instrument and Control (I&C) system supervisor. Per I&C procedure, it is the responsibility of the cognizant system supervisor to ensure scheduling requirements are met. A contributing factor is that the I&C procedure for scheduling and performing work contained a requirement for an internal check by Planning to check with the system supervisor to ensure surveillances are performed but no mechanism existed to routinely satisfy this.<br /><br /> Corrective Actions were to perform the surveillance, counsel the system supervisor involved, and enhance the I&C scheduled surveillance procedure to ensure the Lead Supervisors verify surveillances have been performed.
3891991006 | St. Lucie 2 | 11/29/1991 | 12/20/1991 | 9112300325 | <strong>Engineered Safety Features Actuation System Channel Out of Service Resulted in a Condition Prohibited by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1991, with Unit 2 operating at 100% steady state power, a utility-licensed senior reactor operator noted that the Unit was in a condition prohibited by the Plant's Technical Specifications. Channel 'D' of the Engineered Safety Features Actuation System instrumentation for the Recirculation Actuation Signal had been placed out of service on November 26, 1991 at 0411 and the channel was put in bypass. Technical Specification 3.3.2 requires that with only three channels operable, the inoperable channel must be restored to operable within forty-eight hours or else it should be placed in the tripped condition and the remaining operable channels must be verified to be operable within one hour. However, Channel 'D' remained in bypass until this condition was recognized by a utility-licensed senior reactor operator at approximately 0100 on November 29, 1991, sixty-nine hours after the instrument was placed out of service. <br /><br /> The root cause of this event was cognitive personnel error by utility-licensed operators. The instrumentation had been entered in the equipment out of service log but the return-to-service information was incorrect.<br /><br /> Corrective actions taken included placing the channel in the tripped condition and verifying the remaining channels were operable. Responsible personnel were counselled on the importance of providing accurate information in all of their logs and performing thorough independent verifications of all entries. The Plant Training Department will evaluate this event to determine appropriate training requirements and methods. The procedure governing review of equipment placed out of service will be strengthened. Also, the bypass key for this unique instrument will be modified with a human factors identification tag.
3951991001 | Summer 1 | 02/19/1991 | 03/22/1991 | 9103280305 | <strong>Missed Surveillance for Axial Flux Difference</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1991, at approximately 1200 hours, a computer generated "COMPUTER DELTA FLUX LIMIT EXCEEDED" alarm actuated on the Main Control Board (MCB). The operators, using indications on the MCB and the Nuclear Instrumentation System, verified that the actual Axial Flux Difference was within Technical Specification (TS) limits. Nuclear Computer Services was called to investigate the discrepancy between the MCB indication and the computer generated alarm. The computer engineer arrived in the control room and cleared the alarm, but failed to determine that the computer program that generates the alarm was not running, thereby leaving the alarm cleared but inoperable. With the alarm cleared, the operators considered the alarm operable and did not pursue the compensatory surveillance. On February 21, 1991, at approximately 0820 hours, a review of the computer printout showed that the program that actuates the delta flux alarm had not been running since 1203 hours on February 19. Since the compensatory surveillance had not been performed, this represented a missed surveillance. The program and alarm were returned to operation, and delta flux was verified to be within the TS limits. <br /><br /> As a result of this event, the Annunciator Response Procedures (ARP) for the delta flux alarm and the computer failure alarm were changed. Also, Computer Services has implemented computer program changes to improve the quality and the reliability of the computer generated values for delta flux.
3951991002 | Summer 1 | 04/13/1991 | 05/17/1991 | 9105290206 | <strong>Technical Specification Noncompliance for Turbine Building Sump Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.3.3.8, "Radioactive Liquid Effluent Monitoring Instrumentation." requires that effluent monitoring instrumentation shall be operable with established setpoints that ensure compliance with the limits of Specification 3.11.1.1, "Liquid Effluents." The Specification further requires that the alarm/trip setpoints for the channels be determined in accordance with the Offsite Dose Calculation Manual (ODCM) for the Virgil C. Summer Nuclear Station (VCSNS). <br /><br /> On April 17, 1991, South Carolina Electric & Gas Company (SCE&G) identified a noncompliance with the portion of this Limiting Condition for Operation which requires that the setpoints for the Turbine Building Sump (TBS) Radiation Monitor (RM-L8) be established in accordance with the ODCM. A default condition in the computer software utilized to calculate setpoints along with inadequate procedural guidance resulted in higher setpoints than allowed by the ODCM for releases which occurred on April 13 and 16, 1991. <br /><br /> SCE&G has determined that the instantaneous release limits specified in Technical Specification 3.11.1.1 were not exceeded during the event due to the dilution from other wastewater discharge flows and the circulating water discharge of the facility. Further review of the setpoint guidance has also concluded that the ODCM contains undue conservatism and is therefore overly restrictive with regard to releases from the TBS.<br /><br /> To insure compliance with Technical Specification 3.3.3.8 and its intent to prevent releases from VCSNS in excess of the limits addressed in Technical Specification 3.11.1.1, SCE&G is revising station procedures, providing additional training for personnel, and clarifying the ODCM guidance. These actions will be complete by September, 1991.
3951991003 | Summer 1 | 07/02/1991 | 07/31/1991 | 9108060260 | <strong>Perturbation on Off-Site Source Causes ESF Actuation of a Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At approximately 1723 hours on July 2, 1991, a thunderstorm-induced momentary fault on an off-site power source resulted in the actuation of the "A" Emergency Diesel Generator (EDG). The fault cleared and off-site voltage returned to normal in less than 2.25 seconds. Therefore, the bus continued to be carried by the off-site source and the EDG output breaker remained open. <br /><br /> Several non-critical components de-energized when their respective seal-in contacters opened as a result of the momentary loss of voltage. These components were quickly returned to service and, after confirming the off-site source was stable, the EDG was secured. <br /><br /> A review of this event has shown that plant response was as designed and that no safety consequences occurred. No further actions will be taken regarding this event.
3951991004 | Summer 1 | 05/03/1991 | 08/30/1991 | 9109090242 | <strong>Incorrect Sample Volume Data Results in Computer Error for Tritium Concentration</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1991, Health Physics (HP) personnel identified a calculational error in computer software utilized to evaluate airborne radioactivity in restricted areas as well as effluent releases to unrestricted areas at the Virgil C. Summer Nuclear Station (VCSNS). Incorrect sample volume data resulted in calculations of airborne tritium activity being 100 times less than actual values. The cause of the event was inadequate computer software. A change to the software, implemented in April of 1984, was inadequate from a "Human Factors" standpoint in that it did not prompt the user to calculate the correct sample volume prior to input of data.<br /><br /> A review of airborne tritium analyses records and performance of the liquid scintillation detector determined that the error first appeared on April 22, 1984. This review also confirmed that effluent releases and personnel exposures at VCSNS have remained within Technical Specification and 10CFR20 limits. <br /><br /> The immediate corrective actions involved training of HP personnel, installation of a computer prompt for proper sample volume, procedure upgrades, and submittal of corrected release information in the semiannual effluent report. Additionally, by October 1, 1991, South Carolina Electric & Gas Company will update exposure files with exposure assessments as required by 10CFR20.103(a)(3) for individuals conservatively estimated to have exceeded 10 MPC - Hrs during any one week.
3951991005 | Summer 1 | 06/24/1991 | 08/26/1991 | 9109040384 | <strong>Personnel Error in Surveillance Scheduling Leads to Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1991, Surveillance Test Procedure (STP) 121.002, Main Steam Valve Operability Test, was completed at 0550 hours. This procedure performs in-service test (IST) requirements for 17 valves associated with the main steam system. The initial review of the test, which was completed on May 21, 1991, detected three valves which required an increase in testing frequency. However, during the review of the test package for completeness and correctness, a Regulatory Support specialist discovered that one of the three valves had actually passed the acceptance criteria and did not need an increase in test frequency. The surveillance task sheet was then closed without updating the test frequency while the specialist sought concurrence with his findings. The in-service inspection (ISI) post test reviewer re-examined the test data and agreed with the specialist's finding.<br /><br /> Upon receiving concurrence on May 23, the specialist then completed processing the task and neglected to update the test frequency of the two valves which actually required an increased testing frequency. On July 25, 1991, at 1535 hours, the specialist recognized what had happened and that the frequency requirement for the two valves had been exceeded on June 24 at 0550 hours. The specialist immediately notified the control room of the condition and the control room immediately initiated actions to test the valves. The test was completed satisfactorily at 1616 hours. The scheduled surveillance frequency was increased appropriately.
3951991006 | Summer 1 | 08/04/1991 | 09/03/1991 | 9109090277 | <strong>Personnel Error Leads to an Inadvertent ESF Actuation of a Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>Surveillance Test Procedure (STP) 170.014, Fire Switch Functional Test for XPP-0043B. CHG/SI Pump B, and 170.015, Fire Switch Functional Test for XPP-0043C, CHG/SI Pump C, are performed every 18 months and verifies the fire switch capability to isolate the "B" and "C" Train Charging (CHG)/Safety Injection (SI) pumps from their control circuitry in the control room. Part of the test involves actuating a relay that sends an emergency start signal to the "B" and "C" CHG/SI pumps as well as the "B" emergency diesel generator (EDG). Because the scope of these procedures does not involve starting the EDG, the procedure directs the EDG mode selector switch to be placed in the maintenance mode (this prevents the EDG from starting). <br /><br /> On August 4, 1991, during the performance of these STPs, the Operations crew had completed the functional requirements of the tests and was in the process of restoring the plant equipment from its test condition. The operator at the EDG was directed to restore the "B" EDG to "as found" conditions prior to the procedure step which called for the emergency start signal to be reset. This caused the EDG to start at approximately 2246 hours. The diesel generator was monitored and verified to achieve proper speed and voltage as required from an auto start. Also, all support systems were verified to function properly. <br /><br /> The operations staff was briefed on the necessity of attention to detail and the consequences which might ensue due to an error. Also, specific guidance to increase shift supervision's involvement with new or infrequently (six months or longer) performed tests will be implemented by April 1, 1992.
3951991007 | Summer 1 | 08/24/1991 | 09/23/1991 | 9109300170 | <strong>Programmatic Weakness Leads to a Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>Surveillance Test Procedure (STP) 122.002, Component Cooling Water Pump Test, provides instruction for four separate in-service test (IST) tasks. <br /><br /> The four tasks test the individual component cooling water (CCW) pumps, A, B, and C, and the associated system isolation valves. The logic employed in scheduling these tasks was to test one pump every 28 days. This assures each pump is tested within the required quarterly interval. The valves are not actually scheduled but the procedure directs that the valves be tested in the second month of each quarter (i.e., when the pump for that month is tested). <br /><br /> The "C" pump test was scheduled to be completed in August (2nd month of the quarter); therefore, the valves were to be tested with the "C" pump. The tracking sheet for the "C" pump indicated that its allowable test interval did not end until as late as September 4. However, as a result of previous valve testing with the "A" pump, the allowable test interval for the valves ended August 24. <br /><br /> At 2300 hours on August 26, while reviewing the STP procedure history, it was noted that the allowed interval for testing the valves had been exceeded. Both trains of CCW were affected by the missed surveillance and were declared inoperable. Technical Specification 4.0.3 was applied and the valves were tested successfully which restored CCW to operable status at 0300 hours on August 27.
3951991008 | Summer 1 | 10/04/1991 | 11/01/1991 | 9111080185 | <strong>Steam Generator Tube Eddy Current Results - Category C-3 Applied</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1991, at approximately 1400 hours, the preliminary results of the sixth inservice eddy current examination of the Virgil C. Summer Nuclear Station steam generators were obtained. The planned examinations included 100% of the available (i.e., not plugged) tubes in each steam generator hot leg tubesheet, utilizing Motorized Rotating Pancake Coil Eddy Current Testing. A 100% Bobbin Coil inspection of the full length tubing (Tube End Hot to Tube End Cold) was also performed. The results indicated that since more than 1% of the inspected tubes in each steam generator were defective, a C-3 inspection category, per Technical Specification 4.4.5.2, applied. When all three steam generators entered Category C-3, a prompt notification was made to the NRC Operations Center in accordance with the requirements of Technical Specification 4.4.5.5.c and 10CFR50.72(b)(2)(i). <br /><br /> The results of the inspections performed during the sixth refueling outage are: <br /><br /> Steam Generator # of Tubes Plugged # of Tubes Repaired <br /><br /> A 13 211 <br /> B 21 309 <br /> C 169 92 <br /><br /> The Category C-3 tube degradation is localized in ,the, tubesheet area and is the result of Primary Water Stress Corrosion Cracking (PWSCC). <br /><br /> Tube plugging or repair, as appropriate, was completed on November 1, 1991.
3951991009 | Summer 1 | 10/15/1991 | 11/14/1991 | 9111190329 | <strong>Vendor Concerns Lead to Discovery ECCS Flow Discrepancies</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1991, South Carolina Electric & Gas Company (SCE&G) was notified by Westinghouse of a developing issue based on a vendor recommendation to limit its previously approved pump runout limit of 680 gpm to a new limit of 675 gpm. This new limit is related to several issues that could affect the runout margin available for the CHG/SI pumps. <br /><br /> Based on these issues, it was determined that Surveillance Test Procedure (STP) 230.006, Valve/Charging Pump Operability Testing, should be revised to address these issues and performed. The following deficiency was found to constitute operation outside the provisions of Technical Specification 3.5.2 and thus is reportable per 10CFR50.73(a)(2)(i): For the hot leg recirculation path, all three pumps would exceed the Surveillance Requirement runout limit of 680 gpm. It was also noted that the B pump performance was below the minimum pump curve assumed in the FSAR accident analysis for the high flow region of the curve. <br /><br /> The cause of the CHG/SI pumps exceeding their runout limit in the recirculation alignments was directly related to the new information supplied by the vendor regarding the effects of instrument uncertainty and suction boost. This condition was evaluated and found not to be expected to impact plant safety. <br /><br /> The system was rebalanced and a new analysis was performed to return all pumps to within the vendor recommendations, Technical Specification requirements, and analysis assumptions.
3951991010 | Summer 1 | 11/06/1991 | 12/05/1991 | 9112100233 | <strong>Inadvertant Start of the Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1991, during maintenance of the "A" train Engineered Safety Features Load Sequencer (ESFLS)(XPN-6020), an extender board failed. The failure of the extender board resulted in the loss of power to the circuit board being tested which caused the sequencer to malfunction and the following to occur: <br /><br /> the normal incoming 7.2 KV circuit breaker tripped open; <br /><br /> the Emergency Diesel Generator (EDG) started; <br /><br /> the EDG output breaker closed; and<br /><br /> all normally sequenced loads (except those with breakers racked out) loaded on the Diesel Generator bus in one step (approximately 5000 KW in-rush and 2000 KW running).<br /><br /> Operations personnel immediately took action to restore the normal offsite power to the 7.2 KV bus and to secure the EDG. A Nonconformance Notice (NCN) was initiated to evaluate the EDG for any adverse effects due to the abnormal loading. The NCN disposition identified specific inspections and tests that needed to be performed. The Diesel Generator was inspected, various data and measurements taken, and the unit was run at various loads with additional data taken. It was determined that the EDG was not adversely affected as the result of fast, abnormal loading. <br /><br /> This occurrence was due to test equipment failure.
3971991001 | Columbia | 01/08/1991 | 02/07/1991 | 9102140070 | <strong>RCIC-V-8 Automatic Closure ESF Actuation Due To Failed Electronic Component In Leak Detection System</strong><br /><i>Abstract:&nbsp;</i>At 0727 on January 8, 1991, alarms indicating high Reactor Core Isolation Cooling (RCIC) turbine and equipment area temperatures were received in the control room. Concurrently the outboard isolation valve for the RCIC turbine steam supply, RCIC-V-8, automatically closed. Redundant Control Room instrumentation and inspection of the RCIC locale showed no abnormal temperatures in the RCIC equipment areas. The cause of the isolation was traced to a failed component in the Leak Detection System, which provides input into the RCIC isolation logic. <br /><br /> Operations correctly entered the action statements for Technical Specifications 3.7.3 (RCIC operability) and 3.3.2 (Isolation Actuation Instruments) within one hour of the event. Operations reported the event to the NRC at 0850, since automatic closure of RCIC-V-8 is an ESF actuation, requiring a 4 hour notification (50.72 (b) (2) (ii). The defective component was replaced and the Leak Detection and RCIC systems returned to service. <br /><br /> The apparent cause of this event was an isolated failure of a electronic component associated with one printed circuit input card in Leak Detection Monitor, LD-MON-1A. The root cause is indeterminate at this time. Vendor analysis of the failed component has been requested. This event presented no threat to plant personnel or to the public.
3971991002 | Columbia | 01/10/1991 | 02/08/1991 | 9102140040 | <strong>Reactor Recirculation System Jet Pump Operability Testing not in Literal Compliance with Technical Specifications due to Less Than Adequate Procedure Preparation/Review</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1991 it was determined that current Reactor Recirculation (RRC) System Jet Pump operability surveillance testing did not meet literal compliance with the Technical Specifications. The operability of the Jet Pumps was being determined by matching RRC loop flows instead of flow control valve positions as required by Technical Specification 3.4.1.2. This discrepancy was identified by an NRC Inspector during a routine inspection of Plant Operations activities. <br /><br /> The cause of this event was less than adequate procedure preparation/review to ensure that the procedure for determining Jet Pump operability was in literal compliance with the Technical Specifications. The procedure provided direction to adjust drive flows such that both loops are approximately equal in flow. The Technical Specifications require both recirculation loops to be operating at the same flow control valve position. Immediate corrective action consisted of revising the appropriate procedure to be consistent with the Technical Specifications requirement, and re-performing the surveillance. Further corrective actions include 1) submitting a Technical Specification Change Request to remove the requirement of equalizing flow control positions during Jet Pump operability determinations, 2) implementing a procedure verification and validation process, and 3) reverification of the adequacy of Technical Specification procedural compliance as part of the ongoing Technical Specification Improvement Program (TSIP). <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel. Matching the RRC loop flows meets the intent of the Technical Specification for determining Jet Pump operability.
3971991003 | Columbia | 02/01/1991 | 05/21/1992 | 9205280154 | <strong>Inadequate Technical Specification Surveillance Testing of Standby Gas Treatment</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1991, at 2100 hours a review of surveillance procedure for periodic testing of the downstream Standby Gas Treatment (SGT) High Efficiency Particulate Air (HEPA) filters indicated that methods used were not in compliance with the Technical Specifications due to inadequate air-aerosol mixing. The specific method used was not adequate to meet the requirement in Technical Specification Paragraph 4.6.5.3.b. This paragraph requires that at least once per 18 months each SGT subsystem is to be demonstrated to be operable by test. A review of plant records by Plant Engineers showed that the periodic testing to meet the requirements of this surveillance were completed. However, the testing method used did not assure sufficient air-aerosol mixing for the surveillance test of the downstream HEPA filters. A similar problem had previously been identified for charcoal absorber bed testing during the time period from January 24 to January 29, 1991. This problem was not identified as reportable. Hence, it was not reported in accordance with the requirements of 10CFR50.73. <br /><br /> The root causes of these events were inadequate work practices, inadequate procedures, and less than adequate management programs. A Plant Engineer failed to incorporate the detailed methods required to satisfactorily conduct the surveillance test. The surveillance test procedure did not adequately meet the Technical Specification surveillance requirements. Management programs were in place to detect this omission but were not effectively implemented.
3971991004 | Columbia | 03/28/1991 | 04/28/1991 | 9105070211 | <strong>Inadequate Fire Protection (Thermolag) Of Division Ii Safe Shutdown Cables Due To Inadequate Installation And Inspection</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1991, as part of a scheduled annual inspection, two deficiencies in the Thermolag application on a critical Division II cable tray running through a Division I area were discovered. (Thermolag is a fire protective coating.) At 1615 hours on March 29, 1991, after evaluation of the location and nature of the defects, the deficiencies were determined to be reportable as conditions which are outside of plant design basis. It was determined that a Design Basis Fire in the Division I area could potentially also compromise critical Division II equipment due to insufficient fire protection of the cable tray. The NRC Operations Center was notified at 1640 hours on March 29, 1991, within the required one hour notification time.<br /><br /> Immediately after discovery, the deficiencies were added to the Cable Spreading Room fire impairment list and included as part of the fire tour. <br /><br /> The defects, though on the same cable tray section, are distinct and independent. The root causes for the defects is inadequate installation of the Thermolag and inadequate work practices relating to inspection techniques. The defects will be repaired and inspection personnel will be instructed regarding the importance of checking all cable tray surfaces for degradation of Thermolag protection.<br /><br /> This particular event had no safety significance.
3971991005 | Columbia | 04/02/1991 | 04/01/1993 | 9304050198 | <strong>Oxygen Concentration In Suppression Chamber Was Not Verified Per Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1991, a Plant Operations Engineer determined the oxygen concentration in the wetwell was not being verified to be within limits once per seven (7) days as required by the WNP-2 Plant Technical Specifications. This condition was determined as a result of an evaluation of a previous event in which the technical specification limit for oxygen concentration in the wetwell was exceeded. <br /><br /> The immediate corrective action was to implement a procedure deviation to include the technical specification oxygen verification requirements for the wetwell. The root causes for failing to routinely monitor the oxygen concentration in the wetwell per the Technical Specification surveillance requirements include: <br /><br /> 1) the procedures were less than adequate because they did not require wetwell oxygen concentration be verified to be within limits, and <br /><br /> 2) management direction was less than adequate to ensure that all technical specification surveillance requirements are included within the Plant procedures. A contributing cause was a design deficiency in the containment monitoring system (CMS-CP-1301 and CMS-CP-1401). <br /><br /> Corrective actions include performing a complete review of technical specification surveillance requirements against Plant procedures, require logging of Reactor Building to wetwell vacuum breaker actuations and subsequent monitoring of wetwell oxygen concentration. <br /><br /> The safety significance of this event is minimal because the probability of occurrence of a design basis accident requiring low wetwell oxygen concentration to maintain containment integrity coincident with wetwell oxygen concentration high enough to actually challenge containment integrity is considered low.
3971991006 | Columbia | 04/12/1991 | 02/11/1993 | 9302230461 | <strong>Plant Shutdown Due To Technical Specification Requirement Caused By Inoperable Division 1 Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At 1600 hours on April 12, 1991, a Technical Specification required plant shutdown was initiated due to inoperability of the Division 1 emergency diesel generator (DG1). This action was taken after generator lube oil samples indicated higher than expected wear particle concentration. Cold shutdown was achieved at 1100 hours on April 14. Subsequent disassembly and inspection of the generator revealed that the bearings were in satisfactory condition. Therefore, it is concluded that DG1 was capable of performing its safety function at the time it was declared inoperable, and that this event had minimal safety significance. <br /><br /> The root causes of this event are: 1) the DG1 generator lube oil system was not adequately cleaned after a previous bearing failure; 2) the generator lube oil system design did not provide adequate access for cleaning and inspection; 3) periodic oil changes recommended by the manufacturer were not adequate to reduce contamination levels following bearing break-in, and 4) welds in the lube oil sumps were not oil fight. <br /><br /> Corrective actions included: installation of an additional lube oil reservoir and improved sight glass for the DG1 thrust bearing oil system, repair of the leak in the thrust bearing oil sump, venting of bearing oil sumps, flushing and cleaning of the bearing lube oil systems, and actions taken to trend diesel generator lube oil condition and perform routine sampling on a more frequent basis.
3971991007 | Columbia | 04/15/1991 | 05/15/1991 | 9105280098 | <strong>Reactor Scram And Shutdown Cooling Insulation Due To Inadequate Work Instruments</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1991 at 2347 hours while the Plant was in Operational Mode 4 (Cold Shutdown) with Shutdown Cooling in operation, Control Room Operators received a full reactor scram signal and inboard Residual Heat Removal (RHR) Shutdown Cooling Valve isolation. These events occurred when a low reactor water level signal was generated during an instrument recalibration process. The actual reactor water level was at a normal +37 inches. The full reactor scram signal and the Shutdown Cooling Isolation were both automatic actuations of the Engineered Safety Feature (ESF) system. <br /><br /> As immediate corrective actions, Plant Control Room Operators reset the scram signal by 2352 hours and reestablished shutdown cooling by 2356 hours. The root cause of this event was inadequate work instructions. Further action will be to proceduralize this instrument recalibration process under the Plant Procedures (PPMs). <br /><br /> There was no safety significance associated with the event. At the time of the event the reactor water level was sufficient to provide core cooling. RHR Shutdown Cooling was fully restored in less than 9 minutes. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971991008 | Columbia | 04/16/1991 | 05/10/1991 | 9105150329 | <strong>Entry Into Refueling Mode With Average Reactor Coolant Temperature Greater Than 140 Degrees F Due To Inadequate Plant Procedures</strong><br /><i>Abstract:&nbsp;</i>At 1423 hours on April 16, 1991, just prior to the start of detensioning of the Reactor Pressure Vessel (RPV) head bolts, the reactor was declared to be in Mode 5 (Refueling) with the average reactor coolant temperature greater than 140 degrees F. This is a violation of the Technical Specification Operational Conditions Requirements listed on Table 1.2. <br /><br /> The root cause of this event was less than adequate procedures. <br /><br /> Immediate corrective action was taken to reduce the average reactor coolant temperature. Further corrective action will be taken to place the Technical Specification upper temperature limit in the plant procedures. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971991009 | Columbia | 04/17/1991 | 05/10/1991 | 9105150334 | <strong>Reactor Water Cleanup System (RWCU) Containment Isolation-ESF Actuation Caused By Wiring Error</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1991 at 1251 hours, with the plant shut down for the annual refueling outage, an Engineered Safety Feature (ESF) actuation occurred. This ESF actuation was part of a Nuclear Steam Supply Shutoff System (NS**4) Group 7 isolation and involved the closure of a single valve in the Reactor Water Cleanup System (RWCU). The isolation occurred when contractor electricians cut the wires to the plug of a wind direction recorder which was to be replaced. Although the fuse in this circuit had been pulled, an electrically hot wire to the plug still existed. The momentary grounding of the recorder power supply caused a voltage drop on other circuits in the same electrical panel, which caused a false RWCU high flow differential trip. <br /><br /> As an immediate corrective action, plant operators reopened the RWCU isolation valve, restarted the RWCU pump and restored the system to service. <br /><br /> The root cause of this event was equipment installation error which resulted in the NEUTRAL and HOT wires being switched in a junction box. <br /><br /> This event presented no threat to the health and safety of plant personnel or the public.
3971991010 | Columbia | 04/22/1991 | 07/02/1993 | 9307090019 | <strong>Potentially Inability To Isolate Primary Containment Due To Wiring Separation Error Caused By Inadequate Work Instructions</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1991, during the performance of Single Failure Analysis studies, Design Engineering personnel discovered a wiring separation error affecting the containment isolation valves for the Reactor Recirculation (RRC) flow control valve hydraulic supply. On April 22, 1991, after evaluation of the nature and extent of the identified problems, it was concluded that a "smart short" could prevent primary containment isolation of up to four, 1" diameter lines. This is a condition which alone could have prevented the safety function of the RRC hydraulic isolation valves. <br /><br /> Accessible areas through which the affected circuits run were immediately included on an hourly fire tour.<br /><br /> This condition was caused by inadequate work instructions issued by the Architect Engineer during initial plant construction. <br /><br /> RRC wiring errors will be corrected during the ongoing R6 refueling outage.<br /><br /> No safety significance is attributed to this condition. Routine surveillance has shown these valves to be highly reliable and the probability of the valves actually affecting the containment function is extremely low. Accordingly, this event did not affect the health and safety of either the public or plant personnel.
3971991011 | Columbia | 04/29/1991 | 05/29/1991 | 9106070134 | <strong>ESF Actuation Due To Inadvertent Wire Cutting During Plant Modification Work</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1991, at 1249 hours, while in operational condition 5 (refueling) with the reactor head removed, the reactor cavity flooded up and the fuel pool gates removed, the Outboard Residual Heat Removal (RHR) Shutdown Cooling Valve (RHR-V-8) automatically isolated, causing a loss of shutdown cooling, an ESF actuation. The event occurred when a contractor maintenance electrician, working under an approved Maintenance Work Request (MWR), accidentally cut through the insulation of a wire in the RHR Isolation Control Logic circuit while cutting tie wraps around a wire bundle. Contact of the cutting tool with the bare wire resulted in a blown fuse in the RHR control logic circuit. This loss of power caused RHR-V-8 to close, tripping the RHR shutdown cooling pump (RHR-P-2B). At the time of the event, the reactor vessel temperature was 94.2 degrees F and reactor pressure was atmospheric. Temperature increase during the time shutdown cooling was lost (24 minutes) was negligible. Plant operators restored shutdown cooling at 1313 hours. <br /><br /> The root cause of the event was equipment/design deficiency in that there was inadequate accessibility to the wire bundle for the contractor maintenance electrician to get to the tie wrap to be cut and orient the side cutters parallel to the tie wrap. A contributing factor may have been insufficient attention applied to the task by the electrician.
3971991012 | Columbia | 05/06/1991 | 06/04/1991 | 9106120078 | <strong>Manual Initiation Of Reactor Protection System Due To Low Scram Air Header Pressure Caused By Hose Failure</strong><br /><i>Abstract:&nbsp;</i>At 1248 hours on May 6, 1991 a manual scram was inserted due to decreasing pressure in the scram air header. This is a manual initiation of the Reactor Protection System (RPS).<br /><br /> As part of the Spring 1991 Maintenance and Refueling Outage the Supply System preplanned maintenance on the installed Control Air System (CAS) air compressors and single twin tower regenerative filter/dryers. In order to support the ongoing outage work requiring CAS or the Service Air System (SA) a portable filter/dryer skid and temporary portable air compressor were connected to supply both CAS and SA. Three inch connection hoses with required fittings were procured as Quality Class G items from a local vendor to support this activity. <br /><br /> On May 6, 1991 at 1248 hours with decreasing pressure in the SA and CAS systems the licensed control room operators initiated a manual scram as required by procedure. The scram did not affect the Plant since the reactor was shutdown and all control rods were already fully inserted. Investigation by the operators revealed that one of the hoses on the temporary compressor/dryer unit had blown off. The hose was replaced and SA and CAS were restored to service by 1358 hours. The RPS scram logic was reset at 1405 hours. Because the reactor was in cold shutdown with all the control rods fully inserted this event had minimal safety significance.
3971991013 | Columbia | 05/07/1991 | 08/29/1991 | 9109160148 | <strong>Technical Specification - Surveillance Procedure Verification Program Identification of Non-Conforming Conditions</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1991 the first of several items of non-compliance with the WNP-2 Technical Specification was identified as part of a program of Surveillance Procedure verification. This Surveillance Procedure Verification Program was initiated by the Supply System as a result of problems found in recent months. A total of approximately 145 potential deficiencies were identified by contract Engineers and this effort is complete. A further evaluation by the Plant Staff is being performed on each potential problem item to identify the validity and necessary follow-up actions. A total of twelve items were identified as reportable problems by this process when the time cutoff date for this LER revision occurred. The twelve items cover a variety of subjects involving items of non-compliance. Some of the items are issues where compliance is not possible and a Technical Specification Change or other relief will be requested. <br /><br /> Immediate and further corrective actions include additional testing, Plant Procedure changes, requests for Technical Specification changes or other relief, and possible design changes. The general corrective action is to charter a Quality Action Team (QAT), the Supply System's formal problem solving program, to evaluate and make recommendations to Plant Management for long term improvements to the Technical Specification Surveillance Program.
3971991014 | Columbia | 05/10/1991 | 06/10/1991 | 9106180294 | <strong>Residual Heat Removal Shutdown Cooling Contaminment Isolation Actuation Due To Less Than Adequate Design Drawing Information</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1991 at 2126 hours while the Plant was in Operational Mode 5 (Refueling) with Residual Heat Removal (RHR) Loop B operating in the shutdown cooling mode, an RHR shutdown cooling isolation occurred. This event occurred when a Reactor Protection System (RPS) circuit breaker was opened as part of a clearance order and de-energized relays in the Nuclear Steam Supply Shutoff System (NSSSS). This led to the closure of the RHR shutdown cooling suction line isolation valves. This shutdown cooling isolation was an unplanned automatic actuation of an Engineered Safety Feature (ESF) system.<br /><br /> As immediate corrective actions, Plant Licensed Control Room Operators reestablished shutdown cooling by 2133 hours. The root cause of this event was a less than adequate design drawing. Further corrective action will be to revise the affected drawings and to update the tagging system to indicate this system interrelationship. <br /><br /> There was minimal safety significance associated with the event. At the time of the event the reactor water level was sufficient to provide adequate core cooling for an extended period of time. RHR shutdown cooling was fully restored in seven minutes. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971991015 | Columbia | 06/02/1991 | 06/28/1991 | 9107050214 | <strong>High Pressure Core Spray (HPCS) System Pump Suction Valve Switchover Actuation on High Suppression Pool Level due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1991 at 0106 hours while the Plant was shutdown for maintenance, a High Pressure Core Spray (HPCS) System pump suction switchover from the Condensate Storage Tanks to the Suppression Pool occurred due to a Suppression Pool high water level condition. <br /><br /> Plant configuration at the time was such that HPCS suction was lined up to the Condensate Storage Tanks (CSTs) with CST Suction Valve HPCS-V-1 open and Suppression Pool Suction Valve HPCS-V-15 closed, the normal system lineup (reference Figure 1). The switchover, an Engineered Safety Feature (ESF) actuation, was the automatic closure of HPCS-V-1 and the opening of HPCS-V-15.<br /><br /> During the event period, Plant Control Room Operators were lowering Reactor Vessel level through the Residual Heat Removal (RHR) "A" Heat Exchanger Vents to the Suppression Pool following excess Flow Check (EFC) Valve testing. During this period the Suppression Pool high level alarm annunciator had sealed in the alarm annunciates at +0.5 inches (0.5 inches above normal pool level)!. However, after acknowledging and resetting the alarm, a Plant Control Room Operator failed to take action to either lower Suppression Pool level or manually switchover the HPCS suction valves as directed by procedure. When Suppression Pool water volume reached approximately +3.0 inches indicated level, the automatic switchover occurred.
3971991016 | Columbia | 07/07/1991 | 08/02/1991 | 9108090134 | <strong>ESF Actuation (Containment Instrument Air) Caused by a Blown Rupture Disk</strong><br /><i>Abstract:&nbsp;</i>At 1448 hours on July 7, 1991 an ESF actuation occurred when the safety related portion of the Containment Instrument Air (CIA) System was actuated. Valves CIA-V-39A and CIA-V-39B closed automatically on decreasing nitrogen pressure and Stepping Programmers (CIA-PROG-1A and CIA-PROG-1B) associated with the bottled nitrogen supply were initiated. The ESF actuation occurred when a Rupture Disk (CN-RD-1B) on the normal nitrogen supply Storage Tank (CN-TK-1) blew resulting in a pressure decrease in the system.<br /><br /> At 1448 hours Plant Operators took immediate corrective action to line up the "A" Rupture Disk (CN-RD-1A) and Relief Valve (CN-RV-1A) which isolated the blowdown of the CN system. Action was also taken to manually valve in one of the nitrogen bottles to maintain the "A" header above 150 psig. <br /><br /> Corrective actions were also taken to replace the blown rupture disk and to test the relief valves for proper operating pressure. In addition an Engineering evaluation will be performed to identify methods of eliminating rupture disk failures. <br /><br /> The root cause of the event is indeterminate. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971991017 | Columbia | 07/08/1991 | 06/09/1993 | 9306170211 | <strong>Auto Start of Emergency Diesel Generators While On Backfeed. Undervoltage Was Initiated By A 500 KV Grid Disturbance. Root Causes Are Personnel Error and Equipment Design</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1991, at 0113 hours, Operations personnel responded to the automatic start of the Division 1 and 2 Emergency Diesel Generators. The Diesels started due to undervoltage conditions on their respective vital power buses. The undervoltage condition resulted when a ground fault occurred in the off-site 500KV system. Misalignment of protective relay selector switches at a Bonneville Power Administration (BPA) substation precluded primary protective relays from immediately isolating the faulted line. Backup relaying action to isolate the fault also de-energized the WNP-2 backfeed power source and plant buses. Transfer to the Startup power source did not occur since the transfer logic was not satisfied. WNP-2 undervoltage relays acted to transfer critical bus power to the Backup transformer. <br /><br /> Operations personnel restored station power to the Startup source at 0136 and reestablished Shutdown Cooling at 0156. <br /><br /> The root causes are personnel error on the part of substation operations personnel and substation equipment design deficiencies. Substation personnel are not WNP-2 employees. Personnel and hardware related corrective actions are being pursued by substation management. WNP-2 will monitor the completion of BPA corrective actions. Further, WNP-2 will perform engineering review to confirm existing relating is sufficient to protect the unit if a similar event had occurred while at power.
3971991018 | Columbia | 07/12/1991 | 08/12/1991 | 9108220273 | <strong>Control Room Emergency Filtration and Standby Gas Treatment System Carbon Absorber Surve llances Not In Compliance With Tech. Spec. Due to Less Than Adequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1991 it was determined that the method for implementing the surveillance requirements pertaining to the Control Room Emergency Filtration System carbon absorber was not in compliance with the Technical Specifications. The removed carbon was not being sampled and tested upon replacement as required by Technical Specification 4.7.2. This discrepancy was discovered when a Plant Maintenance Engineer questioned the sampling requirement when the carbon was being replaced during a recent 18-month surveillance test for Division A of the system. On August 8, 1991, as a result of a further corrective action for this event, one additional reportable instance was identified with regard to the Standby Gas Treatment (SGT) System. From an evaluation of other potential areas of concern, it was determined that on April 18, 1990 the carbon was replaced in the SGT, Division B, absorber filter and a sample was not tested. <br /><br /> The cause of these events was less than adequate procedures due to misinterpretation of the Technical Specification requirements for ensuring that the efficiency of the carbon absorber met the provisions and intent of Regulatory Guide 1.52. The Control Room Emergency Filtration System procedures provided the option of removal of the carbon absorber in lieu of testing, but did not require followup testing. The Standby Gas Treatment System procedures did not specify that followup testing was required if the carbon was to be replaced.
3971991019 | Columbia | 07/16/1991 | 03/18/1993 | 9303220230 | <strong>Technical Specification Violation For Failure To Report Out Of Service Time Of Seismic Monitor</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1991 Plant Management determined that the failure to report five periods in excess of 30 days of inoperability of the Reactor Vessel Head Seismic Monitor was a violation of WNP-2 Plant Technical Specifications. During each of the past five annual Maintenance and Refueling Outages, beginning in 1986, the Monitor was inoperable due to the Space Frame, to which the Monitor is attached, being moved to a temporary location so that refueling and in-vessel outage work could be accomplished. <br /><br /> There are two root causes for this event. The design which located the Seismic Monitor on the Space Frame did not meet the standard Technical Specification requirement for the instrument to be operable at all times. The Plant Procedure used to remove the Space Frame had no steps to inform the Shift Manager of the inoperability of the Monitor. <br /><br /> Corrective action includes revising the Plant procedure to include a step to notify the Shift Manager when the Space Frame is moved. <br /><br /> There is no safety significance associated with this event because the Monitor has no safety immediate function.
3971991020 | Columbia | 07/26/1991 | 08/15/1991 | 9108220223 | <strong>Residual Heat Removal (RHR) "B" Valves not Operable Under All Fire Protection (Appendix R) Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1991 an engineering review identified an unanalyzed condition existed in the 10CFR50 Appendix R Fire Protection design. The capability to shutdown the plant in the event of a fire in the main control room could be jeopardized due to a "hot short" in the control circuits associated with the "B" Residual Heat Removal (RHR) valves. This "hot short" would have to occur after the start of the postulated fire while plant operators were traveling to the remote shutdown room from the main control room. After this brief period of time, the transfer switches are activated switching control power from circuits that could be damaged in the control room. It is postulated that during this time the valves could be physically damaged due to loss of the protection provided by the limit and torque switches. <br /><br /> The cause of this event was a design deficiency. The root cause was an inadequate design review. <br /><br /> Corrective action is being taken to prepare a design change and implement wiring changes on the impacted valves. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971991021 | Columbia | 08/01/1991 | 08/30/1991 | 9109110142 | <strong>Tritium Not Sampled at the Main Plant Vent During Startup, Shutdown and Thermal Power Change Evolutions as Required by the Technical Specifications due to Less Than Adequate Procedure/Procedure Review</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1991 it was determined that tritium sampling for the Main Plant Release Point (Vent) was not being performed during startup, shutdown and 15 percent power change evolutions as required by the Plant Technical Specifications. Sampling and analyzing for tritium was, however, being performed on a weekly basis as required by the Technical Specifications. This discrepancy was discovered by Plant Chemistry personnel during procedure verification efforts associated with implementation of NRC Generic Letter 89-01, which provides guidance for relocating the procedural details of the Radiological Effluent Technical Specifications (RETS) to the Offsite Dose Calculation Manual (ODCM).<br /><br /> The cause of this event is less than adequate procedure/procedure review in that the procedure for grab sampling following shutdown, startup and thermal power changes never included the requirement to sample for tritium.<br /><br /> Immediate corrective action consisted of changing the procedure to include the requirement to sample for tritium following shutdown, startup and thermal power changes. Further actions are currently being evaluated and will be resolved as part of the corrective action process for LER 91-013, "Technical Specification - Surveillance Procedure Verification Program Identification of Nonconforming Conditions."
3971991022 | Columbia | 09/05/1991 | 10/07/1991 | 9110160168 | <strong>Residual Heat Removal (RHR) System Shutdown Cooling Isolation On High Suction Line Flow Due To Differential Pressure Instrumentation Drift</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991 at 1122 hours while the Plant was shut down for an outage, the inboard Residual Heat Removal (RHR) System Shutdown Cooling Supply Valve (RHR-V-9) automatically isolated on a high suction line flow signal while Plant Operators were realigning RHR System shutdown cooling from Loop B to Loop A. Closure of RHR-V-9, a Nuclear Steam Supply Shutoff System (NSSSS) containment isolation valve, isolated and tripped RHR Shutdown Cooling Loops A and B which were in service at the time. <br /><br /> The cause of this event was instrumentation drift pertaining to Differential Pressure Indicating Switch RHR-DPIS-12B (RHR Shutdown Cooling Supply Leak Detection High Flow Indicator). As an immediate corrective action Plant Control Room Operators took appropriate steps to re-align the system and, at 1202 hours, one loop of RHR Shutdown Cooling (Loop B) was placed back into service, well within the two hours allowed for shutdown cooling to be out of service.
3971991023 | Columbia | 09/06/1991 | 10/07/1991 | 9110160214 | <strong>High Pressure Core Spray (HPCS) System Pump Suction Valve Switchover Actuation During Maintenance Testing Due to Less Than Adequate Planning and Scheduling</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1991 at 1218 hours while the Plant was shutdown for an outage, a High Pressure Core Spray (HPCS) System pump suction switchover from the Condensate Storage Tanks to the Suppression Pool occurred during maintenance testing.<br /><br /> Plant configuration at the time was such that HPCS suction was lined up to the Condensate Storage Tanks (CSTs) with CST Suction Valve HPCS-V-1 open and Suppression Pool Suction Valve HPCS-V-15 closed, the normal system lineup. The switchover, an Engineered Safety Feature (ESF) actuation, involved the automatic closure of HPCS-V-1 and the opening of HPCS-V-15. <br /><br /> At the time of the event Plant Instrument and Control (I&C) Technicians were in the process of obtaining reference voltage readings on Condensate Storage Tank Level Switches HPCS-LS-3A and HPCS-LS-3B. However, when the Plant I&C Technician connected the first lead of a voltmeter to HPCS-LS-3A the HPCS suction valves
3971991024 | Columbia | 09/09/1991 | 10/09/1991 | 9110240006 | <strong>Unanalyzed Condition Associated With Main Steam Line Failure Outside Containment</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1991 a reportability evaluation was approved which concluded that an unanalyzed condition associated with a postulated main steam line failure outside containment had existed at WNP-2 during prior operating cycles. This condition was discovered by General Electric while performing a recalculation of the accident as a result of updated meteorological data. The unanalyzed condition was caused by the need to consider an additional iodine source term as a result of the postulated mass release through main steam line drains in the event of a high energy pipe break outside the primary containment. This unique accident scenario results in Reactor Pressure Vessel (RPV) depressurization and an increased radiological source term due to iodine spiking that is not usually associated with a main steam line break.
3971991025 | Columbia | 09/11/1991 | 03/20/1992 | 9203250329 | <strong>A Train Of The Containment Atmosphere Control System Rendered Inoperable Longer Than Allowed By The Technical Specifications Due To Loss Of Oil In Hydrogen Recombiner Blower</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1991, a Plant Technical Engineer determined that Train A of the Containment Atmosphere Control (CAC) System, i.e., hydrogen recombiner, had been inoperable longer than the 30 days allowed by the Technical Specifications due to a loss of the oil from the recombiner blower caused by a drain plug vibrating free. Based on immediate failure of the recombiner blower during a surveillance test, it was concluded that the plug vibrated free during the previous surveillance test. This resulted in approximately four months of Plant operation with one train of the CAC System inoperable. <br /><br /> The immediate corrective action was to repair the inoperable CAC Train A and lockwire the drain plugs in the Train A recombiner blower. <br /><br /> The root cause for failure of the CAC train was less than adequate procedures for reassembly of the blower. <br /><br /> Corrective actions include: 1) lockwires have been installed on the drain plugs to the Train B hydrogen recombiner blower, 2) change the appropriate documentation to require the drain plugs in each recombiner blower to be properly installed and lockwired, and 3) a Maintenance and Operations Bulletin will be issued advising use of positive locking ability on critical pipe plugs of vibrating equipment. <br /><br /> The safety significance of this event is negligible because CAC Train B was operable and only one train is required to mitigate the consequences of a postulated design basis accident.
3971991026 | Columbia | 09/18/1991 | 10/16/1991 | 9110280241 | <strong>Reactor Water Cleanup System Isolation Due To Failed Component In The Leak Detection System</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1991 at 2351 hours, with the Plant shutdown for an outage, the Main Control Room received alarms indicating Reactor Water Cleanup (RWCU) System heat exchanger room high temperature, Leak Detection (LD) System high differential flow rate and LD System Division I trouble. At the same time, RWCU Outboard Isolation Valve RWCU-V-4 automatically closed, an Engineered Safety Feature (ESF) actuation, and pump RWCU-P-1B tripped. The reason for RWCU-V-4 closure was due to a failed electronic component in a Leak Detection (LD) System monitor, which provides input into the RWCU isolation logic. <br /><br /> Following the RWCU System isolation, Plant personnel performed a system walkdown and an investigation. After verifying that no actual leakage existed, Plant Control Room Operators bypassed the high temperature trip for RWCU-V-4 and restored the RWCU System to service. <br /><br /> Further corrective actions consisted of replacing a printed circuit input card in Leak Detection Monitor LD-MON-1A and sending the defective input card to the manufacturer (General Electric) for further analysis. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971991027 | Columbia | 09/30/1991 | 11/06/1991 | 9111180031 | <strong>Jet Pump Operability</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1991 it was concluded, based on the results of a Reportability Evaluation, that the previously accepted understanding of Technical Specification requirements for jet pump testing in Mode 2 were not in literal compliance with the Plant Technical Specifications.<br /><br /> On September 26, 1991 at 1636 hours WNP-2 entered Operational Condition 2. At 2338 hours on September 29, 1991 WNP-2 entered Operational Condition 1. On September 30, 1991 a question on jet pump operability and surveillance applicability in Operational Conditions 1 and 2 below 25% of rated thermal power was raised. It was concluded after extended evaluation that the Technical Specification requires performance of the testing within 24 hours after entry into Mode 2. <br /><br /> The immediate corrective actions for this event was that plant startup procedures were deviated to require performance of the surveillance procedure within 24 hours after entry into Mode 2 but prior to exceeding 25% of rated thermal power.<br /><br /> The root cause for this event was procedures less than adequate/instructions ambiguous. The Technical Specification for jet pumps does not clearly define when operability must be demonstrated. In addition, plant procedures failed to provide sufficient information to clearly define when the Specification is applicable.<br /><br /> This event posed no threat to the health and safety of the public or plant personnel since testing confirmed the operability of the jet pumps.
3971991028 | Columbia | 09/30/1991 | 10/30/1991 | 9111060116 | <strong>Containment Airlock Seal Test Not Performed in Allowable Time Period</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1991 at 1036 hours the containment airlock door seal leakage test required by Technical Specification 3/4.6.1.3 was not performed within the allowable surveillance interval. This is a deviation from the plant's Technical Specifications and is reportable in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B). <br /><br /> WNP-2 entered Mode 2 from Mode 4 at 1636 hours on September 26, 1991. From that time the plant had 72 hours (plus 25% or 18 hours) to complete the required airlock seal test. The test was completed approximately four hours after expiration of the Technical Specification allowed surveillance interval, but within the 24 hour period provided in Action Statement 3.6.1.3.c. <br /><br /> The root cause of this event is personnel work practices less than adequate in that an intended or required verification was not performed. <br /><br /> A procedurally required verification that the airlock seal test be performed in the allotted time period was not satisfied. <br /><br /> Corrective actions include: 1) Immediate performance of the required testing within the Action Statement time requirements; 2) Deviations to plant startup procedures to include specific guidance and requirements to ensure the test is performed prior to entry into the applicable Operational Condition; and 3) This LER will be required reading for Operations personnel.
3971991029 | Columbia | 10/31/1991 | 03/31/1992 | 9204080113 | <strong>Inadequate Primary Containment Hydrogen Recombiner Recycle Flow Control</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1991, a reportability evaluation was completed that concluded that a problem associated with flow control of the Primary Containment Hydrogen Recombiners was reportable. A contract engineer, performing a setpoint calculation review, had discovered that incorrect Containment Atmospheric Control (CAC) Recycle Flow Control controllers (CAC-FC-67 A/B) were installed for both divisions in the control room. The plant design and operating procedures required these instruments to be used in the automatic mode of operation to control recombiner recycle flow. If these incorrect controllers had been used in the automatic mode, they would not have controlled recycle flow which could have resulted in a reduced recombination rate or possible system shutdown due to excessive recombination.<br /><br /> Immediate corrective action was taken to change plant procedures requiring operation of these instruments in the manual mode. This allowed plant operators to control recycle flow from the control room by manually positioning the Recycle Flow Control Valve (CAC-FCV-6 A/B). <br /><br /> The root cause of this event was a less than adequate design and design change process during plant construction/startup. A second cause was less than adequate testing programs and procedures.
3971991030 | Columbia | 11/04/1991 | 11/27/1991 | 9112050003 | <strong>Technical Specification Required Plant Shutdown due to Reactor Pressure Bou dary Leakage Through Defective Weld on Residual Heat Removal System Drain Line Piping</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991 at 0423 hours, an inspection team that was performing a routine 1000 psig drywell inspection during startup from an outage, informed the Shift Manager that a small leak (approximately 20 drops per minute) had been identified in a welded connection between a Residual Heat Removal (RHR) System drain valve and the RHR, Loop A, Shutdown Cooling return line. The Shift Manager determined that this condition represented pressure boundary leakage.<br /><br /> Although the leakage could have been isolated by manually closing an RHR isolation valve, the decision was made by Plant Management to declare an Unusual Event and commence a reactor shutdown because of the leakage and the extended length of time required to close the valve and isolate the leakage from the reactor pressure coolant boundary. At 0454 hours an Unusual Event was declared and Plant Control Room Operators commenced shutdown of the Plant. As immediate corrective actions, the Plant was manually scrammed at 0525 hours and, at 0608 hours, the manual isolation valve was closed to isolate the leakage. At 0618 hours, the Unusual Event was terminated.
3971991031 | Columbia | 11/04/1991 | 11/27/1991 | 9112050002 | <strong>Intermediate Range Monitors Control Rod Block Channel Calibrations Not Performed At The Required Frequency</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991 it was determined that the procedures performed to satisfy the Intermediate Range Monitors (IRMs) Control Rod Block function quarterly (every 92 days) Channel Calibration requirements did not meet the Technical Specification definition of a Channel Calibration. This condition is a deviation from the Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). <br /><br /> As an immediate corrective action, the 18-month IRM Reactor Protection System (RPS) Channel Calibration procedures were performed. These procedures also satisfy the quarterly IRM Control Rod Block Channel Calibration requirements. <br /><br /> The root cause of this event was procedures that were less than adequate. The IRM Control Rod Block quarterly surveillance procedures did not perform a complete Channel Calibration. Procedures used to satisfy the IRM Control Rod Block function Channel Calibration requirements will be revised to include those steps necessary to constitute a Channel Calibration.<br /><br /> This event was not safety significant since an IRM Control Rod Block function Channel Calibration was performed every 18 months as part of the IRM RPS Channel Calibration. The IRM Control Rod Block function is not required for accident prevention and mitigation since the licensing basis accidents are mitigated by the RPS system trips (Average Power Range Monitors (APRMs) and IRMs). Additionally, the APRMs also provide Control Rod Block trips. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971991032 | Columbia | 11/19/1991 | 12/19/1991 | 9112300327 | <strong>Reactor Scram And ECCS Injection Due To Failure Of A Feedwater Level Control System Component</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991 at 0741, a reactor scram occurred as a result of Main Turbine Governor Valve Fast Closure initiated by a turbine trip signal from Reactor Pressure Vessel (RPV) high water level signal at Level 8 or +54.5 inches. Later, the High Pressure Core Spray (HPCS) System automatically injected as RPV level approached Level 2 (-50 inches). The high reactor water level was caused by a component failure in the non-safety related Feedwater Level Control (FWLC) System which resulted in the acceleration of the Reactor Feedwater (RFW) pumps in response to an erroneous feed-flow/steam-flow mismatch signal. The erroneous signal was caused by a failed capacitor in a Bailey Type 752 feed flow summation card in the FWLC System, which resulted in opening the 1.0 ampere circuit protection fuse. Low RPV level occurred later as a result of inadequate coolant makeup after the RFW pumps tripped at Level 8. <br /><br /> The immediate corrective action was prompt response by the Plant Operators to maneuver the Plant to a safe shutdown condition and to implement appropriate Plant procedures in a timely manner. <br /><br /> The root cause for failure of the Feed Water Level Control (FWLC) System was a failed capacitor in the feedwater summation circuitry.
3971991033 | Columbia | 11/20/1991 | 12/19/1991 | 9112300333 | <strong>250 Volt DC Bus Inoperable Due to Lack of Adequate Fuse Coordination</strong><br /><i>Abstract:&nbsp;</i>As part of the Supply System effort to upgrade the design calculations for WNP-2, a fuse coordination calculation is being prepared for the Class 1E Direct Current (DC) power systems, including the 250 volt (250VDC) system. Development of this calculation revealed that the time-current minimum melting curve for the Class 1E 250VDC bus battery main fuse, an 800 amp fuse, crosses over the time-current clearing curve for the downstream branch circuit fuse that supplies non-Class 1E loads, a 400 amp fuse. This means that it was possible, under the postulated fault conditions, that the Class 1E battery main fuse could have melted prior to the downstream branch circuit fuse clearing, isolating the 250VDC battery from the bus. Had this event occurred the 250VDC bus would have been supplied by the battery charger, but this is not considered a stable long-term condition and is not credited in the accident analyses. Because of the lack of selective coordination, the 250VDC system has been technically inoperable since the time of initial Plant startup in 1983. Operation with the 250VDC system inoperable was a condition prohibited by the Plant's Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B). This condition, lack of selective coordination on the 250VDC bus, was outside the design basis of the Plant and is reportable in accordance with 10CFR50.73(a)(2)(ii).
3971991034 | Columbia | 11/23/1991 | 12/18/1991 | 9112300329 | <strong>Residual Heat Removal (RHR) System Differential Pressure Indicating Switch Found Isolated During Surveillance Test - Cause Indeterminate</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1991 it was determined (during a reportability review) that a problem which was discovered on November 23, 1991 was reportable in accordance with the requirements of 10CFR50.73 as a condition prohibited by the Technical Specifications. On November 23, 1991 at 1858 hours, during the performance of a calibration surveillance, Plant Instrument and Control (I&C) Technicians discovered Residual Heat Removal (RHR) System Differential Pressure Indicating Switch RHR-DPIS-12B to be isolated. The function of RHR-DPIS-12B is to provide an auto-close signal to RHR-V-9 (RHR System shutdown cooling inboard isolation valve) upon receipt of a high flow indication in the shutdown cooling line. The pressure switch was required to be in service at the time of the event.<br /><br /> Immediate corrective action consisted of successfully completing the surveillance and restoring RHR-DPIS-12B to service at 1954 hours. The cause of this event is indeterminate. A comprehensive review of previous surveillances and work history associated with the instrument, and interviews of Plant personnel, did not reveal a reason for RHR-DPIS-12B to be isolated. Further corrective actions consist of 1) expanding the scope of a Component Status Change Request Form to include valve manipulations during instrument venting evolutions, 2) discussing the use of the Component Status Change Request during I&C Department shop meetings, and 3) issuing a letter describing this event to Operations, Maintenance and Plant Technical personnel. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
3971991035 | Columbia | 12/20/1991 | 01/15/1992 | 9201240151 | <strong>Manual Scram Due to Reaching Technical Specification Limit For Reactor Coolant Conductivity - Main Condenser Tube Leak</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1991 at 1250 hours the Plant was manually scrammed to complete a controlled shutdown due to high reactor coolant conductivity. During the event period, Plant personnel were in the process of attempting to identify the source of a suspected Main Condenser tube leak. This troubleshooting effort was being performed as a result of two conductivity excursions that had recently occurred, but where Technical specification limits were not reached. <br /><br /> During troubleshooting efforts, a leak of approximately 65 gpm developed in Section A of the Main Condenser, and conductivity levels increased. Efforts by Plant personnel to control the conductivity excursion by reducing reactor power and securing one of three Circulating Water (CW) System pumps were unsuccessful. Accordingly, Plant Control Room Operators took appropriate and timely action to shutdown the Plant and maneuver to the cold shutdown condition. <br /><br /> The cause of this event was a failed tube in the Main Condenser. An axial rack, approximately 8 to 12 inches in length, was later discovered on an interior tube. Corrective actions consist of 1) plugging the failed tube and performing sonic leak testing of all condenser tubes, 2) performing a Management Evaluation to resolve problems associated with conductivity excursions, and 3) performing Nondestructive Examination (Eddy Current Testing) of tubing during the Spring 1992 Maintenance and Refueling Outage. This event is reportable in accordance with 10CFR50.73 as a completion of any shutdown required by the Plant Technical Specifications.
3971991036 | Columbia | 12/26/1991 | 02/12/1992 | 9202190359 | <strong>Missed ASME Section XI Surveillance</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1991, a missed ASME Section XI Inservice Test for Fuel Pool Cooling (FPC) relief valve, FPC-RV-117B, was determined to violate the requirements of Technical Specification Sections 4.0.2 and 4.0.5. This oversight was identified by the In-Service Testing (IST) Program Leader on December 20, 1991. <br /><br /> The initial corrective action was to declare FPC-RV-117B inoperable. There are no Technical Specification operability requirements for the Fuel Pool Cooling System, therefore no action statements were required to be entered. <br /><br /> The root causes for this event were identified to be Managerial Methods Did Not Ensure Sufficient Interdepartmental Communication, and Inadequate Documentational Provisions in the procedure resulted in inadequate verification that program requirements were satisfied.<br /><br /> The corrective actions include performing the required ASME surveillance testing on FPC-RV-117B, and revising the affected Plant surveillance procedure to include a description of the program requirements, assignment of responsibilities, and documentation verification provisions. <br /><br /> There is no safety significance associated with this event. There was no condition that challenged the operation of this relief valve. Testing on January 27, 1992 verified that the valve was capable of performing its safety function. This event posed no threat to the health or safety of the public or of Plant personnel.
4001991002 | Harris | 03/05/1991 | 04/04/1991 | 9104100044 | <strong>Technical Specification Violation Due to One Train of Reactor Coolant Pump Underfrequency Reactor Trip Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1991, it was determined that the underfrequency signals from the A and C Reactor Coolant Pumps (RCPs) to the B Train of the Solid State Protection System (SSPS) would not function. This made the Underfrequency-Reactor Coolant Pump reactor trip inoperable on the B Train of SSPS. This placed the plant into Technical Specification (TS) 3.0.3 and a plant shutdown was commenced. Troubleshooting determined that the umbilical cord in the A and C RCP breakers which provide the B train signals were not connected. The umbilical cords were connected, the required surveillances performed, and the plant exited TS 3.0.3. The investigation determined these umbilical cords were disconnected during an outage in November 1990. Training and procedure changes are being made to prevent recurrence of this event. <br /><br /> This event is being reported in accordance with 10CFR50.73 (a) (2) (i) (B) as a violation of Technical Specifications.
4001991003 | Harris | 01/21/1991 | 03/19/1991 | 9103270214 | <strong>Missed Surveillance Test During Emergency Diesel Generator Fuel Oil Sampling</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1991, a fuel oil shipment for the Emergency Diesel Generators arrived on-site. Technical Specifications contain specific sampling and analysis requirements for this oil, prior to off-load. During the sample process the required test to determine kinematic viscosity was inadvertently waived. The cause of this omission was an error during communications between laboratory personnel and technicians in the field. This condition was discovered during a routine documentation review by the Chemistry Foreman on 2/21/91. Upon discovery, the remaining sample was immediately tested for viscosity and was found to meet the applicable Technical Specification requirements. This event is being reviewed by the Chemistry Unit and the applicable procedures will be revised to provide more specific guidance regarding fuel oil sample and analysis requirements. <br /><br /> This event is being reported in accordance with 10CFR50.73 (a)(2)(i)(B) as a Technical Specification violation.
4001991004 | Harris | 03/14/1991 | 04/12/1991 | 9104150295 | <strong>Entry into Technical Specification 3.0.3 due to failed performance test on "B" ESCW system while "A" CSIP was inoperable.</strong><br /><i>Abstract:&nbsp;</i>On 3/14/91, "B" train Essential Services Chilled Water System (ESCW) was declared inoperable due to unsatisfactory performance test results. This subsequently rendered all "B" train Engineered Safety Features components inoperable as well. During this same time period, the "A" train Charging/Safety Injection Pump was inoperable and under clearance for Maintenance. With both CSIP's inoperable, (CSIP) entry into Technical Specification (TS) 3.0.3 was required. "B" train ESCW was restored eight minutes later and TS 3.0.3 was exited. Investigation revealed that similar problems were also encountered during testing on 2/12/91. The causes for these events were the inability to verify seating of a check valve and uncertainty regarding this check valve's effects on chiller operability. Corrective actions include revising appropriate procedures and evaluating the method used to determine check valve closure. These events are being reported in accordance with 10CFR50.73 (a) (2) (i) (B) as conditions prohibited by Technical Specifications.
4001991005 | Harris | 03/13/1991 | 04/12/1991 | 9104150186 | <strong>Entry into Technical Specification 3.0.3 due to failed performance test on "B" Emergency Sequences while "A" CSIP was inoperable</strong><br /><i>Abstract:&nbsp;</i>On 3/13/91, during testing of the 1B-SB Sequencer, the "B-Program" relay contacts failed to close. This rendered "B" train engineered safety features (ESF) components actuated by the sequencer inoperable. During this same time period, the "A" train Charging/Safety Injection Pump (CSIP) was also inoperable for maintenance. With the "A" train and "B" train CSIP's inoperable, control room personnel determined that entry into Technical Specification 3.0.3 was required. Efforts to restore "A" CSIP operability were immediately taken and 3.0.3 was exited within approximately 10 minutes. The 1B-SB sequencer was also restored to operable status 5 hours and 30 minutes later upon replacement of the faulty relay and subsequent successful testing. The cause of this event appears to have been an isolated contact failure in the "B" program relay.<br /><br /> This is being reported in accordance with 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by Technical Specifications.
4001991006 | Harris | 03/19/1991 | 04/17/1991 | 9104230306 | <strong>Technical Specification violation due to missed shutdown margin verification while testing Source Range Nuclear Instruments</strong><br /><i>Abstract:&nbsp;</i>On 3/19/91, during surveillance testing on the source range nuclear instruments, control room operators did not verify shutdown margin requirements per Technical Specifications (TS). Upon discovery, shutdown margin was immediately verified to be adequate. This condition was caused by a misinterpretation of TS requirements. Corrective actions will include a revision to the appropriate procedures and dissemination of this information to operations personnel to clarify the requirements of this TS. <br /><br /> This is being reported in accordance with 10CFR50.73 (a) (2) (i) (B) as a TS violation.
4001991007 | Harris | 03/25/1991 | 04/25/1991 | 9104290294 | <strong>Technical Specification Violation Due to Inappropriately Removing and ESW Pump from Service</strong><br /><i>Abstract:&nbsp;</i>On 3/25/91, at approximately 1900 hours, with the plant in Mode 5 during a refueling outage, one Emergency Service Water (ESW) pump was inappropriately removed from service for outage work. The event was discovered at 0055 hours on 3/26/91, and operability was restored by 0245 hours. <br /><br /> Technical Specifications require two operable Residual Heat Removal (RHR) loops when in Mode 5 with reactor coolant loops not filled. Site Technical Specification Interpretations specify that Component Cooling Water (CCW) and ESW pumps and flowpaths are required to support RHR. <br /><br /> This event was attributed to personnel/management error and will be reviewed with operations management personnel. Technical Specifications for ESW and CCW will be annotated to indicate applicability of Technical Specification Interpretation 90-001.
4001991008 | Harris | 04/03/1991 | 10/13/1992 | 9210210170 | <strong>Common Cause Failure of High Head Safety Injection Alternate Miniflow</strong><br /><i>Abstract:&nbsp;</i>Failures which would have affected both trains of High Head Safety Injection were identified by testing performed in 1991, during the third refueling outage (RFO-3). The failures involved alternate miniflow lines for both Charging/Safety Injection Pumps (CSIPs). These alternate miniflow (AMF) lines are designed to protect the CSIPs, which provide high head safety injection as well as normal charging, from deadhead operation during accidents where the Reactor Coolant System (RCS) repressurizes after safety injection is actuated. Damage to relief valves and drain connections on these AMF lines were such that a significant portion of the safety injection flow would have been diverted from the RCS. The system was repaired and procedures were revised to preclude recurrence. In August, 1992, the decision was made to modify the AMF lines to eliminate the use of relief valves. Subsequent testing during RFO-4 supported the modification plan. The modified system will use orifices and revised motor-operated valve logic to protect the CSIPs from deadhead operation. This report satisfies CP&L's 10CFR21 reporting requirements. <br /><br /> This event was initially reported in accordance with 10CFR50.73(a)(2)(v) as an event that alone could have prevented the fulfillment of a safety function.
4001991009 | Harris | 05/21/1991 | 06/20/1991 | 9106250064 | <strong>AFW actuation due to Steam Generator Hi-Hi Level alarm that was inadvertently generated During troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On 5/21/91, troubleshooting of the Steam Generator (SG) level instrumentation resulted in the generation of a Hi-Hi SG level signal. <br /><br /> This caused a Feed Water Isolation Signal which by design tripped the running Main Feed Pump and started both motor driven Auxiliary Feed Water Pumps. The control room staff immediately took actions to verify proper system response and stabilize SG levels. The cause of this event was personnel error on the part of the maintenance personnel performing the trouble shooting. Corrective actions will consist of counseling the involved technicians, reviewing the incident with other appropriate personnel and developing a procedure that provides specific guidance for troubleshooting activities. <br /><br /> This condition is being reported as an unplanned Engineered Safety Feature Actuation in accordance with 10CFR50.73(a)(2)(iv).
4001991010 | Harris | 06/03/1991 | 07/03/1991 | 9107100289 | <strong>Reactor Trip During Surveillance Testing and One Reactor Trip Breaker Failed To Open</strong><br /><i>Abstract:&nbsp;</i>The plant received an automatic Reactor Trip on RCS Low Flow during the performance of a maintenance calibration procedure on an RCS flow transmitter. All rods fully inserted on the trip signal. The "A" Reactor Trip Breaker did not open on the automatic reactor trip signal but did open on a subsequent manual trip signal. The failure of the "A" Reactor Trip Breaker to open was due to a failed undervoltage output driver card in the "A" Solid State Protection System. The failure of the undervoltage output driver card was the same as described in IE Notice 85-13 and had apparently occurred during maintenance on May 18, 1991. The failed undervoltage output driver card was replaced with a modified card which prevents this failure mechanism. <br /><br /> This event is being reported as a Technical Specification violation and Engineered Safety Features actuation per 10CFR50.73 (a)(2)(i)(B) and 10CFR50.73 (a)(2)(iv).
4001991011 | Harris | 05/12/1991 | 06/10/1991 | 9106130264 | <strong>High Boron Concentration in Refueling Water Storage</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.1.2.1 requires one boration flowpath be available while in Mode 5 and 6. It was identified that the required boration flowpath was functional but not OPERABLE for six days because the Refueling Water Storage Tank boron concentration was 2217 ppm. This exceeded the required boron concentration range of 2000 - 2200 ppm. During this time a flowpath from the Boric Acid Tank was available, if required. Although this flowpath was available, the surveillance on this flowpath was not current, therefore, this flowpath could not be considered OPERABLE.<br /><br /> This event is being reported in accordance with 10CFR 50.73 (a) (2) (i) (B) as a Technical Specification violation.
4001991012 | Harris | 05/15/1991 | 06/14/1991 | 9106190155 | <strong>Unplanned Actuation of Auxiliary Feed Water (ESF actuation) due to failure of "A" Main Feed Pump to start</strong><br /><i>Abstract:&nbsp;</i>On 5/15/91, during plant heat-up, an attempt to start the "A" main feedwater pump (MFP) was made to provide make-up to the steam generator. This pump start was unsuccessful. At the same time, the "B" MFP was under clearance and the "loss of both MFP's" logic was satisfied to actuate an automatic auxiliary feedwater (AFW) pump start signal. The "A" AFW pump started as required. Control room personnel promptly secured the "A" AFW pump to stabilize steam generator level. Investigation was unable to determine the cause of the "A" MFP's failure to start. This is being reported in accordance with 10CFR50.73 (a)(2)(iv) as an unplanned actuation of an engineered safety feature component.
4001991013 | Harris | 05/15/1991 | 06/14/1991 | 9106190146 | <strong>Control Rod Shutdown Bank "C" was withdrawn fully and all other control rods were withdrawn six steps.</strong><br /><i>Abstract:&nbsp;</i>In preparation for cooldown to repair a steam leak, Control Rod Shutdown Bank "C" was withdrawn fully and all other control rods were withdrawn six steps. Nuclear Instrument N-43 was in the tripped condition for installation of monitoring instrumentation during post-refueling start-up testing. When surveillance test instruments were disconnected following Reactor Coolant System resistance temperature detector testing, a spurious Overtemperature Delta Temperature signal was generated causing a reactor trip. The potential for a reactor trip signal during restoration from the surveillance test had been previously discussed by Operations and Maintenance personnel, but the information was not communicated to the shift operators. The procedure governing the RTD surveillance test provided precautions during data acquisition, but failed to identify the risk of generating a trip signal during restoration. This event will be discussed with maintenance and operations personnel and the surveillance test procedure will be revised to include appropriate precautions during restoration.
4001991015 | Harris | 05/19/1991 | 06/18/1991 | 9106250241 | <strong>AFW actuation due to improperly set feed flow transmitter. (Unplanned ESF actuation)</strong><br /><i>Abstract:&nbsp;</i>On 5/19/91, a signal provided by a feed flow transmitter caused the trip of the only running Main Feed Water Pump. This condition satisfied the logic for an automatic actuation of the Auxiliary Feed Water system. The control room staff immediately verified proper system response by ensuring that both motor driven pumps had started as required. This event was caused by an improperly set signal dampening device in the main feed water pump suction flow transmitter. Trouble shooting and subsequent adjustments to this device resulted in successful testing and operation of the flow transmitter and should prevent recurrence of this condition.
4001991016 | Harris | 08/08/1991 | 09/09/1991 | 9109190010 | <strong>Potentially degraded residual heat removal capability due to CCW relief valve lifting and failing to reseat.</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1991 to support testing of a Component Cooling Water (CCW) flow indicator, the "B" CCW pump was started. ("A" CCW pump was already in operation). The start of this additional pump created a momentary pressure spike that caused three system relief valves to open. A decrease in surge tank level was also observed which indicated that at least one of the relief valves had not reseated. This was determined to create a potential for degraded residual heat removal capability under certain accident conditions. There are two primary causes for this event. The cause for the relief valves lifting upon the start of the second pump was an error during initial system design. The cause for the relief valves not reseating was the improper setting of the relief valve nozzle ring adjustments during site maintenance activities. Immediate corrective action was to initiate CCW flow through the Residual Heat Removal (RHR) Heat Exchanger which lowered system operating pressure and would prevent lifting relief valves in the event of an automatic second pump start. Additional corrective actions included an inspection of CCW relief valves and personnel training on proper relief valve setting. Additional procedure guidance has been developed and plant modifications are being pursued to prevent recurrence. Further investigation was also undertaken to determine if similar problems exist in other plant systems.
4001991017 | Harris | 08/27/1991 | 09/24/1991 | 9110010101 | <strong>Technical Specification violation due to missed composite sample During release of Secondary Waste Sample Tank.</strong><br /><i>Abstract:&nbsp;</i>At 1607 hours on 8/27/91, a continuous release from the Secondary Waste Sample Tank (SWST) was initiated. Technical Specifications 3.11.1.1 Table 4.11-1 Action 2.b requires a continuous composite sample proportional to the discharge flow rate from the SWST while conducting a continuous release. Site Chemistry personnel were notified at this time to start the composite sampler and adjust the flow rate corresponding to the release rate. The Chemistry Technician responsible for this action became distracted with other shift duties and did not initiate the required sample. The release was secured at 2345 hours and it was discovered at this time that the sampler had never been started. <br /><br /> The cause of this event was personnel error on the part of the Chemistry Technician due to not initiating a composite sample. Immediate corrective actions were to verify that the effluent stream contained no radioactivity. This was confirmed by the fact that the SWST radiation monitor, which was functioning properly during the release, did not detect any abnormal activity levels. Results of an isotopic analysis that had been performed on this water prior to being transferred to the SWST were also reviewed. These results also indicated no abnormal activity levels. Additional corrective actions will include a procedure revision and a review of this incident with applicable personnel.
4001991018 | Harris | 09/23/1991 | 10/18/1991 | 9110250028 | <strong>Personnel Air Lock Surveillance Interval Exceeded</strong><br /><i>Abstract:&nbsp;</i>An error was identified in the scheduling of Surveillance Requirement 4.6.1.3.b.1 which requires an air lock leakage test once per 6 months. This Surveillance Requirement specifies that the provisions of Specification 4.0.2 are not applicable, therefore this test is required to be scheduled once every 6 months without a 25% grace period allowed. The Emergency Air Lock was scheduled as specified, but the Personnel Emergency Air Lock was inadvertently scheduled with the 25% grace period allowed. A review of the testing history for this air lock revealed one instance, in May 1988, where 6 months was exceeded by 3 days. The schedule for the Personnel Air Lock has been revised to eliminate the use of a 25% grace period. Other Specifications where TS 4.0.2 is not applicable were reviewed to ensure they are properly scheduled. This event was caused by personnel error during the original development of the surveillance scheduling system. <br /><br /> The safety significance of this event was minimal in that the air lock leakage rate was acceptable when tested following these events. <br /><br /> There have been no similar events reported. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a Technical Specification violation.
4001991019 | Harris | 10/22/1991 | 12/11/1992 | 9212160030 | <strong>Unplanned ESF Actuation (Containment Ventilation Isolation) due to spike on radiation monitor.</strong><br /><i>Abstract:&nbsp;</i>On 10/22/91, at 1505 hours, a Containment Ventilation Isolation signal was generated. This constituted an unplanned actuation of an Engineered Safety Feature (ESF) component. The event occurred while removing one of the four containment ventilation radiation monitors from service during surveillance testing. The control room staff immediately verified that all associated containment ventilation components had functioned as required and that no abnormal radiation levels actually existed. The system was then realigned to its normal operating lineup. The cause of the alarm signal was an inadvertent spike on one of the three radiation monitors that remained operable (RM-3561A). Troubleshooting and testing performed during Refueling Outage #4 revealed that this spike occurred due to loose electrical connections and a defective low voltage power supply circuit in the monitors 110 volt supply. These conditions were corrected and the monitor was returned to service. There were no significant safety consequences as a result of this event as the Containment Ventilation System was in the required emergency mode had an actual event occurred. This was originally reported in accordance with 10CFR50.73 (a)(2)(iv) as an unplanned actuation of an ESF component.
4001991020 | Harris | 12/04/1991 | 12/20/1991 | 9112300286 | <strong>Failure to adequately test sealed sources resulting in Technical Specification Violation.</strong><br /><i>Abstract:&nbsp;</i>On 12/4/91, during a routine review of completed test documentation, Radiation Control supervisory personnel identified a deficiency in Radiation Surveillance Test RST-010. This procedure is used for leak testing sealed sources to satisfy Technical Specifications (TS) 4.7.9.1 and 4.7.9.2. This process includes smearing these sources and analyzing the smears with an instrument capable of detecting .005 microcuries of contamination per test sample. It was determined that the instrument used for this analysis did not have the required sensitivity level to detect the low energy emissions produced by sources that contain Nickel-63 and Iron-55 isotopes. These sources are used in the plant access explosive detectors and an alloy analyzer used for non-destructive examination (respectively). Each of the twelve sources that contain these elements were smeared again and were analyzed with a liquid scintillation counter that has the required sensitivity level. No contamination levels in excess of TS limits were found. The cause of this event was a procedural deficiency in RST-010. Adequate guidance was not provided in this procedure to ensure that the proper type of instrument was used for analysis. Corrective actions will include a revision to RST-010 and training for applicable radiation control personnel on this revision. There were no safety consequences as a result of this event. This is based on the fact that no contamination levels were found in excess of TS limits, which would have indicated excessive sealed source leakage. <br /><br /> This event is being reported in accordance with 10CFR50.73 (a)(2)(i)(B) as a TS violation. No similar events have been reported.
4001991021 | Harris | 12/18/1991 | 01/16/1992 | 9201210195 | <strong>Technical Specification violation due to deficient containment sump leakrate computer program.</strong><br /><i>Abstract:&nbsp;</i>On 12/18/91, an error was discovered in the program utilized by the plant process computer for determination of containment sump inleakage flowrate. This error would have prevented the computer from detecting a one gallon per minute increase in flow under certain conditions, as required by Technical Specifications (TS). This condition was discovered by the control room staff during an evolution that included discharging water into the containment sump. The expected level increase was observed, but the computer generated flow rate remained unchanged at zero. The computer program was declared inoperable at this point and compensatory measures were commenced to comply with TS requirements. Investigation revealed that this condition was caused by personnel error during the development of the plant modification that installed this capability into the plant computer in September of 1988. Subsequent corrective actions included correcting the error in the computer program and restoring it to service. This is being reported in accordance with 10CFR50.73 (a)(2)(i)(B) as a TS violation. No similar events have been reported.
4091991001 | La Crosse | 07/30/1991 | 08/26/1991 | 9109040147 | <strong>Loss of 1B Essential Bus</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1991, a technician from the DPC Electrical Test and Maintenance Department (not a LACBWR employee) was on site to reset overcurrent to ground relay targets that were not reset during a recent calibration. While pointing out the features of the relays on an energized 2400-volt breaker (supplying the 1B Essential Bus), the technician demonstrated the reset function before he could be stopped from doing so by the LACBWR employee accompanying him. This action resulted in a breaker trip and a loss of the 1B Essential Bus. The 1B Emergency Diesel Generator (EDG) started and energized the 1B Essential Bus. <br /><br /> The technician immediately recognized his mistake and reset the ground relay trip. The control room operator then re-energized the essential bus from the 2400 V. supply and removed the 1B EDG from service. When the EDG control switch was placed back to "auto," however, the normal supply breaker for the essential bus tripped, and the 1B EDG started and energized the essential bus. One further attempt was then made to return the electrical system lineup to normal, but, once again, the normal supply breaker opened and the EDG started to energize the bus when placed in "auto." This time, however, the EDG output breaker failed to close, leaving the 1B Essential Bus de-energized. Equipment that had been powered from the essential bus was temporarily de-energized and the Containment Building dampers closed automatically. The NRC was notified of the incident.
4101991001 | Nine Mile Point 2 | 01/18/1991 | 02/15/1991 | 9102280266 | <strong>Primary Containment Vent And Purge Valve Isolation (Group 9 Isolation) Due To Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1991, at 1701 hours, with the reactor at 0 percent of rated thermal power and the mode switch in the "SHUTDOWN" position, Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature (ESF) actuation. This event consisted of a Primary Containment vent and purge isolation signal (group 9 isolation) from the Standby Gas Treatment System (GTS) Radiation Microprocessor (2GTS-RU105) located in the Main Stack Tower. <br /><br /> The root cause of this event was determined to be a lightning strike to the Main Stack tower resulting in a power transient/interruption to radiation monitor 2GTS-RU105. <br /><br /> Corrective actions included: returning the system to normal operational status once the isolation signal was determined not to be a high radiation condition; and troubleshooting the source of the false isolation signal.
4101991002 | Nine Mile Point 2 | 02/15/1991 | 03/14/1991 | 9103260197 | <strong>Violation of Technical Specification Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991 at 1630 hours with the reactor mode switch in "Run" at a power level of 100% rated, Nine Mile Point 2 (NMP2) Operations personnel discovered that unsampled diesel fuel oil had been added to the Division I and II Emergency Diesel Generators (EDG) fuel oil storage tanks. At the time of the discovery, the Division III EDG was inoperable due to maintenance. The NMP2 licensed operators immediately declared the Division I and II EDG's inoperable and entered the applicable Technical Specification Action Statement. An Unusual Event was declared. <br /><br /> The immediate cause for this event is human performance deficiency. The root cause is failure to follow procedure. A contributing cause was a breakdown in communication.<br /><br /> The immediate corrective action was to sample the diesel fuel oil. Other corrective actions include: an accountability meeting was held and appropriate disciplinary action will be considered with personnel involved; applicable procedures will be enhanced; and a Lessons Learned Transmittal will be written.
4101991003 | Nine Mile Point 2 | 02/14/1991 | 03/18/1991 | 9103270360 | <strong>Technical Specification Violation - Failure to Use Correct Scale ASME XI Inservice Testing Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1991, while reviewing the recently completed Inservice Quarterly Test procedure for the Residual Heat Removal System (RHS) pump 2RHS*P1B, it was reported that incorrect test equipment had been used during the performance of the test procedure. Specifically, pump inlet pressure instrumentation was not in compliance with ASME Section XI guidelines as required by the plant's Technical Specifications (T.S.). Subsequent test procedure reviews identified six additional tests performed using incorrect instrumentation. Nine Mile Point Unit 2 (NMP2) was operating at 99 percent rated thermal power with the mode switch in the "RUN" position at the time the RHS pump test discrepancy was discovered. <br /><br /> The root cause for these violations was determined to be inadequate work practices. Contributing causes were managerial methods and written communication. <br /><br /> Corrective actions include: Performing a review of previously completed surveillance test procedures; holding an accountability meeting with Operations personnel; issuing a Lessons Learned Transmittal; and revising procedures.
4101991004 | Nine Mile Point 2 | 03/22/1991 | 04/22/1991 | 9105010097 | <strong>Technical Specification Violation - Failure to Restore Structural Integrity of an ASME Component Due to Inadequate Written Communication</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1991, it was determined that Nine Mile Point Unit 2 (NMP2) had not been in compliance with the plant's Technical Specification (T.S.) requirements following a reported Reactor Core Isolation Cooling System (ICS) drain line leak. Specifically, the T.S. required actions of restoring the structural integrity of the affected ASME III Code Class 2 component to within its limits or removing it from service were not completed. At the time the leak was discovered (June 6, 1990), no immediate actions were taken to either isolate the system leak or repair the failed component. <br /><br /> The root cause for this T.S. violation was determined to be inadequate written communication. A contributing cause was training methods. Repair activity corrective actions included: generating a Problem Report; issuing an Occurrence Report; and completing defective weld repairs. <br /><br /> Additional corrective actions include: revising Administrative Procedures; issuing a Lessons Learned Transmittal; and providing technical training.
4101991005 | Nine Mile Point 2 | 03/26/1991 | 04/23/1991 | 9105010100 | <strong>Engineered Safety Feature Actuation due to Low Flow Signal Caused by Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1991 at 0755 hours, Nine Mile Point Unit 2 experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the Secondary Containment (Reactor Building) isolated and an automatic start of the Reactor Building Emergency Recirculation Unit Cooler and the Standby Gas Treatment System (GTS) was experienced. The actuation was initiated by a low air flow signal in the Reactor Building Ventilation system (HVR). At the time of the event, the reactor mode switch was in the "RUN" position (Mode 1) with the reactor operating at 100% rated thermal power. <br /><br /> The root cause of the event has been determined to be inadequate written communication (deficient procedural step). <br /><br /> The immediate corrective actions were to determine the cause of the ESF actuation, and restore the HVR system to its normal operational status. Other corrective actions include revising procedures, issuing a Lessons Learned Transmittal, and further investigation into the number of ESF actuations attributed to this system.
4101991006 | Nine Mile Point 2 | 03/30/1991 | 09/03/1991 | 9109130157 | <strong>Unusual Event Classification and Reactor Shutdown due to an Unisolated Reactor Coolant System Pressure Boundary Leak</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1991, while performing a Drywell inspection to identify the cause for an increased leakage rate from the plant's Primary Containment Drywell floor drains, an unisolable Reactor Coolant System Pressure Boundary leak was discovered. At 1401 hours, an Unusual Event emergency classification was declared and operators commenced plant shutdown. Nine Mile Point Unit 2 (NMP2) was operating at a power level of approximately 14 percent with the mode switch in the "RUN" position (Operational Condition 1) at the time the event was declared. <br /><br /> The cause for the leakage was identified as a failed 3/4 inch stainless steel flexible metallic hose on a Reactor Water Sample System line. An analysis determined the hose failure was caused by a fabrication defect. <br /><br /> Corrective actions included: generating a modification to repair/revise sample System piping; reviewing similar plant flex hose applications; and completing a failure analysis on the damaged flex hose.
4101991007 | Nine Mile Point 2 | 04/11/1991 | 05/13/1991 | 9105210280 | <strong>Two Engineered Safety Feature Actuations due to Spurious Low Air Flow Signals</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1991, at 2102 hours and April 15, 1991, at 1406 hours, Nine Mile Point Unit 2 experienced actuations of an Engineered Safety Feature (ESF). Specifically, for each actuation, the Secondary Containment (Reactor Building) isolated and the Reactor Building Emergency Recirculation Unit Cooler and Standby Gas Treatment system (GTS) started automatically. Both actuations were initiated by a low air flow signal in the Reactor Building Ventilation system (HVR). At the time of each event, the reactor mode switch was in the "RUN" position (Mode 1). On April 11, the reactor was operating at approximately 18% rated thermal power, and on April 15, the reactor was operating at approximately 100% rated thermal power. <br /><br /> The root cause of both events has been determined to be spurious low air flow signals. <br /><br /> The immediate corrective actions were to determine the cause of the ESF actuations, assess the plant for other possible initiating conditions, and restore the HVR system to its normal operational status. Other corrective actions included a calibration check of the air flow switches, and a Deviation Event Report written to Engineering.
4101991008 | Nine Mile Point 2 | 04/30/1991 | 05/30/1991 | 9106060088 | <strong>Reactor Water Cleanup System Isolation (ESF) caused by High Differential Flow Signal due to Inadequate Managerial Methods</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1991, at approximately 2055 hours, Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). This event consisted of an isolation of the Reactor Water Cleanup System (WCS). At the time of the event, the plant was at 100 percent rated thermal power with the mode switch in the "RUN" position (Operational Condition 1). <br /><br /> The isolation, initiated by a high differential flow signal, occurred as plant operators were changing WCS filter/demineralizer units. The root cause for this event has been determined to be inadequate managerial methods.<br /><br /> Immediate corrective actions were for operators to: verify the automatic response of the WCS; verify plant status as normal; and reset the isolation. Additional corrective actions includes: Issuing a Lessons Learned Transmittal and processing a Plant Change Request to install more reliable level instrumentation.
4101991009 | Nine Mile Point 2 | 05/03/1991 | 08/01/1991 | 9108070251 | <strong>Engineered Safety Feature Actuation due to a Spurious High Radiation Level Signal</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1991, at 0831 hours, Nine Mile Point Unit 2 experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the secondary Containment (Reactor Building) isolated and the Reactor Building Emergency Recirculation Unit Cooler and Standby Gas Treatment System (GTS) started automatically. The ESF actuation was initiated by a high radiation level signal in the Reactor Building Ventilation System (HVR). At the time of the event, the reactor mode switch was in the "RUN" position (Mode 1) with the reactor operating at 100% rated thermal power. <br /><br /> The root cause of the event has been determined to be inadequate welder training program content. <br /><br /> The Control Room operators implemented the Emergency Operating Procedure (EOP) for Secondary Containment control until Reactor Building radiation was verified at normal operating levels and the cause for the ESF actuation was determined to be a spurious high radiation level trip. Other corrective actions included: 1) returning the HVR system to a normal line up after welding was complete; 2) issuing guidance to welders to route their welding cables away from instrument cables; 3) discussing the grounding and routing of cables with Maintenance and Building Services welders; 4) enhancing the corporate and site welding programs; and 5) writing a site welding procedure.
4101991010 | Nine Mile Point 2 | 05/08/1991 | 06/07/1991 | 9106180275 | <strong>Reactor Core Isolation Cooling System Isolation due to a Spurious Reactor Building High Area Temperature Signal</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1991, at 0757 hours, with the reactor at 99 percent rated thermal power, and the mode switch in the "RUN" position (Operational Condition 1), Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the Primary Containment inboard isolation valves for the Reactor Core Isolation Cooling (RCIC) System isolated on a spurious Division II Reactor Building general area high temperature signal. <br /><br /> The most probable source of the spurious high temperature signal has been identified as a Panalarm (Riley) Model 86 Thermocouple Monitor. The specific cause of the signal, however, could not be determined.<br /><br /> The immediate actions taken were to: verify that a high Reactor Building area temperature did not exist; and initiate an investigation into the cause for the high temperature signal. Additional actions included: the satisfactory completion of temperature circuit functional tests; returning the RCIC System to its normal standby condition; issuing a Lessons Learned Transmittal; and conducting an accountability meeting.
4101991011 | Nine Mile Point 2 | 05/06/1991 | 06/05/1991 | 9106120350 | <strong>Technical Specification Violation, Missed Chemistry Surveillance due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 1200 hours on May 7, 1991, it was discovered that the reactor water gross Beta and Gamma activity measurements had not been performed within the required 72 hours. These measurements were required to be completed by 0040 hours on May 6, 1991, but were not completed until 0130 hours on May 7, 1991. This is a violation of station Technical Specification section 4.4.5, table 4.4.5.1(1). At the time of the event, the reactor mode switch was in the "RUN" position (Mode 1) and the reactor was operating at 100% of rated thermal power. <br /><br /> The root cause of this event has been determined to be personnel error. <br /><br /> Corrective actions include: 1) Gross Beta and Gamma activity analyses are being performed daily; 2) The methods used to track and review the completion of frequently performed Technical Specification tasks is being reviewed for improvements; 3) All Chemistry Department personnel have been informed of the missed surveillance; 4) An accountability meeting was held to ascertain corrective actions and lessons learned; 5) A Lessons Learned Transmittal will be written concerning tracking of frequently performed surveillances; and 6) A Deviation/Event Report has been written to evaluate the effectiveness of the present Lessons Learned Program.
4101991012 | Nine Mile Point 2 | 05/21/1991 | 06/20/1991 | 9106260392 | <strong>Actuation of Several Engineered Safety Features Caused by a Loss of One Offsite Power Feed, Due to Excavation at Scriba Station</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1991, at 0954 hours, Nine Mile Point Unit 2 (NMP2) experienced actuations of several Engineered Safety Features (ESF) due to a loss of one of the two offsite power feed lines. At the time of the event, the reactor mode switch was in the "RUN" position (Mode 1) and the reactor was operating at 100% rated thermal power. <br /><br /> The root cause of this event has been determined to be inadequate managerial methods. <br /><br /> Corrective actions include: (1) Stabilization of the plant in response to the loss of one 115 Kv feeder; (2) Alignment of Division I and III switchgear to the remaining number 6 line 115 Kv feeder and entry into a 72 hour Limiting Condition of Operation (LCO) per Technical specification 3.8.1.1.a; (3) Bringing of work activities related to the Scriba Station into the envelope of control of the Unit 2 Plant Manager; (4) Explicit directions from Niagara Mohawk Power Delivery Supervision with regards to Scriba Station access for any type of activity.
4101991013 | Nine Mile Point 2 | 06/03/1991 | 06/28/1991 | 9107110189 | <strong>Reactor Water Cleanup System Isolation (ESF) Caused by High Differential Flow Signal due to Inadequate System Operation</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1991, at 1717 hours, Nine Mile Point Unit 2 (NMP2) experienced actuation of an Engineered Safety Feature (ESF). This event consisted of an isolation of the Reactor Water Cleanup System (WCS). Closure of the WCS outboard isolation valve was initiated by Control Room operators immediately before a high differential flow isolation signal was received. The isolation signal occurred as plant operators were manipulating WCS filter/demineralizer units. At the time of the event, the reactor mode switch was in the "RUN" position (Mode 1) and the reactor was operating at 100% rated thermal power. <br /><br /> The root cause of this event has been determined to be inadequate system operation due to unreliable filter/demineralizer level indication.<br /><br /> The immediate corrective actions were for operators to verify automatic WCS system response and determine there was no actual WCS breach. Other corrective actions include: a change to Operating Procedure N2-OP-37; a request to have Maintenance and Operation training programs review this event; a Plant Change Request to improve level element reliability; issuance of a Temporary Modification to simplify operation; and implementation of a comprehensive system operational study.
4101991014 | Nine Mile Point 2 | 06/20/1991 | 07/17/1991 | 9107290242 | <strong>Reactor Building Isolation and Standby Gas Treatment System Initiation due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1991, at 1025 hours, Nine Mile Point Unit 2 experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the Reactor Building isolated, and an automatic start of the Reactor Building Emergency Recirculation Unit Cooler and the Standby Gas Treatment System (GTS) was experienced. The actuation was initiated by a low air flow signal in the Reactor Building Ventilation System (HVR). At the time of the event, the reactor mode switch was in the "RUN" position (Mode 1) with the reactor operating at 100% rated thermal power. <br /><br /> The root cause of this event was determined to be personnel error due to failure to follow procedure. Contributing causes were poor work practices and inadequate training. <br /><br /> Corrective actions include: investigating the cause of the low air flow signal; holding an accountability meeting with the individuals involved in the event; conducting a departmental meeting to review circumstances surrounding the event; issuing a Training Review Request; and issuing a Lessons Learned Transmittal.
4101991015 | Nine Mile Point 2 | 02/20/1991 | 12/13/1991 | 9112240261 | <strong>Standby Liquid Control System Potentially Inoperable During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1991, Nine Mile Point Unit 2 (NMP2) identified that incorrect Technical Specification ACTION requirements were being entered during Technical Specification required Surveillance Testing of the Standby Liquid Control System (SLS). The valve alignments established by the procedure could, for a brief period of time, render both SLS Divisions (1 and 2) potentially inoperable. Prior to this discovery, only one Division was being declared inoperable. At the time this condition was reported, the mode switch was in the "RUN" position (Condition 1) with the reactor operating at approximately 100 percent rated thermal power. <br /><br /> The root cause for this condition was determined to be inadequate procedure development and review.<br /><br /> Corrective actions include: 1) revising the quarterly Surveillance Test Procedure to provide test personnel with a CAUTION statement specifying required actions if a system initiation occurs, and a plant impact statement to specify system operability status during testing; 2) providing information for input into the Institute of Nuclear Power Operations (INPO) Nuclear Network; and 3) reviewing system surveillance tests for similar test conditions.
4101991016 | Nine Mile Point 2 | 07/02/1991 | 11/21/1991 | 9112030419 | <strong>Loss of Configuration Control Caused by Mispositioned Valves due to Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1991, at 0545 hours, during the performance of procedure N2- OSP-SWP-M001, "Service Water Valve Position Verification", Nine Mile Point Unit 2 (NMP2) Operations personnel discovered that the cooling water inlet and outlet valves for Reactor Building unit cooler 2HVR*UC404D were not in their normal operating positions. These conditions resulted in the unit cooler being inoperable. At the time the conditions were discovered, the reactor mode switch was in the "RUN" position (Mode 1) with the reactor operating at 100 percent rated thermal power. <br /><br /> The root cause of this event has been determined to be personnel error due to inadequate work practices. A contributing cause has been determined to be procedural inadequacy. These errors resulted in a loss of unit cooler 2HVR*UC404D configuration control. <br /><br /> The immediate corrective actions were for plant operators to correctly position the cooling water valves for unit cooler 2HVR*UC404D, and to declare the unit cooler operable. Additional corrective actions include: 1) Reviewing the incident with NMP2 Operations personnel; 2) Issuing a Lessons Learned Transmittal; 3) Counseling and disciplining personnel involved with the mark-up; 4) Holding departmental meetings with NMP2 personnel to emphasize expected work practices; 5) Issuing an interim instruction for plant operators to alleviate the procedural inadequacy; 6) Revising the appropriate procedure; 7) Modifying the mark-up computer program; and 8) Reviewing other standby safety systems to ensure similar conditions do not exist.
4101991017 | Nine Mile Point 2 | 08/13/1991 | 08/13/1992 | 9208240063 | <strong>Transformer Fault Causes Reactor Scram and Uninterruptible Power Supply Failure Causes Loss of Annunciation Which Led to Declaration of a Site Area Emergency</strong><br /><i>Abstract:&nbsp;</i>At 0548 hours on August 13, 1991, Nine Mile Point Unit 2 (NMP2) experienced a turbine trip and reactor scram when the 'B' Phase Main Transformer developed an internal fault. The transformer fault created an electrical disturbance throughout the normal electrical distribution system, resulting in the loss of five non-safety related Uninterruptible Power Supplies (UPS). As a result, the Control Room lost annunciation and most Balance of Plant (BOP) instrumentation. The conditions described in this report mandated entry into a Site Area Emergency as specified by the Site Emergency Plan. Prior to the event, NMP2 was in operational condition 1 (RUN) at 100% rated thermal power. <br /><br /> The cause of the transformer fault was a failure of the coil insulation. Due to the magnitude of the failure, the root cause could not be positively determined, however, the proximate cause was a manufacturer's defect. <br /><br /> Control Room operators verified the reactor scram, identified and re-energized the failed UPS's, identified the cause of the reactor scram, and cooled down the reactor to terminate the emergency event. Other corrective actions included: 1) replacing the 'B' phase transformer with the installed spare; 2) modifying the UPS's; 3) replacement of back-up batteries in the UPS's; 4) developing a back-up battery replacement schedule; and 5) revision of the Reactor Water Cleanup Operating Procedure.
4101991018 | Nine Mile Point 2 | 09/09/1991 | 10/09/1991 | 9110240094 | <strong>Reactor Scram During Surveillance Testing due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1991, at 1028 hours with the reactor at 0 percent power, all rods inserted, and the reactor mode switch in the "SHUTDOWN" position (Operational Condition 4), Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature (ESF) actuation. Specifically, while performing surveillance testing on the Turbine Control Valve fast closure scram function, a full reactor scram signal was received from the Reactor Protection System (RPS) scram logic. <br /><br /> The root cause for this event has been determined to be procedural inadequacy.<br /><br /> Immediate corrective actions were to identify the cause for the RPS scram signal and reset the scram. Additional corrective actions include: combining the monthly RPS Operations Surveillance Procedures into one procedure; revising Operations Surveillance Procedure N2-OSP-RPS-W001, "Weekly Turbine Valve Cycling"; and issuing a Lessons Learned Transmittal to those departments associated with the event.
4101991019 | Nine Mile Point 2 | 09/20/1991 | 10/21/1991 | 9110300146 | <strong>Engineered Safety Feature Actuation due to a low air flow caused by a failed component</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1991, at 1048 hours, Nine Mile Point Unit 2 experienced an Engineered Safety Feature (ESF) actuation. Specifically, the Secondary Containment (Reactor Building) isolated and the Reactor Building Emergency Recirculation Unit Cooler and Standby Gas Treatment System (GTS) started automatically. The actuation was initiated by a low air flow signal in the Reactor Building Ventilation System (HVR). At the time of the event, the reactor mode switch was in the "STARTUP" position (Mode 2). The reactor was operating at less than 1 percent rated thermal power during power ascension.<br /><br /> The root cause of the event has been determined to be equipment failure, specifically, a faulty flow switch. <br /><br /> The immediate corrective actions were to determine the cause of the ESF actuation, and to assess the plant for other possible initiating conditions. Other corrective actions included: performing a calibration check of the air flow switches; replacing the faulty flow switch; and evaluating a sample of other applications of the same model flow switch for similar failures.
4101991020 | Nine Mile Point 2 | 09/29/1991 | 10/29/1991 | 9111060344 | <strong>High Pressure Core Spray System Inoperable due to Failed Instrument</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1991, at 0341 hours, the High Pressure Core Spray (HPCS) System was declared inoperable following a failed channel check of a HPCS initiation logic trip unit. Further investigation identified a defective wide range reactor vessel water level transmitter. At the time this condition was discovered, Nine Mile Point Unit 2 (NMP2) was operating at 55 percent rated thermal power with the reactor mode switch in the "RUN" position (Operational Condition 1). <br /><br /> The root cause for this event was determined to be equipment failure. <br /><br /> Corrective actions included: Replacing the defective transmitter; completing calibration on the new transmitter; declaring HPCS System operable; and making preparations to return the failed instrument to the manufacturer for failure analysis.
4101991021 | Nine Mile Point 2 | 09/15/1991 | 10/16/1991 | 9110300158 | <strong>Technical Specification Violation due to Missed Surveillance Caused by a Training Deficiency</strong><br /><i>Abstract:&nbsp;</i>At approximately 2303 hours on September 15, 1991, it was discovered that a source check surveillance, required for a Radwaste Radioactive Liquid Effluent Monitor, had not been performed prior to a controlled low level liquid batch release. This is in violation of Nine Mile Point Unit 2 Technical Specification (T.S.), Table 4.3.7.9-1. At the time of the event, the reactor mode switch was in the "SHUTDOWN" position (Mode 4) with reactor temperature at 1 20 degrees fahrenheit and reactor pressure at three pounds per square inch gauge (psig).<br /><br /> The root cause for this event has been determined to be a training deficiency. <br /><br /> A contributing cause was procedural deficiency. Immediate corrective actions included terminating the discharge within one minute of its start time, and performing the required instrument source check. Additional corrective actions include: Issuing a chemistry supervisory directive; issuing Training Change Orders; and revising the associated Chemistry, Operations, and Radiation Protection procedures.
4101991022 | Nine Mile Point 2 | 12/07/1991 | 01/06/1992 | 9201150149 | <strong>Reactor Scram Caused By A Turbine Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1991, at 0935 hours, with the reactor mode switch in the "RUN" position (Mode 1), and the plant operating at approximately 90 percent rated thermal power (905 MWE), Nine Mile Point Unit 2 experienced an Engineered Safety Feature actuation. Specifically, an automatic reactor scram occurred caused by a Turbine Generator stop valve closure, which was initiated by (most probable cause) an Electrohydraulic Control (EHC) System malfunction. <br /><br /> The root cause investigation is still underway and has not yet determined the exact cause; however, the most probable cause is a defective relay actuation.<br /><br /> The immediate corrective action was to respond to the reactor scram and turbine trip in accordance with plant procedures. A Work Request was issued to investigate the EHC malfunction, which led to the replacement of the relay board containing the suspected faulty relay.
4101991023 | Nine Mile Point 2 | 12/12/1991 | 01/13/1992 | 9201210249 | <strong>Reactor Scram on Low Reactor Water Level due to Loss of Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1991, at 0322 hours, with the reactor mode switch in the "RUN" position and the plant operating at approximately 55 percent rated thermal power, Nine Mile Point Unit 2 (NMP2) experienced a reactor scram on a reactor vessel low water level (Level 3) signal. Specifically, following the startup of Feedwater System pump 2FWS-P1A in support of raising plant power, a Condensate System (CNM) and Feedwater System (FWS) transient occurred, resulting in the loss of both FWS pumps. Reactor vessel water level lowered to 159.3 inches (Level 3 trip setpoint), initiating an automatic reactor scram signal. On December 12, 1991, at 1023 hours, while operators were attempting to return the Reactor Water Cleanup (WCS) System to an operable status following the scram, WCS isolated on a high differential flow signal (Engineered Safety Feature actuation).<br /><br /> The root cause for the reactor scram was determined to be poor work practices. The preliminary cause for the WCS isolation is inadequate system design.<br /><br /> Immediate actions included restoring reactor vessel inventory and commencing a controlled plant shutdown. Additional corrective actions include: 1) administering disciplinary action for individuals involved in the scram; 2) evaluating and revising Operating Procedure N2-OP-3, "Condensate and Feedwater System"; 3) troubleshooting electrical circuitry for Condensate pump 2CNM-P1C; and 4) completing the WCS isolation root cause analysis.
4121991001 | Beaver Valley 2 | 04/20/1991 | 05/20/1991 | 9105280168 | <strong>Inoperable Control Rod Position Deviation Alarm</strong><br /><i>Abstract:&nbsp;</i>On 4/20/91, after inserting control rods 14 steps to support reactor engineering, the operators noted the computer point for average control rod position disagreed with the point that summed total rod steps by more than the allowed 12 steps. This should have activated the rod position deviation alarm, but no alarm had occurred. The computer engineer was consulted and determined that the computer's rod position deviation alarm had been bypassed, preventing the alarm from annunciating. Further investigation determined that the alarm had inadvertently been bypassed on 4/12/91 during a computer cold start/reboot sequence. On that date, the computer engineer performing the reboot, reinitiated the reboot procedure before the initial startup sequence was complete. By terminating the first startup prior to completion, the alarm bypass was activated and not restored by the second reboot. The station has modified the computer software to provide an alarm to the reactor operator whenever this or similar points are bypassed. All personnel in the computer group are being trained on the potential effects of terminating a computer startup prior to its completion. Review of the manual operator rod position logs show that no rod position deviation had occurred while the rod deviation alarm was inoperable.
4121991002 | Beaver Valley 2 | 07/16/1991 | 08/14/1991 | 9108190197 | <strong>Containment Isolation Valve Closure Due to Steam Generator Blowdown Tank High-High Level</strong><br /><i>Abstract:&nbsp;</i>At 1930 hours on 7/16/91, while operating in mode 1, operators were valving in the "A" Turbine Plant Component Cooling Water (CCS) heat exchanger (2CCS-E21A) and isolating the "B" heat exchanger (2CCS-E21B) due to high differential pressure. During the valving operation, CCS temperature, initially at 89 degrees Fahrenheit, began to increase. Since steam generator blowdown is cooled by CCS via the steam generator blowdown demineralizer heat exchanger, blowdown temperature at the heat exchanger outlet began to increase. When the heat exchanger outlet temperature switch (2BDG-TIS112) reached 107 degrees Fahrenheit, steam generator blowdown flow isolated as designed. The resultant high-high level in the blowdown flash tank closed the steam generator blowdown outside containment isolation valves (2BDG*AOV100A1, B1 and C1). An investigation revealed the outlet temperature switch setpoint was incorrectly set at 107 degrees instead of the design value of 120 degrees Fahrenheit. The setpoint was corrected and steam generator blowdown placed back in service at 2050 hours. The turbine building tour operator logs have been revised to periodically verify the setpoint of 2BDG-TIS112. There were no safety implications to the public as a result of this event. The outside containment isolation valves actuated to their safety related positions.
4121991003 | Beaver Valley 2 | 07/24/1991 | 08/23/1991 | 9108260264 | <strong>ESF Actuation - Trip of Containment Air Circulation Fan During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 7/24/91 while operating at 100 percent power, a partial operating surveillance test was being conducted to verify the operability of safeguards protection system relays. To avoid tripping the running containment air recirculation fan (since these fans have a history of vibration problems), an Operating Manual Change Notice was written to lift a lead on the terminal board inside a relay panel. An operator would then verify that the fan received a trip signal by verifying that the designated relay contacts had changed position. Even though the operator in the field had been briefed and had a marked up copy of the OST in hand, nevertheless he directed electrical maintenance to lift a lead for the incorrect fan. When the test switch at the Safeguards Test Panel was actuated, the operating fan tripped as designed. The fan was immediately restarted and the operator counseled. There were no safety implications as a result of this event. Both of the other containment air recirculation fans remained available throughout this event.
4121991004 | Beaver Valley 2 | 10/18/1991 | 11/18/1991 | 9111210090 | <strong>Potential Auxiliary Feedwater Pump Lube Oil Cooler Operation Above Design Pressure</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was operating at 100 percent power when the turbine driven auxiliary feedwater pump (TDAFP) was declared inoperable at 1600 hours on 10/18/91. An Engineering evaluation determined that the pressure developed in the lube oil cooler would exceed the cooler design pressure in some system configurations. Calculations indicated that all portions of the lube oil coolers, except the end bell flange bolts on the TDAFP cooler, would accommodate the pressures experienced. Replacing the flange bolts for the cooler with stud bolts of a higher tensile strength qualified the cooler for the higher maximum calculated pressure. The pump was declared operable on 10/19/91 at 0400 hours. At no time was the margin of safety to the general public reduced. The potential overpressurization of the TDAFP lube oil cooler bolts was calculated based on very conservative assumptions. Additionally, at no time during the operation of Beaver Valley Unit 2 were the auxiliary feedwater lube oil coolers in the system configuration which could have resulted in potential overpressurization. When the pump was purchased during plant construction, the pump vendor had not observed the operating pressure requirements of alternate lineups. Therefore, the coolers were not rated for a higher pressure.
4121991005 | Beaver Valley 2 | 11/26/1991 | 12/23/1991 | 9112300066 | <strong>Reactor Trip Due To Spurious Component Actuation</strong><br /><i>Abstract:&nbsp;</i>On 11/26/91, with the Unit in Power Operation at 100 percent reactor power, a load rejection (closure of the governor and interceptor valves) occurred at 1143 hours. The closure of the governor and interceptor valves was the result of a signal from the Overspeed Protection Control (OPC) circuit. The load rejection caused a rapid reactor coolant system (RCS) heatup of three degrees. The control rods, in automatic, began to step into the core, however, a reactor trip on power range neutron flux negative rate occurred at 1143 hours. This trip was the result of the combined effects of the reactor fuel (doppler) and moderator temperature coefficients due to the RCS heatup resulting from the load rejection. Operations personnel stabilized the plant in Hot Shutdown. An investigation revealed that a solid state relay in the OPC circuit inadvertently actuated causing the load rejection. The failed relay was replaced. There were no safety implications as a result of this event. The reactor control system and the auxiliary feedwater system actuated as designed upon receipt of the reactor trip signal and low-low steam generator level signals.
4131991001 | Catawba 1, Catawba 2 | 11/12/1990 | 02/13/1991 | 9102260129 | <strong>Both Trains of Residual Heat Removal and Auxiliary Containment Spray Inoperable Due to Defective Procedures and Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>In October 1990, Performance became aware of a McGuire Nuclear Station incident that rendered both trains of the Residual Heat Removal (ND) System inoperable while stroke testing valves NI136B, NS38B, and NS43A. With any of these valves open during a Loss of Coolant Accident, ND injection flow could be degraded. These valves have been tested quarterly at Catawba since unit startup. Performance revised test procedures for NS38B and NS43A to close downstream valves so that quarterly testing could continue. While reviewing the Final Safety Analysis Report (FSAR), Performance misinterpreted information related to the auxiliary containment spray headers and allowed the test to be completed without declaring ND/NS inoperable. On November 12, with Unit 1 in Mode 1, Power Operation, 1NS38B was tested with Train A ND inoperable; thereby, rendering both trains of auxiliary containment spray inoperable. This incident is attributed to Defective Procedures that allowed quarterly testing of NI136B, NS38B, and NS43A without regard to possible degraded ND injection flow. The auxiliary containment spray headers were inoperable due to an Inappropriate Action due to misinterpreted information in the FSAR. Corrective actions include rescheduling tests for cold shutdown and FSAR enhancements.
4131991002 | Catawba 1 | 01/13/1991 | 02/12/1991 | 9102190122 | <strong>Technical Specification Violation For Mode Change With The Residual Heat Removal System Train 'A' Inoperable Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1991, at approximately 0119 hours, Unit 1 entered Mode 1, Power Operation, with the Residual Heat Removal (ND) System Pump 1A inoperable due to its suction valve (1FW-27A) from the Refueling Water Storage Tank (FWST) being closed. The valve was closed during the performance of PT/1/A/4200/53A, 1FW-28 Partial Stroke Test, which was being performed while final operability checks were being completed prior to starting the mode change. The Control Room Operator (CRO) who was aware of the in-progress Periodic Test (PT), injected demineralized water into the Reactor Coolant (NC) System to increase Reactor (Rx) power from approximately 4%, Mode 2, Startup, to greater than or equal to 5%. Subsequently, at approximately 0119 hours, Unit 1 Reactor power level was greater than 5% (Mode 1) as indicated by the Operator Aid Computer (OAC) point D4698, Best Estimate Thermal Power > 5% power; thus violating Technical Specifications. This incident is attributed to Inappropriate Action, for the closure of 1FW-27A, due to a less than adequate knowledge of 1FW-27A function and Insufficient Communication between Control Room personnel. A contributing cause for this incident has been assigned as Procedure Deficiency in that the procedure does not state that ND Pump 1A is inoperable with 1FW-27A closed. Corrective actions included completion of the test to restore ND Pump 1A operability and discussion of the incident and the lessons learned with all involved personnel prior to the end of the shift.
4131991003 | Catawba 1 | 01/10/1991 | 02/06/1991 | 9102130088 | <strong>Technical Specification Violation for Emergency Personnel Hatch Being Unlatched Due to Equipment Failure/Malfunction</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1991, at 1530 hours, with Unit 1 in Mode 3, Hot Standby, the Emergency Personnel Hatch, also known as the Submarine Hatch, was found in the down or closed position but not latched. The tamper seal was in place around the handwheel and the hinge. The area in the immediate proximity of the hatch was highly traveled one week prior to finding the problem, for work being conducted in the Lower Ice Condenser. The exact time the hatch became unlatched is unknown; however, the opportunity for the hatch to become unlatched was very high during Ice Condenser work activities. Constant stepping on and off the hatch causes the latching mechanisms to retract. This situation was also enhanced by one of the four latching mechanisms being out of adjustment. Technical Specification 3.6.5.5 requires this hatch to be operable and closed in Mode 1, Power Operation, Mode 2, Startup, Mode 3, Hot Standby, and Mode 4, Hot Shutdown. This incident is attributed to Equipment Failure/Malfunction. Corrective actions include modifying the hatch by installing a tab to match mark the correct closed position of the handwheel and to provide a closer and more secure position to install the tamper seal. The latching mechanisms will be adjusted such that all make simultaneous contact with the latching lip.
4131991004 | Catawba 1 | 01/05/1991 | 02/27/1991 | 9103070006 | <strong>Technical Specification Violation As A Result of A Missed 18 Month Channel Calibration On Radiation Monitor 1EMF48</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1991, with Unit 1 in Mode 3, Hot Standby, a Technical Specification Violation resulted from a missed 18 month channel calibration on 1EMF48, the Reactor Coolant System Radiation Monitor. On January 31, 1991, at 1730 hours, with Unit 1 in Mode 1, Power Operation, a Maintenance Engineering Services (MES) Engineer discovered the incident during a work history review of the process radiation monitors which included 1EMF48. The 18 month channel calibration on Radiation Monitor 1EMF48 is performed by a Standing Work Request (SWR), 3663SWR. The SWR was not issued to perform the 18 month calibration because an inadvertent computer entry was made indicating that 3663SWR was completed on January 12, 1990. However, 3663SWR was actually completed on February 17, 1989. This incident is attributed to Inappropriate Action due to the incorrect computer entry causing the required 18 month channel calibration on Radiation Monitor 1EMF48 to be missed. The corrective actions included declaring 1EMF48 inoperable, performing the 18 month channel calibration on February 2, 1991, and returning 1EMF48 to service.
4131991005 | Catawba 1, Catawba 2 | 02/12/1991 | 03/12/1991 | 9103200166 | <strong>T/S 3.0.3 Entry As A Result Of Both Trains Of Control Room Area Ventilation System Being Inoperable Due To A Possible Design/Installation Deficiency And Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1991, at approximately 1225 hours, with Units 1 and 2 in Mode 1, Power Operation, Technical Specification (T/S) 3.0.3 was entered due to both trains of the Control Room Area Ventilation (VC) and Chilled Water (YC) System being declared inoperable. Train "A" was declared inoperable after its chiller tripped due to its associated low refrigerant temperature cutout switch setpoint being reached. Train "B" was then placed inservice but later its chiller tripped. An investigation revealed that the root cause for the Train "A" YC chiller was due to a refrigerant leak located at its compressor power terminal box. Train "B" YC chiller trip was due to its low refrigerant temperature cutout switch as a result of its associated condenser water auto control valve being inadvertently failed open. The "B" YC chiller was successfully started and T/S 3.0.3 was exited at approximately 1415 hours. This incident is attributed to a possible vendor Design/Installation Deficiency and Inappropriate Action for a less than adequate review of electrical drawings. Subsequent corrective actions involved restoring the condenser water auto control valve and restarting the YC chiller "B". Corrective actions included calibration of the low refrigerant temperature cutout switch and repair of refrigerant leak on the "A" YC chiller.
4131991006 | Catawba 1, Catawba 2 | 03/23/1991 | 04/18/1991 | 9104290082 | <strong>Technical Specification Violation When Nuclear Service Water Valves Were Left Without An Emergency Power Supply Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1991 at 0300 hours, Unit 1 was in Mode 5, Cold Shutdown, in preparation for the End of Cycle refueling outage. Unit 2 was in Mode 1, Power Operations. At 0337 hours, Operations removed the 1A Diesel Generator (D/G) from service using procedure OP/1/A/6350/02, Diesel Generator Operation. A Non-Licensed Operator (NLO) requested Operator at the Controls' (OATC) assistance to ensure that 1EMXG, Essential Motor Control Center, was aligned to 2ELXA, Alternate Blackout Power Loadcenter. The OATC and NLO used the Operator Aid Computer (OAC) graphics and apparently misread the graphic to conclude that 1EMXG was powered by 2ELXA. The Nuclear Service Water System (RN) 'A' Train was removed from service on March 23 at 0500 hours and was returned to service on March 26 at 0445 hours. At 1400 hours, an Engineered Safeguard Feature Bypass Panel (1.47) alarm was received in the Control Room and the operators determined that 1EMXG was without emergency power.<br /><br /> The operators aligned 1EMXG to 2ELXA. This incident has been attributed to an Inappropriate Action in that the NLO and OATC misread the OAC graphics while verifying the alignment of 1EMXG to 2ELXA. OPS personnel have been informed not to use the OAC graphics for procedure sign-offs and OPS Management Procedures will be revised. OAC graphics training will be provided along with an evaluation of OAC graphics accuracy. A clear policy on OAC use will be established.
4131991007 | Catawba 1 | 01/15/1991 | 03/18/1991 | 9103210271 | <strong>Technical Specification Violation From Failure To Perform Reactor Trip System Surveillance Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1991, Unit 1 was returning to power operation following a shutdown to Mode 3 (Hot Standby). During the startup, the surveillance test for the Turbine Emergency Trip System (ETS) required by Technical Specification (T/S) 4.3.1.1 was not performed. On January 15, 1991, Unit 1 exceeded 69% power in violation of T/S 4.3.1.1. An unrelated review of periodic test completion records on February 16 discovered that the surveillance had not been performed. The Turbine ETS surveillance was not performed because the responsible control room operators misunderstood communication regarding previous performance of several Turbine periodic tests. The control room operator inappropriately signed off the procedure step indicating that the required test had been performed when it had not. This incident is attributed to Inappropriate Action on the part of the Control Room Operators. Corrective actions include discussion of the event and their actions with personnel involved, training to improve communications, with emphasis on carrying out procedure steps, and procedure changes.
4131991008 | Catawba 1, Catawba 2 | 02/19/1991 | 03/20/1991 | 9103270265 | <strong>Inability to Maintain Control Room Pressure During Loss of Power Events Due to Design Deficiency Resulting in Entry of Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1991, at 1700 hours, Units 1&2 were in Mode 1, Power Operation. Catawba was notified by McGuire Nuclear Station about a condition that may affect operability of the Control Room Ventilation System (VC). Station personnel investigating the problem discovered that the VC intake valves would close on a Loss Of Offsite Power (LOOP) event. <br /><br /> Existence of an unanalyzed condition was declared; NRC notification was made within one hour. A compensatory action was developed to ensure that the intake valves would be opened promptly following a LOOP event. Problem Investigation Report (PIR) 0-C91-0072 was initiated on February 20. While Design Engineering was developing a permanent solution, it was discovered on February 25 that an emergency generator trip after one minute, following a Loss Of Cooling Accident and a LOOP event, would result in closed intake valves that could not be opened within the required time frame. PIR 0-C91-0086 was initiated at 1605 hours entering the station into Technical Specification (T/S) 3.0.3, Limiting Conditions for Operation. T/S 3.0.3 was exited when a waiver of T/S was received, allowing the intakes to be opened and deenergized. This incident has been attributed to a Design Deficiency in that as the system was designed, the required time frame to reopen the valves was not analyzed. The isolation circuits have been removed from the VC system and the intake valves were energized.
4131991009 | Catawba 1, Catawba 2 | 07/17/1991 | 10/15/1991 | 9110280237 | <strong>Technical Specification Violations Resulting From Improper Overtemperature Delta Temperature Circuit Scaling</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1991, with Units 1 and 2 in Mode 1, Power Operation, at 100 percent power, Maintenance Engineering Services (MES) personnel learned that the Overtemperature Delta-Temperature (OTDT) circuit would not work properly over the entire range. The gain associated with one of the OTDT calculation constants, K2, was applied to only one circuit card in each channel when the OTDT channels were calibrated at both McGuire Nuclear Station and Catawba. This would result in overranging the card, under certain conditions, for the current values of K2. This was discovered by MES personnel at McGuire during the week of July 8, 1991 during a scaling calculation for a new K2 value. It was not determined whether or not the OTDT channels were inoperable per Technical Specifications on July 17. It has been concluded that channels were inoperable in the past and that the plant would have been outside its design basis under some postulated conditions. This incident is attributed to defective vendor documentation and inappropriate action (due to inadequate procedure reviews). The gain value associated with the K2 constant was applied per vendor documentation, to the lead/lag circuit in the OTDT calibration procedures, resulting in potential saturation of the circuitry. Corrective actions included procedure and vendor documentation revisions, OTDT circuit modifications, and interim controls until hardware modifications were complete.
4131991010 | Catawba 1 | 05/26/1991 | 06/20/1991 | 9108300103 | <strong>Feedwater Isolation Due To Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1991, at 2101 hours, with Unit 1 in Mode 5, Cold Shutdown, a Feedwater (CF) System isolation occurred during racking out activities of the "A" Reactor Trip Bypass Breaker. Operations personnel had previously started the Manual Reactor Trip Functional Test, PT/1/A/4600/15, but stopped to pursue higher priority work. Later, after shift change, Operations personnel resumed the procedure to align the breakers for Engineered Safety Features (ESF) "A" Train testing. During this alignment, the Reactor Trip Bypass Breaker "A" was racked from the connect to the disconnect position. During breaker transit, the Operator heard relays activating and apparent closure of CF valves within the Doghouse. CF isolation was immediately reset and valves realigned for ESF testing. All proper personnel, including the NRC, were notified and a work request was initiated to investigate and repair the breaker. The cause for this event is unknown. During the time of the event, the Events Recorder, which could have provided more information as to the cause of this event, was out of service. No problems were found with the breaker upon completion of the work request. Operator error was not evident. Catawba will evaluate the need to replace the Westinghouse W-2 cell switch which has had sensitivity problems in the past. A Design Study is now in progress to find an acceptable substitute.
4131991011 | Catawba 1 | 05/14/1991 | 07/03/1991 | 9107230379 | <strong>Technical Specification Violation Due To Incorrect Flow Orifice Orientation As A Result Of Management Deficiencies, Inappropriate Action, And Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1991, with Unit 1 in Mode 6, Refueling, the flow orifice plate in flow element 1NIFE5000 (Chemical and Volume Control (NV) System Cold Leg Injection 'A' Header) was discovered installed in the reverse orientation. Subsequently, during the same inspection, 1NIFE5510 (Safety Injection (NI) System Cold Leg Injection 'B' Header) flow orifice plate was found installed in the reverse orientation. The inspections performed by the Performance Group were conducted due to concerns of the discovery of several flow orifice plates installed incorrectly in safety related systems at Duke Power Company Oconee Nuclear Station. Both flow orifice plates were removed and reinstalled correctly. Design Engineering evaluated the impact of the reversed flow orifice plates on the previous NI flow balance results and concluded that the NI flow rate would have been lower than Technical Specifications allow, but within safety analysis assumptions for total injection flow. A review of the equipment work history database revealed that both flow instruments were incorrectly installed during the Unit 1 End of Cycle 4 Outage (May 1990). This incident has been assigned a root cause of Management Deficiency and contributing causes of Inappropriate Action, Defective Procedure, and Management Deficiency, due to no training given. Corrective actions will include explanation and discussion of this incident with Maintenance personnel and procedural strengthening and training to ensure proper orifice plate orientation.
4131991012 | Catawba 1 | 05/05/1991 | 06/03/1991 | 9106110294 | <strong>Technical Specification Violation Due to Violation of Containment Integrity During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1991, at 0758 hours, with Unit 1 in Mode 6, Refueling, Ice Condenser (NF) System replenishment activities commenced. Fuel reloading had begun at 0535 hours. During ice bed replenishment, cold air can be drawn from the upper portion of the ice condenser to supply the charging system the air required to blow borated ice into the baskets. Air is extracted through Penetration M371 and returned with borated ice through Penetration M394. However, if core alterations are in progress, suction is not to be taken from the ice condenser. Ice replenishment activities were completed at approximately 1206 hours. During the performance of this work, Technical Specification (T/S) 3.9.4 was violated because suction was being taken from the ice condenser while core alterations were in progress. This incident was discovered on May 7, 1991 at 0800 hours by a Maintenance Engineering Services engineer during discussions with ice machine operators and verification with Operations personnel. This incident is attributed to an inappropriate action, because the ice machine operator did not use the Ice Making and Charging System procedure. This incident is attributed a contributing cause of inappropriate action due to inadequate communication between a Control Room Operator (CRO) and the ice machine operator. A corrective action will be to ensure that initial conditions for ice blowing are satisfied prior to each ice blowing.
4131991013 | Catawba 1 | 06/20/1991 | 02/27/1992 | 9203090349 | <strong>Reactor Trip Due To Reactor Coolant Pump Trip Caused By Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1991, at 0823 hours, with Unit 1 in Mode 1, Power Operation, at 71% power following a refueling outage, a Reactor trip occurred on the "Low Flow P8. Permissive Trip" due to the trip of Reactor Coolant (NC) Pump 1A. The NC Pump 1A safety breaker opened as a result of a defective Silicon Controlled Rectifier (SCR), which tripped the overcurrent relay for the breaker, thereby tripping the pump. Plant response was as expected, with the Main Turbine tripping on Reactor trip, feedwater isolation, and the Auxiliary Feedwater System starting and supplying water to the Steam Generators. Emergency procedures were entered, and appropriate notifications were made. The Unit was brought back on line by 0545 hours on June 21. This incident is attributed to an Equipment Failure; the SCR for the NC Pump 1A safety breaker 50/51 XYZ overcurrent relay was found to be defective, and was replaced. All other SCRs associated with the NC Pump supply and safety breakers have been checked. Inspections of SCRs in other critical applications have been performed.
4131991014 | Catawba 1 | 06/28/1991 | 10/09/1991 | 9110240186 | <strong>Technical Specification Violation Due To Improper Overtemperature Delta Temperature Setpoint Calculation</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1991, at 1600 hours, with Unit 1 in Mode 1, Power Operation at 100% power, the Loop B Overtemperature Delta Temperature (OTDT) Operator Aid Computer alarm was received following Nuclear Instrumentation System calibrations. On June 30, 1991 at 1000 hours, a manual calculation was performed to determine channel operability. The calculations was performed incorrectly, but Loop B OTDT was determined to be operable. At approximately 2200 hours, the on-coming shift performed the OTDT was placed in the tripped condition, as required by Technical Specifications, and a Work Request was issued to repair the channel. This incident is attributed to an inappropriate action due to lack of attention to detail in that a mistake was made during the manual calculation. On July 1, 1991, Neutron Detector N-42 was recalibrated, taken out of the tripped condition, and declared operable. Corrective actions include enhancements of affected procedures and manual calculations methods to improve their reliability.
4131991015 | Catawba 1 | 07/10/1991 | 08/08/1991 | 9108130346 | <strong>Reactor Trip on Turbine Trip Due to Loss of Both Main Feedwater Pumps on Low Suction Pressure</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1991, at approximately 0901 hours, with Unit 1 in Mode 1, Power Operation, and operating at 92% Reactor power level, a Reactor (Rx) trip occurred as a result of a Turbine trip above P-9 (69% Reactor power). The Turbine tripped because of loss of both Main Feedwater (CF) pumps on low suction pressure. The low suction pressure condition occurred during a secondary side transient which began when the heater drain (HW) tank pump 1C1 outlet control valve (1HW59) failed closed as the control air signal line from the level controller to the valve positioner broke. This prevented 1C1 heater drain tank pump flow from entering the Condensate (CM) system, reducing CF pump suction pressure. The standby CM Booster Pump and Hotwell pump had been tagged out for preventive maintenance prior to the transient and were unavailable. While the operators were reducing load to recover CF pump suction pressure, the pumps tripped on low suction pressure. The Turbine and Reactor trips followed. This incident is attributed to a possible Design/Construction/Installation Deficiency. Metallurgical analysis showed that the failure was caused by vibration coupled with excessive stress loading at the positioner fitting. The failed tubing was replaced, and expansion coils were added.
4131991016 | Catawba 1, Catawba 2 | 07/30/1991 | 08/28/1991 | 9109040165 | <strong>Technical Specification Violation As A Result Of The Control Rod Position Alarm Monitor Being Inoperable Due To A Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1991, at approximately 1115 hours, with Units 1 and 2 in Mode 1, Power Operation, and operating at 100 percent power, Operations (OPS) personnel were notified by Performance (PRF) personnel that both Unit's Rod Deviation Monitors (RDMs) were functionally inoperable. On July 25, 1991, Production Support Department (PSD) personnel informed the station PRF personnel that a logic error discovered in the Operator Aid Computer (OAC) Rod Position Alarm Monitor (RAM) program at McGuire Nuclear Station affected the RDMs at Catawba Nuclear Station also. Unit specific Technical Specification Operability Notification (TSON) sheets were issued on July 30 declaring the monitors inoperable and OPS began complying with the Technical Specification (T/S) action and surveillance requirements. This incident is attributed to a Management Deficiency because no policy requiring functional verification of OAC programs existed during the initial startup of the Units. Corrective actions included PSD personnel reprogramming the RAM programs and verifying that the RDMs operated properly. OPS declared the Unit 2 and 1 RDMs operable per TSON sheets on July 30, at 1500 hours, and July 31, at 1200 hours, respectively.
4131991017 | Catawba 1 | 11/09/1990 | 09/11/1991 | 9109300245 | <strong>Technical Specification Violation As A Result Of A Missed 18 Month Charger Capacity Test Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1990, with Unit 1 in Mode 1, Power Operation, at 100% power, a Technical Specification (T/S) Violation resulted from a missed 18 month charger capacity test on battery charger 1ECA. On August 15, 1991, at 1300 hours, with Unit 1 in Mode 1, Power Operation, at 100% power, a Planner discovered the incident during an audit of Standing Work Requests (SWRs). The 18 month charger capacity test on battery charger 1ECA is performed per 003808SWR. The SWR was not issued to perform the 18 month charger capacity test because an inadvertent computer entry was made indicating that 003808SWR was completed on August 11, 1990. However, 003808SWR was actually completed on March 10, 1989. On April 23, 1991, the 1ECA battery charger capacity test was performed as a functional test per Work Request (W/R) 55466OPS. This incident is attributed to Inappropriate Action due to the incorrect computer entry, causing the required 18 month charger-capacity test to be missed. Corrective actions included expanding a one time audit of SWRs in an attempt to identify other data entry errors, entering the correct completion date for 003808SWR, and WMS implementation.
4131991018 | Catawba 1 | 09/06/1991 | 10/03/1991 | 9110160012 | <strong>Unit 1 Essential Bus Blackout Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1991, at 1903 hours, Unit 1 was operating in Mode 1, Power Operations. A Nuclear Operations Technician (NOT B), was shutting down diesel generator (D/G) 1B per PT/1/A/4350/02B, Diesel Generator Operation, following corrective maintenance. NOT B assumed the shutdown following turnover from the day shift. After reducing the load on D/G 1B, NOT B inadvertently opened the Normal B Train Essential Bus (1ETB) Feeder Breaker, 1ETB-3, instead of the D/G Breaker, 1ETB-18. D/G 1B immediately began supplying the loads on 1ETB. NOT B continued the shut down and pressed the STOP pushbutton. The blackout condition initiated the D/G load sequencer, restarted D/G 1B, and loaded the blackout loads. NOT B realized that the D/G had restarted and pressed the STOP button again and the D/G restarted. NOT B finally stopped D/G 1B by using the RUN/STOP plunger. 1ETB-3 was closed and the affected plant systems were reset. Unit 1 continued to operate at 100% power throughout this event. The D/G run was repeated successfully. This event was attributed to an Inappropriate Action. NOT B failed to self-verify actions taken to open 1ETB-18. Contributing Causes include hardware and procedure deficiencies. Corrective actions include an emphasis on the use of self-verification along with procedure and equipment enhancements.
4131991019 | Catawba 1 | 09/11/1991 | 10/08/1991 | 9110180017 | <strong>Reactor Trip On Turbine Trip Due To Los Of Both Main Feedwater Pumps On High Discharge Pressure</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1991, at 13:02:52 hours, with Unit 1 in Mode 1, Power Operation, and operating at 100% Reactor power level, a Reactor (Rx) trip occurred as a result of a Turbine trip above P-9 (69% Rx power). The Turbine tripped because of loss of both Main Feedwater (CF) pumps on high discharge pressure. The high discharge pressure occurred when the Advanced Digital Feedwater Control System (ADFCS) sensed that there was a loss of two out of three Nuclear Power Channel inputs. The ADFCS responded properly by reducing the S/G level setpoint from 66.5% to 38% based on its median selected value of 0% Reactor power. The setpoint change caused the CF control and bypass valves to rapidly close. The valve movement caused the feedwater header pressure to increase, tripping the CF pumps on high discharge pressure and subsequently tripping the Turbine. This incident is attributed to a possible inappropriate action during nuclear instrument calibration, with a contributing cause of inappropriate action of failure to follow policies, directives, or management procedures. Corrective action included addition of a four second delay in the activation of the ladder logic and input circuitry deviation alarms and 120 second lag time constant reducing the S/G program level to the ADFCS. The Independent Verification program is being evaluated to determine if training and program enhancements are needed.
4131991020 | Catawba 1, Catawba 2 | 09/15/1991 | 12/12/1991 | 9112200179 | <strong>Technical Specification 3.0.3 Entry Due To Two Inoperable Trains Of The Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1991, at 1300 hours, with Unit 1 in Mode 1, Power Operation, at 98 percent power and Unit 2 in Mode 5, Cold Shutdown, Operations attempted to swap to Train A of the Control Room Area Ventilation and Chilled Water (VC/YC) System. During this activity, it was discovered that breaker 1EKPG #22, Train A VC/YC System Controls, was open. The breaker was last functionally demonstrated to be closed on September 11 at 2210 hours. A review of all activities between September 11 at 2210 hours and September 15 at 1300 hours did not clearly reveal how/when 1EKPG #22 was opened. However, it is considered most probable that 1EKPG #22 was opened between 0930 and 1520 hours on September 13. Train A VC/YC had been declared inoperable on September 13 from 0455 hours to 2340 hours for work on various Train A components. Prior to this work, a tagout was placed to open 1EKPG #21 instead of #22. It is considered probable that Technical Specification 3.0.3 was entered on September 13 from 0810 to 0930 hours because neither train of VC/YC would have been capable of adequately pressurizing the Control Room. This incident is attributed to Inappropriate Actions. Corrective actions include formation of a task force to study component mispositioning events and discussion of this incident with Operations personnel.
4131991021 | Catawba 1 | 10/02/1991 | 10/30/1991 | 9111080219 | <strong>Turbine/Reactor Trip Due To Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991, at 1200 hours, with Unit 1 at 100% power, a turbine trip resulting in a reactor trip occurred. A vendor, cleaning the area on the 619 elevation of the turbine building with high pressure water, inadvertently sprayed water into electrical box 1TBOX0047 located on the 594 elevation. The water infiltration caused erroneous 2 of 3 high water level signals in Moisture Separator Reheater "D" to initiate a turbine trip, and, subsequently, at 12:00:04 the reactor tripped. An evaluation of plant data has shown that all systems performed as designed following the trip. Procedures EP/1/A/5000/001A, Reactor Trip Response, and AP/1/A/5500/002, Turbine Generator Trip, were entered at 1205 hours, with all systems responding normally. The EP and AP procedures were completed at approximately 1235 hours, and OP/1/A/6100/005, Unit Fast Recovery, was initiated. This event has been attributed to an Installation Deficiency in failing to properly seal the conduit connectors which penetrate the NEMA 4 box. Corrective actions include an inspection of non-safety related NEMA 4 boxes located in the Unit 1 & 2 turbine buildings and sealing of the connectors as required. The vendor will develop a procedure for proper use of the pressure washer.
4131991022 | Catawba 1, Catawba 2 | 10/07/1991 | 10/31/1991 | 9111120191 | <strong>Technical Specification Violation As A Result Of A Missed Grab Sample On Radiation Monitor EMF-36 Due To Inappropriate Action And Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, at 0005 hours, with Unit 1 in Mode 1, Power Operation, at 100% power, a Technical Specification (T/S) Violation occurred due to a missed grab sample for the inoperable Unit Vent Radiation Monitor 1EMF36. The Radiation Protection (RP) Specialist A, who failed to obtain the inoperable 1EMF36 grab sample at the appropriate time, informed his relief, Specialist C, during turnover that he obtained the inoperable 1EMF36 grab sample with the Unit Vent weekly grab sample at 0103 hours. Specialist C discussed this incident with RP Management, and it was concluded that a Technical Specification Violation had occurred because the inoperable 1EMF36 grab sample was not obtained at 0005 hours to comply with the sampling requirement of once per 12 hours when 1EMF36 is inoperable. This incident is attributed to Inappropriate Action due to Specialist A improperly following the correct procedure and a Management Deficiency because less than adequate training had been given. Corrective actions included communicating this incident to all appropriate RP personnel. An enhancement to the RP procedure HP/0/B/1009/11, EMF Loss is planned to further clarify sampling requirements, and training will be provided on this procedure.
4131991023 | Catawba 1 | 11/17/1991 | 12/17/1991 | 9112270110 | <strong>Technical Specification 3.0.3 Entered As A Result Of Both Trains Of Control Room Area Ventilation System Being Inoperable Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1991, at 1040 hours, Unit 1 at 100% power in Mode 1, Power Operation, and Unit 2 in No Mode (Defueled), Operations personnel discovered that damper 1-CR-D-10, suction isolation damper for A Train Control Room Air Handling Unit, in the Control Room Ventilation (VC) and Chilled Water (YC) System had failed closed. With 1-CR-D-10 closed, A Train VC/YC was inoperable. Train B of the VC/YC system had been declared inoperable on November 11, 1991 at 0145 hours, due to B Train Nuclear Service Water (RN) system work. With both Trains of VC/YC inoperable, Unit 1 entered Technical Specification (T/S) 3.0.3, at 1040 hours. Damper 1-CR-D-10 was manually positioned and blocked open to restore operability to A Train VC/YC at 1045 hours and T/S 3.0.3 was exited. Work Request 56692OPS was initiated to investigate and repair the actuator on damper 1-CR-D-10. The actuator was repaired and the damper was declared operable at 1610 hours on November 19, 1991. This incident is attributed to equipment failure/malfunction due to a failed hydromotor. The ventilation task force is evaluating replacement of hydromotors with a more reliable actuator.
4131991024 | Catawba 1, Catawba 2 | 10/09/1991 | 11/07/1991 | 9111180156 | <strong>Technical Specification 3.0.3 Entry As A Result Of Both Trains Of Control Room Area Ventilation Being Inoperable Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1991, at approximately 0912 hours, with Units 1 and 2 in Mode 1, Power Operation, at 100% power, Technical Specification (T/S) 3.0.3 was entered due to both trains of the Control Room Area Ventilation (VC) and Chilled Water (YC) Systems being declared inoperable. Train 'A' was declared inoperable after its chiller tripped due to spurious actuation of the low refrigerant temperature cutout switch. An investigation revealed that the root cause for the Train 'A' YC Chiller trips was due to corroded switch contacts. The Train 'B' YC Chiller inoperability was due to the chiller failing to start. A chiller motor overload occurred as a result of a problem with the guide vane actuator. YC Train 'A' was declared operable and returned to service after replacing the low refrigerant temperature cutout switch. Train 'B' YC Chiller was evaluated and declared operable after corrective action was performed on the guide vane actuator. T/S 3.0.3 was exited at 1515 hours. This incident is attributed to equipment failures. Subsequent corrective actions restored both chillers to operable status. Planned corrective actions include replacing the guide vane actuator on 'B' Chiller. Additional corrective actions may be implemented upon completion of an investigation of both incidents.
4131991025 | Catawba 1 | 07/30/1991 | 11/14/1991 | 9111190355 | <strong>Past Inoperability Of The CA Sump System Due To A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1991, Unit 1 was operating in Mode 1, Power Operation, at 100% power. The Unit 1 High-High Auxiliary Feedwater Turbine Driven Pump (CATDP) sump level annunciator was continuously alarming in the Control Room. Upon investigation, it was discovered that both the 1A & 1B CATDP sump pumps were operating (as expected on receipt of a Hi-Hi alarm) although the sump level was not decreasing. It was also observed that the Liquid Radwaste System (WL) Floor Drain 1D1 & 1D2 sump pumps were running at this time. All four sump pumps discharge to the Turbine Building Sump through radiation monitor 1EMF52 by way of a common header. It was concluded that, with valve 1WL846 throttled, the WL Floor Drain D sump pumps discharge head was overcoming the discharge head of the CATDP sump pumps thereby creating a situation in which there was no flow from the CATDP Sumps. A Past Operability evaluation concluded that the Auxiliary Feedwater (CA) System would not have been able to meet its safety related design basis with 1WL846 throttled. This incident is attributed to a Design Deficiency due to the unanticipated interaction between systems. Corrective action included opening the throttled valve in the common discharge header to restore the CA Sump System to operability and initiation of alternate sampling of the sump discharge. An engineering study will be performed to develop a permanent solution.
4131991026 | Catawba 1 | 10/17/1991 | 11/18/1991 | 9111260293 | <strong>Solid State Protection System Technical Specification Violation Due To A Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1991, at 1330 hours, Unit 1 was operating in Mode 1, Power Operation. During performance of a Solid State Protection System (SSPS) Bimonthly Surveillance, a jumper was discovered across terminals inside the Unit 1 Train B SSPS cabinet by Instrument and Electrical (IAE) Specialists. SSPS Train B was not removed from service. It was determined the jumper would prevent the Train B Reactor Trip Breakers (RTBs) from opening on coincident Train A and B SSPS General Warnings (GW) since the Train A GW input to Train B was blocked. However, the Train A RTBs would have tripped upon receipt of a coincident SSPS GW. All General Warning alarms and annunciators were functional as were all other Reactor trip functions. It could not be determined by the investigation, by review of the surveillance tests, or any related SSPS work history, as to when this jumper was placed or how it was left in the cabinet. This incident is attributed to a Possible Inappropriate Action which may have occurred during activities which require blocking SSPS GW signals. The jumper was removed by 1430 hours. IAE inspected Unit 1 and 2 SSPS cabinets to ensure that similar jumpers were not present. Planned corrective actions include revisions to the IAE procedures, cabinet inspections following the Unit 2 outage, and an evaluation of the current controls over the use of jumpers.
4131991027 | Catawba 1 | 10/18/1991 | 11/20/1991 | 9111260177 | <strong>Vital Battery 1EBB Inoperable Due To Resistance Reading Exceeding Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1991, Unit 1 was operating in Mode 1, Power Operation, at 100% power. Maintenance Engineering Services (MES) personnel determined that Battery Bank 1EBB in the 125VDC Vital Instrumentation and Control Power (EPL) system was inoperable. During the final review of Standing Work Request (SWR) 007877SWR, originated to measure cell to cell and terminal connection resistance, MES identified two battery terminal connections that exceeded the maximum Technical Specification resistance values. The SWR had been performed on August 27, 1991. This incident is attributed to Inappropriate Action due to lack of attention to detail. Corrective actions included replacement of cable connectors, procedure enhancement, and management discussion of the incident with personnel involved.
4131991028 | Catawba 1, Catawba 2 | 10/24/1991 | 11/20/1991 | 9112030405 | <strong>Technical Specification Violation Due To Exceeding Liquid Waste Release Limits As A Result Of Inappropriate Actions</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1991, between 1000 hours and 1120 hours, with Unit 1 in Mode 1, Power Operation, at 100% power and Unit 2 in Mode 5, Cold Shutdown, a Technical Specification (T/S) Violation occurred due to exceeding the Liquid Waste Release (LWR) limits because inadequate dilution flow was available for the LWR discharge rate selected for the LWR. The incident was discovered when Radiation Protection (RP) Specialist B reviewed the LWR because a Chemistry Assistant Technician questioned the validity of the dilution flow requirements specified by the LWR computer. RP Specialist B notified appropriate RP Management of the incident. The excessive discharge flow was selected for the LWR because Chemistry Specialist A misread the exponent on the dilution flow required for the discharge rate selected. Chemistry Assistant Technician B independently verified that the selected discharge rate and dilution flow were correct. This incident is attributed to Inappropriate Actions because the exponent was misread. Corrective actions included counselling the Chemistry Specialist A and Assistant Technician B and appropriate notifications of the incident. Planned corrective actions include procedure enhancements to HP/0/B/1004/04, Radioactive Liquid Waste Release, and OP/0/B/6500/60, Discharge of an AMT to the Environment, and changes to the LWR computer program to improve the information provided.
4131991029 | Catawba 1 | 11/26/1991 | 12/18/1991 | 9112270011 | <strong>Technical Specification Violation From Failure To Perform Reactor Trip System Surveillance Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1991, Unit 1 was in Mode 1, Power Operation, at approximately 100% power. During preparation of a retype of Unit 2 procedures, it was discovered that the surveillance requirement for the Turbine Startup Pressure Switch Alarm (4.3.1.1, Table 4.3-1, Item 16a) had not been performed on Unit 1 during 1EOC5 and subsequent Turbine startups. This surveillance requirement was inadvertently left out of retype #8 of PT/1/A/4250/02B, Weekly Main Turbine Valve Movement Test. Operations Support engineer discovered the error and immediately issued retype #9 to PT/1/A/4250/02B, which included the surveillance requirement. This Inappropriate Action was discussed with the responsible Operation Support engineer. The procedure was placed on shift and performed to satisfy Technical Specification requirement. A Continuing Improvement Action Team has been formed to improve overall quality of the Operations Department.
4131991030 | Catawba 1 | 11/21/1991 | 12/18/1991 | 9112270040 | <strong>Technical Specification Violation Due To A Missed Grab Sample On Radiation Monitor EMF-33 As A Result Of Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1991, at 2200 hours, with Unit 1 in Mode 1, Power operation, at 100% power, a Technical Specification (T/S) violation occurred due to a missed grab sample for the inoperable Condenser Air Ejector Exhaust Monitor 1EMF33. Radiation Protection (RP) Specialist A was involved with other job duties and failed to obtain the grab sample at 2200 hours. The grab sample was obtained at 2250 hours and RP management was notified of the Technical Specification violation due to the inoperable 1EMF33 not being sampled within the required 12 hour time frame. This incident is attributed to Inappropriate Action due to RP Specialist A identifying the proper response, but not in time. As a corrective action, EMF's which require a grab sample every 12 hours when inoperable are now being sampled twice per shift. RP procedure HP/0/B/1009/11, EMF Loss, will be updated to reflect this change. RP also plans to pursue the possibility of obtaining greater flexibility for scheduling EMF grab samples when required by T/S Action Statements. This will be pursued when this T/S is converted into a Selected Licensee Commitment (SLC).
4131991031 | Catawba 1 | 12/01/1991 | 12/30/1991 | 9201060364 | <strong>Technical Specification 4.0.5 Violation As A Result Of Inappropriate Action Due To A Missed IWV Inservice Inspection Stroke Time Test Of Valve 1CA64</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, Unit 1 was in Mode 1, Power Operation. Performance (PRF) technicians were attempting to perform the quarterly IWV Surveillance Stroke Timing Test on valve 1CA64, based on Technical Specification 4.0.5 Surveillance Requirements. Due to a problem with the Operator Aid Computer (OAC) valve indication, PRF was unable to complete the test. A Work Request (W/R) was written to repair the problem. The W/R was assigned an appropriate priority and was "to be completed" by November 25, 1991, within the 25% grace period. Upon discovery on December 2, 1991, that the W/R had not been worked, a 72 hour action statement was entered for CA operability and the valve was tested locally. Instrument and Electrical (IAE) personnel found the limit switches misadjusted on 1CA64. IAE adjusted the limit switches for proper indication. The failure to retest valve 1CA64 within the required time is attributed to Inappropriate Action. Corrective actions included performing a new stroke time test for valve 1CA64 to verify acceptance criteria were met.
4141991001 | Catawba 2 | 01/08/1991 | 02/05/1991 | 9102130013 | <strong>Feedwater Isolation on Hi Hi Steam Generator Level Due to Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1991, a Feedwater Isolation signal occurred at 0207:33 hours as Unit 2 Steam Generator 'A' level increased to the Hi Hi level setpoint. Unit 2 was in Mode 3 at the time of the incident with the Auxiliary Feedwater (CA) System supplying water to the Steam Generators (S/Gs) under manual flow control. The feedwater isolation signal initiated the appropriate system response by tripping the Train B Main Feedwater (CF) pump which was operating in the recirculation mode and closing the appropriate containment isolation valves with the exception of valve 2CA186, S/G B tempering flow to CA nozzle, which had been closed prior to the incident. The Operator at the Controls (OATC) was distracted from the control boards by other Control Room activities while the S/G 2A Level Deviation Alarm was in alarm. This incident is attributed to Inappropriate Action due to the operator not restoring the S/G 2A water level to the normal level to clear the S/G 2A Level Deviation Alarm. The corrective actions included resetting the CA auto start signal, restoring normal S/G water levels, verifying S/G 2B was isolated, and manually closing 2CA188, S/G D tempering flow to CA nozzle. Investigation of the misaligned valve (2CA-186) is planned.
4141991002 | Catawba 2 | 01/06/1991 | 01/31/1991 | 9102070179 | <strong>Technical Specification Violation Due to a Valve Being Returned to Service with and Expired Surveillance</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1990, with Unit 2 in Mode 1, Power Operation, 2NM-197B, S/G Upper shell Sample Insd Cont Isol Vlv, would not open during Auxiliary Safeguards testing. The valve was deenergized and tagged closed to ensure containment integrity, and a work request was generated for its repair. Since 2NM-197B would not open, the required stroke time test was not completed by the late test date, December 18, 1990. However, a Technical Specification Operability Notification Sheet (TSONS) was not generated. On January 6, 1991, with Unit 2 in Mode 3, Hot Standby, work was completed on 2NM-197B and at 1 31 hours the valve was declared operable, even though the surveillance had expired on December 18, resulting in a violation of Technical Specifications. On January 7, at approximately 0800 hours, with Unit 2 in Mode 3, a Performance Test Supervisor noted while reviewing the Shift Manager's Logbook that the repair of 2NM-197B was complete. Performance personnel satisfactorily stroke time tested the valve by 0910 hours. This incident is attributed to an inappropriate action, because Performance personnel did not ensure that a TSONS was submitted to document the surveillance due on valve 2NM-197B. As corrective actions, this incident has been discussed with Performance personnel and a program has been implemented to ensure that a TSONS is generated when a surveillance is due. .
4141991003 | Catawba 2 | 01/08/1991 | 02/06/1991 | 9102130099 | <strong>ESF Actuation Due to Improper Isolation of Control Function During Corrective Maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1991, at 1626 hours, with Unit 2 in Mode 3, Hot Standby, Instrument and Electrical (IAE) technicians were performing corrective maintenance within the Unit 2 Main Feedwater pump (MFWP) control cabinets under direction of a Maintenance Engineering Services (MES) work plan. IAE technicians were placing a jumper to allow elimination of wiring that was not removed during a 1989 modification. An inadvertent initiation of the Auxiliary Feedwater System (CA) occurred when the technicians placed a jumper across terminals causing Train 'A' of the CA system logic to react as if both MFWPs had tripped. After determining the nature of the actuation, Operations terminated the event and returned the plant to normal Mode 3 conditions. Corrective maintenance was resumed and successfully completed after the mistake in circuit isolation was discovered. This event has been attributed to an Inappropriate Action due to a lack of attention to detail. Corrective actions for this event include a review/revision of the existing Independent Verification programs along with training for any revisions made.
4141991004 | Catawba 2 | 04/10/1991 | 05/09/1991 | 9105150211 | <strong>Technical Specification 3.0.3 Entered for Both Trains of Containment Valve Injection Water System Being Inoperable Due to Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1991, at 1755 hours, with Unit 2 in Mode 1 at 100% power, Power Operation, the "B" Train of Containment Valve Injection Water (NW) System was declared inoperable due to the Seal Water to Liquid Radwaste (WL) valve, 2NW68B, failing to open. The NW System "A" Train was also inoperable at this time due to Nuclear Service Water (RN) "A" Train being out of service in support of Unit 1 outage work. Since both trains of the NW system were inoperable, Unit 2 entered Technical Specification 3.0.3. Maintenance work on valve 2NW68B was previously completed on March 2, 1991 on Work Request (W/R) 48118OPS, after the valve failed to open during the Auxiliary Safeguards Test Cabinet Periodic Test, PT/2/A/4200/009A. On April 10, 1991, during a failure analysis, and trending review of the subject W/R, the Maintenance Engineering Services (MES) System Engineer determined that the corrective maintenance performed on valve 2NW68B was inadequate and had reservations as to its operability. The MES Engineer requested Operations to perform a test to verify valve operability. The subsequent test determined that the valve was inoperable. During the verification test, the Seal Water to Nuclear Service Water (RN) valve, 2NW146B, which is located within the same circuit, also failed to open. W/R's were initiated to return these valves to service and a Technical Specification Operability Notification Sheet was originated by the MES Engineer. This event is attributed to an Inappropriate Action in that improper action was taken in signing off a W/R without correcting the root cause of the failure. A program has been developed to notify MES Engineers when a work item requires Staff Engineering support.
4141991005 | Catawba 2 | 02/12/1991 | 03/12/1991 | 9103200170 | <strong>Technical Specification 3.0.3 Entered Due to Both Trains of Nuclear Service Water Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1991, at 0840 hours, with Unit 2 at 99.5% power in Mode 1, Power Operation, Operations personnel discovered 2A1 Diesel Generator (D/G) Starting Air Tank pressure at 200 psig. The minimum operability pressure for these tanks is 210 psig. Being below the minimum pressure, the D/G Starting Air (VG) System was unable to provide the design bases of supporting two starts followed by three days of operation without the use of the VG air compressors. This rendered D/G 2A inoperable. D/G 2B was also inoperable at this time for scheduled maintenance activities. With both Diesel Generators inoperable, Unit 2 entered Technical Specification (T/S) 3.0.3, due to both trains of Nuclear Service Water being rendered inoperable. Tank pressure was quickly restored above 210 psig at 0852 hours by manually opening process flow valve, 2VG041, which had failed in the closed position. T/S 3.0.3 was exited at that time. This incident has been attributed to improper installation. Corrective actions include an expanded preventive maintenance program for the control valves/operators, increasing operating air pressure to the control valves, installing all new solenoid valves, and rerouting air control lines.
4141991006 | Catawba 2 | 04/16/1991 | 05/16/1991 | 9105280194 | <strong>Hi Hi Steam Generator Level (P-14) Resulting In A Turbine Trip And Auxiliary Feedwater Start Due To Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1991, at approximately 1452 hours, with Unit 2 in Mode 1, Power Operation, at approximately 25% Reactor Power, a Hi Hi Steam Generator (S/G) (P-14) signal was received due to '2C' Main Feedwater Control valve, 2CF46, not modulating to meet S/G 'C' demand. The P-14 signal tripped the Main Turbine and the Train 'B' Main Feedwater (CF) pump, resulting in an Auxiliary Feedwater (CA) autostart. The appropriate CF and CA valves started to close, but reopened as designed when the P-14 signal cleared. The Operator at the Controls (OATC) manually initiated a feedwater isolation and inserted rods until power decreased below Power Range indication. An investigation of the event revealed that the Main Feedwater By-pass Check Valves (2CF-166, 167, 168, 169) failed to seat properly. This allowed some of the CA flow to enter the S/Gs through the lower feedwater nozzles. This incident is attributed to an Inappropriate Action by the Instrument and Electrical (IAE) technician. Corrective actions include procedure revisions.
4141991007 | Catawba 2 | 05/10/1991 | 06/04/1991 | 9106110289 | <strong>Technical Specification 3.0.3 Entered As A Result of Both Trains Of Auxiliary Building Ventilation Filtered Exhaust System Being Inoperable Due To An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1991, at approximately 0338 hours, with Unit 2 in Mode 1, Power Operation, Technical Specification (T/S) 3.0.3 was entered due to both trains of the Auxiliary Building Filtered Exhaust (VA) System being inoperable, T/S 3.0.3 was exited at 0351 hours when the operator returned VA 'B' train to service. The Operations worklist for the night shift included the tagging of 'A' train VA in preparation for scheduled maintenance on the day shift. While completing the tagouts, the Non-Licensed Operator (NLO), Work Control Center Senior Reactor Operator (WCC) (SRO), Unit Supervisor (US), and Shift Supervisor (SS) misunderstood confusing information on the worklist. As a result, the 'B' train VA filtered exhaust fan motor breaker was tagged in the off position. This incident is attributed to an inappropriate action due to a lack of attention to detail. An Operations committee, Reduce The Trend (RTT), is reviewing all pre-planned tagouts for the VA System. This committee will provide recommendations on changes and improvements in the VA pre-planned tagouts. In addition, operators during requalification and the hot license class will receive operator proficiency training concerning the incident.
4141991008 | Catawba 2 | 05/29/1991 | 08/27/1991 | 9109090267 | <strong>Unit 2 Reactor Trip Due To An Equipment Failure Which Caused Reactor Coolant Pump 2B To Trip</strong><br /><i>Abstract:&nbsp;</i>On May, 29, 1991, at 0049 hours, Unit 2 was in Mode 1, Power operation, when a Reactor trip,occurred due to low flow on Loop 'B' of the Reactor Coolant (NC) System. The 6900 Volt switchgear feeder breaker, 2TB-3, for NC Pump 2B had tripped due to a spurious activation of a ground fault relay. The unit trip response was normal. Low - Low Steam Generator Level initiated the Auxiliary Feedwater (CA) System. The NC system was stabilized when control room operators reset the CA Auto Start and steam generator levels returned to normal. Power Delivery personnel determined that a Silicon Controlled Rectifier (SCR) within the relay had become electrically degraded, resulting in the spurious initiation of 2TB-3. The SCR was replaced and the relay was returned to service. This incident has been attributed to an Equipment Malfunction due to the degraded SCR. The remaining NC Pump ground fault relay SCRs were tested with no other failures detected. Corrective actions include testing a sample group of switchgear relays and to add SCR tests to the existing switchgear protective relay preventive maintenance activities.
4141991009 | Catawba 2 | 07/10/1991 | 08/08/1991 | 9108130343 | <strong>Technical Specification 3.0.3 Entry Due to High Flow Rates of the Annulus Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1990, a Problem Investigation Report was issued which resulted in limiting the Annulus Ventilation (VE) System flow rates to 8700 CFM due to operability concerns. On July 10, 1991, at 1120 hours, with Unit 2 in Mode 1, Power Operation, at 100% power, two Performance Engineers discovered during a review of a Test Procedure that the Unit 2 VE System flow rates exceeded the 8700 CFM limit. It would be possible, following a Design Basis event, for humidity to reduce the carbon adsorber efficiency because the VE System heaters may be incapable of adequately reducing the humidity which could increase calculated doses. A Performance Engineer did not complete a procedure change to specify the new limit by the time the VE System was tested on June 19, 1991, and July 1, 1991. Train 2A was inoperable at the time of the discovery. Technical Specification (T/S) 3.0.3 was entered at 1155 hours when Train 2B was declared inoperable. T/S 3.0.3 was exited at 1710 hours upon Train 2B operability due to correct flow rate adjustments. This incident is attributed to Inappropriate Action due to failure to complete the procedure change and Management Deficiency due to lack of control/tracking of commitments to comply with operability evaluations. An approved T/S amendment restoring the original flow rate limits and an improved method to control/track commitments will be implemented.
4141991010 | Catawba 2 | 09/11/1991 | 10/09/1991 | 9110180010 | <strong>Technical Specification Required Shutdown Due To An Inoperable Standby Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1991, at approximately 0505 hours, the Unit 2 Standby Diesel Generator (D/G) 2A was removed from service for corrective maintenance on its Starting Air (VG) System. This action required Unit 2 to enter a 72 hour Technical Specification (T/S) Action Statement. After completion of the VG System corrective maintenance, an operability test was initiated to verify engine operability. At approximately 1230 hours, on September 11, D/G 2A tripped when the lube oil outlet temperature setpoint was reached. Subsequent to the trip and while the engine was coasting to a stop, a mild crankcase explosion occurred. The unit was at 100% power at the time of the incident. Because the time required to complete the D/G inspection and maintenance would exceed the 72 hour T/S Action Statement, a controlled shutdown to Mode 5, Cold Shutdown, was initiated. Unit 2 reached Mode 5 at 1055 hours on September 14. This incident has been attributed to an Equipment Failure in that the engine's thermostatic control valve, 2KD-8, failed and did not maintain the engine's lube oil temperature. Corrective actions included maintenance to repair damage to 3 of the 16 D/G 2A engine crankcase cylinders, replacement of the power elements for the thermostatic control valves, and D/G 2A engine testing.
4141991011 | Catawba 2 | 09/13/1991 | 10/14/1991 | 9110250074 | <strong>Unit 2 Cold Leg Accumulator Actuation Resulting From Reactor Coolant System Depressurization Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1991, at 0800 hours, with Unit 2 in Mode 3, Hot Standby, the Operator At The Controls (OATC) noticed the Reactor Coolant (NC) System pressure steadily decreasing. The OATC entered AP/2/A/5500/11, Inadvertent NC System Depressurization, to stop the NC System depressurization. At 0805 hours, the NC System pressure dropped below 600 PSIG, causing the Cold Leg Accumulators to begin injecting borated water into the NC System. Between 0805 hours and 0950 hours, the CLAs injected approximately 1100 gallons into the NC System, and the pressure equalized between the CLAs and the NC System. At 0950 hours, the OATC had Instrument and Electrical (IAE) technician(s) remove the Process Control Cards for Pressurizer Spray Valves, 2NC27 and 29, to close the valves. At approximately 0950 hours, NC System pressure began to increase, and the OATC exited AP/2/A/5500/11. This incident is attributed to a Design Deficiency in the temperature sensitivity of the valve positioner. Work Request 48954OPS was written for 2NC27 and 29, and corrective maintenance performed. The Operations Shift Supervisor determined the event required a four hour NRC notification. The event was later determined to require a one hour NRC notification. Corrective actions included corrective maintenance on 2NC27 and 29 and initiation of a Station Problem Report for 2NC27 and 29. Clarification of NRC notification requirements is planned.
4141991012 | Catawba 2 | 10/17/1991 | 11/18/1991 | 9111260312 | <strong>Unexpected Emergency Safeguard Feature Actuation During Unit 2 Shutdown For Refueling</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1991, with Unit 2 in Mode 1, Power Operation, while in the process of reducing reactor power in preparation for the End of Cycle (EOC) 4 Refueling Outage, an unexpected Emergency Safeguard Feature (ESF) Actuation occurred at approximately 1953 hours. Control Room Operators (CROs) had successfully reduced reactor power level from 100 to 45 percent. Turbine Impulse Pressure (TIP) was approximately 260 psig. CROs were closely monitoring TIP in anticipation of an automatic reset of the Anticipated Transient Without Scram Mitigation System and Actuation Circuit (AMSAC). The automatic reset should occur approximately two minutes after TIP is less than 260 psig. When the CROs realized that AMSAC did not properly reset, action was taken, per procedure, to manually bypass and deactivate the AMSAC circuit. Subsequently, an unexpected, partial actuation of AMSAC occurred resulting in an autostart of the Auxiliary Feedwater (CA) System Pump 2B and isolation of the Steam Generator Blowdown (BB) System and steam generator sampling portion of the Nuclear Sampling (NM) System. The CA Pump 2A was already inservice. This incident is attributed to a functional Design Deficiency of the AMSAC circuit. Corrective actions involved securing the CA Pump 2B, realigning the BB and NM Systems, and investigation of the AMSAC circuit anomaly.
4141991013 | Catawba 2 | 11/02/1991 | 11/27/1991 | 9112090354 | <strong>Technical Specification Violation Due To Inappropriate Action Rendering One Train Of The Boron Dilution Mitigation System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On Sunday, November 2, 1991, Unit 2 was in Mode 6, Refueling. During the morning, sporadic and spurious alarms were received in Train A Boron Dilution Mitigation System (BDMS). During an investigation by Operations, valve 2NV252A (Chemical Volume and Control-NV-Pump Suction from Refueling Water Storage Tank-FWST) was found red tagged closed and deenergized. The valve and its breaker were red tagged since October 26, 1991. This valve is required to open on a high flux signal from BDMS. Therefore, Train A BDMS was inoperable per Technical Specification (T/S). Two trains of BDMS are required for Modes 5 and 6. No action statement was entered and, hence, a T/S violation occurred. B Train was operable and unaffected. To return Train A to operability, the red tags were removed from the valve and breaker and the breaker energized. The BDMS test pushbutton was engaged and the interlocks were verified: 1) both Reactor Makeup water pumps stopped, 2) 1NV188A (Volume Control Tank Outlet Isolation) closed, and 3) 1NV252A opened. This incident is attributed to improper or inadvertent action due to lack of attention to detail during preparation of the tagout. The planned corrective action is to evaluate what reference materials shall reflect BDMS interlocks.
4141991014 | Catawba 2 | 11/05/1991 | 12/04/1991 | 9112160064 | <strong>Unit 2 ESF Actuation Due To Essential Bus Undervoltage Condition</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, at 2300 hours, Unit 2 was in No Mode (Defueled). An Engineered Safety Feature (ESF) actuation occurred as a result of an undervoltage signal generated on A Train 4160V essential bus (2ETA). The undervoltage condition was caused when one of the fuseholder connection stabs of the Undervoltage Relay Potential Transformer (PT) did not make contact with the essential bus. Subsequent Investigation revealed that the connection stab had been bent as a result of a loose PT fuseholder. The loose fuseholder was determined to be caused by improper removal of fuses from the PT fuseholder. This incident is attributed to a Management Deficiency, inadequate training provided for personnel performing high voltage fuse removal. Management will re-evaluate the issue concerning Operations' responsibility of high voltage equipment manipulation at Catawba. Corrective action will include resolution of the responsibility issue, procedure enhancement and development, and additional training.
4141991015 | Catawba 2 | 11/18/1991 | 12/18/1991 | 9112270005 | <strong>Technical Specification Violation Due To Lack Of A Boration Flow Path During Refueling Activities Due To Deficient Communication</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1991 Unit 2 was operating in No Mode with the core defueled. An addition to the Refueling Water Storage Tank (FWST) was made from the Boric Acid Tank (BAT). FWST makeup was completed at 1022 hours on November 19. Core reloading had begun at 2335 hours and Unit 2 entered Mode 6, Refueling. Required tank recirculation was performed. At 0355 hours on November 20, a chemistry sample indicated that the FWST boron concentration was 1975 ppm, less than the Technical Specification requirement of 2000 ppm. The Control Room was notified upon receipt of confirmatory sample results at 0422 hours and core loading was stopped at 0435 hours. A Technical Specification violation had occurred because the minimum required FWST boron concentration was not met, resulting in lack of an operable boration flow path. The FWST was declared operable at 1430 hours after boron addition and acceptable samples were obtained. Fuel loading resumed at 1500 hours. This incident is attributed to Deficient Communication between Chemistry and Operations regarding the proper boron concentration to use in FWST makeup calculations. Corrective actions included termination of fuel loading, FWST makeup to achieve required concentration, and communication enhancements to prevent recurrence.
4141991016 | Catawba 2 | 12/09/1991 | 01/08/1992 | 9201240217 | <strong>Technical Specification Violation Due To Failure Of Pressurizer Power Operated Relief Block Valve 2NC-31B</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1991, at 0230 hours, Unit 2 was in Mode 5, Cold Shutdown. The Pressurizer (PZR) failed to depressurize prior to the PZR Nitrogen fill. A PZR Power Operated Relief Valve (PORV) Block Valve, 2NC-31B, was not open as indicated. 2NC-31B remained closed because the stem separated from the wedge assembly. The PZR PORVs had been closed in the auto open mode since December 2 at 2000 hours. With the final PZR safety relief valve in place, T/S require that an inoperable PZR PORV be returned to service within 7 days or depressurize and vent the NC system within the next 8 hours. Due to the 2NC-31B failure, one of the two PORVs required to be operable was not available and the T/S action requirement was not satisfied. Therefore, the T/S violation occurred. This event is attributed to Equipment Failure. The Unit 1 and 2 PZR PORV isolation valves were radiographed to verify that the valves are open. 2NC-31B was replaced and the initial stem analysis was performed. Planned corrective actions include verification of block valve position following stroke tests and to continue evaluation of stem failure analysis data.
4161991001 | Grand Gulf 1 | 01/14/1991 | 02/13/1991 | 9102190127 | <strong>Delinquent LCO Action For Diesel Generator 11 Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>A Technical Specification limiting condition of operation (LCO) action was not satisfied after the Division 1 diesel generator (DG 11) was removed from standby service to perform preventive maintenance. A Technical Specification LCO report had been generated on the previous shift when DG 11 was made inoperable. The replacement Shift Superintendent and Shift Supervisor were made aware of the required actions. The missed surveillance was due to personnel error by plant licensed operators. Inattention to detail was determined to be the cause of this event. <br /><br /> Station procedure 06-OP-1000-D-0001 was amended to incorporate a surveillance requirement trigger for the diesel generators. The procedure provides a method of completing and tracking surveillances required on a daily or more frequent schedule. The procedure change should prevent recurrence of similar delinquent diesel generator LCO actions. <br /><br /> The late verification of offsite A. C. power sources did not result in a compromise to plant safety. All emergency core cooling systems were operable and available to perform the required safety functions.
4161991002 | Grand Gulf 1 | 04/06/1991 | 07/31/1991 | 9108050329 | <strong>Reactor Scram During ATT Surveillances</strong><br /><i>Abstract:&nbsp;</i>During a routine surveillance of the Main Turbine Mechanical Overspeed Trip Devices, an automatic reactor shutdown occurred. The test was being performed by the Automatic Turbine Tester (ATT) which uses a computerized test program. During the reset step of the computer program, a miniature circuit breaker in the ATT circuitry tripped open. This deenergized three solenoids which were needed to prevent a turbine trip due to testing. The cause of the premature breaker trip is attributed to the circuit breaker being undersized for its application. Due to aging and the breaker operating at loads which sometimes exceeded its rated current value, the breaker was operating in a degraded condition. The operating module which contained the miniature breaker was replaced and the test was successfully completed. <br /><br /> Following a review of the test circuitry design, a breaker with a higher current rating was placed in the test circuit. The circuitry was tested satisfactorily and used to perform the mechanical overspeed test. The installed breaker will remain in service pending further design review. All safety systems functioned as designed. The reactor water remained at least 164 inches above the top of active fuel.
4161991003 | Grand Gulf 1 | 04/25/1991 | 05/28/1991 | 9106040431 | <strong>Containment Penetration Not Surveilled</strong><br /><i>Abstract:&nbsp;</i>A containment penetration was determined to be in noncompliance with local leak rate testing requirements. The horizontal fuel transfer tube design incorporates a bellows seal closure arrangement. The transfer tube closure hatch features double o-rings and test connections. On the initial review of containment penetrations and on subsequent reviews, the closure hatch seal was interpreted to be the only seal arrangement for this penetration subject to 10 CFR 50 Appendix J testing. Due to the complex penetration arrangement, the bellows assembly was not identified as being exposed to containment pressure and therefore was not included in the surveillance procedure for leak rate testing. <br /><br /> Plant documents affected by this discovery will be revised to identify the bellows as part of the containment penetration boundary. Other containment penetrations with bellows assemblies and other atypical sealing arrangements were reviewed to determine if any other similar containment isolation boundaries had been overlooked in development of the surveillance procedure for leak rate testing. No additional deficiencies were found. No safety related equipment was affected adversely by this condition. The health and safety of the general public was not affected.
4161991004 | Grand Gulf 1 | 06/11/1991 | 07/10/1991 | 9107160256 | <strong>Reactor Scram Due To Loss of Feedwater</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1991, a controlled shutdown was in progress for maintenance on the mechanical seals for both reactor recirculation water pumps. In accordance with approved plant procedures, the reactor recirculation water pumps were shifted from fast to slow speed. This caused a swell in reactor water level which resulted in a decrease in feedwater and condensate flow. The condensate system flow rate decreased to the minimum flow setpoint, but the minimum flow valve failed to respond to the low flow condition. <br /><br /> The failure resulted in a loss of feedwater and a subsequent automatic reactor scram. The failure is attributed to a failed pneumatic relay inside the valve positioner. The most probable cause for the relay failure is excessive vibration experienced during minimum flow conditions. The positioner was replaced and retested satisfactorily. An evaluation will be performed to determine methods or modifications to preclude valve failure due to vibration. In the interim, a task will be implemented to perform a functional test and a visual inspection of the positioner prior to controlled shutdowns and start-ups. Additionally, a task will be generated to replace the valve's positioner each refueling outage until a more suitable resolution is determined. Based on reviews of the event, all safety systems functioned as designed. The reactor water remained at least 140 inches above the top of the active fuel during the transient.
4161991005 | Grand Gulf 1 | 06/17/1991 | 10/01/1991 | 9110080224 | <strong>Update on Reactor Scram Due to 500 kV Circuit Breaker Fault</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1991 a fault occurred on the B-phase of breaker J5232 (500 KV). The fault resulted in a loss of power (LOP) to two balance of plant (BOP) busses and two engineered safety feature (ESF) busses. An automatic reactor scram occurred due to a main turbine control valve fast closure signal which was a result of the breaker fault. Power was restored to the BOP busses via their alternate supply. <br /><br /> The emergency diesel generator associated with each deenergized ESF bus responded to the bus undervoltage and functioned as designed. Power to the ESF busses was restored and the diesel generators were secured and placed in standby. The LOP also caused a Main Steam Line Isolation valve closure which resulted in a loss of feedwater and an increase in vessel pressure. Main Steam Line Safety Relief valves (SRV) were manually operated to control pressure. The High Pressure Core Spray System automatically initiated and injected into the vessel due to a low water level (reported per TS 3.5.1.h). <br /><br /> Based on an investigation of the occurrence, it was determined that the cause of the breaker fault is attributed to inadequate maintenance practices. There was no degradation of safety systems or components during the transient. Reactor water level was maintained at least 121 inches above the top of active fuel.
4161991006 | Grand Gulf 1 | 06/25/1991 | 07/25/1991 | 9108020225 | <strong>RWCU Isolation Due To Lightning Strike To 500 kV Transmission Line</strong><br /><i>Abstract:&nbsp;</i>Automatic actuation of the reactor water cleanup (RWCU) system Division 2 containment isolation valves occurred during a storm on June 25, 1991 at approximately 1719 hours. The 500 kV electrical transmission line between GGNS and the fossil fueled Baxter Wilson generating facility sustained a lightning strike. Feeder breakers at both stations tripped open due to the resultant voltage spike. The 500 kV distribution system features shielding wires. <br /><br /> The RWCU leak detection system consists of sensitive Riley Panalarm temperature switches. The RWCU leak detection logic actuates on a single channel trip signal. The voltage spike probably affected the operation of a Riley temperature switch and caused the RWCU isolation. <br /><br /> The actuation of the RWCU isolation system did not compromise the safe operation of GGNS. All safety related equipment operated as designed. <br /><br /> The safety and health of the general public was not affected by this event. No corrective actions are warranted for this event.
4161991007 | Grand Gulf 1 | 07/28/1991 | 08/27/1991 | 9109050155 | <strong>Reactor Scram Upon Load Shed of Balance of Plant Equipment</strong><br /><i>Abstract:&nbsp;</i>A load shed of balance of plant (BOP) equipment occurred while troubleshooting a Division 2 load shedding and sequencing (LSS) system trouble alarm. A reactor scram ensued. Investigation revealed that LSS panels had a logic coupling in that energizing the 15 volt converter without power from the 24 volt converter will cause a BOP load shed. This system response contradicts LSS system specification requirements. A vendor design error occurred and was not detected previously. Pre-operational testing had not detected the logic coupling and was a contributing factor. LSS panels were modified to preclude BOP load shed due to loss of the LSS panel 24 volt power converter. Analysis of the reactor scram and subsequent events determined that safety systems operated as designed. This report is being submitted to describe the ESF actuations pursuant to 10 CFR 50.73(a)(2)(iv) and plant Technical Specification 3.5.1 Action h.
4161991008 | Grand Gulf 1 | 07/28/1991 | 08/27/1991 | 9109050150 | <strong>RPS Actuation Due to Malfunction of Neutron Monitoring</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1991, following an automatic scram, operation personnel inserted the Intermediate Range Neutron Monitors (IRMs) in accordance with approved plant procedures. One monitor, which was inserted, had been previously identified as inoperable due to erratic swings on its local indication panel. <br /><br /> Subsequent to the insertion and stabilization of the plant, maintenance was scheduled to be performed in order to correct the abnormal operation of the IRM. The monitor was required to be withdrawn to perform maintenance. <br /><br /> As the monitor was being withdrawn, an upscale spike occurred causing a trip on the 'A' Reactor Protection System (RPS). This resulted in an automatic RPS actuation due to the 'B' RPS being in the tripped condition. The cause of the RPS actuation is attributed to equipment malfunction.<br /><br /> Inadequate procedural controls, poor control room work practices and a breakdown of administrative controls were major contributing factors in the occurrence. <br /><br /> The IRM was replaced and retested satisfactorily. The licensed operator involved was counselled. The Instrument and Control (I&C) Supervisor was instructed on the control room command function.
4161991009 | Grand Gulf 1 | 07/29/1991 | 08/27/1991 | 9109050158 | <strong>RPS Actuation Due To Low Reactor Water Level Condition</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1991, an automatic Reactor Protection System (RPS) actuation occurred due to a low reactor water level condition. At the time of occurrence, the plant was in the process of completing a shutdown to cold conditions as required by Technical Specifications.<br /><br /> In an attempt to place shutdown cooling (SDC) inservice, the RHR pump was started and the SDC discharge valve opened. System flow increased, then decreased below the minimum flow setpoint. The pump was secured and the discharge and minimum flow valves were closed. Approximately 1 minute following the shutdown of the RHR pump, vessel level began to decrease. The cause of the low level condition was determined to be the formation and collapse of voids in the Residual Heat Removal (RHR) System. Inadequate procedural guidance was a major contributing factor in the formation of the voids in the SDC piping. <br /><br /> Procedures were changed to preclude recurrence and plant personnel will be trained on this occurrence. <br /><br /> All safety systems performed as designed during this occurrence. There was no degradation of plant safety systems or components as a result of the occurrence. The minimum vessel water level was at least 177 inches above the top of active fuel.
4161991010 | Grand Gulf 1 | 08/10/1991 | 09/09/1991 | 9109130187 | <strong>Lightning Induced Spikes Causes APRM Scram</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1991, a severe thunderstorm was in progress in the site vicinity. During the storm, a lightning strike caused a spike on plant neutron monitoring instrumentation. The reactor automatically scrammed due to the spike simulating a high flux signal on the Average Power Range Monitors (APRMs). The spike caused two High Pressure Core Spray (HPCS) low water level channels to trip. HPCS did not initiate due to the short duration of the spike. Reactor water level decreased to -19 inches and was subsequently restored to normal by the feedwater system. <br /><br /> A functional check of APRM indications and HPCS trip units was performed prior to plant startup. No adverse effects were observed. <br /><br /> Following an evaluation, recommendations were made for extending the existing lightning protection system to provide expanded site protection. There was no degradation of safety systems or components as a result of this occurrence.
4161991011 | Grand Gulf 1 | 10/03/1991 | 11/04/1991 | 9111120241 | <strong>Noncompliance With EOC/RPT Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>While scheduling surveillance activities for the next refueling outage, review of previously conducted surveillances discovered that an improper group of components had been surveilled in 1987. This was contrary to the schedule specified by Technical Specification 4.3.4.2.3. Technical Specification 4.3.4.2.3 prescribes that testing of these redundant trip systems be performed in a staggered schedule such that all channels are tested at least once per 36 months. <br /><br /> The schedule developed in 1986 designated the improper group of channels to be surveilled. This scheduling did not consider the staggered schedule of the surveillance requirement. Clearer guidance will be developed to ensure proper scheduling of surveillances. <br /><br /> Performance of the surveillance was conducted successfully on October 5, 1991 on the affected trip system channels to comply with Technical Specification 4.3.4.2.3 requirements. The erroneous surveillance testing situation did not increase the risk of safety function failure. The safety and health of the general public was not compromised by this event.
4161991012 | Grand Gulf 1 | 11/19/1991 | 12/18/1991 | 9112270288 | <strong>Lightning Induced Scram</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991, a thunderstorm with severe lightning occurred in the site vicinity. At approximately 2049, during the storm, the Division 2 Average Power Range Monitors (APRM) IG! received a high neutron flux signal resulting in a trip on the Division 2 Reactor Protection System (RPS). Prior to the trip occurring on the Division 2 RPS, a Maintenance surveillance was in progress which caused the Division 1 RPS to be in the tripped condition. Both systems being in the tripped condition, resulted in an automatic reactor scram. Following the scram, vessel water level decreased to -14 inches. Water level was restored by the Condensate and Feedwater Systems. <br /><br /> Based on a review of computer data, it appears that the output of a five volt power supply associated with the APRMs may have been deenergized, then reenergized. This would have resulted in an APRM scram. A supplemental report will be submitted following the determination of the root cause of the lightning induced scrams experienced at GGNS.
4161991013 | Grand Gulf 1 | 11/19/1991 | 12/20/1991 | 9201030214 | <strong>Rainwater Enters Secondary Containment Via Electrical Conduits</strong><br /><i>Abstract:&nbsp;</i>A construction deficiency was discovered to have provided a flow path for rainwater to enter secondary containment NG! via electrical conduits. The deficiency consisted of improperly installed conduit seals. The event resulted from rainwater collecting in the underground duct banks in the vicinity of the auxiliary building. Contributing factors included exceeding capacity of sump pumps and the cover being off a manhole to these banks. The influx of rainwater exceeded the sump pump capacity and permitted the water level in the first manhole to increase above the pump's power receptacle, thorough tripping its ground fault circuit interruptor. <br /><br /> The floor drain system WK! controlled the influx of water to prevent flooding of the immediate and surrounding areas. Water entered an adjacent switchgear room but did not intrude into any electrical equipment or other safety related equipment in the auxiliary building due to this condition. <br /><br /> Inspection of conduits which penetrate the boundary of secondary containment and control building NA! was performed to determine the extent of the deficiency. Additional conduits were found to have nonconforming seals. All identified conduits were sealed in accordance with M-0800D.
4161991014 | Grand Gulf 1 | 11/19/1991 | 12/20/1991 | 9201020134 | <strong>Voluntary Report on Drywell Airlock Pressurization</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991 following an automatic scram, plant personnel attempted to enter the drywell (D/W) personnel airlock. Entry was prevented by a differential pressure across the outer door. The opening of the door was prevented by a safety interlock. Using calibrated test equipment, the internal pressure of the airlock was determined to be approximately 40 psig, which is greater than the airlock's design pressure (30 psig). Following the depressurization of the airlock, personnel were able to attain entry. <br /><br /> Upon investigating the cause of the overpressurization, personnel discovered a plug installed in the inlet port of the outer equalizing valve (EV). A Material Nonconformance Report was written to document the condition and initiate an evaluation of the airlock. The EV appears to have been plugged since construction. The plant surveillance procedure which governs leak rate testing will be revised to include provisions for plugging the D/W airlock relief valve for leak rate testing the airlock barrel, and removing the plug afterwards. The weekly Operations surveillance procedure has been revised to require internal barrel pressure readings.
4161991015 | Grand Gulf 1 | 11/23/1991 | 12/18/1991 | 9112270291 | <strong>Automatic Isolation of RWCU</strong><br /><i>Abstract:&nbsp;</i>Automatic actuation of the reactor water cleanup (RWCU) system outboard containment isolation valves occurred on November 23, 1991 at approximately 2312 hours. The RWCU system heat exchanger room high temperature annunciator alarmed three times just prior to the isolation. No leakage of the RWCU system was observed. No plant condition or system transient which preceded or coincided with the isolation was determined to have initiated the event. <br /><br /> The RWCU leak detection system (LDS) consists of sensitive Riley Panalarm temperature switches. The RWCU leak detection logic actuates on a single channel trip signal. It is believed that this isolation was actuated by a trip signal from LDS. Previous corrective actions to LDS system have reduced such type occurrences. The suspect temperature switches were replaced following this event. <br /><br /> The actuation of the RWCU isolation system did not compromise the safe operation of GGNS. All safety related equipment operated as designed. The safety and health of the general public was not affected by this event.
4161991016 | Grand Gulf 1 | 12/30/1991 | 02/13/1992 | 9202200209 | <strong>Voluntary Report on Re-Criticality</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1991 during a plant shutdown to perform maintenance on the 'B' Reactor Recirculation Water Pump, operators suspended control rod insertion to perform a channel functional test on the Source Range Monitors (SRMs) as required by GGNS Technical Specifications. Reactor power decreased to Intermediate Range Monitor (IRM) range 1 prior to the completion of the test. During this period, reactor power began to increase due to moderator cooldown. The power increase was self-limiting. The IRMs increased until they reached ranges 7 and 8; then power stabilized. After power stabilized, the SRM functional test was completed and the shutdown was completed in accordance with plant procedures. The cause of the increase in reactor power is attributed to a decrease in moderator temperature which resulted in a positive reactivity addition. Operations personnel understood, anticipated and controlled the event in accordance with plant procedures. The occurrence posed no adverse effects on plant safety or the ability of operable plant safety systems to perform their intended functions. This event is being reported as a Voluntary Report.
4231991001 | Millstone 3 | 01/17/1991 | 02/19/1991 | 9102280221 | <strong>Inadequate Surveillance Procedure for Radiation Detector Beta Scintillation Source Check</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1991, at 0900 hours, with the plant in Mode 1 at 75% power, 578 degrees Fahrenheit and 2250 psia, it was discovered that the source check surveillance procedure for verification of operability of the beta scintillation radiation detectors did not meet the requirements of the applicable plant Technical Specification. The discrepancy was discovered after plant personnel were notified of a similar incident at another nuclear unit. The affected radiation detectors were immediately declared inoperable.<br /><br /> The root cause of this event is procedural inadequacy. The surveillance procedure for source checking the beta scintillation detectors did not require detector exposure to radiation as required by Plant Technical Specifications. On January 18, 1991 the surveillance procedure was revised and performed, and the detectors were declared operable at 1254 hours. <br /><br /> This event posed no significant safety consequences. Although the method for determining operability of the beta scintillation detectors was not in strict compliance with the plant's Technical Specifications, it was in accordance with the equipment manufacturer's recommendations for verifying detector response.
4231991002 | Millstone 3 | 02/02/1991 | 03/04/1991 | 9103130100 | <strong>Setpoint Drift on Main Steam Safety Valves Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>Between 0400 and 1600 hours on February 2, 1991, with the plant at 0% power in Mode 3 (Hot Standby), at 2250 psia and 548 degrees Fahrenheit, setpoint drift was identified while testing the Main Steam Safety Valves. Nine out of twenty valves failed the +/- 1% tolerance band set by Technical Specification Table 3.7-3.<br /><br /> No immediate corrective action was necessary since the plant was in Hot Standby.<br /><br /> The cause of the safety valve setpoint drift is inadequate design. The safety valves do not maintain their setpoint within the +/- 1% tolerance specified in Technical Specifications. The highest/lowest deviation observed was +2.1%/-2.4%. The setpoints on all of the failed safety valves were reset to Technical Specification requirement.
4231991003 | Millstone 3 | 02/03/1991 | 08/30/1991 | 9109120080 | <strong>Spurious Control Building Isolation Signals Due to Deficient Design</strong><br /><i>Abstract:&nbsp;</i>Beginning at 1427 and ending at 1504 hours, on February 3, 1991, in Mode 3 (Hot Shutdown), at 354 degrees Fahrenheit and 399 psia, six spurious Control Building Isolation (CBI) signals were received from the A Train control building ventilation inlet radiation monitor during the reactor plant shutdown for the scheduled refueling outage. On February 16, 1991 at 0648 hours, while in Mode 6 (Refueling), 97 degrees Fahrenheit and 20 psia, another spurious CBI signal was received from the A Train radiation monitor. Upon receipt of each CBI signal, the Reactor Operators immediately responded by observing that the B Train monitor was indicating normal background level while the A Train radiation monitor reading was rapidly decaying from the high alarm level to the normal background level. Having determined the A Train monitor was malfunctioning, the Reactor Operators initiated CBI signal blocks prior to the actuation of automatic control building pressurization, and manually aligned and operated the ventilation system with full recirculated filtered air for the control room pressure envelope. <br /><br /> The root cause of this event is a deficient design that resulted in induced noise causing the spurious CBI signals. <br /><br /> The B Train monitor detector was electrically isolated from the ventilation ductwork. Also, the monitor wiring, cable shielding, and grounding scheme was modified to minimize noise in the system. These modifications were completed on July 30, 1991. The A train monitor will be similarly modified by October 15, 1991.
4231991004 | Millstone 3 | 02/05/1991 | 05/15/1991 | 9105280146 | <strong>Containment Leakage in Excess of Limits Due to Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>While shutdown in Modes 5 (Cold Shutdown) and 6 (Refueling) during the performance of Local Leak Rate Testing (LLRT), the "as found" leak rates for four Containment Isolation Valves exceeded the Technical Specification Type C and Bypass leakage limits of 0.6 La and 0.042 L sub a. <br /><br /> The LLRT failures occurred on February 5, 1991, at 1331 (for 3RHS*MV8702A), February 7, 1991, at 2200 (for 3RSS*V6), February 10, 1991, at 2200 (for 3CDS*CTV91B), and February 19, 1991, at 1330 (for 3RSS*MOV23B). No immediate action was required. Leakage past 3RHS*MV8702A is believed to be due to debris or boric acid crystals on the seating surface. The penetration was flushed with water and retested successfully. <br /><br /> Leakage past 3RSS*V6 was due to improper seating caused by boric acid crystal precipitation on the seating surface. The valve seat was cleaned and an "as-left" LLRT was satisfactorily performed. Leakage past 3CDS*CTV91B was due to failure of an elastomer T-ring which had partially rolled out of its retaining groove. The T-ring was replaced and an as-left LLRT was satisfactorily performed prior to startup. Leakage past 3RSS*MOV23B was caused by separation of the vulcanized rubber seat from the valve body mounting surface. The valve was removed from the system, sent to the manufacturer for overhaul, and was reinstalled and satisfactorily retested prior to startup.
4231991005 | Millstone 3 | 02/16/1991 | 03/13/1991 | 9103210085 | <strong>Spurious Control Building Isolation Signals Due to Radiation Monitor Defective Temporary Breaker</strong><br /><i>Abstract:&nbsp;</i>At 0808, and at 0830, on February 16, 1991, in Mode 6 (Refueling), at 0% reactor power, at 97 degrees Fahrenheit and approximately 20 psia, two Control Building Isolation (CBI) signals were generated by the B Train control building ventilation inlet radiation monitor. On both occasions, the Reactor Operators immediately observed that the CBI signal was due to a loss of power to the B Train radiation monitor. The Operators then initiated a CBI block prior to the actuation of automatic control room pressurization. The control room ventilation system was already in full recirculation filtered air operation for the control room pressure envelope at the time of the spurious CBI signals. <br /><br /> The spurious B Train radiation monitor CBI signals occurred during the scheduled B Train electric power outage. A subsequent investigation revealed the loss of power to the radiation monitor was caused by a defective circuit breaker in the lighting panel that was supplying the temporary electric power to the radiation monitor. The defective breaker was replaced with an equivalent breaker.
4231991006 | Millstone 3 | 02/24/1991 | 03/26/1991 | 9104010354 | <strong>Failure To Fully Implement Radiation Monitor Action Statement Due To Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>At 1530, on February 24, 1991, while shutdown in Mode 6 (Refueling), at 0% power, 92 degrees Fahrenheit and atmospheric pressure, the Shift Supervisor determined that the process gas effluent flow rate measurements for the Turbine Building ventilation vent stack radiation monitor had not been performed in accordance with Technical Specification Limiting Condition for Operation (LCO) 3.3.3.10. The event duration was approximately 14 hours. <br /><br /> Earlier in the morning at 0136, the radiation monitor became inoperable. The midnight Shift Supervisor immediately entered the LCO which requires effluent grab samples, determination of the radiation monitor sample flow rate, and determination of the effluent process now rate. Due to a lack of enough detail in the procedure for the Radiation Monitoring Console (RMC), the required 4 hour interval measurements of the effluent process flow rate were not made in accordance with the LCO. <br /><br /> The root cause of the event is an incomplete RMC procedure. Immediate corrective action was to initiate manual process gas effluent flow rate measurements as required by the LCO. <br /><br /> Action to prevent recurrence was to increase procedural guidance in the referenced RMC procedure. This guidance will be reviewed by licensed operating shift personnel by April 15, 1991.
4231991007 | Millstone 3 | 03/14/1991 | 04/12/1991 | 9104190361 | <strong>Incomplete Implementation of Technical Specification Action Statement Due to Procedural Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1991, at 0145 hours, while shutdown in Mode 6 (Refueling), a nonlicensed operator (PEO) observed that the temporary sample pump associated with the inoperable Engineered Safeguards Features (ESF) Building Gaseous Effluent radiation monitor, 3HVQ*RE49, had been turned off. This violates the continuous sampling compensatory action requirement of Plant Technical Specification 3.3.3.10.b. The PEO was performing the process and sample flow rate estimate surveillance required in support of the inoperable radiation monitor. <br /><br /> Root cause of the event is procedural noncompliance due to a cognitive failure. The Chemistry Technician assigned to perform gas sampling for Noble gases did not restore the temporary sample pump to service following surveillance completion at approximately 2300 hours, on March 13th. Procedural deficiency is a contributing cause in that the associated Chemistry surveillance procedure did not contain positive guidance requirements for returning the temporary sample pump to service. <br /><br /> The immediate corrective action was to turn on the temporary sample pump. The Chemistry Technician was counseled on procedural compliance and attention to detail. Procedural guidance in the applicable Chemistry Department surveillance has been strengthened.
4231991008 | Millstone 3 | 03/18/1991 | 04/17/1991 | 9104240236 | <strong>Pressurizer Level Indication Errors Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1991, while shutdown in mode 5 (Cold Shutdown), an Engineering Evaluation concluded that certain level errors introduced into the three Reactor Coolant System pressurizer level transmitters, created a condition which resulted in two independent channels being inoperable in a single system designed to mitigate the consequences of an accident. The instrument inaccuracies resulted from non-condensable gas accumulation in the condensate pots/reservoirs for the pressurizer level instrument reference legs.<br /><br /> The pressurizer level instrumentation provide the primary indication to the operator for manual actions during and following accident conditions. With the errors postulated, these transmitters would have provided operators misleading information.<br /><br /> The root cause of the accumulation of non-condensible gases is inadequate design. The pressurizer level reference legs were angled upward from the pressurizer to the condensate pots, which allowed gases to build up in the condensate pots. A design change completed during the refueling outage, eliminated the condensate pots. The pressurizer reference leg taps were modified to run straight out and then angle downward via isolation valves to the level transmitters. This allows the free flow of steam and gases along the piping runs to minimize buildup of gases in the reference legs.
4231991009 | Millstone 3 | 04/08/1991 | 05/08/1991 | 9105210278 | <strong>"A" Train Service Water Inoperable Due to Pipe Erosion</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1991, at approximately 1500 hours, with the plant in Mode 4 (Hot Shutdown), an engineering evaluation concluded that a portion of the Service Water (SWP) system had been inoperable due to pipe wall thinning caused by erosion. As a result of the erosion generated wall thinning, the "A" train SWP system may not have been capable of performing its intended safety function during a seismic event. The piping is concluded to have been inoperable from November 6, 1990, to March 8, 1991. <br /><br /> The root cause of the event is program inadequacy. The applicable engineering procedure did not require that a map of the nondestructive examination measurements be made and that all of the examination data obtained on the thinned section of pipe be transmitted to the support Engineering group performing the evaluation. A contributing cause is inadequate design verification due to a cognitive failure during the original design reconciliation of the affected piping section. The checklist used for this process required that the pipe wall thickness shown on the design drawings be checked against that used in the design calculations. This was not done.<br /><br /> There was no immediate corrective action as the affected section of piping had been previously replaced. The eroded section of piping has been replaced with erosion resistant piping. Procedural guidance on pipe leak data transmittal and evaluation was strengthened.
4231991010 | Millstone 3 | 04/10/1991 | 05/10/1991 | 9105150321 | <strong>Carbon Dioxide Storage Tank Pressure Below Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1991, at approximately 1050 hours with the plant at 0% Power in Mode 3 (Hot Standby), a non-licensed Plant Equipment Operator (PEO) discovered that the Fire Protection Carbon Dioxide (CO sub 2) storage tanks pressure was 245 psig. Technical Specification 3.7.12.3 (CO sub 2 Systems) requires that CO sub 2 storage tank pressure be maintained greater that 275 psig. Compensatory firewatch patrols are required for those areas protected by the CO sub 2 fire suppression system within 1 hour of the CO sub 2 system being inoperable. This requirement was not fulfilled. The duration of the event was approximately 24 hours. <br /><br /> The root cause of the event was cognitive error. The PEO failed to notify the Shift Supervisor (SS) upon discovering the discrepancy. Also, the SS did not evaluate the deficient reading when reviewing the surveillance. The CO sub 2 tank pressure had dropped below the pressure limit due to a pressure control switch coming out of adjustment. The pressure control switch was readjusted.<br /><br /> Immediate corrective action was to establish fire patrols in the affected areas. As action to prevent recurrence, the PEO has been counselled concerning the importance of proper notification when a deficiency is discovered. Also, the SS has been counselled concerning the importance of ensuring a thorough review has been completed on all surveillances prior to acceptance.
4231991011 | Millstone 3 | 04/10/1991 | 05/10/1991 | 9105150312 | <strong>Both Trains of High Pressure Safety Injection System Inoperable Due to Relief Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1991, at 2225 hours with the plant at 0% power in Mode 3 (Hot Standby), 557 degrees Fahrenheit and 2250 psia, a safety injection system (SIH) relief valve lifted while performing a boundary valve leak test surveillance procedure. The valve did not reseat until the running "A" safety injection pump was stopped. The 79 gpm flowrate of the relief valve exceeded the 50 gpm assumed for passive failure of the safety system. <br /><br /> The root cause of the event is design deficiency. The setpoint for the relief valves was too close to the operating pressure of the system. The system has historically operated close to the relief valve setpoint. Pressure surges, valve manipulations, and surveillance testing have previously resulted in the lifting of system relief valves.<br /><br /> As immediate corrective action shift management declared the safety injection system inoperable. The "B" train relief valve, which was temporarily gagged to minimize failure during troubleshooting, were ungagged, and the "B" train was declared operable. The system design pressure was reanalyzed and the setpoint of the relief valves was increased to 2250 psia from 1765 psia. Both trains of the safety injection system were declared operable following the increase in setpoint for the "A" train and "B" train relief valves.
4231991012 | Millstone 3 | 05/03/1991 | 06/03/1991 | 9106100099 | <strong>Spurious Control Building Isolation Signals Due to Radiation Monitor Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>At 1430 hours, on May 3, 1991, with the plant in Mode 1 at 90% reactor power, 584 degrees Fahrenheit, and 2250 psia, a spurious Control Building Isolation (CBI) signal was initiated by the B Train Control Building Ventilation Inlet Radiation Monitor during power ascension following the third refueling outage. The Reactor Operators determined that the B Train radiation monitor was malfunctioning and proceeded to block the CBI signal prior to the actuation of the automatic control building pressurization. The Reactor Operators then manually aligned and operated the ventilation system with full filtered recirculated air for the control room pressure envelope. <br /><br /> A subsequent investigation revealed that the spurious CBI signal was caused by a high voltage power supply spike. The root cause of the monitor failure was determined to be a failed Single Channel Area Monitor (SCAM) board high voltage power supply. The SCAM board was replaced and satisfactorily retested. The monitor was returned to service at 1809 hours on May 8, 1991.
4231991013 | Millstone 3 | 05/15/1991 | 06/14/1991 | 9106190412 | <strong>Inoperable B Train Emergency Diesel Generator Due to Inadequate Requirements Review</strong><br /><i>Abstract:&nbsp;</i>At 1630 hours on May 15, 1991, with the plant at 100% power in Mode 1 at a pressure of 2250 psia a temperature of 587 degrees Fahrenheit, a senior licensed operator discovered the Train B Emergency Diesel Generator (EDG) air receiver 1B depressurized and isolated for maintenance with a system cross-connect valve closed. This resulted in only air receiver 2B being available to start the EDG on one bank of cylinders. The EDG will start in this lineup, but a start in the required 11-second time interval is not assured. Consequently, Train B EDG was declared inoperable.<br /><br /> The root cause of this event was improper work practices in that a senior licensed operator failed to verify the Technical Specification (TS) requirements. Testing has demonstrated that the B EDG will start within 11 seconds if the bank cross-connect valve is opened. A review of these requirements for the Train B EDG would have indicated that it was necessary to open the valve with only one receiver available to start the diesel. <br /><br /> Upon discovery, the 1B air receiver was returned to service and the cross-connect valve was closed as required by the normal lineup. The senior licensed operator involved with placing the receiver out of service was counselled on the importance of reviewing the TS requirements associated with removing safety system components from service.
4231991014 | Millstone 3 | 06/09/1991 | 04/20/1992 | 9204280011 | <strong>Reactor Trip Due to Switchyard Relay Malfunction</strong><br /><i>Abstract:&nbsp;</i>At 1125 hours on June 9, 1991, with the plant at 100% power in Mode 1, at 2250 psia and 587 degrees Fahrenheit, a reactor and subsequent turbine trip occurred. The trips were due to a phase to ground fault on a 345 kilovolt (KV) system transmission line (external to the plant) in combination with a faulty switchyard pilot wire relay. The pilot wire relay scheme protects the 345KV transmission zone from the main generator output transformer to the switchyard tie breakers (which connect the plant to the distribution system transmission lines). These faults caused station switchyard breakers to open and resulted in Unit 3 load rejection schemes operating to initiate the trips. <br /><br /> The root cause of the trip was a loose restraint tap on the switchyard pilot wire relay. The tap screw was broken and was not completely tightened on the lug of the tap wire. The loose tap resulted in an open circuit and caused the pilot wire relay to actuate incorrectly to the transmission line fault. The cause of the broken tap screw could not be determined. A Feedwater Isolation and Auxiliary Feedwater actuation occurred as expected following a trip. No other Engineered Safety Feature signals were initiated and the event posed no significant hazard to the health and safety of the public. The broken tap screw and affected wiring were repaired, and the pilot wire relay was returned to service.
4231991015 | Millstone 3 | 06/17/1991 | 07/17/1991 | 9107250215 | <strong>Both Supplementary Leak Collection and Release System Train Inoperable due to Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1991, at 1830 hours, at 100% power in Mode 1, at 586 degrees Fahrenheit and 2260 psia, both trains of the Supplemental Leak Collection and Release System (SLCRS) became inoperable when an access cover for the common exhaust duct was removed to investigate and repair the "B" train SLCRS filter bank exhaust fire damper. The damper had failed closed, resulting in a low flow condition for the "B" SLCRS train. The root cause of the event is procedural inadequacy. The procedure consulted for guidance did not contain references to common ducts or special actions required to perform work on the damper. The procedure, which was used previously to perform fire damper surveillances, should have identified the potential implications for entering Technical Specification 3.0.3. <br /><br /> As immediate corrective action, the Shift Supervisor logged into Technical Specification 3.0.3. The work was completed and the SLCRS restored. <br /><br /> As action to prevent recurrence, the applicable damper testing procedure will be reviewed to address common mode inoperability concerns. The subject damper(s) will be tested during planned outages. The appropriate licensed personnel will be briefed on the incident. These actions will be completed by February 28, 1992.
4231991016 | Millstone 3 | 06/24/1991 | 07/24/1991 | 9108050079 | <strong>Inoperable Power Operated Relief Valve Due to Improper Re- installation of a Control Switch</strong><br /><i>Abstract:&nbsp;</i>At 1127 hours on June 24, 1991, with the plant at 100% power in Mode 1, at 2250 psia and 587 degrees Fahrenheit, the control switch for Power Operated Relief Valve (PORV) 3RCS*PCV455A was found to operate incorrectly. The automatic position and closed position were switched. The investigation was initiated because the PORV test light did not indicate as it should during a quarterly slave relay surveillance test. <br /><br /> The root causes for the event were inadequate information detailing the precise switch that required modification per an approved design, and a failure to perform a retest on a control switch from which its wiring block had mistakenly been removed and then reinstalled incorrectly. As a consequence, the PORV was in the closed position when the control handle was placed in the automatic position. Had the correct switch been removed initially, then a proper retest would have been assured for all work performed. Had a retest been performed, the error would have been identified and corrected. Individuals involved were counselled on the need to give complete information to personnel performing design work and the requirements to perform adequate retests. <br /><br /> The lessons learned from this incident will be incorporated into departmental training and, retest guidelines for removal of any component from a panel will be developed and promulgated by October 25, 1991.
4231991017 | Millstone 3 | 07/02/1991 | 07/31/1991 | 9108070195 | <strong>Both Supplementary Leak Collection and Release System Trains Inoperable Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1991, at 1333 hours, at 100% power in Mode 1, 587 degrees Fahrenheit and 2260 psia, both trains of the Supplemental Leak Collection and Release System (SLCRS) were inoperable when an access cover for the common exhaust duct was removed to allow the repair of fire damper 3HVR*DMPF44. Repairing the damper required entering Technical Specification 3.0.3, which requires commencing of plant shutdown if the repair could not be performed within one hour. The damper had failed closed resulting in a low flow condition for the "A" SLCRS train.<br /><br /> The root cause of the event is design deficiency. The cover required removal in order to repair a broken fusible link on 3HVR*DMPF44.<br /><br /> No corrective action is planned. Entering T.S. 3.0.3 was a conscious decision; it was required in order to repair 3HVR*DMPF44.
4231991019 | Millstone 3 | 07/25/1991 | 12/27/1991 | 9201030302 | <strong>Completion of Shutdown per Technical Specification Due to Service Water Mussel Fouling</strong><br /><i>Abstract:&nbsp;</i>At 2009 hours on July 25, 1991, a plant shutdown was completed by plant Technical Specification (TS) 3.7.4 when the plant entered Mode 3 (Hot Standby), at approximately 558 degrees Fahrenheit and 2260 psia. TS 3.7.4 requires 2 operable Service Water (SWP) trains while Modes 1 (Power Operations) through 4 (Hot Shutdown), or after 72 hours, at least be in Hot Standby (Mode 3) within the next 6 hours, and be in Cold Shutdown (Mode 5) within the following 30 hours. A plant shutdown was initiated from 100% power, on July 25, 1991 at 1140 hours. The plant shutdown was initiated after the B Train SWP was declared inoperable and plant management concluded that the inoperable on July 25, 1991, at 1045 hours due to fouling of the B and C Reactor Plant Component Cooling Water (CCP) Heat Exchangers and the B Emergency Diesel Generators Heat Exchangers due to the accumulation of mussel debris.<br /><br /> The root cause is design deficiency. The chlorination did not treat a portion of the piping system. This allowed mussels growth.<br /><br /> The piping was cleaned and flushed prior to being returned to service. The chlorination injection points were moved to the suction of the Service Water Pumps.<br /><br /> A macrofouling operating strategy has been in place to determine when the service water system is at risk.
4231991020 | Millstone 3 | 07/26/1991 | 08/26/1991 | 9109040450 | <strong>Inadvertent Main Steam Isolation Signal Due to Wrong Switch Operation Due to Improper Work Practices</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1991, at 2254 hours, while in Mode 4 (Hot Shutdown), at 233 degrees Fahrenheit and 380 psia, an inadvertent Main Steam Line Isolation (MSLI) - Engineered Safety Features signal was generated. At the time of the event, a Senior Control Room Operator (SCO) was attempting to reset the Feedwater Isolation (FWI) Signal to support ongoing evolutions during the shutdown. Control Room operators immediately verified that all components actuated as required in response to the MSLI. <br /><br /> Based on the plant computer Sequence of Events (SOE) information, MSLI inputs, and discussions with plant personnel, the root cause of the event is concluded to be improper work practices. The SCO, who was in the process of resetting the FWI signal, inadvertently actuated the MSLI vice the FWI Reset (pushbutton) switch. Although different in color, the MSLI actuation switch is the same type switch and is adjacent to the FWI reset switch on Main Control Board No. 5. The switches are properly labeled.<br /><br /> The importance of self-checking as part of routine work practices is being re-emphasized to all operating shift personnel. Either the MSLI or FWI Reset switch will be modified such that each switch must be operated differently. A practical design modification is being reviewed and evaluated for implementation by December 31, 1991.
4231991021 | Millstone 3 | 07/28/1991 | 08/27/1991 | 9109130171 | <strong>Unlocked and Open Manual Containment Isolation Valve Due to Improper Task Verification</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1991, at approximately 1142 hours, with the plant shutdown in Mode 5 (cold shutdown) at 135 degrees Fahrenheit, and 375 psia, a containment isolation valve required by Technical Specifications to be locked closed was found to be open. The subject valve (3CCP*V886) is a two inch, manually operated valve that provides inside containment isolation of a demineralized water line. No immediate action was required with the plant in cold shutdown. <br /><br /> The root cause of this event was improper task verification. After being verified closed on March 31, 1991, the subject valve was opened on April 2, 1991, to support work evolutions in Containment. While the need to close this valve was identified on the Shift Turnover Report, the Shift Supervisor removed the item from the turnover report without verifying that the valve had been closed and locked. The outboard containment isolation valve was verified closed throughout the event.<br /><br /> This event and its associated root cause will be discussed with Operations department personnel in tailboard discussions by October 1, 1991. In addition, this event will be incorporated into Operations department training in order to emphasize the importance of containment isolation valves.
4231991022 | Millstone 3 | 08/20/1991 | 03/24/1992 | 9204020203 | <strong>Failure to Adequately Perform Overlap Testing of the Containment Depressurization Actuation Loops Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1991, at 0800 hours, in Mode 5 (Cold Shutdown), at 95 degrees Fahrenheit and atmospheric pressure, Instrumentation & Controls (I&C) Department personnel reviewing the test methodology during the performance of the containment pressure monthly analog operational check discovered that closure of one of the comparator trip switch auxiliary contacts, which enables transmission of the Containment Depressurization Actuation (CDA) signal, was not being verified. During the investigation of the event, it was determined that the refueling channel calibration procedures for the four CDA signal pressure channels were not overlap testing the contacts as required by the Technical Specifications. The auxiliary contact in each channel which is normally closed to process a signal, is opened during testing to block the CDA signal. No immediate operator action was required since the plant was shutdown. <br /><br /> The root cause of the event is a management deficiency. Prior to initial plant startup, plant management did not ensure that the vendor protection channel test instructions were incorporated into the applicable procedures. The monthly surveillances were modified to verify contact closure. The contact tested satisfactorily in the as-found condition. <br /><br /> A review of I&C procedures versus the vendor operating instructions was performed. No similar concerns were identified.
4231991023 | Millstone 3 | 08/31/1991 | 09/30/1991 | 9110110140 | <strong>Lifting of Pressurizer Safeties Above the Allowed Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1991, Wyle Laboratories notified Northeast Utilities of out of tolerance test results on two previously installed Pressurizer Safety Valves. The safety valves are required by Technical Specifications to be operable with a setting of 2500 psia 1 percent (2475 - 2525 psia) during Modes 1, 2, and 3. Bench testing at Wyle Laboratory revealed one valve lifted at 2545 psia initially, and at 2535 psia on the second and third lift tests. The other safety valve lifted at 2537 psia, 2548 psia, and 2544 psia during its three lift tests. The third safety valve was within the required tolerance. The out of tolerance safety valves had been installed from July 1989 to February 1991. Since the valves were not installed in the plant when the event was discovered, no immediate operator action was required. <br /><br /> The root cause for the safety valves lifting at pressures outside the 1 percent tolerance is setpoint drift. A search of NPRDS indicates the problem of setpoint drift is common to the industry. Analyses are being conducted for support of a Technical Specification change to allow a 3 percent tolerance during retests.
4231991024 | Millstone 3 | 03/18/1987 | 12/31/1991 | 9201090288 | <strong>Triaxial Peak Recording Accelerograph Range Not in Compliance With Technical Specifications Due to Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, at 1045 hours, while shutdown in Mode 5 (Cold Shutdown), at 94 degrees Fahrenheit and atmospheric pressure, Instrumentation & Controls personnel discovered that the 2g range of the "A" Safety Injection Accumulator Tank Triaxial Peak Accelerograph, 3ERS-PAS28, was not in compliance with the 1g range requirement of Technical Specifications (TS) Table 3.3-7, Seismic Monitoring Instrumentation. The incorrect 2g accelerograph was identified during a calibration documentation review as part of the investigation into reliability concerns with respect to the units installed in the plant. The incorrect range accelerograph had been installed since March 18, 1987. No immediate actions were required by plant operators in response to this event. <br /><br /> The root cause of the event is procedural deficiency. The surveillance procedure did not require verification of nameplate data against the TS requirements as part of the installation evolution. <br /><br /> A 1g range accelerograph was installed by September 6, 1991, to comply with the TS. Procedure guidance has been strengthened to require verification of range. Separate stock codes have been provided for the different ranges. The review of the event revealed that a 2g unit is more suitable. A 2g unit was installed on November 7, 1991. A TS change request has been submitted.
4231991025 | Millstone 3 | 09/10/1991 | 01/21/1992 | 9201270341 | <strong>Failure To Verify De-energization of Solid State Protection Input Relays For Cold Overpressure Protection Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>AT 1300 hours on September 10, 1991, while in Mode 5 (cold shutdown), at 94 degrees Fahrenheit and atmospheric pressure, a procedure deficiency in the test for Solid State Protection System input relays resulted in an incomplete surveillance. Instrumentation and Controls (I&C) Department personnel reviewing the test methodology during a surveillance procedure re-write discovered that de-energization of the SSPS input relays for Cold Overpressure Protection (COPS) was not verified during overlap testing for channel calibration. Testing of this relay is required by Plant Technical Specification. No immediate operator action was required since the plant was shutdown. <br /><br /> The root cause of the event is a procedural deficiency. A non-standard circuit design is a contributing factor. The procedure associated with the Solid State Protection System does not verify that the COPS input relay has been de-energized. There is no main control board annunciator to verify that this relay is operational. The SSPS Operation Test Procedures were modified to verify the relay's operability. The relay was satisfactorily tested in the as-found condition. <br /><br /> A review of Solid State Protection System Loops and their associated surveillance procedures has been completed. Three deficiencies were identified and the applicable procedures have been modified.
4231991026 | Millstone 3 | 09/23/1991 | 10/23/1991 | 9111040103 | <strong>Inadvertent Control Building Isolation Due to Procedural Non- compliance</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1991, at 1843 hours, at 0% power in Mode 5 (Cold Shutdown, at 92 degrees Fahrenheit and atmospheric pressure a spurious high radiation Control Building Isolation (CBI) signal was inadvertently actuated by personnel preparing to perform time response testing on the 'A' train Control Building inlet ventilation radiation monitor (3HVC*RE16A). <br /><br /> The root cause of the event is procedural non-compliance. The CBI was generated when test equipment was connected prior to disabling the radiation monitor. Connection of the test equipment was not in accordance with the sequence of steps in the surveillance procedure. <br /><br /> The I&C technicians involved have been counseled on the need to ensure good communications and the importance of performing steps in the sequence identified in procedures. The company's position on procedural compliance has been emphasized to all plant personnel.
4231991027 | Millstone 3 | 10/14/1991 | 11/13/1991 | 9111250114 | <strong>Source Range Reactor Trip Due to Interference Caused by Malfunctioning Welding Machine</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1991, at 1104 hours while in Mode 5 (Cold Shutdown), at 93 degrees Fahrenheit and atmospheric pressure, a reactor trip signal was generated due to high source range channel 32 detector counts. The reactor trip breakers were open previous to this event. <br /><br /> The probable root cause of this event is electro-magnetic interference on the source range signal caused by a malfunctioning welding machine. A welding machine fan caused a short on one leg of the three phase 480 volt non-vital AC power supply. The power cable and source range cable routing has a minimum 15 feet separation. Procedures have been modified to bypass the source range trip when the reactor trip breakers are open and the source range trip is not required, except for planned testing as dictated by plant procedures. Existing procedures prevent welding in containment with the reactor trip breakers closed during a reactor startup.
4231991028 | Millstone 3 | 12/15/1990 | 03/31/1992 | 9204070338 | <strong>Improper Power Range Trip Rate Decay Time Trip Setpoint Due to Improper Work Practices</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1991, at 1100 hours while in Cold Shutdown, at 93 degrees and atmospheric pressure, Instrument and Control technicians discovered that the power range analog channel operational test was performed incorrectly. The test had been performed incorrectly since December 15, 1990. The neutron flux power range high rate trip was not calibrated within the technical specification Trip Setpoint. It was calibrated within the technical specification Allowable Value. There were no immediate operator actions required. The calibrated values were always within the values credited in the safety analysis. Therefore, safety functions were maintained at all times. Additionally, while investigating this event, it was discovered that the power range response time test did not encompass the entire power range circuit. Nor were the power range drawers time response tested after the digital meter modification.<br /><br /> The root causes of these events are improper work practices, technical error, and incomplete written communications. A full test to Westinghouse specification has been performed. The procedures were modified to include a more detailed description of the rate trip decay time calibration and the proper response time test points. The company's position on procedural compliance had been emphasized to all plant personnel and discovery of this event is the result of diligence towards the compliance position.
4231991029 | Millstone 3 | 11/21/1991 | 03/27/1992 | 9204020194 | <strong>Unsealed Fire Stop and Seal Penetration In the Engineered Safety Features Building</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1991, at approximately 1230 hours, with the plant at 0% power in Mode 5 (Cold Shutdown), an unidentified unsealed fire penetration was discovered between the "A" Train Containment Recirculation Spray system (RSS) and Residual Heat Removal (RHR) cubicles located in the Engineered Safety Features (ESF) building. As immediate corrective action, the unidentified unsealed fire penetration was declared inoperable, the associated fire detectors were verified operable and an compensatory fire watch was immediately established in the affected area.<br /><br /> The root cause of the event is incomplete work practices during construction. The subject fire penetration was not identified on construction drawings. The post construction seal verification process did not properly reconcile the wall configuration against the associated Fire Stop and Seal drawing.<br /><br /> On December 21, 1991, the subject penetration was sealed in accordance with design specifications. The penetration was declared operable and the fire watch patrol terminated on December 23, 1991. A 100% inspection of all wall and floor boundary penetrations in the ESF building has been performed.
4231991030 | Millstone 3 | 12/19/1991 | 01/20/1992 | 9201300183 | <strong>Motor Control Center Auxiliary Control Relay Failure Due to Thermal Aging</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1991, at 1300 hours, while shutdown in Mode 5 (Cold Shutdown), an engineering evaluation concluded the failure of three normally energized auxiliary (control) relays for Motor Operated Valves (MOVs) was caused by insulation breakdown and electrical shorting of the relay coil. The failed Telemecanique model J10 relays caused a loss of control power and rendered the MOVs inoperable. The investigation concluded that a very high potential existed for additional relay failures due to the degree of thermal aging observed during inspections. <br /><br /> The root cause of the relay failure is accelerated thermal aging. The J10 Relays had been energized for approximately seven years. The vendor equipment qualification report qualified the relays for the life of the plant (i.e., 40 years). The relay failures were isolated to normally energized relays mounted in a ganged arrangement. All safety related (SR) J10s were inspected and all normally energized J10s in the SR MCCs were replaced. All non-SR J10s were evaluated and those that could possibly challenge the plant were replaced. A surveillance program to detect future problems will be implemented prior to refueling outage No.4.<br /><br /> The accelerated thermal aging of the J10 relays appears to have generic ramifications due to the relays operation, mounting and maintenance being consistent with vendor recommendations.
4231991031 | Millstone 3 | 12/21/1991 | 01/21/1992 | 9201300225 | <strong>Missed Temporary Surveillance on Ventilation Vent Radiation Monitor Due to Administrative Oversight and Inadequate Planning</strong><br /><i>Abstract:&nbsp;</i>At 0745 hours on December 21, 1991, while in mode 5 (cold shutdown), at 96 degrees Fahrenheit and atmospheric pressure, a Technical Specification surveillance was missed. A manual grab sample surveillance is required to be performed at least once every 12 hours whenever the ventilation vent radiation monitor is out of service. The grab sample was not performed for approximately 21 hours. A sample was obtained after the event was discovered. The samples prior to and following the event were below minimum detectable activity. <br /><br /> The root cause of the event is administrate oversight. A review of the daily chemistry log revealed that the twelve hour sampling surveillance had been missed. The immediate corrective action was to obtain a sample. Procedure changes were implemented to provide a more conservative surveillance frequency. The communication of technical data between Chemistry Department shift personnel during shift turnover was also improved.
4241991001 | Vogtle 1, Vogtle 2 | 02/01/1991 | 02/28/1991 | 9103060137 | <strong>Procedure DI Crepancies Result In Inadequate Surveillance Of Seismic Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On 2-1-91, the last Analog Channel Operational Tests (ACOTs) for four triaxial time-history accelerograph seismic monitoring instruments were found to be in error. Also, the last Channel Calibrations for two of the same accelerographs and for one additional accelerograph were found to be in error. These tests were determined to be in error after it was discovered that surveillance procedures for four of the accelerographs contained component tag number discrepancies such that an incorrect recorder (i.e., a recorder associated with another accelerograph) had likely been utilized during the tests. Use of an incorrect recorder would have resulted in improper verification of the response of the accelerograph being tested. <br /><br /> Due to the discrepancies associated with these tests, a limiting condition for operation was entered for both Units. The involved procedures have been revised and the tests have been satisfactorily reperformed except for the ACOT and Channel Calibration for the accelerograph which has a triaxial sensor located on the pressurizer support in Unit 1 Containment. The vertical axis of that accelerograph did not respond properly during the ACOT, indicating that a Containment entry will be required to perform repair. Since the sensor for that accelerograph is considered inaccessible except during Modes 5 and 6, due to environmental conditions in the vicinity of the sensor, repair of that accelerograph will not be completed until a forced outage requiring entry into Mode 5 or the next refueling outage. Therefore, this report will also serve as the Special Report required by Technical Specification 3.3.3.3 since it is expected that this instrument will be inoperable for more than 30 days.
4241991002 | Vogtle 1 | 02/04/1991 | 02/25/1991 | 9103010213 | <strong>Personnel Error Results In Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2-4-91, plant personnel were performing surveillance testing in the Train B Safeguards Test Cabinet (STC). The Balance of Plant (BOP) Operator and a trainee were in the process of testing a slave relay. The trainee placed his hand on the test button, S935, then removed it to re-verify the step in the procedure. He then erroneously put his hand on the button directly below the proper button, placed it in the test position, and manually depressed it at 0036 CST, before either the trainee or the BOP operator recognized the error. This button (S928) energized a different slave relay which caused the steam inlet valve to the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) to open, starting the pump. The Reactor Operator (RO) in the control room observed the alarm, checked that steam generator (SG) water levels were normal, and took action to limit the TDAFWP discharge to the SGs. After determining the reason for the TDAFWP actuation, the RO secured the TDAFWP and restored the Auxiliary Feedwater System to standby readiness at 0119 CST. <br /><br /> The trainee committed a personnel error by inadvertently failing to follow procedure and in not employing self-checking to verify the button number prior to depressing it. Also, the BOP operator did not exercise sufficient supervision of the trainee. The trainee and the BOP operator have been counseled.
4241991003 | Vogtle 1 | 02/22/1991 | 03/15/1991 | 9103210341 | <strong>Relay Testing Results In RHR Valve Actuation</strong><br /><i>Abstract:&nbsp;</i>On 2-22-91, personnel were performing quarterly slave relay surveillance testing. At 0055 CST, a test switch was placed in the test position and momentarily depressed in order to energize a slave relay. Although no actuation was expected, a Residual Heat Removal (RHR) System containment sump suction valve, 1HV-8811A, opened. Personnel "backed out" of the testing procedure by disconnecting a jumper and test equipment, and 1HV-8811A was closed at 0100 CST. To ensure that the procedure was being properly performed, the test was again conducted, but under the direct supervision of the Shift Superintendent. At 0114 CST, 1HV-8811A again opened, and at 0117 CST personnel backed out of the procedure and 1HV-8811A was closed. Further testing was stopped and the investigation continued. <br /><br /> Valve 1HV-8811A would be expected to open only if two slave relays in series were both energized. Resistance measurements indicated that an electrical grounding problem existed with part of the test circuitry. Following troubleshooting of the circuit and using the process of elimination, personnel were able to determine that an electrical ground exists on a stem-mounted limit switch on the RHR Loop 1 hot leg suction isolation valve, 1HV-8701B, and this caused the actuation of 1HV-8811A. However, since 1HV-8701B is inside of the containment bioshield wall, confirmation and removal of the ground condition will await unit entry into a cold shutdown outage.
4241991004 | Vogtle 1 | 03/06/1991 | 04/05/1991 | 9104100068 | <strong>ESF Actuations Result From Ground Condition Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On 3-6-91, personnel were troubleshooting an electrical ground condition in the 125-volt DC switchgear. At 0718 CST, upon authorization from the Unit Shift Supervisor, a Plant Equipment Operator (PEO) opened breaker 1BD1-01, disconnecting battery 1BD1B from the 125-volt DC switchgear. Power to the switchgear was then being supplied by the battery chargers. The PEO noticed that the battery chargers were making variable pitched noises and the indicator light on the bus alternately dimmed and brightened, so he closed the breaker. In the control room, a large number of annunciators were received, including indications that a Containment Ventilation Isolation (CVI) and a Control Room Isolation (CRI) had occurred. The appropriate valves and dampers actuated, as designed, and control room personnel initiated actions to restore the unit to normal operation. <br /><br /> An investigation found that, during testing, battery charger 1BD1CA was experiencing voltage fluctuations which were responsible for the actuations that occurred. The problem was traced to control circuit boards which were replaced with an improved design which eliminates the voltage fluctuations.
4241991005 | Vogtle 1, Vogtle 2 | 07/03/1991 | 08/02/1991 | 9108060389 | <strong>Improper Pressurizer Pressure Transmitter Calibration</strong><br /><i>Abstract:&nbsp;</i>On 7-3-91 at 1618 CDT, conditions requiring entry into Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 occurred when it was discovered that a static head correction of approximately 25-psi had not been applied during the calibration of the pressurizer pressure transmitters for both units. This correction factor affected the high and low pressurizer pressure reactor trip setpoints, the low pressurizer pressure safety injection setpoint, and the initial pressure used in the safety analyses. Consequently, all four channels of pressurizer pressure instrumentation on each unit were declared inoperable, since a condition not provided for in the action requirements of TS 3.3.1 and 3.3.2 existed, and entry into LCO 3.0.3 was required. A Waiver of Compliance was obtained to allow time for transmitter recalibration. All channels for each unit were recalibrated, and TS 3.0.3 was exited at 0348 CDT on 7-4-91. <br /><br /> The root cause of this event was attributed to inadequate procedures. The static head correction factor had not been incorporated into the calibration procedures for these pressure transmitters.
4241991006 | Vogtle 1 | 07/19/1991 | 08/12/1991 | 9108150240 | <strong>Inadvertent LCO 3.0.3 Entry During Recovery From Control Room Isolation</strong><br /><i>Abstract:&nbsp;</i>On 7-19-91 at 0826 CDT, a control room isolation (CRI) occurred due to a circuit board failure for outside air intake radiogas monitor 1RE-12117. The board failure caused a power reset for 1RE-12117, which resulted in the CRI due to the fail-safe logic of the monitor. All equipment responded as expected. After it was verified that the CRI had not resulted from an abnormal radiological condition, 1RE-12117 was blocked and the balance-of-plant (BOP) operator was directed to reset the CRI, stop the essential chillers, and restore normal control room ventilation. Subsequently, the BOP operator inadvertently allowed the control switches for both essential chillers to be placed in stop at the same time. This caused monitor lights on the system status monitor panel to illuminate, and the reactor operator immediately recognized that both essential chillers were inoperable per Technical Specification (TS) 3.7.11. Technical Specification 3.0.3 was momentarily entered while action was taken to return one chiller to service. Restoration from the CRI was completed at 0940 CDT, and 1RE-12117 was restored to service at 2336 CDT after replacement of the circuit board.<br /><br /> The root cause for the TS 3.0.3 entry was cognitive personnel error. Contributing causes included the lack of a caution in the controlling procedure to perform the chiller shutdown one train at a time and the lack of a review of the described sequence of activities prior to initiating the chiller shutdown. Corrective actions include counseling, procedure changes, and increased emphasis on the use of self verification techniques.
4241991007 | Vogtle 1 | 09/25/1991 | 10/22/1991 | 9110290313 | <strong>Fuel Handling Building Isolation During Radiation Monitor Checks</strong><br /><i>Abstract:&nbsp;</i>On 9-25-91, a technician was performing radiation monitor checks at the process and effluent radiation monitoring system's (PERMS) safety related display console (SRDC) in the control room. Because the feature of the console that automatically transmits history from radiation monitors to the PERMS minicomputers was not operating properly, the technician was required to transmit this data manually. He inserted the key in the console panel, selected monitor ARE-2532B, and began to "transmit history" from that monitor at 0932 EDT. Immediately, the "high" alarm indicator lit. <br /><br /> The unit shift supervisor (USS) noted that a fuel handling building (FHB) isolation had occurred and advised the technician to stop performing his tasks. The support shift supervisor (SSS) determined that no abnormal, high radiation condition existed by checking other monitors and by means of a survey conducted by Health Physics personnel. At 1259 EDT, the FHB normal ventilation units were returned to service and the FHB post-accident ventilation units were secured. <br /><br /> The direct cause of this event is unknown. Personnel attempted to recreate the FHB isolation by repeating the steps performed by the technician but were unsuccessful. An analysis could not determine a means by which these steps could initiate a FHB isolation. Steps are being taken to block the engineered safety features (ESF) signal when work is performed at the SRDC and to eliminate the need for manually transmitting history.
4241991008 | Vogtle 1 | 10/23/1991 | 11/21/1991 | 9111260163 | <strong>Transformer Failure Leads To ESF Actuation And Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On 10-23-91 at 1110 EDT, a transformer was found to be smoking heavily. The involved transformer powers radiation monitor 1RE-2565 and other radiation monitors. A containment ventilation isolation (CVI) signal is initiated from 1RE-2565. Supervision in the control room elected to deenenergize the transformer, in order to stop the smoke propagation, with the knowledge that a CVI actuation would occur. At 1125 EDT, the transformer was deenergized and a CVI actuation occurred as expected. <br /><br /> On 10-24-91, personnel were preparing to test ESF systems. As a part of this testing, the ESF actuation system (ESFAS) sequencer sheds the loads from some buses. One of these buses powers the sample air pump for plant vent radiation monitor 1RE-12444. The Technical Specifications (TS) require at least one plant vent monitor to be in service, but the redundant monitor had been removed from service by the transformer failure. As a result, plant vent monitoring ceased when the ESF testing was initiated. <br /><br /> The primary cause of the CVI and a contributing cause for the TS violation was the failure of the transformer. A task force is investigating the failure.
4241991009 | Vogtle 1 | 10/26/1991 | 11/22/1991 | 9112030272 | <strong>Loss Of Residual Heat Removal Pump Flow During Draindown Or Reactor Cavity</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1991, Unit 1 was in a refueling outage. Core reload was complete but the reactor head had not been installed and the reactor cavity was flooded. At 1833 EDT, the 1A residual heat removal (RHR) pump was started to lower the cavity to just below the reactor flange to allow reinstallation of the head. During the last segment of the draindown evolution, indications of vortexing and air entrainment were observed for the 1B RHR pump which was operating at a higher flowrate in the shutdown cooling mode. Operators took action to reduce the flow of the 1B pump and to stop the draindown via the 1A pump. However, the discharge pressure for the 1B pump remained low. A subsequent review of computer data indicated the 1B pump was operating at or near no-flow conditions.<br /><br /> The 1A pump was realigned to raise the reactor coolant system (RCS) level. Reduced shutdown cooling, via the 1B pump, was reestablished within 16 minutes from the time the 1B pump started showing indication of vortexing, and full shutdown cooling was reestablished within 50 minutes. <br /><br /> The event was caused by inaccurate RCS level indication due to an inadequate pressurizer vent path. A pressurizer safety valve had been removed, and it was thought that an adequate vent path existed; however, a high efficiency particulate air (HEPA) filter had been attached (via a flexible duct) to the flange opening for the safety valve and obstructed the vent, causing a vacuum to develop during the draindown resulting in false high RCS level indication. <br /><br /> Corrective actions include revising procedures to ensure verification of vent paths for all evolutions and tightening controls for HEPA filter installations.
4241991010 | Vogtle 1 | 11/06/1991 | 12/05/1991 | 9112100243 | <strong>Personnel Error Leads To Inadequate Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1991, two valves (11208U4482 and 11208U4169) in the boration flowpath from the boric acid storage tank (BAST) to the reactor coolant system (RCS) were tagged shut to isolate another valve so that work could be performed. <br /><br /> On November 5, 1991, personnel verified that two boration flowpaths to the RCS existed per procedure. However, valve position for manual valves such as 11208U4482 and 11208U4169, which are normally locked open, is not verified by this procedure. Technical Specification (TS) 3.1.2.1 requires one flowpath to be available during shutdown. The flowpath containing the aforementioned manual valves originated from the BAST and continued through the positive displacement pump (PDP) to the RCS. Therefore, this flowpath was not available. Another flowpath originated from the refueling water storage tank (RWST) and continued through the Train B centrifugal charging pump (CCP) to the RCS. <br /><br /> On November 6, 1991, at 0253 EST, as part of planned maintenance the Train B CCP was taken out of service, removing the only remaining and demonstrated operable boron injection flowpath from the RWST to the RCS. The Train A CCP had previously been taken out of service for corrective maintenance. <br /><br /> The cause of this event was a cognitive personnel error on the part of the unit shift supervisor (USS) and reactor operator (RO) on duty when the adequacy of flowpaths was verified. The USS and RO have been counseled.
4241991011 | Vogtle 1 | 11/18/1991 | 12/16/1991 | 9112260326 | <strong>Auxiliary Feedwater Actuation While Preparing For Testing</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1991, personnel were preparing to test the turbine driven auxiliary feedwater (AFW) pump flow rate. Although steam generator (SG) water levels are normally maintained at 60 to 70 percent of the narrow range band, this procedure requires levels to be maintained in the lower end of the narrow range band. <br /><br /> At approximately 0158 EST, the steam generator water level control operator stopped feedwater flow for AFW valve stroke testing. When the operator next checked SG water level, he found that the SG 1 and SG 4 water levels were near 40 percent of the narrow range band. He immediately reinitiated feedwater flow to SG 1. Moments later at 0201 EST, an automatic AFW actuation occurred as SG 1 reached the 37.8-percent, low-low level setpoint for initiating an AFW actuation. The standby motor driven AFW pump started, and valves opened to provide full AFW flow as designed. Steam generator water levels were restored, and normal operations were resumed. <br /><br /> The direct cause of this event was a cognitive personnel error by the operator in not maintaining the SG water levels in accordance with procedure. The operator has been counseled regarding the importance of attention to duty and the need to maintain control over work activities in his area.
4241991012 | Vogtle 1 | 11/18/1991 | 12/16/1991 | 9112260330 | <strong>Manual Actuation Of Reactor Protection System During Rod Drop Time Testing</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1991, Unit 1 was in Mode 3 (Hot Standby). The reactor trip breakers were closed, and withdrawal of shutdown bank (SDB) "A" was in progress per procedure 88006-C, "Rod Drop Time Measurement With Rod Drop Test Cart." After withdrawing SDB "A" to 53 steps, it was noticed that the digital rod position indication (DRPI) for SDB "A" rod D-2 had stopped moving. Shutdown bank "A" was further withdrawn, and at group step counter readings of 59 and 58, DRPI urgent alarms were received and the rod at bottom LED illuminated for rod D-2. The operators thought they had also observed indication of rod D-2 dropping into the core. The abnormal operating procedure (AOP) for rod control system malfunctions was entered, and at 1010 EST, a reactor trip was conservatively initiated as discussed in evolution prebriefings and as directed by the AOP. It was verified that the reactor trip breakers opened properly, and the SDB "A" rods fully inserted into the core.<br /><br /> Subsequent troubleshooting indicated rod D-2 did not actually drop into the core prior to initiation of the reactor trip. Rather, a DRPI Data A problem was indicated to exist. While the exact cause of this problem was not determined, the operability of the DRPI system per Technical Specification requirements was demonstrated and a reactor startup was successfully completed on November 19, 1991. Further troubleshooting to determine the cause of the problem will be completed during a forced outage or the next refueling outage.
4241991013 | Vogtle 1 | 11/25/1991 | 12/20/1991 | 9112300015 | <strong>Opening Hydrogen Monitor Isolation Valves Results In Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1991, during performance of an analog channel operational test (ACOT) for a containment hydrogen monitor, the analyzer pump for the monitor began to unexpectedly cycle on and off. Since the analyzer pump is designed to shut down on flow blockage, a cause for the problem was thought to be a blockage in the sample flowpath. The sample flowpath for the ACOT is established by uncapping and opening test valves located in the sample supply and return lines to the analyzer. This test method originated due to an NRC identified concern that the sample line isolation valves which isolate the hydrogen analyzer from the containment atmosphere should not be opened during Modes 1, 2, 3, or 4 (Reference: NRC Violation 50-424, 425/1990-19-02). To troubleshoot the possible flow blockage, Instrumentation and Controls personnel requested that the sample line isolation valves be opened and an attempt be made to place the monitor in service. The Unit 1 unit shift supervisor (USS) and the shift superintendent reviewed the implications of this request. They had previously reviewed but did not recall both the NRC violation and a Standing Order which directly stated that opening both an inside and outside containment hydrogen monitor isolation valve in the same path during Modes 1, 2, 3, or 4 would result in Technical Specification (TS) 3.0.3 entry. This resulted in the opening of the isolation valves for approximately 4 minutes while an attempt was made to place the monitor in service. Subsequently, the Unit 2 USS pointed out the Standing Order, and it was recognized that a TS 3.0.3 entry had occurred.<br /><br /> The root cause of the event was personnel error. The Unit 1 USS and the shift superintendent were counseled for failing to recognize the TS 3.0.3 entry.
4241991014 | Vogtle 1, Vogtle 2 | 11/26/1991 | 12/20/1991 | 9112270314 | <strong>Fuel Handling Building Isolation From Radiation Monitor Signal</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1991 at 1016 EST, a fuel handling building (FHB) isolation occurred from radiation monitors ARE-2532A and ARE-2532B. Control room personnel verified that equipment actuated properly. Chemistry personnel reported that the ARE-2532A and ARE-2532B data processing module (DPM) had undergone a power reset and that no abnormal radiation condition existed. The ARE-2532A and ARE-2532B engineered safety feature (ESF) actuation signal was blocked and normal FHB ventilation was restored at 1035 EST. <br /><br /> The direct cause of this event was a loss of power to the radiation monitors which caused them to fail to the "safe" condition, resulting in a FHB isolation. The root cause of the loss of power is unknown. Following testing and troubleshooting, the radiation monitors were returned to service.
4241991015 | Vogtle 1 | 09/05/1991 | 05/13/1992 | 9205190325 | <strong>Valve Manufacturing Defect Leads To Containment Isolation Valve Failing Open</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1991, a local leak rate test (LLRT) of a containment isolation valve (CIV), service air system check valve 12401U4034, was conducted. Leakage limits were exceeded, the Technical Specification (TS) limiting condition for operation (LCO) was entered, and a deficiency card (DC) was initiated. On September 5, 1991, an investigation into the cause of the leakage found the disk of this check valve stuck fully open. A casting mark on the valve hinge engaged the hinge support when the disk was in the full open position and would not allow the disk to return to the closed position. <br /><br /> On December 6, 1991, a final review of the DC for adequacy of investigation and corrective actions identified that 12401U4034 may have been stuck in the full open position for a period of time longer than that allowed by the TS LCO action statement requirements. However, since firm evidence for the time that the valve became stuck open does not exist, this report is being submitted as a LER revision for 10 CFR 21 reporting only and is not reportable per 10 CFR 50.73.<br /><br /> The cause of this event was the manufacturer's casting mark on the valve hinge, which caused the disk to bind and remain in the open position. The casting mark was removed, LLRT testing was completed satisfactorily, and 12401U4034 was returned to service.
4241991016 | Vogtle 1 | 12/23/1991 | 01/21/1992 | 9201280074 | <strong>Failure To Complete Technical Specification Required Action For Battery Cell Low Voltage</strong><br /><i>Abstract:&nbsp;</i>On 12-26-91, a maintenance supervisor and plant engineering personnel were reviewing recorded data for a Class 1E battery cell which was being single-cell charged when it was noticed that the cell had displayed abnormal behavior. Per the recorded data, after the cell was placed on single-cell charge on 12-23-91, the cell float voltage had dropped below the Technical Specification (TS) allowable value for approximately 22 hours. Per TS requirements, if float voltage for a connected cell is found to be below the allowable value, then the battery must be declared inoperable. Subsequently, engineering review determined that a temporary internal short had probably existed in the cell and, consequently, an inoperable condition should have been considered to exist.<br /><br /> The root cause of the event was procedure inadequacy. The procedure, which provides instructions for single-cell charging, did not provide a precaution that TS requirements would apply for low cell voltage readings obtained while single-cell charging. In addition to revising the procedure, corrective action has been taken to jumper out the cell due to further unacceptable voltage readings. A new cell is expected to be installed by 2-15-92.
4251991001 | Vogtle 2 | 01/02/1991 | 02/04/1991 | 9102080135 | <strong>Personnel Error Results In Missed Special Condition Surveillance</strong><br /><i>Abstract:&nbsp;</i>During the period between 1518 CST on 1-2-91 and 0743 CST on 1-7-91, the rod position deviation monitor alarm was inoperable and the special condition surveillance requirement of Technical Specification (TS) 4.1.3.2, which is applicable when the monitor is inoperable, was not implemented. The TS requires that the Demand Position Indication System and the Digital Rod Position Indication System be compared at least once per 4 hours when the rod position deviation alarm is inoperable. <br /><br /> The cause of this event was a cognitive personnel error on the part of the Balance of Plant (BOP) operator. The BOP operator failed to follow procedure on 1-2-91 when he improperly entered a computer point value. Contributing to this event was the failure of a relay output circuit card in the interface between the DRPI and the Proteus computer. <br /><br /> The failed relay output circuit card has been replaced and the BOP operator has been counseled regarding the importance of procedural compliance.
4251991002 | Vogtle 2 | 01/09/1991 | 01/31/1991 | 9102050183 | <strong>Detector Failure Results In Containment Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>On 1-9-91, at 1202 CST, an intermediate level alert alarm was received for containment area radiation monitor 2RE-0003. Investigation and comparison with a redundant monitor, 2RE-0002, determined that the alarm was due to a spurious signal spike. At 1255 CST, a high radiation level alarm and a Containment Ventilation Isolation (CVI) were received from 2RE-0003. All equipment responded as designed to isolate containment ventilation and to maintain negative pressure for the piping penetration area. Investigation verified that a failure of 2RE-0003 had occurred. Technical Specifications 3.3.3.1 and 3.3.2 action requirements were entered because less than the minimum required number of radiation monitoring channels which initiate a CVI were operable. After lifting the actuation leads from 2RE-0003, the CVI signal was reset at 1712 CST and normal system alignments were reestablished. <br /><br /> Troubleshooting determined that the detector assembly for 2RE-0003 had failed. The root cause has not been determined. A spare detector assembly is not currently available. Therefore, a containment entry will not be made to complete repairs until after a spare is obtained. Any defective parts will be returned to Westinghouse for analysis.
4251991003 | Vogtle 2 | 01/29/1991 | 06/25/1992 | 9206300067 | <strong>Diesel Generator Nonvalid Failures Due To Negative Reactive Power When Tying To The Grid</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1991, diesel generators (DGs) 2A and 2B experienced what are now classified as nonvalid failures during testing, due to indicated reactive power reaching a value of negative 6000 kVARs as the DGs were loaded to the grid. Initially, investigation was unable to determine a cause for these failures and further testing was unable to repeat the failure for either DG. <br /><br /> Following a similar DG failure on February 5, 1992, extensive research and testing was performed. A review of the test data concluded that, due to the sizing of the power potential transformers and the current transformers, there exists a small area within the leading KVAR range of the generator capability curve in which the voltage regulator will not function. Because this condition can only occur when the generator is operating in parallel with the grid, it does not affect DG response to emergency conditions. Procedural controls have been established to limit operation of the generator in this range of the curve while testing is being performed.
4251991004 | Vogtle 2 | 02/13/1991 | 03/12/1991 | 9103200218 | <strong>Containment Ventilation Isolation Occurs During Lifting Of Detector Actuation Leads</strong><br /><i>Abstract:&nbsp;</i>On 2-13-91, a technician was assigned to lift the actuation leads for the containment ventilation radiation monitor 2RE-2565A, B, and C to allow the monitor to be placed in bypass. While performing this task, the technician inadvertently grounded one of the actuation leads and a Train B Containment Ventilation Isolation (CVI) occurred at 1431 CST. The Train A CVI equipment did not actuate; however, investigation later determined that this was according to design. After completion of testing to verify that both Train A and Train B CVI signals would be initiated from 2RE-2565A, B, and C when appropriate, the CVI signal was reset at 2040 CST and normal system alignments were reestablished. <br /><br /> The root cause of this event was the lack of an original design feature for 2RE-2565A, B, and C which would allow the CVI actuation signals to be blocked without lifting leads. The need for such a blocking feature had been identified by prior CVI events and a modification had been initiated, but not yet completed, to install block switches for 2RE-2565A, B, and C. Due to this event, the modification was completed prior to restoring 2RE-2565A, B, and C to service on 2-18-91.
4251991005 | Vogtle 2 | 02/18/1991 | 03/06/1991 | 9103120031 | <strong>Main Feedpump Slowdown Leads To Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 2-18-91 at 0747 CST, the control room operators observed loss of feedwater and steam flow/feed flow mismatch annunciators, determined that a slowdown of Main Feedpump (MFP) "A" had occurred, and saw that steam generator (SG) water levels were dropping. The reactor control rods were inserted, and the turbine load was reduced. The operators attempted to increase MFP "B" speed in order to maintain the SG water levels. However, MFP "B" speed was locked-in due to the signal memory function and did not increase. An automatic reactor trip occurred due to SG 1 reaching its low-low water level trip setpoint. The Auxiliary Feedwater (AFW) System actuated, and the operators took action to throttle flow to the SGs in order to stabilize SG water levels and maintain a normal Reactor Coolant System temperature. Both MFPs were tripped, and at 0839 CST the turbine-driven AFW pump was secured. The motor-driven AFW pumps remained in service to supply normal feedwater needs with the plant in Mode 3. <br /><br /> An investigation found a faulty component on a circuit board in the MFP "A" speed control which allowed pump speed to decrease to its minimum value after an apparent power fluctuation. The circuit board with the faulty component was replaced and preventive maintenance is being instituted.
4251991006 | Vogtle 2 | 02/23/1991 | 03/21/1991 | 9103270208 | <strong>Failure Of Temperature Channel Circuit Card During NI Surveillance Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 2-23-91, with the overpower delta-T (OPDT) and overtemperature delta-T (OTDT) bistables for reactor protection channel IV tripped for surveillance testing purposes, Reactor Coolant Loop 1 narrow range average temperature (T-avg) failed low. Personnel performing the surveillance on protection channel IV were promptly directed to back out of their procedure and restore the channel to service. However, before any action could be taken, the OPDT and OTDT bistables for protection channel I tripped, and a reactor trip occurred at 1138 CST on OTDT since the required 2 out of 4 logic was satisfied. With the exception of a steam-dump-to-condenser valve that failed open, no equipment malfunctions or abnormalities occurred following the reactor trip and by 1158 CST the plant had been stabilized in Hot Standby.<br /><br /> A subsequent review of computer data indicated that after failing low, Loop 1 T-avg returned to near normal immediately prior to the reactor trip. Utilizing the plant simulator, it was demonstrated that if the signal from the Loop 1 T-hot narrow range temperature instrument failed low slowly and then returned to normal, the channel I OPDT and OTDT bistables would trip due to the apparent sudden increase in temperature. Troubleshooting of the Loop 1 T-hot instrument channel found that a power supply on a Westinghouse 7300 Series RTD Amplifier (NRA) card had failed. <br /><br /> The NRA card was replaced and the channel IV surveillance was completed before returning the reactor to power.
4251991007 | Vogtle 2 | 05/07/1991 | 06/04/1991 | 9106100516 | <strong>Generator Loss Of Field Results In Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 5-7-91 at 0948 CDT, several annunciators and alarms were received on the electrical auxiliary board in the Unit 2 control room. Immediately after receipt of the alarms, an automatic reactor trip occurred due to a trip of the Unit 2 turbine. Except for the tripping of non-1E breakers which supply turbine building lighting and the malfunction of a steam-dump-to-condenser valve, no other equipment malfunctions or abnormalities occurred following the reactor trip, and by 1010 CDT the plant was stabilized in Hot Standby. <br /><br /> A post-trip review of computer data, the plant fault recorder, and the protection relay panel revealed that a generator loss of field occurred just prior to the event, causing a generator trip which then caused the turbine/reactor trip. The root cause for the generator loss of field is indeterminate. Extensive troubleshooting under the direction of a General Electric (GE) representative was performed on 5-8-91 with the generator shut down and on 5-9-91 with the generator at rated speed and voltage. No problem with the generator field excitation circuitry was found, and at 1941 CDT on 5-9-91 the generator was tied to the grid. Continuous monitoring via installed recorders was then performed with the generator online. After no abnormality was detected that might have caused the event, the recorders were removed on 5-19-91.<br /><br /> Subsequently, one recorder has been reinstalled to provide further monitoring of four points.
4251991008 | Vogtle 2, Vogtle 1 | 06/25/1991 | 07/23/1991 | 9107300102 | <strong>LCO 3.0.3 Entry Due To Momentary Closure Of Centrifugal Charging Pump Discharge Valve</strong><br /><i>Abstract:&nbsp;</i>On 6-25-91 at 0143 CDT, the Train B safety injection pump (SIP) was tagged out for maintenance. At 0218 CDT, a quarterly inservice test was initiated for the Train B centrifugal charging pump (CCP). In accordance with the test procedure, the discharge valve for the Train A CCP was closed. Upon observing the closure of the Train A valve, the Shift Supervisor realized that the operability of both emergency core cooling system (ECCS) subsystems was impacted by the B Train test. Since an inoperable condition for both ECCS subsystems is not addressed by the action requirements of Technical Specification (TS) 3.5.2, TS 3.0.3 was momentarily entered while action was taken to reopen the Train A valve. A subsequent review of historical records found that, on at least one other occasion, performance of the test procedure had similarly resulted in an inoperable condition for both ECCS subsystems. <br /><br /> The cause of these events was procedure inadequacy. With a few exceptions, test procedures are written so that performance of the procedure on one train will not affect the operability of the redundant train. While this test procedure contained a step which made it an exception, no specific caution was provided to ensure operator awareness of the effect of the step. Also, additional review has determined that the test methodology can be changed so that the test will not affect the operability of the opposite train.<br /><br /> Corrective action will be taken to change the test procedure methodology.
4251991009 | Vogtle 2 | 08/13/1991 | 06/04/1992 | 9206090289 | <strong>Safety Injection Pump Start During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 8-13-91, personnel were performing Technical Specification (TS) surveillance testing of slave relay K610 from the solid state protection system (SSPS) test cabinet in the control room. The appropriate leads had been lifted to prevent equipment actuation while relay K610 was energized. Following testing, reset switch S-921 was taken to the "Reset" position to deenergize relay K610, and at 0124 CDT, the previously disconnected leads were reconnected. At that moment, personnel in the control room observed the starting of a group of Train B equipment, including safety injection pump (SIP) B. The SIP did not inject water into the reactor coolant system (RCS) because the normal RCS pressure, which existed at the time, was higher than the shutoff head of the SIP. Operators again took switch S-921 to the reset position and visually verified that the K610 relay deenergized. The equipment which had actuated was returned to standby status at approximately 0200 CDT.<br /><br /> The cause of this event was the intermittent failure of reset switch S-921 which will be replaced during the Fall 1993 refueling outage.
4251991010 | Vogtle 2 | 09/23/1991 | 10/22/1991 | 9110290339 | <strong>Inadequate Diesel Fuel Analysis Leads To Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On 8-13-91, diesel fuel oil was delivered and offloaded into the diesel generator (DG) 2A and 2B fuel oil storage tanks. A sample of the newly delivered fuel oil was obtained and sent to an offsite laboratory for analysis in accordance with Technical Specification (TS) 4.8.1.1.2.d.2 which requires, in part, verification within 30 days that the sample meets the requirements of ASTM D975-81. On 9-11-91, the testing laboratory contacted a site foreman and relayed the testing results via telephone, indicating that ASTM D975-81 requirements were satisfied, thereby allowing the foreman to note that the 30-day surveillance requirement had been fulfilled. <br /><br /> On 9-23-91 at 1730 EDT, the foreman received a written test report from the testing laboratory and noticed that the percentage of ash content was not shown. An investigation was immediately begun to determine if the ash sample results were not included due to administrative error or if the testing lab actually failed to analyze for ash content. On 9-24-91 at approximately 1430 EDT, site personnel contacted the testing laboratory and were advised that the sample had since been tested and was found to be within the ASTM D975-81 limit for ash content. <br /><br /> The causes of this event were personnel error and miscommunications which have been addressed by the supervision of the personnel involved.
4251991011 | Vogtle 2 | 10/28/1991 | 11/21/1991 | 9111260232 | <strong>Radiation Monitor Failure Leads To Containment Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>On 10-28-91 at 0004 EST, control room operators observed the annunciation of high and intermediate radiation alarms followed by a containment ventilation isolation (CVI). These alarms and the CVI were initiated by containment area radiation monitor 2RE-0003. All valves and dampers actuated as designed and control room operators verified that redundant radiation monitors exhibited normal readings. Chemistry department personnel verified that 2RE-0003 had experienced a failure and 2RE-0003 was placed in block. At 0017 EST, the CVI signal was reset. <br /><br /> Troubleshooting found that the 2RE-0003 detector tube assembly had failed and caused the event. The detector tube assembly was replaced, and the monitor was restored to service.
4251991012 | Vogtle 2, Vogtle 1 | 12/11/1991 | 02/13/1992 | 9202190046 | <strong>RCP Thermal Barrier Isolation Valves Declared Inoperable Due To Torque Switch Settings</strong><br /><i>Abstract:&nbsp;</i>On 12-11-91, during a review of minimum required thrust values against field measured thrust values for safety-related motor-operated valves, offsite engineering personnel determined that the as-left torque switch settings for valves 2HV-19051, 2HV-19053, 2HV-19055, and 2HV-19057 were inadequate to ensure the design function of these valves. These valves are designed to provide a redundant isolation function to valve 2HV-2041 for isolating a postulated reactor coolant pump thermal barrier tube rupture. The site was notified and Technical Specification (TS) action requirements pertaining to the operability of the thermal barrier isolation function were entered while corrective actions were taken. This included increasing the torque switch settings for 2HV-19051, 2HV-19053, and 2HV-19055 and installing a jumper to temporarily bypass the close torque switch for 2HV-19057. On 1-17-92, the as-left torque switch settings for valves 2HV-2041 and 1HV-2041 were also determined to be inadequate. Due to this discovery, the NRC was notified pursuant to 10 CFR 50.72(b)(2)(iii), and the TS action requirements were again entered while action was taken to increase the torque switch settings for 2HV-2041 and 1HV-2041. <br /><br /> The event was caused by inadequate original vendor specified information. Originally, the valve vendor (Anchor/Darling Valve Company) supplied recommended torque switch settings but did not supply minimum thrust requirements. Therefore, while the close torque switches were set at nominal specified values and valve diagnostic testing was performed for the Unit 2 valves during Unit 2 preoperational testing, the discovery that the specified torque switch settings were inadequate did not occur until the present review of field data. Followup corrective actions will be completed during the next refueling outages.
4401991001 | Perry | 01/01/1991 | 01/31/1991 | 9102050164 | <strong>RWCU Isolation on High Delta Flow While Attempting to Shift Pumps</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1991 at 1935, while attempting to shift Reactor Water Cleanup (RWCU) system flow from the B pump to the A pump, a Delta-Flow High RWCU isolation occurred. At the time of discovery, the Plant was in Operational Condition 2 (Startup). Reactor Pressure Vessel (RPV) temperature was 170 degrees Fahrenheit and reactor pressure was atmospheric. The Operator started the A RWCU pump for a 24 hour run and secured the B RWCU pump. RWCU flow dropped off considerably and the B RWCU pump was restarted approximately 3 minutes later. The A RWCU pump was then secured. A Delta-Flow High RWCU isolation occurred within 1 minute because of flow imbalances within the RWCU system resulting from this evolution. Upon investigation, it was discovered that the A RWCU pump discharge valve was closed. RWCU flow was then properly re-established in accordance with System Operating Instruction SOI-G33, "Reactor Water Cleanup System", using the B RWCU pump. <br /><br /> The root cause of this event was personnel error, inattention to detail, by the Control Room Operator. The operator started the A RWCU pump without first verifying that the pump discharge valve had been opened. <br /><br /> The corrective actions taken for this event include counseling the operator involved and discussing the event during Operator requalification training.
4401991002 | Perry | 01/01/1991 | 01/31/1991 | 9102050167 | <strong>Unexpected Turbine Stop Valve Closure During Performance of a Surveillance Results in a Reactor Protection System Actuation.</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1991, at 2050, while performing activities for Turbine Stop Valve and Reactor Protection System (RPS) testing, an inadvertent Turbine Stop Valve (TSV) closure signal resulted in a full scram signal being generated. At the time of the event the plant was in Operational Condition 2 with all of the control rods inserted. <br /><br /> The root cause of this event is indeterminate. A possible electrical malfunction was investigated by troubleshooting the speed control logic and troubleshooting efforts did not identify any equipment problems. The two surveillances were reviewed for possible interaction effects. Although SVI-N31-T1151, "Main Turbine Valve Exercise Test", could have provided more detail for adjusting control valve position, the operator's chosen methods would not have initiated the RPS actuation and interaction between the surveillances was not found. Control room and I&C personnel were interviewed and the exact actions performed prior to the scram signal were reviewed. Although none of the individuals could distinctly remember depressing or inadvertently touching the CLOSE VALVES button, this action would have caused the TSV to close and a scram to occur. The CLOSE VALVES control button is located in close proximity to the LOAD SET button and was observed to be lit following the scram.<br /><br /> To prevent recurrence, SVI-N31-T1151 is being revised to clarify the actions needed to meet all of the prerequisites. Additionally, this event will be discussed during licensed operator requalification training.
4401991003 | Perry | 01/06/1991 | 02/04/1991 | 9102080015 | <strong>Performance of Inadequate Procedure Results in Main Steam Line Drain Isolations</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1991 at 1311, the performance of an inadequate procedure resulted in Main Steam Line Drain Isolations. Control Room Operators were in the process of restoring Feedwater Heater 6A to service in accordance with system Operating Instruction (SOI-N27) "Feedwater System (Unit One)." At 1257, the Control Room Operators bypassed the trip functions for all four Main Steam Line (MSL) Radiation Monitors and, in addition, placed the NSSSS MSL Drain Isolation Logic Test switches to the "test" position. The resulting logic configuration resulted in the generation of isolation signals to the inboard and outboard MSL Drain Isolation Valves. <br /><br /> The root cause of this event is procedure deficiency. SOI-N27 instructs operators to perform applicable steps of appropriate Surveillance Instructions to bypass the MSL Radiation Monitors. These Surveillance Instructions are used to meet Technical Specification Surveillance requirements and do contain steps that in effect "bypass" MSL Radiation Monitor trip functions; however, these steps are not readily discernible or placed in a specific section separated from other non-applicable steps. As a result, the Control Room Personnel had to determine, without procedural guidance, the "applicable steps" to be performed.<br /><br /> To prevent recurrence, SOI-N27 is being revised to include or reference the appropriate steps to bypass the MSL Radiation Monitors. This event has been discussed with the operators involved and they are aware of the personnel errors that occurred. Additionally, as part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991004 | Perry | 01/20/1991 | 02/15/1991 | 9102190125 | <strong>Blown Fuse Results in Loss of Reactor Water Level-High Trip Relays Resulting in Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1991 at 0650, while performing a periodic test on the reactor-feedpump turbine stop valves IV! a fuse was blown resulting in a loss of valve position indication. Further investigation revealed that the blown fuse also supplied power to the Reactor Water Level-High (Level 8) trip relays RLY! for the main turbine TRB!, the motor driven feedpump P! and the A reactor feedpump turbine (RFPT) TRB!. This blown fuse resulted in all three Reactor Water Level-High (Level 8) channels being inoperable, which is not addressed by Technical Specification 3.3.9 and requires entry into Technical Specification 3.0.3. <br /><br /> Although no particular design criteria was violated, the root cause of this event is attributed to design inadequacy. A single fuse protected not only the trip relay circuitry associated with the main turbine, the motor driven feedpump and the A RFPT, but it also protected much additional non-safety related indication and control circuitry. An apparent voltage spike in this additional circuitry resulted in shorting out a control panel indicating lamp which caused the fuse to blow and resulted in the loss of the three trip relays.<br /><br /> The corrective actions taken for this event included changing the circuitry such that a single fuse now protects only the circuitry associated with these trip relays. A separate fuse protects the additional indication and control circuitry. This modification has been completed. An evaluation of Technical Specifications was performed to verify that this type of fusing arrangement does not exist in any other multiple channel Technical Specification related trip circuitry.
4401991005 | Perry | 01/29/1991 | 02/22/1991 | 9102280004 | <strong>Misapplication Of Technical Specification Action During Rod Control And Information System Maintenance Results In Technical Specification Violation.</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1991, at 2305, maintenance activities on the Rod Control and Information System (RC&IS) resulted in a condition prohibited by Technical Specification 3.1.3.3. Control Room Operators were made aware that the replacement of power supplies would result in the loss of scram accumulator fault indication and also the loss of RC&IS interface capabilities at the main control panel. Due to a misapplication of Technical Specification 3.1.3.3.a.2, Control Room Operators believed the plant was in a 12-hour shutdown LCO action statement; however, the on-coming shift, after reviewing the situation, determined that the Technical Specification 3.1.3.3.a.2 action could not be met and that the plant was in Technical Specification LCO 3.0.3. Actions were initiated in accordance with Technical Specification 3.0.3 to shut down the plant and then RC&IS was returned to service. Operators declared the scram accumulators and RC&IS operable and Technical Specification 3.0.3 was exited on January 30, 1991, at 0200.<br /><br /> The cause of this event was personnel error, inattention to detail. The Unit Supervisor misinterpreted the Technical Specifications and incorrectly applied the twelve-hour shutdown action requirement. <br /><br /> To prevent recurrence, this event has been discussed in detail with the Control Room Operators involved and they are aware of the error made in applying Technical Specifications. Investigation into potential changes to the Technical Specification 3.1.3.3 are also in progress. Additionally, as part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991006 | Perry | 02/02/1991 | 03/01/1991 | 9103050416 | <strong>High Differential Flow Reactor Water Cleanup Isolation While Securing a Filter from Service</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1991, at 1230, Reactor Water Cleanup (RWCU) Inboard Isolation Valves closed on a RWCU Delta Flow High signal during removal of a RWCU filter from service.<br /><br /> The root cause of this event is personnel error, inadequate knowledge. The System Operating Instruction specified that the operator throttle the bypass valve to maintain the appropriate RWCU inlet flow during filter shutdown operations. While attempting to follow the instruction, the operator was monitoring other related instrumentation in addition to the RWCU inlet flow and the bypass valve was opened too far. When flow exceeded the calibrated range of the instrument, the Leak Detection system could no longer accurately determine differential flow, and an artificial differential flow signal was initiated. Because the instruction did not provide appropriate limitations for system flow during this operation, procedural inadequacy is considered to be a contributing factor. <br /><br /> To prevent recurrence, the System Operating Instruction is being revised to provide the necessary guidance for control of system flow during filter operations. The Instrument and Controls support engineer is discussing this event and the associated procedural changes with all onshift operators. Additionally this event will be discussed with all licensed operators during their requalification training.
4401991007 | Perry | 02/09/1991 | 03/08/1991 | 9103130254 | <strong>Differential Pressure Switch Instrument Drift Causes Automatic Start of Annulus Exhaust Gas Treatment System, Train A</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1991, at 2003 the AEGTS train A exhaust fan automatically started when an entry was made into the annulus. On February 10, 1991, at 0712, during the monthly required performance of Surveillance Instruction (SVI-M15-T1239) "Annulus Exhaust Gas Treatment System Operability Test", the A fan unexpectedly restarted after shifting from the A to the B fan. Instrumentation and Control technicians determined the problem to be with the calibration of a differential pressure (d/p) switch PDS! (Solon, Model Number 7PS2DS). Both the high and low differential pressure setpoints were found out of calibration low. The technicians readjusted the setpoints to the proper values and returned the switch to service on February 10, 1991, at 2225.<br /><br /> The cause of these events was component failure. This instrument has been replaced numerous times in the past and has a documented history of drifting out of calibration. During this event, the instrument drifting out of calibration resulted in the automatic starting of exhaust fan A when minor disturbances were introduced to the annulus atmosphere during routine evolutions. <br /><br /> To prevent recurrence, the switch was recalibrated to adjust the setpoints to their proper value. Testing was performed to verify that the calibration of the d/p switch corrected the problem. The calibration frequency of the d/p switch has been increased from six months to three months as an interim measure while an engineering evaluation is in progress to determine a suitable instrument for potential replacement of the Solon d/p switch. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991008 | Perry | 03/05/1991 | 03/29/1991 | 9104080218 | <strong>Inoperability of Control Room Emergency Recirculation System Due to Inoperability of Both Supporting Chillers Results in Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1991 at 1812 both trains of the Control Room Heating and Air Conditioning (CRHVAC) System became inoperable for the Emergency Recirculation mode due to the inoperability of both supporting chillers. The B Control Complex Chiller was secured from service for scheduled maintenance when the A Control Complex Chiller tripped on low refrigerant temperature and the A Chiller and its associated CRHVAC train were declared inoperable. Because this condition is not addressed in Technical Specification 3.7.2., the plant entered Technical Specification 3.0.3. <br /><br /> The root cause of this event was component failure. The event was caused when the solenoid valve on the thermal purge unit did not close when required, resulting in a loss of refrigerant and the low temperature trip. When the thermal purge unit was isolated, the chiller was successfully recharged and returned to service. <br /><br /> To prevent recurrence the solenoid valve was replaced. The exact failure mechanism of this valve will be determined through further troubleshooting. The thermal purge valve of an operable chiller will be plugged until the cause of the valve failure is determined and corrected. Due to the numerous cases of CRHVAC inoperability, an engineering analysis is being performed to evaluate the design of the CRHVAC and its support systems. Additionally, this event will be discussed with the operators during requalification training.
4401991009 | Perry | 03/14/1991 | 04/15/1991 | 9104220302 | <strong>Violation of Technical Specifications and Inoperability of the Division 1 and 2 Diesel Generators Due to Equipment Malfunctions.</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1991 at 0915, a failure of the Division 2 Diesel Generator (DG) occurred when the field failed to flash during the monthly surveillance operability test. The Division 2 DG was declared inoperable and the other divisional DGs were run within 24 hours to verify operability. During the Division 1 DG test, the governor speed control failed to respond to manual operation in the lower direction, preventing synchronization to the grid. The Division 1 DG was declared inoperable on March 14, 1991 at 1425. Following repairs, the Division 2 DG was declared operable on March 15, 1991 at 0220 and the Division 1 DG was declared operable at 2305.<br /><br /> The root cause of both events was equipment malfunction. The Division 2 DG field contactor K1 failed to close due to a component failure, which occurred at completion of the last successful diesel surveillance run during engine shutdown on February 14, 1991. The Division 1 DG equipment malfunction was isolated to the governor control circuit, which was serviced and tested prior to declaring the DG operable.<br /><br /> To prevent recurrence, design and procedural changes were initiated to enhance the reliability of the field contactor and procedural changes will be made for servicing the governor control circuitry. In addition, the Division 2 DG failed component was returned to the vendor for failure analysis and a notification of the event was provided to the DG Owners Groups (DeLaval and General Motors EMD). <br /><br /> Submittal of this report satisfies the requirements of Technical Specifications 4.8.1.1.3 and 6.9.2.
4401991010 | Perry | 04/02/1991 | 05/02/1991 | 9105070222 | <strong>Faulty Contactor Results in Shutdown of Plant in Accordance with Technical Specification Action Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1991 at 2000, reactor power was being reduced to allow drywell entry to investigate an increase in drywell unidentified leakage. An attempt to downshift Reactor Recirculation Pump "A" to slow speed was unsuccessful and resulted in a pump trip. Reactor Recirculation Loop A was declared inoperable and after an additional attempt to start the Reactor Recirculation Pump "A" was unsuccessful, the plant was shut down on April 2, 1991, at 0658 in accordance with Technical Specification Action 3.4.1.1.a. The source of the leakage was a weld on a vent valve for the Reactor Recirculation Loop "B" Suction Isolation Valve. <br /><br /> The cause of the Reactor Recirculation Pump failure to operate in slow speed was a component malfunction. A contactor (General Electric Company, Model Number CR205K00AAD) in the voltage regulator circuit of the Low Frequency Motor Generator (LFMG) failed to close its contacts when energized which resulted in no LFMG output. The cause of the leak on the vent valve weld has not yet been determined but penetrant tests of other similar weld configurations do not indicate that this is a generic problem. <br /><br /> To prevent recurrence, the contactor was replaced and the Reactor Recirculation Pump A was verified to operate properly in low speed. Procedures for cleaning the cubicles, in which the contactors are located, are being developed. The same contactor for the Recirculation Pump "B" circuitry will also be inspected. The vent valve weld configuration that leaked is being sent off site for analysis to determine the cause of the leak. As a part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991011 | Perry | 04/16/1991 | 12/06/1991 | 9112100271 | <strong>Reactor Water Cleanup Containment Isolation Occurred During Plant Shutdown Due to High Differential Flow</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1991 at 0706 hours during a manual plant shutdown, a Reactor Water Cleanup (RWCU) System containment isolation occurred due to high differential flow. Immediate corrective action was taken to verify that no actual system leakage had occurred. The RWCU system was secured and subsequently returned to service.<br /><br /> This event was due to a design deficiency associated with the reduced feedwater temperature mode of operation. The RWCU system was not originally intended to be operated in a reduced feedwater temperature mode, which was added after initial construction in order to minimize the potential for feedwater system thermal stratification and stress. However, operation in the reduced feedwater temperature mode of operation introduced unforeseen system voiding which caused RWCU isolation on high differential flow. After evaluating a number of proposed recommendations for reducing such events, the option of pursuing a Technical Specification change to increase the differential flow timer setpoint was chosen. Additionally, a vendor analysis determined that no long-term deleterious effects had resulted or would result from occasional RWCU system transients involving flashing or voiding.
4401991012 | Perry | 06/05/1991 | 07/03/1991 | 9107100112 | <strong>Program Deficiencies Resulted in an Inoperable Effluent Flow Monitor Without the Required Compensatory Actions Taken, Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1991, it was determined that the effluent system flow rate monitor for the Turbine Building/Heater Bay Building (TB/HB) vent radiation monitor had been inoperable during two fan operation since the summer of 1988. During this time, the effluent flow rate was not estimated every four hours in violation of Technical Specification 3.3.7.10. <br /><br /> The causes of this event were program deficiencies. The preoperational testing program did not fully test the accuracy of the vent effluent flow monitors. The current program does not verify the accuracy of this flow sensing device, or adequately compensate for deviations in air temperature.<br /><br /> All other vent effluent flow monitors were evaluated for similar flow degradation with no problem found. This pitot tube array will be calibrated by capping individual pitot tubes as required and possible degradation will be investigated. The calibration instructions for the TB/HB vent and similar effluent flow monitors will be revised to evaluate the performance of the flow sensing device. Prior to restoring the flow monitor to operable status during two fan operation, a mechanism for temperature compensation will be established. This event will be discussed as part of the licensed operator requalification program.
4401991013 | Perry | 07/23/1991 | 08/22/1991 | 9108270095 | <strong>Missed Main Steam Line Flow High Isolation Actuation Instrumentation Surveillance Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>Between June 21, 1991 and July 13, 1991, two channels of the Main Steam Line High Flow Isolation Instrumentation were inoperable without completion of the action requirements of Technical Specification 3.3.2., which require the associated trip system to be placed in the tripped condition. This condition, which was due to a failure to complete Technical Specification Surveillance Requirements, was discovered on July 23, 1991, during an administrative review of surveillance documents. <br /><br /> The root cause of this event is multiple personnel errors, (inattention to detail/failure to recognize), between June 10 and June 13, 1991. The I&C Unit lead who was required to obtain the functional check surveillance instruction for the A channel mistakenly ordered the similar instruction for the B channel. Additionally, the I&C, Control Room, and Engineering personnel responsible for the assembly of the test package, task assignment, approval, conduct, and review of the test failed to recognize that the wrong surveillance instruction was performed and attached to the test package information sheets. Consequently, the functional check of the A channel instrumentation was not completed, while the functional test of the B channel was performed twice. <br /><br /> To prevent recurrence this event is being discussed in I&C continuing training and has or is being discussed by all other sections involved with this event to re-emphasize the importance of proper test package assembly and review. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991014 | Perry | 07/26/1991 | 08/23/1991 | 9108270115 | <strong>RWCU Isolation Due to a High Differential Temperature Signal During Decontamination Activity</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1991, at 0905, a Reactor Water Cleanup (RWCU) System containment isolation occurred due to a high differential temperature signal in the RWCU Pump Room. During decontamination activity, a Leak Detection System temperature element located in the RWCU A pump room area was sprayed with water resulting in the high differential temperature signal system isolation and pump trip. After verifying that no steam leak existed, operators returned the RWCU B Pump to service. <br /><br /> The cause of the event was personnel error, inadequate training/knowledge. The Health Physics technician who directed the decontamination process and the maintenance personnel performing the decontamination were unaware of the consequence of wetting this instrumentation. There were no signs in the area to communicate the sensitive nature of this instrumentation to the personnel performing the decontamination. <br /><br /> To prevent recurrence of the event, discussions were held with Health Physics and maintenance personnel during weekly meetings. This event will be discussed during continuing training for Health Physics personnel, and during initial Decontamination Techniques training for Plant Helpers, Health Physics Personnel and contractors used to supplement decontamination activities in the plant. Additionally, this event will be discussed with the licensed operators as part of the requalification training. Signs identifying this and other related differential temperature elements, will be permanently posted designating them as "Temperature Sensitive Elements".
4401991015 | Perry | 08/01/1991 | 08/30/1991 | 9109040039 | <strong>Liquid Radwaste Discharge Not Made In Accordance with Technical Specification 3.3.7.9</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1991, a liquid radiological effluent release was performed with radioactive effluent monitoring instrumentation inoperable without independently verifying the discharge line valving as required by Technical Specification 3.3.7.9. During investigation of the August 1, 1991 event, it was discovered that the radwaste high flow discharge header flow instrumentation channel was improperly calibrated between July 22, 1991 and August 1, 1991, which resulted in the discharge with nonconservative indications of discharge flow. <br /><br /> The root cause of this event was personnel error, failure to follow procedure. IAP-0503, "Plant Instrument Calibration and Maintenance", specifies that plant Technical Specification instrumentation will be calibrated utilizing calibration values found in appropriate surveillance instructions. The Instrument and Control (I&C) technician utilized inappropriate calibration values from an uncontrolled document to calibrate the radwaste high flow discharge header flow instrumentation channel. <br /><br /> The I&C technician was counseled with respect to requirements for procedural compliance. Additionally, IAP-0503 will be enhanced to provide further clarity regarding the requirement for utilizing calibration information from surveillance instructions when calibrating Technical Specification instrumentation. All I&C technicians will be trained to this change, and to the circumstances surrounding this event.
4401991016 | Perry | 08/16/1991 | 09/13/1991 | 9109170202 | <strong>Inadvertent Test of Radiation Monitor Results in Backup Hydrogen Purge System Isolation</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1991, at approximately 0830, the Unit Supervisor requested assistance from the Shift Instrumentation and Control (I&C) technician to investigate a potential problem concerning the Drywell Atmospheric Particulate Radiation Monitor indicating lower counts than expected. At 0854, the Shift I&C technician inadvertently mispositioned the front panel switch on the Drywell Atmospheric Gaseous Radiation monitor which resulted in the initiation of a trip signal that caused the closure of the Backup Hydrogen Purge System isolation valves. <br /><br /> The cause of this event is personnel error, inattention to detail. The technician performing the high voltage check, which is a simple front panel switch manipulation, performed the check on the wrong radiation monitor. Although the monitors are located in the same vicinity, they are clearly labeled and can be readily distinguished from each other.<br /><br /> Additionally, further inattention to detail resulted in the switch mispositioning and the related alarms and isolation. <br /><br /> To prevent recurrence, the technicians involved have been counseled and disciplined. This event is also being reviewed by all I&C technicians in continuing training. Additionally, since the Drywell Atmospheric Gaseous Radiation Monitor is the only monitor on this panel which provides an isolation function, engineering personnel are evaluating potential methods to caution operators/technicians when manipulating panel switches. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991017 | Perry | 10/02/1991 | 11/01/1991 | 9111070157 | <strong>High Pressure Core Spray Pump Inoperable Due to Motor Bearing Oil Reservoir Drain Plug Failure</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991, during routine operator rounds, oil was observed leaking from the lower bearing oil reservoir for the High Pressure Core Spray (HPCS) Pump. During the subsequent investigation, the Responsible System Engineer (RSE) determined the source of the leak to be the bearing oil reservoir drain plug. Upon further investigation the RSE determined that the drain plug could not be tightened sufficiently to allow operation of the HPCS motor. The HPCS system was declared inoperable and a four-hour notification made pursuant to the requirements of 10CFR50.72(b)(2)(iii)(D). The drain plug was subsequently replaced and the HPCS system was returned to operable status. Bearing oil drain plugs of similar design were visually inspected for signs of leakage. No additional problems were identified. <br /><br /> As a result of similar previous occurrences, the root cause has been determined to be a design deficiency due to the use of the drain plug as an oil sample collection point. Existing interim corrective action measures will be utilized until Design Change Package (DCP) 88-0256 is implemented. The revised design will replace the drain plugs with a ball valve arrangement to facilitate lube oil sampling activities. Drain plug replacement will occur prior to the end of the next refueling outage on a system availability basis.
4401991019 | Perry | 10/06/1991 | 11/05/1991 | 9111080163 | <strong>Missed Rod Pattern Controller Surveillance Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1991, at 1839, during a plant shutdown, a Technical Specification surveillance requirement for the rod pattern controller was performed late. On At 1827 the first rod/gang (gang 46) had reached the first banked position during the shutdown; however, twelve additional rod/gang movements were performed before properly testing the rod pattern controller before operators realized the error. <br /><br /> The cause of the violation of the rod pattern controller Technical Specification is personnel error, inattention to detail/failure to recognize. The Senior Reactor Operator in control of the shutdown activities knew of the requirement to test the rod pattern controller, but was unaware of actual rod position with respect to the bank limits. A contributing factor to this event is inadequate training, in that the infrequency and level of detail of training to this surveillance left the operating crew unfamiliar with this activity. <br /><br /> The Senior Reactor Operator responsible for the missed surveillance requirement has been counseled concerning importance of attention to detail. Procedures are being revised to clarify the rod pattern controller testing requirement. Additionally, the frequency and detail of simulator training, on performance of this surveillance, is being increased. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991020 | Perry | 10/07/1991 | 01/03/1992 | 9201070360 | <strong>Cable Tray Raceways Found to be Impaired as a Fire Barrier, Adversely Affecting Safe Shutdown Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, discrepancies in the installation of the mechanical fasteners on Appendix R raceways was determined to be a fire barrier impairment which could adversely affect safe shutdown requirements. On December 4, 1991, during corrective actions for this condition, deficiencies in the length and thickness of fire barrier material on the raceways supports/heat transfer items were also discovered. Technical Specifications require these conditions be reported to the NRC through the LER process. The mechanical fastener discrepancy is also considered reportable under 10CFR21.<br /><br /> The cause of the mechanical fastener discrepancy was inadequate design. The information, provided by Gilbert Commonwealth, resulted in various design documents not reflecting the vendor's, Thermal Science, Inc. (TSI), installation criteria concerning maximum spacing of the mechanical fasteners. An inadequate installation instruction and installation errors resulted in the heat transfer items thickness and length discrepancies. <br /><br /> The immediate corrective actions was to initiate hourly watches for the fire impairment situation, which will continue until the Appendix R raceways are upgraded to ensure compliance with all specifications. The affected design documents will be revised to reflect the installation criteria specified by the TSI vendor manual.
4401991021 | Perry | 10/11/1991 | 11/08/1991 | 9111150026 | <strong>Inoperable Preferred Source Breaker Results In Exceeding The Allowable Outage Time Limit Provided By TS 3.8.1.1</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1991 at 1138, preferred source breaker EH1114 would not close on demand from its switch on control room panel 1H13-P877-1. Investigation determined that this breaker had been inoperable since September 4, 1991. As a result, the allowable outage time limit provided by Technical Specification 3.8.1.1 was exceeded. <br /><br /> The primary cause of this event was equipment malfunction, Other. Over the years, modifications were performed on the racking tool utilized to engage and turn the racking lead screw. These modifications allowed interference with the end of the racking release lever as it attempts to settle in the final detent (racked-in) position; thereby allowing the racking lead screw to be overturned, which places the breaker into a trip free condition. <br /><br /> To prevent recurrence, operations personnel visually inspected safety and nonsafety related bus breakers to ensure that their mechanical interlocks were disengaged. All auxiliary operators were retrained to perform visual checks of the mechanical interlock during future racking evolutions. Additionally, spring pins on the applicable racking tools will be shortened to one inch in length. Licensed personnel and auxiliary operators will be trained to this event during current events training.
4401991022 | Perry | 10/11/1991 | 11/08/1991 | 9111150027 | <strong>Previously Unrecognized Radiation Monitor Spiking Results in Backup Hydrogen Purge System Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1991, at 1845, the Senior Reactor Operator manipulated the front panel switches on the Drywell Atmospheric Gaseous Radiation Monitor to check the "Alert Alarm Setpoint". During the switch manipulations, the radiation monitor indication spiked upscale causing a Backup Hydrogen Purge System isolation. <br /><br /> The cause of the event is a previously unrecognized equipment characteristic. During troubleshooting it was noted that manipulating the front panel switches of the radiation monitor to perform setpoint checks would result in the same trip signal that was received during this event. This is due to a combination of equipment design and the value of the trip setpoint, and the spiking is considered normal for this evolution.<br /><br /> To prevent recurrence, an information tag has been attached to the front of the monitor to warn of the potential of an inadvertent Backup Hydrogen Purge System isolation due to spiking during switch manipulations. The appropriate operating instruction is being revised to provide the required guidance to avoid potential problems with the equipment characteristics for this and other applicable radiation monitors. Licensed operator training is being updated to reflect the additional procedural guidance for the applicable radiation monitors. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991023 | Perry | 11/05/1991 | 12/05/1991 | 9112100279 | <strong>Misadjusted leak Detection Instrumentation Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1991, at 1911, the misadjustment of two Main Steam Line isolation Actuation Instrumentation Turbine Building Main Steam Line Temperature - High channels resulted in the inoperability of both channels and in a violation of Technical Specifications. These channels had been considered operable from November 5, 1991 at 1811 until 1917 at which time they were declared inoperable again for testing. However, during this period, both of these channels were in fact inoperable and the action to place at least one trip system in the tripped condition within one hour, as required by Technical Specification LCO 3.3.2 Action c. was not taken. <br /><br /> The cause of this event is equipment problem (other). A Transmation Model 1010 Reference Cell, used as part of the test equipment for surveillance testing, had an intermittent malfunction which caused the reference cell to provide an inaccurate output during the test. This caused the instrumentation channels to appear to require adjustment and resulted in the subsequent inoperability of both channels. <br /><br /> A review of the previous uses of the reference cell in question has been conducted and the operability of other plant equipment has not been affected. Additionally, all applicable reference cells have been checked to ensure that battery connections are clean and tight. To prevent recurrence, qualification training on the reference cell is being enhanced to include direction on how to check the reference cell during usage. The same topic will be covered in I&C continuing training, and the lessons learned from this event have been covered in I&C shift briefings. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991024 | Perry | 12/04/1991 | 03/20/1992 | 9203250058 | <strong>Loss of Emergency Service Water System Loop Due to Inadvertent Isolation of Keepfill System</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1991, a Perry Plant Operator (PPO) performing a weekly check of the Emergency Service Water (ESW) keepfill system discovered the keepfill system pressure reading approximately 3.5 psig. The keepfill system pressure is required to be >/= 13 psig when the ESW A loop is in standby. The PPO checked the position of keepfill isolation valve 1P45-F720A and found it closed. The ESW A loop and associated loads were declared inoperable in accordance with the applicable Technical Specification Action Statements.<br /><br /> The mispositioning of valve 1P45-F720A was attributed to personnel error. The last authorized repositioning of 1P45-F720A occurred on November 21, 1991. Interviews of personnel performing work in the vicinity of the keepfill isolation valve did not reveal the source of the error. It was therefore assumed that the valve mispositioning was an unintentional error by an unidentified person.<br /><br /> To prevent recurrence of a similar incident involving the keepfill isolation valve, the required valve position will be changed from normally open to locked open. Additionally, all licensed and non-licensed plant operators will receive training on this event as part of requalification training.
4401991025 | Perry | 12/12/1991 | 01/13/1992 | 9201220258 | <strong>Cracked Weld on Valve Appendage Results in High Pressure Core Spray System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1991, at 1100, liquid penetrant testing revealed a crack in a weld upstream of the high point vent valve on the High Pressure Core Spray (HPCS) system test return line. The control room was contacted and HPCS, which had been in standby readiness, was declared inoperable on December 13, 1991, at 1542. The cracked weld was reworked to specifications and HPCS was declared operable on December 15, 1991, at 0510. <br /><br /> The weld failure is attributed to a combination of factors. The inspected welds were being checked under a plant initiative to inspect welds as a result of a previous LER. This weld was chosen due to being located in an area subject to relatively high vibration. The weld was at the branch connection between the vent piping and test return piping. <br /><br /> The appendage had two 3/4 inch vent valves supported solely by this branch connection. Additionally, field inspection of the appendage by engineering personnel determined that the cracked weld did not fully meet the specifications required by the design drawings, having insufficient weld metal and contour.<br /><br /> The schedule to inspect other welds identified by the activities resulting from the previous LER has been accelerated. Engineering personnel are in the process of monitoring the reworked weld on the HPCS system for vibration to determine if additional corrective actions may be required. Additionally, engineering personnel will perform a design review to identify applications involving welds with similar profiles. Those identified in the design review will be inspected to ensure compliance with design requirements. As part of the established requalification training program, all plant licensed operators will be instructed on the lessons learned from this event.
4401991026 | Perry | 12/16/1991 | 01/10/1992 | 9201130122 | <strong>Division I Reactor Core Isolation Cooling Isolation During Surveillance Activities</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1991, at 0148, a Division I Nuclear Steam Supply Shutoff System signal resulted in an unexpected Reactor Core Isolation Cooling (RCIC) system isolation during the performance of a surveillance. <br /><br /> On December 16, 1991, at 0135, Instrument and Controls (I&C) technicians began monthly surveillance, (SVI-E31-T0100-A) "RCIC Steam Supply Pressure-Low Channel A Functional for 1E31-N685A." The I&C lead performer of this surveillance incorrectly read that the step to lift leads disabling the RCIC isolation did not have to be performed. When the trip signal was applied the system isolated as designed. The cause of this event is personnel error, inattention to detail. <br /><br /> The technician performing the surveillance was counseled, involved in this investigation, and is fully aware of the consequences of his actions. This LER will be discussed with all I&C technicians as part of their continuing training program.
4401991027 | Perry | 12/22/1991 | 01/21/1992 | 9201290022 | <strong>Plant Shutdown Due to Circulation Water System Pipe Rupture</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1991, at 0205 hours, a manual reactor scram was inserted per Integrated Operating Instruction (IOI) - 8 due to a non-isolable break in the Circulating Water System (N71) piping. The break occurred on a section of 36 inch fiberglass reinforced plastic pipe which supplies cooling water to the auxiliary condensers. At 0259, the shift supervisor declared an Alert based on reports of rising water level received and indications available in the Control Room. All required notifications were made regarding the Alert declaration. <br /><br /> Equipment anomalies and malfunctions which occurred after the manual scram was inserted are summarized in the text of this LER. The cause of the pipe rupture was attributed to a combination of factors which included a pre-existing flaw in the fiberglass, functional degradation of a pipe support and improper installation of an O-ring gasket at the fiberglass to steel transition flange. The plant was restarted on January 3, 1992 after repairs were made to the affected piping and associated supports. Additionally, the equipment anomalies and malfunctions which occurred after plant shutdown were investigated and corrective actions taken where appropriate.
4431991001 | Seabrook | 02/12/1991 | 03/13/1991 | 9109100390 | <strong>Reactor Trip Due To Loss Of Electrohydraulic Control System Pressure</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1991, at 8:22 a.m. EST, a turbine-generator trip with a reactor trip occurred while the plant was at 100% power. The trip was initiated by a loss of Electrohydraulic Control (EHC) system pressure. A Main Feedwater Isolation and an Emergency Feedwater Actuation also occurred subsequent to the trip. <br /><br /> Prior to the event, 480 volt AC unit substation ED-US-14 was cross connected to unit substation ED-US-21 in preparation for various electrical maintenance tasks on the primary breaker, secondary breaker and transformer for ED-US-14. Approximately twenty-five minutes following the cross connection, the secondary breaker for ED-US-21 tripped due to the energization of two large cyclic loads, the turbine building crane and the guardhouse megatherm tank heaters. Consequently, power was lost to both EHC pumps causing a loss of EHC system pressure that resulted in a turbine-generator trip with a reactor trip as designed. <br /><br /> The root cause has been determined to be an inadequate procedure. A contributing cause was inadequate training. To prevent recurrence, operating procedures, maintenance Repetitive Task Sheets and planning and scheduling procedures will be revised to provide additional controls to ensure that the overall connected load is formally evaluated and controlled prior to cross connecting unit substations. The lessons learned from this event will be discussed with all operating crews. Additionally, a Training Development Recommendation (TDR) will be written to address failure mode and consequence thought processes during abnormal system alignments. <br /><br /> This is the first event of this type at Seabrook Station.
4431991002 | Seabrook | 03/30/1991 | 04/26/1991 | 9105030243 | <strong>Manual Reactor Trip Due to Loss of a Vital Bus</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 30, 1991 at 11:48 a.m., a manual reactor trip was initiated while the plant was at approximately 50% power. The reactor trip was initiated due to a turbine runback coincident with a loss of the condenser steam dump valves. <br /><br /> While the plant was at 100% power, an electrical fault occurred in the transformer section of 480 volt AC unit substation EDE-US-52 resulting in a loss of all loads powered from this bus. Consequently, a turbine runback was initiated by a loss of Generator Stator Cooling (GSC) system control power. Additionally, control power to the condenser steam dump valves was lost. In response to the loss of the condenser steam dump valves, all four atmospheric steam dump valves and several steam generator safety valves automatically actuated. <br /><br /> Following the reactor trip and turbine trip, a Main Feedwater Isolation and an Emergency Feedwater actuation occurred as designed. Additionally, upon restoration of power, the Control Room Emergency Air Cleanup and Filtration Subsystem actuated as designed. <br /><br /> The root cause for the electrical fault has been determined to be a turn-to-turn fault on one phase of the 4160/480 volt AC transformer's primary winding. The transformer for the bus was replaced. Additionally, this event will be discussed with operations personnel during requalification training. An emphasis will be placed on the reportability requirements pursuant to 10 CFR 50.72 regarding ESF actuations. <br /><br /> This is the first event of this type at Seabrook Station.
4431991003 | Seabrook | 04/16/1991 | 05/15/1991 | 9105290224 | <strong>Noncompliance with Technical Specifications - Mispositioned Valve</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1991 at 9:45 p.m., EDT, while in MODE 1 at 100% reactor power, it was discovered that an instrument root isolation valve (SI-V61) for two non-safety class pressure instruments (1-SI-PT-2491 and 1-SI-PI-929) was unlocked and open, contrary to its required position of locked closed. This instrument root isolation valve is located outside the primary containment building, between the two containment isolation valves (SI-V70-inside, and SI-V62-outside) for containment penetration X-35A. During the time that SI-V61 was in the open position, and contrary to Seabrook Station Technical Specification 3.6.3, the inside containment isolation valve (SI-V70) for penetration X-35A was not deactivated in the isolation position. When discovered to be open, SI-V61 was immediately locked closed.
4431991004 | Seabrook | 04/01/1991 | 05/23/1991 | 9105290157 | <strong>Feedwater Check Valve Bolting Failures</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1991, during a plant restart, following a March 30, 1991 reactor trip, flow through the feedwater header cheek valve 1-FW-V330 to the A steam generator indicated that the valve was not opening properly, Efforts were made to exercise the valve by varying feedwater flow rates, but the valve did not change position.<br /><br /> Upon disassembly of the subject check valve, it was discovered that seven of the dash plate capscrews were broken and the eighth capscrew was stretched. This resulted in the valve disk becoming jammed in a near closed position. Subsequently, the other three feedwater header check valves were disassembled and similar capscrew failures were identified. As a result of these capscrew failures, Edward Valves, Inc. notified the USNRC, pursuant to 10 CFR 21. <br /><br /> The dash plate capscrews failed due to a differential pressure across the dash plate. The resultant dash plate differential forces created higher than expected tensile loads on the capscrews. The capscrews ultimately failed due to this loading. Valve design modifications were implemented to modify the dash plate and locking ring. These modifications increased the number of capscrews from 8 to 16 and machined the dash plate surface that faces the valve disk in two of the valves. By increasing the number of capscrews the individual capscrew loading will be reduced, preventing future capscrew failures. Additionally, dash plate machining was performed on two valves to prevent the valve disk from contacting the dash plate when the valve fully opens. <br /><br /> This is the first event of this type at Seabrook Station.
4431991005 | Seabrook | 05/29/1991 | 06/28/1991 | 9107020458 | <strong>Noncompliance with Technical Specifications - Unlocked Circuit Breaker</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1991, at 1:30 a.m., it was discovered that the circuit breaker (1-FH-RE-12) feeding the Rod Control Cluster Change Fixture, was unlocked and had been unlocked since May 14, 1991. This event occurred contrary to Seabrook Station Technical Specification (T.S.) 3.8.4.1 which requires the breaker to be padlocked in the open position. <br /><br /> On May 14, 1991, at 8:00 a.m., circuit breaker 1-FH-RE-12 was tagged out of service and unlocked in preparation for an electrical preventative maintenance activity. However, upon completion of the preventive maintenance activity, the circuit breaker was inadvertently not padlocked in the open position. Although the circuit breaker was not padlocked in the open position it was open during the entire period. <br /><br /> The root cause has been determined to be personnel error. <br /><br /> Upon discovery, the breaker was immediately padlocked. Additional corrective actions include: (1) Each Shift Superintendent will discuss this event and other recent similar events involving locked components with his respective operating crew; (2) Signs have been placed on all T.S. 3.8.4.1 circuit breakers identifying them as a locked component; (3) Enhancing Operations Good Practices to provide specific guidance for controlling locked components; (4) Verifying that all components which are required to be locked are listed in the tagging computer; (5) A design change will be initiated to evaluate components required to be locked and to eliminate any unnecessary requirements; and (6) Evaluating the potential installation of lock lanyards on the cabinets for the T.S. 3.8.4.1 circuit breakers. <br /><br /> The above corrective actions are expected to be completed by September 30, 1991. <br /><br /> This is the second event of this type at Seabrook Station.
4431991006 | Seabrook | 06/02/1991 | 07/02/1991 | 9107050002 | <strong>Reactor Trip Due to an Inadvertent Actuation of the Turbine Mechanical Overspeed Protection System</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1991, at 6:47 a.m., a turbine generator trip with a subsequent reactor trip occurred while the plant was at 100% power. The trip was initiated by an inadvertent actuation of the turbine mechanical overspeed protection system. A Main Feedwater Isolation also occurred subsequent to the trip. <br /><br /> During a weekly turbine mechanical overspeed trip test, the oil trip solenoid valve (OTSV) did not return to its original position. Maintenance personnel removed one of the solenoid valve housing covers to conduct a visual verification of the actual position of the OTSV and its limit switch. While the housing cover was removed the limit switch assembly base plate and bracket dropped away from the housing. Consequently, the limit switch changed state causing the mechanical lockout solenoid valve to reset. A turbine trip immediately resulted since the OTSV was still supplying bearing oil to actuate the mechanical overspeed trip lever assembly. <br /><br /> In response to the turbine trip and reactor trip, the condenser steam dump valves actuated as designed. However, two steam dump valves remained open longer than expected. <br /><br /> The cause of the oil trip solenoid valve to remain in the test position was the presence of corrosion products inside the valve body.<br /><br /> The oil trip solenoid valve was replaced and subsequently exercised to ensure free movement. Additional corrective actions include the following: 1) Similar solenoid oil valves will be labeled to warn technicians of the trip potential if the cover is removed; 2) The weekly mechanical overspeed trip test procedures were revised to provide additional guidance for unsuccessful tests and to exercise these valves on a weekly basis to prevent corrosion product buildup; 3). The oil resets, oil trip and mechanical trip solenoid valves in the Emergency Trip System will be replaced; 4) An evaluation of previous problems with the condenser steam dump valves was performed and no generic problems were identified.
4431991007 | Seabrook | 06/15/1991 | 07/12/1991 | 9107180254 | <strong>Actuation of the Control Room Emergency Air Cleanup and Filtration Subsystem</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1991, at 8:23 a.m. EDT, an Engineered Safety Features (ESF) actuation occurred causing the Control Room Normal Makeup Air Subsystem (CBA) to transfer to the Control Room Emergency Air Cleanup and Filtration Subsystem. <br /><br /> The ESF actuation occurred while transferring the CBA ventilation from train "B" to train "A". The operator performing the transfer inadvertently operated the control switch for damper CBA-DP-27A. When this damper opened, fan CBA-FN-16A automatically started. The operator should have operated the control switch for fan CBA-FN-27A as required by step 6.6.2.1 of procedure OS1023.51, "Control Room Ventilation and Air Conditioning System Operation". <br /><br /> The root cause of this event has been determined to be personnel error involving a lack of attention to detail.<br /><br /> A contributing cause was the close proximity and the labeling of the two control switches. <br /><br /> Each Shift Superintendent will discuss this event and the lessons learned with their respective operating crews. In addition, the feasibility of a design change to improve the human factors in this area will be evaluated. <br /><br /> This is the third event of this type at Seabrook Station.
4431991008 | Seabrook | 06/27/1991 | 07/26/1991 | 9108010174 | <strong>Turbine Trip with Reactor Trip Due to an Inadvertent Actuation of Switchyard Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1991, at 1:34 p.m., a turbine generator trip with a subsequent reactor trip occurred while the plant was at 100% power. The turbine trip was initiated when two switchyard 345kV circuit breakers tripped open disconnecting the generator from the offsite distribution system. <br /><br /> The event occurred during the performance of a preventive maintenance activity on a breaker failure relay 50BF-2/11(H)! for 345kV circuit breaker 11. As the relay was being returned to service (closure of two knife blade switches), momentary arcing occurred across the contacts. The arcing caused a high speed tripping auxiliary relay to pick up without picking up an associated lock out relay. This partial relay actuation resulted in 345kV circuit breakers 11 and 163 opening without generating a signal to open the Unit Auxiliary Transformer (UAT) supply breakers to unit busses 1 through 6. Because of this, the automatic transfer to the Reserve Auxiliary Transformers (RAT) was prevented, resulting in the automatic starting of both emergency diesel generators. Offsite power remained available to the RATs at all times. A turbine trip occurred within one second of the opening of the 345kV circuit breakers. The turbine trip initiated a reactor trip. Following the reactor trip, natural circulation was established. A Main Feedwater Isolation and subsequent Emergency Feedwater Actuation also occurred. Additionally, a Containment Ventilation Isolation and an actuation of the Control Room Emergency Air Cleanup and Filtration System occurred due to the momentary deenergization of the Emergency Busses. <br /><br /> The root cause has been determined to be a manufacturing error in the relay housing contact block assembly for the breaker failure relay. This breaker failure relay was caution tagged to preclude any further maintenance until it is replaced during the first refueling outage. Other relays similar in design will be inspected to ensure that the correct switch assemblies are installed. In addition, the automatic transfer scheme from the UATs to the RATs and the tripping scheme for the out of step relay will be reevaluated.
4431991009 | Seabrook | 07/04/1991 | 08/02/1991 | 9108070231 | <strong>Reactor Trip Due to Reactor Coolant System Low Flow</strong><br /><i>Abstract:&nbsp;</i>On July 4, 1991, at 8:25 a.m. a reactor trip with a turbine generator trip occurred while the plant was at 100% power. The reactor trip was initiated due to low flow in Reactor Coolant System (RCS), loop 3. <br /><br /> The initiating event was caused by an electrical fault in a bus bar. This bus bar is located in the electrical terminal connector box for Reactor Coolant Pump (RCP) "C". As a result of the electrical fault, RCP "C" tripped due to protective relaying action. A reactor trip with a turbine generator trip occurred as designed, due to low flow in Reactor Coolant System loop 3. Subsequent to the reactor trip, a Main Feedwater Isolation occurred due to high-high steam generator water level spikes. In addition, an Emergency Feedwater Actuation occurred due to the feedwater isolation.<br /><br /> The root cause for the electrical fault was determined to be a quarter-inch bolt that was missing from the top access cover plate of the electrical terminal connector box. Additionally, the gasket for this cover plate had pulled away from the connector box, The missing bolt and loose gasket created a direct path for dirt and moisture to enter the electrical terminal connector box which caused the electrical fault, The top access cover plate is not ordinarily used for maintenance. There is no history of this cover plate ever being unbolted since it was originally installed, therefore, it is believed that the bolt was never installed.<br /><br /> The subject gasket and bolt were replaced and an inspection of the cover plates for the three remaining RCPs was conducted to ensure that all the required bolts were installed and that the gaskets were intact. Additionally, the electrical terminal connector boxes for the three remaining RCPs will be inspected during the first refueling outage for signs of moisture and dirt intrusion.
4431991010 | Seabrook | 07/25/1991 | 10/02/1991 | 9110070230 | <strong>Reactor Coolant System Unidentified Leakage</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1991, at 8:00 a.m., while in MODE 1 at 100% reactor power, the Reactor Coolant System (RCS)AB! unidentified leakage rate exceeded the 1.0 gpm Technical Specification (3.4.6.2b) limit. The leak was found to be in the vicinity of the pressurizer, but the exact location could not be determined; therefore a controlled reactor shutdown was initiated. <br /><br /> Following plant shutdown, the leakage source was identified as a failed Raychem "CryoFit" tube coupling located in the pressurizer gas space sample line KN!. The failure was a 360 degree circumferential fracture at the coupling midpoint. A second failed CryoFit coupling located in the same line was subsequently discovered. <br /><br /> Safety-related use of CryoFit couplings at Seabrook Station has been limited to sampling and instrumentation tubing applications. NHY has conservatively replaced a large number of CryoFit couplings installed in tubing exposed to RCS chemistry conditions at elevated temperatures. NHY has reviewed applicable industry testing of "Tinel" material and has tested a sample of CryoFit couplings removed from selected locations. The root cause has been determined to be a specification deficiency. The failure mechanism has been determined to be hydrogen embrittlement. <br /><br /> The use of these couplings should be reviewed for applicability in hydrogen environments, paying particular attention to high temperature, high hydrogen, gas space applications at other nuclear facilities.
4431991011 | Seabrook | 08/10/1991 | 09/09/1991 | 9109100390 | <strong>Noncompliance with Technical Specification Action Requirements - Inoperable Source Range Audible Indication</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1991 at 5:00 a.m., during the performance of core alterations (unlatching of the rod cluster control assembly from the drive shafts), it was discovered that the Source Range Neutron Flux Audible Monitors had not been operating for one hour. This is contrary to Seabrook Station Technical Specification 3.9.2. <br /><br /> The loss of audible indication occurred during the performance of procedure RS1708, "Source Range Monitoring Requirements With Either Shutdown Monitor Alarm Inoperable". Specifically, the Unit Shift Supervisor stopped the scaler-timer prior to swapping the source ran e channels. The start pushbutton was depressed subsequent to switching source range channels cut apparently was not depressed long enough to restart the unit.<br /><br /> The root cause of the event has been determined to be personnel error. The Unit Shift Supervisor failed to verify that the audio count rate device was operating when it was restarted. To preclude repetition of this type of event, the following corrective actions were taken: <br /><br /> 1) A caution tag was hung on the scaler-timer stop pushbutton describing the consequences of depressing the pushbutton and a memorandum was sent to the Shift Superintendents providing enhanced guidance on the swapping of source range channels when performing procedure RS1708. <br /><br /> 2) Procedure OS1011.02, "NIS Visual/Audio Count Rate System Operation", was revised to provide enhanced guidance for swapping of source range channels while performing procedure RS1708 and Procedure RS1708 was revised to describe the consequences of depressing the scaler-timer stop pushbutton. <br /><br /> 3) A Request for Engineering Services was initiated to evaluate the feasibility of a design change that will automatically actuate the audible portion of the count rate drawer when a source range channel is selected.
4431991012 | Seabrook | 09/27/1991 | 10/25/1991 | 9110300121 | <strong>Engineered Safety Features Actuation Due to an Inadvertent Safety Injection Signal</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1991 at 2:09 p.m., while in MODE 5, multiple Engineered Safety Features (ESF) associated with Train A actuated upon receipt of an inadvertent Safety Injection (SI) signal for Train A. The inadvertent SI signal was generated during the performance of a Train B ESF test. <br /><br /> Once the inadvertent Sl signal was generated for Train A, all Train A related equipment operated as designed. Specifically, Emergency Diesel Generator (EDG) 1A started, the Train A Phase A Containment Isolation occurred, a Train A Containment Ventilation Isolation signal was generated and the Control Room Normal Makeup Air Subsystem transferred to the Control Room Emergency Air Cleanup and Filtration Subsystem. The EDG start was an unloaded start with no actuation of the Emergency Power Sequencer (EPS). Additionally, no Emergency Core Cooling System (ECCS) pumps started and no ECCS water was injected into the Reactor Coolant System (RCS).<br /><br /> The root cause of this event has been determined to be personnel error. A contributing cause was determined to be an indistinct procedure step. Specifically, two separate operator were contained within one procedure step. <br /><br /> Each Shift Superintendent will discuss this event and the lessons learned with their respective operating crews by October 31, 1991. <br /><br /> Appropriate procedure changes have been made to this and other ESF actuation testing procedures to clarify dual train operation. In addition, Operations' Department procedures related to Solid State Protection System (SSPS) testing will be reviewed and revised as necessary to clarify dual train operation. These procedure changes will ensure that each operator action is distinct and discernible. Specifically, procedure steps which direct separate actions from the two SSPS cabinets will be separated into two steps. It is anticipated that these reviews will be completed by January 31, 1992.
4431991013 | Seabrook | 10/07/1991 | 08/17/1992 | 9208210166 | <strong>Reactor Protection System Actuation During Rod Position Indication 18-Month Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1991, at 6:45 p.m., EDT, while in MODE 3, manual Reactor Protection System (RPS) actuation was performed per Technical Specification 3.1.3.3 when the Digital Rod Position Indicator (DRPI) for Shutdown Bank C, Rod N5, was greater than plus or minus 12 steps of the position indicated on the Demand Counter. A second planned manual actuation of the Reactor Protection System was performed at 9:36 p.m., EDT, during the conduct of troubleshooting activities. <br /><br /> The root cause of this event is indeterminate. North Atlantic has conducted testing which demonstrates that the power cabinet circuitry was not the cause of this event. North Atlantic believes that the DRPI system operated properly and provided an accurate indication of the position of Rod N5, which had dropped due to improper Control Rod Drive Mechanism (CRDM) performance. North Atlantic implemented corrective actions to assist with the determination of the root cause of the malfunction of the Rod Control System. Specifically, North Atlantic conducted additional troubleshooting of the Shutdown Bank C during the Monthly Rod Operability Test (OX1410.02). Discussions with Westinghouse have identified two potential causes of the improper CRDM performance. These are boron precipitation during the last refueling and CRDM wear particulates deposited on the CRDM for Rod N5.
4451991001 | Comanche Peak 1 | 01/03/1991 | 02/04/1991 | 9102060264 | <strong>Inadvertent Actuation Of Control Room Air Conditioning Engineered Safety Feature Caused By Sensitivity Of Radiation Monitoring Device To Overcurrent Conditions</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1991, at approximately 2348 CST, an Auxiliary Operator was attempting to change a burned-out bulb on the local microprocessor associated with one of the radiation monitors in the Control Room air conditioning air intake. When the bulb was unscrewed, a short piece of the bulb's loop filament fell across the two terminal posts inside the bulb. The momentary current surge exceeded the capacity of the power supply output fuse, resulting in a loss of power to the monitor. The Control Room air conditioning system automatically realigned to the emergency recirculation mode. The cause of the event was determined to be equipment sensitivity to overcurrent conditions. Corrective actions included training and administrative controls over bulb replacement in monitors with automatic ESF functions.
4451991002 | Comanche Peak 1 | 01/23/1991 | 02/22/1991 | 9102260303 | <strong>Reactor Trip Caused By Inadequate Setpoints On The Generator Primary Water Head Tank And Less Than Adequate Review Of A Procedure Change</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1991, Comanche Peak Steam Electric Station was in Mode 1, Power Operation, with the reactor at 95 percent of rated thermal power. Operations personnel were in the process of draining the turbine-generator primary water system ion exchanger vessel in preparation for resin changeout. Due to an improperly established vessel isolation, level in the primary water head tank decreased to a point which allowed the introduction of the head tank cover gas into the system flow. The resultant loss of flow indication caused actuation of the generator protection circuit, which lead to a reactor trip. The cause of the event was incorrect head tank low alarm setpoint and an inadequate review of a procedure change. Corrective actions will include setpoint changes and correction to the operating procedure.
4451991003 | Comanche Peak 1 | 01/24/1991 | 04/29/1991 | 9105010137 | <strong>Less Than Adequate Procedure Review Leading To The Failure To Fully Satisfy ASME Section XI Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1991, an engineer was performing a review of a Residual Heat Removal system operability test procedure being developed to support licensing of Unit 2. The reviewer noted that the ASME Section XI test requirements specified in the Inservice Testing Plan were not satisfied by the procedure. The reviewer observed a similar discrepancy in the Unit 1 test procedure. Inadequate implementation of the Section XI test requirements constitutes a failure to meet the operability requirements for a Technical Specification Limiting Condition for Operation. The cause of the event was determined to be inadequate technical review during or following document revision. Corrective actions include a request for relief from the testing requirement and continued evaluation.
4451991004 | Comanche Peak 1 | 02/10/1991 | 03/12/1991 | 9103130246 | <strong>Reactor Trip Caused By Personnel Error And Insufficient Labeling Of Sensitive Equipment</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, at 80 percent reactor power. While conducting on-the-job training, an Auxiliary Operator opened the 6.9 KV switchgear bus "1A3" auxiliary cabinet potential transformer drawer resulting in a load shed signal for the bus loads, which included Reactor Coolant Pump 1-03, followed by a reactor trip due to a loss of flow in reactor coolant loop 3. The root causes were determined to be inadequate labeling on the potential transformer drawer and poor judgement in opening a drawer without knowing the effect it would have on the plant. Corrective actions include labeling the potential transformer drawers, identifying equipment or panels that have interlocks or special sensitivity for equipment actuation, and issuing guidance to personnel on opening switchgear doors.
4451991005 | Comanche Peak 1 | 02/15/1991 | 03/18/1991 | 9103210092 | <strong>Inadvertent Automatic Start Of Turbine Driven Auxiliary Feedwater Pump Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 1627 on February 15, 1991, the Test Engineer completed the response time test of the TDAFW pump from the Train B Solid State Protection System slave relay (K641B). The Test Engineer proceeded to disconnect the chart recorder in accordance with procedure, when he decided to add a length of test lead prior to removing the test lead connection from K641B. The additional length of test lead was to be used in support of the upcoming Train A response time test. <br /><br /> At 1647 on February 15, 1991, the disconnected test leads were inadvertently shorted together resulting in the momentary actuation of K641B and the start of the TDAFW pump. The Test Engineer immediately reported the event to the Reactor Operator who secured the pump and restored actuated components to their original configuration.<br /><br /> Less than adequate personnel performance was the root cause of the event. Corrective action consists of training Performance and Test personnel concerning this event and its root cause. Training will be conducted by the Test Engineer involved in the event.
4451991006 | Comanche Peak 1 | 02/28/1991 | 05/10/1991 | 9105140164 | <strong>Inadvertent Operation Of The Containment Sump Suction Isolation Valves Caused By Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1991, a reactor operator and an Instrument & Control technician were performing quarterly surveillance testing on safeguards slave relays required for automatic operation of the containment sump suction valves. The multimeter being used to measure voltage at points in the control circuit was incorrectly set up to measure current rather than voltage. When the first reading was attempted, the containment sump suction valve received an open signal allowing water to drain from the Refueling Water Storage Tank to the containment sump. The cause of the event was personnel error. Corrective action included event review, training, and procedure enhancement. A voluntary report is being submitted because of the significance and generic interest of the event.
4451991007 | Comanche Peak 1 | 03/15/1991 | 05/31/1991 | 9106040446 | <strong>Less Than Adequate Procedure Review Leading To The Failure To Fully Satisfy ASME Section XI Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 15 and 27, 1991, the Inservice Test Program Coordinator documented examples of incorrect acceptance criteria in Section XI testing requirements for check valves in the auxiliary feedwater system. This condition constitutes a failure to demonstrate operability in accordance with a Technical Specification Limiting Condition for Operation. The cause of the event was determined to be inadequate technical review during or following document revision. Corrective actions include procedure revision and verification of adequacy of similar test procedures. During performance of the procedure verification, additional examples of incorrect test acceptance criteria were documented.
4451991008 | Comanche Peak 1 | 03/17/1991 | 04/16/1991 | 9104190227 | <strong>Reactor Trip Caused By Personnel Error During Testing</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with reactor power at 97 percent. An Auxiliary Operator and trainee were performing a Solid State Protection System, Train A, actuation logic test. During the test, the trainee depressed the shunt the button for the Train B reactor the breaker, instead of the intended Train A the button, causing a reactor trip. Root causes were identified as failure to verify the correct equipment and the Auxiliary Operator allowing his job as a trainer to interfere with his testing duties. Corrective actions include self verification training, enhanced breaker cabinet labels, monitoring operators to ensure self verification techniques are utilized, and additional guidance for trainers on handling trainees.
4451991009 | Comanche Peak 1 | 03/21/1991 | 04/22/1991 | 9104230498 | <strong>Automatic Isolation Of Steam Generator Blowdown Due To Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1991, Comanche Peak Steam Electric Station (CPSES) Unit 1 was in Mode 5, Cold Shutdown, with Reactor Coolant System temperature of 130 degrees F and pressure of 325 psig. Steam Generator Blowdown (SGBD) System was in service and being used to drain the Steam Generators (SG). <br /><br /> At 0300 draining of SG-03 began. The Unit Supervisor followed the System Operating Procedure as written and knew that an ESF actuation would occur at 25 percent level in SG-03, however; he thought this was a controlled evolution, with procedural guidance, and therefore not reportable. Prior to the ESF actuation, the Turbine Driven and both Motor Driven Auxiliary Feedwater pumps, as well as SGBD valves to SG-01, 02, and 04, were secured to minimize the impact on plant equipment. At 0656, a SG Lo-Lo Level ESF actuation occurred, automatically closing the SGBD valve to SG-03. At 0657 the oncoming shift, Reactor Operator, recognized this as a reportable event, started MDAFW pump-02 and re-filled SG-03 to approximately 30 percent, to clear the ESF actuation signal. <br /><br /> The root cause of this event was cognitive personnel error and less than adequate procedural guidance. Corrective actions include training and procedure revisions.
4451991010 | Comanche Peak 1 | 03/22/1991 | 04/16/1992 | 9204210274 | <strong>Unit 1 Operated Outside Technical Specifications Due To Auxiliary Feedwater System Test Line Isolation Not Fully Closed</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1991, an Auxiliary Operator discovered the Train B Motor-Driven Auxiliary Feedwater Pump Recirculation Test Line Isolation Valve one quarter turn open. The valve was last operated on March 13, 1991, during an Auxiliary Feedwater operability test. With the valve one quarter turn open, auxiliary feedwater flow is 8 gallons per minute less than assumed in the safety analysis; therefore, Train B Auxiliary Feedwater was inoperable from March 13 until the valve was closed on March 22. This exceeded the 72 hour Technical Specification Action Statement for one auxiliary feedwater pump or associated flow path inoperable. <br /><br /> The root cause for why the valve was not fully closed could not be determined. Possibilities include the Operator failing to fully close the valve when restoring from the test, the valve being disturbed after it was closed on March 13, or vibration causing the valve to slightly back off its seat. Corrective actions included providing additional guidance to Operators on ensuring these type of valves are closed, having Operators monitor these type of valves during pump runs, and having Engineering take vibration readings on the valve.
4451991011 | Comanche Peak 1 | 03/22/1991 | 04/22/1991 | 9104230464 | <strong>Oversight In Preparation Of A Temporary Modification Resulted In The Failure To Fully Satisfy A Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1991, a 48 inch containment purge exhaust isolation valve failed to demonstrate operability in accordance with the Technical Specification surveillance requirement for verification of leakage rate. As a result, a temporary modification was initiated to install a blind flange on the system. The flange and associated test connection plug are subject to the Technical Specification surveillance requirements for containment integrity; however, the surveillance test procedure was not changed in time to support the temporary modification prior to the first performance of the test following implementation of the modification. As a result, the surveillance requirement was not fully satisfied. The cause of the event is personnel error leading to protracted processing of the procedure change. Corrective actions include procedure enhancement and event review.
4451991012 | Comanche Peak 1 | 03/26/1991 | 04/25/1991 | 9104260240 | <strong>Potential Gas Binding Of Centrifugal Charging Pumps Due To Voids In The Boric Acid Gravity Feed Line</strong><br /><i>Abstract:&nbsp;</i>Ultrasonic examination of the Chemical and Volume Control System (CVCS) suction piping was performed on March 4, through March 15, 1991. These examinations revealed voids in the alternate boration line and the gravity feed line from the Boric Acid Storage Tank (BAT). Engineering evaluation shows that voids in the alternate boration line would not affect operability of the Centrifugal Charging Pumps (CCPs). However, engineering evaluation indicates that the void in the gravity feed line from the BAT could cause damage to or gas binding of the CCPs. <br /><br /> The potential root cause was identified as hydrogen coming out of solution, in the lower pressure CCP suction header. Corrective actions include daily venting of the gravity feed line and further monitoring for hydrogen accumulation. Based on the results of this monitoring, venting requirements will be established.
4451991013 | Comanche Peak 1 | 03/28/1991 | 04/29/1991 | 9105010132 | <strong>Loss Of Offsite Power Caused By Grounded Transmission Line</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1991, at approximately 2253 CST, Comanche Peak Steam Electric Station experienced an Engineered Safety Feature actuation as a result of a line fault on the preferred source of power to the Unit 1 safety-related equipment. Safety-related buses transferred to the alternate source of power, the emergency diesel generator started, and all systems performed as expected. The event occurred again at 0020 hours on March 29. The cause of the two events was determined to be the accumulation of bird droppings on transmission line insulators, providing a current path from the line to the tower. Corrective actions include increased attention to identify the need for cleaning.
4451991014 | Comanche Peak 1 | 04/13/1991 | 05/13/1991 | 9105150358 | <strong>Two Inadvertent Auxiliary Feedwater System Actuations Due To Inadequate Procedures And Mode Selector Switch Design</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1991, a "Safety Injection Without Loss of Power Train B" test was in progress. Upon taking the Solid State Protection System (SSPS) to Normal, an Auxiliary Feedwater (AFW) actuation occurred. The cause was an earlier procedural step that did not completely block an Auxiliary Feedwater actuation from occurring. <br /><br /> On April 15, 1991, a "Safety Injection in Conjunction With Loss of Offsite Power Train B" test had just been completed and restoration was in progress. An AFW actuation occurred when fuses were being installed in the Train B Aux Relay Rack. The cause of the actuation was that the slave relays did not reset as expected due to the presence of a 15 Volt DC test voltage that exists when the SSPS is in the Mode 5/6 lineup. This voltage is not enough to cause the relays to actuate, but is enough to hold the relays once actuated. <br /><br /> The root causes were inadequate test procedures and MODE SELECTOR switch design. Procedure revisions have been made to correct the deficiencies and to be more compatible with the switch design to preclude recurrence of these events.
4451991015 | Comanche Peak 1 | 04/16/1991 | 05/16/1991 | 9105210284 | <strong>Inadvertent Actuation Of Control Room Air Conditioning Engineered Safety Feature Due To Spurious Signal</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, the pressure boundary door seals to the Control Room Heating, Ventilation, and Air Conditioning (HVAC) room were being replaced. The work required the use of a portable electric drill and saw. At 0427 on April 16, 1991, the Control Room HVAC system realigned to the emergency recirculation mode due to a high radiation signal from Radiation Monitor (XRE-5895A). The signal immediately returned to normal. The Reactor Operator (RO) responded to the event in accordance with the applicable procedure. An Auxiliary Operator (AO) was dispatched to investigate the possible cause of the spurious signal. The AO found electrical extension cords within the sensitive zone of XRE-5895A, with work in progress. The AO had the extension cords removed. At 0440 on April 16, 1991, the control Room HVAC system was restored to original configuration. <br /><br /> The root cause of the spurious signal has not been determined. The probable cause has been identified as an electromagnetically induced spike. Corrective actions include procedure revisions and training.
4451991016 | Comanche Peak 1 | 04/18/1991 | 05/21/1991 | 9105290127 | <strong>Manufacturing Error Leading To The Failure Of A Check Valve To Prevent Backflow</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1991, reverse flow testing was being performed on check valves in the Auxiliary Feedwater System. One of eight check valves in the system branch lines failed to meet the test acceptance criteria. The cause of the failure was determined to be a manufacturing deficiency in the finish machining of the rough casting of the valve body. The incomplete machining resulted in excess casting material inside the valve body which interfered with full stroke motion of the swing arm counterweight. Corrective action included finish machining of the affected check valve, inspection of similar valves in the system, and procedure review. A voluntary report is being submitted due to interest resulting from previous experience with check valves in the Auxiliary Feedwater System.
4451991017 | Comanche Peak 1 | 04/29/1991 | 05/29/1991 | 9106030339 | <strong>Personnel Error Resulting In Failure To Satisfy Technical Specification Staggered Test Basis Requirement</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1991, a Quality Assurance auditor discovered that scheduling of Technical Specification surveillance testing of the containment hydrogen monitors had not satisfied the staggered test basis requirement. Early testing of one train resulted in subsequent testing of the alternate train at a subinterval which exceeded the specified subinterval plus maximum allowable extension. The event was caused by personnel error during test scheduling. Corrective actions included training and program changes.
4451991018 | Comanche Peak 1 | 05/28/1991 | 06/27/1991 | 9107020177 | <strong>Technical Specification Violations Due To A Safety Chiller Being Inoperable Greater Than The Allowed Outage Time Of The Supported Systems</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1991, after a review of maintenance and operations history, it was determined that the Train A Safety Chiller may have been inoperable for periods of time between October, 1989, and April, 1991, in excess of that allowed by the supported systems. On October 11, 1989, an oil sump level switch was replaced on the Train A Safety Chiller. The switch incorrectly closed on high sump level and opened on low level; consequently, some of the oil did not return to the chiller sump. As a result, the Train A Safety Chiller could not be guaranteed to perform its design function on an automatic signal due to overload and low oil pressure trips during chiller startup. The problem was masked by other related problems during this period, but on April 18, 1991, troubleshooting the oil return system revealed that the oil sump level switch functioned inversely. A new switch was checked and installed. <br /><br /> The root causes were manufacturing defect and post-installation testing less than adequate. Corrective actions include replacing the switch, verifying no other bad switches exist and incorporating recommendations from a post work test task team.
4451991019 | Comanche Peak 1 | 06/09/1991 | 07/09/1991 | 9107120317 | <strong>Engineered Safety Feature Actuation Due To Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>At 1517 on June 9, 1991, power from the preferred offsite 345kV transmission line was momentarily lost when the transmission line breakers opened, and immediately reclosed, in response to a lightning strike. As a result of the momentary power loss, both safeguards buses transferred to the alternate power supply and both blackout sequencers operated. The Reactor Operator immediately responded to the event in accordance with appropriate procedures and the plant was stabilized at 100 percent power.<br /><br /> Evaluation of this event concluded that all safety systems responded appropriately and no specific corrective actions were required. However, a design modification is being made to the switchyard to enhance the reliability of offsite power sources.
4451991020 | Comanche Peak 1 | 07/13/1991 | 08/12/1991 | 9108140156 | <strong>Reactor Trip Resulting From Erratic Operation Of The Main Turbine Electrohydraulic Controller</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with the reactor at 80 percent of rated thermal power. In preparation for troubleshooting a seal problem on one of the main turbine electrohydraulic controller fluid pumps, the idle pump was started and one of the operating pumps was secured. Following the pump start, air entrained in the fluid flow caused rapid and erratic operation of the main turbine steam control valves. This created a pressure pulse which propagated up the main steam line to the steam generator causing a spike of sufficient magnitude on the steam generator narrow range level transmitter to exceed the Hi-Hi level setpoint. The resulting turbine trip initiated a reactor trip. The root cause of the event will be verified by testing to be performed during a forthcoming outage. Corrective actions include testing and design modification.
4451991021 | Comanche Peak 1 | 07/28/1991 | 08/27/1991 | 9108290275 | <strong>Engineered Safety Feature Actuation Due To Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>At 0704 on July 28, 1991, power from the preferred offsite 345kV transmission line was momentarily lost when the transmission line breakers opened, and immediately reclosed, in response to a lightning strike. As a result of the momentary power loss, both safeguards buses transferred to the alternate power supply and both blackout sequencers operated. The Reactor Operator immediately responded to the event in accordance with appropriate procedures and the plant was stabilized at 100 percent power. Evaluation of this event concluded that all safety systems responded appropriately.<br /><br /> This event is identical to a previous event (LER 91-019). A design modification to the switchyard to enhance the reliability of offsite power sources was partially completed when this event (LER 91-021) occurred. The design modification is scheduled for completion November 27, 1991.
4451991023 | Comanche Peak 1 | 10/03/1991 | 11/04/1991 | 9111050247 | <strong>Reactor Trip Resulting From Erratic Operation Of The Main Turbine Electrohydraulic Controller</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with the reactor at approximately 30 percent of rated thermal power. In order to collect data for evaluation of a problem with the main turbine electrohydraulic control (EHC) system, the idle hydraulic fluid pump was started and one of the two operating pumps was secured. Following the pump switchover, erratic operation of the main turbine steam control valves created a pressure pulse which propagated up the main steam line to the steam generator, causing a spike of sufficient magnitude on the steam generator narrow range level transmitter to exceed the Hi-Hi level setpoint. The main feedwater pumps tripped automatically, and the reactor was manually tripped due to decreasing steam generator levels. Causes include erratic operation of the EHC system and sensitivity of the steam generator narrow range level instrumentation. Corrective actions for EHC system performance anomalies will be determined based on the results of evaluation of test data.
4451991024 | Comanche Peak 1 | 10/04/1991 | 11/04/1991 | 9111050241 | <strong>Inoperable Main Steam Safety Valves Due To Less Than Adequate Lift Setpoint Verification Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1990, the Main Steam Safety Valves (MSSV) were tested and adjusted in accordance with the approved procedure which calculates the lift setpoint from measured parameters. These parameters are documented when the MSSV is heard to lift off of its seat. During this test the Atmospheric Relief Valves (ARV) were open, resulting in extremely high ambient noise. As a result, it was difficult to determine the exact lift point, and the measured parameters were in error (too high). Based on these measured parameters the calculated lift setpoints apparently satisfied the acceptance criteria.<br /><br /> On October 4, 1991, the MSSVs were tested in accordance with the approved procedure. The ambient noise level at the time of the test was minimal; the ARVs were closed. Thirteen of the fourteen MSSVs tested were found to have lift setpoints less than the setpoint tolerance allowed by Technical Specifications. The setpoints were subsequently reset. <br /><br /> The root cause was determined to be a less than adequate procedure. Corrective actions included a revision to the procedure.
4451991025 | Comanche Peak 1 | 10/29/1991 | 02/19/1992 | 9202250330 | <strong>Component Cooling Water Stop Check Valves Inoperable Due To Less Than Adequate Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>At 1215 on October 29, 1991, the stop check valves (SCV) in the Component Cooling Water lines to the Reactor Coolant Pump thermal barriers were being tested to satisfy inservice testing requirements. During the test, five of the eight SCVs failed to stroke closed. The five SCVs were subsequently manually exercised, after which they operated as designed. On November 6, 1991, two of the SCVs were inspected. A small accumulation of corrosion products between the plug and stem of the valves, and a slight scaling along the bore, were found. Larger accumulations of corrosion products that may have been present were flushed out when the valves were manually exercised. At approximately 0215 on November 23, 1991, all five SCVs were in service and determined to be capable of performing their intended function. <br /><br /> The root cause of this event is believed to be the accumulation of corrosion products in the SCVs due to less than adequate preventive maintenance (PM). Corrective action includes the development of a PM procedure to manually exercise these valves and monitoring of the effectiveness of the PM.
4451991026 | Comanche Peak 1 | 10/30/1991 | 11/29/1991 | 9112030278 | <strong>Pressurizer Safety Valves Discovered To Be Inoperable Using New Test Methodology</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1988, all three Pressurizer Safety Valves (PSV) were tested and adjusted at the Crosby Valve and Gage Company using 200 10 degree Fahrenheit water at the valve inlet, approximating installed plant conditions for PSVs with hot water loop seals. On October 28, 1991, using the state-of-the-art test methodology (saturated steam as the test medium), all three PSV were found to have setpoints one to four percent less than the setpoint tolerance allowed by Technical Specifications (TS). All three PSV setpoints were subsequently reset to TS limits. <br /><br /> The root cause of this event was a less than adequate PSV test methodology/procedure. Corrective action included testing of the PSVs to state-of-the-art methodology and resetting the PSVs to TS limits.
4451991027 | Comanche Peak 1 | 11/07/1991 | 12/09/1991 | 9112110249 | <strong>Source Range Flux Doubling Actuation Caused By Circuit Response During Power Supply Transfer</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1991, Comanche Peak Steam Electric Station Unit 1 was in Mode 6, Refueling, with all fuel removed from the reactor vessel. Operations personnel transferred the power source for a portion of the nuclear instrumentation from the alternate power supply to the normal power supply. Coincident with the switchover, a source range flux doubling signal was initiated, actuating the inadvertent boron dilution mitigation function. The cause of the event was determined to be the nuclear instrumentation circuit response to power supply switchover. Corrective action consists of procedure changes to account for circuit response.
4451991028 | Comanche Peak 1 | 11/12/1991 | 12/12/1991 | 9112200221 | <strong>Missed Refueling Machine Auxiliary Monorail Hoist Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1991, with the reactor refueled and the upper reactor internals installed, the next task was to relatch the control rods. The Refueling Reactor Operator (RO) was to ensure that a load test of the refueling machine auxiliary monorail hoist had been performed per surveillance requirements. At 0130 on November 12, 1991, the Shift Supervisor (SS) and the Refueling RO confirmed that a load test had been previously performed. <br /><br /> At 0300 on November 12, 1991, latching of the control rods began, and was completed at 0615. At 0645 on November 12, 1991, the Refueling Coordinator was reviewing paperwork when he discovered that a load test had not been performed. After further review it was determined that the wrong load test documentation had been reviewed, and that the surveillance requirement had not been met. At 0730 on November 12, 1991, a load test was satisfactorily performed on the refueling machine auxiliary monorail hoist. <br /><br /> The root cause of this event was personnel error. Corrective actions included counseling of the personnel involved.
4451991029 | Comanche Peak 1 | 12/04/1991 | 01/03/1992 | 9201090018 | <strong>Technical Specification Violation Due To Steam Supply Valves To The Turbine Driven Auxiliary Feedwater Pump Being Isolated In Mode 3</strong><br /><i>Abstract:&nbsp;</i>During restoration from Comanche Peak Unit 1's first refueling outage, the handswitch positions for the steam supply valves to the Turbine Driven Auxiliary Feedwater (TDAFW) Pump were left in pull-to-lock after entering Mode 3, thus defeating the automatic function of these valves required by the Technical Specifications (T/S). Operators incorrectly assumed that the T/S 4.0.4 exception for testing the TDAFW Pump until sufficient steam pressure could be produced meant that the proper valve lineup for the TDAFW Pump was not required until the surveillance test was run. The Shift Supervisor discovered the discrepancy approximately two hours after entering Mode 3 while making a Main Control Board walkdown. The switches were immediately placed in the auto position. <br /><br /> The root cause was a cognitive error by Operators assuming that there was a T/S 3.0.4 exception to the Limiting Condition for Operation requiring the TDAFW Pump and associated flow path to be operable when entering Mode 3 from Mode 4. Corrective actions include counselling of personnel by the Operations Manager and training of operators on the requirements of T/S sections 3.0 and 4.0.
4451991030 | Comanche Peak 1 | 12/04/1991 | 01/24/1992 | 9201290094 | <strong>Personnel Error Leading To Mispositioned Residual Heat Removal System Crosstie Valves</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1991, Comanche Peak Steam Electric Station Unit 1 entered Mode 3 with two mispositioned valves in the Emergency Core Cooling System. The event is considered to be a failure to satisfy a Limiting Condition for Operation and a surveillance requirement of the plant's Technical Specification. The cause of the event has been determined to be personnel error leading to the failure to properly position the crosstie valves in the Residual Heat Removal System following filling of a portion of the system. Corrective actions include training and procedure enhancement.
4451991031 | Comanche Peak 1 | 12/06/1991 | 01/06/1992 | 9201090031 | <strong>Containment Ventilation Isolation Due To Overconservative Radiation Monitor Setpoint</strong><br /><i>Abstract:&nbsp;</i>At 0909 on December 6, 1991, the Containment was being vented to decrease containment pressure. At 0918 the Containment Particulate, Iodine, Gaseous (PIG) Monitor Gas Channel spiked into an alarm condition. As a result, a containment ventilation isolation automatically occurred. At 0956 on December 6, 1991, the containment ventilation isolation signal was reset. Containment atmospheric conditions were normal.<br /><br /> The root cause of this event was that the PIG gas channel alarm setpoint was set too low. Furthermore, the administrative procedure establishing the alarm setpoint calculation requirements did not consider alarm setpoint calculation with no detectable noble gas activity in the containment atmosphere. Corrective action included recalculation of the alarm setpoint and a procedure change.
4451991032 | Comanche Peak 1 | 12/06/1991 | 01/24/1992 | 9201290101 | <strong>Procedure Error Leading To Nonconservative Miscalibration Of Power Range Nuclear Instrumentation Channels</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1991, an Instrument and Control technician performed calibration activities on the four power range channels of the nuclear instrumentation system. An error in the work instructions resulted in incomplete calibration of the four channels and nonconservative indication of reactor power. On December 11, following synchronization of the turbine-generator with the grid, the shift supervisor observed a discrepancy between indicated and actual plant conditions based on previous experience with the evolution. Performance of a unit calorimetric confirmed the inconsistency between the indicated reactor power of 9% and actual power of 17%. The cause of the event was a procedure error, and corrective actions include procedure revision and training.
4541991001 | Byron 1, Byron 2 | 03/13/1991 | 04/04/1991 | 9104100054 | <strong>ESF Actuations caused by voltage transients from 345KV line trips During wind/ice storm</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1991 at 1233 with Unit 1 in Mode 1 and Unit 2 in Mode 1 both at 100% power, a voltage transient occurred when 345KV line 0624 tripped open. This voltage transient caused several area and process radiation monitors to go into interlock mode causing various Engineered Safeguards actuations. At 1625, 345KV line 15501 tripped open causing another voltage transient which caused some of the same monitors to interlock again. On March 13 at 0337, line 0624 tripped again with similar results. ESF equipment affected by this event included the OB Fuel Handling Building Charcoal Booster Fan, a Containment Ventilation Isolation Signal for both units, the OB Main Control Room Ventilation System Charcoal Absorber, the CC Surge Tank Vent Valves, and the OA Main Control Room Ventilation System Make-up Fan. <br /><br /> The voltage drops were due to phase to phase line faults on transmission lines 0624 and 15501 caused by "galloping conductors". This condition is associated with the icing and strong winds present at the time. The voltage on the buses suppling the affected monitors dropped below the undervoltage setpoint of the monitor causing them to interlock and actuate their associated ESF equipment. Due to a similar occurrence, the undervoltage setpoint for the radiation monitors was previously lowered as much as the equipment would allow. No further action is planned. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) any event or condition that results in a manual or automatic Engineered Safeguards Actuation.
4541991002 | Byron 1, Byron 2 | 05/05/1991 | 05/23/1991 | 9106050238 | <strong>Engineered Safeguard Feature Actuation due to Lightning Strike on 345KV Transmission Lines</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1991 at 1617 with Unit 1 in Mode 1 at 100% Reactor Power and Unit 2 in Mode 1 at 97% Reactor Power, a voltage transient occurred when 345KV lines 0621 and 0622 momentarily opened during a thunderstorm. Process Radiation Monitors for Main Control Room Outside Air Intake OB and Unit 1 Component Cooling Heat Exchanger Outlet sensed the voltage transient when the voltage on the bus supplying the affected monitors dropped below the monitor undervoltage setpoint. This transferred the monitor to the interlock mode causing an Engineering Safeguard Features (ESF) actuation. The main control room ventilation system automatically transferred to emergency mode. The radiation monitors returned to normal operating condition immediately after the voltage transient passed. The Component Cooling Surge Tank Vent Valve automatically closed. The Seismic Monitoring system also experienced a temporary failure.<br /><br /> Due to a similar occurrence, the undervoltage setpoint for the radiation monitors was previously lowered as much as the equipment would allow. No further action is planned.<br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) any event or condition that results in a manual or automatic Engineered Safeguards Actuation.
4541991003 | Byron 1, Byron 2 | 07/29/1991 | 08/28/1991 | 9109050159 | <strong>Overtemperature Delta Temperature Setpoint Scaling Error due to Design Document Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1991, Byron Station determined that concerns with the scaling of the Overtemperature Delta Temperature (OTDT) reactor trip setpoint, identified in Nuclear Network OE 4707, were applicable. The errors in scaling potentially could prevent the OTDT setpoint from initiating a reactor trip. An initial determination was made, based on the best available information, that the OTDT channels were currently operable and that Byron was in compliance with Technical Specification 2.2.1, Reactor Trip Instrumentation Setpoints.<br /><br /> All OTDT loops were rescaled by August 1, 1991. As a measure to prevent similar occurrences in the future, the scaling program will be reviewed. On August 15, Westinghouse Electric Company completed a review of operability for the period prior to July 29, 1991. This review concluded that under some conditions, the OTDT setpoint would not have initiated a reactor trip when required. Other reactor trips were operable to mitigate design basis events.<br /><br /> The event was caused by a deficiency in a design document that indicated how the OTDT setpoint was to be scaled. <br /><br /> There have been no previous occurrences similar to the OTDT scaling error. However, there has been one other scaling error that was reportable. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(v) and 10CFR50.73(a)(2)(vii).
4541991004 | Byron 1 | 10/16/1991 | 11/15/1991 | 9111270039 | <strong>Inadvertant Safety Injection During Refueling due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1991 at approximately 1304, with Unit 1 in Mode 6 (Refueling) a Nuclear Station Operator (NSO) was attempting to reset a status light for "Auto SI Blocked" following a Train A Engineered Safeguards Features Actuation System (ESFAS) surveillance. Cycling the reactor trip breaker control switch did not reset the light, because the breakers were Out-of-Service. The NSO then reset the block on Low Steamline Pressure SI. Train B SI actuated on Low Steamline Pressure. The 1B Diesel Generator and several other pieces of equipment actuated. Most of the Train B SI equipment was Out-of-Service for the outage and did not actuate. The SI signal was reset and equipment was restored. <br /><br /> The cause of the event was cognitive personnel error. Contributing to this event was a lack of guidance in the procedures on how to clear this light when the surveillance was performed with the reactor trip breakers open as during an outage. The procedure will be revised. Additional training will be provided on operation of the Auto SI Block. <br /><br /> This event is reportable per 10CFR50.73 (a)(2)(iv) any event or condition that resulted in manual or automatic actuation of any Engineered Safeguards Feature.
4541991005 | Byron 1 | 10/27/1991 | 11/20/1991 | 9112030148 | <strong>Mode Change Made With Containment Spray System Inoperable due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1991 at 1655, Hot shutdown (Mode 4) was entered with the Containment Spray System and Emergency Core Cooling System Recirculation Sump Isolation Valves inoperable. Technical Specifications require these operable for a mode change from Cold Shutdown (Mode 5) to Hot Shutdown (Mode 4). This event was caused by failure of Control Room personnel to follow the procedure that controlled the mode change. Shift personnel directed their attention to completing the associated Mode Change Checklist which is a sub-document of the Mode Change procedure. Mode Change Checklists will be revised to specifically reference the governing Mode Change procedure to ensure all appropriate steps are completed prior to changing modes. In addition, shift briefings will be held prior to mode changes to discuss related activities and requirements.<br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(ii) an event on condition that results in being in an unanalyzed condition.
4541991006 | Byron 1, Byron 2 | 11/14/1991 | 12/11/1991 | 9112180086 | <strong>Emergency Diesel Generator Inoperability due to Testing Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>During the NRC Electrical Distribution System Functional Inspection at LaSalle County Nuclear Station, the inspection team determined that the testing of the 4160 Volt Engineered Safety Feature (ESF) Bus Undervoltage Relay Circuits was inadequate. Further evaluation of this condition for Byron Station led to the conclusion that a trip circuit for an ESF Bus Undervoltage and Diesel Generator speed and voltage permissive had not been tested. Both Diesel Generators on both units were declared inoperable on November 14, 1991 at 1505. A temporary waiver of compliance was obtained. Testing of the affected circuits was successfully performed on November 15, 1991. Surveillance procedures will be revised to include this testing.<br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(vii). Any event where a single cause or condition caused two independent trains to become inoperable in a single system designed to: (A) Shutdown the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident.
4551991002 | Byron 2, Byron 1 | 03/11/1991 | 04/10/1991 | 9104220012 | <strong>Containment Emergency Hatch Surveillances Missed due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 03/11/91, it was found that a Technical Specification required Local Leak Rate Test on the Unit 2 Containment Emergency Hatch had not been performed within the allowed time period of 72 hours after an Operating Department test on the hatch. On 11/11/90, 2BVS 6.1.3.a-2, "Primary Containment Type B Local Leak Rate Tests of the Emergency Personnel Airlock Door Gasket Interspaces", was not performed within 72 hours following performance of 2BOS 6.1.3.c-1, "Primary Containment Equipment/Emergency Hatch Personnel Airlock Door Operability Test", as required by Technical Specifications. During the investigation of this event, records showed that there had been a similar occurrence on 10/25/88 on Unit 1. <br /><br /> The cause of both of these missed surveillance events were procedural deficiencies. Containment Emergency Hatch Leakage Rates were later verified to be acceptable on both Units. Therefore, the doors would have performed their design function in the event of a design basis accident. Procedure changes are being made to eliminate the procedural weaknesses that caused these events. <br /><br /> The event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) any operation or condition prohibited by the plant's Technical Specification.
4551991003 | Byron 2 | 10/27/1991 | 11/20/1991 | 9112030162 | <strong>Excessive RCS Leakage due to a Valve Packing Leak</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1991, Unit 2 experienced an reactor coolant system (RCS) leak which was in excess of Technical specification requirements for an unidentified leak. The leak was indicated by a high leak detection alarm for the containment floor drain, and was verified using the 2BOS 4.6.2.1.d-1 RCS leak rate test. The leak was approximately 2 gpm and was believed to be located in the 2C RTD bypass manifold area because the RTD bypass flow low alarm for loop C had annunciated shortly before leakage increased. LCOAR 2BOS 4.6.2-1a was entered at 0122 on 10/27/91.<br /><br /> An initial containment entry was made to investigate the suspected area of leakage outside of the missile barrier. No major contributions to the leak were found. The plant started a power ramp down to support a pending containment entry inside the missile barrier. Shortly after entry into mode 3 (Hot Standby), a containment entry inside the missile barrier indicated that the 2RC029C valve had a packing leak. The valve was isolated and subsequently repaired by Mechanical Maintenance. <br /><br /> This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(A).
4551991004 | Byron 2 | 10/30/1991 | 11/25/1991 | 9112030037 | <strong>Train B Feedwater Isolation Signal Actuation due to Logic Card Failure</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1991 at approximately 0100, with Unit 2 in Mode 4, Hot Shutdown, a spurious Train B Feedwater Isolation signal occurred. Various Feedwater valves that had been open closed. The signal was subsequently reset. The cause of this event was a failure in a Universal Logic Card in the Logic Portion of the Solid State Protection System. The card was replaced and was tested to verify proper operation. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) as any event or condition that resulted in manual or automatic actuation of any Engineered Safeguards Feature.
4551991005 | Byron 2 | 11/07/1991 | 12/09/1991 | 9112130056 | <strong>Reactor Trip on Low-2 Steam Generator Level During Startup due to D-5 Steam Generator Level Control</strong><br /><i>Abstract:&nbsp;</i>At 0357, on 11/07/91, after Unit 2 startup and during preparation for the turbine roll, a Low-2 Steam Generator (S/G) level on the 2A S/G was received which initiated a Reactor Trip. All safeguard actuation features functioned as designed.<br /><br /> The Low-2 level in the Steam Generator was the result of difficulty in controlling the Westinghouse D-5 S/G level at low power and due to leak by of the main Feedwater Regulating Valve for the 2A Steam Generator. The level instrument taps in the Steam Generator are being moved during the next refueling outage to reduce this level instability. The Main Feedwater Regulatory valve was adjusted before the next startup. A revision will be made to the startup procedure to verify position of this valve for each Steam Generator. <br /><br /> This event is reportable in accordance with 10CFR50.73 (a)(2)(iv), any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature.
4561991001 | Braidwood 1 | 01/21/1991 | 03/20/1991 | 9104020286 | <strong>1B Containment Spray Pump Inoperable Due to Use of Non Qualified Power Supply Breaker</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1990 the 1B Containment Spray (CS) pump was placed in an Out-of-Service condition for maintenance. In accordance with Technical Specifications, a seven day time clock started. The 1B CS pump power supply breaker was removed for inspection and found damaged. A spare breaker was used to replace the defective breaker. On December 21, the 1B CS pump was started and declared operable. On January 21, 1991 personnel suspected an unqualified breaker had been used. Upon confirmation that a seismically unqualified breaker had been installed, it was determined that the 1B CS pump had been technically inoperable. The Technical Specification time clock actually expired on December 25, 1990. The cause was an incorrect conclusion that any power supply breaker is qualified. The breaker was removed and replaced. This event will be reviewed with all operators. The non-1E breakers will be labeled to prevent recurrence. Additional training will be provided to explain proper breaker usage and the design characteristics of class 1E breakers. There have been no previous occurences.
4561991002 | Braidwood 1 | 02/26/1991 | 03/28/1991 | 9104020280 | <strong>Failure to Restore Service Water Radiation Monitors caused by Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1991, system lineups for Unit 1 Containment Integrated Leakage Rate Test were in progress. All Unit 1 containment penetrations not required to support unit operation were isolated. The Service Water penetration would be isolated by closing valves in the flowpath that provides cooling water to heat exchangers inside containment. After closing the valves, radiation monitors that obtain their suction from the containment return piping lost their sample flows and were declared inoperable. These monitors analyze for radioactivity and operation is required by Technical Specifications. Containment pressurization was completed on February 21. On February 23, the valves were reopened. This reestablished service water flow through containment and the radiation monitors were now required to be in operation. On February 26, operators realized that the radiation monitors were not in service. The monitors were restarted. The cause was inadequate technical review of radiation monitor operability and procedural deficiencies. The applicable procedures will be revised. The details of this event will be discussed in licensed operator training. There has been one previous occurrence. Previous corrective actions are not applicable.
4561991003 | Braidwood 1 | 03/12/1991 | 04/05/1991 | 9104090055 | <strong>Control Room Ventilation to Emergency Mode on a Loss of Power to Outside Intake Radiation Monitor ORT-PR034</strong><br /><i>Abstract:&nbsp;</i>At 2022 on March 12, 1991, the Main Control Room Ventilation system shifted to the emergency mode of operation. The actuation was caused by a momentary loss of voltage to control Room Outside Intake Radiation Monitor ORT-PR034. The voltage drop occurred when 345 Kilovolt Line 0104, an offsite power distribution circuit to Braidwood Station, de-energized due to outside weather conditions. ORT-PR034 automatically restarted and returned to normal operation. The cause of the event was a momentary fluctuation in voltage available to the monitor. When Line 0104 tripped, it resulted in a disturbance to the onsite power distribution system. The cause of Line 0104 tripping was attributed to severe weather conditions in the area. Ice buildup of the Commonwealth Edison distribution system increased the weight of the power lines and reduced the phase-to-phase clearance required. Protective relays actuated to protect the integrity of the offsite power supply distribution network. Within seconds, the monitor regained the required voltage and returned to its pre-event condition. The Main Control Room Ventilation system was restored to a normal alignment. The weather conditions in the vicinity of Braidwood Station improved and the grid returned to a normal condition. There have been previous occurrences of ESF actuations caused by voltage transients. Previous corrective actions are not applicable to this event.
4561991004 | Braidwood 1 | 03/19/1991 | 04/17/1991 | 9104180325 | <strong>Automatic Isolation Of Radwaste Release Flowpath Defeated By Personnel Error During Liquid Release</strong><br /><i>Abstract:&nbsp;</i>Liquid Release Tank Form BwOP WX-500-1T1 was initiated by the Radwaste Supervisor (RWS) to discharge the contents of release tank 0WX01T. An operability determination of radiation monitors 0RE-PR001 (Liquid Radwaste Effluent) and 0RE-PR010 (Station Blowdown) was performed. Monitor 0RE-PR001 was operable. Monitor 0RE-PR010 had previously been declared inoperable. The appropriate Technical Specification action statement was in effect. Samples of release tank 0WX01T were obtained and analyzed to calculate alarm setpoints for 0RE-PR001. The purpose of 0RE-PR001 is to determine the radioactivity level in the release tank effluent. If the alarm setpoints are exceeded, then the monitor will generate a signal to close the release tank outlet valve. On March 19, 1991, sample analysis and monitor setpoint calculations had been completed. The setpoints for the monitor were adjusted. The RWS directed the removal of relay block K1 for monitor 0RE-PR001. This action is only performed when the monitor is inoperable. The release of tank 0WX01T was started. The RWS realized that the relay block K1 for monitor 0RE-PR001 had been improperly removed. The release was terminated. The cause of the event was cognitive personnel error. Monitor 0RE-PR001 was operable and the relay block K1 should not have been removed. The radiation monitor that had previously been declared inoperable was 0RE-PR010, not PR001. The RWS confused these monitors and mistakenly took the actions required during the inoperability of 0RE-PR001. Approximately 16860 gallons of effluent were released. The tank capacity is 33758 gallons. The relay block K1 for monitor 0REPR001 was reinstalled. The liquid release form will be revised. There have been no previous occurrences.
4561991005 | Braidwood 1 | 03/26/1991 | 04/24/1991 | 9104290190 | <strong>Control Room Ventilation to Emergency Mode on a Loss of Power to Outside Intake Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>At 0343 on March 26, 1991, the Main Control Room Ventilation system shifted to the emergency mode of operation. The actuation was caused by a momentary loss of voltage to Control Room Outside Intake Radiation Monitors ORT-PR033 and ORT-PR034. The voltage drop was caused by a lightning strike in the switchyard area. ORT-PR033 and ORT-PR034 automatically restarted and returned to normal operation. The cause of the event was a momentary fluctuation in voltage available to the monitor. When lightning struck the switchyard, it resulted in a disturbance to the onsite power distribution system. Within seconds, the monitors regained the required voltage and returned to their pre-event condition. The Main Control Room Ventilation System was restored to a normal alignment. There have been previous occurrences of Engineered Safety Feature (ESF) actuations caused by lightning. To reduce the number of ESF actuations caused by lightning, the lightning protection system is presently being modified. The grounding system is being improved by the installation of additional ground conductors. A lightning dissipation system is being installed to protect the containment buildings and the auxiliary building ventilation stacks. These locations were chosen because they are the tallest structures at Braidwood Station and the most likely to be struck by lightning. This system has been installed at other nuclear plants and is scheduled to be in service by June 1991.
4561991006 | Braidwood 1 | 04/27/1991 | 05/24/1991 | 9106030093 | <strong>ESF Actuation During Surveillance Testing Caused by Lifted Lead on Undervoltage Relay</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in Mode 5 (Cold Shutdown) with preparations to enter Mode 4 (Hot Shutdown) in progress. On April 27, 1991 surveillance testing had been performed for 4160 Volt Bus 141 and relay 462-B141 failed to operate correctly. The relay design purpose is to start a timer when a degraded voltage condition is detected. To repair the relay, the electrical schematic diagram was reviewed and relay 462-B141 was isolated. At 2011, the 1A Diesel Generator (DG) was started for surveillance testing. At 2204, the 1A DG output breaker was opened after completion of surveillance testing. The System Auxiliary Transformer (SAT) main feed breaker also opened and deenergized Bus 141. The 1A DG output breaker automatically closed but immediately reopened. Bus 141 remained deenergized. This resulted in an unexpected trip of the 1A Residual Heat (RH) and 1A Component Cooling (CC) pumps. An anti-pumping interlock prevented further closure attempts of the 1A DG output breaker. The deenergization of Bus 141 resulted in the generation of a Containment Ventilation Isolation Signal because power was removed to the Containment Fuel Handling Incident Radiation Monitor. At 2210, the 1B RH pump was started and placed in the shutdown cooling mode. At 2332, the anti-pump interlock was reset and the 1A DG output breaker immediately closed to energize Bus 141. The relay had been properly isolated. However, a positive potential was still applied to the disconnected portion of the circuit and allowed for a 125Vdc potential to exist at the 1A DG output breaker contact. When the output breaker was opened, the contact closed and completed the circuit to the load shed relays which tripped the loads on Bus 141. The current flowpath was not readily apparent during the review of the electrical schematic diagram. Relay 462-B141 was replaced and surveillance testing was satisfactorily completed. There have been no previous occurrences.
4561991007 | Braidwood 1 | 07/17/1991 | 08/14/1991 | 9108160278 | <strong>Rod Control System Failure causes Shutdown Bank Control Rods to be in a Condition Prohibited by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1991 surveillance 1BwOS 1.3.1.2-1 "Unit One Movable Control Assemblies Monthly Surveillance" was started to verify operability of each control rod assembly. At this time, all Shutdown (S/D) Banks (A,B,C,D and E) were fully withdrawn. S/D Banks A and B have 8 control rods and are separated into 2 groups with 4 rods in each group. During testing of S/D Bank A, problems were encountered with the control rods in group 1. No rod motion was indicated for two of the Group 1 rods. The other two rods in Group 1 were not fully withdrawn. At 0419, Technical Specification (TS) 3.0.3 was entered. This started a 6 hour time clock to enter Mode 3 (Hot Standby). At 0645 a unit shutdown commenced. Since this shutdown was required by TS, an Unusual Event was declared in accordance with the Braidwood Station Emergency Plan. Troubleshooting revealed that a malfunctioning circuit card was not providing proper current to the control rod drive coils. The power reduction was stopped at 0926. At 0940, the circuit cards were replaced. At 0943, S/D Bank A Group 1 rods were realigned. The rods were satisfactorily tested and were declared operable at 1002. The Unusual Event classification was terminated at 1003. The cause of the event was component failure. A defective transistor in the firing circuit control card was not generating the proper frequency.
4561991008 | Braidwood 1, Braidwood 2 | 07/29/1991 | 08/28/1991 | 9109050064 | <strong>Scaling Deficiency of Over Temperature Delta Temperature Due to Preservice Design Error</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1991 Braidwood Station was notified of a potential operablility problem with the Overtemperature Delta T (OTDT) Reactor Protection (RP) System setpoint. Duke Power Co. (DPC) had sent information, via the INPO Nuclear Network (OE 4707), regarding a problem with the OTDT setpoints at McGuire and Catawba Nuclear Stations. The setpoint for OTDT is dependent on three variables: 1) Reactor Coolant System (RCS) average temperature (T-Avg), 2) Pressurizer pressure, and 3) Axial Flux Difference (AFD). The setpoint provides fuel protection to prevent Departure from Nucleate Boiling (DNB) over a range of RCS temperatures (530-630 Deg F) and pressures (1700-2500 psig). The setpoint is calculated by a mathematical equation. The process engineering units are converted into an equivalent voltage level by the Westinghouse 7300 Process and Instrumention control system. This conversion is known as scaling. During the review of the Nuclear Network message from DPC, it was determined that the OTDT calculation was not being applied over the full required temperature range. As T-Avg increases, the OTDT reactor trip setpoint is reduced in accordance with the mathematical equation. However, an incorrect gain value assigned to a process card in the OTDT circuitry limited the upper range of T-Avg to 597 Deg F. Action was taken to properly scale the OTDT trips for all conditions for both units. On August 1, 1991 the OTDT loops were rescaled by replacement of resistors on summing card TY-0411L, and reducing the gain on lead lag card TY-0412A. On August 15, 1991 after further evaluation, Commonwealth Edison Co. was notified that for certain low-power transient conditions, the OTDT trip would not occur at the time assumed in the analysis. At this time, it was determined that the event would be reportable. The root cause of the event was a preservice design deficiency. The Precautions, Limitations and Setpoints (PLS) manual contained the necessary information for scaling OTDT. The specified PLS gain for lead/lag card TY-0412A was too high. The end result was that the loop output reached its limit prior to the input (T-Avg) being at its upper limit.
4561991009 | Braidwood 1, Braidwood 2 | 08/27/1991 | 09/25/1991 | 9110010289 | <strong>Gas Decay Tank Sample Not Obtained Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1991, a Unit 2 End-of-Life (EOL) startup had just been completed and extra water would be needed to dilute the Reactor Coolant System (RCS) boron concentration. The dilution expelled a large volume of borated water from the RCS. The expelled water was sent to the Chemical Volume Holdup Tank (HUT) via RCS letdown. The HUT is supplied with cover gas from the Waste Gas System. As the HUT filled, the cover gas was displaced and sent to the waste gas vent header. The displaced cover gas was compressed and sent to the On-Line gas decay tank. In accordance with Technical Specification requirements, each tank is limited to less than 50,000 Curies of noble gases. This activity level is required to be calculated at least once per 24 hours when radioactive materials are being added to the On-Line gas decay tank. To determine waste gas tank activity, the Chemistry Dept. performs an isotopic analysis. On August 7, 1991 at 2200, the "C" gas decay tank was placed On-Line. On August 8, 1991 at 0510, the "C" gas decay tank was filled and an automatic transfer placed the "A" gas decay tank On-Line. At 0715, isotopic samples of the "A" gas decay tank were obtained to determine the tank Curie content. On August 27, 1991 it was determined that the required Technical Specification surveillance for the "C" gas decay tank had not been performed. The Chemistry Dept. sampled and analyzed the "C" gas decay tank. The activity level in the tank was 0.51 Curies. The cause of the event was a procedural deficiency. Applicable procedure revisions will be made and the Chemistry Dept. will be notified when the status of a waste gas decay tank is changed.
4561991010 | Braidwood 1 | 09/29/1991 | 10/10/1991 | 9110250037 | <strong>Containment Ventilation Isolation Signal Due to Spurious Spike from 1RE-AR012 as a Result of Component Failure</strong><br /><i>Abstract:&nbsp;</i>At 1111 on September 29, 1991 the Containment Fuel Handling Incident Area Radiation Monitor 1RT-AR012 momentarily went into high high alarm and interlock actuation, due to sudden spiking. This initiated a Train B Containment Ventilation Isolation signal. No components repositioned as all valves were secured in the closed position. On September 23, prior to this actuation, the monitor was identified as showing early signs of instrument drift. It was concluded that detector replacement was required. On October 1, 1991 the detector for 1RT-AR012 was replaced. The cause of the event was component failure. The defective detector was generating spurious high radiation spikes which resulted in the monitor initiating a containment ventilation isolation signal. The detector for this monitor is normally replaced on an 18 month frequency in accordance with the environmental qualification program. The failed detector in this event had been in service since April of 1991. This detector has been returned to the vendor for failure analysis.
4561991011 | Braidwood 1, Braidwood 2 | 10/30/1991 | 11/25/1991 | 9112020218 | <strong>Inadequate Surveillance Review results in Control Room Ventilation System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991 surveillance BwVS 7.6.e-1 "Control Room Ventilation Emergency Mode Test" was started. The surveillance is performed to verify that the Control Room Ventilation system operates in accordance with Technical Specification requirements. The makeup fan was started and flow was aligned through the charcoal adsorber. The makeup flowrate is limited to 5400 - 6600 cubic feet per minute (cfm). To calculate the flowrate, velocity pressures were used in a formula. The flowrate obtained was 6816 cfm. At two locations adjacent to the control row. the differential pressures were 0.10 inch Water Gauge (W.G.) and 0.12 inch W.G., below the required value of 0.125 inch W.G. On October 4, 1991 testing was completed and the surveillance was routed for a technical review. No errors were identified during the initial review and the surveillance was recorded as being satisfactory. On October 30, 1991 the surveillance was reviewed by the Assistant Technical Staff Supervisor (ATSS). The ATSS noticed that the makeup fan flowrate was above 6600 cfm and the control row differential pressure was below 0.125 inch W.G. at two locations. The ATSS recognized that the surveillance had not met the acceptance criteria. The system was then declared inoperable. The cause of the event was personnel error. An inadequate technical review of the completed surveillance failed to identify that the values were outside the limits specified in the surveillance acceptance criteria. The surveillance was then reperformed satisfactorily and the system was declared operable.
4561991013 | Braidwood 1, Braidwood 2 | 11/14/1991 | 12/12/1991 | 9112190112 | <strong>Untested Relay Contacts Cause Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>During a NRC Electrical Distribution System Functional Inspection (EDSFI) at LaSalle Station, a testing deficiency was identified on some relays associated with the 4160 Volt Safety-Related Busses. On November 14, 1991 it was recognized that some relay contacts associated with the ESF 4160 Volt Busses had also not been tested at Braidwood Station. Surveillance Requirement 4.8.1.1.2.f.4.a requires verification of de-energization of the Engineered Safeguard Features (ESF) busses and load shedding from the ESF busses. The existing surveillance procedure did not verify that all breakers on the ESF Buss would open. A failure of these breakers to open during a Undervoltage condition would prevent automatic closure of the Diesel Generator (DG) output breaker. At 1510 this condition was considered unacceptable and all DG's were declared inoperable. A Temporary Waiver of Compliance (TWC) was requested to delay, for 48 hours, the actions required by the applicable Technical Specifications. At 1845 the NRC approved the TWC request. On November 15, 1991 the 2A DG and 1A DG were declared operable after testing was satisfactorily completed. On November 16, 1991 testing of the 1B and 2B DG was satisfactorily completed. The cause of the event was a surveillance procedural deficiency. The applicable surveillance testing procedures will be revised.
4571991001 | Braidwood 2 | 03/08/1991 | 04/05/1991 | 9104080298 | <strong>Containment Ventilation Isolation Signal Due to Spurious Spiking from 2RE-AR012 as a Result of Component Failure</strong><br /><i>Abstract:&nbsp;</i>At 2239 on March 8, 1991 the Containment Fuel Handling Incident Area Radiation Monitor 2RT-AR012 momentarily went into high alarm and interlock actuation, due to sudden spiking. This initiated a Train B Containment Ventilation Isolation signal. No components repositioned as all valves were secured in the closed position. At 2216 on March 9, a second spike occurred on radiation monitor 2RT-AR012 which also resulted in a ventilation isolation signal. On March 6, prior to these actuations, the monitor was identified as slowly drifting. It was concluded that detector replacement was required. On March 11, 1991 the detector for radiation monitor 2RT-AR012 was replaced. The cause of this event was component failure. The faulty detector was creating spurious high radiation spikes which resulted in the monitor initiating the containment ventilation isolation signals. The detector for this monitor is normally replaced on an 18 month frequency in accordance with the Environmental Qualification program. The failed detector in this event had been in service since August of 1990. This detector has been returned to the vendor for failure analysis.
4571991002 | Braidwood 2 | 05/10/1991 | 06/07/1991 | 9106130226 | <strong>Reactor Shutdown caused by Excessive Containment Purse Valve Leakage Discovered During Local Leakage Rate Testing</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1991 local leakage rate test surveillance BwVS 6.1.7.3-1 was started by a System Test Engineer (STE) to verify that the measured leakage rate of the 48 inch containment purge supply containment penetration (P-97) was less than 23.15 Standard Cubic Feet per Hour (SCFH) when pressurized to at least 44.4 psig. P-97 consists of two containment isolation valves in series; 2VQ001A and 2VQ001B. A Leak Rate Monitor (LRM) test rig was attached to the P-97 test connection. The STE started P-97 pressurization by opening an air supply valve. At 2130, it was noted that the highest pressure achieved for P-97 using the LRM test rig was only 33 psig. The LRM was bypassed to directly pressurize P-97 to 46 psig. When the air supply was isolated, the pressure in P-97 decreased to 21 psig in 14 minutes and confirmed that valve leakage was higher than the Technical Specification limit. At 2200 on May 11, 1991 a unit shutdown commenced. Since this shutdown was required by Technical Specifications, an Unusual Event was declared. At 0322 on May 12, 1991 a reactor trip was caused by a spike on Source Range Channel M-31. At 0530 on May 13, 1991 the Unusual Event was terminated when the unit entered Mode 5 (Cold Shutdown). The cause of the seal leakage was attributed to seal degradation. The resilient material seals were replaced for both valves. BwVS 6.1.7.3-1 was satisfactorily performed with a leakage rate of 5.11 SCFH. There have been no previous occurrences.
4571991003 | Braidwood 2 | 08/01/1991 | 08/30/1991 | 9109050166 | <strong>Reactor Trip Caused by Rod Control System Failure</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was operating at 88% reactor power in a coast down mode at the end of core life. On August 1, 1991 at 2354 the unit operator attempted to move the control rods in Bank D to control Reactor Coolant System temperature. A Rod Drive (RD) System failure released numerous control rods and allowed them to fall into the core. A reactor trip signal was generated because the Nuclear Instrumentation (NR) System detected a rapid power decrease. Control Room personnel immediately recognized and responded to the reactor trip. The unit was stabilized with normal post-trip response conditions. During RD troubleshooting, the logic cabinet was analyzed to determine the amount of electric current being supplied to the stationary and movable grippers. The 2BD slave cycler was intermittently giving erratic current demand orders. The rods dropped because the stationary gripper was unable to hold the rods before the moving gripper unlatched. The cause of the 2BD slave cycler failure was a defective binary counter. The counter is required to properly sequence the energization/de-energization of the movable and stationary grippers during rod notion. The 2BD slave cycler binary counter circuit card was replaced. The logic cabinet slave cycler circuits were tested and analyzed for proper operation. A complete functional check of the RD system identified no further deficiencys. To improve RD system performance, a long-term corrective action plan was developed. An evaluation of the effects of high temperatures on the RD system is in progress.
4571991004 | Braidwood 2 | 08/27/1991 | 09/25/1991 | 9110010299 | <strong>Personnel Error Results in Late Performance of Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1991 surveillance 2BwOS 4.6.2.1.d-1, "Unit 2 Reactor Coolant System Water Inventory Balance," was completed at 1515. The surveillance, required by Technical Specifications, calculates how much water inventory is being removed from the Reactor Coolant System (RCS). The surveillance is performed at least once per 72 hours during Modes 1-4. The completed surveillance was reviewed by the Shift Supervisor (SS). However, the SS forgot to record the completed surveillance in the General Surveillance (GSRV) logbook. This logbook is used to track surveillance completion and to ensure that surveillances are performed within their required time interval. On August 25, 1991 a review of the GSRV logbook noted that the date of the last performance of 2BwOS 4.6.2.1.d-1 was missing. An incorrect date, August 24, 1991 was used to update the GSRV logbook. On August 26, 1991 the date from the GSRV logbook was used to update a surveillance tracking and scheduling program. This program is used to provide a surveillance schedule for the next day. A new surveillance schedule listed 2BWOS 4.6.2.1.d-1 with a due date of August 27, 1991. On August 27, 1991 the surveillance was completed satisfactorily. At this time, the Unit 2 logbook was reviewed and it was determined that the allowed Technical Specification surveillance frequency had been exceeded. The cause of the event was personnel error. The GSRV logbook will be updated using the date directly from the surveillance cover sheet. This action will be independently verified by a second review of the GSRV logbook and verification of the correct surveillance performance date.
4571991005 | Braidwood 2 | 08/31/1991 | 09/30/1991 | 9110080282 | <strong>SAMPLE REQUIRED BY TECHNICAL SPECIFICATIONS OBTAINED LATE DUE TO PERSONNEL ERROR</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 067%. ON AUGUST 26, 1991 DECAY TANK NOBLE GAS ACTIVITY PROCESS RADIATION MONITOR ORE-PR002J WAS DECLARED INOPERABLE. TO ENSURE COMPLETION OF TECHNICAL SPECIFICATION ACTION REQUIREMENTS, LIMITING CONDITION FOR OPERATION ACTION REQUIREMENT (LCOAR) OBWOS 3.3.10-1A WAS STARTED. ON AUGUST 27, 1991 ESSENTIAL SERVICE WATER CONTAINMENT OUTLET PROCESS RADIATION MONITOR 2RE-PR002J WAS DECLARED INOPERABLE. LCOAR OBWOS 3.3.9-1A WAS STARTED. SAMPLES OF THE SERVICE WATER (SX) DISCHARGE FLOWPATH FROM CONTAINMENT WERE REQUIRED EVERY 12 HOURS. ON AUGUST 31, 1991 ORE-PR002J WAS DECLARED OPERABLE AT 0630. A CHEMISTRY TECHNICIAN (CT) WAS NOTIFIED THAT THE ACTION REQUIREMENTS FOR THE 'PR 2J' RADIATION MONITOR WERE NO LONGER REQUIRED. A CHEMISTRY ENGINEERING ASSISTANT (EA) WAS TOLD BY THE CT TO CLOSE OUT THE LCOAR FOR THE 'PR 2J' RADIATION MONITOR. THE EA DETERMINED THAT NO MORE SAMPLING WOULD BE REQUIRED FOR THE LCOAR ASSOCIATED WITH 2RE-PR002J. AFTER FINDING A DATA SHEET THAT SHOULD HAVE BEEN INCLUDED IN THE LCOAR FOR 2RE-PR002J, IT WAS DETERMINED THAT THE SAMPLE DATA SHEETS FOR 2RE-PR002J HAD BEEN ATTACHED TO THE LCOAR FOR ORE-PR002J. A CT WAS REQUESTED TO IMMEDIATELY OBTAIN A SAMPLE. HOWEVER, THE 12 HOUR SAMPLE ANALYSIS FREQUENCY REQUIRED BY TECHNICAL SPECIFICATIONS WAS EXCEEDED BY 1 HOUR AND 20 MINUTES.
4571991006 | Braidwood 2 | 12/01/1991 | 12/23/1991 | 9201020129 | <strong>Generator Trip Caused by Spurious Actuation of Neutral Ground Relay</strong><br /><i>Abstract:&nbsp;</i>At 1738 on December 1, 1991 a Generator Neutral Ground Overcurrent backup protective relay actuated and tripped the Unit 2 Main Generator. A turbine and reactor trip followed as designed. Operators performed applicable steps of the reactor trip response procedures and stablized the plant. The generator trip was caused by the neutral ground backup relay. The design purpose of this relay is to actuate when an unbalanced voltage condition exists between the three phases of the generator. An oscillograph, used to record voltage applied across the neutral resistor, indicated that no fault had existed on the generator. Additionally, a megger reading of the generator confirmed that no internal fault existed. With no generator fault, the cause of the trip was in the potential transformer circuitry. Upon completion of troubleshooting, the cause could not be determined. Precautionary measures were taken to prevent an intermittent potential fuse failure from causing another generator trip. <br /><br /> The potential transformer fuses were replaced and the suspect circuitry will be monitored.
4581991001 | River Bend | 02/12/1991 | 03/14/1991 | 9103260056 | <strong>Use of Improper Control Room Filter Initiation Signal due to Discrepancies between Logic Diagrams</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1991, a discrepancy was discovered between the logic diagrams (LSKs) and elementary diagrams (ESKs) for the initiation signal of the main control room ventilation (HVC) charcoal filtration system. The initiation signal configuration to actuate at reactor water level 1 instead of level 2 rendered the HVC charcoal filters unable to perform their design function to mitigate the effects of a main steam line break (MSLB) outside of the containment. Immediate action was taken to start one train of HVC filtration to maintain the plant within the control room habitability analysis. GSU's investigation of this event concludes the following: <br /><br /> 1) Additional discrepancies were identified; however, the safety impact of this event was limited to the HVC filter initiation signal. <br /><br /> 2) Following modification of the HVC initiation signal to actuate on level 2, operation of RBS without compensatory measures has been analyzed and found to be acceptable. <br /><br /> 3) The analysis of plant operating history indicates that this condition did not pose a significant hazard to control room personnel. <br /><br /> Therefore, this event did not adversely affect plant safety or the health and safety of the public.
4581991002 | River Bend | 02/16/1991 | 07/12/1991 | 9107190162 | <strong>Isolation of Reactor Water Sample Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 1059 on 2-16-91 with the reactor in Operational Condition 1 (Power Operation), an engineered safety feature (ESF) actuation occurred when reactor water sample containment isolation valve, 1B33*AOVF019 automatically isolated. At the time of discovery, instrumentation and control (I&C) technicians were performing a monthly channel functional surveillance test STP-051-4510 "Reactor Protection/Residual Heat Removal (RPS/RHR) - Reactor Vessel Steam Dome Pressure High". The ESF actuation was caused by the failure of fuse 1B21H-F76B which de-energized the isolation logic to allow 1B33*AOVF019 to close. The fuse was promptly replaced and the valve was reopened.<br /><br /> Immediate corrective action consisted of replacing the fuse, resetting the isolation logic, and reopening the reactor water sample valve. As a result of the repeated occurrences of fuse 1B21H-F076B failing for undetermined reasons, all associated STPs that test this circuit will be revised to require valve 1B33*AOVF019 to be isolated prior to performing surveillance testing. The revision effort is in progress and all of the STPs will be revised by September 2, 1991.<br /><br /> Isolation of the containment isolation valve placed it in its safe position. Therefore, there was no adverse impact on the safe operation of the plant or the health and safety of the public as a result of this event.
4581991003 | River Bend | 03/22/1991 | 03/16/1993 | 9303190249 | <strong>Damper Isolations And Automatic Swap Of Divisional Control Building Ventilation/Chiller Trains Due To Inadequate Work Plan</strong><br /><i>Abstract:&nbsp;</i>At 1055 on 3/22/91, during maintenance on the Division II control building local air intake radiation monitor 1RMS*RE13B, the Division II control power circuit was de-energized. This resulted in the de-energization of the Division II charcoal filter train suction dampers 1HVC*AOD19D and 1HVC*AOD19F, and isolation of the air operated dampers (AODs) to the Division II air handling units, 1HVC*AOD6B and 1HVC*AOD8B. Note that dampers 19D and 19F were closed at the time of the event. The isolations resulted in a trip of the Division II control building ventilation system/chiller and automatic swap to the Division I ventilation system/chiller. to document the engineered safety feature (ESF) actuations described above. The event occurred during the implementation of Modification Request (MR) 90-0071. This MR specified that the RM-80 mother board was to be removed from 1RMS*RE13B. The root cause of this event is that the maintenance planner overlooked the 115 VAC control power to the RM-80 mother board and thus, the potential for the ESF actuations. <br /><br /> This event concerned the engineering/maintenance planning interface and responsibility. As previously reported in LER 90-033, Revision 3, a task force evaluation of this issue was performed and the task force recommendations have been approved by management and are being implemented.
4581991004 | River Bend | 03/21/1991 | 04/19/1991 | 9104260116 | <strong>Isolation Of The RCIC Turbine Main Steam Supply Line Outboard Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>At 1420 on March 21, 1991, with the reactor in Operational Condition 1 (Power Operation) and the reactor core isolation cooling (RCIC) system isolated for maintenance, an unplanned engineered safety feature (ESP) actuation occurred when the RCIC turbine main steam supply line outboard containment isolation valve, 1E51*MOVF064, isolated. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) since this event constitutes an ESF actuation.<br /><br /> It is postulated that after the RCIC system was isolated for maintenance by shutting 1E51*MOVF063, cooling in the steam supply line caused steam to condense and flow into the variable leg instrument line which resulted in negative differential pressure surges in flow transmitter 1E51*PDTN084A. The negative trip setpoint of the trip unit was reached which caused the ESF actuation. This is the probable root cause of the event. A caution has been added to RCIC system operating procedures that both RCIC turbine main steam supply line containment isolation valves 1E51*MOVF063 and 1E51*MOVF064 should be isolated when the system is removed from service for maintenance to prevent unexpected ESF actuations. <br /><br /> The ESF actuation occurred per design. The RCIC system was inoperable and isolated for maintenance per the action statement of Technical Specification 3.7.3. Therefore, the health and safety of the public was not adversely affected.
4581991005 | River Bend | 03/22/1991 | 04/22/1991 | 9104290301 | <strong>Design Deficiencies In Fire Doors</strong><br /><i>Abstract:&nbsp;</i>On 3/22/91, with the plant at 100 percent power in Operational Condition 1 (Power Operation), a deficient fire door was discovered during a quality assurance audit. The design configuration of door CB-70-25 did not assure the proper closing sequence between the two leaves. Therefore, the door cannot be considered to have been a qualified fire barrier since plant startup, and was inoperable contrary to Technical Specification 3.7.7. This report is submitted pursuant to 10CFR50.73 (a) (2) (i) (B) as operation prohibited by the Technical Specifications. <br /><br /> Upon discovery of the condition, the fire door was declared inoperable and added to the hourly fire watch list. The inactive leaf of door CB-70-25 was closed and the top and bottom latch bolts were engaged. This configuration ensures operability of the door and ensures conformance to applicable NFPA code requirements. The corrective actions specified for door CB-70-25 were also implemented for door CB-98-32. <br /><br /> The areas on both sides of each door, CB-70-25 and CB-98-32, are provided with automatic sprinkler systems and automatic fire detection systems. In the event of a fire from transient combustible sources, these systems would automatically actuate to contain the fire and notify the control room of the conditions. Therefore, the health and safety of the public was not adversely affected by this event.
4581991006 | River Bend | 04/01/1991 | 04/29/1991 | 9105060098 | <strong>Personnel Failure To Replace High Radiation Area Barrier</strong><br /><i>Abstract:&nbsp;</i>At 1530 hours on 4/1/91 with the reactor in Operational Condition 1 (Power Operation) an operations engineering cooperative student, having about 3 months of experience, failed to replace a high radiation area (HRA) rope barricade. The rope was located at the doorway between the residual heat removal (RHR) 'A' pump room and the low pressure core spray (LPCS) pump room. The event occurred during valve operability surveillance testing. Technical Specification (TS) 6.12.1 requires that high radiation areas be barricaded. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical Specifications. <br /><br /> As an interim measure, a standing order was issued to all operations personnel to require permission of the Shift Supervisor/Control Operating Foreman and escort by radiation protection personnel prior to entry into high radiation areas and very high radiation areas. These requirements are in addition to those in the Technical Specifications. <br /><br /> During the period that the barrier was down, no unauthorized personnel entered the HRA. Therefore, this event did not have an adverse impact on the safe operation of River Bend Station or the health and safety of the public.
4581991007 | River Bend | 04/04/1991 | 05/06/1991 | 9105140003 | <strong>Indeterminate Equipment Qualification Status of Resistance Temperature Detectors in the Standby Gas Treatment System</strong><br /><i>Abstract:&nbsp;</i>On 4/4/91, with the reactor in Operational Condition 1 (Power Operation), it was determined that the equipment qualification status of Pyco resistance temperature detectors (RTDs) installed in the standby gas treatment system (SGTS) was indeterminate. It was later confirmed that the installation configuration of the RTDs was not qualified. Since this condition existed from the time of initial installation, the SGTS was potentially inoperable for a period of time in excess of the action statement of Technical Specification 3.6.5.4. Therefore, this event is reportable pursuant to 10CFR50.73 (a) (2) (i) (b) as operation prohibited by the Technical Specifications. <br /><br /> Inspection and replacement of SGTS RTDs was initiated under Modification Request (MR) 91-0035. This MR was initiated to replace Pyco RTD Model 122-4030 with Pyco RTD Model 122-3046 which is a sealed design not requiring a thermowell. These new RTDs are seismically and environmentally qualified. <br /><br /> To estimate the safety significance of SGTS operability, a probabilistic safety assessment (PSA) was performed using ambient relative humidity values as a calculation input. The probability that the SGTS would not adequately mitigate the effects of a core damage event was calculated to be 5.36E-6 per year. This result is judged to be acceptable in view of the associated consequences of the accident scenario. Therefore, this event did not adversely affect the health and safety of the public.
4581991008 | River Bend | 04/15/1991 | 11/30/1993 | 9312130411 | <strong>Fire Hazards Analysis Deficiencies Including Lack Of Fire Wrap/Inadequate Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>At 1345 hours on 4/15/91, with the reactor at full power in Operational Condition 1, it was discovered that electrical cables located in fire area ET-2, which may cause spurious operation of valves 1E51*MOVF063 (RCIC inboard steam isolation valve) and 1E51*MOVF078 (RCIC vacuum breaker valve), did not have fire wrap contrary to Fire Hazards Analysis (FHA) requirements. At 1300 on 4/23/91, additional cables, which could cause the same problem were found in fire areas AB-2, C-2 and C-6. RCIC is required by the FHA for safe shutdown in these fire areas. Since these valves are required not to change position for operation of RCIC and fire damage to these cables may cause loss of RCIC, the cables would require wrapping in these fire areas.<br /><br /> Upon discovery of this condition, the affected cables were treated as having missing fire barriers and the action statement prescribed in Technical Specification 3/4.7.7, "Fire Rated Assemblies", was implemented for areas containing these cables. Errors made during the original development of the FHA were the cause for the identified cables not being wrapped in the identified fire areas. Additional deficiencies were discovered and addressed throughout the FHA review effort as documented in this report and in previous supplements to this LER.<br /><br /> Corrective action was to perform a reverification and to reformat the FHA into a post-fire Safe Shutdown Analysis document including all required analysis for associated circuits. This action was completed on 11/19/93. The associated licensing change notice, procedure changes and design document changes were implemented by 11/25/93.
4581991009 | River Bend | 04/30/1991 | 05/30/1991 | 9106060114 | <strong>Personnel Failure To Properly Move High Radiation Area Barrier</strong><br /><i>Abstract:&nbsp;</i>On 04/30/91 at approximately 1745 with the unit in Operational Condition 1 (Power Operation) two Electrical Maintenance workers moved a high radiation area (HRA) barrier, thereby creating an opening in the barrier. The rope barrier was located on the 95' elevation of the Fuel Building (*ND*) in the cask wash down area. Technical Specification 6.12.1 requires that high radiation areas be barricaded. This report is submitted pursuant to 10CFR50.73 (a) (2) (i) (B) as operation prohibited by Technical Specifications. <br /><br /> All on-essential personnel in the radiologically controlled area (RCA) were required to leave the RCA to attend meetings with management. They were made aware that the Plant Manager would enforce procedural compliance in HRAs and disciplinary action would be taken against violators. Disciplinary action has been taken against the two Electrical Maintenance workers, the Electrical Foreman and the acting Electrical Supervisor. <br /><br /> No unauthorized individual entered the cask wash down area. This event did not affect plant systems and had no operational impact. Therefore, the health and safety of the public was not adversely affected.
4581991010 | River Bend | 05/16/1991 | 06/17/1991 | 9106240251 | <strong>Containment Isolation Valves not Verified Closed Every 31 days as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1991, it was discovered that containment isolation valves 1CPP*MOV104, 1CPP*MOV105 and 1CPP*SOV140 were not being verified closed and secured every 31 days as required by Updated Safety Analysis Report (USAR) Section 6.2.4.3.7.2. Technical Specification 4.6.1.1.b, "Primary Containment Integrity - Operating" also requires that these valves be verified closed every 31 days. Therefore, this report is submitted pursuant to 10CFR50.73 (a) (2) (i) (b) as operation prohibited by the Technical Specifications.<br /><br /> Surveillance Procedure STP-000-0201 was revised to require verification that valves 1CPP*SOV140, 1CPP*MOV104, and 1CPP*MOV105 are closed and secured every 31 days. Procedure GOP-0001 was also revised to add the same requirements when containment is secured. In addition, a review of selected commitments will be performed to identify those with actions which require procedural control. <br /><br /> The subject containment isolation valves were found to be closed and secured when the condition was identified. No evidence that these valves had been incorrectly positioned was found. Therefore, the valves would have performed their containment isolation function and the health and safety of the public was not affected by this condition.
4581991011 | River Bend | 06/04/1991 | 06/15/1992 | 9206240366 | <strong>Inadequate Implementation Of Surveillance Requirements Per Technical Specification 3/4.6.5.2 (Secondary Containment Integrity-Fuel Handling) Due To Procedural Deficiencies</strong><br /><i>Abstract:&nbsp;</i>At 1424 on June 4, 1991, with the reactor in Operational Condition 1 (Power Operation), irradiated fuel was moved in the fuel building without prior performance of surveillance requirements under Technical Specification (TS) 3/4.6.5.2 (Secondary Containment Integrity - Fuel Building). Since the plant was in compliance with TS 3/4.6.5.1 (Secondary Containment Integrity-Operating) and plant staff personnel took conservative actions to verify fuel building integrity, secondary containment integrity was assured prior to fuel movement. Thus, the intent of TS 3/4.6.5.2 was met. However, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) to document the non-compliance with the surveillance requirement. <br /><br /> The procedures used during this evolution provided inadequate guidance to assure the requirements of TS 3.6.5.2 were met. The lack of checklists and/or prerequisite steps requiring signoff, coupled with the duration of the work, led the Shift Supervisor to assume that all pertinent requirements had been met during preparations made in previous shifts.<br /><br /> The fuel building pressure was less than the .25 inches of water vacuum required by the Technical Specifications and the fuel building charcoal filtration train was in service. If a fuel drop accident occurred during fuel movement, the fuel building ventilation exhaust would have filtered as designed.
4581991012 | River Bend | 07/02/1991 | 07/31/1991 | 9108060385 | <strong>ESF Actuations Caused by the Loss of the Division II RPS Bus due to Improper Assembly of a Breaker Termination</strong><br /><i>Abstract:&nbsp;</i>At 1256 on July 2, 1991 with the reactor in Operational Condition 1 (Power Operation), a loss of the Division II reactor protection system (RPS) bus occurred due to the trip of the normal power supply. This resulted in a Division II balance-of-plant (BOP) isolation and the initiation of the control building ventilation, fuel building ventilation, standby gas treatment and annulus mixing systems. Breaker 8B located in RPS panel 1C71-P002 was de-energized pending further investigation. Then at 2256 on July 2, 1991, another loss of the Division II RPS bus occurred due to the trip of the alternate power supply resulting in another Division II BOP isolation. This occurred due to an inadvertent short, during rework addressing the original problem. Following this occurrence, the breaker was replaced and returned to service with no further incidents. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) to document these ESF actuations. <br /><br /> Based on GSU's investigation, it appears that the root cause of the first occurrence was improper assembly by the vendor resulting in arcing of a loose termination on the line side terminal of a breaker supplied by the manufacturer as part of a panel. The second occurrence was initiated by the inadvertent short of a line to ground during rework to address the first occurrence. For each occurrence, all safety systems functioned per their design and the ESF systems were restored within minutes.
4581991013 | River Bend | 07/29/1991 | 08/14/1991 | 9108200168 | <strong>ESF Actuation caused by the Loss of the Division I RPS Bus due to Tripping of the Motor-Generator Set Output Breaker</strong><br /><i>Abstract:&nbsp;</i>At 1101 on July 22, 1991 with the reactor in Operational Condition 1 (Power Operation), the output breaker of the motor-generator set supplying the normal power supply for the Division I reactor protection system (RPS) tripped. This resulted in a Division I balance-of-plant (BOP) isolation and the initiation of the control building ventilation, fuel building ventilation, standby gas treatment and annulus mixing systems. This report is submitted pursuant to 10CFR50.73 (a) (2) (iv) to document the engineered safety feature (ESF) actuations. <br /><br /> Based on GSU's research and investigation, the root cause of this event is indeterminate. All safety systems functioned per their design and the ESF systems were restored within minutes.
4581991014 | River Bend | 07/19/1991 | 08/18/1992 | 9208280034 | <strong>ESF Actuations Due To Relay Malfunctions Having The Same Failure Mode</strong><br /><i>Abstract:&nbsp;</i>On 07/19/91 at 2028 and on 07/23/91 at 2110, with the plant at 100 percent power (Operational Condition 1) in each case, engineered safety feature (ESF) actuations occurred due to relay malfunctions having the same failure mode. On 07/19/91, the failure of relay 1C71*K45D resulted in the isolation of numerous balance-of-plant (BOP) containment isolation valves, and actuation of the control room filter trains, the standby gas treatment system, and the fuel building filter trains. On 07/23/91, the failure of relay 1B21H*K204C resulted in the isolation of valve 1B33*MOVF019, reactor water upstream sample valve. This valve is a containment isolation valve. This event is reported pursuant to 10CFR50.72 (a)(2)(iv) to document the ESF actuations. <br /><br /> The immediate corrective action was to restore the ESF systems and clear the isolations. Subsequent action was to replace both suspect relays, 1C71A*K45D and 1B21H*K204C. GSU is submitting this supplemental report to provide an updated schedule for corrective actions. GSU's safety assessment indicates that the failure rates of these relays result in an increased probability of RPS failures. However, the impact on core damage frequency due to anticipated transient without scram (ATWS) events is insignificant.
4581991015 | River Bend | 09/07/1991 | 09/30/1991 | 9110090176 | <strong>Monthly Surveillance Test On Reactor Coolant System Sump Drain Flow Monitoring Instrumentation Not Performed Within The Time Allowed By The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 1800 on September 7, 1991, with the reactor in Operational Condition 1 (Power Operation), operations personnel discovered that surveillance test procedure (STP)-207-4550, a monthly STP which concerns reactor coolant system leakage monitoring equipment, had not been completed within the required Technical Specification time frame. Operations personnel reviewed the Technical Specification requirements under Section 3.4.3.1, declared the monitor inoperable and entered a 24 hour limiting condition for operation (LCO). The STP was successfully performed by 2300 hours on 09/07/91. To document the non-compliance with the surveillance requirement, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical Specifications. <br /><br /> Based on a task analysis of this event and personnel interviews, the root cause for missing the STP schedule tolerance was personnel error which involved two primary-causal factors, self-checking and communications. The missed STP would not have occurred if the turnover log or STP tolerance notification had been adequately reviewed or if the day shift instrumentation and controls (I&C) foreman had clearly indicated the consequences of not performing the STP by 0620 the following morning. Both of the responsible I&C foremen were counseled on their responsibilities for self-checking and proper communications skills to ensure complete compliance with Technical specification surveillance requirements.
4581991016 | River Bend | 09/23/1991 | 09/01/1992 | 9209090348 | <strong>Excessive Leakage Rate Test Results For Both Inboard and Outboard Containment Isolation Valves In A Single Penetration Due To Corrosion.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0230 on 09/23/91 with the unit in Operation Condition 4 (Cold Shutdown) for a mid-cycle outage, the Division I service water inlet containment isolation penetration was subjected to a local leak rate test (LLRT), surveillance test procedure (STP)-256-3820. Both inboard and outboard isolation valves failed the LLRT. The minimum pathway leakage rate was estimated to be in excess of 0.6 La (leakage allowable). The valves were subsequently reworked and passed the LLRT retests. <br /><br /> The root cause of the LLRT failures was the presence of corrosion products in both valves. Corrosion products deposited in the valve body cavities and on valve internals prevented full closure in each case. These corrosion products have been previously diagnosed as general service water corrosion products. The orientation of valve 1SWP*V174 in a horizontal line, given the corrosion problem, may also have contributed to less than optimal valve performance. The root cause for the service water corrosion has been addressed in LER 89-011 submitted April, 1989 and the supplements submitted in May, 1989 and June, 1989.<br /><br /> The service water system is designed to supply the containment during normal and accident conditions. The design of the service water systems provides for a water seal in the service water piping when the system is shutdown, thus limiting any possible leakage from this penetration.
4581991017 | River Bend | 09/18/1991 | 12/26/1991 | 9201030284 | <strong>Design Discrepancy In The Wiring Diagram For Two Hydrogen Mixing System Valves</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours on September 18, 1991, with reactor in operational Condition 1 (Power Operation), while performing a review of Station Operating Procedure (SOP)-0040 "Hydrogen Mixing, Purge, Recombiners and Ignitors," a discrepancy in the wiring diagram of the hydrogen mixing system (*BB*) was discovered. The wiring diagram of the circuit showed that the outlet valves (*20*) 1CPM*MOV1A(B) and 3A(B) could not be manually bypassed following an isolation in response to a LOCA signal. Although the discrepancy was discovered on September 18, 1991, it is believed that the condition existed since the last modification of the circuit on July 12, 1985. Thus, the manual bypass has been inoperable since 07/12/85; therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical specifications.<br /><br /> Based on a license-basis analysis considering regulatory requirements, a mechanistic analysis of hydrogen generation, a human reliability analysis, and a probablistic risk assessment of the hydrogen generation scenario, GSU has concluded the safety significance of this event is low.
4581991018 | River Bend | 09/29/1991 | 09/03/1992 | 9209100003 | <strong>ESF Actuation When RWCU Isolation Valve Stroked Closed, Cause Unknown But May Have Been Operator Error.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1654 on 09/29/91 with the unit in Operational Condition 4 (Cold Shutdown) for the planned midcycle maintenance outage, an unanticipated engineered safety feature (ESF) actuation occurred when valve G33*MOVF004, outboard reactor water cleanup system (RWCU) isolation valve stroked closed. Per design, the low flow condition caused by the closure of this valve caused both of the RWCU pumps to trip. Approximately four minutes later, a second ESF actuation occurred while operators were attempting to restart the reactor water cleanup system pumps. Due to a problem with the programmable controller which controls the filter/demineralizer portion of the system, flow oscillations occurred upon restarting the first RWCU pump. After 45 seconds, the sensed flow differential resulted in all of the RWCU isolation valves closing. The root cause of this event is indeterminate. It is possible, however, that the operator did not depress the reset pushbuttons hard enough or long enough to ensure all of the isolation relays had time to reset. Indicating lights will be installed on the operator panel adjacent to the reset pushbuttons that will indicate if an isolation signal is present to a portion of the NSSSS logic. These two related events are being reported per 10CFR50.73(a)(2)(iv). This event did not affect the health or safety of the public.
4581991019 | River Bend | 10/26/1991 | 11/24/1991 | 9112030299 | <strong>Surveillance On The Radwaste Building Ventilation Exhaust Duct Noble Gas Activity Monitor Not Met Within The Technical Specification Required Timeframe</strong><br /><i>Abstract:&nbsp;</i>At 2050 on October 26, 1991, with the reactor in operational Condition 2 (Startup), operations personnel discovered that surveillance test procedure (STP)-511-4516, a quarterly STP which concerns the radwaste building ventilation exhaust duct noble gas activity monitor, had not been completed within the required Technical specification time frame. operations personnel reviewed the Technical Specification requirements under Section 3.3.7.11.b-1a, declared the monitor inoperable and entered the action statement requiring chemistry sampling under a limiting condition for operation (LCO). The STP was successfully performed by 2300 hours on 10/28/91. To document the non-compliance with the surveillance requirement, this report is submitted pursuant to 10CFR50.73 (a) (2) (i) (B) as operation prohibited by the Technical specifications. <br /><br /> Based on a task analysis of this event and personnel interviews, the root cause for missing the scheduled performance due date was personnel error which involved two primary causal factors, self-checking and verbal communications between the I&C foreman and control room personnel. Between 10/12/91 and 10/26/91, the monitor was administratively inoperable; however, satisfactory performance of the STP on 10/28/91 verified that the monitor was functional during this timeframe and was capable of performing its intended safety function per design.
4581991020 | River Bend | 10/24/1991 | 09/14/1992 | 9209210166 | <strong>Hydrogen Igniters Declared Inoperable Due To Discrepancies Between The Surveillance Procedure And The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 0800 hours on October 24, 1991, with the reactor in Operational Condition 1 (Power Operation), while performing a review of Technical Specification (TS) Section 3/4.6.6.3 'Primary Containment/Drywell Hydrogen Ignition System', a discrepancy was found between the TS and the applicable surveillance test procedure (STP). The STP has been non-conservative with respect to the TS. Sixty-Two hydrogen igniters were declared inoperable and the reactor was shutdown pursuant to TS Section 3.0.3. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(A) (plant shutdown required by the TS) and 10CFR50.73(a)(2)(i)(B) (operation prohibited by the TS). <br /><br /> Corrective actions included revision of the STP to restore consistency with the TS, additional training, and a review of a sample of STP revisions and temporary change notices for 10CFR50.59 applicability, and a verification of a sample of STPs against the TS. <br /><br /> The reactor was shutdown in accordance with TS 3.0.3. Subsequently, hydrogen igniter system operability was verified pursuant to TS 4.6.6.3.
4581991021 | River Bend | 12/08/1991 | 01/10/1992 | 9201210111 | <strong>Reactor Protection System Actuation Due To Operator Failure To Verify The Scram Discharge Volume Level</strong><br /><i>Abstract:&nbsp;</i>At approximately 1524 on 12/08/91, with the reactor in Operational Condition 3, an unplanned reactor protection system (RPS) actuation occurred when the at-the-controls (ATC) operator placed the control rod drive (CRD) scram discharge volume high water level bypass switches from "bypass" to "normal" without assuring that the scram discharge volume (SDV) water level was less than 49". All control rods were inserted previously and no additional rod motion occurred due to the RPS actuation. This event is reportable pursuant to 10CFR50.73 (a) (2) (iv), as an engineered safety feature (ESF) actuation. <br /><br /> Abnormal Operating Procedure (AOP)-0001 ("Reactor Scram") is being revised to include a dedicated section to provide specific instructions for resetting a reactor scram or RPS (*JE*) actuation. This section will require the ATC operator to place the SDV high water level bypass switches to "bypass" as the first step and verify the SDV high level alarm is clear prior to placing the switches in the "normal" position.
4581991022 | River Bend | 12/23/1991 | 01/22/1992 | 9202040310 | <strong>Indeterminate Equipment Qualification Status Of Resistance Temperature Detectors In The Fuel Building Filter Trains</strong><br /><i>Abstract:&nbsp;</i>On 12/23/91, with the reactor in Operational Condition 4, it was discovered that from 6/4/91 to 6/8/91, fuel was moved in the fuel building while resistance temperature detectors (RTDs) installed in the fuel building heater trains were not environmentally and seismically qualified. Thus the, fuel building filter trains are considered to have been inoperable. Therefore, this report is submitted pursuant to 10CFR50.73 (a) (2) (i) (B) as operation prohibited by the Technical Specifications.<br /><br /> The subject RTDs have been replaced with qualified models. Training will be provided on the importance of communication when performing operability analyses. GSU has performed an ambient humidity analysis and a decay time analysis for the fuel in the spent fuel pool. The results show that it was unlikely that fuel building charcoal filter efficiency was degraded and that if a fuel handling accident had occurred, offsite doses would have been bounded by the design basis fuel handling accident calculation.
4581991023 | River Bend | 12/26/1991 | 01/27/1992 | 9202040042 | <strong>Reactor Water Cleanup Pumps Outboard Suction Valve Isolation During Standby Liquid Control Valve Operability Surveillance Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>At 1212 on 12/26/91 with the unit in Operational Condition 4 (Cold Shutdown), 1G33*MOVF004 (reactor water cleanup pumps outboard suction valve) received an isolation signal from a standby liquid control system manual initiation signal. The valve went fully closed and the reactor water cleanup (RWCU) pumps tripped on low flow. The isolation of the valve constituted an engineered safety feature (ESF) actuation. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(iv). <br /><br /> The root cause of this event was procedure inadequacy. corrective actions included procedure clarification and a review of all related procedures. <br /><br /> The standby liquid control (SLC) system and the reactor water cleanup (RWCU) system responded per design and 1G33*MOVF004 (reactor water cleanup pumps outboard suction valve) isolated properly.
4611991001 | Clinton 1 | 01/21/1991 | 02/20/1991 | 9102270223 | <strong>An Inadequate System Impact Assessment Of Turbine Modification Work Resulted In Automatic Containment Isolation Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 1305 hours on January 21, 1991, during the plant's second refueling outage, while the plant was in Operational Condition 4 (COLD SHUTDOWN), a Group I containment isolation signal was generated from Condenser Low Vacuum Bypass logic resulting in automatic closure of inboard Main Steam Isolation valves 1B21-F022 A, B, C, and D, and inboard Main Steam Drain Line Isolation valve 1B21-F016. At approximately 1315 hours, the 'B' Control Room Operator (CRO) manually tripped the main turbine logic. At approximately 1317 hours, the 'B' CRO reset the Condenser Low Vacuum Bypass logic and reopened valves 1B21-F022 A, B, C, and D, and 1B21-F016. At the time of the event, main turbine modification adjustments and preparations for the reactor vessel hydrostatic test were in progress. The cause of the event was attributed to utility maintenance personnel error in that personnel did not properly assess the impact to the plant of turbine modification during revisions of the Maintenance Work Request (MWR) being used to implement the turbine modification. Corrective actions include: suspending turbine modification work, revising the MWR to include jobsteps to defeat the Group I containment isolation signal, training assistant maintenance supervisors on revising MWRs, and briefing appropriate personnel on this event.
4611991002 | Clinton 1 | 02/18/1991 | 03/20/1991 | 9103270092 | <strong>Complete Loss of Service and Instrument Air Due to Equipment Failure and Personnel Error Resulted in Manual SCRAM Insertion to Minimize the Loss of Reactor Vessel Inventory</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1991, with the plant in Mode 4 (COLD SHUTDOWN), with the number 2 Service Air (SA) compressor in service maintaining header air pressure at 106 pounds per square inch gauge, the number 1 SA compressor automatically started and loaded. Control room instrumentation showed the running current of both SA compressors to be approximately the same, thus leading the operators to believe that both SA compressors were operating and loaded. To prevent equipment damage, the operators shut down the number 1 SA compressor. This action resulted in a complete loss of SA and Instrument Air. SCRAM valves started to drift open resulting in leakage from the reactor vessel to the scram discharge volume. Reactor vessel level decreased from 79 inches to 74 inches. The flow of condensate water to the vessel stopped; however, Emergency Core Cooling Systems remained capable of supplying makeup to the reactor vessel. To minimize the loss of vessel inventory, a manual SCRAM signal was inserted. The SA system was returned to service and air header pressure was reestablished within 35 minutes. The cause of the event is attributed to equipment failure compounded by personnel error. Corrective action consisted of immediately issuing a priority one Maintenance Work Request to return the SA compressor to operation. The operating shift crews have been informed of this event.
4611991003 | Clinton 1 | 02/20/1991 | 03/20/1991 | 9103270045 | <strong>Jarring of the Division III Diesel Generator Breaker Cubicle Panel Door b Utility Maintenance Personnel Resulted in Automatic Start of the Division III Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At approximately 1450 hours on February 20, 1991, while the plant was in Operational Condition 4 (COLD SHUTDOWN), the Division III Diesel Generator (DG) automatically started. The cause of the event was attributed to personnel error in that an electrical maintenance foreman applied a significant amount of force to open a misaligned Division III DG breaker cubicle panel door. When the breaker cubicle panel door came free, it opened with significant velocity and came in contact with the adjacent open breaker cubicle panel door. The jarring of the DG breaker cubicle panel door resulted in contacts of relays 62S5X and 252X1-DG1C momentarily touching which produced the following effect: the 4160 volt (v) 1C1 Bus main feeder breaker tripped open, the 4160v 1C1 Bus reserve feeder breaker closed-permissive circuit was blocked, the Division III DG automatically started, and the Division III DG feeder breaker closed to energize the 1C1 Bus. Corrective actions include: verifying the proper operation of normal to alternate circuit transfer of Division III power supply; aligning the hinges and guide pins on the DG breaker cubicle panel door; developing a Preventive Maintenance activity to check alignment of hinges and guide pins for cubicle panel doors of the Division III switchgear; and briefing appropriate personnel on this event.
4611991004 | Clinton 1 | 08/19/1991 | 09/17/1991 | 9109230070 | <strong>Reactor Core Isolation Cooling System Isolation Due to Rosemount Transmitter Failure</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1991, with the plant in Mode 1 (POWER OPERATION) at 100 percent reactor power, the Reactor Core Isolation Cooling (RCIC) system isolated due to a "RCIC DIV 2 STEAM LINE DIFFERENTIAL PRESSURE HIGH" signal. The inboard RCIC steam supply valve, 1E51-F063, closed per design. Additionally, the only other potential automatic action was the closure of the supply valve bypass valve, 1E51-F076; however, this valve was already closed. All other plant parameters were normal. The Shift Supervisor was notified of the RCIC isolation. RCIC was declared inoperable per Technical Specification 3.7.3. Troubleshooting by plant maintenance personnel revealed that the isolation signal was due to a failed flow transmitter, 1E31-N083B. Specifically, the transmitter exhibited a negative pressure oscillation (signal spike). Troubleshooting revealed that 1E31-N083B was producing excessive differential pressure signal spikes that were not present on sister channels. The transmitter was replaced and, based on acceptable post maintenance testing results, the RCIC system was declared operable and returned to STANDBY. The cause of the event was attributed to equipment failure of the Rosemount transmitter.
4611991005 | Clinton 1 | 10/15/1991 | 03/13/1992 | 9203180123 | <strong>Inadequate Design For Verifying Filter Paper Advancement Results In Inoperable Leak Detection Fission Product Particulate Sample Panel.</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1991, with the plant in POWER OPERATION, a technician performing scheduled preventive maintenance discovered the moving filter paper in the Leak Detection System fission product particulate sample panel 1E31-P002 had stopped advancing. The filter paper had not advanced since the last preventive maintenance task had been completed on October 3, 1991. The Operations Shift Supervisor determined that the failure of the filter paper to advance constituted an inoperable drywell atmosphere particulate radioactivity monitoring system and directed the drywell atmosphere to be manually sampled and analyzed at least once per 24 hours as required by the Technical Specifications. Operating the plant with an inoperable drywell atmosphere particulate radioactivity monitoring system without complying with the required action statement is a condition which is prohibited by Technical Specification 3.4.3.1. The cause of this event was inadequate design of the sample panel. Corrective actions include: implementing a temporary modification to allow visual verification of filter paper advancement; briefing personnel on this event; evaluating new fission product monitors for potential replacement of the existing sample panel; and incorporating the filter paper replacement activity into a procedure and the surveillance tracking program.
4611991006 | Clinton 1 | 11/16/1991 | 12/16/1991 | 9112300025 | <strong>Waterbox Isolation With Degraded Condenser Performance And Inadequate Steam Jet Air Ejector Suction Alignment Caused Decreased Condenser Vacuum Which Resulted In A Manual SCRAM.</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1991, with the plant in Power Operation, a rapid plant shutdown with a manual SCRAM was initiated due to decreasing condenser vacuum. The decreasing vacuum occurred during a plant down-power to repair leaking condenser tubes. At 0358 hours, with reactor power decreased to 65 percent, the 'A' waterbox was isolated. Immediately, condenser vacuum decreased and condensate temperature increased, as expected. Condenser suction isolation valve 1CA001A was left open while the waterbox was draining. Condenser vacuum and condensate temperature failed to stabilize. Reactor power was decreased in an effort to maintain vacuum. At 0645 hours, with the reactor at 34 percent reactor power and with condenser vacuum decreasing below 25 inches mercury vacuum, a rapid plant shutdown was initiated followed by a manual SCRAM. The cause of this event was attributed to a combined effect of degraded condenser performance and valve 1CA001A positioning which resulted in a failure to isolate the air removal pathway ultimately causing a loss of the intercondenser loop seal. Corrective actions for the event include a revision to plant procedures to clarify reactor power limitations prior to isolating a condenser waterbox and to clarify positioning of valve 1CA001A/B prior to draining a waterbox. The main condenser will be mechanically cleaned during the third refueling outage.
4611991007 | Clinton 1 | 12/12/1991 | 03/27/1992 | 9204030105 | <strong>Undetected Failure Of An Air Handling Unit And Operations Lack Of Understanding Of The Air Handling Unit Design And Operation Resulted In Inoperable Leak Detection Instruments.</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1991, with the plant in Power Operation, the 'B' Reactor Water Cleanup (RWCU) heat exchanger (Hx) room air handling unit (AHU) fan failed resulting in inoperable leak detection (LD) differential temperature (delta T) instrumentation. The Shift Supervisor noted the 'B' RWCU Hx room temperature increasing and the delta T recorder indicating zero, indicating a possible problem with the LD system. During the event, the LD instruments were initially declared inoperable and then incorrectly declared operable due to Operations lack of understanding of the AHU design and operation. Subsequent to this event, a review of the delta T recorder strip chart showed that the fan failed approximately two hours and twenty-five minutes before the Shift Supervisor had indication of the failure. Therefore, the requirements of Technical Specification 3.3.2 to isolate the HX within one hour were not met. No remote indication is available to identify the failure of the AHU within one hour. The causes of this event are an undetected failure of a fan resulting in inoperable LD instruments and Operations lack of understanding of the effect of the fan failure on the LD instruments. Corrective actions include submitting a proposed Technical Specification change, reworking the failed fan, and training Operations personnel on this event.
4611991008 | Clinton 1 | 12/22/1991 | 01/20/1992 | 9201280165 | <strong>Failure of The Reactor Recirculation Flow Control Valve Position Feedback Position Feedback Loop And Leaking Hydraulic Valves Resulted in Entrance Into Restricted Operating Region And Manual SCRAM</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1991, with the plant in POWER OPERATION, a manual SCRAM was initiated due to operation in the restricted zone of the thermal power versus core flow map of Technical Specification 3.4.1.3. While the control room operators conducted a scheduled power reduction, the "B" Reactor Recirculation (RR) flow control valve (FCV) started to operate erratically. Control room operators, attempting to stop the erratic operation, hydraulically locked out the "B" RR FCV. The "B" RR FCV continued to operate erratically and then suddenly closed enough to cause core flow to drop into the restricted zone. The control room operator immediately initiated a reactor SCRAM in accordance with plant procedure 3005.01, "Unit Power Changes". No reactor power oscillations were observed. The causes of this event are attributed to the failure of the "B" RR FCV position feedback loop and to internal leakage of the hydraulic valves on the hydraulic power unit. Corrective actions for this event include replacing the RR FCV position and velocity transducers, replacing the leaking hydraulic valves, examining and testing the feedback sensor and associated lead, and determining if any long-term corrective actions are appropriate.
4821991001 | Wolf Creek | 01/01/1991 | 03/29/1991 | 9104010290 | <strong>Technical Specification Violation - Leak In Rupture Disc Allows An Unplanned Release Of Waste Gas Decay Tank Without Prior Sampling</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1991, a pressure drop of 6.4 psig in Waste Gas Decay Tank (WGDT) #8 was identified at 1100 CST. This release did not exceed Technical Specification limits. However, this situation constitutes a violation of Technical Specification 3.11.2.1, which requires, in part, sampling of a WGDT prior to its release. The initial investigation by Mechanical Maintenance personnel revealed that leakage was occurring on the Catalytic Hydrogen Recombiner SHA01A rupture disc, which was replaced in mid-December, 1990.<br /><br /> Activities to resolve this issue resulted in contacting the vendor and the completion of an engineering evaluation which provided a correct torque value to use. The problem was later identified as a slight misalignment between the faces of the disc flange. Work instructions for disc replacement have been enhanced to overcome this alignment problem and documentation has been changed to reflect the correct torque value. SHA01A was returned to service on February 20, 1991.
4821991002 | Wolf Creek | 01/28/1991 | 02/26/1991 | 9102280187 | <strong>TECHNICAL SPECIFICATION VIOLATION - ESSENTIAL SERVICE WATER FLOW TO CONTAINMENT COOLING UNITS BELOW LIMITS BECAUSE OF INACCURATE EQUIPMENT</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 090%. ON MAY 26, 1989, A POST-ACCIDENT ESSENTIAL SERVICE WATER ALIGNMENT FLOW TEST WAS CONDUCTED. THE TEST RESULTS INDICATED THAT FLOWS TO THE CONTAINMENT COOLING UNITS WERE BELOW TECHNICAL SPECIFICATION 4.6.2.3 REQUIREMENTS OF 4000 GALLONS PER MINUTE. ON JUNE 2 AND 3, 1989, FLOW WAS ADJUSTED BASED ON THE CONSERVATIVE INDICATIONS PROVIDED IN THIS FLOW TEST. AN EVALUATION CONDUCTED DURING REFUELING IV (MARCH-MAY 1990) REVEALED THAT THIS EVENT OCCURRED AS THE RESULT OF INACCURATE FLOW READINGS PROVIDED BY LOCAL ANNUBARS. REVIEW OF PREVIOUS NORMAL FLOW TEST RESULTS REVEALED TWO INSTANCES IN WHICH ADEQUATE NORMAL FLOW WAS BELOW TECHNICAL SPECIFICATION 4.6.2.3 LIMITS BECAUSE OF RELIANCE ON THE ANNUBARS. ULTRASONIC FLOW MEASUREMENT TEST EQUIPMENT HAS BEEN USED TO PERFORM THE ASSOCIATED SURVEILLANCE PROCEDURE SINCE REFUELING IV. ON JANUARY 28, 1991, FOLLOWING AN ENGINEERING EVALUATION OF TEST RESULTS, IT WAS DETERMINED THAT THE LOW POST-ACCIDENT ESSENTIAL SERVICE WATER FLOW TO THE CONTAINMENT COOLING UNITS IS REPORTABLE PURSUANT TO 10 CFR 50.73(A)(2)(I) CONCERNING A CONDITION PROHIBITED BY THE PLANT'S TECHNICAL SPECIFICATION.
4821991003 | Wolf Creek | 02/02/1991 | 03/04/1991 | 9103110129 | <strong>Technical Specification Violation - Failure To Perform ASME Section XI Required Visual Inspection Of ASME Code Class 2 Piping</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 090%. ON FEBRUARY 1, 1991, IT WAS DISCOVERED THAT AN ASME CODE CLASS 2 PORTION OF THE FUEL POOL COOLING AND CLEANUP SYSTEM WAS NOT INCLUDED IN THE PROCEDURE FOR THE ASME SECTION XI REQUIRED VISUAL INSPECTION. THE FAILURE TO EXAMINE THESE LINES IS NOT IN ACCORDANCE WITH TECHNICAL SPECIFICATION 4.0.5. PERFORMANCE OF VALVE LEAK CHECKS AND LOCAL LEAK RATE TESTS HAVE INDICATED THAT THIS PIPING WOULD HAVE MET THE CRITERIA REQUIRED BY ASME SECTION XI FOR A VISUAL EXAMINATION OF ASME CODE CLASS 2 PIPING. THIS EVENT WAS THE RESULT OF A PERSONAL ERROR DURING PROCEDURAL DEVELOPMENT OF THE SURVEILLANCE PROCEDURE. A RANDOM REVIEW OF SURVEILLANCE PROCEDURES COVERING A WIDE VARIETY OF PLANT SYSTEMS WAS CONDUCTED TO ENSURE THAT ALL ASME CODE CLASS 1, 2, AND 3 COMPONENTS WERE INCLUDED. NO SIMILAR SITUATIONS WERE FOUND DURING THE REVIEW. SURVEILLANCE PROCEDURE STS PE-048C, REFUELING POOL SKIMMER SYSTEM PRESSURE TEST', WILL BE REVISED TO INCORPORATE THE ASME CODE CLASS 2 PIPING BY MAY 1, 1991. ALSO, THE ASME SECTION XI VISUAL EXAMINATION ON THIS PIPING WILL BE PERFORMED DURING REFUEL V.
4821991004 | Wolf Creek | 03/12/1987 | 11/11/1991 | 9111180238 | <strong>Technical Specification Violation - Failure To Recognize The Emergency Diesel Generator Ventilation System As Essential for Emergency Diesel Generator Operability</strong><br /><i>Abstract:&nbsp;</i>Licensee Event Report (LER) 482/91-004-00 is being replaced by LER 482/87-061-00. <br /><br /> On February 6, 1991, it was determined that three separate situations involving the Emergency Diesel Generator (EDG) Building Ventilation System may have caused EDGs A or B to be inoperable. The first situation involved the removal of the motor to EDG Ventilation Supply Fan CGM01B, on March 12, 1987. On May 15, 1987, CGM01B was restored to operable status. The second event involved a procedure change, initiated on August 29, 1988, placing the handswitches to EDG Ventilation Supply Fans CGM01A & B in pull-to-lock without implementing proper compensatory operator actions. This procedure was corrected in August 1990. The third event involved clamping EDG Room "A" Recirculation Air Damper GMD003 in its non-safety position between July 17, 1988 and April 28, 1990. A subsequent evaluation concluded that the first two situations rendered the EDGs inoperable. <br /><br /> The root cause for these events stems from personnel failing to recognize that the EDG Ventilation System is essential to operability of the EDGs. Since the time these events occurred, administrative guidance has been revised to include the EDG Ventilation Supply System as essential for EDG operation. .
4821991005 | Wolf Creek | 02/08/1991 | 03/08/1991 | 9103120358 | <strong>Failure To Incorporate Correct Values Results In Incorrect Setpoint For The Containment Base Slab Triaxial Response Spectrum Recorder</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1991, it was determined that the setpoint for the Containment Base Slab Triaxial Response Spectrum Recorder was incorrectly set. Technical Specification 3.3.3.3 requires that seismic monitoring instrumentation be operable at all times. Because it was not recognized that the Recorder was inoperable, a Special Report was not submitted within the required time frame. <br /><br /> Subsequent investigation into this occurrence revealed that the design specification had been changed in June of 1984. When the setpoint was originally established in November of 1984, the values provided in a previous revision of the design specification incorporated. Consequently, the setpoint has been incorrectly set since that time. Because the individuals involved are no longer employed at Wolf Creek, attempts to recreate the events that led up to this error have been unsuccessful. The surveillance test procedure and the Wolf Creek Setpoint Document have been revised to reflect the correct setpoint values. The recorder was restored to operable status on March 1, 1991 at 1048 CST. A review is being conducted to ensure other errors of this nature have not occurred.
4821991006 | Wolf Creek | 05/12/1991 | 06/07/1991 | 9106120111 | <strong>Auxiliary Feedwater Actuation And Control Room Ventilation Isolation When Power Supply In Engineered Safety Features Actuation System Failed</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1991 at 1800 CDT, a "B" Control Room Ventilation Isolation occurred, the "B" Train Auxiliary Feedwater Pump started, the Turbine Driven Auxiliary Feedwater Pump started, and "B" Train Steam Generator Blowdown and Sampling isolated, as a result of a power supply failure in Engineered Safety Features (ESF) Actuation System cabinet SA036D. As a result of the loss of the "A" Train logic and actuation relays a plant shutdown was initiated as required by Technical Specifications, and a Notification of Unusual Event was declared. The power supply was replaced by 2150 CDT and the Notification of Unusual Event terminated at 2208 CDT. All ESF equipment functioned properly. <br /><br /> The cause of the ESF actuation was a faulty pre-regulator board in the 15 volt DC power supply in cabinet SA036D. Root cause of the failure could not be determined. Testing and monitoring of this type of power supply has indicated that a generic problem does not exist.
4821991007 | Wolf Creek | 05/22/1991 | 06/21/1991 | 9106260342 | <strong>Technical Specification Violation - Inadequate Testing of Component Cooling Water to Reactor Coolant Pump Thermal Barrier Check Valves</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1991, it was discovered that Inservice Testing (IST) procedure STS EG-206, Revision 0, "Component Cooling Water System Inservice Valve Test", does not adequately test the Component Cooling Water to Reactor Coolant Pump Thermal Barrier Check Valves in their closed position because of an inadequate test boundary. This test deficiency, which has been present in the five times this test has been performed, is contrary to Technical Specification 4.0.5. <br /><br /> This test deficiency resulted from personnel not providing sufficient technical content during initial development of the IST procedure. The root cause of this initial test deficiency could not be determined because the personnel involved are no longer employed by Wolf Creek Nuclear Operating Corporation. Because of this deficiency and other identified deficiencies that did not result in noncompliance, a complete technical review of IST procedures will be performed. Certain Inservice Inspection Program procedures will also be included among this review.
4821991008 | Wolf Creek | 05/28/1991 | 06/27/1991 | 9107050232 | <strong>Engineered Safety Features Actuations Caused By Insufficient Self-Checking By Operator Who Erroneously Restored Radiation Monitor During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1991, at 1457 CDT, an Engineered Safety Features (ESF) actuation occurred when a radiation monitor was erroneously restored to service during the performance of a surveillance procedure. This resulted in a Containment Purge Isolation Signal (CPIS) and a Control Room Ventilation Isolation Signal (CRVIS). All required ESF equipment responded properly to the CPIS and CRVIS. The error was subsequently identified, the signals reset and the ventilation systems were restored to normal configuration at 1519 CDT. <br /><br /> The root cause of this event has been identified as insufficient self- checking by the licensed operator who erroneously restored Radiation Monitor GT RE-22 rather than GG RE-27. To prevent recurrence of this event, the Manager Operations has issued a letter to all Operations personnel reinforcing the practice of self-checking.
4821991009 | Wolf Creek | 06/12/1991 | 07/12/1991 | 9107170247 | <strong>Technical Specification Surveillance Requirement Not Satisfied Prior To Equipment Return To Service Of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1991, at approximately 1045 CDT, during a review of the Equipment Out-Of-Service Log (EOL), it was discovered that surveillance testing had not been performed within the time interval for the Main Steam Loop 1 Low Point Drain Valve AB LV009, thereby violating Technical Specification 4.0.2. Upon discovery, the required surveillance testing was performed satisfactorily. <br /><br /> This event resulted from cognitive personnel errors by licensed operations personnel. Because of an oversight, the EOL was not updated after performance of a surveillance test nor was it reviewed for required surveillance tests prior to restoration of AB LV009. A contributing factor to the occurrence of these errors is the absence of an adequate program interface between the performance of surveillances, the EOL, and Clearance Orders. To preclude future occurrences, the procedures governing Clearance Orders and Surveillance Testing will be enhanced to provide an adequate interface between these programs to ensure that surveillance testing is not overlooked.
4821991010 | Wolf Creek | 05/09/1991 | 07/18/1991 | 9107220311 | <strong>Containment Emergency Escape Air Lock Hatch Closed Without Having The Required Leak Rate Test Performed Because Of Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1991, it was determined that the outer hatch to the containment emergency escape air lock had been opened and closed on May 9, 1991 under a Security System Work Request (SSWR). The required emergency escape air lock seal test was not performed following closure contrary to Technical Specification 3.6.1.3 which requires, in part, demonstration of containment Air lock operability within 72 hours following each closing. Following discovery, the required emergency escape air lock seal test was performed satisfactorily. <br /><br /> The root cause of this event was the lack of administrative controls involving the use of SSWRs. Signs have been placed on the containment emergency escape Air lock informing personnel that air lock seal tests are required after each closing. Also, the procedure governing the issuance of SSWRs will be enhanced to ensure that appropriate reviews are conducted before troubleshooting associated with the security system are allowed to proceed.
4821991011 | Wolf Creek | 05/31/1991 | 08/19/1991 | 9110010250 | <strong>Late Surveillance Test Performance Caused By Error In Completing Status Chart</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1991, at approximately 1121 CDT, it was determined that the quarterly Component Cooling Water System (CCW) inservice valve test had not been completely performed during the second quarter of 1991, causing inoperability of two trains of CCW and certain Containment Isolation Valves, which required entry into Technical Specification (TS) 3.0.3. The required test was performed on the "A" Train valves at 1158 CDT. The "A" Train was declared operable and TS 3.0.3 was exited. At 1208 CDT, it was recognized that the "A" Train was inoperable because of preventative maintenance activities, and the requirements of TS 3.0.3 still applicable. Testing of the "B" Train valves was completed at 1210 CDT, restoring one CCW train to operable status, and TS 3.0.3 was exited. At 1428 CDT, the "A" Train was restored to operable status. The individual involved in the premature exit from TS 3.0.3 has been reminded of the importance of not allowing rapid evolutions to distract from knowledge of plant status. <br /><br /> This event occurred because the Control Room surveillance tracking chart was improperly marked after partial performance of the surveillance test on May 14, 1991. Proper use of the chart has been discussed with the individual involved. As a second check to ensure surveillances are completed, scheduling personnel will independently verify surveillance test completion.
4821991012 | Wolf Creek | 07/30/1991 | 08/29/1991 | 9109040075 | <strong>Failure to Follow Procedures Results in Failure to Log Control Rod Position Comparisons While Rod Deviation Monitor Was Inoperable</strong><br /><i>Abstract:&nbsp;</i>During the period of July 30, 1991, at approximately 0900 CDT through July 31, 1991, at approximately 0748 CDT, the four-hour comparison of control rod demand position to digital position indication was not performed as the result of misinformation concerning the operability of the rod position deviation monitor. This condition is contrary to Technical Specification Surveillance Requirement 4.1.3.2. Although the monitor was not operable, the annunciator fed by the rod position deviation monitor would have alarmed correctly. <br /><br /> The misinformation occurred because personnel had overlooked four failed pulse counter cards. When the cards failed on July 18, 1991, a Corrective Work Request was not initiated. The individuals involved have been counseled and procedural guidance will be enhanced.
4821991013 | Wolf Creek | 08/21/1991 | 09/19/1991 | 9109250056 | <strong>Inoperability Of Certain Safety Related Equipment Due To The Potential Of A Fault In A Non-safety Related Circuit Propagating Into A Safety Related Circuit.</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1991, at approximately 0958 CDT, it was discovered that a field routed lighting conduit was in contact with safety related cables that were entering a ceiling penetration. An engineering evaluation of this condition determined that this condition could have potentially caused one independent train to become inoperable in multiple systems to mitigate the consequences of an accident if a high energy fault resulting in massive failure of the lighting circuits had occurred. The lighting conduit was moved.<br /><br /> Because the separation violation most likely occurred during plant construction, it was not possible to determine the root cause of this event. It is conceivable that the separation problem with the lighting conduit and the safety related cables was caused by penetration sealing activities. The applicable procedures have been revised to include a caution to maintain the minimum separation distance. Additional inspections of conduit and cable in heavily congested areas will be performed to ensure that no other similar situations exist.
4821991014 | Wolf Creek | 09/05/1991 | 10/04/1991 | 9110100083 | <strong>Incorrect Accumulator Pre-charge Curve Results in Potential Failure of Main Steam Isolation Valves to Fully Close Under all Conditions</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, it was discovered that a sufficient amount of hydraulic fluid may not be available to fully close the Main Steam Isolation Valves (MSIVs) at certain temperatures. Investigation into this condition identified that MSIV AB HV-0017 did not have a sufficient amount of fluid in the accumulators to independently stroke the valve closed. Also, a concern was raised regarding the possibility that the accumulators may have been degraded simultaneously at various times throughout operation of the plant. Therefore, under certain conditions, the plant could have been placed in unanalyzed condition. <br /><br /> This condition resulted from an incorrect accumulator pre-charge curve supplied by the vendor for the conditions under which the accumulators operated. The data was based on elevated pressure, zero pre-charge tolerance, ambient rather than accumulator temperature and an incorrect model of nitrogen behavior at elevated pressures. Upon discovery of this condition the hydraulic fluid pressure in the accumulators was raised to charge the accumulators with sufficient fluid. A correct pre-charge curve is being developed for incorporation into the vendor manual and plant procedures.
4821991015 | Wolf Creek | 09/07/1991 | 10/07/1991 | 9110110197 | <strong>Procedural Inadequacy And Failure To Follow Procedures Lead To Failure To Remove Temporary Filter Resulting In Residual Heat Removal Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>Between September 7, 1991, at approximately 0900 CDT, and September 9, 1991, at approximately 0830 CDT, a temporary filter was in place on the intake to the Residual Heat Removal (RHR) Pump Room "A" cooler so that the room cooler could be periodically operated during preparations for the application of decontamination coatings in the room. Subsequent evaluation determined that with a dirty temporary filter in place, the design heat removal for the room coolers could not be obtained. Although this event did not result in a Technical Specification violation since both RHR Pumps were not inoperable simultaneously nor was one RHR Pump inoperable for more than 72 hours, it was determined that a voluntary Licensee Event Report (LER) would be submitted.<br /><br /> The root causes of this event are procedural inadequacy and failure to follow procedures. The workers have been counselled on the importance of following all the steps in the procedures. On September 16, 1991, the procedure was revised to include an evaluation of potential impacts of the activities on systems that remain in service.
4821991016 | Wolf Creek | 09/09/1991 | 10/03/1991 | 9110100036 | <strong>Technical Specification Violation - Removal of Ductwork Damper Inspection Covers Results in Inoperability of Ventilation Systems</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1991, at approximately 0845 CDT, it was discovered that five (5) of the Control Building Heating, Ventilation and Air Conditioning System (HVAC) ductwork damper inspection covers had not been reinstalled since the initiation of preventive maintenance activities on September 9, 1991, at approximately 0830 CDT. Subsequent testing of the Control Room Emergency Ventilation System (CREVS) and the Auxiliary Building Emergency Exhaust System (EES) determined that with these ductwork damper inspection covers removed, neither train of these systems were capable of maintaining the pressure requirements independently as required by Technical Specifications. <br /><br /> The root cause of this event is inadequate work controls. The work instructions did not provide directions for the sequential removal and reinstallation of the ductwork damper inspection covers. A procedure will replace the work instructions used in the past for performing maintenance on ventilation dampers. A review of work package instructions will be conducted and instructions revised where necessary to strengthen the restoration instructions.
4821991017 | Wolf Creek | 09/20/1991 | 01/15/1992 | 9201240208 | <strong>Resolution of Potential Inoperability of Fuel Building and Auxiliary Building Emergency Exhaust Systems</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1991, at 0748 CDT, Security personnel notified Control Room operators that a Fuel Building/Auxiliary Building pressure boundary door was found propped open without a continuous watch having been established. Subsequent evaluation concluded that with this door open, the Fuel Building and Auxiliary Building Emergency Exhaust Systems (EES) may not have been able to maintain a negative pressure greater than or equal to .25 inch Water Gauge independently as required by Technical Specification 3.7.7 and 3.9.13 for Fuel Building and Auxiliary Building EES operability. Subsequent testing has shown that with this door open the Fuel Building and Auxiliary Building EES were able to maintain a negative pressure greater than or equal to .25 inch Water Gauge independently as required by Technical Specifications. <br /><br /> The root cause of this event is failure to follow procedures by the craftsmen who propped the door open to move scaffolding through the door. To prevent recurrence of this event, the manager Modifications has discussed this event and its ramifications with his craftsmen's supervision.
4821991018 | Wolf Creek | 10/02/1991 | 10/28/1991 | 9111040223 | <strong>Containment Purge Isolation and Control Room Ventilation Isolation Caused by High Gaseous Activity During Containment Purge</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1991, at 0352 CDT, shortly after initiation of a containment purge, a Containment Purge Isolation Signal and Control Room Ventilation Isolation Signal were generated by signals from the gaseous channels of the Containment Purge Radiation Monitors, GT RE-22 and GT RE-33. All required Engineered Safety Features equipment responded properly to the signals. After confirming there were no unusual radiological conditions in containment, the purge was re-established at 0713 CDT without further incident. <br /><br /> The root cause of this event is failure to follow procedures by licensed Control Room operators. To prevent recurrence, the Control Room operators who were involved in this event were counseled on the importance of using all available resources, including procedures, when restoring systems to operation rather than relying on memory. Evaluations of alternate venting methods will be completed and any necessary changes to the venting process will be in place before the next venting operation is scheduled in Refueling Outage VI.
4821991019 | Wolf Creek | 10/11/1991 | 11/05/1991 | 9111150005 | <strong>Fretting Between Grid Strap And Fuel Rod Results In Broken Fuel Rod</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1991, at 0240 CDT, during fuel off-load operations, Control Room operators notified that a broken fuel rod had been identified in fuel assembly F31 located in core position L-9. Subsequently, it was determined that the fuel rod was broken in two locations resulting in a segment approximately four inches in length. Additional inspection activities resulted in the discovery of fuel defects in fuel assemblies F05 and F17, and additional defects in fuel assembly F31. <br /><br /> From the investigations and evaluations conducted, grid-to-rod fretting has been identified as the principal failure mechanism and appears to have occurred solely in the second cycle of the fuel assemblies' operation. Extensive investigation has been unsuccessful in identifying the root cause for this failure mechanism.
4821991020 | Wolf Creek | 12/05/1991 | 01/06/1992 | 9201150109 | <strong>Containment Isolation Valves Failed Local Leak Rate Test Causing Total Path Leakage And Overall Integrated Leakage To Be Above 0.6 La and 0.75 La Respectively</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1991, during Refueling Outage V, with all fuel removed from the core, the Control Room informed that the total path Containment Local Leakage Rates for Type B and C tests was above the Technical Specification Limit of 0.6 L sub a. This was determined following the performance of a Local Leak Rate Test on Containment Isolation Valves EF HV032 and EF HV034. These valves, associated with Penetration 28, isolate Containment Air Coolers "B" and "D" from Essential Service Water Train "B". Also, these valves are normally open valves and receive an open signal on a Safety Injection Signal. On December 5, 1991, at 1600 CST, following calculations to determine the "as-found to condition for the Overall Containment Integrated Leakage Rate (ILR), it was determined that the overall ILR was greater than 1.0 L sub a after factoring in the total path leakage for all applicable penetrations including Penetration 28.<br /><br /> The excessive leakage through valves EF HV032 and EF HV034 resulted from erosion/corrosion (E/C) of the valve discs. The valve discs were replaced. An evaluation of E/C damage to the newly installed discs will be conducted during the next refueling outage.
4821991021 | Wolf Creek | 10/21/1991 | 11/18/1991 | 9111250126 | <strong>Voluntary - Emergency Diesel Generator "A" Restored With Incorrect Post-Welding Hydrostatic Test Pressure on Jacket Water and Lube Oil Heat Exchangers.</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1991, with the unit shutdown and all fuel removed from the core, it was identified that the post-maintenance hydrostatic test for the Emergency Diesel Generator (EDG) "A" jacket water heat exchanger and lube oil heat exchanger water boxes was performed at an incorrect test pressure. EDG "A" had been considered operable since completion of post-maintenance testing on October 21, 1991. Subsequent to returning EDG "A" to service, EDG "B" was removed from service on October 21, 1991; therefore, an operable EDG was not available until EDG "A" was again returned to service on October 30, 1991, following completion of the hydrostatic test at the correct pressure. This condition is not in compliance with administrative controls and it was therefore decided to voluntarily report this condition. <br /><br /> Use of the incorrect test pressure resulted from a cognitive personnel error by non-licensed personnel who misinterpreted an equipment drawing. An enhancement will be added to procedure ADM 08-217, "Hydrostatic and Pneumatic Testing," which will include guidance to be used when obtaining a system's design pressure.
4821991023 | Wolf Creek | 11/19/1991 | 07/02/1992 | 9207070015 | <strong>Accidental Bumping of 120 Volt Supply Panel Results in Engineered Safety Features Equipment Actuations</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991, at 2106 CST, 480 Volt Supply Breaker 52NG02BAF4 tripped, resulting in a loss of power to various radiation monitors. This loss of power initiated a Control Room Ventilation Isolation Signal, a Fuel Building Isolation Signal, and a Containment Purge Isolation Signal. <br /><br /> The root cause of this event has been attributed to inadvertent bumping of the operating switch to breaker 52NG02BAF4 by non-licensed personnel. Exercising caution while working near plant equipment has been re-emphasized with the responsible work group and the remaining groups in the department. Additionally, the operating switch has been inspected and it was determined that a hardware problem did not contribute to the breaker tripping.
4821991024 | Wolf Creek | 12/05/1991 | 03/27/1992 | 9203310209 | <strong>Deficiencies Discovered In Motor-Operated Valve Testing Program Which Caused Potential Inoperability of Safety Related Valves</strong><br /><i>Abstract:&nbsp;</i>In November of 1991, deficiencies were discovered in Wolf Creek Nuclear Operating Corporation's (WCNOC) program for implementing commitments to the provisions of Generic Letter 89-10 (GL 89-10), "Safety Related Motor- Operated Valve Testing and Surveillance". In response to these deficiencies a team effort was initiated to determine the operability of safety related motor-operated valves (MOV) in the MOV testing program. This team determined that 28 safety related MOVs may have been inoperable or may not have met the requirements of GL 89-10 at certain times in the past. Operability of all valves was assured prior to restart from the fifth refueling outage.<br /><br /> The failure of the MOVs to meet the requirements of GL 89-10 resulted from WCNOC management's failure to communicate expectations to personnel involved in the MOV program. An evaluation of existing WCNOC programs was initiated to ensure that conditions adverse to quality were being identified and promptly resolved through the appropriate corrective action process. No other similar situations were discovered. Also, a Management Action Plan was initiated to focus attention and resources on significant performance and program improvement issues so that WCNOC achieves excellence in all its activities.
4821991025 | Wolf Creek | 11/19/1991 | 08/17/1992 | 9209090131 | <strong>Positive Reactivity Changes With No Operable Centrifugal Charging Pumps And Boron Injection Flow Path Results In Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1991, from 1541 CST until 1914 CST and on November 20, 1991, from approximately 1930 CST until November 21, 1991, at 0655 CST, positive reactivity changes occurred when borated water was charged at a lower concentration than the Reactor Coolant System boron concentration while both Centrifugal Charging Pumps (CCPs) were inoperable. With no CCP operable, the action statements for Technical Specifications 3.1.2.1 and 3.1.2.3 require the suspension of all operations involving positive reactivity changes thus requiring the charging boron concentration to be higher than the Reactor Coolant System boron concentration even if the charging concentration exceeds shutdown requirements. <br /><br /> Several causes contributed to these events' occurrences, including procedural inadequacy and ineffective training on the Reactor Makeup Control System. One Reactor Operator did not have a complete understanding of the Reactor Makeup Control System and has been counselled on the proper operation of the system. To prevent recurrence, the appropriate procedures have been revised. Additionally, information concerning the control system default to the 120 gallon per minute setpoint when selected to automatic mode has been added to the licensed operator essential reading.
4821991026 | Wolf Creek | 12/12/1991 | 01/13/1992 | 9201210149 | <strong>Unplanned Engineered Safety Features Resulting From Radiation Monitor GK RE-004 Not Fully Bypassed When Breaker Was De- energized.</strong><br /><i>Abstract:&nbsp;</i>On 12, 1991, at 2100 CST, with the plant in Mode 5, Cold Shutdown a Control Room Ventilation Isolation Signal (CRVIS) was received. The CRVIS occurred when the bypass key for Control Building Supply Air Radiation. Monitor GK RE-004 was not placed fully in the bypass position as required prior to commencing troubleshooting activities on 480 Volt Supply Breaker 52NG02BAF4. Troubleshooting activities on the breaker being performed as a result of an event previously reported by License Event Report (LER) 91-023-00. Therefore, when the supply breaker was de-energized, a CRVIS was initiated. <br /><br /> It was concluded that the switch performed as designed and that the event resulted from a personnel error by a licensed individual not placing the bypass key in a fully bypassed position. This event is considered an isolated case. A discussion of this LER will be included in Licensed Operator Requalification Training and a copy placed in Operations Required Reading.
4831991001 | Callaway | 11/19/1990 | 09/12/1991 | 9109170187 | <strong>Technical Specification 4.0.4 Violated During Power Ascension Following Refuel By Entering Modes 3, 2 And 1 With The Surveillance Not Current For OT Delta T, OP Delta T and Vessel Delta T</strong><br /><i>Abstract:&nbsp;</i>On 3/1/91 and 8/1/91, while in Mode 1, Power Operations, at 100 percent power, it was determined that Technical Specification (T/S) 4.0.4 had been violated during power ascensions following Refuels 2, 3 and 4. T/S 4.0.4 requires that surveillance requirements be current prior to entering a mode covered by the T/S. Contrary to this, Modes 3, 2 and 1 were entered without overtemperature delta temperature (OT Delta T), overpower delta temperature (OP Delta T) and vessel Delta T surveillances being current. <br /><br /> OT Delta T and OP Delta T are calculated by T/S 2.2.1 equations which use Delta T sub o as an input. Vessel Delta T is expressed as a percentage of and calibrated to Delta T sub o. Delta T sub o is the indicated delta T at rated thermal power. At the start of a new cycle, Delta T sub o is not known. However, T/S 4.3.1.1 and T/S 4.3.2.1 which determine operability of OT Delta T, OP Delta T and vessel Delta T channels do not contain an exception to T/S 4.0.4. Mode 3, 2 and 1 should not have been entered prior to determining Delta T sub o. Delta T sub o cannot be determined below 100 percent power. Thus, T/S wording makes power operations after refuel impossible without violating T/S. <br /><br /> Delta T sub o was measured and final adjustments completed by 0100 on 11/30/90. Procedures will be revised to verify Delta T loop scaling at intermediate power levels. An operating license amendment was submitted to request an exception to T/S 4.0.4 for the applicable T/S. <br /><br /> At no time were the safety limits in T/S 2.2.1 exceeded.
4831991002 | Callaway | 06/19/1991 | 07/18/1991 | 9107230403 | <strong>Blown Fuse For An Ultimate Heat Sink Cooling Tower Fan Caused Entry Into Technical Specification 3.0.3 With Inoperability Of Both Trains Of Safety Injection Pumps</strong><br /><i>Abstract:&nbsp;</i>On 6/19/91 at 0123 CDT, Technical Specification (T/S) 3.0.3 was entered when both trains of Emergency Core Cooling system Safety Injection (SI) pumps were rendered inoperable. Plant was in Mode 1 - Power Operations at 100% reactor power. <br /><br /> On 6/18/91 at 2045, 'A' train SI pump was declared inoperable for planned maintenance. On 6/19/91 at 0123, a non-licensed Equipment Operator (EO) mistakenly attempted to perform a surveillance test on 'B' train Ultimate Heat Sink (UHS) cooling tower fans. Three Engineered Safety Features Actuation System alarms prompted an investigation. At 0441, a blown control power fuse for the 'D' UHS fan was discovered, rendering the 'B' train SI pump inoperable and T/S 3.0.3 was entered. At 0505, the 'D' UHS fan was restored operable with a fuse replacement from 'A' train 'A' UHS fan. T/S 3.0.3 was exited at 0528. This event is attributed to the EO's failure to comply with a procedure precaution to wait 15 minutes after securing the fan in slow speed before starting it in fast speed. He also performed the surveillance on both trains rather than just the 'A' train. Procedures will include guidance to lineout non-applicable portions of surveillance procedures. Operators were reminded to use train specific communication and procedure verbatim compliance. The test procedure will be split into two train specific procedures. Availability of replacement fuses will be evaluated.
4831991003 | Callaway | 05/18/1989 | 07/26/1991 | 9107290221 | <strong>Mispositioned Safety Injection System Throttle Valve Caused Inoperability Of Both Safety Injection Pumps and Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>At 1300 CDT on 6/28/91, it was discovered that the Emergency Core Cooling System (ECCS) Safety Injection (SI) cold leg injection throttle valve, EM-V-0095, had been mispositioned since 5/18/89 following valve maintenance during a refueling outage and subsequent entry into Mode 3. Because of valve position, Technical Specification (T/S) 4.5.2(h)(2)(b) SI flow upper limit of 655 gpm would have been exceeded rendering both SI trains inoperable, and thus requiring entry into T/S 3.0.3. At the time of event, the plant was in Mode 6 - refueling. At time of event discovery, the plant was in Mode 1 - Power Operations at 100 percent reactor power. <br /><br /> On 5/4/89 during performance of valve lineup procedures, two utility Equipment Operators failed to properly verify EM-V-0095's position. <br /><br /> On 6/26/91 at 0800, a utility engineer discovered a recorded SI pump flow of 695 gpm during a review of 9/30/90 surveillance results. An investigation into the cause of the excessive flow found that EM-V-0095 was mispositioned. EM-V-0095 was repositioned at 1300 CDT on 6/28/91. Other ECCS pump surveillance tests were reviewed, but no T/S flow limits for pump runout and flow balance were violated. <br /><br /> A procedure will be developed to include guidance for verifying throttle valve position. T/S ECCS flow limits will also be incorporated into appropriate procedures. This event will be reviewed with utility Operations personnel.
4831991004 | Callaway | 05/23/1989 | 09/23/1991 | 9109300160 | <strong>Steam Generator Low-Low Level Trip Time Delay Design Oversight Resulting In Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>At 0800 CDT on 8/23/91, utility engineers determined the Steam Generator (S/G) Low-Low (Adverse) reactor trip and the Auxiliary Feedwater Pump start channels were inoperable on seven occasions while in Modes 1, 2 and 3 between plant startup from Refuel 3 on 5/23/89 to 5/4/90 with power below 20%. This was a condition prohibited by Technical Specification (T/S) 3.3.1-13.a and T/S 3.3.2-6(d)(1)(a), thus requiring entry into T/S 3.0.3. At time of discovery, the plant was in Mode 1 - Power Operations at 100% reactor power. <br /><br /> On 5/23/89, a Trip Time Delay (TTD) circuit was added to the S/G Low-Low level reactor trip circuitry. On 5/21/90, the utility was notified that the TTD circuit created the potential for S/G instrument errors during a low power feedwater pipe break with adverse containment resulting in reference leg heatup beyond design. The cause was due to vendor and utility design oversight. The time delay between the discovery date and the final operability determination was caused by: a belief that conservative analysis values had been used; computer modeling problems; and a low priority since the TTD circuits have been removed from service since 5/4/90. <br /><br /> A modification will bypass TTD timers in an adverse containment. Regular management meetings will review potentially reportable items. The plant could have been shutdown with diverse protection if an adverse containment had occurred.
4831991005 | Callaway | 10/11/1991 | 11/12/1991 | 9111190053 | <strong>Missed Containment Air Lock Door Interlock Surveillances Due to Human Performance</strong><br /><i>Abstract:&nbsp;</i>On 10/11/91 while in Mode 1 at 100%, a utility Quality Assurance engineer discovered that the six month Technical Specification (T/S) normal and emergency personnel containment air lock door interlock test had not been performed since 11/6/90. The air locks were declared inoperable at 1515 CDT and T/S 3.0.3 was entered. The surveillances were completed satisfactorily at 1547 CDT on 10/11/91.<br /><br /> The root cause of this event is human performance. The surveillance task sheet (STS) generation was not properly coordinated by the assigned utility personnel during a surveillance test procedure revision. <br /><br /> The following steps have been implemented to prevent recurrence. A step was added to the plant's Procedure Request Form that requires a review of all STS associated with the surveillance procedure before the procedure can be issued. The plant's computerized Reference Tracking System and Commitment Tracking System have been enhanced to aid procedure writers in identifying an STS that may need revision. Procedures will be checked to ensure the T/S referenced includes a current STS to properly implement the surveillance. <br /><br /> The operability of these hatches was documented by other surveillance tests during refuels between 2/88 and 10/11/91. A review of surveillance tests for these containment access hatches indicated no significant increase in leakage during the periods of missed surveillances.
4831991006 | Callaway | 11/05/1991 | 12/05/1991 | 9112100165 | <strong>A Reactor Trip Due To A Failure Of A Gating/Sequencing Card In The Inverter For A 120 Volt AC Instrument Bus</strong><br /><i>Abstract:&nbsp;</i>On 11/5/91, at 1031 CST, a reactor trip occurred due to the failure of a gating/sequencing card in the inverter (NN12) supplying a 120 volt AC safety-related instrument bus (NN02). The NN02 bus was de-energized. This failed a controlling feedwater channel resulting in a high water level in the 'A' steam generator which caused a Turbine Trip signal. The reactor trip occurred on a Unit Trip/Turbine Trip signal. A Feedwater Isolation and an Auxiliary Feedwater Actuation were generated by design. The plant was in Mode 1 - Power Operations at 100 percent reactor power. The reactor coolant system temperature was 588 degrees F and the pressure was 2237 psig. The licensed operators recovered from the trip and the Engineered Safety Feature actuations via plant procedures. The NN02 bus was energized from backup power via the Sola transformer at 1109. The failed inverter card was replaced and the inverter lined up to NN02 at 0242 on 11/6/91. <br /><br /> The plant was returned to Mode 1 - Power Operations at 2018 on 11/6/91. Corrective actions include: an analysis of the card failure; a determination if additional preventive maintenance for this card is necessary; procedures will be developed with NN bus load information for operator use; and operator training on this type of event will be developed and performed.
4831991007 | Callaway | 11/14/1991 | 12/12/1991 | 9112170531 | <strong>Failure To Verify Load Rejection Surveillance Value Of 1352 Kw For Emergency Diesel Generators Since This Value Does Not Reflect Actual Configuration</strong><br /><i>Abstract:&nbsp;</i>On 11/13/91, utility management was notified by a similar plant that a potential concern existed with the ability to satisfy the 1352 Kilowatt (Kw) Essential Service Water (ESW) pump load rejection requirement of Technical Specification (T/S) Surveillance 4.8.1.1.2.f(2). Utility management immediately initiated an investigation into the applicability to Callaway Plant. On 11/14/91 at 1515 CST, it was determined that the plant had not demonstrated verbatim compliance with T/S surveillance 4.8.1.1.2.f(2) and T/S 3.0.3 was entered. The plant was in Mode 1 - Power Operations at 100% reactor power. <br /><br /> The utility Shift Supervisor immediately scheduled a plant shutdown to begin at 1715 CST. On 11/14/91 at 1620 CST, a Temporary Waiver of Compliance was granted to waive the requirement to initiate action to shutdown the plant per T/S 3.0.3 until an emergency T/S amendment to change the 1352 Kw load rejection requirement was approved. The value of 1352 Kw is not representative of the actual installed configuration. The value was based on assumed load values used to size the diesel generators. The proposed change will clarify that the ESW pump is the largest single emergency load without specifying a Kw rating. Previous surveillance testing has verified the ability of the diesel generators to reject the largest single emergency load and maintain required voltage and frequency.
4831991008 | Callaway | 12/10/1991 | 12/31/1991 | 9201140152 | <strong>Failure To Verify That Containment Penetration Vent Valve Was Locked Closed Per Technical Specification 4.6.1.1.A Prior To 1989 Due To Incorrect Locked Valve List</strong><br /><i>Abstract:&nbsp;</i>On 12/10/91, while in Mode 1 at 100 percent power, a review of surveillance procedure OSP-GP-00001, Containment Integrity Verification, revealed that the Residual Heat Removal (RHR) pump 'A' suction header vent valve (EJV154) had not been verified as locked closed prior to 3/14/89. Technical Specification (T/S) 4.6.1.1.a requires that containment penetrations with valves located inside containment be verified during cold shutdown as locked closed. <br /><br /> EJV154 was not included in a 3/12/82 listing of locked containment penetration valves. This caused a RHR system drawing revision deleting the locked requirement. As this drawing was used to develop procedure OSP-GP-00001, EJV154 was not included. On 10/21/87, a utility licensed operator requested that EJV154 be designated locked closed on plant drawings for containment integrity purposes. When EJV154 was determined to require locked closed verification on 11/27/87, utility personnel reviewing this did not evaluate the applicability of T/S 4.6.1.1.a. <br /><br /> The drawing, valve line-up, and surveillance procedures have been revised to ensure that EJV154 is verified locked closed. No other T/S prohibited conditions were identified by the most recent utility review of containment penetrations. This is an isolated occurrence. No additional corrective actions are required.
4981991001 | South Texas 1 | 01/22/1991 | 02/21/1991 | 9102260312 | <strong>Unplanned Containment Ventilation Isolation Actuation Due To A Spurious Signal From The Radiation Monitoring System</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1991, Unit 1 was in its third refueling outage with no fuel in the reactor vessel. At 1520 hours, a Containment Ventilation Isolation actuation occurred. Operations personnel verified that all equipment actuated as designed. The radiation monitoring system did not indicate any high radiation conditions. Radiation levels in the Reactor Containment Building were determined to be normal prior to and following the actuation. The Containment Ventilation Isolation actuation appears to be the result of a spurious actuation of the radiation monitoring system. However, the cause of the spurious signal from the radiation monitoring system could not be determined.
4981991002 | South Texas 1 | 01/26/1991 | 11/18/1991 | 9111250173 | <strong>Unplanned Safety Injection Actuation Due to Less than Adequate Work Instructions for a Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1991, Unit 1 was in its third refueling outage with no fuel in the reactor vessel and the Reactor Coolant System vented to atmosphere. At 0850 hours, during the first performance of a preventive maintenance (PM) work activity, an automatic actuation of the Safety Injection (SI) system occurred in one of three trains (Train C) as a result of less than adequate PM work instructions. All associated Engineered Safety Features (ESF) equipment operated as expected. The cause of the less than adequate work instructions was personnel error in that two supervisors failed to require further review of work instructions which they believed had potential for causing an unplanned ESF actuation. Corrective actions include inactivating the subject PM and the associated PMs for the other actuation trains in both Units. These PMs will be corrected prior to future use. Further corrective actions were taken to issue a training bulletin to appropriate operations and maintenance supervisors describing the event, and to counsel the two supervisors on the necessity of performing thorough reviews of procedures and work instructions that have the potential to cause unplanned ESF actuations.
4981991003 | South Texas 1 | 01/27/1991 | 02/20/1991 | 9102250306 | <strong>Unplanned Engineered Safety Features Actuation Due to a Radiation Monitor Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1991, Unit 1 was in its third refueling outage with no fuel in the reactor vessel. At 0335 hours a radiation monitor for the Control Room Envelope went into high alarm and actuated the Control Room Ventilation System to the recirculation with filtered makeup mode. The alarm cleared after approximately two minutes. Samples of the Control Room atmosphere did not identify any activity. The redundant monitor remained in the normal range throughout this period. Maintenance was performed on the actuated monitor and the monitor was successfully calibrated. The cause of this event is unknown.
4981991004 | South Texas 1 | 02/15/1991 | 03/15/1991 | 9103260059 | <strong>Partial Loss of Offsite Power Actuation During Routine Maintenance</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1991, Unit 1 was in its third refueling outage with no fuel in the reactor vessel. At 0259 hours, a partial loss of offsite power occurred during maintenance of an overcurrent protection relay. The supply breaker to 13.8 kV Standby bus 1H tripped which supplies power to the 4.16 kV Engineered Safety Features (ESF) bus E1C. Standby Diesel Generator #13 loaded as required, restoring power to Train C. The cause of this event was determined to be lack of attention to work performance methods. An electrician inadvertently touched the trip contact on the protective relay in the process of inserting the contact plug. Corrective actions include training of maintenance personnel, revision of appropriate GE relay calibration procedures and addition of a training objective on the proper method for installing relay contact plugs.
4981991005 | South Texas 1 | 02/18/1991 | 03/20/1991 | 9103270165 | <strong>Technical Specification Violation Due to Opening the FHB Truck Bay Doors During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1991, Unit 1 was in Mode 6. At 1334 hours, the Fuel Handling Building (FHB) truck door was opened while operations personnel were involved in fuel handling as part of the core reload. At approximately 1340 hours, an operator on the FHB fuel bridge noted that the door was opened and secured all fuel movement. The doors were closed at 1359 hours. The FHB exhaust air system was rendered inoperable when the FHB truck doors were opened. Fuel movement was suspended immediately upon discovery as required by Technical Specification 3.9.12 until the FHB ventilation system was restored to an operable condition. The cause of this event was incomplete administrative controls on the FHB truck door. There were no controls in place to ensure the appropriate Technical Specification requirements for the FHB exhaust air system were followed. Corrective actions include placement of additional locks on the FHB truck doors, issuance of a bulletin/night orders to security and health physics personnel to ensure that in addition to security and health physics that operations personnel are also present at the door prior to opening, issuance of a memorandum to licensed operators discussing this incident, an evaluation to determine the effect of the FHB doors on the operability of the FHB exhaust air system, establishment of appropriate administrative controls and the identification of any other doors which require similar controls.
4981991006 | South Texas 1 | 02/22/1991 | 03/22/1991 | 9103280307 | <strong>Class 1E 120 Volt AC Distribution Panel Energized by Alternate Power Source in Violation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1991, Unit 1 was in Mode 6 in its third refueling outage. At 0603 hours during performance of a surveillance test, it was discovered that the Class 1E 120 volt distribution panel DP002 was energized from its alternate power supply in violation of Technical Specification 3.8.3.2. Immediate actions were taken to restore the distribution panel to its proper alignment. The causes of this event were failure to coordinate the transfer of power to the distribution panel due to inadequate verbal communications and failure to monitor the associated alarms which annunciate in the control room during an undervoltage condition. Corrective actions include training of licensed and non-licensed operators, and an evaluation of the plant's numbering scheme for electrical panels.
4981991007 | South Texas 1 | 03/09/1991 | 10/08/1991 | 9110180008 | <strong>Engineered Safety Features (ESF) Actuation Due To Switchyard Breaker Fault</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1991, Unit 1 was in Cold Shutdown during a refueling outage, and Unit 2 was operating at 100 percent power. While returning a transmission line to service, a switchyard breaker experienced a phase to ground flashover caused by a dislodged connecting pin in the interruptor linkage mechanism. The snap ring which holds the connecting pin in place had fallen out. The breaker fault caused protection circuitry to clear the South bus and offsite power was lost to several Engineered Safety Features (ESF) buses. One Unit 1 Standby Diesel Generator (SBDG) and two Unit 2 SBDGs started and carried their loads. Although the immediate cause of this event is the dislodged connecting pin, the cause for the snap ring falling out of place is not known. As a result of this event, the breaker has been repaired and a modified pin design has been installed in all breakers of the same model as the breaker which had a fault.
4981991008 | South Texas 1 | 03/15/1991 | 10/15/1991 | 9110240262 | <strong>Partial LOOP on Trains A and B Caused By Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1991, Unit 1 was in mode 5 due to a refueling outage. The unit experienced a partial loss of offsite power (LOOP) to Train A at 1313 hours due to actuation of the unit auxiliary transformer pilot wire relay which opened a switchyard breaker. During recovery from the first LOOP, a LOOP occurred on Train B of Unit 1 at 1328 hours when a 13.8 KV standby bus feeder breaker was opened by a control room operator. Both LOOP events were due to inadequate procedures. The subject procedures have been revised appropriately. In addition, a Load Center feeder breaker failed to close due to inadequate lubrication. Work requests have been issued to address proper lubrication.
4981991009 | South Texas 1, South Texas 2 | 03/11/1991 | 07/30/1991 | 9108050280 | <strong>Diesel Generator #12 and #13 Valid Failures Due to Cracked Fuel Injector Nozzles Tips</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1991, a cracked fuel injector nozzle tip from lot 150010 was found in Standby Diesel Generator (SDG) #12. On March 13, 1991, a cracked nozzle tip from lot 150006 was found in SDG #13, Houston Lighting & Power (HL&P) conducted eddy current examination of 151 injector nozzle tips from these and other SDGs as well as spares, and identified several additional cracked nozzle tips from lot 150006. Cooper-Bessemer (the SDG supplier) notified the NRC pursuant to 10CFR21 and HL&P filed LER 91-009 Rev. 0 accordingly. Additional investigations resulted in the conclusions that inadequate ligament thickness and excessive nitriding depth are the probable causes of the failures. HL&P also removed lot 150009 from service, which showed cracking in laboratory examination, and, as a conservative measure, all lots of the 1500XX series manufactured by Allied Signal were also removed. A review of current manufacturing methods showed that improvements had been made in dimensional control. The information developed has been shared with Cooper-Bessemer and MPR Associates (Project Manager of the Cooper Bessemer Owner's Group). Additional recurrence controls have been added at STPEGS including examination for depth of nitriding.
4981991010 | South Texas 1 | 04/04/1991 | 11/18/1991 | 9111250183 | <strong>Manual Engineered Safety Features Actuation Due to a Toxic Gas Alarm</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1991, Unit 1 was in Mode 1 at 13 percent power. At 0843 hours, the main control room received a toxic gas high concentration alarm. The control room ventilation system was manually placed into the recirculation mode as a conservative response. No toxic gas was determined to be present after an immediate investigation. The alarm occurred as a result of a failure in the Emergency Response Facilities Data Acquisition and Display System computer. The cause of the alarm was a failed fiber optics data acquisition controller subsystem printed circuit board. The failed printed circuit board has been replaced as a result of the event.
4981991011 | South Texas 1 | 04/08/1991 | 05/08/1991 | 9105140266 | <strong>Steam Generator 1D Feedwater Isolation Valve (FWIV) failed the partial stroke test</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1991, Unit 1 was in Mode 1 at 77% power. At 2205 hours, an operability test was performed on the Train D Feedwater Isolation Valve (FWIV). The valve stroked as required; however, one of the two redundant solenoid valves which actuates the feedwater valve failed. Since the conditions of Technical Specification 3.7.1.7 for Modes 1 and 2 could not be met, a plant shutdown was initiated and a Notification of Unusual Event (NOUE) was declared. The NRC was notified at 0023 hours on April 9, 1991. The FWIV was secured and tagged at 0650 hours and Unit I was brought to Mode 3 at 0803 hours. The cause of this event was failure of one of two redundant FWIV solenoid valves to operate due to hydraulic fluid polymerization. Corrective actions include eliminating the major source of moisture entry into the hydraulic system, flushing the hydraulic system and replacing the hydraulic fluid, revision of Preventive Maintenance activities and plant modifications to add clean-up skids and relocate the solenoid valves.
4981991012 | South Texas 1 | 04/12/1991 | 10/31/1991 | 9111070005 | <strong>Reactor Trip Due to Motor Generator Malfunction</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, at 0418, the Unit 1 reactor tripped from 40% power. A turbine trip, feedwater isolation and auxiliary feedwater actuation occurred as a result of the reactor trip. Systems operated as designed in response to the reactor trip. It was determined that Rod Drive Motor Generator (RDMG) Set #11 tripped due to a transient induced by RDMG #12 which was found running with its motor and generator breakers closed with no output voltage to the Reactor Trip Switchgear. It is believed that intermittent pick-up and drop-out of the 2R relay, which actuates contacts to supply power to the RDMG Set #12's generator voltage regulator, caused instability in the voltage regulator operation. The 2R relay malfunction was due to a defective output switch. The instability of the voltage regulation resulted in transients that caused a reverse current to the RDMG Set #11 and a subsequent trip of the generator output breaker. It is also believed that the 2R relay contacts supplying power to the voltage regulator eventually remained open long enough to allow a loss of the generator field in the RDMG Set #12. A loss of the generator field results in zero output voltage from the generator. The loss of both of the power sources to the Reactor Trip Switchgear resulted in a reactor trip. The 2R relay's timer and control relay were replaced and a procedural change has been made to enhance the detection of relay timer malfunctions. An additional procedural change has been made to require the marking of leads that do not have unique identification markings.
4981991013 | South Texas 1 | 04/12/1991 | 05/10/1991 | 9105130376 | <strong>Train B ESF Actuation Caused by Less Than Adequate Troubleshooting by Instructions</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1991, Unit 1 was in Mode 3 at normal operating pressure and temperature. At 1321 hours, during troubleshooting of an Engineered Safety Feature (ESF) Sequencer automatic testing failure, a mode III (safety injection coincident with loss of offsite power) sequencer actuation was initiated in Train B. The actuation resulted from less than adequate troubleshooting instructions. Plant equipment operated as designed and there were no significant transients as a result of the ESF sequencer actuation. Troubleshooting program procedures will be revised as a corrective action.
4981991014 | South Texas 1 | 04/20/1991 | 01/15/1992 | 9201220010 | <strong>Erratic Containment Extended Range Pressure Channel Output</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1991, Unit 1 was in mode 1 at 100% power. At 0406 hours, while conducting a containment supplemental purge to lower the containment pressure in response to a Containment High Pressure alarm, containment extended range pressure channel 9759 was found to read 5 psig while channel 9760 read 0 psig. Channel 9759 was declared inoperable at 0407 hours. Review of historical computer records indicated that the channel had been inoperable in excess of the seven-day allowed outage time. After initial recalibration, subsequent channel check surveillance revealed an additional erratic output signal by the transmitter. The transmitter control card was replaced and the transmitter was calibrated. Channel checks were performed weekly for one month to confirm the channel was repaired. Although no generic failure mechanism has been established, the failure rates are consistent with industry experience. These transmitters are being monitored under the facility trending program.
4981991015 | South Texas 1 | 04/22/1991 | 05/22/1991 | 9105300179 | <strong>Engineered Safety Feature Actuation Caused by a Failed Light Emitting Diode</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1991, Unit 1 was in Mode 1 operating at 100% power. At 0200, during performance of a Train C Engineered Safety Feature Sequencer surveillance test, the Train C Auxiliary Feedwater (AFW) Pump inadvertently started. The pump was secured at 0208. The cause of this event was failure of a Light Emitting Diode (LED) in the Sequencer test circuitry. The LED has been replaced. An evaluation has determined that a similar failure of an LED in the Sequencer actuation circuitry, rather than the test circuitry, would prevent actuation of the associated ESF component. The functionality of the sequencer is tested quarterly. In addition, if such a failure occurred, an alarm would indicate the affected component had failed to start and operator action could be taken to start the component. Therefore, since there has been only one such failure at STP, no additional corrective action is planned.
4981991016 | South Texas 1 | 05/13/1991 | 06/11/1991 | 9106180160 | <strong>Failure to Perform a Surveillance Test Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1991, at approximately 2230 hours, Unit 1 was in Mode 1 at 100 percent power. It was discovered that the Technical Specification 3/4.7.1.4 requirements for determining the specific activity of the secondary coolant system had not been performed within the required surveillance interval. This is a violation of Technical Specification 3/4.7.1.4 and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). Steam generator blowdown radiation monitor data was checked, and it was verified that secondary activity had not exceeded normal values or the Technical Specification limit during this period. The cause of this event was failure to ensure testing was performed before exceeding the surveillance interval. Corrective actions included issuance of special orders, and changing procedure and Laboratory schedules to improve visibility and increase awareness of surveillance times.
4981991017 | South Texas 1 | 05/26/1991 | 06/25/1991 | 9107020304 | <strong>Control Room Ventilation Actuation of Recirculation Mode Due to a Spurious SignaL from a Toxic Gas Analyzer</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1991, Unit 1 was in Mode 1 at 100 percent power. At 1534 hours, the control room ventilation system actuated to the recirculation mode as a result of a spurious trip from a toxic gas analyzer. The exact cause of the event could not be determined but has been attributed to poor electrical connection on one or more plug-in integrated circuit chips in the analyzer. Corrective actions include troubleshooting of the failed analyzer, further design improvements to minimize false actuation signals, and development of preventive maintenance tasks to periodically reseat integrated circuit chips in the toxic gas analyzers.
4981991018 | South Texas 1, South Texas 2 | 07/02/1991 | 08/01/1991 | 9108050243 | <strong>Technical Specification Violation Due to Inoperable Radioactive Gaseous Effluent Alarm</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1991, Units 1 and 2 were in Mode 1 at 100 percent power. At about 1300 hours, an engineer realized that the alarm associated with the Condenser Air Removal System (CARS) wide range noble gas activity monitor was not functioning. As a result the CARS noble gas monitor was declared inoperable. It was determined that this condition has existed since the startup of each unit. The cause of the event has been attributed to misunderstanding of the internal functions of the monitor when process flow is below design values. Corrective actions include changing and reviewing the database configurations of the gas activity monitors, and verification of the process flow substitute value function.
4981991019 | South Texas 1 | 09/05/1991 | 02/25/1993 | 9303080068 | <strong>Reactor Coolant System Leak Rate Greater Than Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, Unit 1 was in, Mode 1 at 100% power. At 1806 hours, the Control Room received a Reactor Coolant Drain Tank (RCDT) level HI-HI/LO-LO alarm. At 1838 hours, Reactor Coolant System (RCS) leakage was determined to be approximately 15 gallons per minute (GPM) which is greater than the Technical Specification 3.4.6.2 limits. As a result, the Plant declared an Unusual Event. At 1954 hours, plant personnel entered the Reactor Containment Building (RCB) to investigate. By isolating normal letdown with excess letdown in service and observing the leak rate decrease, the leakage was identified to be in the RCS letdown valve A1CVLCV0465. This event resulted from damaged valve packing. The valve was inspected and no evidence was found to indicate a cause for the packing failure. The valve was repacked and returned to an operable status. The RCS letdown valve was subsequently disassembled to attempt to locate and repair the cause for the two original packing failures. No specific causal factor was identified.
4981991020 | South Texas 1 | 09/14/1991 | 10/14/1991 | 9110250041 | <strong>Technical Specification Violation Due to Failure to Perform Two Rod Position Surveillances</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1991, at 1439, Unit 1 was in Mode 1 at 100% power when the Rod Position Deviation Monitor was incorrectly declared operable by the Shift Supervisor. The error was discovered on September 15, 1991, at 0415 when the "ROD DEVIATION" annunciator was received. During the time the monitor was incorrectly considered operable, two increased frequency surveillances were missed, resulting in a Technical Specification violation. The cause of the event was that errors were made by three Shift Supervisors in implementing the procedural requirements regarding the Operability Tracking Log system. Also, the Shift Supervisor who incorrectly declared the monitor operable did not consult all references prior to making an operability determination. An additional cause was inadequate identification of the effect of the Temporary Modification package which documented the monitor inoperability. A briefing will be given to the licensed operators stressing the importance of the Operability Tracking Log system as described in the Configuration Management Procedure. Also, a memo has been sent to all Senior Reactor Operators stressing the need to exhaust all available references prior to making operability determinations. The Temporary Modification request form has been revised to provide a clearer operability determination reminder.
4981991021 | South Texas 1 | 10/10/1991 | 11/08/1991 | 9111250263 | <strong>Reactor Trip Due to Personnel Error Inadvertently Tripping the Feeder Breaker to Auxiliary Bus "1J"</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1991, at 2056, Unit 1 was in Mode 1 at 100% power when power from the 1J Bus was lost. During the performance of work activities, a Maintenance Electrician misapplied multimeter test leads in an energized circuit with the multimeter set to read "RESISTANCE". The misapplied test leads energized relay 2A which actuated the 86X lockout relay causing breaker P150 to trip and de-energize the 1J Bus. Upon loss of power on 1J Bus, Reactor Coolant Pump (RCP) 1D tripped and caused a reactor trip due to low coolant flow. The bus was re-energized at 2059 from the Unit Auxiliary Transformer with no further incidents. The primary cause of this event was personnel error. The Maintenance Electrician's attention to detail during work performance, elementary drawing reading and troubleshooting techniques were less than adequate. A training session is being held for appropriate Plant Personnel stressing the application of Self Verification during work performance.<br /><br /> A testing program will be implemented to ensure that applicable personnel are qualified to use elementary drawings to aid in performance of maintenance activities.
4981991022 | South Texas 1 | 10/14/1991 | 11/13/1991 | 9111190266 | <strong>Reactor Trip During Performance of SSPS Logic Functional Test</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1991, at 2304 hours, Unit 1 was in Mode 1 at 100% power. Solid State Protection System (SSPS) Logic Train R Functional Test was in progress when the Licensed Operator performing the surveillance misunderstood the intent of a note in the procedure and failed to block the Turbine Trip signal before proceeding to the next step. The "Memories" test switch was placed in position 16 and an automatic Train R trip signal was generated. Train R trip signal generated a "Turbine Trip upon Reactor Trip" signal which had not been blocked and the "Memories" test switch also malfunctioned, which if it had functioned properly should have also blocked the trip signal. Subsequently, the Main Turbine tripped and, coincident with a "Reactor Power Above 50%" signal, a valid Train S Reactor Trip signal was generated tripping the reactor. The cause of this event was personnel error by the Licensed Operator who exercised poor judgement while performing the test. Contributing factors were a less than ideal procedure and the malfunction of the "Memories" test switch. Corrective actions include site-wide training sessions for appropriate plant personnel stressing the application of self verification during work performance, counseling of the licensed operator involved in the event, revision of all SP series surveillances performed at power that have the potential to trip the unit/main turbine, to specifically require that an appropriate turbine/reactor trip block be instituted whenever there is a possibility that the SSPS will generate an unwanted trip signal.
4981991023 | South Texas 1, South Texas 2 | 10/20/1991 | 11/19/1991 | 9111270022 | <strong>Residual Heat Removal Motor Lead Cracking at Epoxy Interface</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1991 Unit 1 was in Mode 4 and Unit 2 was in No-Mode during a scheduled refueling outage, when the determination was made that cracks found on the Residual Heat Removal (RHR) motor "T" leads epoxy interface were reportable. On October 11, 1991, while performing work on Unit 2 RHR motor "A", leads for the motor were discovered to be damaged. Examination of the remaining Unit 2 RHR pump motors and Unit 1 Train A and Train C, revealed similar motor lead insulation cracking on all of these RHR pumps. The apparent cause of this cracking is that differences in the flexibility of the motor lead between the original insulation and insulation using Raychem sleeves, concentrated the bending stress in the cable in the area adjacent to the epoxy causing the cracking. The Unit 1 RHR pump motor "T" lead insulation cracks have been repaired, and Unit 2 RHR motor "T" leads will be repaired during the current refueling outage. The repairs are designed to prevent recurrence of the cracking.
4981991024 | South Texas 1, South Texas 2 | 10/31/1991 | 11/22/1991 | 9111270005 | <strong>A Safety Analysis Deficiency Concerning the Pressurizer Safety Relief Valve (SRV) Loop Seal Delay Time</strong><br /><i>Abstract:&nbsp;</i>During a review of NRC Information Notice 89-90 Supplement 1, dated September 5, 1991 and WCAP-12910, with Unit 1 in mode 1 at 100 percent power and Unit 2 in a mode 6 refueling outage, it was discovered that the UFSAR Chapter 15 safety analysis did not consider the time required to purge the loop seal for the pressurizer Safety Relief Valves (SRVs). Immediate actions taken to investigate the problem confirmed that the calculated peak RCS pressure for the Locked Rotor event with the pressurizer SRV loop seal delay time would exceed the NRC safety limit of 110% design pressure. On October 30, 1991, a Station Problem Report was issued identifying the deficiency in the safety analysis. On November 5, 1991, a Justification for Continued Operation (JCO) was issued. The JCO concluded that the condition does not result in either STPEGS Units 1 or 2 being in an unsafe condition. The cause of the event was that the NSSS vendor did not consider the delay time associated with purging the pressurizer SRV loop seals in the safety analysis. Since the JCO for this issue identified that no unsafe condition exists, no immediate corrective actions are planned. After the NRC approval of WCAP-12910 and Westinghouse Owners Group (WOG) resolution of this issue, additional actions will be developed as necessary.
4991991001 | South Texas 2 | 01/09/1991 | 02/08/1991 | 9102110269 | <strong>Manual Reactor Trip Due to Full Closure of a Feedwater Isolation Valve During Operational Problem Investigation</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1991, Unit 2 was in Mode 1 at 100% power. At 2207 hours, Feedwater Isolation Valve (FWIV) 2C closed during the investigation of low nitrogen and low hydraulic pressure alarms for FWIV 2C. The resultant loss of feedwater flow caused a decrease in Steam Generator (SG) level and the reactor was manually tripped. The cause of the manual reactor trip was a failed-closed feedwater isolation valve. The feedwater isolation valve closed when an operator incorrectly removed a power supply fuse to the trip solenoid. The fuse was removed when trying to determine the source of power loss to the FWIV hydraulic skid. This was caused by failure to coordinate operational problem investigation and the use of information without providing necessary verification; annunciator response procedures did not provide direction pertaining to a loss of power; and lack of formal training on the investigation of power supplies. Corrective actions include: training of licensed and non-licensed operators; revision of annunciator response procedures; as well as other recurrence measures.
4991991002 | South Texas 2 | 01/31/1991 | 03/04/1991 | 9103120274 | <strong>Technical Specification Violation Due to the Failure to Perform a Required Post Maintenance Test</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1991, Unit 2 was in Mode 1 at 100% power. During a review of a completed work package for weld repairs on the turbine-driven Auxiliary Feedwater (AFW) Pump 24 steam supply line, it was discovered that the ASME Section XI pressure test required by Technical Specification 4.0.5 had not been performed prior to returning the system to service. This resulted in the AFW Pump 24 being administratively inoperable from December 5, 1990 to February 3, 1991. The causes of this event are less than adequate procedural controls which allowed the planner to defer completion of the pressure test data sheet, less than adequate review of the revised work package by the cognizant system engineer and less than adequate review of the post maintenance test requirements prior to return to service. Corrective actions include successful performance of the Code pressure test, revision of appropriate procedures and training of appropriate maintenance planners and system engineers.
4991991003 | South Texas 2, South Texas 1 | 03/14/1991 | 04/15/1991 | 9104220136 | <strong>Reactor Trip Caused by Actuation of a Generator Protective Relay</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1991, Unit 2 was operating at 100% while Unit 1 was in Mode 5. At 1810 hours, Unit 1 Control Room personnel closed the switchyard breaker to energize the Unit 1 Main and Auxiliary Transformers. Immediately following this breaker closure, the Unit 2 B Phase Generator Isophase Bus differential relay actuated. This caused the generator lockout relay to actuate which resulted in a turbine trip and reactor trip. During the recovery process the Main Steam Isolation Valves (MSIV) were closed. A Steam Generator (SG) MSIV was subsequently reopened while a SG level was near the low-low setpoint and caused an Auxiliary Feedwater actuation. The protective relay actuation was caused by differences in the saturation rates of the two current transformers that supply the differential relay. The AFW actuation was caused by operating procedures that failed to provide guidance regarding minimum SG levels during MSIV manipulations. The corrective actions relative to the current transformers will be reported in LER 91-004, which describes a similar subsequent reactor trip event. Procedures will be revised and this event will be included in requalification training to minimize the potential for unnecessary AFW actuations.
4991991004 | South Texas 2, South Texas 1 | 03/30/1991 | 04/29/1991 | 9105060214 | <strong>Reactor Trip Caused by Actuation of a Generator Protective Relay</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1991, Unit 2 was operating at 100% while Unit 1 was in Mode 3. Unit 1 Control Room personnel closed the switchyard breaker to energize the Unit 1 Main and Auxiliary Transformers. Immediately following this breaker closure, the Unit 2 B Phase Generator Isophase Bus differential relay actuated. This caused the generator lockout relay to actuate which resulted in a turbine trip and reactor trip. The protective relay actuation was caused by differences in the saturation rates of the two current transformers that supply the differential relay. An evaluation is underway to establish the feasibility of hardware changes to address this problem. As an interim measure, a temporary modification has been installed that removes the protective function from the affected differential relay. Redundant protection is provided by other protective relays.
4991991005 | South Texas 2 | 04/11/1991 | 11/11/1991 | 9111180286 | <strong>Engineered Safety Features (ESF) Actuation of Control Room Envelope HVAC Trains B and C Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1991, Unit 2 was in Mode 1 at 100 percent power. At 1130, an automatic Engineered Safety Features (ESF) actuation of CRE HVAC Trains B and C to emergency mode occurred. Control Room Envelope (CRE) HVAC Train A had been manually actuated to the emergency mode in support of a surveillance procedure. No indication of a high radiation or safety injection signal was found. There has been no cause established for this actuation.
4991991006 | South Texas 2 | 05/16/1991 | 06/14/1991 | 9106180374 | <strong>Control Room Ventilation Actuations of Recirculation Mode Due to Two Spurious Signals from a Toxic Gas Analyzer</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1991 Unit 2 was in Mode 1 at 100 percent power. At 0558 hours, the control room ventilation system actuated to the recirculation mode as a result of a spurious trip from a toxic gas analyzer. The spurious actuation signal self-reset at 0559 hours. Also at 0042 hours on May 21, 1991 another similar actuation occurred from the same analyzer as the first event. The exact cause of both events could not be determined but has been attributed to poor electrical connection on one or more plug-in integrated circuit chips in the analyzer. Corrective actions include troubleshooting of the failed analyzer, further design improvements to minimize false actuation signals, and development of preventive maintenance tasks to periodically reseat integrated circuit chips in the toxic gas analyzers.
4991991007 | South Texas 2 | 05/22/1991 | 01/29/1992 | 9202030253 | <strong>Reactor Trip Caused By Inadvertent Actuation of Generator Breaker Emergency Trip</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1991, Unit 2 was in mode 1 at 100% power. At approximately 2220 hrs, while waiting in the area of the main generator breaker to unlock a local cabinet for an Electrical Maintenance individual, a non-licensed operator inadvertently actuated the local generator breaker emergency trip pushbutton. The sudden loss of secondary load caused an automatic over temperature delta temperature (OTDeltaT) reactor trip. Pressurizer spray was unable to reduce the pressure before the pressurizer PORVs opened at approximately 2335 psig. Steam generator 2C power-operated relief valve (PORV) failed to open even though the pressure exceeded the lift setpoint. The non-licensed operator responsible for the trip was counselled with regards to paying strict attention to performance of operations activities. The Steam Generator 2C PORV has been repaired. Other switch designs have been reviewed to identify changes that can prevent similar inadvertent actuations.
4991991009 | South Texas 2 | 07/07/1991 | 08/23/1991 | 9108290165 | <strong>Engineered Safety Feature Actuation Caused by a Failed Light Emitting Diode</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1991, Unit 2 was in Mode 1 at 100% power. During performance of an A train Engineered Safety Feature (ESF) Sequencer Surveillance test the A train Auxiliary Feedwater (AFW) pump inadvertently started. The test was secured at 0220 hours. The cause of the event appears to be a failed open Light Emitting Diode(LED) in the circuit associated with the blocking relay for the AFW pump. This conclusion is based on indications noted during ESF Sequencer troubleshooting. The circuit board associated with the AFW pump blocking relays and the blocking relay circuits were tested satisfactorily. An engineering review will be conducted to determine if a generic problem may exist with the LEDs used in sequencer circuits.
4991991010 | South Texas 2 | 12/24/1991 | 09/23/1992 | 9209300002 | <strong>Automatic Reactor Trip and Safety Injection Actuation due to Low Pressurizer Pressure</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1991, at 1644 hours, Unit 2 was operating at 30% Rated Thermal Power (RTP) when pressurizer spray valve PCV-655C failed open. This ultimately caused an automatic reactor trip and Safety Injection (SI) actuation on low pressure at 1648 hours from 16% RTP. Three Reactor Coolant Pumps (RCPs) were secured to terminate the transient. All available safety equipment performed as designed and no actual injection to the reactor occurred. The cause was disengagement of the feedback arm linkage to the valve stem connecting plate on the pressurizer spray valve controller. Locking nuts were added to the spray valve feedback arm linkage connecting screws. Corrective actions included improving maintenance work instructions, conducting plant management reviews with personnel to discuss the event, and providing training on lessons learned from the event. LER\92227001.U2
5281991001 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 01/10/1991 | 02/11/1991 | 9102200280 | <strong>Postulated Reactor Coolant System Leak Not Included In Design Basis</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 MST on January 10, 1991, Palo Verde Units 1, 2, and 3 were in MODE 1 (POWER OPERATION) at approximately 100 percent power when PVNGS Engineering determined that a postulated break in a Reactor Coolant Pump (RCP) high pressure seal cooler could result in a reactor coolant system (RCS) leak outside containment. A conservative evaluation of this postulated event based on assumptions used in the Standard Review Plan (NUREG 0800) determined that the Exclusion Area Boundary cumulative thyroid dose could exceed 10CFR100 limits. An evaluation based on existing RCS activity showed that doses would be a small fraction of 10CFR100 limits. <br /><br /> The cause was that a tube rupture in the seal cooler and its effect was not considered in the original plant design. <br /><br /> Immediate corrective actions were taken to: 1) monitor RCS activity to ensure 10CFR100 limits would not be exceeded as a result of this postulated event and 2) monitor the Nuclear Cooling Water System to provide early detection of a seal cooler leak. A design change is being developed to mitigate the postulated event described in this LER. The design change is expected to be completed in Units 1, 2, and 3 by July 1993. <br /><br /> No previous similar events have been reported in accordance with 10CFR50.73.
5281991002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 02/06/1991 | 04/24/1991 | 9104300155 | <strong>Surveillance Performance Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1991, at approximately 1200 MST, Palo Verde Unit 1 was in Mode 5 (COLD SHUTDOWN) and Palo Verde Units 2 and 3 were operating at approximately 100 percent power when Compliance personnel determined that the 18 month Technical Specification (TS) required surveillances to demonstrate operability of each Emergency Diesel Generator (EDG) were conducted during unit operation. This was contrary to the TS requirement that the surveillances be performed during shutdown.<br /><br /> The cause of the event was a misinterpretation of the basis for performing the TS required surveillance while shutdown. The phrase "during shutdown" was incorrectly interpreted as only applying to the surveillance requirements which could not be performed within the 72 hour ACTION period for the EDG being out of service. <br /><br /> The event was discussed with responsible PVNGS management and a memorandum was issued to ensure that TS required surveillances would only be performed during Modes 4 (HOT SHUTDOWN), 5, or 6 (REFUELING - including core defueled) when TS states "during shutdown." <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281991003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 02/08/1991 | 03/09/1991 | 9103150009 | <strong>Spray Pond Cross Valves Not Included in Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1538 MST on February 8, 1991, Palo Verde Unit 1 was in MODE 5 (COLD SHUTDOWN) and Palo Verde Units 2 and 3 were in MODE 1 (POWER OPERATION) at approximately 100 percent power when the Unit 1 Shift Technical Advisor identified that the essential spray pond cross connect valves had not been verified to be in their correct position (closed) in accordance with Technical Specification Surveillance Requirement 4.7.4.1. <br /><br /> Therefore, the operability requirements of Technical Specification Limiting Condition for Operation 3.7.4 and the associated ACTION were not met. However, these valves are routinely maintained in the closed position to maintain independence of each essential spray pond and its associated essential spray pond loop. <br /><br /> The cause of this event was a failure to recognize that the position of the essential spray pond cross connect valves was required to be verified in accordance with Technical Specification Surveillance Requirements and the resultant omission of these valves from valve position verification procedures. <br /><br /> As immediate corrective action the valve positions were verified. As action to prevent recurrence, the valves were locked shut and added to the locked valve procedure. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281991004 | Palo Verde 1 | 03/20/1991 | 04/19/1991 | 9104230003 | <strong>ESF Actuation Due to Loss Of Power To 4.16 KV Bus</strong><br /><i>Abstract:&nbsp;</i>At approximately 1414 MST on March 20, 1991, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a supply breaker opened between the Unit 1 non-Class 1E 13.8 KV switchgear busses resulting in a loss of power to the Unit 1 train "A" Class 1E 4.16 KV bus. This resulted in a Loss of Power (LOP) Engineered Safety Feature (ESF) signal being generated. The ESF signal resulted in automatic load shed of the Class 1E bus and started the train "A" Emergency Diesel Generator (DG). The DG started and assumed the loads as designed. All equipment functioned as designed. No other ESF protection signals were activated and none were required. Unit 1 continued to operate normally at 100 percent power throughout the event.<br /><br /> The cause of the event was personnel error by an electrical maintenance worker who was performing periodic maintenance on the non-Class 1E 13.8 KV switchgear. The individual inadvertently brushed the breaker trip relay which resulted in the actuation. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281991005 | Palo Verde 1 | 04/25/1991 | 05/16/1991 | 9105230229 | <strong>ESF Actuation Due to Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1991, at approximately 1735 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) at approximately 100 percent power, when a spurious Train "A" Containment Purge Isolation Actuation Signal (CPIAS) was initiated on the Balance of Plant Engineered Safety Features Actuation System. The Train "A" CPIAS resulted in the designed cross trips of Train "B" CPIAS and Train "A" and "B" Control Room Essential Filtration Actuation Signals (CREFAS). The actuations occurred when the Train "A" Power Access Purge Area Radiation Monitor (RU-37) spiked above its high alarm/trip setpoint. At the time of the event, no containment purge was in progress and all Containment Purge System isolation valves were closed. All components operated as designed. Control Room and Radiation Protection personnel verified that normal radiation levels existed in the area of RU-37. <br /><br /> The cause of the RU-37 spiking was an infantile failure of the detector's Geiger-Mueller tube. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 which resulted from a failure of a detector's Geiger-Mueller tube.
5281991006 | Palo Verde 1 | 05/17/1991 | 06/11/1991 | 9106190435 | <strong>ESF Actuation Due To Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1991, at approximately 0629 MST, Palo Verde Unit 1 was in (POWER OPERATION) at approximately 100 percent power, when a spurious Train "B" Containment Purge Isolation Actuation Signal (CPIAS) was initiated on the Balance of Plant Engineered Safety Features Actuation System. The Train "B" CPIAS resulted in the designed cross-trips of Train "A" CPIAS and Train "A" and "B" Control Room Essential Filtration Actuation Signals (CREFAS). The actuations occurred when the Train "B" Power Access Purge Area Radiation Monitor (RU-38) spiked, went off line, and was unreachable from the Radiation Monitoring System (RMS) Data Control Unit (DCU). At the time of the event no containment purge was in progress and all Containment Purge System isolation valves were closed. Following the spurious Train "B" CPIAS all components operated as designed. Control Room and Radiation Protection personnel verified that no abnormal radiation levels existed in the vicinity of RU-38. <br /><br /> The cause of the event was a malfunctioning Central Processing Unit and Random Access Memory board on the Train "B" Power Access Purge Area Radiation Monitor (RU-38). As corrective action, the boards have been replaced. <br /><br /> A previous similar event was reported in LER 530/90-001.
5281991007 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 08/22/1991 | 03/15/1992 | 9203250347 | <strong>Technical Specification Bases Not Supported By Design</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1991, at approximately 1010 MST, Palo Verde units 1, 2, and 3 were in Mode 1 (POWER OPERATION) when an evaluation was completed pertaining to the capability of the normal heating, ventilation, and air conditioning (HVAC) systems to meet essential HVAC cooling loads in areas served by the Essential Chilled Water System (ECWS). The evaluation determined that the normal HVAC system cooling to various Engineered Safety Features (ESF) pump rooms is not adequate to meet essential cooling loads. The Technical Specification (TS) BASES 3.7.6 for the ECWS states that the normal HVAC system is redundant to the essential HVAC system. The TS BASES also states that based on the availability of normal HVAC and the high reliability of offsite power, the allowed out-of-service time for a train of the ECWS is 7 days. However, the allowed out-of-service time for affected ESF pumps is 72 hours. Therefore, whenever the ECWS was inoperable for greater than 72 hours, the appropriate ACTION statements for the affected ESF pumps were not met. <br /><br /> The cause of the TS BASES being inconsistent with the design was that Bechtel, Combustion Engineering, and APS personnel reviewing TS 3.7.6 and TS BASES 3.7.6 did not recognize that the normal HVAC system was not 100 percent redundant to some components served by the essential HVAC system. As corrective action, administrative guidance was issued to enter the TS Limiting Condition for Operation (LCO) for the affected equipment, reducing the ECWS allowed out-of-service time to 72 hours with only one train of the ECWS OPERABLE.
5281991008 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 08/16/1991 | 10/23/1991 | 9111040140 | <strong>RCS Leakage Possibly Exceeding Makeup Due To A Postulated Fire</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1991, Palo Verde Units 1 and 3 were in Mode 1 at approximately 100 percent power and Unit 2 was in Mode 1 at approximately 64 percent power (until a reactor trip occurred at approximately 0839 MST: Reference LER 529/91-004) when APS engineering personnel determined that a design basis Appendix R fire in the Control Room could result in loss of Reactor Coolant Pump seal cooling. The loss of RCP seal cooling could result in RCP seal damage which may result in Reactor Coolant System leakage in excess of available charging. Upon discovery of this potential event, appropriate compensatory measures were established in accordance with the PVNGS Fire Protection Program. Subsequently, APS engineering determined that a fire outside the Control Room could also result in the loss of RCP seal integrity. <br /><br /> The cause of this postulated event was a failure of the original Appendix R evaluations to recognize the potential for RCP seal leakage greater than the makeup capacity of one charging pump (44 gallons per minute) due to a Control Room fire.<br /><br /> No previous similar events have been reported pursuant to Technical Specification 6.9.3 and 10CFR50.73.
5281991009 | Palo Verde 1 | 09/14/1991 | 10/14/1991 | 9110180122 | <strong>Reactor Trip and ESF Actuation Due To Number 1 Steam Generator High Level</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1991, at approximately 1722 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) at approximately 55 percent power when a reactor trip and a Main Steam Isolation Signal (MSIS) Engineered Safety Features actuation occurred due to high steam generator level. Prior to the reactor trip and MSIS, reactor power had been reduced as a result of a Part-Length Control Element Assembly slipping part way into the core during monthly testing. This power reduction was required by Technical Specifications. There were no other safety system responses required. The reactor trip was diagnosed as an uncomplicated reactor trip. The plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip and MSIS on high steam generator level was due to the number 1 steam generator economizer valve failing open which resulted in overfeeding the steam generator. The economizer valve failure was due to a failure of the economizer valve positioner. <br /><br /> Troubleshooting was performed, the ability to withdraw the part-length CEA was restored, the economizer valve positioner replaced and tested, and both were returned to service. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281991010 | Palo Verde 1, Palo Verde 3 | 10/27/1991 | 11/26/1991 | 9112030305 | <strong>Unit 1 and Unit 3 Reactor Trips Caused by Grid Perturbation</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1991, at approximately 0722 MST, Palo Verde Units 1 and 3 were operating at approximately 100 percent power when a grid perturbation caused the Main Turbine Control System to fast close and immediately reopen the turbine control valves (TVCs). The momentary reduction in steam flow caused the steam bypass control valves in Units 1 and 3 to quick open. A reactor power cutback occurred in Unit 3, but not in Unit 1. Reactor trips in Units 1 and 3 occurred when reactor power exceeded the Core Protection Calculator Variable Overpower Trip setpoints. Immediately following the trips, Safety Injection Actuation System (SIAS) and Containment Isolation Actuation System (CIAS) Engineered Safety Feature Actuation System actuations occurred on low pressurizer pressure. All safety system components actuated as designed in each unit. By approximately 0805 MST on October 27, 1991, the plants were stabilized in Mode 3 (HOT STANDBY). <br /><br /> The cause of the event was determined to be the expected plant response to a unique combination of circumstances. The event was precipitated by a grid fault resulting from a lightning strike on a substation feeder line. The fault which occurred was different from previous grid disturbance events (i.e., fault without ground). The generator output current at Palo Verde decreased triggering a momentary Power/Load Unbalance turbine protection actuation. This submittal also provides a Special Report in accordance with Technical Specification 3.5.2 ACTION b.
5281991011 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 10/29/1991 | 11/27/1991 | 9112040081 | <strong>Loss of Essential Air Handling Unit Due to Postulated Fire</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1991, Palo Verde Units 1 and 3 were in MODE 3 and Unit 2 was in Mode 6 at approximately 96 degrees Fahrenheit and depressurized to atmospheric pressure when APS engineering personnel determined that a design basis Appendix R fire in the Control Room could result in the loss of one Train "B" Essential Air Handling Unit (AHU). The Train "B" Essential AHU provides cooling to Train "B" Engineered Safety Features (ESF) equipment, Train "B" DC equipment, and Train "B" DC battery rooms. The Train "B" equipment is necessary for the safe shutdown of the plant if there was a fire in the Control Room. Upon discovery of this potential event, appropriate compensatory measures were established in accordance with the PVNGS Fire Protection Program. <br /><br /> The cause of this postulated event was a failure of the original Appendix R evaluation to recognize the control circuit for the Essential AHU being in the Control Room. <br /><br /> A previous similar event was reported pursuant to Technical Specification 6.9.3 in LER 528/91-008-01.
5281991012 | Palo Verde 1 | 12/05/1991 | 12/26/1991 | 9201020094 | <strong>Inadvertent Control Room Essential Filtration ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1991, at approximately 0950 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATIONS) at approximately 100 percent power when an inadvertent Control Room Essential Filtration Actuation Signal (CREFAS) Balance of Plant Engineered Safety Features Actuation System (BOP ESFAS) actuation occurred. The actuation was a result of an improper restoration by a control room operator of the Channel, B CREFAS module that had been placed in BYPASS mode for scheduled surveillance testing.<br /><br /> The CREFAS actuation was verified to not be the result of a valid signal. The equipment actuated by the CREFAS was verified to operate as designed and subsequently returned to normal configuration. <br /><br /> The cause of the inadvertent CREFAS actuation was a cognitive personnel error by the operator who removed the CREFAS module from BYPASS mode prior to resetting the trip inputs. The error was a result of not following an approved station procedure. As corrective action, the operator was temporarily removed from shift and discipline was administered in accordance with the PVNGS Positive Discipline Program. <br /><br /> Similar events were reported in LERs 528/86-022, 529/85-006, 529/86-039, 529/90- 011, and 530/91-009.
5291991001 | Palo Verde 2 | 06/05/1991 | 06/24/1991 | 9107110204 | <strong>CPIAS/CREFAS Actuations Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1991, at approximately 1131 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a Train "B" Containment Purge Isolation Actuation Signal (CPIAS) was initiated on the Balance of Plant Engineered Safety Features Actuation System. The Train "B" CPIAS resulted in the designed cross trips of Train "A" CPIAS and Train "A" and "B" Control Room Essential Filtration Actuation Signals (CREFAS). The actuations resulted when the Train "B" Power Access Purge Area Radiation Monitor's (RU-38) alarm/trip setpoint was inadvertently reset below the background radiation level. All components operated as designed. At the time of the event, no containment purge was in progress and all Containment Purge System isolation valves were closed. Control Room personnel verified that normal radiation levels existed in the area of RU-38. <br /><br /> The cause of this event was a cognitive personnel error when a chemistry radiation monitoring system technician changed the alarm setpoint on the wrong radiation monitor at the Remote Indication and Control Unit outside the Control Room. To prevent recurrence the technician was counseled in accordance with the APS Positive Discipline Program and chemistry radiation monitoring system technicians in Units 1, 2 and 3 will be briefed on this event in industry events training. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 resulting from the same cause and sequence of events.
5291991002 | Palo Verde 2 | 06/19/1991 | 07/17/1991 | 9107260153 | <strong>Daily Reactor Coolant Pump Vibration Data Engineering Evaluation Missed</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1991, at approximately 1745 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when the Unit 2 Shift Technical Advisor (STA) discovered that the daily engineering review of Reactor Coolant Pump (RCP) vibration data for June 18, 1991, had not been completed pursuant to item IV.A.2 of the Unit 2 Confirmatory Order Modifying Facility Operating License NPF-51 dated November 19, 1987. The STA reviewed the RCP vibration data for June 18, 1991, and determined that it met the acceptance criteria for RCP vibration. <br /><br /> The cause of this event was a cognitive personnel error by the STA on the previous shift who did not complete the engineering evaluation on June 18, 1991. To prevent recurrence, the STA was counseled and this event was discussed with all STAs.<br /><br /> There was a previous similar event reported in Unit 1 LER 528/89-001-00.
5291991003 | Palo Verde 2 | 08/09/1991 | 09/05/1991 | 9109180125 | <strong>Manual Reactor Trip During Shutdown</strong><br /><i>Abstract:&nbsp;</i>At approximately 0648 MST on August 9, 1991, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) at approximately 40 percent power when the reactor was manually tripped due to Axial Shape Index (ASI) approaching its trip setpoint on the Core Protection Calculator. At the time of this event, the reactor was being shut down due to the loss of Control Element Drive Mechanism cooling fans. Following the trip, two of the four reactor coolant pumps (RCPs) did not transfer to their alternate source of power and stopped. The remaining two RCPs supplied adequate forced circulation. The reactor trip was diagnosed as an uncomplicated reactor trip. No safety system responses occurred and none were required. At approximately 0658 MST the plant was stabilized in Mode 3 (HOT STANDBY) at normal temperature and pressure.<br /><br /> The cause of the manual reactor trip was ASI approaching its trip setpoint during shutdown. The corrective action was to trip the reactor and ensure ASI remained within limits.<br /><br /> Previous similar events were reported in LER 528/87-018-01 and LER 529/90-001-00.
5291991004 | Palo Verde 2 | 08/16/1991 | 01/24/1992 | 9202050243 | <strong>Reactor Trip Following Generator/Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1991, at approximately 0839 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 64 percent power when a reactor trip occurred due to high pressurizer pressure. Immediately prior to the reactor trip, the Main Generator tripped initiating a Main Turbine trip. At approximately 0900 MST on August 16, 1991, the plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. The event was diagnosed as an uncomplicated reactor trip. No other safety system responses occurred and none were required.<br /><br /> The reactor trip on high pressurizer pressure has been determined to be the normal plant response to a load rejection at 64 percent power with 7 of the 8 steam bypass control valves (SBCVs) in service. The cause of the reactor trip was a generator/turbine trip in combination with a cognitive personnel error by the Control Room personnel who did not comply with procedural requirements to have the 8 SBCVs in service at power levels below 75 percent. Control Room personnel were disciplined in accordance with the PVNGS Positive Discipline Program. The Main Generator trip was caused when a Generrex A.C./D.C. gate board's static switch failed and the Generrex excitation control system entered an abnormal state (i.e., excessively high field voltage, current and VARS). The gate board was replaced and the Generrex System was successfully retested and returned to service. <br /><br /> A previous similar event was reported in Unit 1 LER 528/90-006.
5291991005 | Palo Verde 2 | 10/09/1991 | 12/04/1991 | 9112100244 | <strong>MSSV and PSV Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1991, while Unit 2 was in Mode 1 (POWER OPERATION) at approximately 97.5 percent power, an engineering evaluation of ASME surveillance testing results determined that eleven (11) of the twenty (20) Main Steam Safety Valve (MSSV) as-found relief settings were out of the tolerance limits specified in Technical Specification (TS) 3.7.1.1 and in the testing requirements established by APS. The testing and adjustments were performed during the period of October 8 through October 9, 1991, while Unit 2 was in Mode 1, to verify the relief settings of the MSSVs. <br /><br /> On November 4 and 5, 1991, while Unit 2 was in Mode 6 with the core offloaded ASME surveillance testing was performed on the Pressurizer Safety Valves. Three of four valves were out of tolerance on the initial lift. <br /><br /> The cause of the event is setpoint drift. As immediate corrective action the MSSVs and PSVs have been adjusted and tested satisfactorily.<br /><br /> Previous similar events were reported in MSSV LERs 528/88-014-01, 528/89-010-00, 529/89-002-00, 529/89-007-00 and 530/91-001-00.
5291991006 | Palo Verde 2 | 10/27/1991 | 11/26/1991 | 9112030355 | <strong>Technical Specification Violation During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1991, Palo Verde Unit 2 was in Mode 6 (REFUELING) with the reactor vessel head removed during a planned refueling outage. At approximately 1220 MST, the Control Room shift supervisor was notified that the control element assemblies had been withdrawn approximately one (1) foot out of the core during defueling operations without direct communication established with the Control Room during this core alteration and without the refueling senior reactor operator present to observe and directly supervise the core alteration. This is contrary to the requirements of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.9.5 and TS Administrative Control 6.2.2b. Core alterations were immediately suspended per the ACTION requirement of LCO 3.9.5. Following resumption of core alterations after implementation of immediate corrective actions, core alterations were not suspended at 1716 MST contrary to the ACTION requirements of TS 3.8.3.2 when one (1) of the two (2) required 120 volt vital AC busses transferred from its normal power source to its alternate power source. <br /><br /> The cause of these events was due to a combination of cognitive personnel errors. <br /><br /> The Control Room shift supervisor suspended core alterations and plant management suspended all work affecting or involving core alterations. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291991007 | Palo Verde 2 | 12/05/1991 | 01/02/1992 | 9201090152 | <strong>Technical Specification Violation - Containment Integrity During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1991, during a planned refueling outage, Palo Verde Unit 2 was in Mode 6 (REFUELING) with the reactor vessel head removed and the reactor coolant system at approximately 100 degrees Fahrenheit and atmospheric pressure when maintenance personnel discovered that a containment isolation valve (SIA-UV-673) which was required to be closed during core alterations was in the open position. Technical Specification Limiting Condition For Operation (TS LCO) 3.9.4.c.1 requires that each penetration providing direct access from the containment atmosphere to the outside atmosphere shall be closed by an isolation valve, blind flange, or manual valve during core alterations. If TS LCO 3.9.4.c.1 is not satisfied, the associated TS LCO ACTION requires the immediate suspension of all operations involving core alterations. From November 30, 1991 to December 5, 1991, core alterations were in progress. Therefore, the ACTION requirements of TS LCO 3.9.4 were not met. <br /><br /> The cause of SIA-UV-673 being open was due to procedure inadequacy in that the valve stem was not required by procedure to be matchmarked or locked in the closed position when the actuator was removed. The valve disc unexpectedly opened. The actuator was reinstalled when the valve disc was open. This resulted in the valve being open when the indicated position showed the valve to be closed. As corrective action, procedures will be revised appropriately. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291991008 | Palo Verde 2 | 12/23/1991 | 01/27/1993 | 9302010234 | <strong>Loss of RCS Inventory During Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 1555 MST on December 23, 1991, Palo Verde Unit 2 was in Mode 5 (COLD SHUTDOWN) during startup from a planned refueling outage, when a relief valve on the "A" train shutdown cooling (SDC) loop stuck open resulting in a loss of reactor coolant system (RCS) inventory. In accordance with Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.1.4.1, the A" train SDC loop was OPERABLE and operating, and the "B" train SDC loop was OPERABLE and in standby. At the time of this event two charging pumps were in operation.<br /><br /> As immediate action, a third charging pump and a High Pressure Safety Injection pump were manually started to provide sufficient makeup to the RCS to restore pressurizer level. The "A" train SDC loop was isolated from the RCS, terminating the loss of RCS inventory. <br /><br /> This is being reported as an information-type LER (i.e., voluntary LER). <br /><br /> No previous similar events have been reported pursuant to 10CFR50.73.
5291991009 | Palo Verde 2 | 12/31/1991 | 06/01/1993 | 9306170028 | <strong>Operation With Steam Generator Tube Not Plugged As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On May 7, 1993, Unit 2 was in its fourth refueling outage in Mode 6 (REFUELING) when Palo Verde Nuclear Generating Station (PVNGS) Engineering personnel determined that Technical Specification (TS) Surveillance Requirement (SR) 4.4.4.2, for performing the inservice inspection of steam generator (SG) tubes, was not met per the acceptance criteria of TS SR 4.4.4.4.b. It was discovered that a SG tube mechanical plug was installed and verified in an incorrect location on the hot leg side of SG 2 during the previous refueling outage. This rendered SG 2 administratively inoperable during Cycle 4 operation. The misplugged tube performed its intended function as demonstrated during Cycle 4 operation. This was confirmed post-cycle by leak and eddy current testing performed during the current refueling outage. The cause of the event was determined to be cognitive personnel error during the plugging of the SG tube in November 1991. Comprehensive training has been developed and conducted with PVNGS Quality Control personnel involved in current SG tube plugging verification activities and will be a prerequisite for performing future tube plugging verification activities. A previous similar event was reported pursuant to 10CFR50.73 in Unit 2 LER 90-005-00.
5301991001 | Palo Verde 3 | 03/15/1991 | 06/09/1991 | 9106140167 | <strong>Safety Valve Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1991 while Unit 3 was in Mode 1 (POWER OPERATION) at approximately 70 percent power, an engineering evaluation of ASME surveillance testing results determined that ten (10) of the twenty (20) Main Steam Safety Valve (MSSV) as-found relief settings were out of the tolerance limits specified in Technical Specification (TS) 3.7.1.1 and in the testing requirements established by APS. The testing and adjustments were performed during the period of March 13 through March 15, 1991, while Unit 3 was in Mode 1, to verify the MSSV relief settings. <br /><br /> After shutdown for a scheduled refueling outage, the Unit 3 Pressurizer Code Safety Valves (PSV) were removed and sent to an offsite testing lab. The Unit 3 PSVs were tested April 1 and 2, 1991 and three (3) of the four (4) PSV as-found relief settings were out of the tolerance limits specified in TS 3.4.2.2 and in the testing requirements established by APS. <br /><br /> The cause of the event is setpoint drift. As immediate corrective action the MSSVs and PSVs have been adjusted and tested satisfactorily. A safety analysis determined that the as-found setpoints would not have resulted in any safety limits being violated. <br /><br /> Previous similar events were reported in MSSV LERs 528/88-014-01, 528/89-010- 00, 529/89-002-00, 529/89-007-00 and PSV LERs 528/89-007-01 and 529/90-004-01.
5301991003 | Palo Verde 3 | 06/19/1991 | 10/23/1991 | 9111040113 | <strong>Inadvertent Containment Spray Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1991, at approximately 1002 MST, a Spurious Containment Spray System actuation occurred during the performance of the monthly Engineered Safety Features Actuation System (ESFAS) surveillance testing of the Plant Protection System (PPS). Control Room personnel determined that the Containment Spray System actuation was not the result of a valid condition (i.e., high containment pressure) and terminated the containment spray flow. Control Room personnel manually tripped the reactor at approximately 1004 MST and stopped the four reactor coolant pumps at approximately 1007 MST, in accordance with an approved procedure. At approximately 1022 MST, on June 19, 1991, natural circulation cooling was verified and the plant was stabilized in Mode 3 (HOT STANDBY). No other safety system responses occurred and none were required.<br /><br /> The spurious Containment Spray System actuation was the result of the incorrect assembly of a logic matrix relay hold pushbutton test switch in the test circuitry located in the PPS cabinet. The pushbutton test switch was replaced. The other logic matrix relay hold pushbutton test switches in Units 1, 2 and 3 were inspected and found to be assembled correctly. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301991004 | Palo Verde 3 | 07/13/1991 | 07/31/1991 | 9108120240 | <strong>ESF Actuation Due to Radiation Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1991, at approximately 2329 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power, when a spurious Train A Containment Purge Isolation Actuation Signal (CPIAS) was initiated on the Balance of Plant Engineered Safety Features Actuation System. The Train A CPIAS resulted in the designed cross trips of Train B CPIAS and Train A and B Control Room Essential Filtration Actuation Signals (CREFAS). The actuations occurred when the Train A Power Access Purge Area Radiation Monitor (RU-37) spiked above its high alarm/trip setpoint. At the time of the event, no containment purge was in progress and the Containment Purge System isolation valves were closed. All components operated as designed. Control Room and Radiation Protection personnel verified that normal radiation levels existed in the area monitored by RU-37. <br /><br /> The cause of the RU-37 spiking above its high alarm/trip setpoint was a premature failure of the detector's Geiger-Mueller tube resulting from a dent on the tube's sidewall. Technicians were briefed on the importance of ensuring that replacement Geiger-Mueller tubes have no signs of physical damage prior to installation in the radiation monitor's detector assembly.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 which resulted from a damaged Geiger-Mueller tube.
5301991005 | Palo Verde 3 | 07/31/1991 | 08/23/1991 | 9109160294 | <strong>ESF Actuation Due to Monitor Failure</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1991, at approximately 0912 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power, when a spurious Train A Containment Purge Isolation Actuation Signal (CPIAS) was initiated on the Balance of Plant Engineered Safety Features Actuation System. The Train A CPIAS resulted in the designed cross trips of Train B CPIAS and Trains A and B Control Room Essential Filtration Actuation Signals (CREFAS). The actuations occurred when the Train A Power Access Purge Area Radiation Monitor (RU-37) spiked above its high alarm/trip setpoint. At the time of the event, no containment purge was in progress and the Containment Purge System isolation valves were closed. All components operated as designed. Control Room and Radiation Protection personnel verified that normal radiation levels existed in the area monitored by RU-37. <br /><br /> The cause of RU-37 spiking above its high alarm/trip setpoint was an infantile failure of the monitor's Geiger-Muller tube in the detector assembly. <br /><br /> A previous similar event was reported in Unit 1 LER 528/91-005-00.
5301991006 | Palo Verde 3 | 08/24/1991 | 09/19/1991 | 9109240342 | <strong>ESF Actuation Due To Loss Of Power To 4.16 KV Bus</strong><br /><i>Abstract:&nbsp;</i>At approximately 1934 MST on August 24, 1991, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when the normal supply breaker opened between the Unit 3 non-Class 1E 13.8 KV bus and the start-up transformer resulting in a loss of power to the Unit 3 Train "B" Class 1E 4.16 KV bus. This resulted in a Loss of Power (LOP) Engineered Safety Feature Actuation Signal (ESFAS) being generated. The ESFAS resulted in an automatic load shed of the Class 1E bus and start of the Train "B" Emergency Diesel Generator (EDG). The EDG started and assumed the loads as designed. All equipment functioned as designed. No other ESF actuation signals occurred and none were required. Unit 3 continued to operate normally at 100 percent power throughout the event. <br /><br /> The cause of the event was a moisture induced short circuit in the trip circuit for the normal supply breaker. A wind and rain storm was in progress and water was driven into the plant multiplexer cabinet past a degraded seal around an air conditioning duct penetration.<br /><br /> An inspection of the plant multiplexer cabinets for Units 1, 2, and 3 was performed. In Units 1 and 2 no evidence of water intrusion was found. The degraded seal in the Unit 3 multiplexer cabinet was upgraded to metal flashing and resealed. <br /><br /> A previous similar event was reported in Unit 1 LER 528/88-003.
5301991007 | Palo Verde 3 | 08/31/1991 | 09/27/1991 | 9110090109 | <strong>Reactor Shutdown Required by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>At approximately 0119 MST on August 31, 1991, Palo Verde Unit 3 was in Mode 3 (HOT STANDBY) at normal temperature and pressure when a plant shutdown was completed in accordance with ACTION b.(2) of Technical Specification (TS) 3.8.3.1 due to a Class 1E inverter that could not be returned to operable status within the allowed ACTION time. The plant was stable at normal temperature and pressure. No safety system responses occurred and none were required. The event was determined to be an uncomplicated normal plant shutdown. At approximately 1902 MST on August 31, 1991, TS 3.8.3.1 ACTION b.(2) was exited when the Class 1E inverter was returned to service and the 120-volt Vital A.C. electrical bus was reenergized from its associated inverter. <br /><br /> The cause of this event was a cognitive personnel error by an Operations Computer Systems maintenance technician who improperly attached a variable power source to the energized control element assembly calculator circuit while it was being fed from the inverter. This resulted in the inverter failure. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301991008 | Palo Verde 3 | 11/14/1991 | 12/13/1991 | 9112240273 | <strong>Reactor Trip Due to Lightning Induced Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>At approximately 1449 MST on November 14, 1991, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) at approximately 100 percent power when a lightning induced electrical fault on the A phase main transformer caused a generator trip, turbine trip, and reactor power cutback (RPCB). Approximately 35 seconds following these events, the reactor tripped on low Departure from Nucleate Boiling Ratio (DNBR) signals. The plant was stabilized in Mode 3 (HOT STANDBY) at normal operating temperature and pressure. The Control Room shift supervisor classified the event as an uncomplicated reactor trip in accordance with the emergency plan implementing procedure. No other safety system responses occurred and none were required. The post trip review found that the low DNBR reactor trip was due to a control element assembly (CEA) subgroup deviation. During the post trip investigation, APS engineering discovered that a problem with the control element assembly calculator (CEAC) software design may have delayed the reactor trip for up to 16 seconds when a second CPC time delay was initiated. At the time of the second time delay, one CEA subgroup was thought to be misaligned greater than the allowed limit in the CPCs. <br /><br /> The cause of the second time delay was that the CEAC software design did not anticipate that there would be CEA slips lasting less than 0.5 seconds. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301991009 | Palo Verde 3 | 11/18/1991 | 12/13/1991 | 9112240263 | <strong>Inadvertent Control Room Essential Filtration ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1991, at approximately 0859 MST, Palo Verde Unit 3 was in Mode 3 (HOT STANDBY) at approximately 565 degrees Fahrenheit and 2252 pounds per square inch-absolute when an inadvertent Control Room Essential Filtration Actuation Signal (CREFAS) Balance of Plant Engineered Safety Features Actuation System (BOP ESFAS) actuation occurred. The actuation was a result of an improper restoration by a control room operator of the Channel A CREFAS module that had been placed in BYPASS mode for scheduled surveillance testing. <br /><br /> The CREFAS actuation was verified not to be the result of a valid signal. The equipment actuated by the CREFAS was verified to operate as designed and subsequently returned to normal configuration. <br /><br /> The cause of the inadvertent CREFAS actuation was a cognitive personnel error by the operator who removed the CREFAS module from BYPASS mode prior to resetting the trip inputs. The error was a result of not following an approved station procedure. As corrective action, the operator was temporarily removed from shift and discipline was administered in accordance with the PVNGS Positive Discipline Program.<br /><br /> Similar events were reported in LERs 528/86-022, 529/85-006, 529/86-039, and 529/90-011.
5301991010 | Palo Verde 3 | 11/15/1991 | 01/30/1992 | 9202060068 | <strong>ESF Actuations Caused by Manual Deenergization of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1991, at approximately 0913 MST, Palo Verde Unit 3 was in Mode 3 (HOT STANDBY) when Control Room personnel, responding to a report that a mobile crane was in contact with an energized 13.8 kV overhead power line, secured power to the Train B 13.8 kV non-Class 1E intermediate switchgear bus (NAN-S06). This resulted in the expected loss of power to the Train B Class 1E 4.16 kV bus, and a Loss of Power (LOP) Engineered Safety Feature Actuation System (ESFAS) actuation. The Train B Emergency Diesel Generator (EDG) started and loaded per design. At approximately 0914 MST, the Control Room was notified that the line the crane was in contact with was still energized and that the Train A 13.8 kV non-Class 1E intermediate switchgear bus (NAN-S05) needed to be deenergized, Control Room personnel proceeded to reenergize the NAN-S06 bus prior to deenergizing the NAN-S05 bus. At approximately 0922 MST, Control Room personnel deenergized the NAN-S05 bus which resulted in the expected loss of power to the Train A Class 1E 4.16 kV bus and a Train A LOP ESFAS actuation. The Train A EDG started and loaded per design. <br /><br /> All equipment functioned as designed. No other safety system responses occurred and none were required. <br /><br /> Based on investigation results, the cause of the crane coming in contact with an energized 13.8 kV power line was determined to be personnel error. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301991011 | Palo Verde 3 | 11/04/1991 | 11/30/1991 | 9112090450 | <strong>Auxiliary Feedwater Flow Transmitters Equalizing Valve Improperly Aligned</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1991, at approximately 2342 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when an auxiliary operator (AO) assisting in the performance of a surveillance test (ST) discovered that the Channel "B" auxiliary feedwater flow transmitter AFB-FT-41B equalizing valve was improperly aligned. The AO notified the Control Room reactor operator designated as the ST Test Leader of the improper valve alignment. While waiting for Control Room response, the AO discovered that the other Channel "B" auxiliary feedwater flow transmitter AFB-FT-41A equalizing valve was also improperly aligned. Since both Channel "B" flow transmitters were found to be improperly aligned, one less than the required number of channels (i.e., two) specified in the Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.3.6 was operable. Since it has not been determined when the flow transmitter equalizing valves were manipulated, it is assumed that the OPERABILITY requirements and the associated seven (7) day ACTION were not met for TS LCO 3.3.3.6 since the last time that the flow transmitters were determined to be operating properly on October 27, 1991.<br /><br /> Based upon the results of the investigation, the cause of the auxiliary feedwater flow transmitter equalizing valves being improperly aligned has not been determined. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.