## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
1331993001 | Humboldt Bay 3 | 11/24/1993 | 12/23/1993 | 9312300180 | <strong>Missed Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1993, while the Unit was in SAFSTOR, an engineer performing the weekly review of surveillance test results, found that the surveillance to verify the spent fuel pool level monitors had been missed. Technical Specifications Section V .B.5 requires that the spent fuel pool level monitors be verified monthly. Subsequent to the discovery that the surveillance had been missed, Surveillance Test Procedure (STP) 3.6.2, 'Spent Fuel Pool Level Monitor Verification,' was performed successfully on November 24, 1993, and the acceptance criteria for the test were met. <br /><br /> The root cause of this event was personnel error, as the surveillance had been in Advertently left unscheduled. <br /><br /> Corrective action to prevent recurrence included placing the instructions for scheduling and reviewing the surveillances into an administrative procedure and establishing a method of verifying that all required surveillances have been scheduled.
1551993001 | Big Rock Point | 01/09/1993 | 02/04/1993 | 9302120259 | <strong>Failure To Post High Radiation Area Pursuant To Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Big Rock Tech Spec 6.12.1 requires that: '...each high radition area in which the intensity is less than 1000 mR/h at 45 cm (18 in) from the radiation source or from any surface which the radiation penetrates shall be barricaded and conspicuously posted as a high radiation area (HRA)...'. <br /><br /> On January 11, 1993, a reviewer observed tha t dose rates on a vacuum filter unit located on the reactor deck measured 3.9 Rem/hr contact and 500 mRem/hr at twelve inches as of a January 9, 1993 survey. The sheet did not, however, document that the area had been posted as an HRA. <br /><br /> The cognizant technician believed the reactor deck to be a high radiation area; further posting of the filer unit was not required. On January 11, 1993 the filter unit was immediately barricaded and shielded. The status sheet was updated to reflect current conditions. <br /><br /> The event has been discussed at the Chemistry/ Health Physics weekly meeting. Actions will also be taken to prevent the unit from becoming an HRA. No dose limits were exceeded.
1551993002 | Big Rock Point | 06/29/1993 | 07/23/1993 | 9307270152 | <strong>Loss of Containment Integrity via Feedwater System Piping</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3.6 requires that 'Containment Sphere integrity shall be maintained during power operation, refueling operation, shutdown and cold shutdown conditions except as specified by a system of procedures and controls to be established for occasions containment must be breached during cold shutdown'. <br /><br /> Contrary to the above, containment integrity was not maintained between 2206 on June 27, 1993, and 1850 on June 29, 1993. (The facility had entered a refueling outage June 26, 1993). The minor breach occurred in the feedwater system. The facility also exited the cold shutdown condition per technical specification definition for a period of four and one-half hours during this period.<br /><br /> The root cause for this event was an inadequate review of the switching and tagging order (with regards to containment integrity) controlling the work. To prevent recurrence, valves located in containment in lines entering and exiting containment will be identified with labels warning of the potential for breach of containment. Caution statements will be added to appropriate procedures addressing the concern. <br /><br /> The safety significance of this occurrence was minimal. No outage related activities challenging containment integrity transpired during this time.
1551993003 | Big Rock Point | 07/08/1993 | 08/04/1993 | 9308120134 | <strong>Reactor Coolant High Pressure Sensors Found Out-Of-Technical Spec Tolerance</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 11.3.3.4.A requires that 'During power operation, both of the two containment spray systems shall be operable'. <br /><br /> Contrary to the above, on July 8, 1993 at 1130, two out of four Reactor Containment High Pressure sensors were found out-of-tolerance high. (the facility had been removed from service on June 26, 1993 for a scheduled refueling outage). The Primary Containment Spray would not have automatically operated until a slightly higher pressure than required was reached.<br /><br /> The root cause of the setpoint increase has been correlated to the use of a vent plug in the switch housing. In this configuration, an increase in temperature can induce an internal pressure rise causing an increase in the switch setpoint. The vent plugs will be removed and the switches recalibrated before start-up from the refueling outage.<br /><br /> The safety significance of this discovery is negligible. The out-of-tolerance condition would not have inhibited actuation when challenged because of the rapid rate-of-rise of containment pressure and required operator action under all (small, medium large) LOCA conditions.
1551993004 | Big Rock Point | 07/09/1993 | 12/01/1994 | 9412080201 | <strong>Reactor Water Level And Primary System Pressure Sensors Found Out-Of-Tech Spec Tolerance</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 11.3.1.4.A requires that 'The two core spray systems (original and redundant) shall be operable whenever the plant is in a power operation condition'. <br /><br /> Contrary to the above, on July 9, 1993, at 1730, a routine surveillance test performed during a refueling outage, demonstrated that pressure and level sensors controlling the automatic actuation of MO-7070, a Redundant Core Spray valve, were out of technical specification tolerance. <br /><br /> The root causes established for the pressure and level sensors were a diaphragm/spring failure and a leaking sensing line valve, respectively. The pressure switch was replaced and recalibrated. The sensing line leak was isolated and the level switch was recalibrated. <br /><br /> The safety significance of this event is minimal. The Redundant Core Spray system would still have operated, albeit not in accordance with the Technical Specification requirements; and the Primary Core Spray System remained available for service.
1551993005 | Big Rock Point | 07/14/1993 | 08/10/1993 | 9308170177 | <strong>Primary Containment Spray Valve Motor Operator Capability May Have Been Insufficient To Open Valve Under Degraded Conditions</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 11.3.3.4.A requires that 'During power operation, both of the containment spray systems shall be operable'. <br /><br /> Contrary to the above, on July 14, 1993, at 1530, the Primary Containment Spray motor operator capability may have been insufficient to open MOV-7064 under degraded conditions. This situation was discovered during the current refueling outage during VOTES diagnostic testing pursuant to Generic Letter 89-10, Safety-Related Motor-Operator Valve Testing and Surveillance. However, stroke timing demonstrated that the valve was acceptable based on former operability test requirements. <br /><br /> The torque switch will be reset and VOTES testing performed to set-up the valve within the required thrust window during this refueling outage. <br /><br /> The Backup Containment Spray System could have been placed into service if conditions warranted. In addition, MOV-7064 should have been able to perform its intended function because it has met past operability requirements.
1551993006 | Big Rock Point | 07/15/1993 | 08/09/1993 | 9308160251 | <strong>Failure To Post And Barricade A High Radiation Area</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification, Section 10, 6.12.1, requires that 'each high radiation area (HRA) in which the intensity of radiation is less than 1000 mR\h at 45 cm (18 in.) from the radiation source or from any surface which the radiation penetrates shall be barricaded and conspicuously posted as a high radiation area ...' <br /><br /> Contrary to the above, On July 15, 1993, at 1730 a HRA was found unposted and not barricaded during a Managers shutdown/refueling tour. The boundary chain, with the HRA sign attached, was not in place. <br /><br /> The barricade and posting was immediately re-established. <br /><br /> The root cause has been identified as an Insufficient Degree of Attention applied by the contracted Health Physics technician to the area posting requirements and as-left status. Additional training and increased management oversight are expected to prevent recurrence. <br /><br /> For the days the barricade and posting were removed, no unexpected doses were documented by station personnel. Status sheet reflected current conditions.
1551993007 | Big Rock Point | 08/08/1993 | 09/08/1993 | 9309200067 | <strong>UNPLANNED ENGINEERED SAFETY FEATURE (ESF) ACTUATION: ELECTRIC FIRE PUMP START DURING SURVEILLANCE TEST</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On August 3, 1993, at 0816, the Electric Fire Pump, an Engineered Safety Feature at Big Rock Point, automatically actuated during a surveillance test. The plant was in the cold shutdown condition. The technicians tried to reseat a module board to get a spurious test light to drop out. This action may have induced a 'spike', causing the electric fire pump to actuate. The pump was shutdown at 0854 after Maintenance/Operations determined that the pump had not received a valid signal. The surveillance test was completed that same day. A precaution statement will be added to TR-48 by the next refueling outage (scheduled for 1994) that cautions against module board movement causing unwanted spikes imposing spurious signals in the RDS. Any board movement will require the affected RDS channel to be placed in 'bypass'.
1551993008 | Big Rock Point | 08/13/1993 | 09/13/1993 | 9309210081 | <strong>Welds Not Included In Technical Specification Inservice Inspection Program</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 9.3.a, requires that 'Inservice Inspection (ISI) of ASME Code Class 1, 2 and 3 components...be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10 CFR 50.55a(g)...' <br /><br /> Contrary to the above, on August 13, 1993, at approximately 1400, two welds were discovered to have been omitted from the Big Rock Point Inservice Inspection program. This discovery was made while performing repairs to the reactor head vent line flange during a scheduled refueling outage. <br /><br /> The two subject nozzle-to-flange welds were successfully inspected in accordance with Section XI of the ASME Code. <br /><br /> The root cause of this event has been identified to be the use of incomplete vendor manual drawings. A comprehensive review of the Combustion Engineering Fabrication drawings will be performed for the reactor vessel and steam drum. The Big Rock Point staff has concluded (based on the current IGSCC program), that the significance of this event is minimal.
1551993009 | Big Rock Point | 09/16/1993 | 10/19/1993 | 9310270238 | <strong>Check Valves Not Included In Technical Specification Required Program</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 9.3.a, requires that 'Inservice Inspection (ISI) of ASME Code Class 1, 2, and 3 components....be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10 CFR 50.55a(g)...' <br /><br /> Contrary to the above, on September 16, 1993, four Containment spray check valves were discovered to have been omitted from the program during a routine Nuclear Regulatory Commission Inspection. They had originally been installed in 1980. The engineer responsible for the check valve installation, and those performing technical and management reviews, did not recognize the requirements of the code. <br /><br /> The valves were immediately added to the program. <br /><br /> A schedule to inspect the valves during the next cold shutdown or 1994 refueling outage has been implemented.
1551993010 | Big Rock Point | 10/21/1993 | 11/17/1993 | 9312020634 | <strong>Licensed Operator Requal Training Not Performed In Accordance With Facility Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1993, an apparent violation of 10 CFR 50.54(i-1) was identified during a routine NRC Requal Training Inspection. Several Licensed Operators did not receive all of the required requal training during the 1991-1992 training cycle. In addition, Technical Specification 6.4.1 requires that 'A retraining and replacement training program for the plant staff shall be maintained and implemented'. Therefore this event is reportable to the NRC pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the station's Technical Specifications. <br /><br /> An evaluation was immediately conducted for each on-shift reactor operator (RO) and senior reactor operator (SRO). One SRO was required to complete a make up training session prior to standing a watch. The remaining LOs were deemed qualified to perform the task associated with the missed training, and allowed to remain on shift. A training action plan has been developed for the missed 1991-1992 training. The creation of new tracking and scheduling programs will be implemented to prevent recurrence.
1551993011 | Big Rock Point | 11/02/1993 | 11/29/1993 | 9312070212 | <strong>Inadvertent Removal Of Redundant Core Spray Valve From Service At Power Operation</strong><br /><i>Abstract:&nbsp;</i>Big Rock Technical Specifications require that the original and redundant core spray systems be operable whenever the plant is in power operation. <br /><br /> Contrary to the above, on November 2, 1993, at 0734, a redundant core spray valve was inadvertently removed from service for approximately 12 minutes. This action rendered the redundant core spray system inoperable. The original core spray system remained in service and would have been capable of mitigating the consequences of an accident as designed. <br /><br /> The root cause of the event has been attributed to human error resulting in an inadequate switching and tagging order being written and approved for use. <br /><br /> The facility was recently assessed a proposed civil penalty on November 9, 1993, with regards to management attention to licensed activities. Corrective actions are in the process of being formulated/implemented, and were not developed sufficiently to prevent this additional example of the basis for the penalty from occurring. Immediate and long term corrective actions are expected to prevent any further occurrences.
1551993012 | Big Rock Point | 12/06/1993 | 01/03/1994 | 9401120177 | <strong>Inadvertent Removal Of Diesel Fire Pump From Service During Facility Power Operation</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1993, at approximately 1045, the diesel fire pump fuel line was punctured. An inspection hole was being drilled in the floor near the fire pump to accommodate a zebra mussel observation camera system. The fuel line was not shown on the plant drawings and was not detected by radar equipment used to map the floor. <br /><br /> The pump was immediately declared inoperable and a Limiting Condition of Operation (LCO) entered. The NRC Operations Center was notified by 1430 of the event. Repairs were performed within the window of the Technical Specification LCO, and the pump returned to service on December 7, 1993, at 0528. <br /><br /> The root cause of the event has been attributed to human error, incorporating several causal factors that address protective equipment use and management oversight. <br /><br /> Corrective actions will include revisions to plant procedures and safety standards to address the use of drill stop boxes; and a generic review of safety evaluations will be performed.
2131993001 | Haddam Neck | 01/07/1993 | 04/01/1993 | ML09152039 | <strong>Fire Door Opened Without Entering LCO and Establishing Fire Watch</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1993, at 1039 hours, with the plant operating in Mode 1 at 100% power, a door in a Technical Specification fire barrier protecting the 'A' Switchgear Room from the Turbine Building was found open for other than routine access without establishing the appropriate fire watch. This door, which was opened so it could be painted by plant personnel, is covered by Haddam Neck Technical Specification 3.7.7, Fire Rated Assemblies. The cause of the event was personnel error since the required administrative controls were not adhered to. Since the door was opened without first implementing the required LCO Action, this event is conservatively judged to be reportable per the requirements of 10CFR50 50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications. This Supplemental Report is being submitted to provide the results of a review of past corrective actions for previous fire door related events and to describe corrective action plans for this event.
2131993002 | Haddam Neck | 03/23/1993 | 04/20/1993 | 9304260194 | <strong>Control Rod 31 and 32 Malfunction</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1993, at 0844 hours, with the plant at 100 percent power, operators attempted to insert control Bank B. When rods were inserted one step, control rods 31 and 32 from Bank B dropped approximately 50 steps. A decision was made to recover the misaligned rods. Rods 31 and 32 were placed in disconnect to prevent further insertion. When the remaining rods in Bank B were inserted one step, control rods 31 and 32 dropped approximately another 100 steps. Immediate operator action was to initiate a manual trip of the reactor. Subsequent investigation revealed that a faulty contactor allowed the control rods to drop during a demand for rod insertion. The root cause was inadequate procedural verification on the maintenance of control rod contactors. Corrective action will be implemented through procedural enhancement. This event is reportable under 10CFR50.73 (a)(2)(iv) since it resulted in manual actuation of the Reactor Protection System.
2131993003 | Haddam Neck | 03/24/1993 | 04/28/1993 | 9305030266 | <strong>Fire Barriers Inoperable Due to Fire Seal Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1993, with the plant in Mode 3 (Hot Standby), a plant employee conducting a fire barrier inspection found two fire barrier penetrations in two separate Technical Specification controlled fire barriers which did not have qualified fire seals installed within the openings. One penetration was unsealed and the other penetration was found with only temporary seal material installed in the penetration. This temporary material provided some fire resistance for the opening but did not provide a fire rated design. These fire barriers are required to be operable by Technical Specification 3.7.7. The cause of the event can be attributed to past procedure deficiencies with the penetration seal program as well as an isolated omission in the sealing of penetrations. Immediate corrective action involved the establishment of a fire watch and the permanent sealing of the openings with rated fire seals. Corrective action to prevent recurrence has been accomplished with the elimination of the use of temporary unrated fire seals and the completion of the penetration fire seal upgrade program. This event is reportable per 10CFR50.73 (a) (2) (i) (B) since it involved a condition prohibited by the plant's Technical Specifications.
2131993004 | Haddam Neck | 05/12/1993 | 10/13/1993 | 9310190136 | <strong>Entry Into Technical Specification 3.0.3 Due to Inoperable Service Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1993 at approximately 1208 hours, with the plant in Mode 1 at 99% power, while testing the 'A' service water pump, the control switches for the 'B' and 'C' service water pumps were placed in trip pullout (TPO) resulting in an entry into Technical Specification 3.0.3. The action was performed to prevent the pumps from automatically starting on low service water header pressure which was expected when additional service water flowpaths were valved in to achieve a 6000 gpm flowrate for the pump being tested. A Control Room Operator was in attendance for the duration of the test and the switches were taken out of TPO within one hour, in accordance with Technical Specification 3.0.3. The root cause of the event was procedural inadequacy in that the test procedure did not restrict performance of the test to Modes 5 or 6. A contributing cause was the failure to differentiate between entry into an action statement to facilitate required surveillance testing and entry into Technical Specification 3.0.3. Corrective action includes revising similar test procedures to include a Test Summary Sheet. Additionally, Operations personnel have been reminded of their responsibility not to enter Technical Specification 3.0.3 to facilitate surveillance testing. This event is reportable under 10CFR50.73 (a) (2) (i) (B) since it resulted in a condition prohibited by the plant Technical Specifications.
2131993005 | Haddam Neck | 05/18/1993 | 06/14/1993 | 9306180336 | <strong>Failure of Containment Isolation Valve to CLose Due to Corrosion in SOV</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1993, at 0915 hours, with the plant in Mode 5 (Cold Shutdown) it was discovered that one of the containment isolation valves for the reactor coolant letdown line (LD-TV-230) could not be closed from the control room using the control switch. LD-TV-230 is a normally open air operated valve located inside the containment. The problem was traced to a failure of the air pilot solenoid valve associated with LD-TV-230. The failure of this solenoid valve is believed to have been caused by corrosion inside the valve as the result of water intrusion from the containment control air system due to a malfunction of the containment control air dryer. Initial corrective action involved isolating the letdown line using other redundant valves in the line and initiating an investigation into the cause of the failure. At the time of discovery, the plant Technical Specifications did not require the containment isolation valves to be operable. Followup actions include replacement of the failed solenoid valve, a blowdown of the air system to remove any remaining water, and repair of the dryer malfunction. It is unknown how long this valve was inoperable prior to discovery, but is believed to have been longer than the action time allowed by the plant Technical Specifications. As such, this event is reportable under 10 CFR 50.73 (a) (2) (i) (B), since the plant had been in operation with a condition prohibited by the Technical Specifications.
2131993006 | Haddam Neck | 05/25/1993 | 06/22/1993 | 9306290245 | <strong>Emergency Diesel Generator Failure Resulting From Diode Assembly Short</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1993, at 1330 hours, with the plant in Mode 6 (Refueling) the 'A' Emergency Diesel Generator was manually shut down after 22 hours of a planned 24 hour endurance run at full rated load. Erratic diesel output and abnormal kilowatt, kilovar and ampere indications prompted the unplanned shutdown. Investigations within the generator excitation cabinet revealed that two voltage suppression devices (selenium rectifiers) had shorted and that the cabinet exhaust fan was not running. The root cause of this event was lack of adequate cooling inside the excitation cabinet, resulting in the failure of the selenium rectifiers which initially led to an abnormal field voltage condition and ultimately a loss of generator field. Initial corrective action included the installation of new diode assemblies and ventilation fan motors for both generators. This is being reported under 50.73 (a)(2)(vii) since it was an event where a single cause or condition caused two independent trains (EG2A and EG2B) to potentially become inoperable in a single system (onsite AC power) designed to mitigate the consequences of an accident.
2131993007 | Haddam Neck | 05/25/1993 | 06/22/1993 | 9306290295 | <strong>Pressurizer PORV Emergency Air Supply Pressure Decay Test Failure</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1993 at 0000 hours, with the plant in Mode 5 (Cold Shutdown) and performing a pressure decay test of the pressurizer Pilot-Operated Relief Valves (PORVs) emergency air supply system, it was determined that the pressure decay exceeded the Technical Specification acceptance criterion of 0.3 psi/hr. The problem was traced to a leak in the diaphragm assembly of one of the PORVs (PR-AOV-568). This leak was caused by both the inadequate sealing of the PORV diaphragm assembly and the failure of the PORV air supply pressure regulating valve (CA-PRV-836A). The failure of the air pressure regulating valve was caused by corrosion inside the valve due to water intrusion from the containment control air system. The moisture in the containment control air system was due to a malfunction of its air dryer. Corrective action includes the replacement of the PORV diaphragm assembly with one that has a configuration for tighter sealing, the replacement of the regulating valve, the blowdown of the air system to remove any remaining water, and repair of the air dryer malfunction. It is not known how long the PORV had been inoperable prior to this surveillance, but it is believed to have been longer than the ACTION time allowed. Therefore, this event is reportable under 10 CFR 50.73 (a)(2)(i)(B), since the plant had been in operation with a condition prohibited by the Technical Specifications.
2131993008 | Haddam Neck | 06/13/1993 | 07/12/1993 | 9307190151 | <strong>Steam Generator Eddy Current Testing Results Classified as Category C-3</strong><br /><i>Abstract:&nbsp;</i>Scheduled steam generator Eddy Current Testing (ECT) was conducted during the 1993 Refueling Outage in accordance with ASME Section XI and Technical Specification 4.4.5. On June 13, 1993 at approximately 0630 hours, with the plant in Mode 6 (Refueling), it was determined that analyzed ECT data placed steam generators No. 2 and 4 into the C-3 Category. This required an expansion of the ECT program to 100 percent of the tubes in all four steam generators. A prompt report of this event was made under 10CFR50.72 (b) (2) (i). The major cause of the tube defects was attributed to primary water stress corrosion cracking. As a result of the inspections, a total of 39 tubes were plugged and 83 tubes were re-rolled in the four steam generators. This event is reportable per 10CFR50 .73 (a) (2) (i) (B) since it involves a condition prohibited by the plant's Technical Specifications.
2131993009 | Haddam Neck | 06/22/1993 | 07/20/1993 | 9307290173 | <strong>Temporary Loss of Power Due to Breaker Protection Scheme Miswiring</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1993, at 0936 hours, with the plant in Mode 5 (Cold Shutdown), a temporary loss of offsite power was experienced. Test personnel were performing a test of the transfer trip scheme for the 115kV Station Service yard tie breaker 389T399. The test procedure included tripping of downstream breakers by the 389T399 Breaker Failure (BF) scheme. To accommodate the test, the bus 3 supply was transferred to Bus 2 through the 2T3 (4160v tie breaker) placing all station service power through the 3891 breaker. The 3991 breaker was withdrawn to the test position and closed to allow verification of the test trips without impacting other plant equipment. The procedure then specified to trip this breaker via the 389T399 BF lockout relay. During this step, the 3891 breaker tripped open instead of the 3991 breaker resulting in a temporary loss of offsite power. The cause of this event has been identified as wiring errors of the BF relay. The lockout contact and its associated isolation switch wiring for the 3991 breaker was found in the 3891 breaker trip circuit, in parallel with the contact arrangement for the 3891 breaker. This is being reported under 50.73 (a) (2) (iv) since there was an automatic actuation of an Engineered Safety Feature.
2131993010 | Haddam Neck | 06/26/1993 | 07/23/1993 | 9307280130 | <strong>Temporary Loss of Power During Surveillance Testing Due to Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1993, at 1917 hours, with the plant in Mode 5 (Cold Shutdown), a temporary loss of offsite power occurred while Operations personnel were performing a Partial Loss of AC test. Station bus 3 (powering half of the plant) was to remain energized through breaker 3991. When the bus 2 (powering the other half of the plant) supply breaker 3891 was tripped opened, the 3991 breaker also opened resulting in a total loss of normal power. The cause of the trip was traced to the bus 3 Undervoltage Trip and Lockout Scheme where the bus 3 undervoltage relay was found tripped due to a blown fuse. The cause of blown fuse is unknown. Similar usage on other bus undervoltage sensing relays was reviewed for the likelihood of a blown fuse going unnoticed. it was concluded that any other similar situations would have resulted in other indications which would initiate an investigation of the circuit malfunction. The Operator's shift log procedure was revised to cycle the Main Control Board (MCB) 4160 volt meter phase selector switch to check for blown fuses. This is being reported under 50.73 (a) (2) (iv) since there was an automatic actuation of an Engineered Safety Feature.
2131993011 | Haddam Neck | 07/06/1993 | 08/03/1993 | 9308090152 | <strong>Engineered Safety Features Actuation Due to Loss of Vital Buses C & D During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1993, at 0112 hours, with the plant in Mode 5 (Cold Shutdown), the High Containment Pressure Engineered Safety Feature was actuated when vital buses C and D were de-energized. The vital buses were inadvertently de-energized during the performance of PMP 9.1-35, 'Local Load Testing of EG2B'. Inverter C was supplying buses C and D at the time because inverter D was out of service. Inverter C had transferred to its alternate supply on instantaneous overcurrent and was blocked from retransfer because the 'auto retransfer' switch was 'off'. Personnel were unaware that inverter C had transferred to its alternate supply because the common main control board annunciator (vital C or D trouble) was locked in due to inverter D being out of service. This event is reportable under 10CFR50.73 (a) (2) (iv) since there was an unplanned automatic actuation of an Engineered Safety Feature. Procedural changes have been made to ensure the auto retransfer switch remains 'on'.
2131993012 | Haddam Neck | 07/14/1993 | 10/22/1993 | 9310270240 | <strong>Inadvertent Isolation of High Steam Flow Transmitters</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1993, at 1300 hours, with the plant in Mode 3 (Hot Standby) I&C Specialists discovered all four steam line flow transmitters isolated (low and high side isolation valves shut and equalizer valve open) during a routine leak check. Technical Specification 3.3.2, Engineered Safety Feature Actuation System Instrumentation, requires each steam line flow channel to be operable in Modes 1, 2 and 3. Each steam line flow transmitter provides an input signal to the Reactor Protection System which trips the reactor when high steam flow is detected in any two of four main steam lines. This signal also provides an input to the Engineering Safety Feature Actuation system which closes the main steam trip valves when high steam flow is detected in any two of four main steam lines. Short term corrective action consisted of returning each steam line flow transmitter to service. Long term corrective action will be developed based on the results of the Human Performance Enhancement System evaluation. This event is reportable under 10CFR50.73 (a) (2) (i) (B) since it resulted in a condition prohibited by the plant's Technical Specifications. This Supplemental Report provides the results of a Human Performance Enhancement System evaluation and identifies long term corrective action.
2131993013 | Haddam Neck | 07/19/1993 | 10/18/1993 | 9310250283 | <strong>Reactor Trip During Nuclear Instrumentation Testing</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1993 at 1448 hours with the plant in Mode 2 at 0.04 percent thermal power following a refueling outage, a control room operator was performing NOP 2.1-8, 'Nuclear Instrumentation Short Form'. After releasing the 'CAL' test switch while testing wide range channel #1, the operator inadvertently placed his initials adjacent to the next step which was to press and release the 'TRIP RESET' switch. The operator then proceeded to check wide range channel #2 at which time the 2 out of 4 high startup rate reactor trip logic was satisfied and a reactor trip occurred. The root cause of the event was inappropriate work practices, specifically the lack of exercising self-checking and verification techniques. Short term corrective action was to implement a procedure change to NOP 2.1-8 to add caution statements prior to testing each channel to ensure there are no trips present prior to proceeding. Long term corrective action will be to use a specific procedure for operability checks of the appropriate power range channel after disconnecting the reactivity computer used for low power physics testing. <br /><br /> This event is reportable under 10CFR50.73 (a) (2) (iv) as an event that resulted in the automatic actuation of the Reactor Protection System.
2131993014 | Haddam Neck | 06/04/1993 | 09/02/1993 | 9309080292 | <strong>Pressurizer Safety Valve Setpoint Drift Discovered During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1993, at 1430 hours with the plant in Mode 6 and defueled, a review of pressurizer safety valve test results determined that the lift setpoints for two of the three valves were out of tolerance. An engineering evaluation concluded on August 17, 1993, that this condition was reportable. The cause of this condition is attributed to the drift of the safety valve lift setting over the last operating cycle. Subsequent disassembly and inspection of the valves revealed no condition that could have affected the setpoint. Both valves were readjusted and satisfactorily tested. This event is being reported under 10CFR50.73 (a)(2)(i)(B) since it involves a condition prohibited by the plant's Technical Specifications.
2131993015 | Haddam Neck | 08/16/1993 | 09/09/1993 | 9309150056 | <strong>Erosion/Corrosion of Service Water Filter Housing</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1993 at approximately 1605 hours, with the plant in Mode 1 at 100 percent power, the results of an engineering evaluation were received that determined that the previously discovered erosion and corrosion in the Service Water Primary Adams Filters housing had degraded the filter to an inoperable condition during a postulated design basis seismic event. The degradation was discovered during the Cycle 17 refueling outage while performing routine maintenance. No actual component failures had taken place. The root cause of the event was component wear out due to flow induced erosion and river water corrosion which took place gradually over the last 26 years of operation. The corrective actions taken were to inspect and restore both Adams Filters to original design thickness by weld resurfacing. These activities were accomplished prior to startup from the recent refueling outage. This event is reportable under 10CFR50.73 (a) (2) (v) (D) since it was a condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
2131993016 | Haddam Neck | 09/20/1993 | 10/13/1993 | 9310190132 | <strong>Potential Inventory Diversion from the Demineralized Water Storage Tank</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1993, at 1525 hours, with the plant in Mode 1 at 100 percent power, an Engineering analysis concluded that, prior to the Cycle 17 refueling outage, the operability of the Auxiliary Feedwater system (AFW) could have been compromised by a failure of the condenser hotwell make-up valve concurrent with loss of both main Feedwater and Condensate pumps. The analysis determined that the potential existed to divert inventory from the demineralized water storage tank (DWST) to the hotwell at a rate greater than that previously assumed (reference LER 89-002-00). In this event, AFW might not have had an adequate water supply in the DWST to meet the basis of Technical Specifications. This event is historical since installation of a new condensate storage tank, during the May 1993 refueling outage, currently provides make-up and high level dump capacity for the hotwell and eliminated the potential for diversion of DWST inventory. This event is reportable under 10CFR50.73 (a)(2)(v)(B) since the historical condition could have prevented the fulfillment of the safety function of a system needed to remove residual heat.
2131993017 | Haddam Neck | 11/01/1993 | 11/19/1993 | 9312020110 | <strong>Both Trains of Service Water Declared Inoperable During Pump Maintenance and Strainer Cleaning</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1993, at 0550, with the plant operating in Mode 1 at 100 percent power, both service water headers were declared inoperable and the plant entered Technical Specification 3.0.3. The 'D' service water pump had been taken out of service for replacement on 10/31/93. At 0550 hours, the 'A' and 'B' service water pump strainers entered the required cleaning region of their fouling curve and the associated pumps were taken out of service one at a time to perform cleaning activities. This resulted in both service water headers being declared inoperable and necessitating entry into Technical Specification 3.0.3. Completion of strainer cleaning allowed the north service water header to be returned to service at 0600 hours and the plant exited Technical Specification 3.0.3. This scenario was repeated approximately once per shift the next two days until the 'D' service water pump was returned to service. The root cause of the event was excessive amounts of leaves and debris in the Connecticut River and the failure of the 'D' service water pump which necessitated replacement. This event is reportable under 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
2131993018 | Haddam Neck | 12/07/1993 | 01/03/1994 | 9401140128 | <strong>Feedwater MOVs Declared Inoperable Due to Insufficient Closing Torque</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1993, at 1330 hours, with the plant in Mode 1 at 50 percent power for main feedwater pump repairs, an Engineering evaluation determined that the Feedwater isolation motor operated valves (MOVs), FW-MOV-11, 12, 13 & 14, may not be capable of closing against their design basis differential pressure. Immediate operator action was to enter Technical Specification Action Statement 3.7.9. The Engineering evaluation was based on data released from EPRI on December 1 and 2, 1993, which indicated that valve factors assumed in original valve designs may not be sufficiently conservative. Analysis of the manufacturer's design valve factor used in the current setup of the M OVs indicated that the valves may not have been able to isolate flow under design bas is conditions. The cause of the event was the use of non- conservative valve factors in the original valve design basis. A modification was made to the operators to ensure that they would perform their intended safety function for the rest of the current operating cycle. This was accomplished by changing the control circuitry to electrically bypass the torque switch until valve travel reached the point of disk-seat overlap. This modification was successfully tested to ensure proper performance and the valves were returned to service on December 9, 1993 at 1324 hours.
2131993019 | Haddam Neck | 12/17/1993 | 01/14/1994 | 9401260015 | <strong>Incorrect Action Statement Applied to Inoperable Fire Door</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1993, at 1000 hours, with the plant in Mode 1 at 100 percent power, plant personnel determined that an inappropriate ACTION statement had been used while attempting to comply with the requirements of Technical Specification 3.7.7, 'Fire Rated Assemblies'. On December 13, 1993, at 1857 hours a fire door (T594) which separates the turbine building upper level from the service building access hallway was declared inoperable due to damage to the door. An hourly fire watch patrol was established in accordance with ACTION statement a.1. On December 17, 1993, it was determined that the conditions allowing the use of ACTION statement a.1 did not exist and that a continuous fire watch was required in accordance with ACTION statement a.2. The cause was misinterpretation of the Technical Specification ACTION statement. This interpretation had been used in the past for similar occurrences and was determined to be appropriate at the time. Immediate corrective action was to establish a continuous fire watch at 1000 hours on December 17, 1993. Additional corrective action will consist of issuing a clarification of Technical Specification 3.7.7 ACTION statements to plant operators. This event is reportable under 10CFR50.73 (a) (2)(i)(B) since it resulted in a condition prohibited by the plant's Technical Specifications.
2191993001 | Oyster Creek | 01/01/1993 | 01/20/1993 | 9301270190 | <strong>Standby Gas Treatment System Initiation Caused by Lightning Arrestor Failure</strong><br /><i>Abstract:&nbsp;</i>On January 1, 1993, at 1130 hours a lightning arrestor on an offsite power line failed, causing power perturbations in the plant electrical system. A Standby Gas Treatment System (SGTS) initiation signal was generated by a high level trip of the Reactor Building Ventilation radiation monitor resulting from the power perturbations. The plant was shut down and defueled at the time and part of the electrical distribution system was out of service for maintenance. The offsite line's breaker was manually opened until repairs could be made to the lightning arrestor (1210 hours). The Reactor Building Ventilation system was returned to operation and the SGTS was secured at 1140 hours. The safety significance of the event is minimal because it represented only an unnecessary challenge to Secondary Containment isolation and SGTS initiation circuits.
2191993002 | Oyster Creek | 01/25/1993 | 02/26/1993 | 9303040257 | <strong>Reactor Coolant Exceeds Temperature Limit While Shutdown Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1993 at 1730 hours, plant personnel discovered that reactor metal temperature was above 212 degrees F without Primary Containment in effect, without Isolation Condensers operable, without Containment Spray/Emergency Service Water operable., with only one system of the Core Spray operable, and without a Shift Technical Advisor stationed. The plant was shut down for a refueling outage at the time. Reactor water level had been lowered in accordance with a temporary procedure change which did not provide for sufficient forced circulation to cool the reactor. The cause of the event was personnel error in improper implementation of technical guidance and subsequent reviews prior to implementation which did not recognize the error. The event had safety significance in that reactor temperature exceeded 212 degrees F for several hours without detection. Immediate corrective action was taken to reduce reactor coolant temperature and cancel the temporary procedure change. Future corrective actions include: revising the Shutdown Cooling operating procedure, reviewing the effectiveness of safety review of temporary procedure changes, discussion with personnel involved with the procedure change, and training of procedure reviewers.
2191993003 | Oyster Creek | 01/30/1993 | 02/26/1993 | 9303100114 | <strong>Scram Discharge Volume High Level Scram Caused by Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>A full reactor scram was initiated while performing system lineups to return the Control Rod Drive system to its normal configuration after a Primary Containment integrated leak rate test on January 30, 1993, at 1258 hours. The plant was shut down for a refueling outage at the time. The cause of the occurrence was an inadequate procedure. The order in which the procedure steps were written led the operator to remove the Scram Discharge Volume (SDV) high water level scram bypass signal while there was still a high water level in the SDV. The next step instructed the operator to open the vent and drain valves, which would remove the water from the volume. The order of these steps should have been reversed. This event has no safety significance since the scram functioned as required and represented only an unnecessary challenge to the equipment. Immediate corrective action was taken to bypass the scram signal, drain the SDV, and reset the scram. The bypass switch was returned to normal. The Primary Containment integrated leak rate test procedure will be revised as necessary to prevent this event from recurring.
2191993004 | Oyster Creek | 06/02/1993 | 12/23/1993 | 9401060050 | <strong>Incorrect UFSAR Resulted in Potential Design Concerns</strong><br /><i>Abstract:&nbsp;</i>The Updated Final Safety Analysis Report, Section 6.2.3.2, describes blow out panels in the Reactor Building which would relieve Reactor Building internal pressure at a pressure of 0.25 psig. During the performance of a recent engineering evaluation, the blow out panels could not be located either by document review or inspection of the visible section of the Reactor Building. Initially, a preliminary calculation indicated that Reactor Building internal pressure would reach 0.95 psig during a high energy line break outside of containment. This resulted in four areas of concern: 1) damage to the torus; 2) failure of internal masonry block walls adjacent to the southeast corner room; 3) Reactor Building structural damage; and 4) Equipment Qualification profiles. <br /><br /> A final calculation has demonstrated that the Reactor Building siding will relieve pressure at 0.20 psig. Therefore, the four previous potential concerns were eliminated and this discovery has been determined to be not reportable. The cause of this event was inadequate documentation. The UFSAR and any other affected document will be revised to include the results of the recent evaluation.
2191993005 | Oyster Creek | 09/09/1993 | 08/31/1994 | 9409140088 | <strong>Second Level Undervoltage Trip Protection Setpoint May be Incorrect</strong><br /><i>Abstract:&nbsp;</i>During a review of the Limiting System Setpoints in the Oyster Creek Nuclear Generating Station Technical Specifications, it was determined that Technical Specification 2.3.P.(2) could not be proven to adequately protect loads on the 4160 volt AC buses as designed. This setpoint, 3671 VAC +/-1%, protected Oyster Creek from a degraded grid undervoltage condition and was approved by the USNRC on October 16, 1981. <br /><br /> During the month of August 1993, it was discovered that the possibility existed that under certain conditions some loads downstream of the 4160 VAC buses may not be able to perform their intended safety functions. This occurrence is of minimal safety significance as a degraded grid condition is highly unstable and would be of limited duration. <br /><br /> Additional analysis was performed in February of 1994 to include the 120V Vital AC system. Administrative controls were implemented to monitor startup transformer 4160V bus voltage to ensure adequate offsite voltage available for all loads. A Technical Specification Change Request was submitted to raise the degraded grid undervoltage setpoint. Modifications to support the proposed setpoint will be implemented.
2191993006 | Oyster Creek | 05/08/1992 | 12/15/1994 | 9412230109 | <strong>Plant Operation Outside Design Basis During Surveillance Testing Due To Procedure Omission</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1991, Technical Specification Amendment 153 became effective requiring a Maximum Average Planar Linear Heat Generation Rate (MAPLHGR) reduction to less than 90% if one Core Spray loop/component becomes inoperable. <br /><br /> On October 21, 1993, it was identified that several Core Spray System surveillance procedures have both main pumps or main discharge valves of either loop disabled. On four occasions the MAPLHGR exceeded 90% during the execution of these procedures, thus placing the system outside of its design basis. The cause of this event was the omission of the above mentioned procedures to be revised subsequent to the issuance of the Technical Specification Amendment 153. Safety Significance is minimal since the design basis conservatism exceeds the amount by which the plant operated above the Technical Specification limits for MAPLHGR. In addition, operator actions could have brought the disabled Core Spray loop to full operating status, had an accident occurred. <br /><br /> Interim Corrective Action was taken to ensure that MAPLHGR does not exceed 90% during the execution of the subject procedures. All pertinent surveillance procedures have been revised to ensure MAPLHGR has been reduced to 90% or below prior to their execution.
2191993007 | Oyster Creek | 11/17/1993 | 12/17/1993 | 9312300055 | <strong>Failure to P rform Required APRM Surveillance with Maximum Recirc Flow</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993 while the plant was in the RUN mode, it was discovered that the Average Pow er Range Monitor (APRM) system flux scram was not being tested with simulated recirculation flows greater than 100%. This condition has existed since initial plant operation and had resulted from a misunderstanding of the Technical Specification requirements. The existing surveillance procedure required testing the flux scram setpoint with simualted flows of 50% and maximum operating flow of 100%, but did not require testing flux scram setpoints with simualted flows greater than 100%. <br /><br /> Immediate corrective action was taken to surveil the flux scram setpoint with simulated recirculation flow greater than 100%. Seven of the eight APRM channels tested after the discovery of the omission were found to be within Technical Specification limits. The safety significance of this event is considered minimal as: 1) controls specify the upper range of recirc flow to be 61 x 10** 6 lbm/hr which is equal to 100% rated flow; and 2) seven of the eight channels were found in specification. A review of Technical Specification section 2.3 was conducted to verify that appropriate setpoints are being surveilled.<br /> ?
2191993008 | Oyster Creek | 12/03/1993 | 12/23/1993 | 9401060036 | <strong>Inadvertent Actuation of Core Spray System I During Surveillance Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1993 at approximately 1115 hours, the reactor was operating at approximately 100% power and Procedure 610.3.105, Core Spray System I Instrument Channel Calibration Test and System Operability Surveillance was in progress. I & C Technicians performing this test removed fuses from System II rendering it inoperable. When System I was tested, it inadvertently initiated. Reactor Pressure Vessel injection did not occur because the Core Spray System is designed to inject at pressures less than 350 psig. This event was caused by inattention to duty. <br /><br /> Core Spray System I was returned to operation. System II was returned to operation and operability was demonstrated. A critique was held and appropriate personnel actions were taken with respect to the individuals involved. Corrective actions will be incorporated into the I & C Personnel training program. <br /> ?
2201993001 | Nine Mile Point 1 | 01/11/1993 | 02/05/1993 | 9302180082 | <strong>Operation in Excess of 100 Percent Rated Core Thermal Power Due to Lack of Procedural Requirement and Poor Man- Machine Interface</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1993 at 1022 hours, with the mode switch in the 'RUN' position, Nine Mile Point Unit 1 (NMP1) discovered that it had exceeded 100 percent of rated core thermal power (i.e., 1850 Megawatts Thermal (MWt)). Specifically, reactor power was found to be 100.5 percent of rated core thermal power (i.e., 1858 MWt). As a result, NMP1 operated in excess of the licensed maximum power level of 1850 MWt, exceeded the power-flow limiting values of the Core Operating Limits Report, and operated outside of its design basis. <br /><br /> The Reactor Water Cleanup (RWCU) System flow rate process computer point input dropped out of the computer's core thermal power calculation, causing NMP1 to exceed rated core thermal power. The root cause of this was the failure of multiple barriers that should have allowed operators to detect the loss of the RWCU System flow rate computer point. Contributing causes were managerial methods and procedure deficiencies. <br /><br /> Immediate corrective actions included reducing reactor power below 100 percent of rated core thermal power. Long term corrective actions include the requirement to perform an OD-3, 'Core Thermal Power Calculation,' following events or plant evolutions which may impact computer points that input into the core thermal power calculation. Additionally, training, procedure changes, and equipment repair will be performed. This event is being reported in accordance with Technical Specification 3.1.7.g as well as 10CFR 50.73.
2201993002 | Nine Mile Point 1 | 01/26/1993 | 07/07/1993 | 9307190055 | <strong>Automatic Reactor Scram on High Neutron Flux Signal Received During Surveillance Testing due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1993 at 0936 hours, Nine Mile Point Unit 1 (NMP1) received an automatic reactor scram initiation signal. Specifically, while performing a monthly calibration test on Average Power Range Monitor (APRM) Flow Converters, a high neutron flux trip signal was inadvertently initiated on Reactor Protection System (RPS) Channel 12 while a manual halfscram signal was inserted on RPS Channel 11. At the time of the event, the plant was operating at 100 percent rated thermal power with reactor pressure at 1030 pounds per square inch gauge (psig) and reactor temperature at 531 degrees Fahrenheit. <br /><br /> The root cause for this event has been determined to be personnel error by failure to follow a procedure.<br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. Additional corrective actions included: 1) improving management expectations during pre-job briefing activities; 2) revising supervisory roles during surveillance testing and; 3) issuing a Lessons Learned Transmittal.
2201993003 | Nine Mile Point 1 | 03/07/1993 | 07/02/1993 | 9307130372 | <strong>Local Leak Rate Tests Exceed Regulatory Limit</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1993 and March 7, 1993, with the Nine Mile Point Nuclear Station Unit 1 (NMP1) in a refueling outage and primary containment not required, valves 33-01R (Reactor Water Clean Up Inside Isolation Valve) and 33-03 (Reactor Water Clean Up Outside Isolation Valve), respectively, failed their Technical Specification required Local Leak Rate Test (LLRT) limit of 5 percent L sub to (i.e., 13.07 Standard Cubic Feet per Hour [SCFH!). These valves are the isolation valves for primary containment penetration X-154. As a result of the failed LLRTs, the primary containment Technical Specification required leak rate limit of L sub t (348.85 SCFH at 22 psig) and the 10CFR50 Appendix J limit of 0.6 L sub a (386.45 SCFH at 35 psig) were exceeded. Under this condition, the primary containment is considered inoperable with respect to providing a leakage boundary and represents a degradation of a principal safety barrier. <br /><br /> Root cause analyses were performed for both valve 33-01R and for valve 33-03. The cause of valve 33-01R failing its LLRT was improper fit-up of the valve's internal components and incorrect seat tightness when the valve was installed in 1991. The cause of valve 33-03 failing its LLRT was deterioration of the soft seat due to a design deficiency. <br /><br /> The immediate corrective action was to declare the valves inoperable. Valves 33-01R and 33-03 were repaired and they subsequently passed their LLRTs.
2201993004 | Nine Mile Point 1 | 03/13/1993 | 04/12/1993 | 9304160081 | <strong>Loss of Effluent Monitoring Caused by Personnel Error Resulted in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1993 at 0035 hours, it was discovered that Nine Mile Point Unit 1 (NMP1) was operating outside of a Technical Specification requirement to continuously monitor gaseous effluents in accordance with the requirements of Technical Specification Table 3.6.14-2. Specifically, a selector switch for the two installed continuous monitoring systems was placed in a position that interrupted the auxiliary equipment sample path. At the time of the event, NMP1 was in a refueling outage with the reactor vessel head removed and all the fuel removed from the reactor to the spent fuel pool. <br /><br /> The root cause of this event has been determined to be a personnel error caused by less than effective operator training. A contributing cause was inadequate written communications. <br /><br /> The immediate corrective actions were to restore the auxiliary sampling from the stack, place a yellow hold out tag on the selector switch, and properly return the continuous stack gaseous monitoring system to service. Other corrective actions include: 1) upgrading Operations training on the system; 2) revising the Operations procedure; 3) installing a warning label on the selector switch; and 4) modifying the markup data base.
2201993005 | Nine Mile Point 1 | 03/31/1993 | 04/30/1993 | 9305120278 | <strong>Tech Spec violation caused by inadequate jumper control due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1993, Nine Mile Point Unit 1 (NMP1) was in a refueling outage with fuel in the vessel and the mode switch in REFUEL. At 1615 hours, during control rod exercising, a jumper was found on the 'One Rod Permissive' logic for control rod 3003. With the jumper installed, the potential existed to withdraw two control rods (Rod 30-03 and any other control rod). This is a violation of Technical Specification (TS) 3.6.2g(7), requirement that a rod block prevent the withdrawal of more than one rod with the mode switch in the refuel position. <br /><br /> The root cause of this event was personnel error due to inadequate work practices that failed to maintain configuration control over the 'One Rod Permissive' logic bypass jumper. Contributing to the event were deficiencies within Fuel Handling Procedure, (FHP) N1-FHP-27B, 'Whole Core Reload'. <br /><br /> The immediate corrective actions taken included removal of the jumper, and verification that control rod 30-03 had been fully inserted when any other control rod was exercised. A lessons learned transmittal will be generated and communicated to cognizant personnel associated with the refueling process to stress the corrective actions that were taken in accordance with procedure NIP-ECA-02. In addition, N1-FHP-27B will be revised.
2201993006 | Nine Mile Point 1 | 04/13/1993 | 05/10/1993 | 9305140179 | <strong>Reactor Scram on Intermediate Range Monitor High Neutron Flux Caused by Electrical Noise</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1993, at 1810 hours, Nine Mile Point Unit 1 (NMP1) received an automatic reactor scram initiation signal resulting in a full scram. While performing N1-IPM-092-231, 'IRM Monitor Gain Adjustment to Reactor Power,' a spurious Intermediate Range Monitor (IRM) high-high neutron flux trip was received when 17 IRM was taken out of bypass. At the time of the event, the plant was being started up with the mode switch in the 'STARTUP' position and the reactor at the point of adding heat, reactor pressure was atmospheric and reactor temperature was 140 degrees Fahrenheit. <br /><br /> The root cause of this event was determined to be electrical noise generated by energizing/de-energizing the IRM bypass relays. <br /><br /> Immediate operator actions included commencing scram recovery activities. <br /><br /> Additional corrective actions included determining the cause for the IRM spike and installing a noise suppression circuit to correct the cause.
2201993007 | Nine Mile Point 1 | 08/31/1993 | 09/24/1993 | 9310010057 | <strong>Loss of Offsite Power Due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1993 at 14:33 hours (during a severe thunderstorm), with the mode switch in 'RUN,' reactor power at 97.8 percent thermal and station service power being supplied from the main turbine generator, Nine Mile Point Unit 1 (NMP1) experienced a momentary Loss of Offsite Power (LOOP) that resulted in the automatic start of Emergency Diesel Generators (EDG) 102 and 103. The LOOP resulted in the de-energization of Power Board (PB) 101, which caused the subsequent loss of Reactor Recirculation Pump (RRP) #13. The loss of RRP #13 reduced reactor power to approximately 87 percent thermal. An Unusual Event was declared per Emergency Plan Procedure EPP-01. <br /><br /> The cause of the event was two concurrent lightning strikes on both 115kv lines, line #1 at NMP1 and line #3 at Lighthouse Hill. <br /><br /> The immediate corrective action was to enter Special Operating Procedure N1-SOP-5, 'Loss of 115kv,' verify auto start of EDGs, stabilize plant electrical loads according to procedure, and contact Relay and Control Personnel to analyze the event and record relay flags received. The Loss of Offsite Power was corrected approximately 12 seconds into the event when breaker R30 auto re-closed re-energizing line #3.
2371993001 | Dresden 2 | 01/08/1993 | 04/05/1993 | 9304080139 | <strong>Historical Analysis determined unanalyzed support removed on Isolation Condenser fill line outside FSAR Limits</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1992, Unit 2 was in the RUN mode at 73% core rated thermal power. At approximately 0730 hours, as part of plant modification M12-2-90-057C 'Isolation Condenser Upgrade, Non-Outage Portion', pipe fitters removed sway support M-1170D-58 from Isolation Condenser [BL] Clean Demineralized Water [KC] Fill Line 2-4388-4'-LX. It was determined that the modification design was improperly scoped and that the line was not analyzed with the support removed. Work began immediately to install the new support. On December 23, at 1645 hours, NED determined that with the support removed the line was operable. The new support was installed by December 24, 1992. On January 8, 1993, a historical analysis determined that with the support removed the FSAR limits were exceeded. On January 29th a walkdown of the subject piping revealed that a four way restraint was missing. On February 3, 1993 it was determined that ENS notification of this event should have been made on January 8, 1993. ENS notification was made at 1702 hours on February 3, 1993. The apparent cause of the initial event was procedural deficiency. The designers and installers walkdown checklists did not provide enough direction to prompt consideration of how temporarily removing the support would affect unit operations. The immediate corrective action was to install the new support. Four similar occurrences were identified, but due to root cause differences this is considered an isolated event.
2371993002 | Dresden 2 | 01/21/1993 | 11/21/1994 | 9411290270 | <strong>Type B And C Primary Containment Local Leak Rate Testing Limit Exceeded Due To Leakage Past Head Cooling Inlet Isolation Valve 2-205-2-4.</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1993 with Unit 2 in a refuel outage, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the Head Cooling Inlet Isolation Valve 2-205-2-4 to be leaking an undetermined amount. This exceeded the maximum pathway leakage rate for Type B and C primary containment leakage, 488.452 scfh (0.6L sub a), as listed in Technical Specification 3.7.A.2.b.(2)(a). Once the leakage rate was recorded, the valve was again verified to be in the fully closed position. The measured leakage rate dropped to 3.0 scfh upon increasing the seating force. The valve operator was repaired under Work Request D10353, which reduced the leakage to 2.84 scfh. The safety significance of the leakage past valve 2-205-2-4 has been considered to be minimal since the redundant Head Cooling Isolation Valve 2-205-27 leaked 3.31 scfh; therefore, the total through leakage out of the penetration, on a minimum pathway basis, was 3.31 scfh. <br /><br /> The total as-found minimum pathway leakage (Type A test) was 2.3718 wt%/day which exceeded the Technical Specification 3.7.A.2 limit of 1.2 wt%/day. Calculations have been performed to prove this leakage did not exceed 10 CFR Part 100 limits.
2371993003 | Dresden 2 | 01/19/1993 | 02/18/1993 | 9308020149 | <strong>Outboard Main Steam Line Isolation Valve 2-203-2A As Found Leakage Rate Exceeded the Technical Specification Limit of 11.5 scfh</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1993 with Unit 2 in a refuel Outage, the performance of Dresden Technical Surveillance (DTS) 250-03, Main Steam Isolation Valve Local Leak Rate (Wet) Test, identified that the 'A' Main Steam Line Outboard isolation Valve [SB], 2-203-2A, was leaking 14.96 scfh. This leakage rate exceeds the limit specified in Technical Specification 3.7.A.2.b.2.c, which limits the leakage past any main steam isolation valve (MSIV) to 11.5 scfh when tested with air at a pressure of 25 psig. The Shift Engineer was notified that the leakage rate for the 2-203-2A MSIV had exceeded the Technical Specification limit of 11.5 scfh and a Problem Identification Form (PIF) was initiated per Dresden Administrative Procedure (DAP) 02-27, Integrated Reporting Process. Work Request (WR) 15596 was written to inspect and repair the valve to reduce leakage. The safety significance of the leakage past outboard MSIV 2- 203-2A has been considered to be minimal since the redundant inboard MSIV 2-203-1A had a leakage rate of 2.39 scfh; therefore, the total through leakage out of the penetration, on a minimum pathway basis, was 2.39 scfh and would not cause the maximum off site dose rates established in 10 CFR 100 to be exceeded. MSIV 2-203-2A was inspected and repaired to identify and correct the cause of the unsatisfactory leakage. In addition, inboard MSIVs 2-203-1C and 2-203-1D were also inspected and repaired, since the as-found leakage past these valves indicated an upward trend.
2371993004 | Dresden 2 | 01/31/1993 | 03/01/1993 | 9303040202 | <strong>Main Steam Line High Temperature Switches Found Outside Technical Specifications Limits Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1993, while performing Dresden Instrument Surveillance (DIS) 250-9, Main Steam Line (MSL) Tunnel Area Temperature Switch Calibration and Maintenance Inspection, the as-found.trip setpoints for temperature switches 2-261-15A, -16A, -17A, -18A, -15D, and -18D were found outside of Technical Specification (Tech. Spec.) limits. The apparent cause of the event was attributed to setpoint drift of the temperature switches. No physical damage or excessive wear was found on the switches to account for the drift experienced. The safety significance was determined to be minimal since sufficient redundancy was maintained to assure a Primary Containment Group I Isolation from MSL tunnel high temperature was available. In addition, the reactor was in the Refuel mode at the time of the event. As corrective action, all affected switches were replaced and calibrated in accordance with DIS 250-9. Similar previous events are listed under Section F of this report.
2371993005 | Dresden 2, Dresden 3 | 03/05/1993 | 03/26/1993 | 9307200260 | <strong>Postulated LPCI Swing Bus Loss Resulting From an Original Construction Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1993, Dresden Station determined there exists a potential design deficiency concerning the LPCI Swing Bus during degraded voltage conditions. Specifically, the potential exists that during a LOCA condition concurrent with degraded voltage that there are single component failures that result in the failure of the LPCI Swing Bus and the associated 4 KV Safety Bus to transfer to their respective alternate supplies, resulting in sustained degraded voltage. Sustained degraded voltage on the LPCI Swing Bus and associated 4 KV Safety Bus results in the failure of both LPCI and Division II Core Spray Systems, resulting in an Emergency Core Cooling response that is more limiting than the current licensing basis. <br /><br /> Based on the review of this issue, Dresden Station has concluded that this event is not within the current licensing basis, and due to the extremely low probability of occurrence and availability of core cooling systems, is of minimal safety significance. Therefore this event was deemed not reportable. However, because of the nature of this issue, Dresden Station has elected to provide this voluntary report.
2371993006 | Dresden 2, Dresden 3 | 04/28/1993 | 05/28/1993 | 9306030050 | <strong>Inadvertent Auto Start of 2/3 Diesel Generator Due to BUS 33 Main Feed Breaker Auxiliary Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1993 at 1712 while transferring Auxiliary Power (Bus 33 feed from transformer (TR) 32 to TR 31) the unit 2\3 Diesel Generator auto-started. Bus 33 was being fed from TR 32. The feed breaker from TR 31 to Bus 33 was closed in. The Operator verified the breaker closing by the breaker position indication and verified load pickup on TR 31 to the bus. When Bus 33 feed breaker from TR 32 was opened to complete the power transfer, the 2/3 Diesel Generator auto started. <br /><br /> The feed breaker from TR 32 was reclosed to Bus 33 and the feed breaker from TR 31 was reopened. Inspection revealed that the linkage arm for the stationary auxiliary switch contacts was not in place. With these contacts not actuated the 2/3 Diesel Generator logic saw both Main feed breakers to Bus 33 as open. The feed breaker from TR 31 was taken OOS and a Work Request (D 18154) was initiated to repair the stationary contact arm. EMD found the linkage had come apart at a connection point. The entire linkage was removed, reassembled and reinstalled. The breaker was then reinstalled and tested satisfactorily.
2371993007 | Dresden 2 | 05/04/1993 | 05/28/1993 | 9306090099 | <strong>ESF actuation (ADS) Due to Simultaneous Performance of LPCI and ADS Surveillance</strong><br /><i>Abstract:&nbsp;</i>While performing Auto-Blowdown Logic Test (DIS 250-4) and LPCI Pump Operability Test (A monthly surveillance, DOS 1500-6) simultaneously, all five Automatic Depressurization System (ADS) valves received an open signal. <br /><br /> On May 4, 1993 at 1929 with Unit 2 in a refueling outage, the Unit 2 Automatic Depressurization System Relief Valves received a signal to open during the performance of the monthly LPCI Operability surveillance, (DOS 1500-6). Instrumentation Technicians were performing Auto-Blowdown Logic Testing (DIS 250-04) at the same time. The ADS Logic Testing was immediately secured.
2371993008 | Dresden 2 | 07/06/1993 | 07/30/1993 | 9312210145 | <strong>Trip of Bus 29 Feed Breaker to Motor Control Centers 29- 2 and 29-4 Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>During performance of Dresden Operating Surveillance (DOS) 1500-05, Low Pressure Coolant Injection (LPCI) System Quarterly Flow Rate Test, while cycling Motor Operated Valve (MOV) 2-1501-38B, an Average Power Range Monitor (APRM) HI HI channels 1/2/3 half scram was received and 480 Volt Switchgear 29 breaker cubicle 3D opened. Motor Control Center (MCC) 29- 2 and MCC 29-4 de-energized. Shortly thereafter, trips of Unit 2 125 Volt Charger 2, Unit 2/3 250 Volt Battery Charger, LPCI/Core Spray Cooling Area Fan 2B occurred. Reactor Building Ventilation System isolated and Standby Gas Treatment System auto-started. Unit 2 was placed in a 24 hour shutdown Limiting Condition for Operation. The immediate corrective actions were to restore the tripped plant equipment. The Switchgear breaker was replaced. With Unit 2 in run mode, eleven days after the first trip, a second trip occurred. LCO was entered. Power was restored to the MCCs, and RPS Channel A was placed on alternate power. No apparent cause has been identified, and the investigation into the tripping events is still in progress. The safety significance of the trips is considered minimal. No previous events have been identified.
2371993009 | Dresden 2 | 03/02/1993 | 03/26/1993 | 9304060037 | <strong>HPCI Steam Piping Found Outside FSAR Design Limits Due to Absence of Grout in the HPCI Steam Line Floor Penetration</strong><br /><i>Abstract:&nbsp;</i>At 1330 hours on March 2, 1993, with Unit 2 shutdown and in the refuel mode, an engineering evaluation was completed that determined that the Unit 2 HPCI (BJ) steam line piping was operable but outside the Final Safety Analysis Report (FSAR) design limits. This evaluation was initiated as a result of an engineering walkdown of the HPCI steam line that called into question whether the HPCI steam line floor penetration was grouted (as analyzed for under IE Bulletin 79-14) or not. While the piping analysis was being performed for the postulated scenario of an ungrouted penetration, a work request was initiated to remove the insulation from the penetration in order to determine if it was grouted or not. The inspection showed the penetration indeed was not grouted creating a discrepancy between the analyzed and the as-built configurations. The engineering evaluation was completed showing that the HPCI piping was outside its design basis limits but was operable. A Problem Identification Form (PIF) was generated to document the discrepancy. The Nuclear Engineering Department confirmed through walkdowns that this problem did not exist on Unit 3 and recommended that the Unit 2 penetration be grouted prior to startup of Unit 2. This action is being implemented during the present D2R13 refuel outage. The safety significance of this event is minimal since the HPCI piping meets operability requirements. There has been one previous occurrence involving a 79-14 issue in which systems were discovered outside of design allowables.
2371993010 | Dresden 2 | 03/03/1993 | 03/30/1993 | 9304050217 | <strong>Main Steam Safety Valve Outside Technical Specification Limit Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1993 while performing Dresden Maintenance Procedure (DMP) 200-03, Main Steam Safety Valve Pre-Maintenance Test, the as-found lift setpoint for main steam safety valve 2-203-4C was found outside of Technical Specification (Tech. Spec.) limits. The apparent cause of the event was attributed to setpoint drift. The safety significance was determined to be minimal since the setpoint drift did not exceed the 3% ASME band which is also used in the reactor vessel overpressurization reload analysis. As corrective action, the affected valve will be rebuilt and calibrated in accordance with DMP 200-30, Reactor Main Steam Safety Valve Repair and Post Maintenance Testing, and DMP 040-30, Safety/Relief Valve Lapping. A rebuilt, calibrated safety valve was installed in its place. Similar previous events are listed under Section F of this report.
2371993011 | Dresden 2, Dresden 3 | 03/03/1993 | 06/04/1993 | 9306140284 | <strong>Emergency Source of Water to ECCS Keep Fill Valved Out, Supplement 1</strong><br /><i>Abstract:&nbsp;</i>At 1600 hours on March 3, 1993, with Unit 2 in Refuel mode and Unit 3 in Shutdown mode, a Problem Identification Form was initiated by the Nuclear Engineering Department (NED) which stated that the emergency source of water to the Containment Cooling Service Water (CCSW) Keep Fill system was 'valved out' and is currently unavailable on both Units 2 and 3. In an effort to ensure adequate cooling water flow to the Emergency Diesel Generator by valving out flow to the ECCS room coolers, the emergency source of water to the Containment Cooling Service Water Keep Fill system was inadvertently 'valved out'. The exact cause of the improper valve line up is still under investigation. A loss of keep fill pressure for a prolonged time could allow system drain down. If system drain down occurs a water hammer could occur which could pipe stresses to exceed pipe stress allowables identified in the FSAR. It appears, that after analyzing a water hammer event discovered in October 1981, a temporary loss of keep fill to a filled CCSW system will not result in a water hammer and therefore the safety significance of this event is minimal. Corrective actions include the installation of a new keep fill line on both Units Two and Three. These new keep fill lines will be in addition to the existing keep fill system and will be fed directly from the corresponding Unit's Emergency Diesel Generator Cooling Water Lines.
2371993013 | Dresden 2 | 05/19/1993 | 06/11/1993 | 9306230040 | <strong>Momentary Reactor Manual Control System Rod Select Matrix Interlock Failure Due to Relay Failure</strong><br /><i>Abstract:&nbsp;</i>At 1030 hrs, on May 19, 1993, the Dresden Unit 2 Reactor Manual control System's JD single rod selection interlock failed when it allowed two control rod drives to be selected at the same time with the reactor in the Refuel mode. Control Rod Drive (CRD) Stall Flow Test at the time of the event. Both rods accepted an insert signal and traveled from position '00' to the overtravel-in position before settling back at position '00'. No rod withdrawal occurred during the event. The immediate corrective action was deselecting both rods by turning the power to the control rod select matrix off. The event was deemed reportable per 10CFR50.73(a)(2)(ii). The most probable cause of this event is a temporary malfunction of the auxiliary relay connected in parallel with the rod select matrix switch holding coil for rod H-09. A work request has been issued for the replacement of this relay.
2371993014 | Dresden 2 | 07/08/1993 | 07/29/1993 | 9308060358 | <strong>Drywell Equipment Drain Sump (DWEDS) Pumping Interval Exceeded Due to Sump Pumps Tripping Thermally</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1993 at 0900 hours a 24-hour Shutdown Limiting Condition for Operation (LCO) was initiated because drywell leakage could not be quantified. The Drywell Equipment Drain Sump (DWEDS) pumps tripped thermally prior to reaching the low level cutout point during the 0800 hours pump down evolution. Per Technical Specification 4.6.D.1 and 3.6.D.1 the drywell sumps must be pumped down every 4 hours and drywell leakage quantified. Because the pumps were tripping thermally, the control switches were placed in Pull-To-Lock (PTL) and the DWEDS allowed to fill until it overflowed to the Drywell Floor Drain Sump (DWFDS). At 1800 hours the DWFDS was pumped down and drywell leakage was determined to be 2 gallons per minute, the same as before the DWEDS pumps tripped thermally. At 1815 hours the LCO was terminated. Subsequent pumping of the DWFDS quantified total drywell leakage to be 2 gallons per minute. <br /><br /> This event had minimal safety significance because there were no abnormal inputs to the DWEDS during this time frame. Once the DWEDS pump control switches were placed in PTL, any significant drywell leakage would have been indicated by the DWFDS level alarms. It is believed that some type of foreign object is restricting the DWEDS pumps suction causing the breakers to trip thermally. Currently the DWEDS pumps are being operated to clear the high level alarm and every 4 hours the DWEDS are operated to clear the high level alarm. In this way drywell leakage is quantified and Technical Specifications are fully met. The DWEDS pumps breakers still trip thermally on occasion when pumping to clear the high level alarm every 4 hours. When a Unit 2 shutdown permits a drywell entry, the DWEDS pumps will be removed per Station Work Requests and the DWEDS cleaned as required. Q:\6945\237\180\93\014
2371993015 | Dresden 2 | 05/27/1993 | 06/18/1993 | 9306290059 | <strong>Unit 2 Reactor Scram, Group 2 and Group 3 Isolation, While Shutdown Due to Instrumentation Valving Error</strong><br /><i>Abstract:&nbsp;</i>At 0149 hours on May 27, 1993, with Unit 2 in Refuel, the Instrument Maintenance Department (IMD) was completing Dresden Instrument Surveillance (DIS) 1500-01, Reactor Low Pressure (350 psig) ECCS Permissive (returning Pressure Switch 2-26352A to service), when an inadvertent Reactor Scram, Group 2, and Group 3 occurred. All control rods were fully inserted before the Scram signal was received (no rod motion occurred. All Group 2 and Group 3 isolation valves functioned properly and Standby Gas Treatment started as expected. Reactor Water Cleanup System was restarted at 0153 and Shutdown Cooling was restarted at 0155. Reactor Building Ventilation was started and Standby Gas Treatment secured at 0207. There was no change in Reactor Coolant Temperature while Shutdown Cooling was isolated. PS 2263-52A has a common sensing line with LT 2-263-57A and LT 2-263-57B, which are the level transmitters for Reactor Vessel Level Scram. Due to a valving error while returning PS 2-263-52A to service, a pressure spike was introduced into the common sensing line which activated LT 2-263-58A and LT-263-58B. Review of records indicates no adverse trend of events of this type while performing instrumentation valving.
2371993016 | Dresden 2 | 08/05/1993 | 08/27/1993 | 9309070246 | <strong>High Pressure Coolant Injection Declared Inoperable Due to Turning Gear Failure</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1993 at 1000 hours, with Unit 2 at 92% rated core thermal power, while performing Dresden Operating Surveillance (DOS) 2300-7, High Pressure Coolant Injection (HPCI) Cold Quick Initiation, the HPCI Turning Gear (TGR) failed to engage. The HPCI System Engineer observed that a pin which holds the engagement linkage together had fallen out. Without the ability to engage the TGR from the control room the HPCI system was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. A work request was written for the Electrical Maintenance Department (EMD) to reinstall the pin . The HPCI TGR was tested satisfactorily, and the seven day LCO was terminated on August 6, 1993. The Safety Significance of this event is minimal because the HPCI System was available for core injection if needed, and since all other Emergency Core Cooling Systems (ECCS) required by TS 3.5.C.2.a were operable. A previous event involving Unit 2 HPCI TGR engagement failure is documented in LER 92-024/050237.
2371993017 | Dresden 2 | 09/08/1993 | 12/21/1993 | 9401030136 | <strong>Unusual Event not Declared in July from Both Unit 2 and Unit 2/3 Diesel Generators Being Inoperable due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On four occasions during the time periods of 1625 to 2053 On 7/6/93 between 1415 to 1419 on 7/7/93, between 0523 to 0604 and between 1152 to 1200 on 7/17/93. It was not recognized that when the feed breaker from Bus 29 to Motor Cont Centers (MCC) 29-2 and 29-4 was open that both the Unit 2 and Unit 2/3 Emergency Diesel Generators (EDG) were inoperable and unusual events should have been declared per BWR Emergency Actions Levels (EALs) 3.e. The Unit 2 EDG was correctly considered inoperable due to lose of power to its cooling water pump as fed from MCC 29-2. The Unit 2/3 EDG was not considered inoperable per Dresden Operating Annunciator Procedure (DAN) DG 2/3 B (C2) (C3) because of a loss of power to its Circulating Lube Oil pumps that are ted from MCC 29-4. This was in error. The DAN that administratively declares the EDGs inoperable states the EDG may be used in an emergency. Since the 2/3 EDG could be used, Personnel in the Control Room did not declare the 2/3 EDG inoperable. The review of this event conducted by the Site Engineering Construction (SEC) group to determine if procedure revisions or plant modifications were required is now complete. Corrective action # 3 is changed.
2371993018 | Dresden 2 | 08/27/1993 | 02/09/1994 | 9402160365 | <strong>Unit 2/3 Emergency Diesel Generator Cooling Water Pump Low Flow due to Excess Back Pressure</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1993 during performance of the unit 2/3 Emergency Diesel Generator (EDG) monthly surveillance, the required minimum EDG cooling water flow of 840 gpm could not initially be achieved. The current plant conditions were such that the Unit 2B and 2C Containment Cooling Service Water (CCSW) pumps were operating at the time. Subsequently it was observed that by reducing the CCSW flow that EDG cooling water would increase (820 to 870 gpm). On August 28, 1993 upon further review of the events that had transpired concerning the Unit 2/3 EDG cooling water flow, the Shift Engineer (SE) decided to investigate what flow could be achieved with all four Unit 2 CCSW pumps operating at rated flow. The 2A & 2D CCSW pumps were started and flows of 6270 and 6496 gpm were achieved in the CCSW loops. The Unit 2/3 EDG cooling water flow decreased to 640 gpm. Upon verification of the Final Safety Analysis Report (FSAR), it was uncertain if the Unit 2/3 EDG was operable based upon a design bases of 840 gpm at 95 degrees. The unit 2/3 EDG was declared inoperable and both dresden Station Unit 2 and 3 were entered into a 7 day Limiting Condition for Operation (LCO).
2371993019 | Dresden 2 | 10/01/1993 | 10/29/1993 | 9310290042 | <strong>High Pressure Coolant Injection Declared Inoperable Due to Failed High Reactor Water Level Turbine Trip Switch</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1993 at 1130 hours, with Unit 2 at 99% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 500-3, Reactor Water Level ECCS Initiation Indicating Switch Calibration, level switch 2-263-72B contact 3/4, High Pressure Coolant Injection (HPCI) Turbine Trip, failed to operate. The HPCI System was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. The Instrument Maintenance Department (IMD) replaced the High Reactor Water Level HPCI Turbine Trip Switch. The switch was calibrated and DIS 0500-3 was performed satisfactorily. The seven day LCO was terminated on October 2, 1993. The Safety Significance of this event was minimal since all other Emergency Core Cooling Systems (ECCS) required by TS 3.5.C.2.a were operable. A previous event involving the failure of the High Reactor Water Level HPCI Turbine Trip is documented in LER 93-018/050249.
2371993020 | Dresden 2 | 09/12/1993 | 11/16/1995 | 9511210241 | <strong>Undetected Thermal Limit Violation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1993 the Fuel Design Limiting Ratio for Centerline Melt (FDLRC) thermal limit was violated during a xenon transient which resulted from an earlier load drop and subsequent recovery. The violation went unnoticed at the time and as a result appropriate actions as specified by the Technical Specifications were not taken. The violation condition existed for a period of nearly two and one half hours during the evening of September 12. The maximum value of the FDLRC thermal limit was exceeded by 0.4%. Discovery of the event did not occur until the following morning during routine review of computer output by the Nuclear Engineers. After review of events described in LER 95-005-00 (Docket Number 0500249), it was determined that the true root cause of this event was the informal control of planned reactivity changes. The previous root cause has been changed to a contributing cause: failure of the Qualified Nuclear Engineer (QNE) responsible for monitoring the unit to periodically review core conditions. New corrective actions include formalizing planned reactivity changes, briefing/ training of on-coming shift personnel and nuclear engineers on the event, reassigning the Unit QNEs' System responsibilities. No previous events were found involving failure to follow technical specification required actions after a thermal limit violation.
2371993021 | Dresden 2 | 10/01/1993 | 10/29/1993 | 9311010221 | <strong>Defective Check Valves on CCSW Pump Discharge, LPCI Pump Discharge, HPCI Auxiliary Cooling Pump Discharge Due to Improper Bonding of the Viton Seat by the Manufacturer.</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1993 at 1945 hours, an operability determination per commonwealth Edison procedure, QE-ENC-40.1 was written and distributed to the Dresden Station Manager and Operations Department. The operability determination involved the Low Pressure Coolant (LPCI) Pump Discharge check valve, the High Pressure Coolant Injection (HPCI) Auxiliary Pump Discharge check valve and the Containment Cooling Service Water (CCSW) Pump Discharge check valves. Some of these check valves are C&S Valve Co. Dual Plate check valves with Viton seats. Two failures the Viton seats of this type of check valve occurred at Dresden Station. An investigation determined that the seat failure is generic for these check valves and was due to improper seat bonding by C&S Valve Co. The safety significance was determined to be minimal for HPCI and LPCI. For CCSW, the pump discharge loop had a potential to drain undetected. However previous pump surveillance history has not shown any problems due to an improperly filled loop, and a compensatory action for CCSW to ensure a seat failure would not drain the discharge loop was installed. All defective check valves will be replace with suitable ones. The failure of these check valves is considered to be 10 CFR Part 21 reportable.
2371993022 | Dresden 2 | 12/16/1993 | 01/10/1994 | 9401260109 | <strong>Floor Drains in the RCA Have Potential Inputs Into Non- Contaminated Processing Systems Contrary to FSAR 9.1 page 9.1.0-3</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1993, at 1645 hours, with Unit 2 at 95% power and Unit 3 at 84% power, an engineering review of turbine building floor drain paths found several floor drains within the Radiation Control Area (RCA) input into non-contaminated processing systems contrary to FSAR 9.1, page 9.1.0-3. An action plan was immediately formed to identify all floor drains that had input into non- contaminated processing systems and place labels and/or signs above and around the drains to administratively control inputs. An enhanced sampling program was immediately initiated by the chemistry department. The operations department put all control switches from the 2/3 floor drain oil separator and the unit 1 oil separator to pull-to-lock (PTL). Before pumping out of either of these pits, chemistry analyzed the water to determine if any contamination existed. No contamination was found in any of the samples. Plans were formulated to pump the water if future analysis indicated activity, to lined containers thereby preventing any unmonitored releases. During the construction of the plant, several floor drains were designed to have her inputs go to non-contaminated processing systems. Routine sampling of these areas over the years saw no contamination in any of the samples.
2371993023 | Dresden 2 | 10/12/1993 | 09/01/1995 | 9509070010 | <strong>High Pressure Coolant Injection (HPCI) Declared Inoperable Due to Internal Wear of MO2-2301-3</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1993 at 1018 hours, with Unit 2 at 100% rated core thermal power, annunciator 902-3 C-11, High Pressure Coolant Injection (HPCI) Exhaust Drain Pot High Level, was received on Unit 2. The Nuclear Station Operator followed Dresden Annunciator Procedure (DAN) 902-3, C-11 in an attempt to clear the alarm. The alarm reset approximately 25 minutes after it was received. An initial walkdown could not determine a problem with the Exhaust Drain Pot. A second 902-3 C-11 annunciator was received at 1631 hours. A second walkdown revealed leakage past the MO2-2301-3, HPCI Turbine Main Steam Isolation Valve. The HPCI system was isolated and declared inoperable and a seven day Limiting Condition for Operation was entered per Technical Specification 3.5. An investigation determined that the valve was not leaking past the seat. Further actions included cycling the valve to obtain a Motor Signature and VOTES trace. A review of these traces could not identify any problems. As a future preventative measure a monitoring system was developed to take temperature every shift on the MO2-2301-3 leak-off line to identify any leakage in the future. The system was placed in a standby line up and the seven day LCO was terminated.
2371993024 | Dresden 2 | 11/23/1993 | 12/23/1993 | 9401030151 | <strong>Type B and C Primary Containment Local Leak Rate Testing Limit of 0.6L sub a Exceeded Due to Conservatively Assumed Leakage Past Drywell Equipment Drain Sump Containment Isolation Valve 2-2001-6</strong><br /><i>Abstract:&nbsp;</i>At approximately 0600, on November 23, 1993 with Unit 2 shutdown for maintenance, the Drywell Equipment Drain Sump (DWEDS) Outboard Containment Isolation Valv o 2-2001-6 was disassembled to determine the cause of an unusuall y low flow in the Drywell Equipment Drain Sump system. Upon disasse mbly, it was discovered that the valve diaphragm had become disconnec ted from the valve stem. In addition, when the diaphragm was remove d from the valve body, it was found to be damaged with a cut that pen etrated through the diaphragm creating a potential leakage path. This damage was attributed to incorrect setting of valve stroke length. Because 10 CFR 50 Appendix J does not require 'as found' Local Leak Rate Tests (LLRT) for mid- cycle maintenance, an 'as found' LLRT was not perform ed. Due to the fact that the diaphragm was badly damaged and that an as-found LLRT had not been performed, it was conservatively assumed that the valve may have failed an as-found LLRT with an undetermined amount of leakage and therefore would have exceeded Technical Specifi cation leakage limit 0.6L sub a. The safety significance of the leakage past the DWEDS Isolation valve 2-2001-6 was considered to be minimal, since the redundant DWEDS Isolation Valve 2-2001-5 leaked 0 scfh. The leaka ge out of containment, as determined on a minimum pathway basin, woul d not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded in the event of a LOCA. The final LLRT after repairs and stroke length adjustments to both DWEDS Isolation Valves yielded 0 scfh leakage.
2371993025 | Dresden 2 | 11/29/1993 | 12/27/1993 | 9402100038 | <strong>DOS 500-8, DOS 500-9, and DOS 500-10 Half Scram Surveillances Not Performed in a Timely Manner Due to Incorrect Station Tech Spec Interpretation</strong><br /><i>Abstract:&nbsp;</i>During Unit 2 Reactor Startup on November 29, 1993, Reactor Mode was changed from 'Startup' to 'Run'. Technical Specification Surveillance (DOS 500-8, Main Steam Line Isolation Valve Closure Scram Circuit Functional Test; DOS 500-9, Turbine Control Valve Fast Closure (Load Reject) Scram Circuit Functional Test; DOS 500-10, Turbine Stop Valve Closure Scram Circuit Functional Test) were not performed until the Startup came to a hold point at about 400 Mwe. This is consistent with past practice; however, on December 1, 1993, Operation's raised a question for interpretation regarding the timeliness of these surveillance's. A review indicated that the surveillance's should have been performed within the Technical Specification Limiting Condition for Operation. As a result this LER is being submitted under the requirements of 10 CFR 50.73(a)(2)(i)(B). Additional reviews have been performed on the Startup Checklist, Startup procedures and On-site review procedures and additional guidance will be added requiring Operators to review overdue surveillances against Tech Spec's and to detail the entry point into the Tech Spec LCO.
2371993026 | Dresden 2 | 10/30/1993 | 11/29/1993 | 9312070220 | <strong>Main Steam Line Isolation Valves 2-203-2A and 2-203-1D As-Found Leakage Rates Exceeded the Technical Specification Limit of 11.5 scfh</strong><br /><i>Abstract:&nbsp;</i>At approximately 2330, on October 30, 1993 with Unit 2 shutdown for maintenance, the performance of Dresden Technical Surveillance DTS 0250-01, Main Steam Isolation Valve Local Leak Rate (Dry) Test, identified the 'A' Main Steam Line Isolation Valves (MSIVs) to be leaking 31.81 scfh. Technical Specifications states that primary containment leakage rates shall be limited to 11.5 scfh for any Main Steam Isolation Valve (MSIV) at a test pressure of 25 psig. Dresden Technical Surveillance DTS 0250-03, Main Steam Isolation Valve Local Leak Rate (Wet) Test identified that the majority of the leakage (30.25 scfh) was from the Outboard MSIV 2-203-2A. This valve had been repaired during the previous Unit 2 Refueling Outage D2R13. It was determined that the other Main Steam Lines which had seat ring work during the previous refuel outage ('C' and 'D') would also be tested to identify any leakage. <br /><br /> Results of both wet and dry LLRTs showed that the Inboard MSIV 2-203-1D, which also had seat ring repairs during the D2R13 outage, leaked 135.4 scfh. The safety significance of the leakage past the 2A and 1D MSIVs was considered to be minimal, since the redundant MSIVs leaked 1.56 scfh and 3.2 scfh respectively. The leakage out of containment from MSIVs, as determined on a minimum pathway basis, would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded in the event of a LOCA. Final LLRTs after disassembly, inspection and repair of these MSIVs yielded 0.10 scfh leakage for the 'A' MSIVs and 8.8 scfh leakage for the 'D' MSIVs.
2371993030 | Dresden 2, Dresden 3 | 12/22/1993 | 01/20/1994 | 9401280035 | <strong>Station Procedure for Containment Purging Allow Venting Through the RBVS Which is Not in Accordance With the UFSAR and May Not Agree With the ODCM</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1993 with Units 2&3 operating it was determined that Dresden was outside its Design Basis due to a discrepancy between operating procedures and the UFSAR. Previously an engineering review to rebaseline the UFSAR identified an open item in which containment venting through the Reactor Building Ventilation (RBV) system during normal operation was allowed. This conflicts with UFSAR section 6.8.3.2 (rebaselined UFSAR section 6.2.5.3.1) which requires venting during normal operation to be accomplished via the Standby Gas Treatment (SBGT) system. The cause of the UFSAR discrepancy which appeared in the first UFSAR in 1982 is unknown. Venting through the RBV system is consistent with station operating procedures retrievable to 1975 and docketed correspondence to the NRC. The safety significance of this discrepancy is minimal due to procedural atmospheric sampling requirements, automatic isolation features and existing analysis which determined that the 10CFR100 limits would not be exceeded prior to isolation during a LOCA while purging. The immediate corrective action consisted of restricting containment venting operations to SBGT. It has been determined that the discrepancy described above is the result of a past update to the UFSAR which did not reflect the licensing basis.
2371993031 | Dresden 2 | 12/22/1993 | 12/01/1994 | 9412050210 | <strong>Reactor Vessel Level Instrumentation Found Outside of Technical Specification Limits Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1993 at 0945 hours, with Unit 2 at 99% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0500-03, Reactor Water Level ECCS Initiation Indicating Switch Calibration, 2-263-72C contact 5/6 was found outside of Technical Specification (TS) limits. Level Indicating Switch (LIS) 2-263-72C contact 5/6, is part of the High Pressure Coolant Injection (HPCI) and Low Pressure Coolant Injection (LPCI) Loop 1-59 inch initiation one out of two/twice logic. LIS 2-263-72C was declared inoperable. The necessary redundant switches were available during this event allowing both systems to remain operable. The contacts were readjusted and tested satisfactorily using DIS 0500-03. The Safety Significance of this event is minimal since the redundant switches that make up the one out of two twice logic were available throughout this event. A previous event involving the failure of 2-263-72B, High Reactor Water Level HPCI Turbine Trip is documented in LER 93-019/050237.
2441993001 | Ginna | 03/12/1993 | 04/12/1993 | 9304160043 | <strong>Loss of Source Range Detector Indication During Energization, Due to Faulty Detectors Causes a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1993, at 1425 EST, with the reactor subcritical during a planned shutdown, both source range detectors were found inoperable with the reactor trip breakers closed. <br /><br /> The Control Room operators immediately entered and performed the applicable actions of equipment restoration procedure ER-NIS.1 (SR Malfunction). The reactor trip breakers were opened within five (5) minutes of the event. <br /><br /> The most likely cause of the source range detector failures was center electrode degradation due to gamma corrosion of the bare tungsten center electrode (center wire). (This event is NUREG-1022 (B) cause code). <br /><br /> Corrective action was to replace the failed detectors with qualified spares. Corrective action to prevent recurrence is outlined in section V(B).
2441993002 | Ginna | 04/04/1993 | 05/04/1993 | 9305140080 | <strong>Steam Generator Tube Degradation Due To IGA/SCC, Causes Quality Assurance Manual Reportable Limits to be Reached</strong><br /><i>Abstract:&nbsp;</i>During the 1993 Annual Refueling and Maintenance Outage, subsequent to the eddy current examination performed on both the 'A'and 'B' Westinghouse Series 44 Steam Generators, 122 tubes in the 'A' steam generator and 171 tubes in the 'B' steam generator required corrective action due to tube degradation.<br /><br /> The immediate cause of the event was that the 'A' and 'B' steam generator tube degradation was in excess of the Ginna Quality Assurance Manual Reportability Limits. <br /><br /> The underlying cause of the tube degradation is a common steam generator problem of a partially rolled tube sheet crevice with recurring intergranular attack/stress corrosion cracking (IGA/SCC) and Primary Water Stress Corrosion Cracking (PWSCC) attack on steam generator tubing. (This event is NUREG-1022 (X) cause code) <br /><br /> Corrective action taken was to either sleeve or plug the affected tubes with accepted industry repair methods.
2441993003 | Ginna | 03/28/1993 | 07/09/1993 | 9307280206 | <strong>During Planned Maintenance, Failures of Safeguard Service Water System Were Discovered</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1993 at approximately 1200 EST, with the reactor in the defueled condition, the Maintenance Department, during valve improvement program maintenance, discovered that two manually operated Service Water System Valves, that were required to be open during normal operation, were failed in the closed position, and some isolation valves had excessive seat leakage. <br /><br /> No immediate operator action was necessary because the failures were identified on out of service sections of the Service Water System. <br /><br /> The cause of these events was determined to be partly due to design and partly due to the operating environment. (This event is NUREG-1022 (B) and (X) cause codes). <br /><br /> Corrective action taken was to replace the affected valves with qualified spares. Corrective actions to prevent recurrence are discussed in section (V) (B) of this report.
2441993004 | Ginna | 07/07/1993 | 08/06/1993 | 9308120083 | <strong>Feedwater Control Perturbations, Due To A Secondary Transient, Causes Steam Generator High Level Feedwater Isolations</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1993 at approximately 0915 EDST, with the reactor at approximately 97% full power, main feedwater isolations occurred on the 'B' Steam Generator (S/G). These feedwater isolations were caused by overfeeding the 'B' S/G, following a secondary side condensate and feedwater pressure transient.<br /><br /> Immediate operator action was to manually control the Feedwater Regulating Valves (FRVs) to restore the S/G water levels and stabilize the plant. <br /><br /> The immediate cause of the event was due to a secondary side condensate and feedwater pressure transient. <br /><br /> The underlying cause of the event was determined to be not isolating the 5A heater high level dump valve prior to troubleshooting. (This event is NUREG-1022 (X) Cause Code). <br /><br /> Corrective actions taken or planned are discussed in Section V of the text.
2441993005 | Ginna | 10/11/1993 | 11/10/1993 | 9311170036 | <strong>Failure to Perform Surveillance, Due to Misinterpretation of Requirements, Cause a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1993, at 1330 EDST, with the reactor at approximately 97% full power, evaluation of surveillance testing procedures determined that Technical Specification 4.6.1.e.3.(a) requirements were misinterpreted. Therefore, it was concluded that verification of load shedding capability of safeguards loads had not been adequately performed.<br /><br /> Immediate corrective action was initiated to complete testing that would verify this load shedding capability. This testing was completed within 24 hours of discovery, achieving compliance with Technical Specification 4.6.1.e.3.(a) requirements.<br /><br /> The underlying cause of the failure to perform this surveillance was a misinterpretation of Technical Specification surveillance requirements. (This event is NUREG-1220 (E) cause code.) <br /><br /> Corrective action was to perform the testing. Corrective action to preclude repetition is outlined in Section V (B).
2441993006 | Ginna | 11/10/1993 | 12/10/1993 | 9312270027 | <strong>Feedwater Transient, Due to Loss of Ability to Control Feedwater Regulating Valve, Cause a Lo Lo Steam Generator Level Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1993, at approximately 0848 EST, with the reactor at approximately 97% reactor power, the ability to control the "A" main feedwater regulating valve was lost. This resulted in steam generator level transients. At 0850 EST, the reactor tripped on Lo Lo level ( 17%) in the "A" steam generator. The Control Room operators performed the actions of procedures E-0 and ES-0-1. <br /><br /> The underlying cause was determined to be disconnection of the "A" main feedwater regulating valve positioner feedback linkage arm from the valve actuator linkage rod, due to disengagement of the connecting screw and nut. (This event is NUREG-1220 (B) cause code.)<br /><br /> Corrective action was to install a new screw and nut. Corrective action to preclude repetition is outlined in Section V (B).
2441993007 | Ginna | 11/22/1993 | 12/22/1993 | 9401110017 | <strong>High Source Range Flux Level During Reactor Startup Caused a Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>The plant was at hot shutdown condition, with a reactor startup in progress. At 0644 EST the reactor tripped on High Source Range Flux Level (>/= lE5 counts per second).<br /><br /> The underlying cause was determined to be a Control Room operator no t adequately focused on approaching the reactor trip setpoint. With two status lights burned out and a misleading PPCS alarm message, the operato r was focused on Permissive P-6 setpoint instead of the reactor trip setp oint. (This event is NUREG -1220 (A) cause code.) <br /><br /> Corrective actions were to replace the status lights, correct the PPCS alarm message, and apprise t he Control Room operators of the need to focus on reactor trip setpoints. Corrective action to preclude repetition is outlined in Section V (B).
2451993001 | Millstone 1 | 01/08/1993 | 05/04/1995 | 9505120213 | <strong>Snubber Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1993, while at 100% power, completion of an engineering evaluation determined that previous snubber failure of HSS-018, 'B' Safety Relief Valve (SRV) discharge line, resulted in failure to meet Technical Specification Limiting Condition for Operation Section 3.6.1.4. <br /><br /> During the 1991 refuel outage, hydraulic snubber HSS-018 was scheduled for rebuild/replacement per Millstone Unit 1 Seal Life Program. Snubber HSS-018 was removed for functional test and replacement on April 24, 1991. which was functionally tested to a generic acceptance criterion prior to the outage. The snubber removed from HSS-01 8 location failed the functional test. <br /><br /> During an extended unplanned cold shutdown outage in January 1992, hydraulic snubber HSS -018 was retested because of its functional failure in the previous outage. The snubber failed the retest. It was determined that following the failure in the 1991 refuel outage, the spare snubber that was installed did not have the correct lockup and bleed rate settings for the specific location. The plant started up following the 1991 refuel outage on August 14,1991 with this snubber installed, and operated until October 1, 1991. Plant operation with an inoperable snubber during this time frame resulted in failure to meet Technical Specification 3.6.1.4. <br /><br /> The snubber settings were reset, functionally tested satisfactorily, and reinstalled prior to plant startup in March 1992. The maintenance procedures utilized for the removal, functional testing, rebuild, and reinstallation have been revised to ensure that there will not be a recurrence of this condition.
2451993002 | Millstone 1 | 03/14/1993 | 08/15/1996 | 9608270175 | <strong>Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1993 at 1330 hours with the plant at 100% power (532 degrees F, and 1032 (PSIG)), Millstone Unit 1 declared Secondary Containment Inoperable and commenced an orderly shutdown. While investigating the lack of negative pressure in the Reactor Building, one of the seven, 3' x 6' Reactor Building Roof Relief Ventilators (sometimes referred to as blowout panels) was found open. The opening of the 18 SQ. FT. penetration resulted in a significant decrease in Reactor Building negative pressure and an assumed loss of Secondary Containment. Engineering and Maintenance personnel inspected the roof relief ventilators seating surface and restored the ventilator to its closed position.<br /><br /> No safety systems were required to function as a result of this event.
2451993003 | Millstone 1 | 04/26/1993 | 05/26/1993 | 9306030268 | <strong>LLRT Failure</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1993, at 1415 hours with the plant at 100% power, it was identified during the performance of Local Leak Rate Test (LLRT) on primary containment penetration X-25/202D (Atmospheric Control system valves 1-AC-7 through 1-AC-12) that this penetration exceeded the maximum allowable leakage rate for single penetration as specified by Technical Specification 4.7.A.3.e. <br /><br /> This LLRT was performed as part of the Northeast Nuclear Energy Company, Millstone Unit One, Corrective Action Plan (CAP) submitted to the NRC by letter dated November 4, 1992. This also fulfills a Northeast Nuclear Energy Company, Millstone Unit One commitment to a 10CFR50, Appendix J exemption granted by the Nuclear Regulatory Commission. <br /><br /> The valves responsible for this penetration failing to meet the local leak rate test requirements were repaired and satisfactorily retested.
2451993004 | Millstone 1 | 04/30/1993 | 05/28/1993 | 9306040326 | <strong>Improperly Restrained Main Steam Venturi Instrument Lines</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1993 at 1030 hours with the plant in Cold Shutdown, (175 Degrees F and 0 PSIG), the 1' instrument lines from the Main Steam line flow venturis were found to be missing pipe restraints in several locations. The improperly restrained instrument lines associated with the 'A' and 'B' Main Steam line flow venturis made contact in several locations. External wear resulting from the pipe to pipe contact was identified. <br /><br /> An evaluation of the piping in its as-found condition determined that excessive piping stresses would have resulted in a potential failure of the instrument lines following a postulated seismic event. NDE thickness measurements and calculations were also performed to assess the structural integrity of the piping system at the locations of external pipe wear. These calculations were performed assuming that the missing pipe restraints were restored. The calculations demonstrated that the piping stress levels were within the code allowable tolerances. The missing pipe restraints were reinstalled. <br /><br /> No safety systems were required to function as a result of this event.
2451993005 | Millstone 1 | 04/29/1993 | 07/19/1994 | 9407260317 | <strong>Hydraulic Snubber HSS-039</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1993, with the plant in Cold Shutdown, Hydraulic snubber HSS-039 was identified with an unacceptable end attachment to the 'A' recirculation pump motor. The snubber is attached to the motor with a clevis and load pin. One of the two (2) cotter pins which holds the load pin in the clevis attachment was missing which allowed the load pin to shift and come out of one of the ears of the clevis. This condition was conservatively determined to make the snubber unavailable to perform its intended function, thus inoperable. <br /><br /> In addition to the above condition, there was evidence of fluid leakage and an unacceptable fluid level. This snubber was removed for functional testing and replaced with a spare snubber. <br /><br /> All other snubbers were inspected for the above conditions and corrected (if required) prior to startup. <br /><br /> The maintenance procedure utilized for the removal and installation of snubbers has been revised to ensure that there will not be a recurrence of condition found with respect to cotter pins.<br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2451993006 | Millstone 1 | 06/04/1993 | 08/10/1993 | 9308180123 | <strong>Technical Specification Fire Penetration</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1993, at 1450 hours, with the plant at 100% power (530 degrees Fahrenheit and 1030 psig), while performing the 18 month fire barrier penetration inspection, an unsealed fire barrier penetration was discovered in a Technical Specification fire wall. This penetration is located in a wall between the auxiliary boiler room (fire area T-6) and the maintenance shop (fire area T-7). On June 19, 1993, at 1300 hours, with the plant at 100% power (532 degrees Fahrenheit and 1031 psig), while continuing to perform the 18 month fire barrier penetration inspection, an unsealed fire barrier penetration was discovered in a Technical Specification fire wall. This penetration is located in a wall between the 'B' station battery room (fire area T-19) and the diesel day tank room (fire area T-20). These barriers are Technical Specification fire barriers in accordance with the requirements of 10CFR50 Appendix A, and reduce the potential exposure to safety-related components created by the hazards on one side of the barrier. Fire detection and/or suppression systems governed by Technical Specifications, are installed, and were operable, in each fire area. These fire areas are located in the same Appendix R fire area (F-3A), therefore, a postulated fire with an unsealed penetration would not adversely affect Appendix R safe shutdown scenarios. The available fire protection features provided in these areas minimize any potential adverse impact on safety related equipment and safe shutdown capability. Immediate actions were taken to compensate for the unsealed penetrations, and the penetrations were properly sealed with an approved penetration seal design to meet the requirements of the affected barrier.
2451993007 | Millstone 1 | 06/23/1993 | 12/08/1993 | 9312150136 | <strong>Turbine Building Secondary Closed Cooling Water (TBSCCW) System Pressure Boundary Integrity</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1993 at 1705 hours with the plant at 100% power (530 degrees F, and 1030 psig), it was determined that a 3/4' branch line in the Turbine Building Secondary Closed Cooling Water (TBSCCW) System was non- QA and non-seismic downstream of its normally open isolation valve. As a result, failure of the pressure boundary integrity of this downstream piping during a seismic event coupled with a loss of normal system make- up capability, could have resulted in a loss of the TBSCCW system. The TBSCCW system provides cooling to the diesel generator room coolers, and also to the Condensate, Condensate Booster, and Reactor Feed Pumps, (equipment composing the safety-related Feedwater Coolant Injection (FWCI) subsystem) as well as their associated area coolers. However, while FWCI operability is not credited for seismic event scenarios, a loss of the diesel generator room coolers would result in eventual diesel generator inoperability. <br /><br /> The 3/4' normally open isolation valve was closed to isolate and provide an acceptable boundary between the non-safety-related portion of the branch line and the safety-related portion of the TBSCCW system. There were no safety consequences, and no safety systems were required to operate as a result of this event.
2451993009 | Millstone 1 | 07/06/1993 | 08/05/1993 | 9308130062 | <strong>Failure of 1-LP-9B to open</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1993, at 1005 hours, with the plant operating at 100% power (530 degrees F and 1030 psig), during performance of a routine surveillance test of the plant's Containment Isolation Valves, the outboard Low Pressure Coolant Injection (LPCI) to Recirculation Loop Valve 1-LP-9B failed to open electrically after being manually closed. During the performance of the surveillance, the motor operator's declutch fork jammed the motor clutch in mid-position, precluding manual or electrical operation of the valve. This resulted in the inoperability of the LPCI system.<br /><br /> Repairs were initiated and the declutch fork and clutch were repositioned to permit both manual and electrical operation of the motor operator. At 1415 hours repairs were completed and the valve was opened electrically. The LPCI system was then returned to service. <br /><br /> All other safety systems were operable at the time of the event and there were no consequences.
2451993010 | Millstone 1 | 09/17/1993 | 05/25/1994 | 9406010043 | <strong>Generator Load Reject Analysis Inconsistencies</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1993, at 1400 hours with the plant operating at 100% power (531 degrees F, 1031 PSIG) it was discovered that the analysis performed for the generator load rejection scenario contained design assumptions which are not appropriate for Millstone Unit 1. Specifically, the analysis assumes an automatic reactor recirculation pump runback to 70% on a generator load rejection event with select rod insert functioning. Millstone Unit 1 does not have the automatic reactor recirculation pump runback circuitry in place, and therefore, no automatic reactor recirculation pump runback would occur. <br /><br /> General Electric has completed analysis based on the 'as built' configuration of Millstone Unit 1 for the Generator Load Rejection. The results of the reanalysis have confirmed that the Generator Load Rejection with Turbine Bypass Valve Failure remains the limiting transient. <br /><br /> The discrepancies between analytical assumptions and plant design features do not impact the analysis of the limiting transient and do not adversely affect the operability of any safety system. No safety systems were required to function as a result of this event and no safety consequences resulted from this event.
2451993011 | Millstone 1 | 09/17/1993 | 07/15/1996 | 9608010148 | <strong>Spent Fuel Pool Cooling Capability</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1993, with the plant at 100 percent power (1030 psig, 530 degrees Fahrenheit), it was determined through engineering analysis that during prior refueling outages the spent fuel pool cooling system, by itself, would have been incapable of maintaining pool temperature below the 150 degree Fahrenheit design limit, under certain conditions. The conditions in question involve the transfer of a full reactor core into the spent fuel pool. In an analysis assuming a full core offload beginning 150 hours after reactor shutdown, and assuming maximum ultimate heat sink temperature (75 degrees Fahrenheit) and a single active equipment failure of the 'A' train of Shutdown Cooling System, with no compensatory actions to restore adequate cooling capability, it was determined that the spent fuel pool temperature would exceed the acceptance limit. <br /><br /> NNECO's typical practice during refueling outages has been to perform full core offloads. Additionally, a review of data from previous refueling outages revealed that on nine occasions, a reactor core offload commenced sooner than 1 50 hours after reactor shutdown. <br /><br /> Refinement of supporting analyses was completed and appropriate schedular and procedural controls were implemented during RFO14 <br /><br /> There were no safety consequences as a result of this event and no safety systems were required to operate as a result of this event.
2451993012 | Millstone 1 | 09/17/1993 | 10/18/1993 | 9310280062 | <strong>FWCI Area Coolers Power Supply Qualifications</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1993, at 2033 hours, with the plant at 100% power (530 degrees Fahrenheit, 1030 psia), the results of a reportability evaluation determined that a reportable condition existed. Components required to support the safety related function of the Feedwater Coolant Injection (FWCI) System were found not to be Category 1 or seismically qualified. An operability determination was performed which determined that the FWCI System was operable, since reasonable assurance was obtained that the equipment would function for those safe shutdown and accident scenarios for which the FWCI System must be available. No safety consequences resulted from the event.
2451993014 | Millstone 1 | 09/23/1993 | 10/25/1993 | 9311040203 | <strong>Potential Uninhabitability of the Control Room</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1993, at 1715 hours with the plant operating at 100% power (530 degrees Fahrenheit, 1030 PSIG), it was determined a previously discovered opening in the Standby Gas Treatment (SGT) Trains could potentially release radioactivity that would result in radiation levels in the control room greater than that established by the Millstone Unit 1 Updated Final Safety Analysis Report. Specifically, in the event of a postulated design basis loss of coolant accident with SGT operation, a 1/2 inch diameter opening downstream of the SGT fan could discharge radioactivity into an area that communicates with the control room. This condition could have rendered the control room uninhabitable. <br /><br /> The openings were plugged to preclude a potential discharge of radioactivity. No additional openings were found. <br /><br /> No safety systems were required to function as a result of this finding.
2451993015 | Millstone 1 | 10/12/1993 | 11/12/1993 | 9311190447 | <strong>Fire Watch Found Inattentive</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1993, at approximately 1030 hours, with the plant at 100% power (530 degrees Fahrenheit and 1030 psig), a Plant Equipment Operator (PEO) discovered that a fire watch was inattentive. Attempts by the PEO to rouse the fire watch were unsuccessful. The Medical Department was contacted and immediately dispatched personnel to the scene. The Emergency Medical Technicians (EMTs) responding to the scene were able to revive the fire watch. Immediate actions were taken to replace the continuous fire watch. This event has been attributed to a medical condition. <br /><br /> Subsequent investigation has shown that the fire watch, posted due to degraded ceiling fire proofing material, had called the dispatch desk at 1015, as required by the fire watch contractor's policy. The policy requires each continuous fire watch to call the dispatch desk every fifteen (15) minutes. The PEO entered the area and discovered the inattentive fire watch at 1025. The fire watch has stated that he heard some one enter the area, and his next recollection is that he was being revived by the EMTs. Therefore, the potential existed for a violation of continuous fire watch requirements for a very short period of time. The available fire protection system in this area was operable during this event, minimizing any potential impact on safety related equipment and safe shutdown capability.
2451993018 | Millstone 1 | 10/05/1993 | 11/05/1993 | 9311160312 | <strong>Spurious Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1993, at 0859, while operating at 100% power, a spurious reactor scram occurred. The scram event was not preceded by any warning or annunciation. Operators performed actions specified in appropriate procedures and stabilized the plant. As a result of the scram, reactor vessel water level decreased to the Group II isolation setpoint, and as expected initiated the Standby Gas Treatment (SGT) System. Other than the Reactor Protection System (RPS) and SGT, no other safety systems were called upon during this event.<br /><br /> The scram cause is unknown and it has been determined to be spurious. Because the cause was unknown, all surveillances related to the RPS were performed as specified in the Scram Recovery procedure. The surveillance results indicated that the RPS is fully functional and operated according to its intended design.
2451993019 | Millstone 1 | 11/11/1993 | 12/13/1993 | 9312270052 | <strong>Standby Gas Treatment (SBGT) Surveillance Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1993 at 1345 hours with the plant operating at 100% power, it was determined that the requirements of Technical Specification (Tech. Spec.) 4.7-B-3.c were not being met due to inadequate surveillance testing. Specifically, Tech. Spec. Surveillance Requirement 4.7.B.3.c states that 'when one circuit of the standby gas treatment system becomes inop erable, the other circuit shall be demonstrated to be operable immed iately and daily thereafter.' The applicable surveillance procedure used to fulfill these requirements was determined to be insufficient to definiti vely verify the operability of all active components in the Standby Gas Treatment (SBGT) system at the specified frequency required by this Tech. Spec. <br /><br /> Additional surveillances have and will be performed to verify SBGT train operability. No safety consequences resulted from this event.
2451993020 | Millstone 1 | 10/21/1993 | 11/22/1993 | 9312060033 | <strong>Emergency Diesel Generator Historical Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1993, at 1330, while at 100% power (530 degrees F 1030 psi) the reportability of a historical emergency diesel generator inoperability was determined. The emergency diesel generator (EDG) was inoperable from May 22, 1986, to July 22,1986, due to one of the non-redundant room coolers being out of service. During this time the emergency gas turbine generator (GTG) was also inoperable for short periods of time for preventive maintenance. Both emergency power supplies being inoperable concurrently is considered a condition that could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident.
2451993021 | Millstone 1 | 10/29/1993 | 11/29/1993 | 9312080117 | <strong>Service Water Leak</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1993 at 2245 with the plant operating at 100% power, a plant equipment operator identified water seeping up through cracks in the floor slab adjacent to the 24' Service Water discharge header located in the Turbine Building. The leakage was determined to be the result of a through wall defect in the Service Water piping within the floor slab. The location of the defect within the floor slab prevented characterization of the flaw utilizing NDE thickness measurements (See figure for details). In the absence of thickness measurements a severance of the 24' pipe at the floor slab was assumed and a piping stress analysis was conducted. The results of this analysis determined that the resulting stresses in the 24' piping exceeded the design allowables, but remained within Generic Letter 91 -18, 'Information to Licensees Regarding Inspection Manual on Resolution of Degraded and Non Conforming Conditions and on Operability,' operability criteria for piping stresses. The root cause of this event has been determined to be erosion/corrosion of carbon steel piping. The degraded piping will be replaced during the upcoming refueling outage scheduled to begin on January 15, 1994. <br /><br /> No safety systems were required to function as a result of this event.
2451993022 | Millstone 1 | 11/22/1993 | 12/22/1993 | 9401110231 | <strong>Condensate Booster Pump Lube Oil System Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1993 With the plant operating at 100% power, it was determined that the bearing lubrication system for the 'A' and 'B' Condensate Booster Pumps may be inadequate to ensure proper bearing lubrication during certain accident scenarios. Specifically,it has been postulated that given a failure of the non-safety-related forced bearing lubrication system, the safety-related back-up slinger-type bearing lubrication system may be insufficient to ensure proper bearing lubrication and continued Booster Pump operability following a pump start. This may result in the inability of the Condensate Booster Pumps to perform their intended safety-related function as part of the Feedwater Coolant Injection (FWCI) system. <br /><br /> Procedures are currently in place to ensure booster pump cold-starts are not performed without the forced lubrication system in service. Bearing failures are not expected to occur after a Booster Pump is restarted following a Loss of Normal Power (LNP) scenario due to the short time period the forced lube oil system would be unavailable. However, the forced lube oil system is being upgraded to Safety Class Category 1. No safety consequences resulted from this event.
2451993023 | Millstone 1 | 10/15/1993 | 12/10/1993 | 9312270041 | <strong>Degradation of Service Water Piping RBCCW Heat Exchange</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1993 at 1400 hours, with the plant operating at 100% power, a plant equipment operator identified leakage coming from what appeared to be a s mall defect in the Service Water discharge piping from the 'A' Reacto r Building Closed Cooling Water (RBCCW) heat exchanger. Thickness measurements and radiography revealed degradation on the 'A7 and 'B' RBCCW heat e xchanger discharge piping. Based on the extent of the degradation, t he discharge piping from the 'A7 and 'B ' RBCCW heat exchangers was assumed to fail under design loading conditions. The plant was brought to cold shutdown and the 'A7 and 'B' RBCCW heat exchanger discharge piping w as replaced. <br /><br /> No safety systems were required to function as a resul t of this event.
2451993025 | Millstone 1 | 12/03/1993 | 01/03/1994 | 9401120293 | <strong>Reactor Water Clean-up Valves (1-CU-2 and 1-CU-3) Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1993 at 1730 hours with the plant operating at 100% power (5300 F and 1030 PS IG) Reactor Clean- up Valves 1-CU-2 and1-CU-3 were declared inoperable and the valves were placed in their isolated condition. <br /><br /> This conclusion was reached when valve factors derived for valves 1 -CU-2 and 1 -CU-3 were found to meet original design requirements, however EPRI data suggested that a higher valve factor (>O.4) is more appropriate to ensure operability. The existing valve factors did not provide sufficient thrust margin to provide reasonable assurance the valves would perform their intended safety function to isolate postulated line breaks outside containment. <br /><br /> On December 5, 1993, the torque switches were electrically bypassed from 100% open to approximately 5% open. This will ensure that sufficient margin (an a ppropriate valve factor of >0.4) will exist through the period when the required closure thrust is a maximum, and the design functions of the valve to close is met. <br /><br /> No safety system actuations were required and no safety consequences resulted from this event.
2471993001 | Indian Point 2 | 02/07/1993 | 03/07/1995 | ML10043090 | <strong>Tears in Refueling Cavity Liner</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1993, at approximately 1630 hours, with the unit in cold shutdown and in its ninth day of a refueling outage, a tear in the west wall of the refueling cavity stainless steel liner was observed by outage support personnel. Upon further inspection, additional smaller tears were noted in the vicinity of the larger observed defect. Subsequent visual inspections of the Refueling cavity liner on February 15 and 20, 1993, identified additional defects in the liner. On February 5, 1995, with the unit in Cold Shutdown and in its second day of a refueling outage, 28 additional small tears were noted by plant personnel during a followup inspection of the liner as previously committed. The conditions detected in 1993 were rectified during the 1993 refueling outage by different methods that included welding of stainless steel plates and application of a high strength polymer over the affected areas. The tears detected during the 1995 refueling outage were immediately rectified with the application of the same high strength polymer over the affected areas as a permanent repair. The root cause of all the defects observed was determined to be transgranular stress corrosion cracking (TGSCC) caused by exposure of the stainless steel liner to an aqueous environment containing chlorides. <br /><br /> No NRC limit was exceeded and there was no impact on public health and safety.
2471993002 | Indian Point 2 | 02/08/1993 | 03/10/1993 | ML10043085 | <strong>Auto-Start of Emergency Diesels</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1993, during a cold shutdown refueling outage, the three emergency diesel generators automatically started. de-energized a 6.9 kV bus and the 480V bus which it was supplying. The diesels received an undervoltage signal from the 480V bus which initiated the start. All offsite power remained available, and all Engineered Safety Features performed as expected. A perturbation on the DC circuit associated with the bus lockout relay due to an inadvertent bumping of the breaker cubicle door handle is the most probable cause for initiating the bus lockout signal.
2471993003 | Indian Point 2 | 02/15/1993 | 03/17/1993 | ML10043086 | <strong>Isolation Valve Seal Water System Leakage Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>Surveillance tests of valves categorized by Appendix J as types 'B' and 'C' were performed during the current refueling outage. When individual valve leakage amounts were totaled, it was determined that the 14,700 cubic centimeters per hour leakage permitted by the Technical Specification for the Isolation Valve Seal Water System was exceeded. Excessive leakage occurred across five containment isolation valves. The valves have been repaired and testing will be performed prior to plant startup to ensure leakage is within acceptable limits.
2471993004 | Indian Point 2 | 03/04/1993 | 04/05/1993 | ML10043086 | <strong>Emergency Disel Generator Auto-Start</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1993, during a refueling outage with the reactor at cold shutdown and all fuel discharged from the core, two emergency diesel generators automatically started. following preventive maintenance, the bus tie breaker tripped and de-energized the 480V bus. The two diesels received an undervoltage signal from the 480V bus, which initiated the start. The third diesel did not auto start because it was tagged out for maintenance. All offsite power remained available during the event. Failure of a trip bale wire in the 480V bus supply breaker to properly reset was the cause of initiating a trip signal to the tie breaker.
2471993005 | Indian Point 2 | 03/05/1993 | 04/05/1993 | ML10043086 | <strong>Cable Spreading Room and Electrical Tunnel Ventilation Single Failure Determination</strong><br /><i>Abstract:&nbsp;</i>As a result of the design of 480 Volt (V) Switchgear Room ventilation which was previously reported in LER No. 91-20, engineering reviews of interfacing system effects on other ventilation systems were initiated. <br /><br /> In a follow-up engineering evaluation of a previously discovered and temporarily corrected interaction between the Cable Spreading Room (CSR) Halon fire protection system and the electrical tunnel exhaust fans ventilation system, an additional condition was found which potentially affected CSR / electrical tunnel ventilation system fan operability under certain conditions. Specifically, the tunnel exhaust fans, which are required to be operable whenever the reactor is critical pursuant to the Indian Point Unit 2 Technical Specification 3.3.I are interlocked with the tunnel fire protection deluge system. It was determined that a fault in a single deluge pre-action relay could lead to an undetected failure of both fans, which in turn could result in exceeding the maximum manufacturers' recommended temperature for operability of safety-related equipment in the CSR and electrical tunnel.
2471993006 | Indian Point 2 | 03/24/1993 | 04/23/1993 | ML10043086 | <strong>Emergency Diesel Generator Auto Start</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1993, during a refueling outage with the reactor at cold shutdown, two emergency diesel generators automatically started. While removing a 480V bus from service for maintenance, the blackout undervoltage relays associated with the bus initiated an undervoltage signal which resulted in the start of the two diesels. The third diesel did not automatically start because it was tagged out for maintenance. All offsite power remained available during the event. A personnel error resulted in an incomplete disablement of all the undervoltage relays associated with the 480V bus prior to a planned evolution. When the 480V bus was subsequently de-energized, an undervoltage signal resulted in the start of the two diesels.
2471993007 | Indian Point 2 | 10/10/1991 | 05/17/1993 | ML10043086 | <strong>Emergency Diesel Generator Automatic Transfer Switches</strong><br /><i>Abstract:&nbsp;</i>During the licensee's Electrical Distribution System Functional Inspection performed in October, 1991, the NRC inspection team observed that DC control power to each Emergency Diesel Generator was supplied through an automatic transfer switch. At that time each diesel had a primary and backup DC source of control power. If the primary DC source was lost, the automatic transfer switch transferred control power to the backup source in approximately two seconds. Since two diesels had the same battery for the primary DC source, there was a concern that two diesels might be affected by a single loss of DC event. At that time, it was determined that the momentary interruption of DC control power to the diesels may de-energize relays which would short the field, disable the field flashing circuit and trip the diesel output breaker. In response to this potential concern a temporary modification disabling the automatic feature of the transfer switches and placing each diesel on a separate DC control power source (separate batteries) was implemented in October, 1991. During the 1993 refueling outage a permanent modification restored the automatic feature of the transfer switches and modified the field flashing circuitry for each diesel. This modification removed the potential that the momentary interruption of DC control power could short the field. The unitization of the DC control power sources so that no two diesels share the same primary DC source of control power was included in this modification.
2471993008 | Indian Point 2 | 02/05/1993 | 08/09/1993 | ML10043087 | <strong>Fan Cooler Unit Damper Test</strong><br /><i>Abstract:&nbsp;</i>During the performance of the Safety Injection System Test in the course of the 1993 Refueling Outage, the normal outlet damper for Fan Cooler Unit 21 did not go to its incident position when Safety Injection Train B was tested. valves associated with the damper were connected to Train A. The design drawings provided for one solenoid to be connected to Train A and the other to Train B so that either train could actuate the damper. This wiring error was corrected during the refueling outage. <br /><br /> An investigation was conducted to determine when the wiring error occurred. The damper had been properly actuated during previous testing, however it could not be determined whether the wiring error occurred before or after previous successful tests. For the first time, this test was performed with instrument air maintained available. It was concluded that the damper could have operated successfully during previous tests because the safety injection signal stripped the power supply to the solenoid causing it to de-energize with the damper going to its 'fail-safe' position. Re-energization of the solenoid after resetting the power supply may not have been detected during the previous tests because the damper remained in its 'fail-safe' position due to lack of sufficient instrument air pressure after containment isolation of the instrument air line. Thus, the normal loss of instrument air during previous performances of the test served to mask the failure that has now been discovered.
2471993009 | Indian Point 2 | 08/10/1993 | 09/09/1993 | ML10043087 | <strong>Entry Into Technical Specification 3.0.1</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, August 10, 1993, two separate occurrences of entry into Technical Specification 3.0.1 and initiation of plant shutdown took place. <br /><br /> The first occurrence took place with Indian Point 2 operating at full power. service for scheduled Preventative Maintenance (PM). Service Water Pump (SWP) No. 22 on the non-essential header was inoperable (later determined to be caused by a failed pump shaft coupling). At 0740 hours, SWP No. 21 was declared inoperable due to a low flow/pressure condition (later determined to be caused by a failed pump shaft coupling). The simultaneous inoperability of SWP No. 21 and EDG No. 22 created a condition that was not in accordance with Technical Specification 3.7.B.1, which in turn caused entry into the Limiting Condition for Operation (LCO) requirements of Technical Specification 3.0.1, which called for the plant to be placed in hot shutdown within 7 hours. At 1430 hours, No. 22 EDG was returned from PM, tested successfully, and declared operable, allowing exit from Technical Specification 3.0.1. <br /><br /> The second occurrence was at 1525 hours when one of two DC control power fuses for EDG No. 22 blew. This caused EDG No. 22 to again be declared inoperable and recreated the TS 3.0.1 condition. The fuses were replaced, the EDG retested successfully, and declared operable again at 2130 hours. The health and safety of the public were not affected by this event.
2471993010 | Indian Point 2 | 08/18/1993 | 09/17/1993 | ML10043087 | <strong>Unavailable Nitrogen Backup Flow for the Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1993, it was determined by an engineering analysis that regulating valves PCV-1276 and PRV-5954, which are installed in the nitrogen backup to the Instrument Air System for the Main Steam Power Operated Relief Valves and the Auxiliary Feedwater System (AFWS), were not fully capable of performing their function in the manner set forth in the Final Safety Analysis Report (FSAR). <br /><br /> Specifically, the nitrogen backup regulator is described in the FSAR as capable of automatically supplying nitrogen in the event of loss of instrument air. The nitrogen regulating valves were designed and installed with an unrequired equalizing line between the upper spring chamber vent and the downstream air line. This equalizing line was found to compromise the ability of the nitrogen regulating valves to automatically modulate (or regulate) the nitrogen pressure and flow. The nitrogen regulating valves would therefore only pass nitrogen to the extent that it leaked past the valve seat or the valve was preset to a given opening. The nitrogen regulating valves could still have been operated manually. The valves are manufactured by CASHCO, model HP 1-32-45-S36 0.5 in. <br /><br /> Immediate corrective action was not required since a jumper (including separate regulating valves) had been installed on August 12, 1993 to bypass these regulating valves and maintain the nitrogen backup in service while investigation and repair of unrelated system leakage was in progress. This er maintains the backup function as described in the FSAR.
2471993011 | Indian Point 2 | 01/30/1993 | 09/29/1993 | ML10043087 | <strong>Auxiliary Feedwater Pump Failed to Deliver Minimum Required Flow</strong><br /><i>Abstract:&nbsp;</i>While performing test PT-R7A on January 30, 1993, with the plant in the Hot Shutdown Mode and proceeding to Cold Shutdown for refueling, the AFWP23 discharge flow control valve FCV-406D failed to automatically deliver the required minimum flow of 190 gpm within 15 seconds to Steam Generator #24 (SG24 actual flow was 170 gpm). Immediate action was to declare AFWP23 discharge flow control valve FCV-406D inoperable and enter a 72 hour Limiting Condition of Operation (LCO), in accordance with Technical Specification 3.4.B.1, until the Reactor Coolant System Temperature was below 350 degrees F. A subsequent evaluation indicated that current safety analyses were still satisfied with the slightly reduced flow.<br /><br /> Flow control valves FCV-406A and FCV-406B from AFWP21 to SG21 and SG22 respectively and FCV-406C from AFWP23 to SG23 all tested satisfactorily. <br /><br /> This voluntary LER is being submitted because of potential interest in this type of event.
2471993012 | Indian Point 2 | 09/10/1993 | 10/12/1993 | ML10043088 | <strong>Weld Channel and Penetration Pressurization System Nitrogen Backup Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1993, during a review resulting from a previously identified and reported condition associated with nitrogen backup pressure control valves for the Auxiliary Feedwater System, a condition was identified which could have rendered the Weld Channel and Penetration Pressurization System (WCPPS) air receiver and nitrogen backup system inoperable in the event of loss of the normal and backup air supply systems. Since these features are an integral part of the design of the WCPPS system, the WCPPS was declared inoperable, resulting in the entry of the plant into Technical Specification 3.0.1 at 1715 hours on September 10, 1993. Based on 10 CFR Part 100, the condition was determined to have minimal safety significance. Shortly thereafter, the NRC was contacted verbally with a request for enforcement discretion to allow continued operation for up to twenty-four hours. This request was subsequently granted verbally the same day.
2471993013 | Indian Point 2 | 09/22/1993 | 10/22/1993 | ML10043088 | <strong>Missed Source Checks for Process Radiation Monitor R-50</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1993, while the plant was at 100% power, plant personnel discovered that the monthly source check of the gas decay tank process radiation monitor (R-50) had not been performed the prior two months. This resulted from a data entry error to the computerized test database. Upon discovery, the source check, which is required by Technical Specification Table 4.10-4, was promptly performed. The test results were satisfactory. The test database was reviewed to verify that there were no similar errors, and changes were made to the test database to prevent a similar occurrence. The health and safety of the public were not affected due to the extended interval between tests.
2471993014 | Indian Point 2 | 11/30/1993 | 12/30/1993 | 9401120243 | <strong>Chemical Spill in Emergency Diesel Generator Building</strong><br /><i>Abstract:&nbsp;</i>During the addition of a biocide (NALCO 7338 Liquid) into the 23 Emergency Diesel Generator (EDG) jacket water cooling system on November 30, 1993, a blocked chemical fill line caused a spill of a small amount (200 ml) of the chemical within the EDG building. The building was evacuated, a Notification of Unusual Event was declared, and, as precautionary measures, the Central Control Room and Primary Auxiliary Building ventilation systems were isolated from their outside air supplies. Self-contained breathing apparatus were also staged at the EDG building for use by operations personnel in the event entry into the building was required. The EDG building was subsequently ventilated and the spill cleaned up. The procedure governing biocide use in the EDG jacket water cooling system has been revised to strengthen controls on the transport of the chemical, to require verification that the fill line is clear of blockage prior to adding chemicals, and to flush the fill line after chemical addition. Procedures governing the use of the biocide in two other systems will be revised prior to the next addition of the chemical to those systems. The health and safety of the public were not affected by this event.
2491993001 | Dresden 3 | 01/13/1993 | 02/09/1993 | 9402220207 | <strong>Emergency Core Cooling Level Indicating Switch Out of Calibration Due to Instrument Drift</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993 at 0110 hours with Unit 3 at 100 percent rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 500-3, Reactor Low Low Water Level Emergency Core Cooling System (ECCS) Initiation Indicating Switch Calibration and Functional Test the Instrument Maintenance Department (IMD) found Level Indicating Switch (LIS) 3-263-72A outside the required Technical Specification range. Contacts [5-6] were found to trip at 114.9 inches of water dP which corresponds to 83.1 inches above the top of active fuel. Contacts [7-8] were also found to trip at 114.9 inches of water dP which corresponds to 83.1 inches above the top of active fuel. At 0200 hours January 13, 1993 (50 minutes following the testing of LIS 3-263-72A) the IMD found LIS 3-263-72B outside the required Tech. Spec. range. Contacts [5-6] were found to trip at 114.8 inches of water dP which corresponds to 83.3 inches above the top of active fuel. Both switches were immediately recalibrated to within acceptable range. An ENS phone call was made at 0922 hours January 13, 1993. The root cause to these switches failing to actuate at the ideal tolerances specified has been attributed to instrument drift. Unit 3 Low Pressure Coolant Injection (LPCI) would not have initiated at Specifications but would have initiated at -59.9 inches reactor level. Since the LPCI initiation would have occurred at a reactor level 0.9 inches less than the level required by Technical Specifications the safety significance of this event is minimal. Failure to make the ENS phone call within the required time period has been attributed to management deficiency.
2491993002 | Dresden 3 | 01/17/1993 | 02/05/1993 | 9302230278 | <strong>Control Valve Fast Closure Half-Scram Pressure Switches Out-of Calibration Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On Unit 3, while performing Dresden Instrument Surveillance (DIS) 5600-3, Generator Load Rejection Control Valve Fast Acting Solenoid Valve Pressure Switch Calibration, three out of four Main Turbine Control Valve (TCV) Fast Acting Solenoid Valve (FASV) Pressure Switches (PS) were found to actuate below the minimum setpoint limit per Technical Specification Table 3.1.1., Reactor Protection System Instrumentation Requirements. These pressure switches provide a Load Rejection Scram signal to the RPS circuitry upon initiation of fast closure of the TCV. This scram signal is provided in anticipation of the rapid increase in pressure and neutron flux resulting from fast closure of the TCV due to a load rejection. Previous testing has concluded that instrument drift over pressure switch settings in the range of 120 - 590 psig. has negligible significance relative to instrument response time to actuate a Reactor Protection System (RPS) trip. All three of the switches were replaced, all were calibrated, and left to trip within the required setpoint limits.
2491993004 | Dresden 3 | 01/16/1993 | 02/16/1993 | 9302190334 | <strong>Manual Reactor Scram Due to Loss of Instrument Air Through Unit 3A IA Dryer Inlet Valve AO 3-4799-1194 and Failure of SA/IA Cross-Tie Valve AO 3-4701-500 to Open Timely</strong><br /><i>Abstract:&nbsp;</i>At 1213 hours on January 16, 1993, with Unit 3 at 83% power, a Unit 3 Instrument Air [LD] Header Pressure low Alarm was received in the Control Room [IB]. At 12:15:43, a Scram Header Low Pressure Alarm A-1 was received on the Sequence of Events Recorder (SER). Instrument Air Header pressure was observed to be decreasing rapidly. At 12:15:53, the Unit 3 NSO manually scrammed the reactor in accordance with Dresden Operating Abnormal Procedure DOA 4700-01. The Unit 2 and Unit 3 RX Building Ventilation System [VA] auto isolated and the 2/3 'B' SBGT system [BH] auto started at 12:16 on a Group II Isolation. At 1219 the 2/3 'B' SBGT train tripped and the 'A' train auto started. <br /><br /> Loss of Instrument Air is attributed to mechanic al failure of the 3A Instrument Air Compressor dryer inlet valve to close during the dryer purge cycle with concurrent failure of the backup Service Air to Instrument Air Cross-tie valve to promptly open on a low instrument air pressure signal. Corrective action include replacing the SA/IA cross-tie valve air regulator and pressure relief solenoid, replacement of the dryer inlet and purge valves and solenoid operators. <br /><br /> The safety significance of this event is minimal sinc e a manual reactor scram was initiated and all safety systems performed as required. A previous un-reportable event occurred on March 10, 1990, where a dryer exhaust valve failed in an open position following valve replacement. The root cause was attributed to inadvertent reverse connection of the switching valve air supply lines.
2491993005 | Dresden 3 | 01/26/1993 | 02/25/1993 | 9303010217 | <strong>Failure of the Drywell Vent Valve 3-1601-63 Due to a Degraded O-Ring on the Two Way Versa Valve</strong><br /><i>Abstract:&nbsp;</i>At 1210 hours on January 26, 1993 with Unit 3 in the Run mode and at 99% power, the Technical Staff was notified by Operations of an air leak on the fail-safe accumulator system for Drywell Vent Valve 3-1601-63. The valve was successfully cycled and timed per Dresden Operating Surveillance (DOS) 1600-05, Unit 3 Quarterly Valve Timing; however, air was identified to be leaking out of a weep hole on the two way mechanical Versa Valve. To demonstrate operability of the fail safe accumulator system, Dresden Technical Surveillance (DTS) 1600-29, Air Operated Valve Fail-Safe And Accumulator Integrity Test, was performed. At 1633 hours, valve 3-1601-63 was opened and the instrument air supply was isolated and taken Out-Of-Service. At this time Unit 3 entered a Limiting Condition For Operation (LCO) since Technical Specification 3.7.A.6.c requires the primary containment purge system to be operable whenever the reactor is in power operation. After the instrument air supply was isolated, a fitting located downstream of the instrument air isolation valve was loosened to further simulate a loss of instrument air. Shortly after performing this step, the valve repositioned to its fail-safe position (closed). However, as a result of air leakage through the weep hole on the two way mechanical Versa Valve, the accumulator pressure dropped from 83.8 psig to 70.2 psig in the following ten minutes. Work Request 15762 was generated to replace the two way mechanical Versa Valve. A post maintenance accumulator fail-safe test was successfully performed in accordance with DTS 1600-29. The apparent cause for the leakage out of the weep hole in the two way Versa Valve was due to degradation of the O-ring seals caused by aging and fatigue of the O-ring material. The safety significance of the failed two way Versa Valve is considered minimal since the valve timed in accordance with the criteria in DOS 1600-05 and was able to reposition to its fail-safe position upon loss of the instrument air supply.
2491993006 | Dresden 3 | 03/13/1993 | 04/12/1993 | 9310060159 | <strong>Type B and C Primary Containment Local Leak Rate Testing Limit of 0.6 L sub a Exceeded Due to Leakage Past Inboard Feedwater Check Valve 3-220-58A</strong><br /><i>Abstract:&nbsp;</i>With Unit 3 in a forced maintenance outage, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the Inboard 'A' Feedwater Line Check Valve 3-220-58A and the Traversing Incore Probe (TIP) Purge Check Valve 3-4799-514 to be leaking 196.67 scfh and 45 scfh respectively. These values when added to the existing maximum pathway leakage rate for Type B and C primary containment leakage, 488.452 scfh (0.6L sub a), as listed in Technical Specification 3.7.A.2.b.(2)(a). The Inboard 'A' Feedwater Line Check Valve 3-220-58A was disassembled and an inspection of the valve internals revealed a worn hinge pin/bushing. The seat, disk and hinge pin/bushing were replaced under Work Request (WR) 16938. <br /><br /> The TIP Purge Check Valve 3-4799-514 was not inspected but the most likely cause for failure was debris on the seat. This check valve was replaced under WR 17211. The safety significance of the leakage has been considered to be minimal, since the additional leakage out of containment, on a minimum pathway basis, was 48.65 scfh and would not cause the maximum off site dose rates established in 10 CFR 100 to be exceeded. Final as-left local leak rate tests (3-220-58A = 0.1 scfh, 3-4799-514 = 1.8 scfh) were performed in accordance with DTS 1600-01 to verify the valves' seating integrity prior to placing them back into service.
2491993007 | Dresden 3 | 02/26/1993 | 03/25/1993 | 9304020293 | <strong>Reactor Scram on High Reactor Pressure Caused by Blockage of the High-Pressure Section of the Main Turbine</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1993, at 16:17 hours with Unit 3 operating at a steady thermal power of 99.4%, an automatic reactor scram occurred due to high reactor pressure. Review of plant data indicated that the high reactor pressure was caused by a flow blockage in the high pressure turbine. Disassembly revealed that foreign objects had entered in the first stage of the high-pressure turbine. One of the objects, or debris from internal damage, came in contact with the rotating assembly and caused damage which restricted steam flow. The safety systems functioned as designed during the subsequent scram recovery. Damage to the first-stage diaphragm and rotor will be repaired. The Foreign Material Exclusion (FME) program will be enhanced to prevent further events of this nature. A history search revealed there were no similar events of objects entering the turbine and causing damage at Dresden.
2491993008 | Dresden 3 | 02/25/1993 | 03/25/1993 | 9304050050 | <strong>Suppression Pool Temperature Monitoring Element Conduit Support Found Outside Design Criteria Allowables.</strong><br /><i>Abstract:&nbsp;</i>At 1730 hours on February 25, 1993, with Unit 3 at 99% power, an engineering evaluation determined that a conduit for Unit 3 Torus Temperature Element TE-3-1641-211, which was missing a support, was operable but outside design criteria allowables. Several preceding events led to the determination that the conduit was outside design allowables. An engineering walkdown was being performed on February 23, 1993 for a modification to the Suppression Pool Temperature Monitoring system. During the walkdown it was noticed that the conduit was approximately 7 inches away from the support. The two closest supports on either side of the missing support were a junction box mounted on 3 inch tube steel and the thermowell mounted to the Torus. A Problem Identification Form (PIF) was written by the Nuclear Engineering Department (NED) to document the discrepancy on February 23, 1993. On February 24, 1993, an operability determination was completed by NED which determined that the temperature element be declared operable. When it was determined that the Temperature element was outside design allowables, NED generated another PIF to document the finding and generated a work request to re-support the conduit. The safety significance of this event is minimal since the Temperature Element meets operability requirements. This event is the first occurrence where a Temperature Element conduit was found outside design allowables.
2491993009 | Dresden 3 | 05/12/1993 | 07/28/1993 | 9308090236 | <strong>Isolation Valve for Isolation Condenser Initiation Pressure Switch, PS 3-263-53C, Found Closed During Performance of Surveillance DIS 1300-1 Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>At 1920 on May 12, 1993 while performing Sustained High Reactor Pressure Calibration Surveillance (DIS 1300-1), the isolation valve for Isolation Condenser Initiation Pressure Switch (PS 3-263-53C) was found in the closed position in violation of Technical Specification Table 3.2.2 by not having two operable instrumentation channels per trip system. The station event reporting process did not identify the event as reportable to the NRC via an LER. As a result, this LER is not being reported within the 30 day reporting criteria.
2491993010 | Dresden 3 | 04/16/1993 | 05/11/1993 | 9305180403 | <strong>Standby Liquid Control System Piping Found Outside FSAR Design Limits Due to Missing U-Bolt on Support</strong><br /><i>Abstract:&nbsp;</i>At 1700 on April 16, 1993, with Unit 3 shutdown and in the refuel mode, an engineering evaluation was completed that determined the Unit 3 Standby Liquid Control System was operable but outside the Final Safety Analysis Report (FSAR) design limits due to a missing U-bolt on piping support M-1190D-268. This discrepancy was discovered by the system engineer during a quarterly system walkdown. A Problem Identification Form (PIF) was generated to document the discrepancy. The missing U-bolt was replaced prior to restart of the unit. A walkdown was performed on the Unit 2 Standby Liquid Control System and no piping support discrepancies were observed. <br /><br /> The safety significance of this event is minimal since the Standby Liquid Control System piping meets operability requirements. There have been no previous occurrences involving Standby Liquid Control System piping support discrepancies.
2491993011 | Dresden 3 | 04/21/1993 | 05/17/1993 | 9305280260 | <strong>Spurious Group V Primary Containment Isolation While Shutdown Due to Flow Spikes</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1993, at 1430 hours, with Unit 3 in the refuel mode with all control rods inserted, a spurious Group V Primary Containment isolation occurred during the MO 3-1301-3 valve Votes testing. All of the Isolation Condenser isolation valves automatically responded as required. The system was walked down following the event, and no line, break, open fuses, or electrical problems were found. Calibration checks were performed on April 20, 1993, and all setpoints were verified to be within tolerance. The Group V Primary Containment Isolation signal was reset after it was determined to be spurious. Isolation Condenser operability is not required whenever reactor pressure is less than 150 psig; also, had this event occurred under power operation, the High Pressure Coolant Injection or Automatic Depressurization Systems could have been utilized for reactor pressure control. The root cause of this event appears to be a flow spike in the Isolation Condenser condensate return line when the MO 3-1301-3 valve was manually cracked open for Votes testing. A similar event was reported by LED 93-003/050249.
2491993012 | Dresden 3 | 07/10/1993 | 08/03/1993 | 9308100184 | <strong>Spurious Group V Primary Containment Isolation While Shutdown Due to Flow Spiking</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1993, at 1531 hours, with Unit 3 in the Shutdown mode and all control rods inserted, a spurious Group V (Isolation Condenser Line Break) Primary Containment Isolation occurred. All of the Isolation Condenser isolation valves automatically responded as required. An operator was dispatched to check the area surrounding the instrument rack and no one was seen nearby. Unit 3 had experienced a reactor scram approximately 12 hours earlier and was in the process of cooling down when the Group V Isolation occurred. Reactor pressure was 0 psig and moderator temperature was approximately 198 degrees Fahrenheit at the time of the event. Control Room operators indicated that no changes in plant status were occurring at the time of the event. Since the Isolation Condenser is not required when the reactor pressure is less than 150 psig, the system was taken Out-of-Service after the event. Unit 3 has experienced eight spurious Group V Isolations since 1986. A preliminary engineering evaluation determined the root cause to be a spurious flow pike caused by operation of systems required to bring the Unit to cold shutdown and over-conservatism in the flow itch setpoints.
2491993013 | Dresden 3 | 08/09/1993 | 09/01/1993 | 9309080303 | <strong>High Pressure Coolant Injection Declared Inoperable Due to Control Valve Limit Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1993 at 1300 hours, with Unit 3 at 100% rated core thermal power, while performing Dresden Operating Surveillance (DOS) 2300-3, High Pressure Coolant Injection (HPCI) Monthly Surveillance Test , the HPCI Turbine Failed to reset following a trip test. The HPCI System was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered per Technical Specification (TS) 3.5. A work request was written for the Electrical Maintenance Department (EMD) to inspect the Turbine Trip Logic. It was determined that Limit Switch (LS) 7 , Control Valve position, was not making contact with the control valve plunger which prevented the Turbine from being reset from the control room. The EMD readjusted LS7 and the HPCI Turbine was tripped and reset satisfactorily several times. DOS 2300-3 was performed satisfactorily and the seven day LCO was terminated on August 10, 1993. The Safety Significance of this event is minimal since all other Emergency Core Cooling Systems (ECCS) required by TS 3.5.C.2.a were operable. There have been no similar events involving the inability to reset the HPCI Turbine.
2491993014 | Dresden 3 | 07/10/1993 | 08/04/1993 | 9308160120 | <strong>Reactor Scram on Main Condenser Low Vacuum Due to Indeterminate Cause</strong><br /><i>Abstract:&nbsp;</i>While in the process of performing DOP 4400-8 'Circulating Water flow Reversal', a Unit 3 Reactor Scram occurred on Main Condenser Low Vacuum at 0358 on July 10, 1993 with Unit 3 at 93% power and 996 psig pressure.
2491993015 | Dresden 3 | 08/11/1993 | 09/08/1993 | 9309160007 | <strong>A & B CCSW Pumps Only Producing 6000 Gallons Per Minute</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1993 at 0914 while performing a special procedure on the Unit 3 Containment Cooling Service Water system it was determined that the Unit 2 'A' and 'B' CCSW pumps could produce a combined flow of only 6000 gpm. Table 6.2.4.1 of the Dresden FSAR requires a CCSW Loop flow of 7000 gpm. The Station administratively entered the LCO for 1 CCSW subsystem inoperable. This LCO allows continued operation for seven days. On August 16, 1993 at 0931 the 3-1501-3B valve (the flow control valve for the 'B' loop of the Unit 3 CCSW system) was stroked to verify proper valve travel. This valve would not fully open. The Station administratively entered the LCO for 2 CCSW subsystems inoperable. This LCO requires the reactor to be in cold shutdown within 24 hours. The Station requested and was granted enforcement discretion so that Unit 3 be allowed to continue to operate until August 25, 1993, in order to allow time to procure, install and test the flow control valve component which is causing the degraded flow condition. The root cause of the degraded flow on both Unit 3 Containment Cooling loops was the original design drawing for the 3-1501-3A(B) valves states that valve has its maximum flow at a stroke of 2 inches. Consequently, the valve actuator was designed for a valve with a 2 inch maximum stroke. The safety significance of the degraded flow condition is minimal based on the containment analysis performed in December 1992 and service water inlet temperature of 77 degrees F and Suppression pool temperature of 83 degrees F, which are significantly below the analysis input values of 95 degrees F. Corrective actions included repairing the valve actuator to allow full stroke and verifying loop flows of 7000 gpm following this repair.
2491993016 | Dresden 3 | 09/29/1993 | 10/29/1993 | 9404110029 | <strong>Type B and C Test Leakage Limit of 0.6.L sub a Exceeded Due to Leaking Valve.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1600, on September 29, 1993 with Unit 3 operating at 99% power, the performance of Dresden Special Procedure SP 93-8-73, Local Leak Rate Testing of Primary Containment Isolation Valves During Reactor Operation, identified the Atmospheric Containment Atmosphere Dilution (ACAD) System [BB] Check Valve 32599-23A to be leaking an undetermined amount. This value when added to the existing maximum pathway leakage rate exceeded the maximum pathway leakage rate for Type B and C primary containment leakage, 488.452 scfh (0.6L sub a), as listed in Technical Specification 3.7.A.2.b (2) (a). The safety significance of the leakage past valve 3-2599-23A was considered to be minimal since the additional leakage out of containment, on a minimum pathway basis, was 7.93 scfh from the inboard isolation valve 3-2599-2A and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. Upon completion of maintenance, the valve was retested. This test yielded a leakage rate of 2.44 scfh. This supplement has been submitted to report the cause and corrective actions for three other valve failures which occurred during the course of the Unit 3 exemption period.
2491993017 | Dresden 3 | 11/01/1993 | 11/17/1993 | 9406080323 | <strong>High Pressure Coolant Injection Declared Inoperable Due to Broken Room Cooler Drive</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1993 at 2250 hours, with Unit 3 at 99% rated core thermal power, after successfully performing Dresden operational Surveillance (DOS) 2300-0-3, High Pressure Coolant Injection System Operability Verification, it was discovered that the HPCI room cooler drive belts had broken subsequent to the completion of DOS 2300-03. The HPCI System was declared inoperable and a seven day Limiting Condition for operation (LCO) was entered per Technical Specification (TS) 3.5. The Electrical Maintenance Department (EMD) replaced the drive belts per Nuclear Work Request (NWR) D21492 as an immediate corrective action. Dresden Electrical Procedure (DEP) 5700-04, HPCI Room Cooler Fan Preventive Maintenance was successfully completed. Additionally, long term corrective actions have been initiated to prevent recurrence. The LCO was terminated on November 3, 1993. The Safety Significance of this event is minimal since all other Emergency Core Cooling Systems (ECCS) required by TS 3.5.C.2.a were operable. A similar previous occurrence was reported by LER 89022 on docket 050237.
2491993018 | Dresden 3 | 08/16/1993 | 09/10/1993 | 9309200042 | <strong>High Pressure Coolant Injection Outside of FSAR Design Requirements Due to Disabled Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1993 at 2310 hours, with Unit 3 at 100% rated core thermal power, the High Pressure Coolant Injection (HPCI) High Reactor Water Level Trip (+48 inches) was disabled. Previously, during the performance of Dresden Instrument surveillance (DIS) 0500-03, Reactor Level Emergency Core Cooling System (ECCS) Switch Calibration, level switch (LS) 3-263-72B contacts 7-8, Reactor Low Level ECCS Initiation (-59 inches), tripped outside of Technical Specification (TS) limits. LS 3-263-72B was placed in the downscale position to provide a half channel trip condition. The placement of the switch in the downscale position disabled the HPCI High Reactor Water Level Trip. The applicable TS sections were reviewed and it was concluded that the HPCI system would remained operable. A caution card was placed on 3-2340-1, HPCI Flow Controller, to alert the Nuclear Station Operator (NSO) of the disabled trip. However, a subsequent review determined that the HPCI system was outside of Final Safety Analysis Report (FSAR) design requirements. The HPCI system was immediately declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered. The HPCI High Reactor Water Level Trip was restored and the LCO was terminated on August 17, 1993. The Safety Significance of this event is minimal since steps were taken to insure manual tripping of the turbine and all other ECCS required by T.S. 3.5.C.2.a were operable during the time HPCI was Inoperable. Previous occurrences resulting in the disabling of the HPCI High Reactor Water Level Trip have been during planned LCOs and therefore not reported.
2491993019 | Dresden 3 | 12/14/1993 | 01/13/1994 | 9401260139 | <strong>Auto Closure of the HPCI Isolation Valve 3-2301-4 Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1993 at 2255 hours, with Unit 3 at 85% power an 'A' Electrical Maintenance (EM) worker was reinstalling a cover on the High Pressure Coolant Injection (HPCI) [BJ] Auto Isolation Relay (3-2330-124), located in the Auxiliary Electric Equipment Room (AEER) 903-3 panel and inadvertently operated the relay. After the cover was installed, the Unit Nuclear Station Operator (NSO) phoned the AEER to inform the Electrical Maintenance personnel that the high Pressure Coolant Injection Valve (3-2301-4) had closed. After discussion between the Shift Engineer, 'A' EM worker and HPCI System Engineer the valve was reopened.
2501993001 | Turkey Point 3, Turkey Point 4 | 01/15/1993 | 07/13/1993 | 9307220073 | <strong>Axially Mispositioned Wet Annular Burnable Absorber (WABA) Rods</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1993, with Turkey Point Units 3 and 4 in Mode 1 (POWER OPERATION) at 100% power, Florida Power and Light (FPL) was notified by Westinghouse Electric Corporation (nuclear fuel supplier) that the wet annular burnable absorber (WABA) assemblies were not manufactured according to the design specification. Both units were operating in Cycle 13. Specifically, beginning with Unit 3 Cycle 12 reload, FPL introduced a new fuel assembly design feature involving debris resistant fuel rods. The debris resistant design involved increasing the length of the solid fuel rod end cap and repositioning the active fuel height up 1.368 inches from the bottom of the fuel rod. The reload design for Unit 3 Cycle 13 and Unit 4 Cycle 13 required the absorber section of the WABAs be repositioned on center to match the corresponding repositioned active fuel height. During the startup of Turkey Point Unit 3 Cycle 13, FPL measured a higher local peaking factor (Fq) and a more top-peaked beginning of cycle axial power distribution than predicted by core models. As a result of further investigations, Westinghouse determined that the absorber section of the WABA had not been manufactured in accordance with design specification for the fuel reload. <br /><br /> At no point was either Unit 3 or Unit 4 operating in a condition outside of the design bases of the plants. <br /><br /> This LER is submitted as VOLUNTARY.
2501993002 | Turkey Point 3 | 01/15/1993 | 02/05/1993 | 9302110423 | <strong>Reactor Coolant System Pressure Boundary Leakage; Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1993, Turkey Point Unit 3 was in Mode 1 at 100 percent power. At about 1432, a msall steam leak was discovered ib ab abandoned pressurizer spray valve bypass line. The leak emanated from a socket weld connceting a pipe cap to the pipe nipple. An Unusual Event was declared for pressure boundary leakage. The Unusual Event was terminated when the unit entered Mode 5. <br /><br /> Increase in Containment radio activity had been occurreing since late December, 1992, but with no measurable change in leakage. The cause of the leak appears to be personnel error in that welders did not ensure adequate pullback of the pipe cap when it was installed in 1985. The inadequate pullback caused excessive local stress, which resulted in stress corrosion cracking of the fillet weld.<br /><br /> As corrective action, the fa ulted line was removed and a new pipe cap welded on. The abandoned spray valve bypass line on Unit 4 will be inspected and/or replaced during the next refueling outage.
2501993003 | Turkey Point 3 | 01/16/1993 | 01/29/1993 | 9302020448 | <strong>Both Trains Of Containment Spray Pump Manual Discharge Valves Isolated Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>During the review of operator logs on the afternoon shift of January 16, 1993, Operations personnel discovered that the manual discharge valves of both trains of the containment spray system had been isolated early that morning while in Mode 4. Containment spray pumps must remain operable in Modes 1 through 4 in accordance with Technical Specification 3.6.2.1. When the isolation was discovered the plant had already been cooled down to Mode 5. <br /><br /> Communication errors were identified as the root cause of the isolation. A contributing cause was a procedure attachment designed for multiple mode use. <br /><br /> Corrective actions include detailed discussions with personnel responsible for valve manipulation and procedure revisions.
2501993004 | Turkey Point 3 | 03/24/1993 | 04/14/1993 | ML09152041 | <strong>Failure To Maintain An Hourly Fire Watch Patrol; Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>Turkey Point Unit 3 was in Mode 1 at 100% power. An hourly Fire Watch patrol had been established (required by Technical Specification 3.7.9) whose rounds included the Unit 3 west penetration room. The Fire Watch had entered the room at 1630. Entries required at 1730, 1830, and 1930 were not made because the door could not be opened. The Nuclear Plant Supervisor was notified of the missed entries at 1920; at about 2000 the door was forced open, and the hourly Fire Watch patrol was resumed. <br /><br /> The root cause was inadequate control of painting of the door. The door was allowed to close before the paint was sufficiently cured; the uncured paint created seals which required substantial effort to break. A contributing cause was inadequate training of Fire Watch personnel to ensure timely notification of conditions preventing completion of assigned duties. <br /><br /> All Fire Watch personnel have been briefed on the event, and the need for timely notification of problems. All Fire Watch personnel will be retrained using a newly completed Fire Watch Training Manual. Utility Fire Protection staff personnel have been assigned to specific shifts for three months, to oversee the operations of Fire Watch personnel. Directions have been given to ensure that adequate steps are taken to prevent newly painted doors from sticking.
2501993005 | Turkey Point 3, Turkey Point 4 | 03/25/1993 | 04/26/1993 | 9305030309 | <strong>Setpoint For Overpressure Mitigating System Found Non- Conservative With Respect To 10 CFR 50 Appendix G.</strong><br /><i>Abstract:&nbsp;</i>On On March 25, 1993, Turkey Point Units 3 and 4 were in Mode 1 at 10006 power. On that date, Florida Power & Light (FPL) received information from its Nuclear Steam Supply System vendor that the setpoint for the Overpressure Mitigating System (OMS) is nonconservative with respect to 10 CFR 50 Appendix G. FPL therefore determined that the overpressure mitigating system on both Units 3 and 4 is placed outside the limiting design and licensing bases OMS analysis under the following conditions: <br /><br /> 1. Reactor Coolant System (RCS) temperature less than 105 degrees F,<br /> 2. RCS is water solid, and<br /> 3. Three Reactor Coolant Pumps (RCPs) are running. <br /><br /> The acceptance criteria for the setpoint assumes a mass addition produced by the start of a Safety Injection (SI) pump. Technical Specification requirements and administrative controls prevent the injection of water into the RCS due to a start of an SI pump. Additional administrative controls have been instituted to limit the number of RCPs running at low RCS temperatures.
2501993006 | Turkey Point 3 | 09/30/1993 | 10/22/1993 | 9310280278 | <strong>Reactor Trip During Shutdown Due To Excore Nuclear Instrument Source Range Failure</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1993, Turkey Point Unit 3 was shutting down to repair a steam leak on the pressurizer manway. At 2205 the excore nuclear instrument source range channel N31 spiked high when it was automatically re-energized. The spike generated a reactor trip signal, and the reactor trip breakers opened. At the time of the trip, the reactor was subcritical but all rods had not yet been fully inserted. All rods inserted on the trip, and all other plant equipment responded as expected. The reactor was stabilized in Mode 3. <br /><br /> The cause of the spike was a faulty high voltage power supply.<br /><br /> The faulty power supply was replaced, the source range channel was recalibrated, and the channel was returned to service upon successful completion of the surveillance test. Other methods of minimizing the risk of a preventable reactor trip from a faulty source range are being explored.
2511993001 | Turkey Point 4, Turkey Point 3 | 02/22/1993 | 03/18/1993 | 9303220369 | <strong>Failure To Post Continuous Fire Watch; Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>Turkey Point Unit 4 was in Mode 1 at 100 % power. The fire suppression system deluge valve for the Unit 4 charging pump room was isolated, making the deluge system inoperable. The fire detectors in the room were also taken out of service. A continuous fire watch was not established within one hour as required by Technical Specifications. The condition was discovered several hours later by management on an off-hours tour, and corrected immediately. <br /><br /> The immediate cause of the event was personnel error in that the Fire Watch Shift Supervisor (FWSS) did not ensure that the continuous fire watch was posted within the hour. The root cause was inadequate training of the FWSS in that he was not aware that he was responsible for ensuring the fire watch was posted. A contributing cause was inadequate communication between the FWSS, the operators, and the maintenance planners and workers. <br /><br /> A night order to operators and a letter to FWSS's now require that planned fire protection impairments have compensatory measures in place before the impairment is approved,. The administrative procedure governing fire protection impairments will be revised to incorporate this requirement. A formal qualification has been developed for FWSS's. The FWSS involved was removed from duty until he completes the formal qualification.
2511993002 | Turkey Point 4 | 06/22/1993 | 07/22/1993 | 9307270061 | <strong>Reactor Trip Due To Manual Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On the morning of June 22, 1993, Turkey Point Unit 4 was at 100% power and conducting a turbine trip test on the main turbine in accordance with procedures and procedural requirements. At the successful completion of the turbine trip test, the plant operators were unable to relatch the turbine trip. Turkey Point Unit 4 was reduced in power with the intent of taking the turbine off line to trouble shoot and repair, if necessary, the turbine trip latching mechanism. <br /><br /> At 1231 Eastern Daylight Time (EDT), with reactor power having been reduced to approximately 33% power, loss of turbine control oil pressure resulted in a turbine anti-motoring trip followed by a generator lockout. Based on the turbine anti-motoring indication and the generator lockout, plant operators manually tripped the turbine. A reactor trip at 1232 EDT resulted from the manual turbine trip. The NRC was notified in accordance with 10 CFR 50.72 (b) (2) (ii) June 22, 1993, at 1315 EDT.<br /><br /> Extensive investigations of probable cause for the turbine anti-motoring trip and generator lockout were completed. The investigations concluded that the cause was an inadvertent operation of the auxiliary governor trip lever by personnel restoring the turbine controls to normal after the turbine trip test. The unrelated inability to relatch the turbine trips was caused by incorrect clearances in the overspeed trip block between the trip relay and the relay bushing, and between the relay cup valve and the relay cover plate. These clearances were corrected and Unit 4 was returned to service on June 26, 1993.
2511993003 | Turkey Point 4 | 08/16/1993 | 09/07/1993 | 9309130279 | <strong>Turbine Trip/Reactor Trip Due To Hi-Hi Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1993, Turkey Point Unit 4 was in Mode 1 at 28% power. The two high pressure feedwater heaters were being placed in service. The restoration of the feedwater heaters was not done smoothly, and feed flow to the steam generators was severely curtailed. The loss of flow was recognized, an extra condensate pump and feed pump were started, and steam generator levels began to recover. Simultaneously, both feedwater heaters were completely restored to service in an attempt to aid in the recovery of feed flow. As a result steam generator levels rose faster than the reactor operators could control them. At 2233, the turbine tripped on high-high level in the 4C steam generator, which generated an automatic reactor trip.<br /><br /> The cause of the event was personnel error in that the high pressure feedwater heaters were not returned to service correctly. Contributors were an inadequate pre-evolution briefing, inadequate knowledge of the operation of the heater inlet valves, inadequate communications, and existing equipment failures which required both high pressure feedwater heaters to be valved out. <br /><br /> The operators involved were counselled, the procedure is being revised, management expectations for briefings are being emphasized, and operators are being trained on the operation of the three-way inlet valves.
2541993001 | Quad Cities 1, Quad Cities 2 | 02/04/1993 | 03/05/1993 | 9303100366 | <strong>HPCI/RCIC Declared Inoperable Due to Missed Tech Spec Surveillance Requirement.</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1993 at 1425 hours, Unit One and Two were in the RUN mode at 100 percent rated core thermal power. It was determined that the CCST low water level and Torus high water level switch contacts and logic circuitry were not functionally tested for both Unit One and Two HPCI and RCIC systems as required by Technical Specifications. Unit One and Two HPCI and RCIC systems were declared inoperable and Outage Reports were initiated. <br /><br /> While transferring the pump suctions paths from the CCST to the Torus, the HPCI torus suction check valves were determined to be leaking. The check valves were repaired and the level switches successfully tested. Unit One and Two RCIC were declared operable and outage reports terminated on February 4, 1993 at 1818 hours and 2110 hours, respectively. Unit One and Two HPCI were declared operable on February 6, 1993 at 1200 hours. <br /><br /> This event was caused by inadequate testing of a Technical Specification surveillance requirement. The disk misalignment of both the HPCI system check valves was due to an inadequate maintenance procedure which did not provide any acceptance criteria for checking and aligning the valve disk assemblies. <br /><br /> This report is being submitted to comply with 10CFR50.73(a)(2)(i)(B).
2541993002 | Quad Cities 1, Quad Cities 2 | 03/02/1993 | 09/27/1993 | 9310050183 | <strong>Failure Of Secondary Containment Test</strong><br /><i>Abstract:&nbsp;</i>At 0337 hours on March 2, 1993, Unit One was in the RUN mode operating at 80 percent of rated core thermal power, and Unit Two was in the RUN mode operating at 85 percent of rated core thermal power. The results from QTS 160-5, Secondary Containment Capability Test indicated that a differential pressure of 0.10 inches of water vacuum could be attained; whereas an average of 0.25 inches of water vacuum is required by Technical Specification 4.7.C.1.c. <br /><br /> At 0447 hours the Turbine Building Ventilation was adjusted from positive 0.075 inches of water to 0 inches of water vacuum. At this time Secondary Containment differential pressure increased to 0.29 inches of water vacuum. The test was restarted and at 0611 hours the differential pressure had reached 0.295 inches of water vacuum. <br /><br /> The cause of this event is attributed to a testing deficiency which resulted in placing the Turbine Building ventilation in an excessively conservative configuration.<br /><br /> The safety consequences of this event were minimal because the Secondary Containment was capable of performing its design function at all times.
2541993003 | Quad Cities 1, Quad Cities 2 | 03/05/1993 | 03/31/1993 | 9304090203 | <strong>Postulated Loss Of LPCI Swing Bus Due To An Original Design Weakness</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1993, Quad Cities Station determined there exists a potential design deficiency concerning the LPCI Swing Bus during degraded voltage conditions. Specifically, the potential exists that during a LOCA condition concurrent with degraded voltage that there are single component failures that could result in the failure of the LPCI Swing Bus and the associated 4 KV Safety Bus to transfer to their respective alternate supplies, resulting in sustained degraded voltage. Sustained degraded voltage on the LPCI Swing Bus and associated 4 KV Safety Bus could lead to the failure of both LPCI and the Division II Core Spray Sub systems resulting in an Emergency Core Cooling response that is more limiting than the current licensing basis. <br /><br /> Based on the review of this issue Quad Cities Station has concluded that this event is not within the current licensing basis and due to the extremely low probability of occurrence and availability of core cooling systems, is of minimal safety significance. Therefore, this event was deemed not reportable. However, because of the nature of this issue, Quad Cities has elected to provide this voluntary report.
2541993004 | Quad Cities 1 | 03/31/1993 | 04/28/1993 | 9305060213 | <strong>U-1 RCIC, 1A And 1B RHR Pumps And 1A Core Spray Pump Inoperable Due To Removal Of Floor Drain Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1993 at 1430 hours Unit One was in the RUN mode at 99.8 percent of rated core thermal power. At 0900 hours mechanical maintenance personnel had removed the 1A Residual Heat Removal (RHR)[BO] and 1A Core Spray [BM] rooms' floor drain [WK] isolation valves to facilitate hydralasing of the drain lines. At 1430 hours an Equipment Attendant identified that plugs were not installed in the floor drains as is required anytime the isolation valves are removed from the drain lines. The cause of this event was inadequate communication, both verbal and written. The work package contained insufficient detail for the control of the temporary alteration that should have been installed. The communication between Operations and Maintenance was also lacking in that neither Operations nor Maintenance confirmed the installation of the temporary alteration, both assumed it had been installed. Revisions to the Work Request procedure will be developed to positively control temporary alterations used in work packages. Shift Engineers will sign the 'shift authorization to start work' only immediately prior to the actual work commencing in the field. Human factor enhancements and training on the temporary alteration process will also take place. This report is being submitted to comply with the requirements of 10CFR50.73(a)(2)(v)(D) and (a)(2)(viii)(D).
2541993005 | Quad Cities 1 | 06/09/1993 | 07/09/1993 | 9307150108 | <strong>HPCI Inoperable Due To Rupture Disc Failures During QCOS 2300-5</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1993 at 0851 hours, Unit One was in the run mode at 72 percent rated core thermal power. At this time, the Nuclear Station Operator (NSO) was performing QCOS 23005, quarterly HPCI pump operability test, when numerous alarms were received in the control room including the HPCI turbine rupture disc high pressure alarm. The NSO then tripped the HPCI turbine. Subsequent investigation determined that the HPCI rupture disk had ruptured, releasing a steam/water mixture into the room. As a result of this, the secondary containment interlock doors and fire doors were damaged, and five people in attendance were injured (first and second degree burns). The cause of the rupture disk failure was due to a water slug that was present in the turbine casing. A contributing factor to this event was due to procedural inadequacies and interpretation problems during QCOS 2300-5 procedure. Short term corrective actions included repairing the damaged doors and a walkdown of the rooms to look for any significant operability concerns. Long term corrective actions include testing the HPCI and RCIC steam supply level switches on a periodic basis, changing the procedure to provide better guidance and interpretation, establishing inspection program for the HPCI and RCIC rupture disks, and providing training on the procedure and this event. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(v)(D) and 10CFR50.73(a)(2)(i)(A)>
2541993006 | Quad Cities 1 | 04/20/1993 | 05/14/1993 | 9305250240 | <strong>Inadvertent Start Of The U-1 Diesel Generator Due To A Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1993, at 0215 hours, Unit One was in the RUN mode at 100 percent of rated core thermal power. At this time, the Unit Two Nuclear Station Operator (NSO) inadvertently started the Unit One Diesel Generator (DG) [EK] when attempting to start the shared (1/2) DG. The Unit One DG was shut down, and the 1/2 DG subsequently started successfully. <br /><br /> The cause of this event is personnel error. Corrective actions include compiling a list of evolutions where operators can 'fail' and operate a wrong switch/breaker, presented to heighten the level of operator awareness at a department tailgate meeting. Further, performing Self Check techniques throughout evolutions will be reinforced. <br /><br /> This report is submitted in accordance with 10CFR50.73(a)(2)(iv), which states in part that the licensee shall report any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature unless the initiation occurred as a result of preplanned operations or testing.
2541993008 | Quad Cities 1, Quad Cities 2 | 07/09/1993 | 08/11/1993 | 9308190153 | <strong>U1 and U2 Rx Bldg Vent Radiation Monitors Hi Hi Setpoint Non-conservative Due To Calibration Error Caused By An Errant Computer Program Used To Calculate Source Exposure.</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1993, at 0952 hours, both Unit One (U1) and Unit Two (U2) were in the SHUTDOWN mode. A System Engineer informed the Shift Engineer the reactor building ventilation radiation monitor [MON][IL] setpoints had been set non-conservatively four times over the last five years due to an error in an Instrument Maintenance (IM) computer program. This event is being reported according to 10CFR50.73(a)(2)(i)(b), which requires the licensee to report any operation or condition prohibited by the plant Technical Specifications. The root cause of this event was personnel error by the IM management who wrote the program. The immediate corrective action was to verify the affected radiation monitor's setpoints were correctly set. A new program has been developed and submitted for approval. Until the new program is approved, calibrations will be performed using graphs. Calibration data on all U1, U2, and U0 area radiation monitors will be reviewed for similar setpoint discrepancies. The IM Department will conduct training on the use of QAP 1600-12. Finally, all station departments will review their software to ensure it meets all requirements of the Quality Assurance manual.
2541993009 | Quad Cities 1, Quad Cities 2 | 07/14/1993 | 08/13/1993 | 9308180097 | <strong>SBGT Methyl Iodide Test Failure Due To Age Of Charcoal</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, July 14, 1993, Unit one was in cold shutdown and Unit two was in the run mode at 20% of rated core thermal power. On June 29, 1993 the A SBGT train charcoal methyl iodide efficiency was shown to be 75.4% Tech Spec 3.7.B.2.a.3 require a methyl iodide efficiency of 90%. Both SBGT trains charcoal were replaced by July 4th. At 1500 hours on July 14th, the results of the old B Standby Gas Treatment (SBGT) [VI] train charcoal showed a methyl iodide efficiency of 72.1%. Therefore, before the charcoal replacement on both trains of SBGT on July 4th, both trains of SBGT were inoperable. A 4 hour Emergency Notification Phone call was made at 1610 hours on July 14, 1993. <br /><br /> The apparent cause of the failed methyl iodide efficiency test is the age of charcoal combined with the more stringent test criteria. <br /><br /> One corrective action was to replace the charcoal adsorber [ADS] in both trains of SBGT upon discovery of the A Train methyl iodide efficiency failure. Followup corrective actions are to install modification M04-0-92-013, which replaces the pneumatic flow switches with electronic flow switches. This modification will allow relaxation of the testing criteria. Until the modification is completed and the Tech Spec revision approved, the station will test the methyl iodide efficiency of the charcoal every 6 months.
2541993010 | Quad Cities 1 | 07/20/1993 | 08/19/1993 | 9308240039 | <strong>U-1 HPCI Inop Due To IST Flow In Required Action Range During QCOS 2300-5</strong><br /><i>Abstract:&nbsp;</i>At 2122 hours on July 20, 1993, Unit One was in the Startup mode at 9 percent of rated core thermal power. At this time, the NSO was performing the IST portion of IP-193, HPCI Periodic and Quarterly Pump Operability Test. During this test, the HPCI pump achieved approximately 4890 gpm at 1255 psig and 3700 rpm's. The IST acceptable range for the pump is between 5123-5559 gpm at 1255 psig pump discharge pressure and 3800 rpm's. Because the flow rate fell in the IST required action range, the Shift Engineer declared HPCI inoperable and initiated QCOS 2300-2, HPCI Outage Report.<br /><br /> The cause of this event was due to a new procedure. A contributing factor to this event was the 1-2358 FT, HPCI flow transmitter. <br /><br /> Corrective actions will include revising the surveillance procedure to ensure the MSC is at the HSS during IST testing of the HPCI system and calibrating the HPCI square root convertor every cycle. <br /><br /> This report is being submitted to comply with 10CFR50(a)(2)(v)(D).
2541993011 | Quad Cities 1 | 07/21/1993 | 06/03/1994 | 9406290352 | <strong>Unit One A Core Spray System Inop Due To Random Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>At 0917 hours on July 21, 1993, Unit One was in the RUN mode at 25 percent of rated core thermal power. It was discovered that 4KV breaker [BKR] #68, feeding the 1B Core Spray [BM] Pump Motor, was open and discharged. This resulted in the 1B Core Spray loop being declared inoperable. Since the High Pressure Coolant Injection System [BJ] (HPCI) was also inoperable at the time, this placed Unit One in a 24 hour Limiting Condition for Operation (LCO) per Technical Specification section 3.5.C.4. <br /><br /> The breaker was changed out and the 1B Core Spray loop was tested satisfactorily and the LCO was exited at 1017 on July 21, 1993. Troubleshooting indicated the breaker malfunction was caused by a random component failure of the 52-SM/LS (Spring Monitor Limit Switch) switch [33]. This prevented the breaker from recharging because this switch controls the operation of the charging motor. <br /><br /> Since this condition was determined to have existed prior to reactor startup, this report is being submitted in accordance with 10 CFR 50-73(a)(2)(i)(b) due to unintentional operation outside of Technical Specification section 3.5.A.1.
2541993012 | Quad Cities 1 | 07/26/1993 | 08/24/1993 | 9309010094 | <strong>Unit One HPCI Control Power Lost Due To A Short Circuit In The HPCI Turning Gear "Engaged" Light Socket</strong><br /><i>Abstract:&nbsp;</i>At 2152 hours on July 26, 1993, Unit One was in the RUN Mode. The High Pressure Coolant Injection (HPCI) turning gear 'engaged' light socket shorted out when an operator reset the HPCI logic power. The socket failure caused a loss of power to the HPCI control logic and as a result, the HPCI system was rendered inoperable. The cause of the logic power failure was a short circuit to the light socket. <br /><br /> The cause of the short could not be determined at this time. An investigation is being performed to determine the cause. The corrective actions will include installing a fuse or a current limiting device in similar indicating lights to protect their associated logic circuitry from a short. Also, operations will tailgate this event to heighten the awareness level when operating personnel working on indicating lights.
2541993013 | Quad Cities 1, Quad Cities 2 | 07/29/1993 | 08/27/1993 | 9309080017 | <strong>Control Room HVAC Charcoal Canister Testing Deviated From Tech Spec</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1993, at 0845 hours, Unit One and Two were in the RUN mode at 100 and 32.1 percent of rated core thermal power, respectively. At this time, a possible deviation from Technical Specification and Regulatory Guide 1.52 requirements for methyl iodide testing of charcoal sample canisters was identified. Through discussions with Nuclear Consulting Services, Inc. (NUCON), the Control Room [NA] (CR) ventilation system engineer verified that a deviation had occurred. On July 30, 1993, the Shift Engineer (SE) decided that the deviation was reportable per 10CFR50.73(A)(2)(i)(B). <br /><br /> The apparent cause of this event was a lack of understanding by the present and previous system engineer of the sample canister testing criteria. <br /><br /> The corrective actions were to investigate the incident, decide reportability, and ship additional sample canisters to NUCON for further testing. A procedure change request was submitted and the system engineer qualification card was updated.
2541993014 | Quad Cities 1 | 09/02/1993 | 10/01/1993 | 9310120313 | <strong>IRM #11 and APRM #3 Were Both Bypassed Without A 1/2 Scram Being Inserted</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in the RUN mode at 100% power on 09/01/93 at 1714 hours when Average Power Range Monitor (APRM) IG, MON! #3 was placed in the bypassed condition. On 09/02/93 at approximately 0100 hours, Intermediate Range Monitor (IRM) IG, MON! #11 was placed in the bypassed condition due to being subject to spiking problems, and no half scram was inserted as a result of IRM #11 and APRM #3 both being in the bypassed condition. <br /><br /> At 0825 hours on 09/02/93, the Unit 1 Nuclear Station Operator (NSO) discovered that IRM #11 and APRM #3 were both in the bypassed condition without a half scram being inserted. <br /><br /> The immediate corrective action performed by the Unit 1 NSO was taking IRM #11 out of the bypassed condition at 0825 hours on 09/02/93. <br /><br /> The primary causal factor of this event is WORK PRACTICES.
2541993015 | Quad Cities 1 | 08/17/1993 | 09/24/1993 | 9309290094 | <strong>Compensatory Actions Not Put In Place After Safe Shutdown Pump Room Cooler Declared Inop</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1993, Unit One and Unit Two were in the RUN mode at 100% of rated core thermal power. The Safe Shutdown Makeup Pump Room Cooler was out of service for repair. A review of Safe Shutdown Equipment and Fire Protection Requirements identified that compensatory measures had not been properly established as required by the stations Administrative Technical Requirements (ATRS) for fire protection. <br /><br /> The cause of this event was inadequate managerial attention to developing procedures to implement the ATRS. Corrective actions to previous events were not broad enough in scope to cover other procedure changes required, training requirements, and preventive maintenance.
2541993016 | Quad Cities 1, Quad Cities 2 | 08/19/1993 | 09/17/1993 | 9309280087 | <strong>Operability Concern Based Upon Problems With The QARPS and Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>At 1826 on 08/19/93, Unit 1 and Unit 2 were both in the RUN mode at 100% of rated core thermal power. During an ongoing comparison review of the Safe Shutdown (SSD) Program, inconsistencies and inaccuracies were identified in the Quad Cities Appendix R Procedures (QARP's) by the Fire Protection System Engineer and a contracted Subject Matter Expert. As written, it appeared as if the QARP's (if applied to selected Appendix R scenarios) could not have supported the achievement of a safe plant shutdown condition in the required amount of time. <br /><br /> The primary causal factors of these deficiencies can be attributed to ineffective CHANGE AND RESOURCE MANAGEMENT, MANAGERIAL METHODS and WORK ORGANIZATION/PLANNING. TRAINING/QUALIFICATION is a secondary contributing factor. <br /><br /> As immediate compensatory measures, fire watch surveillances were established in all areas containing SSD equipment. The Station will continue in the current sixty seven (67) day Limiting Condition for Operation (LCO), as required by the Appendix R Conformance Safe Shutdown Report. During the LCO period, which expires on 09/22/93, all of the QARP's will be re-reviewed, revised as needed and approved.
2541993017 | Quad Cities 1, Quad Cities 2 | 08/22/1993 | 09/20/1993 | 9309280099 | <strong>U-1 and U-2 HPCI Drain Pot Level Switches Found Isolated</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1993, Unit 1 was in the RUN mode of operation at 73 percent of rated core thermal power and Unit 2 was in the RUN mode of operation at 41 percent of rated core thermal power. Quad Cities Station during the weekend of August 21 and 22, 1993 while conducting routine testing of the Unit 1 and 2 HPCI pumps experienced an incorrect valving operation due to personnel error. This resulted in a four hour Event Notification (ENS) phone call per 10CFR50.72 due to declaring both Unit 1 and 2 HPCI pumps inoperable for the period of time the valves were incorrectly positioned. CECo Engineering with support of General Electric, the original HPCI supplier, have subsequently performed an evaluation which determined the HPCI pumps would have performed their design function and were operable throughout the period the valves were closed. <br /><br /> Corrective actions include changing certain operating and administrative procedures, developing a formal station policy to clearly define the interface methods when nonoperating personnel are assisting Operations in the performance of plant evolutions, implementation of existing plans to conduct a programmatic evaluation of the System Engineering program, and implement plans to formalize the policy for details of the self checking program. <br /><br /> This is being submitted as a voluntary Licensed Event Report.
2541993018 | Quad Cities 1 | 08/31/1993 | 09/29/1993 | 9310050079 | <strong>APRM# 4 Bypassed While Its Companion IRM# Was Also Bypassed.</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in the RUN mode at 100% power on 08/31/93 at approximately 1743 hours with Intermediate Range Monitor (IRM) [IG, MON] #16 bypassed when the extra Nuclear Station Operator (NSO) relieved the Unit 1 NSO. At 1748 hours, the extra NSO bypassed Average Power Range Monitor (APRM) [IG, MON] #4 without inserting a half scram. <br /><br /> At 1804 hours on 08/31/93, the Unit 1 NSO identified the problem during the process of relieving the extra NSO, and immediately took APRM #4 out of bypass. <br /><br /> The primary causal factor of this event is WORK PRACTICES. <br /><br /> This situation has been discussed with the NSO involved. In addition a Technical Specification Revision is being prepared to remove the companion trip feature from the Quad Cities Technical Specifications.
2541993019 | Quad Cities 1 | 09/03/1993 | 10/01/1993 | 9310120321 | <strong>Inadvertent Start of 1A RHR Pump</strong><br /><i>Abstract:&nbsp;</i>At 0059 hours on September 3, 1993, performance of QCOP 1000-27, 'Flushing A RHR Heat Exchanger using Two RHR Service Water Pumps.' was in progress. At the point in the procedure requiring the start of the A Residual Heat Removal (RHR) Service Water pump, the 1A RHR pump was inadvertently started. The pump was immediately secured. <br /><br /> The cause of this event is personnel error. The Unit One Nuclear Station Operator (NSO) failed to ensure that the correct switch was located prior to actuation, and as a result, the 1A RHR pump was started instead of the intended 1A RHR Service Water pump. <br /><br /> The NSO was immediately counselled by the Shift Engineer on the importance of self-check. Additional disciplinary action was also administered.
2541993020 | Quad Cities 1 | 11/11/1993 | 12/09/1993 | 9312210216 | <strong>Partial Loss Of Shutdown Cooling Flow Due To Opening Of Reactor Recirculation Discharge Valve MO-1-202-5B</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1993, at 0333 hours, Unit-1 was in cold shutdown for a maintenance outage. Unit-1 Nuclear Station Operator (NSO) closed Reactor Recirculation (RR) pump discharge valve 1-202-5B, per procedure for testing. Later the NSO reopened the 1-202-5B valve, without procedure guidance. At 0750 hours, the Control Room determined that short cycling of SDC flow could occur with the RR Discharge Valve open and closed the discharge valve. <br /><br /> The Station has initiated the following immediate actions: Station Management held shift briefings on this event as each crew came onshift, an Interim Procedure change was made to the RR Pump Operating Procedure concerning positioning of the pump discharge valve, 1-202-5A/B were taken Out of Service closed, reporting of the event pursuant to 10CFR50.72(b)(2)(iii), and a Level 2 Investigation was initiated. <br /><br /> The Causal Factors (C/F) for this event are attribed to Work Practices, Written and Verbal Communication, Managerial and Supervisory Methods, and Training Content. <br /><br /> A Summary of recommended corrective actions to be completed are to effectively communicate and enforce management expectations regarding procedural adherence and craft capability, enhance training for shutdown conditions, enhance the procedures which were used during this event, and a voluntary LER is submitted because of the potential severity of the event.
2541993023 | Quad Cities 1 | 12/16/1993 | 01/12/1994 | 9401260303 | <strong>Engineered Safety Feature Actuations Caused By Main Turbine Control Logic Relay Failure</strong><br /><i>Abstract:&nbsp;</i>At 2355 hours on December 16, 1993, the Unit-1 main turbine [TA] tripped from 97 percent reactor core thermal power. The turbine stop valve closure initiated a reactor scram. Spurious main steam line low pressure signals generated a group one primary containment isolation (PCI) [JM]. The turbine trip was caused by a main condenser [SG] low vacuum signal, but vacuum was found to be normal. The main steam isolation valves were reopened and a reactor cooldown was started. A relay contact for condenser low vacuum turbine trip was found to have failed in the closed position. <br /><br /> The root cause of this event was a relay failure due to manufacturing specification. A contributing cause of this event was design analysis. <br /><br /> The relay was replaced like for like and tested satisfactorily. Other trip relays that provide turbine trip signals, but are not routinely tested through periodic surveillance were tested prior to start up. The station is investigating options for improving the reliability and possibly adding redundancy to the turbine trip logic.
2551993001 | Palisades | 01/06/1993 | 02/05/1993 | 9302160003 | <strong>Loss Of Emergency Onsite Ac Power Due To Both Emergency Diesel Generators Being Simultaneously Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1993 at 0110 hours, with the reactor operating at 100% power, Emergency Diesel Generators (DG) 1-1 and 1-2 were simultaneously inoperable. At the time of the event DG 1-2 had just been shut down after being run to verify operability prior to taking DG 1-1 out of service for maintenance. DG 1-1 was then rendered inoperable by racking out the DG 1-1 incoming breaker in accordance with the switching and tagging order controlling the work. One of the subsequent steps in the switching and tagging order was to trip the over-speed trip device for DG 1-1. The auxiliary operator performing the work described in the switching and tagging order inadvertently renderd DG 1-2 inoperable when he manually tripped the over-speed trip device for DG 1-2. The auxiliary operator immediately recognized the error and took corrective action to restore DG 1-2 to an operable condition. The DGs were simultaneously inoperable for a total of two minutes. DG 1-2 was again test started to verify operability and this test was satisfactorily completed at 0127 hours. <br /><br /> The cause of this event was personnel error on the part of the licensed auxiliary operator who failed to follow the switching and tagging order instructions. <br /><br /> Corrective action for this event included labeling the DG over -speed trip devices with their respective DG identification numbers, disciplining the individual involved in accordance with Consumers Power Company policy, and reinforcing the self-check policy within the Operation Department.
2551993002 | Palisades | 03/06/1993 | 09/03/1993 | 9309140375 | <strong>Potential Loss Of Containment Integrity Due To The Failure Of The Emergency Escape Airlock Equalizing Valve - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1993, at 1400 hours, with the plant operating at 100% power, it was determined that containment integrity, as defined in Technical Specifications 1.4 and 3.6.1a, may have been violated due to equalizing valve of the emergency escape airlock sticking open. At the time of discovery the plant staff was performing technical specifications surveillance procedure (TSSP) SO-4b, 'Escape Air Lock Penetration Leak Test.' The escape air lock had been satisfactorily tested on September 21, 1992. <br /><br /> This event is not considered a safety significant issue since a significant radiological source term did not exist and the outer door of the escape air lock was operable. Only one door of an air lock is required for containment integrity in accordance with Technical Specification 1.4c. <br /><br /> The cause of this event was that the escape air lock inner door equalizing valve was stuck in the open position, thereby defeating the isolation capability of the inner door. The possible cause of the equalizing valve sticking open is that the emergency escape airlock door mechanisms, including the equalizing valves, are not cycled routinely, therefore, it is believed that the lubricant used on the O-ring seals dries and becomes tacky due to heat in containment and lack of use. <br /><br /> Corrective action for this event included performing maintenance on the escape airlock inner door equalizing valve during the 1993 Refueling Outage.
2551993003 | Palisades | 04/28/1993 | 05/28/1993 | 9306090504 | <strong>Plant Shutdown Required By Plant Technical Specifications Due To Primary Coolant System Unidentified Leakage In Excess Of The Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1993 at approximately 1300 hours, with the reactor operating at 100% power, an abnormal decreasing trend in the level of the volume control tank (VCT) was observed by the control room operators. Operators implemented procedural actions in an attempt to identify and reduce the primary coolant system (PCS) leakage. Following completion of the procedural actions, the PCS leakrate was 1.08 gpm, which is greater than the 1.0 gpm unidentified leakage limit imposed by the plant Technical Specifications, therefore, an Unusual Event was declared and an immediate plant shutdown commenced. <br /><br /> The cause of this event was increased leakage from the control rod drive mechanism mechanical seals that had been previously identified and for which a plant shutdown had been scheduled to commence at 1800 hours on April 28, 1993. <br /><br /> Corrective action for this event is to repair previously identified leaking CRDM mechanical seal packages.
2551993004 | Palisades | 06/30/1993 | 10/14/1993 | 9310190062 | <strong>Fuel Rod Failure And Subsequent Loss Of Special Nuclear Material Discovered Following Refueling Operations - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1993, at approximately 2300 hours, while draining the refueling cavity in preparation for re-attaching the reactor head to the reactor vessel, an object located in the reactor cavity tilt pit exhibited contact dose rates of approximately 7000R/hr. A review of a remote camera inspection video tape led to the postulation that the object was a piece of fuel rod. Further remote camera inspection of the tilt pit resulted in the discovery of three additional pieces of what appeared to be a fuel rod. Subsequent investigation determined that fragmented pieces of failed fuel rod S-15 dislodged from fuel assembly I-024 during refueling operations.<br /><br /> The failure of the fuel rod was caused by a core shroud and fuel assembly interface problem that resulted in the wear and failure of a single fuel rod. The damaged fuel rod became dislodged from the fuel assembly during refueling operations.<br /><br /> Corrective action for this event includes increased fuel assembly inspections, inspection of the core shroud during the next full core offload, Cycle 11 core redesign incorporating stainless steel rods in selected fuel assemblies, limiting the use of the standard bi-metallic fuel assembly design to four cycles or less, continued periodic reactor noise analysis, procedure changes, and implementation of the Failed Fuel Response Plan.
2551993005 | Palisades | 07/20/1993 | 02/04/1994 | 9402280061 | <strong>Engineered Safety Feature Actuation - Emergency Diesel Generator Start Due To An Inadvertent Loss Of Power To Safeguard Bus 1C - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1993, at 1743 hours, both emergency diesel generators started after receiving an undervoltage signal due to the de-energization of electrical Bus 1C. Simultaneous with this inadvertent ESF actuation, a spare breaker was being installed in the cubicle for the Start-up Transformer breaker. As the spare breaker was inserted into the Start-up Transformer cubicle, the Safeguards Transformer 1-1 feeder breaker opened, de-energizing Bus 1C. An undervoltage condition resulted which initiated an emergency diesel generator start. Shutdown cooling was not affected since safeguards electrical loads were being supplied by the opposite channel safeguards bus. <br /><br /> The cause of this event is attributable to inadequate design information. <br /><br /> The remaining corrective action for this event is developing a methodology for the control of spare breakers.
2551993006 | Palisades | 08/04/1993 | 09/03/1993 | 9309130261 | <strong>Regulatory Guide 1.97 Pressurizer Level Indicator Powered From A Non-Class 1e Power Supply</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1993, at approximately 1400 hours, with the plant in cold shutdown for refueling, it was determined that a Regulatory Guide 1.97, Category 1, pressurizer level indicator was powered from a non-safety related power supply. This condition was discovered during the review of electrical prints in support of the ongoing Configuration Control Program (CCP) drawing review. Field verification of the electrical print confirmed that the pressurizer level indicator was powered from a non-safety related power supply.<br /><br /> The cause of this event was personnel error and inadequate post modification testing.<br /><br /> Corrective action for this event includes powering indicator LIA-0102A from the correct power source prior to the end of the 1993 refueling outage, training personnel on the confusion that may result when dealing with wire labeling associated with panels of similar alpha-numeric designation, and evaluating the need for changes to procedures.
2551993007 | Palisades | 08/17/1993 | 05/23/1995 | 9506010126 | <strong>Degradation Of Boraflex Neutron Absorber In Surveillance Coupons - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1993 the plant was in cold shutdown for refueling. A Boraflex surveillance coupon was removed from the spent fuel pool in order to conduct a visual inspection, neutron attenuation test, and a hardness test. While removing the coupon from the spent fuel pool, a dark debris cloud was observed in the spent fuel pool around the edges of the coupon. Upon removal of the sheet metal coupon cover, the Boraflex material was found to be approximately 90 percent disintegrated or missing. Additional coupons were removed from the spent fuel pool and examined with varying amounts of Boraflex material found missing. <br /><br /> The cause of this event is flow induced deterioration of the full length surveillance coupons due to inadequate holding canister design. The full length surveillance capsules have since been determined to be poor indicators of the actual rack Boraflex condition. <br /><br /> Corrective actions include completion of neutron attenuation testing on the spent fuel pool racks and a change to the surveillance method for verification of rack Boraflex condition.
2551993008 | Palisades | 08/24/1993 | 11/24/1993 | 9312070323 | <strong>Inoperable Safeguards Room Coolers Resulting From Improper Thermal Overload Protection Design</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1993, at approximately 2000 hours, with the plant in cold shutdown following refueling, a technical specifications surveillance test was being performed on the engineered safeguards room cooling and ventilation system. During performance of the test, the V-27D safeguards room cooling fan motor failed to start. Investigation found that the contactor for the fan motor had tripped on thermal overload. Further investigation revealed that a recent reduction in the thermal overload protection may not have allowed continuous operation of all the engineered safeguards room cooling fans, causing both trains of engineered safety features to be considered inoperable. <br /><br /> The cause of this event is attributable to inadequate design control and post maintenance testing. <br /><br /> Corrective actions include the following: reanalyzing, revising, and testing the fan motor thermal overload settings to provide operability margin; reviewing all thermal overload setting changes made in 1993 to ensure that appropriate post maintenance testing was performed; forming a multi-disciplinary group to review the event and evaluate corrective actions; and stopping further protection device setting changes until the multi-disciplinary group reviews are complete.
2551993009 | Palisades | 09/16/1993 | 11/18/1993 | 9312010345 | <strong>Pressurizer Penetration Safe End Crack Results In Pcs Leakage</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1993, at approximately 1900 hours, the plant was in the process of heating up following a refueling outage. The plant's primary coolant system (PCS) was in a hot shutdown condition (532 degrees F and 2060 psia) when plant operations personnel identified a leak in the power operated relief valve (PORV) line near the nozzle connection to the pressurizer. The plant was returned to cold shutdown.<br /><br /> The crack initiated due primary water stress corrosion cracking (PWSCC) in the heat affected zone (HAZ) of the power operated relief valve (PORV) Inconel 600 safe end. <br /><br /> Corrective actions include removing a portion of the safe end containing the crack for evaluation, examining the remaining safe end to establish its condition for future use, rewelding the PORV pipe to the examined safe end to replace the piping that was removed, and examining and evaluating the remaining pressurizer nozzles and other primary coolant system nozzles to provide assurance of operability prior to returning the plant to service.
2551993010 | Palisades | 09/17/1993 | 10/18/1993 | 9310250185 | <strong>Exceeding The Primary Coolant System Cooldown Rate As Defined In The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>on September 17, 1993, at 1356 hours, with the plant in cold shutdown, a primary coolant system (PCS) cooldown was in progress to perform repairs on a leaking pressurizer relief valve nozzle. During the cooldown, the PCS cooldown rate of 20 degrees F/hr in any one hour, as defined in the Technical Specifications, was exceeded. <br /><br /> The cause of this event was a combination of personnel error and inadequate procedures. <br /><br /> Corrective action for this event includes evaluations of the affect on reactor vessel material as a result of this event, evaluations of the heat-up and cooldown processes used at Palisades, procedure evaluations, verification of proper temperature monitoring techniques for heat-up and cooldown, verifying equipment operation and reliability, remedial training and simulator performance evaluations of the operating crew involved in this event, management discussions with the operating crews about the implications of this event, and incorporating the lessons learned from this event into training lesson plans.
2551993011 | Palisades | 10/09/1993 | 11/02/1993 | 9311090219 | <strong>Pressurizer Temperature Element Crack Results In PCS Leakage</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1993, at approximately 0900 hours, the plant was in cold shutdown and beginning heat up. Inspection of the pressurizer upper temperature nozzle penetration (TE-0101) found it to be leaking. Subsequent inspection of the lower temperature nozzle penetration (TE-0102) found it to be leaking also. The cause of this event has been attributed to primary water stress corrosion cracking of the Inconel 600 nozzle material. <br /><br /> Other similar penetrations in the PCS were inspected and none showed evidence of any past or present leakage. The two leaking pressurizer temperature nozzle penetrations were repaired. A comprehensive Inconel 600 inspection and maintenance program will be developed for the Palisades plant.
2551993012 | Palisades | 11/03/1993 | 11/24/1993 | 9312070325 | <strong>Containment High Pressure (CHP) And Containment High Radiation (CHR) Relays Operability</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1993, with the plant in a hot standby condition, it was concluded that seismic qualification did not exist for relays that had been previously installed in the CHP and CHR circuits. During the refueling outage these relays were determined to have undersized coils and were therefore modified. Seismic testing of the relays in their original configuration did not prove they could operate following a design basis earthquake. Subsequent evaluation has also determined that no consideration was made relative to the relay circuit voltage drop, which when taken into account would result in a condition in which the pre-modified relays might not meet their design function. <br /><br /> The root cause of the event is the undersized relay coils. These are original plant design deficiencies. <br /><br /> Corrective action for this event includes seismically qualifying the relays consistent with the installed configuration, replacing the undersized coils in the relays, evaluating other similar relays, evaluating the effects of voltage drop in the relay circuits, updating equipment control documents, and ensuring staff and procedures are knowledgeable and reflect the lessons learned from this event.
2551993013 | Palisades | 04/27/1993 | 02/10/1994 | 9402280016 | <strong>Loss Of Emergency Onsite Ac Power Due To Both Emergency Diesel Generators Being Simultaneously Inoperable - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1993, at 0428 hours, with the plant operating at 100% power, diesel generator (DG) 1-1 was test started and loaded to approximately 500KW prior to removing BG 1-2 from service to perform preventive maintenance. After approximately 5 minutes of operation, the load on DG 1-1 dropped to zero and DG 1-1 was declared inoperable. In accordance with our technical specifications, DG 1-2 was started and loaded to verify operability; however, by paralleling DG 1-2 to the electrical distribution grid to accept load, DG 1-2 was also rendered inoperable for a period of five minutes. Therefore, both DGs were simultaneously inoperable, Technical Specification 3.0.3 (plant shutdown within 1 hour) was entered, and an Unusual Event was declared in accordance with our emergency operating procedures. <br /><br /> The cause of this event was paralleling DG 1-2 to the electrical distribution grid and rendering it inoperable while DG 1-1 was also inoperable. Paralleling DG 1-2 was determined to be necessary to verify there was no common mode failure and to ensure DG 1-2 operability. A similar event which occurred in 1992 and was not reported to the NRC is discussed in the body of this LER. <br /><br /> Corrective action for this includes submitting a revision to the electrical section of our technical specifications which will emulate the NUREG 1432, 'Standard Technical Specifications for CE Plants,' electrical section.
2551993014 | Palisades | 12/07/1993 | 01/06/1994 | 9401140099 | <strong>Failure Of Electrical Containment Penetrations To Meet Design Features Described In Technical Specifications and FSAR</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1993, at 1240 hours, with the plant operating at 100 % power, it was determined that the containment electrical penetrations in the north and southwest penetration rooms did not meet all the design criteria specified in the Palisades Final Safety Analysis Report (FSAR) and the Technical Specifications. In each room, a non-seismic nitrogen system is connected to each electrical penetration between the double barriers. Furthermore, the bottles and connecting piping for the nitrogen system to the southwest penetration room lie outside the auxiliary building and, therefore, are not tornado protected. <br /><br /> The cause of this event was inadequate design control. The design of the electrical penetrations was modified in 1970 and again in 1982 without recognizing all of the design requirements of the electrical penetrations as containment isolation boundaries.<br /><br /> Corrective action for this event includes evaluating appropriate actions to address the deficiencies in the electrical penetration design, evaluating the containment isolation boundaries for the electrical penetrations, incorporating electrical penetration design requirements for the nitrogen supply into plant design documents, implementing permanent corrective action for the electrical penetration design deficiency, and providing a lessons learned memo to plant engineers emphasizing the evaluation of functional interfaces when making changes to plant equipment.
2591993001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 01/10/1993 | 02/26/1993 | 9303080047 | <strong>Reactor Building Crane Surveillance Missed As A Result Of Ambiguous or Missing Instruction</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1993, at 1740 hours, the reactor building crane surveillance instruction (SI) could not be verified to have been performed to support the new fuel receipt and inspection activities. The handling of the new fuel had started on January 10, 1993, in preparation for the Unit 2, Cycle 6 refueling outage. <br /><br /> The missed SI is a conditional surveillance which is required to be performed quarterly on the reactor building crane prior to handling new or spent fuel or the spent fuel cask. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the technical specifications.<br /><br /> The root cause of the event was determined to be ambiguous or missing instructions as to who should sign off the SI verification step in the new fuel operations instruction. Contributing to the event was the lack of formalized guidance to determine the status of completed SIs.<br /><br /> Immediate corrective actions were to stop all reactor building crane activities and perform the required crane surveillance. GOIs will be revised to identify work control as the required signoff organization to verify SI completion. Operations personnel will be instructed to verify the latest SI performance through work control. TVA will review conditional SIs to determine if sufficient procedural controls are in place to ensure that conditional SIs are performed as required.
2591993002 | Browns Ferry 1, Browns Ferry 2 | 02/12/1993 | 03/11/1993 | 9303190196 | <strong>Diesel Generator Auto-started As A Result Of Breaker Cell Switch Operation</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1993, diesel general D auto-started on undervoltage following an unexpected trip of shutdown bus 2 alternate feeder breaker. At the time of the event, the bus 2 normal feeder breaker had been removed from its compartment for periodic maintenance and performance of the maintenance resulted in actuation of the cell switch in the breaker board compartment. This in turn opened bus 2 alternate feeder breaker and deenergized bus 2. Deenergization of bus 2 led to an undervoltage transfer of 4kV shutdown board D to bus 1 and an undervoltage auto-start of diesel generator D. Concurrently, essential equipment cooling water pump A1 auto-started in response to the diesel generator start. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in automatic actuation of an engineered safety feature (ESF). <br /><br /> The root cause was inadequate procedures. The preventive maintenance instruction did not provide a caution to specify that operation of the cell switch could result in an ESF actuation. Contributing to the event was the mindset of the involved personnel that performance of this maintenance would not impact other equipment.<br /><br /> To prevent recurrence, TVA will revise the preventive maintenance program to require a bus outage to perform breaker compartment maintenance that could cause an ESF actuation. Additionally, a caution note regarding potential cell switch operation will be added to the electrical preventive instruction used to perform breaker compartment maintenance.
2591993003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/19/1993 | 05/14/1993 | 9305200307 | <strong>Engineered Safety Feature Actuation Caused By A Sudden Pressure Relay Being Struck By Tool.</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1993, at 1359 hours, during the BFN Unit 2 refueling outage, the Athens 161 kV offsite power supply deenergized when a sudden pressure relay closed. This event was initiated by an electrician working overhead who inadvertently dropped a tool onto the sudden pressure relay causing it to close. The loss of this offsite power initiated several Engineered Safety Features systems as designed. Emergency Diesel Generators C, D, 3A, and 3B auto-started, and the Control Room Emergency Ventilation and Standby Gas Treatment Systems initiated. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in manual or automatic actuation of an engineered safety feature. <br /><br /> The root cause of the event was inadequate prejob planning that failed to prepare the work area to provide sufficient level of protection for sensitive plant equipment. Specifically, the barriers that were installed to protect the relays from modification activities were insufficient and the scaffolding configuration was inadequate. <br /><br /> As a result of this event, TVA will conduct briefings on this incident with both management and field personnel to reiterate the importance of identifying all sensitive equipment in the area of work activity. Additionally, BFN procedures will be expanded to include an evaluation of work performed around sensitive equipment in the 3C relay room.
2601993001 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 01/24/1993 | 02/23/1993 | 9303020006 | <strong>Inoperable Reactor Core Isolation System Due To Ground Fault in the 250 Volt DC Power System</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1993, at 2230 hours the Reactor Core Isolation Cooling (RCIC) system was declared inoperable when the outboard steam line isolation valve was discovered closed.<br /><br /> The root cause of this event was failure of a Reactor Water Cleanup (RWCU) isolation valve bonnet pressure seal ring. The ring failed allowing RWCU water to spray filling the local control station for the RCIC outboard steam line isolation valve with water and grounding the local switch. <br /><br /> Corrective actions to prevent recurrence will be removal of the RCIC local control station and associated hand switch, and repair of the RWCU valve involved.
2601993002 | Browns Ferry 2 | 01/31/1993 | 06/28/1993 | 9307060230 | <strong>Main Steam Line Isolation Valves Exceeding Allowable Leakage During Testing.</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1993, at 1030 hours during performance of local leak rate testing (LLRT), it was determined that the main steam system isolation valves (MSIV) on main steam line 'C' were found to have leakage in excess of the technical specification limit of 11.5 standard cubic feet per hour. Additional LLRT resulted in a total as-found maximum path leak rate of 6625 standard cubic feet per hour (SCFH).<br /><br /> The root cause of the unforeseen failure of the 'C' Main Steam Line Inboard Isolation Valve was abnormal wear. Upon inspection of the valve, TVA identified rib guide wear on the bottom guide where the poppet contacts the guide when the valve is in the open position. Because of this wear, the main poppet tilted as the valve traveled to the closed position, failing to contact the seat properly and isolate. <br /><br /> TVA repaired the 'C' MSIV valve and successfully retested it. <br /><br /> Additionally, TVA repaired, modified, or replaced other failed components. During subsequent retesting, TVA attained a total as left maximum path leakage of 160.1642 SCFH.
2601993003 | Browns Ferry 2 | 03/23/1993 | 04/22/1993 | 9304260154 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Setpoint Limit to Open as Result of Disc/Seat Bonding.</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1993, TVA was notified that of the first six of the thirteen Unit 2 main steam safety/relief valves bench-tested at Wyle Laboratories five failed the setpoint test acceptance criteria. On March 26, 1993, with the testing of all thirteen Unit 2 main steam safety/relief valves completed, a total of eleven valves had failed to open within one-percent of their setpoints. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's technical specifications. <br /><br /> The apparent cause was corrosion bonding of the valve pilot disc/seat interface resulting in an upward setpoint drift. This bonding resulted in an increase in the valve opening pressure due to the need for additional opening force above the setpoint value. Corrosion is being attributed to radiologically produced oxygen collecting at the disc/seat interface. <br /><br /> TVA plans to use the Unit 2 main steam safety/relief valves on Unit 3. The out-of-tolerance valves will be refurbished, retested, and recertified prior to the startup of Unit 3 cycle 6. The Unit 2 main steam safety/relief valves will be replaced with the recertified safety/relief valves from Unit 3 prior to the restart of Unit 2 from its current cycle 6 refueling outage. <br /><br /> TVA will continue to participate in BWROG's Evaluation on the long term solution concerning the SRV setpoint drift problem.
2601993004 | Browns Ferry 2 | 05/11/1993 | 06/10/1993 | 9306170030 | <strong>High Reactor Pressure Condition Resulted In Anticipated Trip Without Scram Signal That Tripped The Reactor Recirculation Pump And Initiated An Alternate Rod Insertion Signal.</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1993, TVA was performing the Surveillance Instruction (SI) 'ASME Section XI System Leakage Test of the Reactor Pressure Vessel and Associated Piping,' and 'Functional Test of Instrument Line Flow Check Valve SI.' At 2324 hours on this date, an unplanned actuation of Engineered Safeguard Features including Reactor Protection System actuation occurred when a high reactor vessel pressure signal initiated an Anticipated Trip Without Scram signal. This event tripped the Reactor Recirculation system pumps and initiated an Alternate Rod Insertion (ARI) signal. The ARI signal resulted in a depressurization of the scram pilot air header and subsequent scram condition due to low scram air header pressure. <br /><br /> The root cause of this event is lack of attention to detail in that the Unit Operator did not adequately track the progress of the Instrument Line Flow Check Valve SI. <br /><br /> Corrective actions include counselling personnel involved in the event, and issuance of a briefing on the event. The method for identifying instruments in the Instrument Line Flow Check Valve SI will be evaluated. Additionally, the Functional Test of Instrument Line Flow Check Valves will be designated as a complex infrequently performed test.
2601993005 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 05/20/1993 | 06/21/1993 | 9306290202 | <strong>ESF Actuation Resulting From A Lifted Neutral Lead On A MSIV Solenoid Circuit.</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1993, at 0145 hours, a Modifications electrician lifted a jumper and the neutral lead of the power supply to an ammeter for the main steam isolation valve solenoid circuit. The neutral lead in a daisy-chain configuration was removed, which opened the circuits to several Division 1 relays. This resulted in a primary containment isolation system (PCIS) Division 1 actuation. Thus, this event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as an event that resulted in a manual or automatic ESF actuation. <br /><br /> The root cause for this event is personnel error for failing to identify the impact for the removal of the neutral lead when preparing and reviewing the work plan. The work plan writer and independent qualified reviewer (IQR) did not consider that the procedural precaution for lifting the neutral lead from the power supply was necessary under the plant configuration at the time of the event. <br /><br /> Work plan writers and IQR will be trained on individual's responsibilities to the requirements of proper review criteria for Modifications work plans and the circumstances of this event. In addition, the BFN's Modifications Training Handbook, will be revised and work plan writers and IQRs will be trained on special precautions implementation.
2601993006 | Browns Ferry 2 | 05/25/1993 | 06/22/1993 | 9306290277 | <strong>Manual Scram After Multiple Intermediate Range Monitors Downscale Indications.</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1993, at 1926, with the reactor critical during startup and power increasing at a 125 second period, multiple intermediate range monitor (IRM) downscales were received while changing from range six to seven. IRM C was returned to range six resulting in a Reactor Protective System half scram. When the control rod was inserted to lower power, the control rod double notched. With the Rod Worth Minimizer (RWM) set for zero insert errors, this double notching resulted in an insert rod block. Due to the IRMs indicating downscale and control rod movement blocked in both the insert and withdraw directions, a manual scram was initiated at 1936 on May 25, 1993. <br /><br /> The multiple IRM downscale readings were due to the lack of any requirement to ensure the IRM transition gain is correctly adjusted at power when changing from the range six to the seven. During the subsequent startup, the RWM setting for insert errors was reset at two and the IRM transition gain was adjusted during the changing from six to seven. TVA will revise the startup procedure and the technical instruction to ensure the IRM transition gain is adjusted to ensure a smoother transition from range 6 to 7. TVA will revise the appropriate startup instructions to ensure the RWM error settings are appropriate.
2601993007 | Browns Ferry 2 | 05/27/1993 | 06/23/1993 | 9306300206 | <strong>Reactor Shutdown Due To Recirculation Pump Seal Leakage.</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1993, at 2015 hours, while operating at approximately eight percent power in the run mode following the BFN Unit 2 refueling outage, the Number 2 mechanical seal for the 2A Reactor Recirculation pump failed and the pump was removed from service. The Limiting Condition for Operation for Technical Specification 3.6.F.1 (TS) was entered which requires the plant be placed in a hot shutdown condition within 24 hours after taking one recirculation loop out of service. At 2225, an orderly plant shutdown was initiated in accordance with TS requirements. On May 28, at 0140, plant shutdown was completed in an orderly manner. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) as a condition that resulted in manual shutdown of the plant required by the plant's TS.<br /><br /> The root cause of the recirculation pump seal failure was due to inadequate procedures. An investigation of this event determined that the pump seal failed due to a small amount of loose particles (e.g., welding related material) collecting in the seal spring packing assembly causing the spring to jam and the seal not to seat properly. To prevent this problem from recurring, TVA revised site procedures to require seal purge flow to be established, to supply water to the seal cavity before opening the recirculation pump isolation valves following maintenance activities.
2601993008 | Browns Ferry 2 | 06/16/1993 | 07/15/1993 | 9307220316 | <strong>LCO For A Turbine Stop Valve Was Exceeded Due To Personnel Error Resulting In A Condition Prohibited By TS.</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1993, at 0637 hours, during the performance of a functional test for the #1 turbine stop valve closure for the reactor protection system (RPS) trip, an anticipated half scram signal was not received when the valve was closed to approximately 90 percent of full open. Operations personnel removed the fuse to the B1 trip relays. However, Operations personnel did not remove the fuse to the A1 trip relay within one hour as required by technical specification. The event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. <br /><br /> The root cause for this event was determined to be personnel error for failing to remove fuses for A1 and B1 RPS relays within the time requirement specified in TS. Namely, Operations personnel did not realize that the limit switch also affected the A1 trip circuit. <br /><br /> A work request to repair the turbine stop valve's limit switch was initiated by a unit operator. Operations personnel removed a fuse to simulate the condition that the valve was closed. Upon further review, Operations personnel concluded that the broken component also affected the A1 RPS trip system and removed the A1 trip system relay fuse. Operations personnel will be required to read this event to ensure a heightened awareness to this unique plant condition. The turbine stop valve and main steam isolation valve divisional surveillance instructions will be revised to include checks of the relays not being tested in the other RPS division.
2601993009 | Browns Ferry 2 | 08/22/1993 | 09/17/1993 | 9309230112 | <strong>Unexpected Group 5 Isolation During Performance of the Reactor Core Isolation Cooling High Temperature Functional Test.</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1993, at 0531 hours, during performance of the Reactor Core Isolation Cooling (RCIC) Steam Line Space High Temperature Functional Test, an unexpected Group 5 Primary Containment Isolation Signal (PCIS) occurred. The Group 5 PCIS resulted from the completion of Unit 2 RCIC isolation logic as a result of having two isolation relays from two separate RCIC logic channels energized simultaneously. The RCIC system was declared inoperable and a seven day Limiting Condition for Operation was entered. During the event, other required emergency core cooling systems were operable. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as an unplanned actuation of an Engineered Safety Feature. <br /><br /> The root cause of the event was personnel error. A lack of self checking by a nonlicensed utility Assistant Unit Operator (AUO) resulted in the AUO mistakenly reporting that an isolation relay had tripped when, in fact, the relay was still energized. <br /><br /> Immediately after RCIC isolation occurred, the test was stopped and an investigation of the cause of the event was initiated. Appropriate personnel corrective action for the involved AUO was taken. This event will be made required reading for nonlicensed and licensed operators.
2601993010 | Browns Ferry 2 | 05/25/1993 | 09/20/1994 | 9409290279 | <strong>A Technical Specifications required surveillance test was not performed due to inadequate procedures and drawings.</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1994, TVA discovered that a test connection valve, which was part of a primary containment boundary, was not tested pursuant to Technical Specifications (TS) 4.7.A.2.g. Specifically, a TS local leak rate test (LLRT) was not performed following maintenance on the valve internals on February 25, 1993, during the Unit 2 Cycle 6 refueling outage. Once the valve's internal parts were replaced, the valve should have had an LLRT prior to establishing primary containment. On May 25, 1993, (the event date of the LER) primary containment for Unit 2 was restored without the LLRT having been performed. Therefore, this event is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant TS. The cause of this event was inadequate documentation regarding primary containment boundaries. Specifically, plant drawings and procedures did not clearly distinguish those components that are part of the primary containment boundary. Applicable drawings and procedures will be revised accordingly. Additionally, Work Order Planners and Work Order personnel have been trained on the criteria for a primary containment boundary.
2601993011 | Browns Ferry 2 | 05/25/1993 | 02/27/1995 | 9503030222 | <strong>An invalid local leak rate test on the drywell head seals resulted in a condition prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1994, during the Unit 2 Cycle 7 refueling outage, TVA was removing the Unit 2 drywell head when it was noticed that a sealant material (i.e., Room Temperature Vulcanizing [RTV]) caused the LLRT performed during the last outage to be invalid. This condition existed when Unit 2 was restarted on May 25, 1993. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by BFN Technical Specifications. The root causes of the event were a result of schedular pressure and a commonly held belief that all engineering requirements will be met by the use of the sealant material. This belief also resulted in the bypassing of approved work practices and in an unquestioning attitude by the personnel involved. Corrective actions to preclude recurrence are: a design change notice was issued controlling the amount of RTV, the drywell head was installed using an approved procedure, an incident investigation (II) of this event was reviewed by the involved individuals, a site-wide bulletin on this eve was issued to emphasize the lessons learned from the II, and an associated notice of violation reply addressing this event was incorporated into the appropriate mechanism for indoctrinating personnel.
2611993001 | Robinson 2 | 02/02/1993 | 03/04/1993 | 9303090470 | <strong>Technical Specification 3.0 Implementation Due To Excessive PPS Leakage</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1993, with H. B. Robinson Unit No. 2 operating at one hundred percent power, it was discovered that total Penetration Pressurization System (PPS) leakage exceeded the rate allowed by Technical Specification 4.4.1. Because Technical Specification 4.4.1 does not contain an action statement, Technical Specification 3.0 was implemented, and an eight hour Limiting Condition for Operation (LCO) was entered. <br /><br /> The cause of the leakage was determined to be a failure of the seal material for the inboard Containment Purge Exhaust Valve V12-9. This event has no adverse impact on plant safety because the Outboard Purge Valve V12-8 remained closed and operable with no seat leakage during the time that seat leakage existed on the V12-9 valve. <br /><br /> The seating surface of the valve was inspected for defects, and none were found. The actuator stop screw on the valve was then adjusted, allowing the valve to close tighter. As a result, the leakage stopped, and the valve was returned to service. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(i) as a condition prohibited by the plant's Technical Specifications.
2611993002 | Robinson 2 | 02/13/1993 | 03/15/1993 | 9303190170 | <strong>Information Report: Exceeding Fire Protection System Action Statement</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1993, with H. B. Robinson Unit No. 2 operating at one hundred percent power, a scheduled Fire Protection System surveillance test was being performed which removed certain Fire Protection equipment from service. Due to personnel error, the equipment was not returned to service within the time allowed by the Technical Specification (TS) Limiting Condition of Operation (LCO), and the compensatory actions required by TS 3.14.6.1 were not in place. Upon discovery, the Shift Supervisor entered TS 3.0 based on the action statement of the TS that had been exceeded, and notified the NRC Operations Center as such. <br /><br /> At the time of this event, CP&L had been authorized to relocate Fire Protection Technical Specifications to the FSAR pursuant to Amendment 142 to the H. B. Robinson Operating License, and a 90-day period for implementation of this amendment was in affect. Although procedures were not yet in place to reflect the amendment, the amendment was effective immediately upon issuance (December 7, 1992). As such, the reporting requirements of 10 CFR 50.73 do not apply. <br /><br /> This report is provided as information to followup the immediate notification made to the NRC Operations Center on February 13, 1993.
2611993003 | Robinson 2 | 04/06/1993 | 05/06/1993 | 9305140252 | <strong>Technical Specification 3.0 Entry Due to Reduced Temperature of Boric Acid Flowpath</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1993, during performance of a routine, daily maintenance surveillance test, it was discovered that the secondary channel of heat trace circuit 25 was inoperable. This circuit is associated with Chemical and Volume Control System (CVCS) piping between the Boric Acid Storage Tanks (BAST) and the Charging Pumps' suction. Although the primary channel of this circuit was functioning and operable, the Technical Specifications (TS) required that a 24 hour Limiting Condition for Operation (LCO) be initiated. As such, the affected heat trace circuit was declared inoperable and the LCO entered at 0558 hours. In order to facilitate troubleshooting and repair of this circuit, it was necessary to remove the insulation pads covering the heat tracing. Although the primary heat trace circuit was operable, the heat loss from the uninsulated piping caused the temperature to decrease below 145 degrees F which is the lower temperature limit for solubility of 13% boric acid solution. Since the secondary heat trace circuit was inoperable, and the primary circuit was unable to maintain the minimum required temperature while the insulation pads were removed, TS 3.0 was entered at 1510 hours on April 6. Subsequently, the insulation pads were replaced, piping temperature was restored to greater than 145 degrees F, and the flowpath was determined to be operable by verifying the flow of boric acid through the affected piping. TS 3.0 was exited at 1901 hours on April 6. Repairs to the secondary heat trace circuit were completed and the 24 hour LCO was exited at 0030 hours on April 7, 1993. As defined within NUREG-1022, including Supplements No. 1 and 2, entry into TS 3.0 is considered to be an operation or condition prohibited by the TS, and is therefore reportable pursuant to 10 CFR 50 .73 (a) (2) (i) (B).
2611993004 | Robinson 2 | 05/12/1993 | 07/14/1993 | 9307220251 | <strong>Unusual Event Caused By Reactor Coolant System Leakage</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER and is being submitted to follow-up on Emergency Notifications made to the NRC Operations Center on May 12, 1993. <br /><br /> At approximately 1725 hours on May 12, 1993, with the H. B. Robinson Unit No. 2 1_/ operating at 100 percent power, the unit entered AOP-016, Excessive Primary Plant Leakage, and a 12-hour to hot shutdown Limiting Condition of Operation (LCO) required by Technical Specifications. The actual leakage rate at 1725 hours was 3.6 gallons per minute (gpm) and at 1812 hours on May 12, 1993, had increased to 11.2 gpm, which required declaration of an Unusual Event due to leakage greater than 10 gpm. At 2113 hours, the leakage was identified as coming from a positive displacement Charging Pump Suction Relief Valve. With the Charging Pump isolated, RCS leakage decreased to less than 1 gpm. The leakage through the 3/4-inch Crosby JRAK-B Relief Valve has been attributed to vibration causing the valve setpoint adjustment to change. Corrective actions will provide additional guidance for tightening the adjusting bolt lock nut. <br /><br /> 1_/ H.B. Robinson Unit No. 2 is a Pressurized Water Reactor in commercial operation since March, 1971.
2611993005 | Robinson 2 | 06/02/1993 | 07/02/1993 | 9307090076 | <strong>Apparent Temperature Violation of the Boric Acid Storage Tank</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER. <br /><br /> At approximately 1840 hours on June 2, 1993, with the H. B. Robinson Unit No. 2 1_/ operating at 100 percent power, an Operability Determination concluded, based on indicated temperatures recorded on a Heat Trace Recorder, that the Boric Acid Storage Tanks (BASTs) had been inoperable due to a portion of the tank volume being below the Technical Specification requirement of 145 degrees F. Testing and investigation determined that the calibration of the recorder was erroneously biased by an ambient temperature compensation made to the millivolt signals injected by the Biddle Versa Cal Calibrator. When the 10 degree correction, resulting from eliminating the erroneous bias is applied to the recorder temperatures originally documented on June 2, 1993, then it is apparent that a Technical Specification violation did not occur. Corrective actions taken and planned include appropriate calibration, adjustment/replacement of equipment. <br /><br /> 1_/ H. B. Robinson Unit No. 2 is a Pressurized Water Reactor in Commercial Operation since March, 1971
2611993006 | Robinson 2 | 07/12/1993 | 08/13/1993 | 9308170102 | <strong>Inadequate EDG Ventilation System Due To Bypassed Air Recirculation Damper</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1993, with H.B. Robinson Unit No. 2 operating at one hundred percent power, the 'A' Emergency Diesel Generator (EGG) Ventilation System Air Return Damper was discovered to have been mechanically positioned partially open with a wooden wedge. Because the dampers should have been closed under the existing outside ambient temperature conditions, the operability of the EGG under accident conditions was questioned. <br /><br /> This condition is attributed to personnel error. Although the condition was bounded and the time frame in which the blockage existed was determined, the source of the wooden wedge could not be determined. Upon discovery of this condition, the wedge block was removed, and the damper automatically closed as designed. <br /><br /> This condition had no impact on safety. Although analyses indicate that the 104 degree F ambient temperature limit of the room would have been exceeded at a design basis day of 95 degrees F, the equipment was not exposed to design limit temperatures, and the blocked damper did not have any effect on the EGG performance life. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(ii) as a condition that was outside the design basis of the plant.
2611993007 | Robinson 2 | 07/30/1993 | 09/30/1993 | 9310050323 | <strong>Ventilation System Outside Design Basis Due To Positive Pressure Condition</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1993, with H. B. Robinson Unit No. 2 operating at one hundred percent power, review of an Operability Determination for the Reactor Building Auxiliary System determined that the system had been operating in a condition outside the design basis of the plant. <br /><br /> At the time this condition was discovered, a modification was in progress which had removed one set of doors serving the building. By this configuration change, an air movement was identified that indicated a negative pressure environment was not being maintained in accordance with the design basis for the building.<br /><br /> The cause of this condition is attributed to inadequate design control in concert with weaknesses in the monitoring of the design requirement to maintain a negative pressure. <br /><br /> Upon discovery of this condition, system flow balancing activities were initiated that re-established a negative pressure condition. This condition was reported to the NRC via the ENS on August 2, 1993, at 2234 hours pursuant to 10 CFR 50.72(b)(1)(ii)(b). This LER is issued pursuant to 10 CFR 50.73(a)(2)(ii) as a condition that was outside the design basis of the plant.
2611993009 | Robinson 2 | 08/05/1993 | 09/03/1993 | 9309160057 | <strong>Tech. Spec. 3.0 Entry For Service Water Pump Operability Testing</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1993, H. B. Robinson was operating at one hundred percent power. At 1045 hours, following performance of Service Water (SW) system surveillance testing, a 24 hour Limiting Condition for Operation (LCO) was entered in accordance with Technical Specification (TS) 3.3.4.2, due to the inability for the 'A' SW Pump to meet the acceptance criteria of the test for flow. TS 3.3.4.2 requires that, with one pump out of service, the remaining pumps be in continuous operation. In order to conduct additional maintenance activities for the 'A' SW pump, the 'B' pump was required to be secured from the service water header. At 1508 hours, the 'B' pump was secured and TS 3.0 was entered in order to conduct troubleshooting activities for the 'A' pump. Following testing, activities were initiated to replace the 'A' pump. On August 6, 1993 at 0812 hours, following replacement activities, the 'B' SW pump was again secured and TS 3.0 was entered in order to conduct post installation testing of the new pump. TS 3.0 was exited at 0840. At 0940 hours, following review and acceptance of the surveillance test data, the 'A' SW pump was declared operable and the 24 hour LCO was exited. <br /><br /> This report is submitted pursuant to 10 CFR 50.73 (a)(2)(i)(B) as an operation in a condition prohibited by Technical Specifications.
2611993010 | Robinson 2 | 08/16/1993 | 09/30/1993 | 9310040367 | <strong>Alert Caused By An Oil Fire On "A" Diesel Generator Exhaust Manifold</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER. At 1509 hours on August 16, 1993, during the performance of OST-401, 'Emergency Diesels Slow Speed Start,' and with the H. B. Robinson Unit No. 2 1_/ operating at 100 percent power, a small oil fire occurred on the exhaust manifold of 'All Emergency Diesel Generator (EDG). The fire was immediately extinguished by the Operator and the Diesel continued to operate for the period of time required by the OST to declare it operable. At 1519 hours on August 16, 1993, an Alert was declared based on a fire with the potential to affect safety-related equipment. The Alert was downgraded and the emergency terminated at 1637 hours on August 16, 1993. The exhaust manifold gasket was found crimped and has been replaced. The gasket installation procedure will be revised to include more specific guidance on installation. <br /><br /> 1_/ H. B. Robinson Unit No. 2 is a Pressurized Water Reactor in commercial operation since March, 1971.
2611993011 | Robinson 2 | 09/27/1993 | 10/27/1993 | 9311020181 | <strong>Potential for Uncontrolled Release Due to Equipment Hatch Seal Leak During Refueling</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1993, H. B. Robinson unit 2 was in cold shutdown condition for a scheduled refueling outage. At 1130 hours, licensee Operations personnel were notified of the existence of minor leakage through the Containment Building Equipment Hatch seal. Technical Specification 3.8.1.a states that the Equipment Hatch must be properly closed for refueling operations. Full core offload had been completed on September 27 at 1120 hours. However, reasonable evidence existed to believe that the leak path existed during fuel movement operations.<br /><br /> The cause of this event is attributed to procedural inadequacy. Procedures for interim Equipment Hatch installation did not provide bolt torquing or sequencing requirements.<br /><br /> The NRC was notified of this event via the ENS on September 27, 1993, at 1521 hours as a condition that alone could have prevented the fulfillment of the safety function of the structures or systems needed to control the release of radioactive material.
2611993012 | Robinson 2 | 10/02/1993 | 10/29/1993 | 9311080081 | <strong>Engineered Safety Feature Actuation At Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1993, H. B. Robinson Unit No. 2 was in cold shutdown condition for a scheduled refueling outage. At 1428 hours, a licensee operator was performing an investigation for a 'B' Emergency Generator (EDG) Trouble Alarm and depressed the 'Local/Remote' switch on the EDG to determine if a faulty switch existed. At this time the 'B' EDG inadvertently started and came up to 900 rpm. Following verification that an undervoltage condition did not exist on Emergency Bus E2, the operator shut the engine down from the Generator Control Panel. The 'EDG-B Trouble Alarm' remained locked in, and the 'B' EDG was declared out of service. <br /><br /> The cause of the inadvertent EDG start is attributed to failure of the 'B' EDG Local/Remote switch. This event had no adverse impact on safety because the EDG was operable when the start signal occurred, and would have been capable of performing its intended function had the signal been from valid source. The Local/Remote switch in both the 'B' and the 'A' Emergency Diesel Generators was replaced. Subsequent testing demonstrated that the new switch functioned properly and as expected. <br /><br /> This event is reportable pursuant to 10 CFR 50.73 (a) (2) (iv) as an event that resulted in actuation of an Engineered Safety Feature.
2611993013 | Robinson 2 | 08/14/1993 | 09/13/1993 | 9309200148 | <strong>Technical Specification 3.10.1.3 Implementation Due To Exceeding Rod</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1993, with H. B. Robinson Unit No. 2 operating at one hundred percent power, a turbine runback occurred during the performance of a surveillance test. Following the turbine runback, Technical Specification 3.10.1.3 was violated for a period of 5 minutes and 15 seconds due to exceeding control rod bank insertion limits as specified in the Core Operating License Report (COLR). <br /><br /> Control Rod Insertion limits were exceeded due to normal plant response to a turbine runback. No operator error or procedural problem occurred to cause this Technical Specification violation. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(ii) as a condition that was outside the design basis of the plant.
2611993014 | Robinson 2 | 10/15/1993 | 11/15/1993 | 9311300121 | <strong>Surveillance Tests Exceeded Technical Specification Test Intervals</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1993, with H. B. Robinson Unit No. 2 in a refueling outage, a Nuclear Assessment Department audit determined that two Engineering Surveillance Tests (ESTs) were performed outside their Technical Specification-required interval. Contrary to the requirement to complete the surveillance test within a six (6) month frequency +/- 25% (184 +/- 46 days), EST-010 was separated by 239 days versus the allowed 230 days. In addition, EST-002 was performed on June 18, 1993, and again on July 30, 1993, separating the testing periods by forty-two (42) days versus the allowed thirty-eight (38) days. Further investigation by Technical Support revealed that an additional surveillance test had been performed outside the required interval.<br /><br /> This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i) as a condition prohibited by the plant's Technical Specifications.
2611993015 | Robinson 2 | 10/12/1993 | 11/10/1993 | 9311160159 | <strong>Pressurizer Pressure Transmitters Out Of Calibration</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1993, with the H. B. Robinson Unit No. 2 1_/ in cold shutdown for Refueling Outage 15, it was determined that the three (3) Pressurizer Pressure Transmitters providing reactor protection functions were out of calibration and in violation of Technical Specifications due to the unavailability of appropriate as-found data. This determination was reached following the evaluation of the data resulting from the refueling calibration performed on September 16, 1993, and September 17, 1993. On October 13, 1993, and again on October 15, 1993, these transmitters were recalibrated to ensure that they were correctly calibrated. The October 13, 1993, calibration found the transmitters to be out of calibration, and the data collected during this calibration could not be used to establish the original as-found data. The cause of the event is attributed to personnel error. Corrective actions include appropriate calibration of the transmitters and additional training in the use of Dead Weight Testers for the work group that performed the calibration.
2611993016 | Robinson 2 | 10/23/1993 | 11/22/1993 | 9312030074 | <strong>Ventilation System Outside Design Basis Due To Positive Pressure Condition</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1993, H. B. Robinson Unit No. 2 was in cold shutdown condition for refueling. ring performance of Operations Surveillance Test OST-411, "Emergency Diesel Generator 'B ' (Twenty Four Hour Load Test)", licensee personnel determined that the EDG Room recirculation damper was not opening as designed. This configuration resulted in the first floor Auxiliary Building hallway being in a positive pressure condition, and therefore outside the design basis of the system.<br /><br /> The cause of this condition is attributed to personnel error. An incorrect wiring configuration for the EDG Room Recirculation Air Damper, HVS-5, was found which prevented the damper from operating. <br /><br /> This event has no adverse impact on plant safety. During the time period that a positive pressure situation existed, the plant was in cold shutdown condition. During the time of testing, no contaminated material was released to the environment which exceeded 10 CFR 20 limits.<br /><br /> This event is reported pursuant to 10 CFR 50.73 (a) (2) (ii) as a condition that was outside the design basis of the plant.
2611993017 | Robinson 2 | 11/11/1993 | 12/10/1993 | 9312150248 | <strong>Degraded Condition Due To Non-Safety Fuses Installed In ESF Application</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1993, H. B. Robinson Unit No. 2 was in hot shutdown condition and preparing for startup from Refueling Outage 15. During a routine review, licensee Engineering personnel discovered that non-safety related fuses had been installed in the 'B' Instrument Inverter. Battery Feeding Instrument, Buses three and eight, which provides power to the High-High Containment Pressure functional unit for Containment Spray. Licensee Operators declared the equipment inoperable at 1130 hours, and a thirty hour to cold shutdown Technical Specification Limiting Condition for Operation (LCO) was entered. On November 11, 1993, at 1849 hours, following an evaluation of the fuses which qualified them for the application, the LCO was exited. <br /><br /> The cause of this is attributed to personnel error. Licensee engineers inappropriately procured non-Q fuses for use in a Q application. The fuses were subsequently installed in the 'B' Instrument Inverter.<br /><br /> This report is submitted pursuant to 10 CFR 50.73 (a) (2) (ii).
2611993018 | Robinson 2 | 11/14/1993 | 12/14/1993 | 9312220331 | <strong>Tech. Spec. Violation Due To Exceeding Ramp Rate During Startup</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1993 while returning H. B. Robinson Unit 2 to power operation following Refueling Outage 15, a significant mismatch occurred between actual reactor power and the Power Range Nuclear Instrumentation indicated power level. With the operating crew belief that the net megawatt output of the plant was at 20% power, the actual power was determined by calorimetric to be 30.26%. This constitutes a Technical Specification violation because the power was increased from 20% to 30% at greater than 3% per hour. This event had no adverse impact on safety. The basis for the Technical Specification ramp rate is to minimize the effects of adverse cladding stresses. During this event, the core was maintained in a safe operating condition, and no fuel damage occurred. <br /><br /> This cause of this event is attributed to ineffective startup procedures and operator training. Appropriate procedure revisions and operator training will be completed prior to start-up from the current outage. <br /><br /> This report is submitted pursuant to 10 CFR 50.73 (a) (2) (i) as a condition prohibited by the plant's Technical Specifications.
2611993019 | Robinson 2 | 11/22/1993 | 02/10/1994 | 9402280007 | <strong>Degraded Condition Due To Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1993, H. B. Robinson Unit 2 was in cold shutdown condition for a forced outage. While performing a scheduled surveillance test for the 'A' Emergency Diesel Generator (EDG), the licensee Control Operator reported that when he field flashed the 'A' EDG, the voltage did not automatically come up to the 480 volts required for operability. The 'B' EDG was then tested, and subsequently failed to start. operable with the plant previously at operating conditions, the plant was considered to have been in a degraded condition at that time. <br /><br /> The cause of the 'A' EDG failure is attributed to a misadjusted automatic voltage control knob on the Generator Control Panel. The primary cause of the 'B' EDG failure is an inadequate test procedure, resulting in damage to the Air Start Distributor. <br /><br /> This event had no impact on plant safety. Calculations have been performed which indicate that, although the 'A' EDG was considered inoperable with the voltage setting below the required value of 480 volts, the safety function would have been met. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(ii).
2611993020 | Robinson 2 | 11/19/1993 | 01/03/1994 | 9401100075 | <strong>Tech. Spec. Violation Due To Exceeding F-Delta-H Hot Channel Factor</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1993, H. B. Robinson Engineering personnel determined that while operating at 30% reactor power prior to shutdown on November 17, 1993, the Technical Specification 3.10.2.1, hot channel factor F-Delta-H limit, was exceeded by 0.36 percent of the Core Operating Limit Report limit value. The reason that the thermal limit was exceeded was that fuel rods in certain assemblies in the core were not loaded as designed which had the effect of accentuating power peaking in the core, causing the thermal limit to be exceeded. A preliminary determination had been made on November 19, 1993, that the Technical Specification limit was exceeded, and the NRC was notified as such at 1440 hours via the ENS. A followup notification was made on December 6, 1993, at 1748 hours to provide the results of the validated calculation. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i) as a condition prohibited by the plant's Technical Specifications.
2611993021 | Robinson 2 | 11/30/1993 | 12/30/1993 | 9401100085 | <strong>TECHNICAL SPECIFICATION VIOLATION DUE TO MISSED CHANNEL FUNCTIONAL TEST</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. The Plant Vent Monitor (RMS-014) is required to have a channel functional test performed on a quarterly basis as listed in the plant's Environmental Monitoring Procedure (EMP-024) and Technical Specifications Table 4.19-2. The quarterly time limit for the channel functional test was exceeded by nine (9) days. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (i) as a condition prohibited by the plant's Technical Specifications.
2611993022 | Robinson 2 | 11/20/1993 | 02/17/1994 | 9403040318 | <strong>Tech. Spec. Violation: Failure To Obtain Hydrogen/Oxygen Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1994, H. B. Robinson management determined that an event which occurred during earlier plant cooldown activities was reportable. <br /><br /> On November 19, 1993, H. B. Robinson Unit 2 was in hot shutdown condition. Reactor Coolant System degassing activities had been initiated at 0045 hours. Technical Specifications require that the Waste Gas Decay Tank be sampled once per four hours when the Gas Analyzer is out of service and degassing is in progress. During a period between November 19, 1993, and November 20, 1993, when the Gas Analyzer was out of service, five required samples were not collected. <br /><br /> This event was caused by failure to follow Chemistry sampling procedures. <br /><br /> The individuals involved have been counseled, and procedures are being revised to provide additional prompts for increasing sample frequency when changes in plant condition warrant. This event had no adverse impact on Plant safety. The routine samples taken during the time when degassing was in progress demonstrated that the Waste Gas Decay Tank gas mixture remained within Technical Specification requirements. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i) as a condition prohibited by the plant's Technical Specifications.
2631993001 | Monticello | 01/29/1993 | 03/01/1993 | 9303080037 | <strong>Potential Single Failure of Standby Gas Treatment Room Heater Could Cause Temperatures Above Equipment Ratings for Both Standby Gas Treatment Trains</strong><br /><i>Abstract:&nbsp;</i>During the performance of a design bases review, a potential single failure was identified that could affect both trains of the Standby Gas Treatment System. A failure of an electric room heater to de-energize would cause elevated room temperatures. The cause of this event was design error. Operating procedures were modified to detect and cope with a malfunctioning Standby Gas Treatment room heater during accident conditions. The 'All train-room heater was disabled to prevent a failure of the heater to de-energize and the 'A' train thermostat was set to provide remote indication of a Standby Gas Treatment room over temperature condition. A Safety Evaluation was completed for operation of Standby Gas Treatment with the above corrective action in place. A modification will be completed to eliminate the potential single failure of the room heater.
2631993002 | Monticello | 01/31/1993 | 03/02/1993 | 9303090218 | <strong>Closure of Primary Containment Isolation Valves Caused by Reactor Protection System Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>With the plant in a refueling outage, a failure of a Reactor Protection System breaker resulted in the closure of several primary containment isolation valves. Additional actions which resulted were initiation of Standby Gas Treatment, isolation of Reactor Building Ventilation, and tripping of the Reactor Protection System. The cause of the breaker failure was high breaker contact resistance. The isolation was verified, the breaker was replaced, the isolation was reset, and Standby Gas Treatment and Reactor Building Ventilation were returned to normal. All similar breakers in the same division of the Reactor Protection System were visually inspected, electrical terminations were verified to be tight and a thermal scan for signs of over heating was performed. These same inspections will be performed for similar breakers in the other division of the Reactor Protection System prior to startup from this refueling outage. These Reactor Protection System breakers will be placed on the preventive maintenance schedule.
2631993003 | Monticello | 01/31/1993 | 10/26/1993 | 9311020148 | <strong>Main Steam Isolation Valve Local Leak Rate Exceeded</strong><br /><i>Abstract:&nbsp;</i>Main Steam Line Isolation Valve leak rate tests conducted during a refueling outage determined that the Technical Specification leakage limit for individual valves was exceeded. The causes included changes in test methodology, wear, thermal creep and aging, seat pitting from original manufacturing, and friction effects related to valve design and orientation. All failed valves were machined/lapped and repaired as needed. Samples of an oxide film found on the valve seats were analyzed and the results indicated normal coolant concentrations. The valves were re-tested with satisfactory results. Long-term modifications and repairs are being evaluated to address issues related to design and original manufacture.
2631993004 | Monticello | 03/10/1993 | 04/08/1993 | 9304130217 | <strong>Primary Containment Isolation Caused by Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1993, several Primary Containment isolation valves closed during the performance of post modification testing. The cause was a blown fuse in the isolation logic. The blown fuse was most likely caused by modification activities conducted during the outage. The test was stopped, the cabinet was inspected, the fuse replaced, the isolation reset and Shutdown Cooling returned to service.
2631993005 | Monticello | 02/15/1993 | 04/14/1993 | 9304200210 | <strong>Bus Transfer Due to High Diesel Generator Voltage Caused By Inadequate Information</strong><br /><i>Abstract:&nbsp;</i>While in cold shutdown for a refueling outage, the 480 Volt LPCI (Low Pressure Coolant Injection) Swing Bus transferred to the alternate power supply during the once per cycle simulated automatic actuation test of the Emergency Core Cooling Systems. The LPCI swing bus transferred due to a sensed over-voltage condition on the primary power supply. The cause of this event was lack of adequate detailed information concerning the Emergency Diesel Generator voltage regulator and governor characteristics which lead to inadequate voltage setting. The LPCI Swing bus was transferred back to the normal power source, the Emergency Diesel Generator surveillance procedure was revised, and additional information on operation of the voltage regulator has been obtained and included in the Emergency Diesel Generator technical manual. This is a voluntary report submitted because of possible generic interest.
2631993006 | Monticello | 03/23/1993 | 06/09/1993 | 9306170076 | <strong>Reactor Protection System Actuation From High Pressure Caused By Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>During startup from a refueling outage a Reactor Protection System trip from high reactor pressure occurred. The trip occurred while performing the main turbine Stop Valve tightness test. The cause of the event was an inadequate procedure. Contributing factors were inadequate knowledge by the individuals involved in the procedure revision, incorrect simulator modeling and an inadequate vender technical manual procedure. During the event one control rod scram solenoid failed to operate resulting in a slow rod insertion time. The Turbine Stop and Control Valve Tightness Test procedure has been revised. The plant simulator was modeled to reflect actual operation. The failed scram solenoid pilot valve was replaced and all scram solenoid pilot valves were verified to function properly. This event and the lessons learned from the event will be presented in Engineering Technical Staff Continuing Training and License Operator Requalification training. The vendor technical manual on pressure control will be revised.
2631993007 | Monticello | 06/04/1993 | 07/06/1993 | 9307130189 | <strong>ESF Actuation Caused By Loss of Reactor Protection System Power Supply</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1993, a time delay relay coil in the Division II Reactor Protection System (RPS) Motor Generator failed causing a loss of the Division II RPS power supply. The loss of power resulted in a half scram, Reactor Building Ventilation isolation, Standby Gas Treatment System initiation and closure of eight primary containment isolation valves. The cause of the relay failure is unknown. The relay was replaced and the Motor Generator Set was returned to service on June 4, 1993. A search was completed to identify the use of other relays of this type in the plant. The Reactor Protection System Motor Generator preventive maintenance procedure will be revised to ensure periodic replacement of the failed relay coil.
2631993008 | Monticello | 07/31/1993 | 06/15/1995 | 9506290062 | <strong>Reactor Protection System Actuation From Low Reactor Water Level Caused by Main Condensate Pump Trip</strong><br /><i>Abstract:&nbsp;</i>During normal full power operation a Reactor Protection System trip from low reactor water level occurred. The Standby Gas Treatment System and several containment isolation groups were also initiated on low reactor level. Normal post trip procedures were followed to restore stable conditions. One condensate and one feedwater pump remained in operation during the event. Level remained well above the ECCS initiation setpoint. There were no failures or other complications. The immediate cause was a reduction in reactor feedwater flow due to a ground fault relay trip of a main condensate pump. motor stator. The motor will be rewound or scrapped.
2631993010 | Monticello | 10/27/1993 | 11/23/1993 | 9312020510 | <strong>Main Control Room Emergency Filtration Train Outside Design Basis Caused by In-leakage Across Inlet Dampers</strong><br /><i>Abstract:&nbsp;</i>At 1500 on October 27, 1993, 1300 hours, while operating at 100% rated thermal power, both trains of the Control Room Ventilation-Emergency Filtration Train (CRV-EFT) system were declared inoperable. It was determined after the completion of an evaluation that the in-leakage across the outside air inlet isolation dampers could exceed the amount assumed in the control room operator radiation dose and toxic chemical calculations. The cause of this event was failure to identify and establish all the inspections/tests needed to insure that system operability would be maintained. A contributing cause was the low priority assigned for completion when it was identified that testing and inspection of the dampers should be performed. Both CRV-EFT trains have been modified to eliminate the outside air in-leakage, a Safety Evaluation was completed, a License Amendment Request to remove the Chlorine detection Technical Specification requirements had been initiated, a review of the Operating Events Tracking System assignments was completed, and Control Room dose and toxic gas calculations were performed. This event will be presented in Engineering Technical Staff Continuing Training, preventive maintenance/test procedures will be developed, and the Operating Experience Assessment process will be revised.
2651993001 | Quad Cities 2 | 01/07/1993 | 02/04/1993 | 9302120156 | <strong>Reactor Flux Scram While Transferring "B" RPS To Dirty Power From 2-203-2A Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1993, Quad Cities Unit Two was in the Run mode at 100 percent of rated core thermal power. At 1008 hours, Reactor Protection System (RPS) Bus B was being transferred to its alternate power supply in preparation for the semi-annual testing of the RPS Electrical Protection assemblies (EPA) units. When the breaker for the RPS Bus B was opened the 2-203-2A Main Steam Isolation Valve (MSIV) closed causeing the reactor flux and pressure to exceed the scram setpoints. All safety feature actuations occurred as designed. An Emergency Notification System (ENS) notification was completed at 1205 hours on January 7, 1993. <br /><br /> The cause of the 2 -203-2A MISV closing during the transfer of the B RPS Bus is attributed to the failure of the DC solenoid coil on the MSIV manifold assembly. Corrective actions will include proposed changes to the Technical Specifications and changes to QOP 7000-1, Reactor Protection System MG Sets. <br /><br /> This reports is being submitted to comply with 10CFR50.73(a)(s)(iv).
2651993002 | Quad Cities 2 | 01/13/1993 | 02/11/1993 | 9302170330 | <strong>HPCI Inoperable Due To Dirty Contacts That Are Causing MSC Switch To Fail</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993, at 0100 hours, Unit Two was in the RUN mode at 7 percent rated core thermal power. At this time, the NSO was completing the high pressure testing portion of QCOS 2300-1, Periodic HPCI Pump Operability Test. The NSO tripped the turbine and noticed that the motor speed changer (MSC) light indication remained lit at the high speed stop (HSS). HPCI was declared inoperable and the HPCI outage report was initiated retroactive to 0100 hours. It was determined the MSC pressure switch, 2-2341-10 PS, was not working correctly. IM cleaned the switch's contacts under Nuclear Work Request Q05243, and at 0307 hours on January 14, 1993, HPCI was successfully tested. The outage report was terminated. <br /><br /> The cause of this event is due to dirty contacts for the MSC pressure switch, 2-2341-10 PS. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(v)(D). DVR 359
2651993003 | Quad Cities 2 | 01/11/1993 | 02/10/1993 | 9302170289 | <strong>Loss of HPCI Control Light Indication Due To Cocked Saddle On Terminal Block</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1993, at 2330 hours, Unit Two was in the SHUTDOWN mode at 0 percent rated core thermal power. At the start of the shift, the Unit Two NSO had started a surveillance check of the control room panels. At this time, the NSO discovered no light indication existed for the HPCI Motor Gear Unit (MGU), Motor Speed Changer (MSC), and Stop valve. Electrical Maintenance (EM) personnel were notified and Nuclear Work Request #Q05233 was initiated. HPCI was not required to be operable per Technical Specifications and was already isolated due to a low reactor pressure isolation. EM determined the loss of power was due to a cocked saddle which did not allow the wire and terminal to make proper contact. The saddle was straightened and Work Request Q05233 was closed out. <br /><br /> The cause of this event is from a cocked saddle on the terminal block AA, fuse f-12.<br /><br /> Corrective actions included Operating verifying the fuses and feedbreakers on the HPCI system did not create an open circuit and EM straightening the cocked saddle for three fuses. <br /><br /> This report is being submitted to comply with 10CFR50(a)(2)(v)(D).
2651993004 | Quad Cities 2 | 01/14/1993 | 02/27/1993 | 9303100035 | <strong>Missed Off Gas Recombiner Technical Specification Surveillances (4.8.A.5) Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1993 at 0100 hours, Unit Two was in the RUN mode at 74 percent of rated core thermal power. The shift one Nuclear Station Operator (NSO) noticed that the recombiner temperatures had not been verified to be in the allowable band during the previous four shifts as required by Technical Specification 4.8.A.5. <br /><br /> The missed surveillance was caused by personnel error with inadequate procedures as a contributing cause. The Nuclear Station operators confused two different Off Gas system surveillance requirements when they assumed that the recombiner temperatures did not have to be verified while the reactor was at less than thirty percent of rated core thermal power. <br /><br /> This event will be tailgated with all operating personnel. Procedures and surveillance sheets used to verify that the recombiner temperature was within limits will also be revised. <br /><br /> This report is being written in accordance with 10CFR50.73(a)(2)(i)(b): The licensee shall report any operation or condition prohibited by the plant's Technical Specifications.
2651993005 | Quad Cities 2 | 01/29/1993 | 02/26/1993 | 9303040140 | <strong>ESF Actuation from Spurious High Reactor Pressure due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>At 1340 hours on January 29, 1993, Unit Two was in the RUN Mode when a full SCRAM occurred. <br /><br /> The SCRAM was initiated by a spurious high reactor pressure signal. The indicated reactor pressure was normal for plant operations. The apparent cause is due to a contractor accidentally bumping the reactor high pressure switches' common sensing line while performing the Reactor Vessel Water Level Indicating System modification work. <br /><br /> This event will be tailgated with groups performing work in the plant to enhance personnel awareness of the sensitivity of the reactor high pressure switches and their associated sensing lines.
2651993006 | Quad Cities 2 | 03/06/1993 | 04/01/1993 | 9304120009 | <strong>Unit Two Manual Reactor Scram Due To 3E Relief Valve Failure To Close</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1993, Unit Two was in the RUN mode at 71% of rated core thermal power. At 2019 hours, the 2-203-3E Electromatic Relief Valve (ERV) [RV] failed to close during routine testing. At 2021 hours, the reactor [RCT] was manually scrammed per procedure and the relief valve reseated on its own at 193 psig reactor pressure. The Unit was in cold SHUTDOWN at 0112 hours on March 7, 1993. During a Drywell inspection it was discovered that the leakoff line from the 2-203-3E ERV was sheared off where it attaches to the 8 inch discharge header. NRC notification was completed at 2156 hours on March 6, 1993 per 10 CFR 50.72(b)(2)(ii). <br /><br /> Investigation revealed that the cause of the event was component failure. The pilot valve seat bushing had severe steam cutting. The fractured leakoff line piping is being sent off site for failure analysis. This ERV will be replaced with an overhauled valve during the current refuel outage and it will be tested along with all of the other relief valves during reactor startup.<br /><br /> This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv).
2651993007 | Quad Cities 2 | 03/07/1993 | 06/28/1993 | 9307070185 | <strong>B Loop Main Stream Isolation Valve Exceeded Technical Specification Leakage Limits For Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During performance of combined Local Leak Rate Test of the 'B' loop MSIV's, the leakage exceeded the 11.5 scfh Tech Spec limit of T.S. 3.7.A.2.e. The measured leakage was 89.32 scfh. This report is being submitted to comply with 10 CFR 50.73 (a)(2)(ii)(B). DVR 466
2651993008 | Quad Cities 2 | 04/02/1993 | 04/28/1993 | 9305060217 | <strong>Recirc Pipe 2-0209B" Has Through Crack Due To Probable Weld Defect</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1993, Quad Cities Unit Two was shut down to begin the twelfth refueling and maintenance outage. On March 31, 1993, with the reactor mode switch in SHUTDOWN, a visual inspection revealed a Recirculation weld area (ISI Weld 02-F2B) with water seeping from a small crack. The exact cause of the crack indication has not been determined but it is being postulated to come from either a weld defect, a crevice assisted Intergranular Stress Corrosion Crack (IGSCC) or from high cycle vibration fatigue. Corrective actions for this situation will be to apply a weld overlay, to allow continued operation for one fuel cycle. If an inspection technique cannot be developed to reliably examine the weld overlay, the area will be repaired next outage. This report is being submitted to comply with the requirements of 10CFR50.73(a)(2)(ii), which requires the reporting of any event or condition that resulted in the condition of a nuclear power plant, including its principal safety barriers, being seriously degraded.
2651993009 | Quad Cities 2 | 04/08/1993 | 05/07/1993 | 9305140176 | <strong>Missed Tech Spec Surveillance To Estimates Sample Flow on Rx Building Vent Samples Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993, at 0900 hours, Unit Two (U2) was in the REFUEL mode. A Chemistry technician was conducting his normal rounds when he realized he had failed to estimate sample flow at 0700 hours for the U2 reactor building vent sampler [FLT] [IL]. The U2 reactor building vent sampler flow rate monitor [FI] [IL] had been inoperable since 0530 hours on March 11, 1993, due to modification M04-2-87-051B. The technician went immediately and estimated sample flow. He reported the event to his supervisor who informed the SE. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(b), which requires the licensee to report any operation or condition prohibited by the plant's Technical Specifications. The cause of the event was personnel error. The technician forgot to perform the surveillance at 0700 hours. The technician was counseled by Chemistry Supervision on the importance of properly completing all Technical Specification required surveillances.
2651993010 | Quad Cities 2 | 04/22/1993 | 05/18/1993 | 9306010156 | <strong>1/2 Diesel Generator Cooling Water Pump Failure To Start Due To Original Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1993, at 1322 hours, Unit Two was in the SHUTDOWN mode at 0 percent of rated core thermal power. At that time, Technical Staff personnel were performing 4kV Bus 23-1 Undervoltage Functional Test, QOS 6500-4. During performance of this surveillance the 1/2 Diesel Generator Cooling Hater Pump (1/2 DGCWP) failed to start as required. An Emergency Notification System (ENS) notification was completed at 2145 hours on April 22,1993. <br /><br /> The root cause for the 1/2 DGCWP failing to start is a design deficiency in the Bus 28 breaker close logic that has existed since the plant was originally designed. This deficiency causes the breaker to lockup following an undervoltage condition. The design deficiency has also existed on the Bus 18 breaker control logic since the installation of modification M04-1/2-83-014 in 1985. However, the lockup on Unit One would only occur if the power selector switch was in the Bus 18 position. Corrective actions included a modification to add an undervoltage contact in the Bus 28 close logic to the 1/2 Diesel Generator Cooling Water Pump<br /><br /> This report is being submitted to comply with 10CFR50.73 (a)(2)(ii)(B). DVR 433
2651993011 | Quad Cities 2, Quad Cities 1 | 06/02/1993 | 07/02/1993 | 9307120082 | <strong>HPCI Inoperable Due To Slow MSC Ramp Time During QCOS- 2300-13</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1993, at 1740 hours, Unit Two was in the RUN mode at 72 percent rated core thermal power. Prior to this, HPCI was declared inoperable in order to perform QCOS 2300-13. HPCI was initiated and reached required flow of 5000 gpm in 52 seconds. Because the time exceeded the acceptable limit, HPCI was declared inoperable. It was determined the MSC gearbox was creating a binding problem, thus causing the MSC to ramp at a slower rate. The integral setting of the HPCI flow controller was changed to compensate for the slower MSC response time. On June 4, 1993, at 1530 hours, HPCI was successfully tested and the outage report terminated. On June 30, 1993, during a maintenance outage, the MSC gear box was dissassembled and inspected. The gearbox's stem, stem gear, and thrust washers were found to be scored and worn. <br /><br /> The cause of this event is due to the MSC stem and stem gear being scored and worn from age causing excessive friction in the stem and stem gear connection. <br /><br /> Short term corrective actions include repairing or replacing the stem, stem gear, and thrust washers. Long term actions include dissassembling the MSC gearbox every 10 years and timing the Unit One and Two MSC's during each refuel cycle. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(ii)(B).
2651993012 | Quad Cities 2 | 06/01/1993 | 06/30/1993 | 9307070189 | <strong>U-2 Diesel Generator Cooling Water Pump Inoperable.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 hours on June 1, 1993,Unit 2 was in the run mode at approximately 7 percent of rated core thermalpower. CECo concluded on June 1 through review of available information that the U-2 Diesel Generator [DG] Cooling Water Pump (DGCWP) [P] was inoperable during the period from February 16 to March 15, 1993. <br /><br /> The Unit 2 DGCWP was inoperable from February 16 to March 15 due to incorrectly assembled due to inadequate training on how to set and position this type of oiler. <br /><br /> Corrective actions include replacing the U-2 DGCWP, walkdowns to verify the adequacy of drawings/instructions used by Operations and Maintenance, and ensure proper installation of oilers and sightglasses on other plant equipment. Operations and Maintenance personnel, revision of maintenance lesson plans, and communication of lessons learned to other CECo facilities. A self-assessment was also chartered to look at craft capability, work package detail and other maintenance practices.
2651993013 | Quad Cities 2 | 06/13/1993 | 07/13/1993 | 9307210005 | <strong>Reactor Scram From Turbine/Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1993 at approximately 0624 hours, Unit 2 was in the RUN mode at 57% power when an internal electrical fault within the Unit 2 Main Power Transformer resulted in an automatic generator trip. The Main Turbine tripped and caused a reactor scram due to turbine stop valve closure. All safety features functioned as designed, however an unexpected Group I isolation occurred immediately following the turbine trip. An Emergency Notification System (ENS) call was completed at 0726(CST) on June 13, 1993, to comply with the requirements of 10CFR50.72(b)(2)(ii). <br /><br /> The transformer was determined to be damaged beyond repair and was determined to be damaged beyond repair and was replaced with a new ABB transformer. The Group I isolation was determined to be caused by pressure fluctuations caused by the rapid closure of the main stop valves following the turbine trip. A modification to eliminate the spurious Group I has been designed and is scheduled to be implemented during Q2R13 and Q1R14.
2651993014 | Quad Cities 2, Quad Cities 1 | 08/11/1993 | 09/10/1993 | 9309200070 | <strong>U-1 And U-2 HPCI Systems Outside Design Basis When Lines Are Found To Be Inadequately Supported.</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1993, Unit 1 was in the RUN mode of operation at 98 percent of rated core thermal power and Unit 2 was in the RUN mode of operation at 79.8 percent of rated core thermal power. During a walkdown of Unit 1 and Unit 2 High Pressure Coolant Injection (HPCI) systems, it was determined that line numbers 2-2359-2 1/2'G, 1-2389-1/2'-A, 1-2390-1/2'-A, 1-2391-1/2'-A, 1-2395-1/2'-A and 1-2398A-1/2'-LX may not have been adequately supported. On August 8, 1993, Site Engineering Services Request (SESR) #4-1623 was submitted to evaluate this condition. <br /><br /> Sargent and Lundy (S&L) calculations (EMD-067697 and EMD-067759) demonstrated that even though the lines were outside the UFSAR allowable seismic design stress limits, the lines would not be subject to catastrophic failure because the lines did not exceed the UFSAR seismic design yield stress limits and therefore the system was determined to remain operable. <br /><br /> The apparent cause of this event for the HPCI turbine oil reservoir line is due to an inadequate 1983 design review process. The apparent cause for the HPCI instrument lines could not be determined. <br /><br /> Design resolution for instrument line numbers 1-2389-1/2'-A, 1-2390-1/2'-A, 1-23911/2'-A, 1-2395-1/2'-A and 1-2398A-1/2'-LX was completed on August 23, 1993. Design resolution for line number 2-2359-1/2'-G was completed on September 1, 1993.
2651993015 | Quad Cities 2 | 08/15/1993 | 09/14/1993 | 9309210170 | <strong>U-2 HPCI Declared Inoperable When the Drain Pot High Level Alarm Came In And Would Not Clear</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1993, Unit 2 was in the RUN mode of operation at 100 percent of rated core thermal power. At 0545 hours the control room received the 'HPCI TURBINE EXH DRAIN POT LEVEL' alarm during the performance of QCOS 2300-1, Periodic High Pressure Coolant Injection Pump Operability Test. The test was aborted without rolling the HPCI turbine. The operating crew was not aware that Interim Procedure #193 which was a temporary procedure for HPCI pump testing existed due to a procedural inadequacy. At 1200 hours during performance of Interim Procedure #193, HPCI Quarterly and Periodic Pump Operability Test, the control room received the 'HPCI TURBINE EXH DRAIN POT LEVEL' alarm. Slow starts of the HPCI pump lead to a build-up of condensate in the exhaust drain system during chest warming and HPCI pump cooldown. At 1205 hours the HPCI system was put into a standby line-up and declared inoperable.<br /><br /> On August 16, 1993, The HPCI exhaust drain system was drained and the test procedure was revised to reduce the overall time to get to full rated flow and speed. test was performed using the new procedure and the HPCI system was declared operable.<br /><br /> Corrective actions will be to revise the licensed and non-licensed operating lesson plans to provide a detailed narrative explanation of the HPCI drain system and change the procedure for processing interim procedures to ensure multiple notification sheets are completed for an IP change that affects multiple procedures.
2651993016 | Quad Cities 2 | 08/14/1993 | 09/13/1993 | 9309210308 | <strong>Uncontrolled Access To High Radiation Area Caused By Inappropriate Personnel Action</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1993 at 0257 hours, Unit One was in the RUN mode at 100 percent rated core thermal power. While checking the status of Locked High Radiation Area (LHRA) access doors during routine plant duties, a Radiation Protection Technician (RPT) found an LHRA door to the main condenser area of the Turbine Building (TB) unlocked and unattended. <br /><br /> Station procedures require that all applicable high Radiation area doors and barriers be locked (and verified locked), while unattended. The failure to perform this action and verification was an inappropriate worker action. The RPT controlled access to the door until a key was obtained. The lock and door worked properly (verified) and the door was re-locked. All other TB LHRA doors were immediately checked and verified locked.<br /><br /> As an interim surveillance measure, the Health Physics (HP) Department performed daily verifications that all locked High and Very High Radiation area (LVHRA) door locks and padlocks were secure. Additional corrective actions to reduce the probability of recurrence will be implemented.
2651993017 | Quad Cities 2 | 08/24/1993 | 09/23/1993 | 9309290103 | <strong>Inadequate Safe Shutdown Fire Watch Performed For The U-2 MSIV Room</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in the RUN mode at approximately 97% of rated core thermal power. Compensatory once per hour firewatch inspections were required due to inoperable Safe Shutdown (SSD) systems. Compensatory measures included surveillance of the Main Steam Isolation Valve (MSIV) [SB] room in each Unit by using a remote camera [TVC]. However, because the Unit 2 MSIV room camera had been inadvertently removed, a once per hour physical inspection was being performed. On 08/24/93, it was determined that the MSIV room inspection was not being performed in accordance with the requirements of the SSD analysis. <br /><br /> The primary Causal Factors of this deficiency can be attributed to inappropriate WORK PRACTICES, ineffective VERBAL COMMUNICATIONS and INTERFACE DESIGN CONTROL and inadequate TRAINING/QUALIFICATION. <br /><br /> At 1700 on 08/24/93, a camera was re-installed and hourly inspections commenced. Additionally, all firewatches have been instructed to immediately notify Operating Shift Management of camera unavailability and a formal process for control of cameras will be implemented.
2651993018 | Quad Cities 2 | 08/28/1993 | 03/29/1994 | 9404040155 | <strong>Failure Of MOV 1301-61 Due To Broken End Bell Tie Bolts</strong><br /><i>Abstract:&nbsp;</i>At approximately 1605 on 08/28/93, Unit-2 was in the Run mode at approximately 97 rated core thermal power. Operations was informed by System Engineering that Diagnostic Evaluation Team (DET) members had found bolts broken on Reactor Core Isolation Cooling (RCIC) [BN] valve 2-1301-61. Investigation revealed two of four Motor Operated Valve (MOV) [ISV] motor end bell tie bolts were completely broken due to shear. The RCIC system was declared inoperable at 1640, August 28, 1993. <br /><br /> The root cause for the RCIC 2-1301-61 MOV broken motor end bell tie bolts was not determined. Possible causes investigated were Written Communication, Change Management, Design and Configuration Analysis, Equipment Specification, Manufacture & Construction, Maintenance and Testing. <br /><br /> Corrective actions completed were to replace the remaining Porter/Peerless Class 8, DC MOV motors of 25 pounds with an improved motor, testing the failed bolts, and performing an operability evaluation on remaining valves of similar manufacturer and model. A documented review of the Station trending program will be initiated to evaluate how the program failed to identify an adverse trend associated with these motors.
2651993019 | Quad Cities 2 | 08/31/1993 | 09/29/1993 | 9310050046 | <strong>Main Steamline Rad Monitor Inoperable For An Extended Period Of Time With No 1/2 Scram Or 1/2 Group I Isolation In Place.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0830 on 08/30/93, Unit 1 and Unit-2 were in the Run mode at about 96 percent power. Operations was coordinating with System Engineering in preparation for Hydrogen Water Chemistry Stress Corrosion Monitoring Test (Special Test 2-108 Rev. 0). This test was to add hydrogen to the feedwater for the purpose of reducing oxygen in the Reactor Vessel. This test would increase the Main Steam Line (MSL) Radiation above the normal levels. The setpoint of the MSL Log-Rad Monitors were to be raised to 1500 Units for the Alarm setpoint, and 2250 Units for the SCRAM setpoint using a setpoint adjustment procedure. While performing the setpoint adjustment procedure, the 2-1705-2B MSL Radiation monitor was placed in the INOP MODE at 0345. At 1110, August 31, 1993 the A & B monitor setpoints were being returned to normal (as required by special test 2-108) when the Systems Engineer realized the channel 2B MSL Log-Rad Monitor had been inoperable for approximately 7 Hours and 25 Minutes. The monitor was returned to normal operation at 1135.<br /><br /> The causes of this event were Written Communication and Managerial Methods.<br /><br /> A procedure has been written governing the length of time that a Technical Specification instrument can be inoperable. In addition, the System Engineers will receive training on the procedure governing Special Tests and Experiments.
2651993020 | Quad Cities 2 | 09/01/1993 | 10/01/1993 | 9310080275 | <strong>Continuous Fire Watch Missed For The Hydrogen Seal Oil And Turbine Seal Oil Tank Deluge System</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in the RUN mode at approximately 89% of rated core thermal power. At 0200 on 8/31/93, a ground [GBU] on the 125 Volt Direct Current (VDC) system [EI] on Unit 1 was reported. Between 0257 and 0438, while performing ground isolation checks, a switch [HS] which controls power to various Unit 2 Fire Protection (FP) Deluge valves [KP], was operated. At 0438, this switch was inadvertently left open (although not detected), which disabled the FP valves (for greater than one hour), which does not meet requirements of the Fire Protection Program. <br /><br /> The primary Causal Factor (C/F) of this event was an inappropriate WORK PRACTICE; contributing C/F's include ineffective WRITTEN COMMUNICATIONS (procedure) and inadequate TRAINING/QUALIFICATION. <br /><br /> At 2333 on 8/31/93, the degraded FP condition was noted and compensatory firewatches were established. The open switch, which caused the problem, was identified and reclosed at 1042 on 9/1/93. The ground isolation procedure will be revised and Operators will receive additional training on the interpretation of FP system alarms.
2651993021 | Quad Cities 2 | 08/24/1993 | 09/23/1993 | 9407060133 | <strong>U-1 Diesel Generator Relay, Metering Panel and Excitation Cabinet Not Attached To The Floor</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in the RUN mode at 95% power on 08/24/93 at 1730 hours at which time the Unit 2 Emergency Diesel Generator (EDG) [DG] Relay and Metering Pan el [PL], and Excitation Cabinet [CAB] were found to be not seismically attached to the structure. <br /><br /> The primary causal factors of this deficiency are inadequate WRITTEN COMMUNICATION and EQUIPMENT SPECIFICATION, MANUFACTURE AND CONSTRUCTION.' <br /><br /> The Unit 2 EDG was declared inoperable at 1910 hours on 08/24/93. The Relay and Metering Panel, and Excitation Cabinet on both the Unit 1 EDG and Unit 1/2 EDG were verified to be secured to the structure. After repairs, the Unit 2 EDG was declare operable at 0650 hours on 08/26/93.
2651993022 | Quad Cities 2 | 10/07/1993 | 11/02/1993 | 9311120187 | <strong>ECCS Room Floor Drain Check Valves Inoperable</strong><br /><i>Abstract:&nbsp;</i>Each event occurred on Unit 2 while in the RUN mode at 97% of rated thermal power. At 0925 on 10/07/93, the 2B Core Spray (CS)/Reactor Core Isolation Cooling (RCIC) [BN] system room drain valve [LCV] to the Reactor Building [NG] Floor Drain Sump (RBFDS) [WK] failed the quarterly leak test. At 1515 on 10/11/93, debris was found in the RCIC bedplate drain check valve, which created a flooding pathway into the room. <br /><br /> Primary Causal Factors include inadequate DESIGN CONFIGURATION for the 10/07/93 event and MANAGEMENT/SUPERVISORY METHODS and WRITTEN COMMUNICATIONS in both events, because foreign materials intruded into the drain valves. <br /><br /> All flowpaths, from the RB basement to the ECCS rooms (on both Units), were plugged. Existing float-operated ECCS room drain valves will be removed and replaced with manual isolation valves; flooding flowpaths will be administratively controlled. Bedplate drains will be re-routed to floor drains inside ECCS rooms. Foreign material exclusion controls will be strengthened.
2651993023 | Quad Cities 2 | 12/09/1993 | 01/07/1994 | 9401250269 | <strong>1/2 Emergency Diesel Generator Inop To Bus 23-1 With A Loss Of TB Bus 1A Due To A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 12/9/93, Unit Two (2) was in a planned maintenance outage, Q2M11, Reactor [RCT] thermal power was at zero percent with the Reactor mode switch in SHUTDOWN. During a review of the Electrical Load Monitoring System (ELMS), it was determined that should a Loss of Offsite Power (LOOP) occur concurrent with a Loss of Cooling Accident (LOCA) and a single failure of the 125 VDC Turbine Building (TB) Bus 1A [BU,EJ], Unit 2 would be without an Emergency Diesel Generator (EDG)[EK]. This scenario placed Unit 2 in an unanalyzed condition that had the potential to significantly compromise plant safety. However, the probability of this event occurring was minimal and the consequences of this event would have been reduced due to operator training. <br /><br /> The primary causal factor of this deficiency is DESIGN CONFIGURATION and ANALYSIS. The design deficiency has existed as part of the original plant design. <br /><br /> A modification has been completed that allows the 1/2 EDG to auto-load to Bus 23-1 with a loss of TB Bus 1A.
2651993024 | Quad Cities 2 | 12/02/1993 | 12/23/1993 | 9407060116 | <strong>Unit Two Reactor Scram Due To Low Level Signal</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1993, two Instrument Maintenance (IM) Technicians were performing Quad Cities Instrument Surveillance (QCIS) 200-1. Quarterly Reactor (Rx) High Pressure SCRAM Calibration and Functional Test on Unit 2 High Rx pressure switch (PS) 63! 2-263-55A. The Control Room received a Unit 2 Rx Low Level SCRAM. It was believed at that time that the SCRAM was caused due to a leaky isolation valve ISV!. <br /><br /> The valve was removed and disassemble for inspection. The inspection revealed stainless steel particles inside the valve. These particles are assumed to have wedged in between the valve seat and disc which caused the valve to remain partially open when the valve was initially closed. The SCRAM appears to have been due to pressure wave propagation in the common tapped instrument sensing lines. <br /><br /> Immediate corrective actions taken were as follows: The Unit 2 Rx was brought to a cold shutdown condition. The Operations Department withheld the performance of this surveillance test on the rest of the pressure switches on both units, until the preliminary investigation was completed. The IM Department along with the Operations Department developed a method for performing surveillances, involving pre-pressurization valves, to determine if the instrument isolation valve was leaking by. This method was documented in IM memorandum #25. The IM Department is also backflushing all instrument lines on both units that have the same valve design configuration. <br /><br /> Recommended corrective actions include the review and possible re-design of the isolation valve configuration and the review and possible inclusion of these valves into a preventive maintenance schedule for backflushing. .
2651993025 | Quad Cities 2 | 12/05/1993 | 05/11/1994 | 9405170217 | <strong>A Loop Main Steam Isolation Valves Exceed Tech Spec Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in the SHUTDOWN mode at 0% power for a maintenance outage on 12/05/93 at 2300 hours at which time, during the performance of a combined Local Leak kate Test of the 'A' loop Main Steam Isolation Valves (MSIV's) [SB] [ISV], the leakage exceeded the 11.5 standard cubic feet per hour (scfh) Technical Specification limit of T.S.3.7.A.2.e. The measured leakage was 24.8 scfh. The MSIV's are 20 inch Y-pattern globe valves, Crane Drawing DR-34289, Revision 'H'. <br /><br /> The 1A MSIV was subsequently disassembled for inspection. The cause of the excessive leakage was steam erosion on the pilot and main disc. The fasteners which retain the main valve disc to the valve stem were also found to be loose. <br /><br /> The apparent cause of the valve internal deficiencies was the failure of the fastener locking devices. The primary causal factors of this deficiency are inadequate MAINTENANCE/TESTING and WRITTEN COMMUNICATION which both resulted in the improper use of the fastener locking devices.
2651993026 | Quad Cities 2 | 12/24/1993 | 01/24/1994 | 9402030060 | <strong>Reactor Scram Due To A Sudden Pressure Release From The 2-220-118A Valve.</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1993, at 0833 hours, with Unit 2 at zero percent power and in the shutdown mode (Mode 1) of operation, the Control Room received a Reactor Low Level SCRAM (All Rods IN). <br /><br /> The SCRAM was determined to have been caused by pressure wave propagation in instrument sensing lines for the Reactor Low Level Differential Pressure Transmitters. The pressure wave was propagated from the sudden release of water spray from the 2-0220-118A isolation valve [ISV] during repacking work.<br /><br /> The proximate root cause of this event was due to an inadequate pre-job briefing and lack of verification of the 118A valve position prior to the start of Mechanical Maintenance work to repack the valve. A contributing root cause was determined to be due to inadequate overall job planning and implementation. <br /><br /> The recommended corrective actions include revising procedures, development of guidelines for Nuclear Work Request task analysis and reviewing this LER report with the entire maintenance line management/operations organization as a lesson learned.
2661993001 | Point Beach 1, Point Beach 2 | 01/07/1993 | 02/04/1993 | 9302230212 | <strong>Inoperability of the Degraded Voltage Relays</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1993, an evaluation was completed that showed the settings for the degraded grid voltage relays on the 4160V safety-related buses could be too low to provide adequate protection for all safety-related equipment. Therefore, all 4160V degraded grid voltage protection channels were declared inoperable at 1515 CST, invoking the requirements of Technical Specification Table 15.3.5-3, 'Emergency Cooling,' Item 4.a. This invoked Technical Specification 15.3.0, which requires that the affected units be placed in hot shutdown within 3 hours and in cold shutdown within 48 hours if the condition is not corrected. An NRR Waiver of Compliance was requested and granted to allow time to determine new setpoints, calibrate the relays, submit a Technical Specification Change Request, and receive a license amendment for this setpoint change. The new setpoint determinations and setpoint changes were performed. These actions were completed January 15, 1993. A Technical Specification Change Request was submitted to the NRC in a letter dated January 18, 1993.
2661993002 | Point Beach 1, Point Beach 2 | 02/18/1993 | 03/22/1993 | 9303310057 | <strong>Inoperability of Both Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>At approximately 0845 hours on February 18, 1993, with both units operating at full power, the synchroscope switch for the Train B Emergency Diesel Generator (EDG) G-02 was turned on while the synchroscope switch for Train A EDG G-01 was already on. This caused a fuse in the EDG G-02 output metering circuit to blow. EDG G-02 was declared inoperable. EDG G-01 had been previously taken out of service for its annual maintenance outage on February 15, 1993. Therefore, both Emergency Diesel Generators G-01 and G-02 were inoperable, a condition prohibited by Technical Specifications. Technical Specification 15.3.0 was entered. Technical Specification 15.3.0 requires that the affected units be placed in hot shutdown within 3 hours and in cold shutdown within 48 hours if the condition is not corrected. The condition was corrected by replacing the blown fuse. EDG G-02 was declared operable at approximately 0953 hours. The daily operability test of EDG G-02, required by Technical Specification 15.3.7 for EDG G-01 being inoperable, was successfully completed at 1138 hours.
2661993003 | Point Beach 1, Point Beach 2 | 03/19/1993 | 04/19/1993 | 9304230154 | <strong>Setpoints for Low Temperature Overpressure System Found to be Nonconservative</strong><br /><i>Abstract:&nbsp;</i>Wisconsin Electric Power Company has discovered a nonconservative condition associated with the Point Beach Nuclear Plant Low Temperature Overpressure system. The location of the reactor coolant system pressure transmitters was not considered in the Low Temperature Overpressure system setpoint development analysis. For Point Beach Nuclear Plant Units 1 and 2, the pressure difference across the reactor core is 63 psid with two reactor coolant pumps in operation, and 25 psid with one reactor coolant pump operating. After taking safety margins into account, the setpoint is approximately 34 psig too high to operate both reactor coolant pumps throughout the entire temperature range during the worst case mass input transient. During conditions when the Low Temperature Overpressure system is in service, reactor coolant pressure may not be limited to below the plant operating curves in Point Beach Technical Specification Figures 15.3.1-1, "Heat-up Limitations," and TS 15.3.1-2, "Cooldown Limitations."
2661993004 | Point Beach 1 | 04/09/1993 | 05/10/1993 | 9305180058 | <strong>Containment atch Temporary Third Door Tied Open During Refueling Operations</strong><br /><i>Abstract:&nbsp;</i>At approximately 1915 on April 8, 1993, with refueling operations in progress, a plant employee exiting the containment found the temporary third door to the Unit 2 containment personnel hatch on the containment 66 foot elevation was secured open. This is in violation of Technical Specification section 15.3.8, 'Refueling.' Specification 15.3.8.1 states in part, 'A temporary third door on the outside of the personnel lock shall be in place whenever both doors in a personnel lock are open.' The door was immediately closed by the plant employee who recognized that the door was to remain closed during refueling operations. The employee had found the door closed at 1900 when he had entered the containment for shift turnover. Procedure changes are being made to ensure the door is monitored and remains closed during refueling operations.
2661993005 | Point Beach 1 | 04/15/1993 | 05/14/1993 | 9305210054 | <strong>Inadvertent Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>At approximately 1045 hours on April 15, 1993, while adjustments were being made to Point Beach Nuclear Plant Containment Accident Fan 1-W1C1, Time Delay Relay 1-TDR-26, Turbine Building Cooler Service Water Inlet Valve 1SW-2880 unexpectedly closed. The closure of 1SW-2880 was caused by actuation of an Engineered Safety Feature associated with Relay 1-TDR-26. The closure of 1SW-2880 did not impact the availability of any Engineered Safety Features. The Engineered Safety Feature system for Unit 1 was not required to be operable because the unit was shutdown with the reactor core defueled for its annual maintenance and refueling outage. Only nonessential service water loads are serviced through 1SW-2880. Office area cooling loads were isolated as a result of this event.
2661993006 | Point Beach 1, Point Beach 2 | 04/16/1993 | 05/17/1993 | 9305250246 | <strong>Containment Isolation Valve not Leak Tested in Accordance with Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1993, with Unit 1 in a refueling shutdown condition and Unit 2 operating at 100% power, we discovered that outside Containment Isolation Valve CV-00369A on Penetration P-10 for both units was not included in our 10 CFR 50, Appendix J, 'Primary Reactor Containment Leakage Testing for Water-Cooled Power Reactors,' Type C leakage testing program as required by Technical Specification 15.4.4.III.D. Redundant outside Containment Isolation Valve 1CV-00369B for PBNP Unit 1 was also found with excessive leakage. Subsequent inspection revealed that Check Valve 1CV-00369B had a 1/16 inch hole machined into its disk (as specified by valve model design). The hole in the disk was determined to be the cause for the leakage previously identified. Further investigation revealed that the wrong model valve was installed as part of a modification performed in 1972. The model number for the installed valve was virtually identical to the model number of the check valve designed for the modification except for one character. Valve 1CV-00369B was replaced and a test connection was added to allow leak testing of Valve 1CV-00369A. Penetration 10 (encompassing Valves CV-00369A&B) also has inside containment automatic Isolation Valve CV-00371A which is Appendix J tested. A modification will be performed during the next scheduled Unit 2 refueling outage to add a test connection to allow Appendix J testing of Valve 2CV-00369A. Valve 2CV-00369B was inspected and it appears that the proper valve was installed. However, this will be verified during the next scheduled Unit 2 refueling outage. The NRC Resident Inspector was notified of this event.
2661993007 | Point Beach 1, Point Beach 2 | 07/26/1993 | 11/12/1993 | 9312010032 | <strong>Inadvertent Emergency Diesel Start And Loss Of A Station Battery Charger</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1993 at about 1333 hours, with both units at full power, a fuse in the Unit 1, B train, 4160V emergency bus 1A-06 metering and relaying circuit blew during calibration of the 1A-06 voltmeter. The blown fuse caused a 1A-06 undervoltage signal to be generated. The undervoltage signal caused the normal power supply breaker for 1A-06 to open and deenergize the bus. The emergency diesel generator G-02 immediately started and reenergized the 1A-06 bus. One of the four station battery chargers (D-108) tripped off, as designed, during the momentary loss of power to the Unit 1, B train. Technical Specification 15.3.7.A.1.h requires a battery charger to be in operation to each of the four DC buses. If this condition is not met, Technical Specification 15.3.0 states that the units must be in Hot Shutdown within 3 hours. D-108 was restored at 1355 hours, which ended the Technical Specification 15.3.0, 3-hour limiting condition for operation. The DC buses for PBNP are shared by both units, therefore, this LCO was applicable to both units. Normal configuration of the other equipment that was affected was re-established. The blown fuse was replaced at about 1430 hours and the normal configuration of the electrical distribution system was re-established at 1443 hours. The blown fuse was caused by human error during calibration of the 1A-06 voltmeter.
2661993008 | Point Beach 1, Point Beach 2 | 09/10/1993 | 11/30/1993 | 9312100133 | <strong>SW-LW-61 Determined to be Inoperable During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At 0205, on September 10, 1993, during the performance of In-Service Test, IT-72, 'Service Water Valves (Quarterly),' SW-LW-61, the service water inlet isolation to each unit's blowdown tank vent condenser, the blowdown evaporator overhead condenser, and the blowdown evaporator distillate cooler, failed to shut as required. The subsequent inspection revealed that the instrument air tubing was incorrectly connected to the valve ports of SW-LW-61-S, the associated solenoid valve. Incorrectly connecting this tubing prevented instrument air from properly venting off when the solenoid valve shut. This prevented SW-LW-61 from shutting, as required. Maintenance was subsequently performed to correct the situation, with the valve being returned to service at 1422 on September 10, 1993, following the successful completion of post-maintenance testing.
2661993009 | Point Beach 1, Point Beach 2 | 12/02/1993 | 12/22/1993 | 9401040256 | <strong>Inoperability Of Both Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>At 0401 hours CST, on November 29, 1993, with both units operating at full power, Emergency Diesel General (EDG) G01, the Train A EDG, was voluntarily removed from service-for turbocharger and idler stubshaft assembly replacement. This required placing both PBNP units into the LCO defined in Specification 15.3.7.B.1.g which states that an emergency diesel generator can be inoperable for up to 7 days provided the other diesel generator (in this case the Train B EDG G02) is tested daily to ensure operability. On December 2, 1993, at 2256 hours CST, EDG G02 was declared inoperable due to a relay malfunction in one of the redundant starting circuits. The declaration of EDG G02 as inoperable placed both units in a condition, which by Technical Specification 15.3.0.A, required both units be placed in hot shutdown within 3 hours (by 0156 on December 3, 1993). A Notice of Enforcement Discretion (NOED) was requested from the NRC to allow additional time in the LCO to return at least one EDG to service. The NOED was granted at 0225 CST on December 3, 1993. At 0230 CST, EDG G01 was returned to an operable status, Technical Specification LCO 15.3.0.A was exited, and the 7-day LCO required when one EDG is inoperable (EDG G02) was continued.
2671993001 | Fort St. Vrain | 01/26/1993 | 02/25/1993 | 9303020327 | <strong>Overflow of Radioactive Liquid Effluent Line</strong><br /><i>Abstract:&nbsp;</i>From 1705 hours until 2245 hours on January 26, 1993, a release was made from the Fort St. Vrain radioactive liquid waste system. It was later discovered that some of this release overflowed an underground off separator and spilled onto the adjacent ground.<br /><br /> At 0120 hours on January 27, 1993, water was observed to have overflowed the oil separator in the Fort St. Vrain radioactive liquid effluent release line. Water spilled onto the surrounding ground and flowed east into the yard drain system. All of the spill was confined to the restricted area of the plant. Water that entered the yard drains was then fully diluted with water from the cooling tower blowdown/bypass line, and was released to the unrestricted area in the normal liquid effluent release path. Based on area surveys and water samples, there was negligible radioactive contamination of affected soil. <br /><br /> The overflow was caused by an ice plug in the drain line downstream of the oil separator, due to an unusual period of extended sub-freezing weather. The ice plug was thawed and heat tracing was added to prevent recurrence of this event. <br /><br /> This event is reported as a condition that could have prevented the ability to control the release of radioactive material.
2671993002 | Fort St. Vrain | 02/10/1993 | 03/11/1993 | 9303170204 | <strong>Fuel Handling Machine in Unqualified Location</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1993, with the Fort St. Vrain reactor permanently shutdown and decommissioning actively in progress, the Fuel Handling Machine (FHM) was being used to remove radioactive core components from Equipment Storage Well No. 5. At approximately 11:30 a.m., the Reactor Building crane was detached from the FHM. Equipment Storage Well No. 5 is not a seismically qualified location for the FHM if it is not attached to the Reactor Building crane, so this action placed the plant in an unanalyzed condition. <br /><br /> This event occurred due to a misinterpretation of the applicable procedural requirements. <br /><br /> After about 1 hour, the correct explanation of the procedural requirements was identified and the Reactor Building crane was re-attached to the FHM.<br /><br /> This event did not compromise decommissioning safety in that all safety barriers were maintained at all times. However, if a design basis earthquake had occurred, it is conceivable that the 165 ton FHM could have toppled and damaged the Reactor Building confinement or structural integrity. <br /><br /> PSC and its decommissioning contractor reviewed this event with all involved personnel and emphasized the need to prevent recurrence. Also, the applicable procedure was revised to strengthen FHM/crane attachment requirements.
2671993003 | Fort St. Vrain | 05/05/1993 | 06/03/1993 | 9306100243 | <strong>New Natural Gas Source Within One-Half Mile</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1993, with the Fort St. Vrain (FSV) reactor permanently shutdown, defueled to the Independent Spent Fuel Storage Installation (ISFSI) and decommissioning actively in progress, a new source of natural gas was introduced within 0.5 mile of the ISFSI and the Reactor Building without prior NRC approval. This violates license conditions in both ISFSI Materials License No. SNM-2504 and FSV Facility License No. DPR-34, and Technical Specification 5.11. <br /><br /> The event occurred due to field routing of a natural gas pipe from a new oil/natural gas well to a connection point which differed from the routing previously agreed upon by PSC and the well operator (outside the 0.5 mile restriction). <br /><br /> This condition was bounded by previous analyses of postulated ruptures of higher capacity natural gas pipelines much closer to the Reactor Building and ISFSI. The well operator isolated the new well until a new pipeline is installed, outside the 0.5 mile distance from these structures.
2671993004 | Fort St. Vrain | 09/27/1993 | 10/26/1993 | 9311020043 | <strong>Incorrect Reactor Building Ventilation System HEPA Filters</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1993, Public Service Company of Colorado (PSC) discovered that the filters in Train A of the Reactor Building ventilation exhaust system were not high efficiency particulate air (HEPA) filters, as required by the Fort St. Vrain Decommissioning Technical Specifications during graphite block removal operations. The wrong filters had been installed on December 29, 1992, and passed the applicable surveillance test requirements before Train A was declared operable. <br /><br /> HEPA filters are required during activated graphite block handling, which was in progress from the time the incorrect filters were installed until March 16, 1993. <br /><br /> This condition was due to an incomplete review of material requirements documentation and to erroneous information in applicable material stock code documents, and is considered an isolated occurrence. PSC examined all required FSV HEPA filters to visually verify that they are the correct filters, and surveillance tests were conducted on all filters to ensure operability.
2691993002 | Oconee 1 | 01/29/1993 | 03/01/1993 | 9303090029 | <strong>Operator Inattention To Detail Results In An Unplanned Reactor Protective System Actuation During Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1993 at approximately 1536 hours, Unit 1 was at Hot Shutdown conditions, following a refueling outage, when a leaking valve was discovered. Reactor Coolant System (RCS) pressure and temperature had to be reduced in order to repair the leaking valve. During the depressurization and cooldown of the RCS, an unplanned Reactor Protective System (RPS) actuation occurred. The Reactor was subcritical with Safety Rod Group 1 at approximately 50% withdrawn. The operator was decreasing RCS pressure and temperature when his attention was diverted to a control rod problem. One RPS channel tripped unexpectedly on low RCS pressure, followed by another RPS channel trip. The unit shutdown continued in accordance with the shutdown procedure. The Root Cause of this event is Inappropriate Action (Improper Action - Lack of Attention to Detail) and a contributing cause of Management Deficiency (Deficient Supervision - Insufficient Supervision). Corrective actions include, Reactor Operator A and the Control Room SRO conveying the lessons they learned as a result of this event to all five operating shifts and making changes to the shutdown procedure.
2691993003 | Oconee 1, Oconee 2, Oconee 3 | 02/18/1993 | 03/22/1993 | 9303290055 | <strong>Design Deficiency Results In The Technical Inoperability Of The Alternate Reactor Coolant Makeup System</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1993, at 1145 hours, Oconee units 1, 2, and 3 were at 100% full power. Oconee Engineering determined that the Standby Shutdown Facility (SSF) Reactor Coolant Makeup (RCMU) pump was inoperable. The technical inoperability was due to excessive nitrogen pressures in the suction stabilizer bladder which could have prevented the stabilizer from functioning properly during SSF scenarios. All three units entered a seven day Limiting Condition for Operation (LCO) for SSF RCMU system inoperability. On February 21, 1993, the pressure was vented off each units' SSF RCMU pump suction stabilizer and the RCMU system LCOs were exited. The root cause of this event is design deficiency: unanticipated environmental interaction, temperature. Corrective actions include venting the pressure from the RCMU pump suction stabilizers, revising procedures and completing the Design Basis Document for the SSF.
2691993004 | Oconee 1, Oconee 2, Oconee 3 | 04/08/1993 | 10/28/1993 | 9311040259 | <strong>A Postulated Single Failure During A LOCA/LOOP May Result In The Loss Of Post Accident Cooling Due To A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1993 during an inspection of the Emergency Condenser Cooling Water System, a NRC resident discovered that the control logic associated with the Condenser Cooling Water (CCW) Pump discharge valves may not be single failure proof. An evaluation by Oconee Engineering revealed that a single failure could close all CCW Pump Discharge Valves on a single unit following a LOCA/LOOP. This would isolate the primary suction flow path for the Low Pressure Service Water (LPSW) Pumps. At 1730 hours, on April 8, 1993, with all three Oconee Units at 100% Full Power, a 24 hour action statement for Technical Specification 3.3.7 was entered due to the inability of the LPSW System to withstand a design basis accident and a single failure in the CCW system. The root cause of this event is Design Deficiency: unanticipated Interaction of Systems, (Design oversight). <br /><br /> Corrective action was to cross connect the CCW system of all three Oconee Units to overcome the single failure vulnerability of the LPSW suction. In addition, a modification is planned to ensure that at least one CCW Pump discharge valve will remain open when all CCW Pumps trip, even with a single failure in the control circuitry.
2691993005 | Oconee 1, Oconee 2 | 05/04/1993 | 06/03/1993 | 9306140150 | <strong>Inoperable Control Rods Due To Defective Procedure Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>Three Control Rods, one in Unit 2 and two in Unit 1, initially failed to meet the Technical Specification (TS) required drop times during the most recent refueling outages, but were successfully tested prior to restart. On April 29, 1993, Unit 2 began a refueling outage. The Unit 2 rod was tested at hot shutdown conditions at the start of the refueling outage and again failed the TS drop time. As a result, the Unit 1 test data was reevaluated and two Unit 1 Control Rods were declared inoperable on May 4, 1993, at 0900 hours, while Unit 1 was at 100% full power. Discretionary enforcement was obtained for continued operation of Unit 1. The Unit 2 Control Rod Drive Mechanism was replaced. The root cause of this event is Defective Procedure. A contributing cause of this event is Equipment Failure/Malfunction. Corrective actions include obtaining NRC approval for use of an interim acceptance criteria for Control Rod drop times on Oconee Unit 1, enhancing the Control Rod Drive Rod Drop Time Test Procedure and completing the necessary repair/replacement on the Control Rod Drives.
2691993006 | Oconee 1, Oconee 2, Oconee 3 | 06/02/1993 | 08/29/1995 | 9509080007 | <strong>Design Deficiency Results In A Condition Outside The Design Basis of Containment For A Main Steam Line Break</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1993, at 1630 hours, Oconee Unit 1 and 3 were at 100% full power and Unit 2 was shutdown for refueling. A reanalysis, for extended fuel cycle designs and reload design optimization, resulted in the discovery of a condition outside the design basis of the plant. The main steam line break analysis in the Oconee Final Safety Analysis Report (FSAR) based on the original analysis by Babcock and Wilcox, had not taken into account the passive structural metal of the Reactor Coolant System acting as a heat source or the worst case scenarios regarding feedwater isolation. The reanalysis indicates that these are a significant heat source and shows potential for containment design pressure to be exceeded. Evaluations have concluded that existing procedures and training for operator action are adequate to limit containment pressure to below the design pressure for the most probable scenarios. The root cause is Design Deficiency; Functional design deficiency; Mechanical. Corrective actions are to continue the reanalyses of the accident scenarios in the FSAR, supplement the response to IE Bulletin 80-04, and modify the feedwater system.
2691993007 | Oconee 1 | 07/01/1993 | 06/14/1994 | 9406280319 | <strong>Design Deficinecy Results In The Technical Inoperability Of The Alternate Reactor Coolant Makeup System</strong><br /><i>Abstract:&nbsp;</i>In May 1992, Oconee Engineering (OE) initiated an evaluation of the parameters that affect the Reactor Coolant Makeup (RCMU) system operability. The evaluation was initiated after an excessive Reactor Coolant (RC) pump seal leakage event on Unit 1 (LER 269/92-09). Specifically, the evaluation was to determine the adequacy of the RCMU system to supply the RC pump seals during a Standby Shutdown Facility (SSF) event. On July 1, 1993, with Unit 1 at 100% full power, OE determined that the Unit 1 SSF RCMU system had been inoperable in the past. The Unit 1 RC pump seal leakage rates have occasionally exceeded the newly established maximum allowed seal leakage rates. The root cause of the SSF RCMU system inoperability is a Design Deficiency, functional design deficiency, mechanical. A wiring error contributed to the event from March through May 1992. Corrective actions included completing the design calculation for allowable RC pump seal leakage rates, revising appropriate procedures and initiating modifications to install higher accuracy flow gauges and to correct wiring errors.
2691993008 | Oconee 1 | 08/23/1993 | 09/22/1993 | 9309280265 | <strong>Inappropriate Actions Result In Loss Of Vital Power Panelboard And A Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1993 at 1117 hours, with Unit 1 operating at 100% Full Power, a breaker was opened to allow for a peak inverse voltage test on the DC power system diodes. Upon opening the breaker, one of the unit's AC and DC Instrumentation and Control Power Panelboards was lost. The supply breaker input leads in the alternate power path were found rolled, causing the loss. The loss of these power panelboards resulted in the loss of the 125v DC Electro-Hydraulic Control circuit, tripping the Main Turbine and causing an anticipatory reactor trip. Main Feedwater system responded to the reactor trip; however, due to an inappropriately installed Output Limiter card in the Integrated Control System, Main Feedwater Pump speed was limited. This resulted in the initiation of the 'Dryout Protection' circuit, automatically starting both Motor Driven Emergency Feedwater Pumps. The root causes of this event are inappropriate Actions (Improper Action, Lack of Attention to Detail, and Failure to Follow Procedures) with contributing cause of Management Deficiency (Policy or Directive). Corrective actions include procedure changes, directive enhancements and personnel training.
2691993009 | Oconee 1, Oconee 2, Oconee 3 | 09/27/1993 | 10/27/1993 | 9311040188 | <strong>Design And Installation Deficiencies In Load Shed Circuitry Result In Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>In January 1987, a modification was performed installing dedicated fuse blocks for each local load shed trip initiate relay in the 4160V switchgear on Unit 3. On August 3, 1993, with Unit 3 at 100% full power, an inspection of 3TD 4160V switchgear revealed that the power source for relay 3DLS1 had been incorrectly connected to bus potential (AC) fuses rather than essential power (DC) fuses. This resulted in one channel of the load shed portion of Emergency Power Switching Logic being technically inoperable, which violated Technical specifications. On October 12, 1993, with all three Units at 100% full power, Oconee Safety Review personnel reviewing the associated drawings for the modification, determined that the Unit 1, 2, and 3 TD switchgear were not single failure proof for load shed due to the arrangement of the DC power supplies. The root causes are Installation Deficiency (improper installation) and Design Deficiency (Equipment Configuration or Functional Design Deficiency). Corrective actions include revising the wiring connections, and reviewing and revising the load shed test procedure as required.
2691993010 | Oconee 1 | 11/03/1993 | 04/18/1994 | 9404260194 | <strong>Equipment Failure Causes Low Generator Water Level Resulting In Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1993, Unit 1 was operating at approximately 88% Full Power due to a feedwater heater drain pump being out of service. A manual reactor trip at 13% Full Power was initiated at 0100 hours after a plant transient. This transient resulted from a momentary circuit interruption due to a broken wire termination lug in the terminal box on Main Steam Stop Valve (MSV) 2 causing MSV 2 to partially close. The other three MSV's closed due to an interlock. The circuit interruption then cleared and MSV 2 began to open. The other three MSV's received a signal to reopens however, only MSV 1 reopened. Two MSV'S, associated with the A Main Steam line, remained closed due to stuck test solenoid valves. This condition resulted in only the B Steam Generator (SG) supplying steam to the Main Turbine and A SG isolated with its' Main Steam Relief Valves open. This ultimately lowered SG B pressure and water level to a point where the reactor was manually tripped by the Control Room Operator in accordance with Operations Management Procedures. Emergency Feedwater initiated to restore SG level and other systems responded as expected to stabilize the unit. The root cause of the event is Equipment Failure. Corrective actions include repairing the wire lug in the control cabinet, inspecting and cleaning the test solenoid valves, and evaluating the need to require a manual reactor trip on low SG pressure.
2701993001 | Oconee 2 | 04/29/1993 | 05/27/1993 | 9306030021 | <strong>Possible Equipment Failure Results In A Manual Reactor Protective System Actuation While Subcritical</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1993, at 0505 hours, Unit 2 was taken subcritical in preparation for a refueling outage. At 0556 hours, with Control Rod Groups 3 through 7 inserted and Group 2 Safety Control Rods insertion in progress, a momentary loss of 2KI power was experienced. A computer alarm was received indicating a 'Main Steam Pressure Mismatch' on the 2B Main Steam header pressure. Also observed was that the operating 2A Main Feedwater Pump had tripped, the Emergency Feedwater Pumps started and the Loss of Feedwater Abnormal Procedure was entered. The Reactor Protective System was manually initiated, inserting the remaining Control Rods. The Control Room personnel entered the Emergency Operating Procedure, and the unit was stabilized. An investigation revealed a faulty Current Limit Module caused the opening of the Inverter Power fuse and the Static Transfer Switch fuse resulting in a temporary loss of power to 2KI. The root cause of this event is Equipment Failure/Malfunction. Corrective actions include the replacement of both fuses and the Current Limit Module. Also, an evaluation will be performed on the inverter and static transfer switch that led to the momentary loss of 2KI.
2701993002 | Oconee 2, Oconee 3 | 06/10/1993 | 07/12/1993 | 9307220209 | <strong>Equipment Failure May Result In A Loss Of Containment Integrity During A Postulated Event</strong><br /><i>Abstract:&nbsp;</i>In May 1993 an Engineer was reviewing a procedure which was generated as a result of Generic Letter 88-14 (Instrument Air Supply System Problems Affecting Safety-Related Equipment) to test air operated valves (AOV) with backup accumulators. He questioned the test method and acceptance criteria of the procedure and initiated an evaluation of air leakage from backup accumulators on AOVs associated with containment integrity. The evaluation revealed that containment integrity could be lost during a postulated Loss of Instrument Air coincident with a Small Break Loss of Coolant Accident because Unit 2 and 3's HP-21 valves may return to the open position due to accumulator leakage. This evaluation was completed on June 10, 1993 with Unit 3 at 100% full power and Unit 2 shutdown for refueling. These valves were determined to have been inoperable in the past and currently conditionally operable based on a change to the Abnormal Procedure (AP) for Loss of Instrument Air (LOIA). The changes to Unit 2 ad 3's APs require the operators to close HP-21 manually within three hours following a LOIA. The root cause of this event is Equipment Failure. Oconee Engineering will perform an evaluation to determine the long range plans for these valves, including a possible replacement for Unit 2 and 3's HP-21.
2701993003 | Oconee 2, Oconee 3 | 08/10/1993 | 09/09/1993 | 9309170244 | <strong>Design Deficiency Results In Technical Inoperability Of The Reactor Coolant Makeup System</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On August 10, 1993, at 1515 hours, Oconee Units 2 and 3 were operating at 100 % Full Power. While preparing the Design Basis Document for the Standby Shutdown Facility (SSF), Oconee Engineering determined that the SSF Reactor Coolant Makeup (RCMU) System was technically inoperable. The inoperability was due to the RCMU system letdown line orifices being too small to pass adequate flow during certain SSF accident scenarios. Oconee Units 2 and 3 entered a seven day Limiting Condition for Operation (LCO) for SSF RCMU system inoperability. On August 13, 1993, at 2041 hours, the SSF RCMU systems for Oconee Units 2 and 3 were declared operable and the LCO was exited after compensatory procedure changes were made. These changes included the use of the Reactor Vessel Head Vent valves to control pressurizer level during an SSF event. The root cause of this event is design deficiency: functional mechanical design deficiency. Corrective actions include revising procedures, completing the Design Basis Document for the SSF and installing appropriately sized letdown line orifices.
2701993004 | Oconee 2 | 08/23/1993 | 09/22/1993 | 9309280195 | <strong>Emergency Feedwater Required Technical Specification Surveillance Interval Exceeded Due To Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 0915 hours on August 23, 1993, with Unit 2 at 100 % full power, it was discovered that the maximum Technical Specification surveillance interval of 45 days had been exceeded by 28 days for Unit 2 Motor Driven Emergency Feedwater Pumps (MDEFDWP) initiation circuitry. This error was discovered when an Instrument and Electrical supervisor attempted to coordinate a minor modification functional test with the surveillance test procedure. The supervisor asked the Planner for the next scheduled surveillance test date. The Planner discovered that after the last refueling outage, the computer program which schedules periodic tests was not updated to return this test to an active status. The test should have been performed no later than July 26, 1993. The surveillance test was immediately performed on August 23, 1993 and indicated that MDEFDWP initiation circuitry had been operable. The root cause for this event is Management Deficiency (training, less than adequate training given and inadequate planning/scheduling). Corrective actions include placing restrictions on surveillance tests placed in the suspend mode and revising the program to track task placed in the suspend mode.
2701993005 | Oconee 2 | 08/25/1993 | 09/23/1993 | 9310010108 | <strong>Operator Isolated Potential Transformers On The Wrong Unit Resulting In A Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1993, at 2330 hours, Unit 2 reactor tripped from 100% full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout following an indicated loss of load. The loss of load indication occurred when an operator pulled generator metering, relay and regulating equipment drawers to the disconnect position on the Unit 2 generator instead of Unit 1. The operator was supposed to perform the work in preparation for returning Unit 1 generator to service. Post trip operator response stabilized the plant. The root cause of the event is Inappropriate Action (Improper action; the action chosen was incorrect because of a lack of attention to detail). Corrective actions include reemphasizing the Stop, Think, Act, Review (STAR) process, adding Unit specific labeling and repairing locks on the equipment.
2701993006 | Oconee 2 | 09/02/1993 | 10/04/1993 | 9310130034 | <strong>Containment Isolation Valve Mispositioned Due To An Unknown Cause, Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1993 at 0200 hours, Unit 2 was operating at 100 % full power. Containment Isolation valve 2CF-41 (2B Core Flood Tank Pressure Gauge Isolation) was found open by a Non-Licensed Operator while adding borated water to the 2B Core Flood Tank. Upon discovery, the valve was closed as required by Technical Specification for containment integrity. Documentation revealed that the valve was placed in the closed position on May 26, 1993, after the performance of a leak rate test and it was verified closed prior to startup. The investigation did not reveal any evidence as to when the valve was subsequently opened. The root cause of this event is Unknown (possible inappropriate action). Corrective actions include management emphasizing their position prohibiting the practice of repositioning components without proper documentation.
2701993007 | Oconee 2 | 10/24/1993 | 11/23/1993 | 9312030096 | <strong>Inappropriate Action, Deficient Procedure, And Low Flow Spike Result In Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1993, at 0634 hours, Unit 2 tripped from 100 % full power on a flux/flow/imbalance trip of the Reactor Protective System (RPS). The flux/flow/imbalance trip occurred when transmitters monitoring flow in both loops of the Reactor Coolant System (RCS) simultaneously indicated that flow spiked low. Post trip operator response stabilized the unit. An investigation revealed that the method used to calibrate the RCS flow inputs to the RPS flux/flow/imbalance trip introduced an error which reduced the operating margin associated with the trip function. Also, it was found that an error was made while performing the last completed calibration procedure, which further reduced the margin. Therefore, the root causes of this event are considered to be Deficient Procedure (technical deficiency) and an Inappropriate Action (failure to follow procedure, improperly followed the correct procedure) in conjunction with an indicated low RCS flow spike. Corrective actions included reanalyzing core operating limit calculations to increase the operating margin, revising the calibration procedure, and reviewing this event with personnel involved in the procedure error.
2711993001 | Vermont Yankee | 12/17/1992 | 07/07/1993 | 9307140180 | <strong>Degraded Vital Fire Barriers due to inadequate documentation of assumptions and inadequate procedures</strong><br /><i>Abstract:&nbsp;</i>On 12/17/92, with the plant at 100% power, when the insulation was removed from a piping penetration (RA-515-SF), an indeterminate fire penetration seal configuration was identified. The piping penetration was only partially filled with the expected fire barrier material. This configuration was determined to be different than expected and potentially not in compliance with design requirements. The penetration was repaired to conform with the sealing requirements for penetrations specified in the original design change. <br /><br /> During subsequent investigations additional insulated lines were also determined to be indeterminate. Additionally, concerns were raised with the qualification of some non-insulated penetrations (piping, conduit, and cable trays), the failure to consider pipe displacement in the selection of appropriate seal type, and with issues surrounding the Quality Control practices of the contractor. The root cause of issues identified during this effort were attributed to (1) inadequate documentation of assumptions, (2) inadequate procedures, (3) human error, and (4) failure to follow procedures.<br /><br /> Corrective actions included repairing all identified discrepancies and performing an enhanced surveillance on all fire barrier penetration seals.
2711993002 | Vermont Yankee | 01/04/1993 | 02/03/1993 | 9302110191 | <strong>Missed Technical Specification Surveillance, Source Check Of Steam Jet Air Ejector (SJAE) Process Monitor Due To Inadequate Training</strong><br /><i>Abstract:&nbsp;</i>On 1/4/93, it was discovered that a Technical Specification required monthly surveillance test, Source Check of Steam Jet Air Ejector (SJAE) (EIIS = MON), had not been completed within the allowable time frame of thirty eight days. The test was completed in thirty nine days.<br /><br /> The root cause of this event is attributable to inadequate training of the implementing department Test Coordinator in the Surveillance Testing program with a contributing cause being an inadequate Surveillance Testing Control procedure. <br /><br /> Since the test had been successfully completed at the time of the discovery, no immediate corrective action was necessary. Subsequent corrective action will be to train department surveillance coordinators in the Surveillance Testing Program and to revise the Surveillance Testing Control procedure to clarify the statement regarding the conduct of early tests.
2711993003 | Vermont Yankee | 02/05/1993 | 03/05/1993 | 9303090157 | <strong>Failure To Properly Leakage Rate Test Portions Of The Primary Containment Hydrogen / Oxygen Monitoring System</strong><br /><i>Abstract:&nbsp;</i>On 02/05/93, with the reactor operating at 100% power, a review of the primary containment isolation requirements for the Hydrogen/Oxygen (H sub 2/O sub 2) Monitoring System (EIIS=IP) identified that portions of the System had not been leakage rate tested as required by the Vermont Yankee Appendix J Program and Technical Specifications. <br /><br /> The H sub 2/O sub 2 Monitoring System was immediately declared inoperable and the H sub 2/O sub 2 Monitors, SAH-VG-5A&B, were isolated from the primary containment. Subsequent leak rate testing was acceptable and SAH-VG-5A and SAH-VG-5B were returned to service on 02/06/93 and 02/07/93, respectively. <br /><br /> The root cause for this event has been determined to be an inadequate procedure. Procedure OP 4029, 'Type A - Primary Containment Integrated Leak Rate Testing', did not provide the proper instructions for leakage rate testing of the H sub 2/O sub 2 Monitoring System. Procedure OP 4029 has been revised to provide the proper instructions for leakage rate testing of the entire H sub 2/O sub 2 Monitoring System.
2711993004 | Vermont Yankee | 02/25/1993 | 08/19/1993 | 9308240014 | <strong>Jet Pump Operability Surveillance not Performed During Single Loop Operations as Required by Technical Specifications Due to inadequate plant procedures.</strong><br /><i>Abstract:&nbsp;</i>On 11/9/92 at 1429 hours, with the reactor at approximately 99% power, the 'A' Recirculation Pump Motor Generator (EIIS = AD MG) Set tripped due to electrical problems. From 11/9/92 at 1429 hours until 11/13/92 at 1130 hours the plant was in single loop operation. On 2/25/93, during a review of the surveillance, it was discovered that the required surveillance for the Jet Pumps (EIIS = AC P) in the idle loop, during single loop operation was not performed in accordance with Technical Specification 4.6.F.2 The root cause of this event was our failure to ensure that Technical Specifications requirements were appropriately incorporated into the plant procedures. The plant had returned to two loop operation prior to the time of discovery of the event. The immediate corrective action was to revise OP-4110, 'Reactor Recirc Surveillance' and OP-2428, 'Single Loop Operations', to provide specific instructions to correct this problem. Additionally, Procedure OP-4110 has been revised to include OP-2428 as a reference. <br /><br /> No similar events have been reported to the Commission in the last five years.
2711993005 | Vermont Yankee | 04/06/1993 | 08/15/1993 | 9308190039 | <strong>Control Rod Drive Scram Times Greater Than That Required By Technical Specifications Due To Scram Solenoid Pilot Valve Components, Supplement 1.</strong><br /><i>Abstract:&nbsp;</i>On 4/6/93, following Control Rod Drive scram time testing, it was concluded that the core average scram time and the scram times of seven (7) of the 2X2 control rod arrays at notch forty-six (46) were not in compliance with Technical Specifications (TS) Section 3.3.C. On 4/6/93, the plant was shutdown due to an unrelated minor leak in the Feedwater System. Subsequent follow-up investigation into past scram time testing revealed that on 10/15/92, the plant should have been shutdown when the 'as-found' scram times for one 2X2 array, at notch forty-six (46), was found not to be in compliance with Technical Specifications. The cause of the slow scram times has been attributed to degraded performance of the Scram Solenoid Pilot Valves (SSPVs). The cause for the failure to comply with TS on 10/15/92 and shutdown the reactor was the result of an incorrect interpretation of a Technical Specification Limiting Condition for Operation. Following the 4/6/93 shutdown, immediate corrective actions were to rebuild the Scram Solenoid Pilot Valves to address the slow scram times, and to no longer allow the use of repeated scrams to determine TS compliance. Other corrective actions included forming a task team to investigate the slow scram times, and a task team to investigate possible programmatic issues associated with the event.
2711993006 | Vermont Yankee | 05/27/1993 | 06/24/1993 | 9306300221 | <strong>Core Spray Systems A and B Declared Inoperable Due To Calibration Procedure Error.</strong><br /><i>Abstract:&nbsp;</i>At approximately 2030 on 5/27/93, with the plant operating at 100% steady state power, both the A and B Core Spray System trains were declared inoperable based upon the identification of a calibration procedure error which resulted in the setpoint of the differential pressure indicating switches (DPIS-14-43A/B) for Core Spray Sparger Break Detection being set non-conservatively. The procedure was revised, instruments recalibrated, and the A and B Core Spray Systems were returned to service. The decision by plant management to declare both A and B trains of the Core Spray System inoperable was based upon a Technical Specification requirement, integrity of the Core Spray Sparger was not in question.<br /><br /> Due to dynamic forces acting on the pressure switch during plant operation, a head correction is factored into the calibration of the pressure indicator. However, when the procedure instructed the technician to set the switch setpoint, it did not incorporate the offset into the value to be read from the measuring and test equipment (M&TE). Corrective actions include: a review the Technical Specification setpoint for Core Spray Sparger High Pressure; consideration of a replacement for the existing Barton 288 instrument; review of other procedures for a similar situation.
2711993007 | Vermont Yankee | 06/09/1993 | 07/16/1993 | 9307260211 | <strong>Failure To Perform Daily Instrument Checks Due To Management And Human Factors Weakness</strong><br /><i>Abstract:&nbsp;</i>On June 9 1993 it was determined that the Daily Instrument Checks required by Technical Specifications Table 4.2.1 were not included in the Operators Rounds for the Auxiliary Power Monitor and the Pump Bus Power Monitor for the Core Spray system and the Low Pressure Coolant Injection system. On June 21, 1993 additional Daily Check omissions from the Operator Rounds were found in Table 4.2.1 for the High Drywell Pressure instrumentation in the Emergency Core Cooling System, and on June 23, 1993 in Table 4.2.2 for the High Drywell Pressure instrumentation in the Primary Containment Isolation System and Table 4.2.9 for the Reactor Core Isolation Cooling Logic Bus Power Monitor. <br /><br /> The root cause of these events has been determined to be Management weakness in evaluating surveillance requirements with contributing causes of Human Factors and Personnel Error due to a lack of instrument tag numbers in the Tech Spec Tables. <br /><br /> Immediate corrective actions consisted of revisions to the 'Conduct of Operations and Operator Rounds' Procedure , issuance of Standing Order #8, and expanded review for potential problems with other Daily Instrument Checks in this TS Section. A continuing effort will review all other TS Sections and will result in issuance of an LER supplement and TS revisions if required.
2711993008 | Vermont Yankee | 07/01/1993 | 07/30/1993 | 9308040281 | <strong>"A" RHRSW pump was not declared inoperable as required by the Inservice Testing (IST) Program.</strong><br /><i>Abstract:&nbsp;</i>During technical specification surveillance testing performed on May 15, 1991, the 'A' RHRSW (P-8-1A) pump was not declared inoperable when the differential pressure entered the IST Required Action Range. The relevant technical specification LCO (Limiting Condition of Operation) was not entered. However, a review of system operability testing performed on 5/15/91 reveals the LCO requirements were satisfied. Also, a review of testing data both prior to and following the 5/15/91 test indicates that the 'A' RHRSW pump was able to provide the required cooling water flow. Thus, there was no impact to the safe operation of the plant.<br /><br /> The root cause of this event is attributed to a cognitive personnel error. The shift engineer who evaluated the surveillance data failed to correctly identify that the pump's differential pressure had entered the 1ST Required Action Range. The lack of independent review of the resultant test data has been identified as a contributing cause.<br /><br /> The Plant procedure (AP 0164) which is used to evaluate pump IST data is being revised to address these identified problems.
2711993009 | Vermont Yankee | 07/16/1993 | 08/13/1993 | 9308190021 | <strong>"B" Core Spray System Declared Inoperable Due To Instrument Out Of Tolerance As A Result Of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 7/16/93 at 0840, with the plant operating at 100% power and the 'B' Train of the Residual Heat Removal System (RHR) removed from service, the 'B' Train of the Core Spray System (CS) was declared inoperable. In accordance with Technical Specifications, with one RHR System and one Core Spray System inoperable, a 24 hour shutdown LCO was entered. The basis for declaring the 'B' Train of the CS System inoperable was the identification that the respective Sparger Break Detection System differential pressure indicating switch (DPIS) setpoint was out of specification. DPIS-14-43B was calibrated to within the required limits and at 0930 on 7/16/93 the 'B' Core Spray System was returned to service. As discussed in LER 93-006, an interim administrative setpoint for the Sparger Break Detection Sensors was imposed by Plant Management on 5/27/93 due to questions relative to the appropriateness of the TS setpoint. On 7/12/93, DPIS-14-43B was calibrated and left outside the administrative limit due to the fact that the calibration procedure had not been revised to the new interim setpoint values. The root cause of this event is personnel error in that timely revision to the instrument calibration procedure was not performed by the responsible manager. The instrument was immediately re-calibrated to within the interim administrative setpoint, the calibration procedure was revised to reflect the new setpoint, and a corrective action report is being prepared.
2711993010 | Vermont Yankee | 08/03/1993 | 08/31/1993 | 9309080149 | <strong>Failure To Perform Annual Valve Cycling As Required By Plant Technical Specification 4.13.B.1.d For A Valve In The Vital Fire Suppression Water System Flow Path Due To Procedural Omission.</strong><br /><i>Abstract:&nbsp;</i>On 08-03-93, with the plant operating at 95% power, during a review of fire protection system valves (EIIS Identifier = KP) that are cycled annually to meet the requirements of Technical Specification 4.13.B.1.d, it was determined that valve V76-420 had not been cycled annually since its installation in 1981. The valve is normally sealed open and provides manual isolation for three Turbine Building hose stations. <br /><br /> The root cause was determined to be human error in the failure to include the valve in the applicable surveillance procedure. <br /><br /> Immediate corrective actions included: revising the applicable surveillance procedure to include V76-420: successfully cycling the valve (on 08-06-93); and, initiating a review of the vital fire suppression water system and surveillance procedures to determine whether there were any other valves not being cycled as required by plant Technical Specifications. This review has not identified any additional valves that require cycling. <br /><br /> One similar event was reponed to the Commission within the last five years (LER #90-02).
2711993011 | Vermont Yankee | 08/28/1993 | 09/24/1993 | 9310040059 | <strong>Group 4 Primary Containment Isolation on initiation of "B" Shutdown Cooling System due to pressure spike</strong><br /><i>Abstract:&nbsp;</i>On 8/28/93 at 0333 hours, with the Reactor Vessel cooldown in progress following a Reactor Shutdown for scheduled refueling, and with the 'B' loop Residual Heat Removal (RHR) system flushed and lined up for Shutdown Cooling, a Group 4 Primary Containment Isolation Signal (PCIS) was received while attempting to start the 'B' RHR pump. The Group 4 Isolation signal resulted in a trip of the 'B' RHR Pump and closure of Shutdown Isolation Valves. The Group 4 Isolation signal was reset and the 'B' RHR pump was successfully restarted for shutdown cooling at 0340. The root cause of this event was identified in LER 91-006 as a section of the RHR piping between the inboard check valve and the outboard injection valve remaining depressurized following the completion of a system flush prior the system initiation. Represurizing this section of piping during RHR pump starts caused a pressure surge in the 'B' RHR loop which resulted in a system isolation. Earlier procedural changes initiated to correct this problem during the 1992 Refueling Outage were successful although the pressure spike still existed. This pressure spike was not of sufficient magnitude to cause the Group 4 isolation. The procedure was altered to reduce the throttle time in an effort to prevent excessive flow through the system when the RHR pump is started. By reducing the throttle time, the procedure changes no longer corrects the initial problem. An evaluation is ongoing to review the data collected and determine the options for additional procedural changes or equipment modifications to correct this problem.
2711993012 | Vermont Yankee | 09/08/1993 | 01/19/1994 | 9401260073 | <strong>Appendix J Type B and C Failure Due to Seat Leakage</strong><br /><i>Abstract:&nbsp;</i>On 09/08/93 and 09/18/93 while performing Type C Leak Rate Testing with the Plant shutdown for the 1993 refuel outage, Containment Air check valve CA-89C (EIIS=LF) and Traversing Incore Probe (TIP) Ball Valve #2 (EIIS=IG) were found to have seat leakage above that permitted by Technical Specification 3.7.A.4. <br /><br /> On 09/08/93, the sum total as-found maximum pathway leakage for Type B (penetrations) and Type C (valves) exceeded that allowed by 10CFR50 Appendix J. The pathway leakage exceeded that allowed by Appendix J as a result of the leakage through check valve CA-89C. Appendix J limits the total B and C penetration leakage to 0.60 La.<br /><br /> Vermont Yankee has performed maintenance on the valves that were found to be leaking to determine and correct the cause of the failure. The valves have been retested to verify that seat leakage is within allowable limits. <br /><br /> The root cause for the failure of valve CA-89C is a design problem that allows dirt/corrosion fouling of the valve internals. The root cause of the TIP ball valve failure was not conclusively determined but appears to be related to a buildup of graphite type material on the valve internals.
2711993013 | Vermont Yankee | 09/18/1993 | 12/30/1993 | 9401100207 | <strong>Safety Related Switchgear Found to have Less Anchorage than required by the Original Plant Design</strong><br /><i>Abstract:&nbsp;</i>On 9/18/93, with the mode switch in Shutdown during a refueling outage, structural inspections were made of 4KV switchgear. The engineers inspecting the switchgear observed anchorage they believed to be insufficient to meet the plant's seismic design bases. The first bus inspected was 4KV bus 4, which is one of the main switchgear for safety related/ECCS loads. <br /><br /> In-service redundant 4KV bus 3 was also found with anchorage believed to be insufficient. Safety related 480V busses 8 and 9 were inspected and were also found to have anchorage believed to be insufficient to meet the plant's seismic design bases. <br /><br /> Busses 3 and 4 are designed to be welded or bolted to existing embedded channel in the floor. Busses 8 and 9 are designed to be bolted to existing embedded channel in the floor. The root cause was determined to be an original construction deficiency.<br /><br /> Immediate corrective actions included: welding the frame of busses 3 and 4 to the embedded channel, and bolting the frame of busses 8 and 9 through the embedded channel and into the concrete slab. <br /><br /> Review and analysis of the industry seismic experience data base lead to the conclusion that in the as-found condition, the switchgear were operable and would have functioned properly in a design basis seismic event.
2711993014 | Vermont Yankee | 09/24/1993 | 01/07/1994 | 9401180111 | <strong>Inoperable Alternate Cooling System due to Inadequate Inspection/Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On 10/09/93 while shutdown for refueling, the Alternate Cooling System was determined to be inoperable. The objective of the Alternate Cooling System is to provide an alternate means of shutdown cooling in the unlikely event of the failure of the Vernon Dam. The Alternate Cooling System provides a reservoir of water in a deep basin below the cooling tower. Silt and other materials accumulated in the Alternate Cooling System suction pipe pit in the deep basin, rendering the system inoperable. The root cause was determined to be personnel inadequately establishing acceptance criteria for inspection of the cooling tower basin and suction pit. Prior to plant startup, the entire cooling tower basin, suction pit, and suction pipe was thoroughly cleaned of all silt and debris. Inspection procedures, inspection frequency, and acceptance criteria will be reevaluated and revised. Revisions will be based upon the results of surveillance activities and identification of the deposition rate of silt during the next operating cycle. Modifications to the suction pipe and pit will be considered as part of this evaluation.
2711993015 | Vermont Yankee | 10/08/1993 | 01/07/1994 | 9401250150 | <strong>Low Pressure Core Spray Suction Strainers Found To Be Of Different Size Than Previously Assumed</strong><br /><i>Abstract:&nbsp;</i>During the 1993 Refueling Outage, inspections of the Low Pressure Core Spray (EIIS=BM) suction strainers were performed to respond to a BWR Owners Group request for information. On 10/08/93, it was identified that the size of the strainers was smaller than that assumed in the calculations of record. <br /><br /> The Low Pressure Core Spray Systems were not required to be operable at the time of the discovery. The suction strainers were replaced with larger strainers on 10/13/93 and 10/14/93, prior to returning the Low Pressure Core Spray Systems to operation. <br /><br /> The root cause for this event has been determined to be the use of unverified information on the size of the suction strainers in an NPSH analysis performed in 1986. This resulted in an incorrect conclusion that the strainers were of adequate size such that sufficient pump net positive suction head (NPSH) existed when post Loss of Coolant Accident (LOCA) debris loading was considered.
2711993016 | Vermont Yankee | 10/21/1993 | 11/22/1993 | 9312020473 | <strong>Generic Failure Mechanism in RHRSW Pump Motor Cooling Supply Due to Inadequate Original Construction Design Review</strong><br /><i>Abstract:&nbsp;</i>On 10/21 /93 while performing corrective maintenance and with the Plant shutdown for the 1993 refuel outage, three components in the motor cooling sub-system for each of the four Residual Heat Removal Service Water (EIIS = BI) Pumps were found to be under-rated for certain modes of system operation. <br /><br /> The root cause of this event is inadequate design review of a revision to the motor cooling sub-systems prior to initial commercial operation. <br /><br /> Vermont Yankee installed a temporary modification to revise the design to provide lower pressure water for the motor cooling sub-systems prior to Plant start-up from the 1993 refueling outage. A design change will be prepared and implemented to permanently revise the design.
2711993017 | Vermont Yankee | 10/24/1993 | 11/24/1993 | 9312020472 | <strong>Procedural deficiency resulted in bypass valves open with low condenser vacuum isolation bypassed</strong><br /><i>Abstract:&nbsp;</i>During startup from the 1993 refueling outage on 10/24/93, plant operations personnel were increasing power in parallel with efforts to establish condenser vacuum. The low condenser vacuum isolation switches were bypassed to allow the MSIVs to be opened to enable plant startup, as allowed by Note 10 of Tech Spec Table 3.2.2 and plant startup procedure OP 0101. This isolation signal normally closes MSIVs on low condenser vacuum which could jeopardize condenser integrity. <br /><br /> Contrary to Note 10 of Tech Spec Table 3.2.2, the turbine bypass valves were partially open before the low vacuum isolation bypass switches were returned to normal. When the event was discovered, operators raised the MPR setpoint to close the bypass valves. The root cause of the event was a procedural deficiency which resulted in a personnel error.
2711993018 | Vermont Yankee | 12/17/1993 | 03/18/1994 | 9403230292 | <strong>Group 4 Primary Containment Isolation on Initiation of "A" Shutdown Cooling System due to Pressure Spike</strong><br /><i>Abstract:&nbsp;</i>On 12/17/93 at 1844 hours, with the Reactor Shutdown and vessel cooldown in progress for repairs to the main condenser to correct inleakage, and with the 'A' loop Residual Heat Removal (RHR) system flushed and lined up for Shutdown Cooling (SDC), a Group 4 Primary Containment Isolation Signal (PCIS) was received while attempting to start the 'A' RHR pump. The Group 4 Isolation signal resulted in a trip of the 'A' RHR Pump and closure of Shutdown Cooling Isolation Valves. The Group 4 Isolation signal was reset and the 'A' RHR pump was successfully restarted for shutdown cooling at 1857. The cause of this event is a pressure spike caused by the collapse of voids formed between the Injection valve and the downstream check valve upon startup of the 'A' RHR pump. The Root Cause has been determined to be in the original design specification in that no high point vent was factored into the RHR SDC loop to address voids in the piping. An engineering evaluation and a review of piping an vessel thermal analyses has resulted in a proposed procedural changes for an alternate fill path from the condensate transfer system which will eliminate voids prior to system startup. Supplemental instrumentation will be installed on the RHR SDC system piping to monitor the effectiveness of the proposed procedure change.
2721993001 | Salem 1 | 01/11/1993 | 02/09/1993 | 9302170235 | <strong>Inoperability of Analog Rod Position Indication for Maintenance Troubleshooting.</strong><br /><i>Abstract:&nbsp;</i>On 1/11/93, from 1038 to 1039 hours and from 1041 to 1043 hours, Technical Specification (TS) 3.0.3 was entered for action beyond TS 3.1.3.2.1, due to removing the main and auxiliary 115-volt alternating current power supply fuses to the 13-volt direct current power supply for the Analog Rod Position Indication (ARPI) system. Fuse removal eliminated the possibility of electrically shorting the ARPI signal conditioning module of control rod 2D4 and damaging the 13-volt dc power supply during troubleshooting of erratic 2D4 indication. Nuclear Shift Supervisor (NSS) approval was obtained prior to removing the fuses and he was advised of the consequences of removing the fuses. channel check showed the ARPI system operable, and TS 3.0.3 was exited. Upon a Reactor trip, I&C technicians, performing the troubleshooting, could have reinstalled the fuses restoring the ARPI. The 2D4 ARPI erratic indication resulted from failure of the 2D4 ARPI connector at the Reactor vessel head. Pipe flange leakage, immediately upstream of the Reactor head vent manual isolation valve, corroded the connector wire. The leakage was stopped through a temporary modification and the connector was repaired, restoring proper indication for 2D4. During the next unit refueling, a design change will be installed to relocate the involved flange to eliminate a potential leak path that could affect ARPI connections.
2721993002 | Salem 1 | 01/16/1993 | 02/21/1993 | 9302220468 | <strong>Manual Reactor Trip due to Trouble with the Turbine Bypass System</strong><br /><i>Abstract:&nbsp;</i>On 1/16/93, during shutdown to Mode 3 (Hot Standby) for maintenance, a manual reactor trip was initiated when 12 Steam Generator Feedwater Pump (SGFP) tripped (11 SGFP was cleared and tagged) due to a turbine trip/feedwater isolation signal (from a 13 Steam Generator (S/G) High-High Level signal). Prior to the turbine trip, Turbine Bypass System control was being transferred from 'T sub ave' to 'Steam Pressure'. During this evolution, Turbine Bypass Valves went full open causing a S/G 'swell'. 13 S/G swelled to the high-high level alarm setpoint resulting in the turbine trip/feedwater isolation signal, an Engineered Safety Feature (ESF). Per design, the 20 valves which provide steam from the S/Gs to the Turbine-Generator isolated and the operating SGFP tripped. Following this, the Turbine Bypass System valves were closed and a manual Reactor trip was initiated. Plant response was as expected following the reactor trip including the degree of Reactor Coolant System cooldown (as has occurred after prior plant trips). Per procedure, a Main Steamline Isolation (an ESF) was initiated stopping the cooldown. The plant was stabilized in Mode 3. The root cause of this event is equipment failure. The Turbine Bypass Pressure Controller and the associated servo potentiometer module of the Turbine Bypass Control System failed causing the controlling station setpoint to go from approximately 1040 psi to 196 psi in approximately 5 seconds. This caused the Turbine Bypass Valves to fully open. The faulty Turbine Bypass System components were replaced. The Unit was returned to service 1/24.
2721993003 | Salem 1 | 01/27/1993 | 02/22/1993 | 9302230313 | <strong>Inoperability of Both Boric Acid Storage Tanks' Level Indication.</strong><br /><i>Abstract:&nbsp;</i>On 1/23/93, at 2330 hours, and 1/27/93, at 1410 hours, the level indicator of No. 11 BAST was declared inoperable due to respective false high level indications. In each case, No. 12 BAST was unavailable, Action 3 as shown in TS Table 3.3-11 was not met, and action associated with Technical Specification 3.0.3 was entered. In each case, TS 3.0.3 was subsequently exited (at 0002 hours on 1/24/93 and 1440 hours on 1/27/93) upon respective restoration of No. 11 BAST level indicator to service. The root cause of each event is design of the BAST level indication system. BAST level indication failures have been a recurring problem at both Salem Units and result from bubbler tube blockage. Several past corrective actions have been unsuccessful. No. 12 BAST inspection and cleaning revealed a boron slug accumulation in the bubbler tube bottom two inches. The No. 11 and No. 12 BAST's and the bubbler tubes of each tank were inspected and cleaned. The corresponding Unit 2 Nos. 21 and 22 BASTs will be inspected and cleaned. The bubbler tube nitrogen flow rates of both Salem Units have been readjusted to 3 scfh, to minimize boric acid precipitation. A design change is being developed which includes reducing BAST boron concentration to help minimize boron precipitation in the level indicator bubbler tubes. System Engineering is continuing to monitor BAST level indication to determine adequacy of current corrective action and to determine additional actions, such as periodic steam cleaning, until implementation of the design change.
2721993004 | Salem 1 | 02/16/1993 | 03/11/1993 | 9303190144 | <strong>Automatic Reactor Trip Due to Overtemperture Delta Temperature Trip Signal (2/4 channels).</strong><br /><i>Abstract:&nbsp;</i>At 1656 hours on 2/16/93, an automatic reactor Overtemperature Delta Temperature (OTDT) signal (2/4 channels) occurred due to tripping the OTDT Loop 11 Channel I bistables while the Loop 13 bistables were already tripped for ongoing Nuclear Instrumentation channel calibration. The unit was stabilized in Hot Standby. The root cause of this event is failure of the gain selector switch of Loop 11 OTDT input module QM-411B due to intermittent high contact resistance. This resulted in the Loop 11 OTDT setpoint decreasing to the point of actuating the loop bistables. A large spurious spike on the input to the Loop 11 OTDT setpoint calculator drove it down which provided the necessary coincident logic to trip the loop bistables. Testing showed the QM-411B flux module output would trip high erratically with heat or minimal physical agitation. The 1QM411B module output gain selector switch, as well as the gain selector switches of the OTDT input modules for the balance of the unit's loops, were cleaned and exercised prior to the subsequent Reactor startup. Preventive Maintenance (PM) requirements for the subject modules (Westinghouse-Hagan) are being assessed to identify required changes to help ensure module service reliablity.
2721993005 | Salem 1 | 02/18/1993 | 03/22/1993 | 9303250090 | <strong>RPS actuation: Reactor Trip/Turbine Trip Signal due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 2/18/93, at 0835 hours, Unit 1 experienced a Reactor Protection System Reactor Trip/Turbine Trip signal, when 12 Steam Generator (SG) level decreased to 25%. This level satisfied the reactor trip signal for SG low level coincident with steam flow/feed flow mismatch. The mismatch signal was satisfied by ongoing 12 SG steam flow channel I circuit troubleshooting, which manually tripped the channel bistables. 12 SG level, which was reduced to between 24 and 25%, was restored within approximately 7 minutes. Reactor Coolant System (RCS) T sub ave was being maintained via the Auxiliary Feedwater System (AFW) in conjunction with the respective MS10 atmospheric relief valves. The root cause of this event is personnel error due to misjudgment by the secondary console Operator. He chose to increase Ta e by reducing AFW flow to 12 SG level to support completion of an in-progress RCS leak rate surveillance. This event has been reviewed by Operations Department management and disciplinary action has been taken. This event will be reviewed with applicable Operations Department personnel. This event will be reviewed by the Nuclear Training Center for incorporation in applicable training programs.
2721993006 | Salem 1, Salem 2 | 02/21/1993 | 03/23/1993 | 9303260150 | <strong>Tech Spec Required Shutdown Due to Loss of One Offsite</strong><br /><i>Abstract:&nbsp;</i>At 1332 hours on 2/21/93, the 2 Station Power Transformer (SPT), 12 SPT, and 22 SPT deenergized due to tripping (open) the Units' common 13KV ring bus section 4 breakers and 500KV section 1 breakers. This resulted from closing the site 13KV gas turbine/generator (Unit 3) output breaker (3TG) onto the energized 13KV ring bus, while Unit 3 was not running. Unit 1 was in MODE 2 and Unit 2 was at 100% while troubleshooting the breaker during testing of Unit 3. Unit 1 was shutdown to MODE 3, as per Technical Specification (TS) 3.4.1.1, due to loss of 13 and 14 Reactor Coolant Pumps. TS 3.8.1.1 was entered for both units due to loss of an independent offsite AC power source to each unit. The root cause of this event is personnel error. Due to inadequate communication between personnel involved with troubleshooting a problem with the breaker, it was closed. A contributing factor was insufficient knowledge of the breaker and the associated relay operation. Caution tags were hung on the 3TG breaker and its control switch. The importance of communications and adhering to proper command and control has been reinforced. Lessons learned were discussed with station management and the involved personnel. The existing Lamacoid at the 3TG breaker cubicle will be replaced with a different one to provide better information concerning racking-out the breaker. The 3TG breaker and the protective interlocks affected by operation of the breaker will be assessed for appropriate training and design enhancements.
2721993007 | Salem 1 | 02/25/1993 | 03/25/1993 | 9303310325 | <strong>2 Tech Spec 3.0.3 Entries; More Than 1 Analog Rod Position Indicator Per Bank Inop.</strong><br /><i>Abstract:&nbsp;</i>On 2/24/93, at 2024 hours, Control Rod 1D4 Analog Rod Position Indication (ARPI) was discovered indicating greater than a +/- 12 step deviation from its group demand counter. Technical Specification (TS) 3.1.3.2.1a Action 'a' was entered. Initial investigation indicated high resistance readings at the coil stacks. On 2/25/93, at 1514 hours and on 2/26/93, at 2126 hours, the ARPI for Control Rod 2D1 (both times) was found indicating greater than a +/- 12 step deviation from its group demand counter. Since ARPI indication for Control Rod 1D4 had not been corrected from 2/24/93, TS 3.0.3 was entered each time. Flux traces verified that Control Rods 2D1 and 1D4 were correctly positioned. When more than one ARPI per bank is inoperable, TS 3.1.3.2.1a is exceeded; therefore, TS 3.0.3 applies. On 2/25/93, at 1522 hours, TS 3.0.3 was exited after the 2D1 control rod position indication was corrected. On 2/26/93, at 2212 hours, TS 3.0.3 was exited after the 2D1 control rod position indication returned to within +/- 12 steps of the group demand position. The root cause of these events is system design. The ARPI system electronics settings, associated with the coil stack, will have some drift due to the stacks' susceptibility to temperature change. Investigation of the Control Rod 1D4 coil stack concern revealed that the high resistance reading was not correct. The high reading was due to AC induced noise from other coil stacks in the vicinity. On 2/27/93, after adjustment of the 1D4 control rod position indication, TS 3.1.3.2.1a Action 'a' was exited.
2721993008 | Salem 1, Salem 2 | 03/04/1993 | 04/02/1993 | 9304080266 | <strong>Design Concern - Control Air Containment Isolation Valves Fail As-Is on Loss of Power</strong><br /><i>Abstract:&nbsp;</i>Engineering assessment determined on 3/4/93 that design of the Control Air (CA) System air-operated containment outboard isolation valves on both Salem Units is not as described in the units' Updated Final Safety Analysis Report (UFSAR). These valves (11 and 12 CA330 on Unit 1 and 21 and 22 CA330 on Unit 2), which are normally open, fail 'as-is' on loss of 125VDC power to their solenoid actuators. UFSAR Section 6.2.4.3 states that automatic isolation valve closures are fail safe (initiate closure) upon loss of voltage and/or control air. UFSAR Section 7.3.2.5 states air-operated containment isolation valves were designed to close upon loss of power. General Design Criterion (GDC) 56, dated July, 1971, of 10CFR50, Appendix A, requires containment isolation valves to go to their position of greater safety upon loss of actuating power. This condition is attributed to Design, Manufacturing, construction/Installation during design of Salem Units 1 and 2. A Justification for Continued Operation has determined the as-built design of the CA330 valves is appropriate with no changes required. PSE&G is providing the NRC with additional information (in accordance with 10CFR50.90) detailing this event. Pending completion of the NRC review, the UFSAR and design documentation will be revised as applicable. A review of all other air operated containment isolation valves was conducted. This review determined that these valves fail in accordance with their UFSAR design requirements.
2721993009 | Salem 1 | 03/06/1993 | 04/01/1993 | 9304080152 | <strong>Inoperability of 12 Boric Acid Storage Tank Level Indication with 11 BAST Out of Service.</strong><br /><i>Abstract:&nbsp;</i>At 0050 hours, on 3/6/93, the 12 Boric Acid Storage Tank (BAST) level indicator was declared inoperable due to false high level indication. At the time 11 BAST was out of service for maintenance. Therefore, Action 3 of Technical Specification (TS) Table 3.3-11 was not met, and the TS 3.0.3 was entered. 12 BAST level indication was returned to service and TS 3.0.3 was exited, at 0140 hours (same day). The root cause of this event is 'Design, Manufacturing, Construction/Installation' of the BAST level indication system. BAST level indication failures at both Salem Units result from bubbler tube blockage caused by boron precipitation in the BAST level bubbler tubes. Past corrective actions, on both Units' BASTs, included adjustments to the nitrogen flow rate, increasing the system blowdown frequency to once/seven days, and cleaning the bubbler tubes. A design change is being developed which includes reducing BAST boron concentration to help minimize boron precipitation. An Engineering Work Request has been initiated to increase the BAST temperature controller setpoint on both units to 180-190 degrees F to help minimize boron precipitation. A recurring task has been established for routine steam cleaning of both units' BAST bubbler tubes. system Engineering is monitoring BAST level indication failures to determine adequacy of current corrective actions. Following completion of maintenance, 11 BAST was returned to service.
2721993010 | Salem 1, Salem 2 | 04/07/1993 | 05/04/1993 | 9305110314 | <strong>Less Than Design Service Water Flow through the Diesel Generators' Jacket Water Cooler</strong><br /><i>Abstract:&nbsp;</i>On 4/7/93, it was determined that Service Water (SW) flow through the Diesel Generators' (DGs') jacket water and lube oil coolers (installed in series) was less than the design requirement of 700 gallons per minute (GPM). Engineering determined that operability of the coolers is unaffected at SW inlet temperatures less than 60 degrees F. This condition was due to an incorrect setpoint, which existed from the original 1978 System Description. This setpoint is for the differential pressure (D/P) controllers that modulate the cooling water outlet control valves of the three (3) DG's on each Salem Unit. A D/P drop of approximately 12 pounds per square inch gauge (PSIG) across the flowpath of the coolers (installed in series) is needed to achieve the required flow rate. However, the setpoint was 6 PSIG, which matched the D/P drop required to achieve this flow across a single cooler. This event was identified through investigation of unexpected flow and D/P readings across DG 'C' jacket water and lube oil coolers during flow testing for upgrading the SW piping of the Unit 2 DGs. The proper setpoint for the control valves was determined, verified by field testing, added to the plant database via design changes, and subsequently implemented for both Units during the week of 4/19/93.
2721993011 | Salem 1 | 06/08/1993 | 07/08/1993 | 9307150058 | <strong>Reactor Trip from 85% Power; 4 Circulating Water System Circ. Pumps Tripped due to Debris.</strong><br /><i>Abstract:&nbsp;</i>On 6/8/93, at 1745 hours, an automatic reactor trip from 85% power occurred due to a Main Turbine trip from low condenser vacuum and P-9 trip permissive (i.e. reactor trip on turbine trip > 50% power). This occurred during diver cleaning of the unit Circulating Water System (CWS) trash racks. Prior to this event a turbine load reduction had been initiated and a subsequent order had been given, at 1744 hours, to manually trip the reactor in response to decreasing condenser vacuum. However, before the trip was initiated, the automatic reactor trip occurred. The vacuum decrease resulted from manual tripping of 13A CWS pump and automatic tripping of 12A, 11B, and 11A CWS pumps due to high differential pressure across the pumps' traveling screens. The unit was stabilized in MoDE 3 (Hot Standby). The root cause of this event is 'Management/Quality Assurance Deficiency' with a contributing causal factor of 'External'. specific contributing factors include trash rack debris removal, maintenance of the trash rake which limited its ability to adequately clean the trash racks, and not implementing a past corrective action to modify the trash rake. Unit 1 CWS trash rack cleaning was completed prior to subsequent Unit startup. The circulating water intake structure was dredged. The CWS trash rack rake will be overhauled or replaced. The practice of using divers to clean CWS trash racks will be evaluated to help reduce risks associated with this type activity. Administrative controls will be developed and implemented, as appropriate, to address operation of the CWS trash racks' rake.
2721993012 | Salem 1 | 06/09/1993 | 07/08/1993 | 9307150052 | <strong>ESF Actuation; 1C 4KV Vital Bus Undervoltage Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1993, at 1443 hours, 1C Vital Bus sensed an undervoltage condition resulting in an automatic start and blackout loading of 1C Diesel Generator (D/G). The automatic D/G start and loading is an Engineered Safety Feature (ESF). At the time of the event, Maintenance personnel were conducting the monthly functional surveillance test of the 1C 4KV Vital Bus in accordance with procedure S1.MD-FT.4KV-0003 (Q), 'ESFAS Instrumentation Monthly Functional Test 1C 4KV Vital Bus Undervoltage'. The root cause of the 1C Vital Bus trip is personnel error attributed to inattention to detail. The Maintenance technician did not self-check as required by station work practices. The technician conducting the monthly functional surveillance test was supposed to place the 1B3 test signal switch (one (1) of three (3) SEC 91% undervoltage test signal switches located on the 1C SEC lower section) to the 'off' position. He inadvertently placed one (1) of the other two (2) test signal switches to the 'on' position satisfying the logic for single vital bus undervoltage ESF Mode Op sequence. This event has been reviewed by Maintenance Department management. Positive disciplinary action with the individual(s) involved has been completed. The circumstances surrounding this event will be reviewed with applicable Maintenance Department personnel.
2721993013 | Salem 1 | 07/19/1993 | 08/12/1993 | 9308190119 | <strong>Rx Trip On 14 Steam Generator Low Level Coincident With SF/FF Mismatch & TS Noncompliance.</strong><br /><i>Abstract:&nbsp;</i>On 7/11/93, at 2038 hours, the Unit experienced a reactor/turbine trip signal due to steam flow/feed flow mismatch coincident with low level in 14 Steam Generator (SG). This trip resulted from closure of 14 SG Feedwater Regulating Valve, 14BF19. Shutdown had been in progress per Tech. Spec. 3.3.2.1 Action 13, due to inoperability of part of the Solid State Protection System (SSPS). It was determined that relay BD601 was inoperable requiring its removal. During relay removal, the 125 VDC lead to the component normal actuation circuit was removed causing associated components (solenoid valves for the 14BF19 valve and its bypass valve, 14BF40) to deenergize. The 14BF19 valve closed per design (14BF40 was already closed) causing the trip. The root cause is personnel error. Due to inattention to detail, the maintenance supervisor did not fully assess the affect of disconnecting the BD601 wiring. Corrective discipline has been taken with the supervisor. This event will be reviewed with applicable personnel. Relay BD601 was replaced. On 8/5/93, management review of the reactor trip event investigation determined that the SSPS slave relay operability determination was not diagnosed accurately on 7/11/93, at 0530 hours, and that expeditious troubleshooting was not initiated as appropriate. The cause of this event is personnel error. Appropriate corrective discipline will be taken with the operations personnel involved. This event will be reviewed with all licensed operator personnel.
2721993014 | Salem 1, Salem 2 | 07/22/1993 | 10/05/1994 | 9410200158 | <strong>Voluntary Reporting of 4 Kilo-Volt Vital Bus Second Level Undervoltage (UV) Protection Dropout Setpoint.</strong><br /><i>Abstract:&nbsp;</i>On 7/22/93, it was determined that the 91.6% dropout setpoint for second level undervoltage protection of both Salem Units' 4 kilovolt (KV) vital buses would not fully protect the 230 and 460 volt (V) motors should the 4KV bus voltage degrade to less than 93.2%, but greater than 91.6%. At that time it was concluded the intent of the Updated Final Safety Analysis Report and guidance provided in 'Safety Evaluation And Statement Of Staff Positions Relative To The Emergency Power Systems For Operating Reactors' NRC letter, dated 6/2/77, were not fully met. Continued operation of both Salem Units was based upon self-imposed administrative controls on 4KV bus alignment until implementation of design changes to change the dropout setpoint. A subsequent detailed study shows the motors would have performed their intended safety functions with the 91.6% setpoint. As such, this report is made voluntarily for informational purposes.
2721993015 | Salem 1 | 09/13/1993 | 10/07/1993 | 9310180256 | <strong>T/S 3.0.3 Entries; Inoperability Of 12 BAST Level Indication With 11 BAST Out Of Service.</strong><br /><i>Abstract:&nbsp;</i>On 9/13/93, at 0137 hours, and 9/16/93, at 0935 hours, the 12 Boric Acid Storage Tank (BAST) level indicator was declared inoperable due to false level indications. In each case 11 BAST was unavailable, Technical Specification (TS) Table 3.3-11 could not be met, and action associated with TS 3.0.3 was entered. Following each event, TS 3.0.3 was then exited (at 0210 hours on 9/13/93, and at 1015 hours on 9/16/93) upon restoration of 12 BAST level indicator to service. The root cause of each event is design of the BAST level indication system. BAST level indication failures have been a recurring problem at both Salem Units and result from bubbler tube blockage. Past corrective actions to this design problem have been marginally effective. Both events resulted from blockage of the 12 BAST level indicator bubbler tube. Following each event, the bubbler tube was blown down to remove blockage and level indication returned to normal. The recurring task for blowdown of the bubbler tubes on each unit will be revised to specify use of Control Air. A design change, which includes reducing the BAST boron concentration to 4% to help minimize boron precipitation in the tank level indicator bubbler tube, is scheduled to be implemented. A similar Unit 2 design change will also be implemented.
2721993016 | Salem 1 | 10/21/1993 | 11/22/1993 | 9312020421 | <strong>ESF Actuation; Diesel Generator Blackout Signal Loading of 1A & 1C 4KV Vital Bus</strong><br /><i>Abstract:&nbsp;</i>On 10/21/93, at 1525 hours, the infeed breakers to 1A and 1C 4 Kilo-Volt (KV) buses tripped on an undervoltage (UV) signal, resulting in automatic starting and 'blackout signal' loading of the buses from 1A and 1C Diesel Generators (D/Gs). At approximately 2030 hours (same day), infeed power to the buses from 12 Station Power Transformer (SPT) was restored and the D/Gs were secured and returned to standby. The root cause of this event is electrical shorting within the 4KV switchgear, due to personnel error associated with ongoing relay maintenance activities. The electrical shorting most probably occurred between adjacent terminals on the 12 SPT undervoltage (UV) relay circuit within the B vital bus 12BSD breaker cubicle. As a result of this event, work associated with SPTs and 4KV vital switchgear was reevaluated to ensure minimized plant safety risk. Increased coordination of activities and the importance of exercising caution in the vicinity of 4KV switchgear and protective relays was emphasized with key supervisory personnel and workers. A vital bus and switchyard work standdown was imposed by the station General Manager, to allow review of remaining outage-related activities. Station outage management will review scheduling of similar activities to ensure incorporation of lessons learned into future outage schedules.
2721993017 | Salem 1 | 11/06/1993 | 12/03/1993 | 9312130423 | <strong>ESF Actuation; Diesel Generator Blackout Signal Loading of 1B 4KV Vital Bus.</strong><br /><i>Abstract:&nbsp;</i>On 11/6/93, at 0859 hours, while attempting to transfer offsite power to 1B 4 Kilo Volt (KV) Vital Bus from 12 Station Power Transformer (SPT) to 13 SPT for testing, 13BSD (infeed breaker from 13 SPT) failed to close. This resulted in automatic starting and 'blackout signal' loading of the bus from 1B Diesel Generator (D/G). 11th refueling outage was in progress with the Reactor defueled. Equipment functioned as required and spent fuel pit cooling was maintained during this event. At 0943 hours (same day), 13 BSD was closed to establish infeed power to the bus from 13 SPT and 1B D/G was secured and returned to standby. 13BSD had failed to close because the breaker control power was turned off. Root causes of this event are personnel error, inadequate communication, and procedure inadequacy due to insufficient detail in the test procedure. Discipline, in accordance with our Positive Discipline Program, has been conducted concerning the personnel error. An Information Directive will be provided to all appropriate personnel. The test procedure will be revised to provide adequate detail prior to implementation for Unit 2.
2721993018 | Salem 1, Salem 2 | 12/03/1993 | 01/03/1994 | 9401110191 | <strong>Inadequate Testing of Both Salem Units' Containment Spray Actuation Instrumentation.</strong><br /><i>Abstract:&nbsp;</i>On 12/3/93, during a review for NRC information Notice 93-38, it was determined that monthly testing of the Solid State Protection System (SSPS) Containment Pressure Hi Hi Input Channels (Containment Spray - CS) did not verify that the SSPS input circuit path is reclosed following testing (applicable to both Salem Units). If a switch/relay contact in this circuit path that was opened for the monthly testing did not close, the CS channel(s) affected would be inoperable with no visual/audible indication. 18-month interval test procedures did verify that the channel input circuit path is closed. The CS channel is normally deenergized and must be energized to provide input to the SSPS therefore, a verification step is required. Following event discovery, circuit integrity of both Units' affected channels was confirmed. The root cause of this event is 'Design, Manufacturing, construction/ Installation', per NUREG-1022. Vendor Manual Instructions, used to develope the test procedures for initial plant startup and initial issue of the surveillance procedure, do not address circuit verification. A contributor is the design of the CS input circuitry, which is reversed as compared to the standard SSPS circuit. Procedures will be revised to verify reclosure of the respective channels' Containment Hi Hi Pressure Bistable Test Switch after repositioning and to verify reclosure of the Spray Channel Test Relay contacts after operating the Spray Test Channel pushbuttons. Other normally deenergized SSPS input circuits, which must energize to perform their protective functions, will be reviewed for applicability to NRC Information Notice 93-38.
2721993019 | Salem 1 | 12/05/1993 | 01/04/1994 | 9401310028 | <strong>Waste Gas Holdup System Oxygen Concentration Greater Than 2% For More Than 48 Hours.</strong><br /><i>Abstract:&nbsp;</i>Oxygen (O sub 2) concentration within the Waste Gas Holdup System was > 2% for > 48 ours. On 12/3/93, at 0910 hours, Technical Specification (TS) Action Statement 3.11.2.5.a. was entered due to O sub 2 concentration of 2.17% by volume in 13 Waste Gas Decay Tank (WGDT). Efforts to reduce the O sub 2, concentration to < 2% were implemented. O sub 2 concentrations above 2 were subsequently measured in other WGDTs; 3.04% in 11 WGDT on 12/8/93, 3.11% in 14 WGDT on 12/8/93, and 3.29% in 12 WGDT on 12/9/93. The maximum O sub 2 concentration was 4.25% in 13 WGDT on 12/4/93. The root cause is attributed to 'Design, Manufacturing, Construction/Installation', as per NUREG-1022. The source of the O sub 2 is attributed to routine refueling/maintenance outage activities. In addition, extensive modifications to the Waste Gas Analyzer and Waste Gas System were performed requiring these systems be opened. Prior to closure, steps were performed to purge these systems with nitrogen. However, the design of these systems does not lend itself to effective purging. Furthermore, the calibration of the Waste Gas Analyzer introduced additional O sub 2 into the system. This was further complicated due to the fact that the online O sub 2 analyzer was out of service for replacement. O sub 2 concentration within the Waste Gas System was reduced to < 2% on 12/12/93, at 0408 hours, at which time the TS Action Statement was exited. Lessons learned from this event will be incorporated into future planning regarding Waste Gas System modifications.
2721993020 | Salem 1, Salem 2 | 12/23/1993 | 01/21/1994 | 9402030337 | <strong>RCS Accumulator Upper Range Level Indication Inaccuracies Affecting Both Salem Units.</strong><br /><i>Abstract:&nbsp;</i>Since initial startup of the units, the upper Technical Specification limit of 6,500 gallons for borated water volume in each Reactor Coolant System (RCS) accumulator may have been exceeded. Discovery occurred on 12/23/93 while investigating problems with implementing revised unit 1 RCS accumulator level scaling factors. This event occurred due to calibrations of six Unit 1 and seven Unit 2 level transmitters for the RCS accumulators using incorrect original scaling factors. Use of the original scaling resulted in inaccuracies: The effect of these inaccuracies was conservative for the low level alarm and indication and nonconservative for the high level alarm and indication. Westinghouse assessment shows this event does not involve a significant safety concern. The root cause is Design, Manufacturing, Construction/ Installation. adequately consider elevation differences between the accumulators' upper sensing bellows and taps. The accumulators on both Units have been correctly rescaled. Controlled scaling for the RCS accumulators level transmitters has been issued. Design drawings will be updated to reflect the as-built configurations of the RCS Accumulator level taps and sensing bellows, as depicted in plant surveys. Appropriate E&PB personnel have been made aware of the importance of reviewing existing plant scaling information as part of the verification of new scaling calculations.
2751993001 | Diablo Canyon 1, Diablo Canyon 2 | 01/13/1993 | 10/17/1994 | 9410210279 | <strong>Component Cooling Water System Potentially Outside Design Basis Due to Nonconservatisms in the Designs-Basis Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993, with Units 1 and 2 in Mode 1 at 100 percent power, PG&E determined that, under a combination of worst-case conditions and parameters, the component cooling water (CCW) system water temperature design-basis temperature limits may be exceeded. A one-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(1)(ii)(B) on January 13, 1993, at 1053 PST.<br /><br /> The root cause of this event was nonconservatisms in the design- basis analysis for the CCW system. The design records do not contain sufficient information to conclude whether the root cause of this event was an error, an oversight, or that it was the judgment of the engineer that the effect on the conclusions of the analysis were insignificant. <br /><br /> Surveillance Test Procedure V-13A, 'CCW Flow Balancing,' was revised to implement the CCW flow balancing calculations. Also, STP M-51, 'Routine Surveillance Test of Containment Fan Cooler Units,' was revised to assure the flow balance requirements are verified during routine testing to demonstrate compliance with the Technical Specifications.
2751993002 | Diablo Canyon 1 | 01/08/1993 | 02/08/1993 | 9302170253 | <strong>Containment Isolation Valve Not Isolated In Accordance With Technical Specification 3.6.3 Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1993, at 0739 PST, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.6.3 was not met when chemical and volume control system Unit 1 relief valve (RV) CVCS-1-RV-8117 failed to fully reseat during the performance of Surveillance Test Procedure P-17B, 'Surveillance Test of Reciprocating Charging Pump.'<br /><br /> On January 8, 1993, at 1415 PST, TS 3.6.3 was exited when CVCS-1-RV-8117 reseated. <br /><br /> The root cause of this event is personnel error (cognitive), in that non-licensed plant personnel failed to properly implement License Amendment Nos. 72 and 73, which permitted removal of TS 3.6.3 containment isolation valves to Administrative Procedure (AP) C-3S1, 'Surveillance Testing and Inspection.' <br /><br /> Additional reviews will be added to the license amendment implementation process to ensure that this event does not recur. AP C-3S1 will be revised to include CVCS-1-RV-8117 on the list of containment isolation valves in accordance with the plant licensing basis. During the next Unit 1 refueling outage, CVCS-1-RV-8117 will be inspected and repaired, if necessary. Operations Annunciator Response PK 04-21, 'Letdown Press/Flo Temp,' was revised to provide guidance to plant operators on immediate actions to be taken when the containment penetration affected by this condition is inoperable. 1092S/85K
2751993003 | Diablo Canyon 1, Diablo Canyon 2 | 01/08/1993 | 06/01/1993 | 9308310256 | <strong>Low Temperature Overpressure Protection Setpoint Analysis Nonconservatism Due To Miscommunication</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1993, at 1500 PST, with Units I and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that a condition existed that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. The pressurizer power-operated relief valve setpoint had been calculated without consideration of the pressure drop between the core beltline and the low temperature pressure sensor due to the dynamic pressure effect of running a reactor coolant pump (RCP) and the effect of elevation head. On January 8, 1993, at 1605 PST, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(D). <br /><br /> During the review of operating experiences at another nuclear power plant, PG&E determined that a similar condition existed at Diablo Canyon. <br /><br /> The immediate cause was that the Westinghouse Low Temperature Overpressure Protection setpoint analysis did not consider the above-mentioned nonconservatisms. The root cause of this event was determined to be the result of miscommunication during the collaborative efforts between Westinghouse and a Westinghouse Owners Group subcommittee when establishing parameters for the LTOP setpoint analysis. <br /><br /> Corrective actions for this event included restricting RCP operation at low temperature conditions.
2751993004 | Diablo Canyon 1, Diablo Canyon 2 | 07/21/1993 | 10/18/1993 | 9310290090 | <strong>Non-Conservative Penalty Used For The Heat Flux Hot Channel Factor Multiplier Due To Vendor Oversight</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being submitted for information only purposes as described in Item 19 of Supplement 1 to NUREG-1022.<br /><br /> The heat flux hot channel factor penalty of 2 percent in Technical Specification (TS) 4.2.2.2.e. was identified by PG&E personnel as being potentially non-conservative during the Unit 1 Cycle 6. The penalty of 2 percent was assumed by Westinghouse in the development of TS 4.2.2.2.e. to conservatively bound decreases in the heat flux hot channel factor margin between monthly core flux maps for anticipated increases in the heat flux hot channel factor. Units 1 and 2 have experienced decreases in the heat flux hot channel factor margin of more than 2 percent between monthly flux maps in the early portions of Unit 1 Cycle 6 and Unit 2 Cycles 4 and 5. <br /><br /> The root cause of this event was vendor oversight. A Westinghouse interim methodology for calculating a conservative penalty to the heat flux hot channel factor has been implemented. PG&E will implement, as appropriate, Westinghouse's long-term resolution of the heat flux hot channel factor non-conservative penalty issue.
2751993006 | Diablo Canyon 1, Diablo Canyon 2 | 10/06/1993 | 11/05/1993 | 9311160231 | <strong>Technical Specification 3.3.3.10 Explosive Gas Effluent Monitoring Action Requirement Violations Due To Personnel Error During Original Procurement</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1993, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E conservatively declared the waste gas oxygen analyzers inoperable due to unexpected inaccuracy. <br /><br /> On October 6, 1993, a PG&E Technical Review Group determined that when the hydrogen concentration in the waste gas system exceeded ten percent by volume, the waste gas oxygen analyzer channel uncertainties exceeded setpoint requirements and might not assure alarms in accordance with Technical Specification (TS) 3.11.2.5 limits. Thus, TS 3.3.3.10 was not met whenever the hydrogen concentration was greater than ten percent by volume, since grab samples were not collected at least once per four hours and analyzed within the following four hours. <br /><br /> The immediate corrective actions are to take and analyze grab samples in accordance with TS 3.3.3.10 until a design change has been implemented to replace the existing waste gas oxygen analyzers and associated loop instruments with equipment not subject to hydrogen interference. In addition, other analysis systems are being reviewed for possible interference mechanisms. Significantly improved engineering procedures, checklists, and guidelines (since the 1979 timeframe) should preclude this event from happening again.
2751993007 | Diablo Canyon 1, Diablo Canyon 2 | 08/18/1992 | 05/28/1993 | 9306100053 | <strong>Technical Specification 6.8.4.E Not Met Due To Inadequate Review Of Licensing Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1992, Technical Specification (TS) 6.8.4.e, 'Post-Accident Sampling,' was not met when PG&E discontinued the qualified remote grab sample gas chromatograph method as a backup for monitoring reactor coolant dissolved hydrogen. NUREG-0737 Item II.B.3 requires a backup method that meets the 10 CFR 50 General Design Criterion (GDC) 19 dose limit criteria. TS 6.8.4.e establishes the program that meets these regulatory requirements. In addition, the Unit 2 in-line monitor (primary method) was unavailable for a period of time.<br /><br /> The root cause was determined to be personnel error (cognitive) in that non-licensed plant personnel did not adequately review NUREG-0737 requirements. <br /><br /> As a corrective action, a backup method for monitoring dissolved hydrogen that met GDC 19 criteria was implemented. The procedures for reactor coolant dissolved hydrogen analysis were revised. Formal training of assigned shift chemistry and radiation protection technicians was provided. <br /><br /> In addition, pursuant to Item 19 of Supplement 1 to NUREG 1022, PG&E is submitting information regarding post-accident plant vent effluent radioiodine and particulate sampling and analysis during the installation of a new digital radiation monitoring system. 1128S/85K
2751993008 | Diablo Canyon 1, Diablo Canyon 2 | 08/24/1993 | 10/19/1993 | 9310280151 | <strong>Block Valves Installed On Inlet/Discharge Side Of Overpressure Protection Devices Due To Vendor Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being submitted pursuant to NUREG-1022. <br /><br /> On August 24, 1993, Operations personnel determined that the Volume Control Tank (VCT) manual block valves that are installed downstream of a relief valve is a configuration that does not meet the intent of ASME Section III requirements because positive 'controls and interlocks' are not provided for. <br /><br /> Following identification of this issue, Nuclear Engineering Services (NES) personnel reviewed other safety-related systems that have block valves installed upstream or downstream of overpressure protection devices, and identified that the Regenerative Heat Exchanger (RHE) manual block valve that is installed upstream of the spring-loaded thermal relief check valve is another configuration that does not meet the intent of ASME Section III requirements. <br /><br /> The root cause is attributed to a vendor design deficiency because these block and relief valve configurations were part of the original standard designs. To prevent recurrence, PG&E transmitted a letter to Westinghouse to request research of the generic design issue. PG&E will submit a relief request from ASME Section III requirements to the NRC to allow the current configurations. 6247S/85K
2751993009 | Diablo Canyon 1 | 11/01/1993 | 11/24/1993 | 9312060295 | <strong>Actuation Of Wrong Undervoltage Relay Causes Unplanned Diesel Generator Start (ESF Actuation) Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1993, routine surveillance testing was scheduled for Diesel Generator 1-1 on Unit 1 and Diesel Generator 2-2 on Unit 2. On November 1, 1993, at 2252 PST, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, an unplanned start of Diesel Generator 1-3 was initiated when a licensed operator inadvertently actuated the wrong startup bus undervoltage relay. This event constitutes an engineered safety feature actuation. The control room operators returned all actuated equipment to normal status. <br /><br /> On November 2, 1993, at 0020 PST, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> The root cause of this event was personnel error (cognitive), inattention to detail, by the operator actuating the startup bus undervoltage switch. <br /><br /> An Operations Incident Summary will be prepared discussing this event and introducing the new Operations Policy on performing surveillance test procedures. In addition, labeling will be provided on the 4kV switchgear interconnecting doors and the labeling on the startup bus undervoltage relay cutout switch will be enhanced.
2751993010 | Diablo Canyon 1, Diablo Canyon 2 | 11/19/1993 | 12/20/1993 | 9401040011 | <strong>Violation Of Technical Specification (TS) 3.6.2.3 Due To Inadequate Incorporation Of Plant Design Basis And Operating Configuration In TS</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1993, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that Technical Specification (TS) 3.6.2.3, Containment Cooling, was not met for both Units when all five containment fan cooling units (CFCU) were inoperable in Mode 4 (Hot Shutdown). Since initial plant startup, whenever either Unit enters Mode 4 from Mode 3 (Hot Standby), both residual heat removal (RHR) heat exchangers are placed in service to remove decay heat from the core. However, placing the RHR heat exchangers in service without throttling results in the component cooling water (CCW) flow to the CFCU cooling coils decreasing below that required by TS 4.6.2.3a.2) for operability. <br /><br /> The root cause of this event is that the TS did not adequately incorporate plant design basis and operating configurations.<br /><br /> A license amendment request (LAR) will be submitted to revise TS 3.6.2.3. Also, operating and surveillance procedures will be revised following issuance of the LAR. In addition, a review of the CCW and CFCU TS and procedures will be performed to ensure all design requirements are appropriately implemented in plant procedures. Also, PG&E QA Safety System Functional Audits and Reviews will be required to review TS against associated design requirements.
2751993011 | Diablo Canyon 1 | 12/26/1993 | 01/25/1994 | 9402040170 | <strong>Turbine And Reactor Trip Due To A Generator Excitation Protection Transducer Failure And Subsequent Electrical System Disturbance</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1993, at 1423 PST, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Unit 1 experienced a turbine trip and subsequent reactor trip. The unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A four-hour, nonemergency report was made in accordance with 10 CFR 50.72(b)(2)(ii) at 1455 PST. <br /><br /> The event was due to a failed excitation system isolation transducer combined with a fault on the Midway-Kern #1 and #2 230 kV lines. The fault, combined with the excitation protection system transducer failure, resulted in a unit trip. <br /><br /> The operators manually closed the main steam isolation valves (MSIVs) in response to a reactor coolant system (RCS) pressure and temperature decrease. This action was successful in stopping the cooldown. The RCS pressure was recovered and the MSIVs were reopened. An investigation concluded that the cooldown was due to a combination of auxiliary feedwater (AFW) flow and the additional steam flow to the Moisture Separator Reheater (MSR) 1-2A.<br /><br /> The generator excitation protection transducer was replaced. The other two Unit 1 DC-DC isolation transducers were verified to be within tolerances. The Unit 2 generator isolation transducers will be inspected during the next outage of sufficient duration.
2751993012 | Diablo Canyon 1, Diablo Canyon 2 | 12/30/1993 | 05/27/1994 | 9406030063 | <strong>Auxiliary Saltwater System Outside Design Basis Due To Fouling</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1993, at 1150 PST, with Unit 1 in Mode 3 (Hot Standby) at 0 percent power and Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the auxiliary saltwater (ASW) system and its associated component cooling water (CCW) heat exchangers for both units may not have met their design basis for certain time periods prior to implementation of continuous chlorination. Continuous chlorination was fully implemented in September and November 1992 for Units 1 and 2, respectively. This condition was reported to the NRC as a one-hour, non-emergency report in accordance with 10 CFR 50.72 (b)(1)(ii)(B) at 1150 PST on December 30, 1993. <br /><br /> The cause of this condition was an inadequate understanding of the effects of fouling on the CCW heat exchangers. <br /><br /> The ASW systems for both units currently are operable given the present maintenance, operational, and testing activities. These activities assure that the ASW system will remain sufficiently clean such that fouling will not prevent the system from performing its design basis functions. CCW heat exchanger tests on both units will be performed to provide additional confirmation of the adequacy of operational and maintenance practices to assure that the CCW heat exchangers meet their design basis requirements. An equipment control guideline was implemented to ensure compensating actions are taken if the ASW chlorination system becomes inoperable.
2771993001 | Peach Bottom 2 | 01/01/1993 | 01/28/1993 | 9302020489 | <strong>High Pressure Coolant Injection System Being Inoperable due to the Loss of Hydraulic Priming in the Lube Oil and Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>On 01/01/93 at 2205 hours, the High Pressure Coolant Injection (HPCI) system was declared inoperable following the performance of a Surveillance Test (ST), when the HPCI system start time exceeded 30 seconds. The purpose of this ST is to ensure that the HPCI system response time from a cold and un-primed condition is less than the 30 second limit specified in the Updated Final Safety Analysis Report. During this test, HPCI reached rated flow and discharge pressure in 30.12 seconds. This condition would have delayed the HPCI system from starting within 30 seconds per its intended design. The cause of this event has been determined to be the loss of hydraulic priming in the HPCI lube oil and hydraulic control system. This was due to back leakage through the motor driven Auxiliary Oil Pump Discharge Check Valve. Currently, routine trending or maintenance is not performed for the check valve. The motor driven HPCI Auxiliary Oil Pump Discharge Check Valve was replaced and the HPCI system was tested satisfactorily. An evaluation will be performed for this and other similar check valves to identify if any additional actions are required to assure continued proper operation of the HPCI oil system. No actual safety consequences occurred as a result of this event. One previous similar event has been identified.
2771993002 | Peach Bottom 2, Peach Bottom 3 | 11/02/1992 | 01/28/1993 | 9302020495 | <strong>Technical Specification Violation when a Continuous Firewatch was not Performed</strong><br /><i>Abstract:&nbsp;</i>On 01/05/93 at 2000 hours, k was discovered that a continuous firewatch was not in place for the Unit 2 Turbine Building Condensate Demin Piping Tunnel area (50-78A) from 11/02/92 at 0140 hours to 01/05/93. This is a violation of Technical Specification 3.14.D.2. On 11/02/92, the fire detector auto code box (A-400) in the 50-78A area was bypassed and declared inoperable. At this time an hourly fire watch was ensured to be in place instead of the required continuous firewatch. The cause of the event is that the Shift Supervisor (SSV) did not ensure that the appropriate firewatch was performed for this area. The SSV directed compensatory actions sufficient only for A-400 becoming inoperable. The actions were not sufficient for A-400 becoming inoperable because A-400 was being used to justify an hourly firewatch for a Thermo-Lag fire barrier impairment. The SSV missed the fact that A-400 was taken credit for as being operable. A contributing factor to this event was that the SSV, who processed the fire impairment for A-400, was the only barrier in preventing the error. A-400 was then restored to an operable status. The procedure used to control and track fire impairments will be revised to require two individuals to review and approve impairments. There were three previous similar events.
2771993003 | Peach Bottom 2 | 01/31/1993 | 02/23/1993 | 9303020163 | <strong>High Pressure Coolant Injection System being Inoperable due to a Flange Leak on the Gland Seal Condenser</strong><br /><i>Abstract:&nbsp;</i>On 01 /31/93, the High Pressure Coolant injection (HPCI) system was declared inoperable following the performance of a Surveillance Test (ST), when the HPCI Gland Seal Condenser upper head flange gasket failed. This allowed the HPCI Gland Seal Condenser tube side cooling water to be sprayed into the HPCI room onto the control relay panels for the HPCI Auxiliary Oil Pump, HPCI Condensate Pump, and the HPCI Vacuum Pump. Therefore, the applicable Technical Specification Limiting Condition for Operation was entered. The cause of this event has been determined to be a failure of the HPCI Gland Seal Condenser upper head flange gasket. Following the event, the HPCI control relay panels were opened to allow drying. in addition, the Unit 3 HPCI Gland Seal Condenser gasket was visually inspected, from the outside for signs of deterioration. The Unit 3 HPCI system was considered satisfactory. After Unit 2 Gland Seal Condenser gasket replacement and control relay panel component testing, the HPCI system was tested satisfactorily per the ST. The Unit 3 HPCI Gland Seal Condenser gasket will be inspected and replaced as necessary during an upcoming HPCI system outage. An evaluation will be performed to identify what additional corrective actions are required. No actual safety consequences occurred as a result of this event. There were no previous similar events identified.
2771993004 | Peach Bottom 2 | 03/02/1993 | 03/26/1993 | 9304010184 | <strong>Automatic Scram on Reactor Water Level when a Condensate Pump Trip Caused Two Reactor Feed Pumps to Trip on Low Suction Pressure</strong><br /><i>Abstract:&nbsp;</i>On 03/02/93, the 'C' Condensate Pump breaker tripped open and caused the 'A' and 'C' RFPs to trip on low pump suction pressure. The Reactor water level decreased to the scram setpoint. The High Pressure Coolant Injection (HPCI) and the Reactor Core isolation Coolant (RCIC) systems started on low Reactor water level. The HPCI and RCIC systems continued to restore Reactor water level until the 'C' RFP was returned to service. An Unusual Event was declared due to the HPCI injection to the reactor from a valid initiation signal. The Unusual Event was terminated at 1908 hours. The cause of the scram has been determined to be an unexpected trip of the 'C' Condensate Pump. An investigation was conducted to inspect the relays and components which could have caused the 'C' Condensate Pump trip and no equipment problems could be reproduced. <br /><br /> Therefore, it has been concluded that the trip was not due to equipment failure. An investigation did identify a human factors issue with the location of the control switches. After HPCI had completed its function, it was discovered that the HPCI Auxiliary Oil Pump (AOP) would not start. The cause of the HPCI AOP failure has been determined to be a spurious failure of a time delay relay to properly operate. The relay coil has been replaced and setup. An evaluation will be performed on this event and previous similar type relay problems to identify additional corrective actions.
2771993005 | Peach Bottom 2 | 12/05/1992 | 04/20/1993 | 9304280043 | <strong>Technical Specification Violation due to Long Stroke Times of Main Steam Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 3/9/93, it was determined that two inboard Main Steam Isolation Valves (MSIVs), AO-80A and AO-80C, were potentially unable to meet their Technical Specification stroke times at very low power levels. Primary Containment integrity was unaffected by this concern. These power levels occurred for a short time on or about 12/5/92, 1/2/93, and 3/2/93. The purpose of the MSIVs is to isolate the four Main Steam lines within 10.5 seconds in the event of certain design basis events. During these design basis conditions (i.e., reactor at operating temperature), all MSIVs were fully capable of performing their function. There are two MSIVs for each Main Steam line. On 3/2/93 following a reactor shutdown AO-80A required approximately 18 minutes to close. All other MSIVs closed as required. The valve disc to body clearances on two MSIVs, AO-80A and AO-80C, were found to be inadequate causing the valves to bind during approximately the last 3/4' of the full 10' valve stroke. No safety consequences occurred as a result of this event. AO-80A and AO-80C operated as designed during tests at higher reactor power levels. The valve disc to body clearances on AO-80A and AO-80C were increased.
2771993006 | Peach Bottom 2, Peach Bottom 3 | 03/14/1993 | 04/07/1993 | 9304130114 | <strong>Snowstorm Results in Inaccessibility of Site</strong><br /><i>Abstract:&nbsp;</i>On 3/14/93 at approximately 0100 hours, access roads to the site were determined to be impassable due to snow drifts resulting from a severe snowstorm. The snowstorm began during the evening hours on 3/12/93 and lasted until late in the evening on 3/13/93. Because the roads were impassable for most vehicles until late in the day on 3/14/93, personnel would have been unable to respond to the site in the event of an emergency. There were no safety consequences as a result of the event. If an emergency had occurred a full complement of operations personnel were on site. Off-site communications capability and plant assessment capability was unaffected by the storm. Pre-planning resulted in having ample operations and other personnel available on site such that no Technical Specification violations of operations staffing or overtime limits occurred. There were no previous events identified.
2771993007 | Peach Bottom 2 | 04/03/1993 | 04/29/1993 | 9305060197 | <strong>Technical Specification Violation due to a Mispositioned Valve on the Drywell Radiation Monitor as a Result of an Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On 4/3/93 at 1130 hours with Unit 2 operating at approximately 100% power, it was discovered that the Drywell Atmospheric Radiation Monitor (DARM) was isolated from the drywell atmosphere for an indeterminate period of time. The cause of the event has been determined to be a mispositioning of the DARM manual sample/purge valve. The valve was last seen in its proper position on 03/09/93. This is a violation of Technical Specification (Tech Spec) 4.6.C.2, which requires that drywell atmospheric radiation levels be monitored and recorded at least daily. In addition, with the DARM unknowingly inoperable, grab samples were not taken as required in Tech Spec 3.6.C.3. The mispositioned valve was returned to the normal position and drywell atmospheric radiation levels were verified to be within expected normal operating values. This valve and the same valve on the other unit have been inspected and mechanically secured to prevent inadvertent mispositioning. As an interim corrective action, these valves will be removed under a Temporary Plant Alteration until the valves are permanently removed as part of a future DARM upgrade modification. The pertinent information from this event will be provided to the appropriate station personnel. There were no actual safety consequences as a result of this event. One previous similar event was identified.
2771993008 | Peach Bottom 2, Peach Bottom 3 | 04/09/1993 | 05/20/1993 | 9305250377 | <strong>Technical Specification Violation when the Unit 2 Fire Suppression Carbon Dioxide Storage Tank Pressure Dripped below the Minimum Limit</strong><br /><i>Abstract:&nbsp;</i>On 04/09/93, a Technical Specification (Tech Spec) violation occurred when the appropriate compensatory actions were not established when the Unit 2 Fire Suppression Carbon Dioxide Storage Tank pressure went below the Tech Specs limit. The CO2 tank low pressure condition was identified by a Nuclear Plant Operator (NPO) during the performance of a Surveillance Test (ST). The NPO notified the Chief Operator (CO) that the ST was going to fail, however, the required compensatory actions were not implemented. Testing identified that the tank pressure switch setpoint had drifted. Following as found tank instrumentation testing, this event was determined to be reportable on 04/22/93. The cause of the event was setpoint drift of a pressure switch in conjunction with less than adequate communication. The NPO notified the CO that the ST was going to fail but did not specifically communicate that the failure involved a Tech Spec step in the ST. After discovery of the event, the Shift Technical Advisor verified that tank pressure had recovered. The tank pressure switches have been properly calibrated. An investigation is currently being performed on this pressure switch problem and corrective actions will be implemented. The event has been discussed with the involved individuals. The information will be provided to the appropriate Operations personnel.
2771993009 | Peach Bottom 2 | 04/22/1993 | 05/20/1993 | 9305260057 | <strong>Technical Specification Violation when the Unit 2 Containment Sump Pump Collection and Flow Data was not Recorded in the Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On 04/22/93 at approximately 2400 hours, it was discovered that the previous shift failed to monitor and record the Reactor coolant system leakage at 1600 and 2000 hours. Tech Spec 4.6.C.1 specifies that "Reactor coolant system leakage shall be determined by the primary containment (Drywell) sump collection and flow monitoring system and recorded every 4 hours or less". Therefore, this condition resulted in a violation of the Tech Specs because the required containment sump collection and flow data was not monitored and recorded. After discovery of the event, its was verified that the actual containment pump out data contained no indications of unusual containment leakages. The cause of the event has been determined to be that the Unit 2 Reactor Operator failed to monitor and record the primary containment sump collection and flow data. The event has been discussed with the involved individual. As a result of this event and other previous performance problems, the involved individual has been permanently relieved of license operator duties. The pertinent information from the event will be provided to the appropriate Operations personnel. One previous similar event has been identified.
2771993010 | Peach Bottom 2 | 04/25/1993 | 05/20/1993 | 9305250380 | <strong>Plant Shutdown Required by Technical Specifications due to Inoperable Reactor Water Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On 04/25/93, it was noticed that the Wide Range Reactor level indications associated with the 2A condensing chamber had drifted higher than level instruments associated with the 2B condensing chamber. The water level instrumentation associated with the 2A condensing chamber was declared inoperable. Safety systems would still have been properly initiated by the instrumentation associated with the 2B condensing chamber. A shutdown was immediately initiated. Following plant shutdown, an investigation identified that an equalizing valve associated with a level instrument was leaking through. This caused a loss of water inventory in the 2A condensing chamber reference leg through the instrument equalizing valve. The instrument block valve was replaced and the instrument lines were backfilled. An evaluation has been performed which identified other susceptible type instrument block valves. Corrective actions have been established as necessary. Long term condensing chamber modifications are currently being designed to ensure adequate reference leg water inventory can be maintained under similar conditions. Following inspection and repairs, a plant startup was commenced and Reactor water levels were closely monitored during and after startup to ensure proper level indications. No actual safety consequences occurred as a result of this event. There were two previous similar events identified.
2771993011 | Peach Bottom 2, Peach Bottom 3 | 05/28/1993 | 06/25/1993 | 9307060159 | <strong>Technical Specification Violation when new fuel oil was added to an EDG Fuel Oil Storage Tank prior to completion of the chemical analysis</strong><br /><i>Abstract:&nbsp;</i>On 05/28/93, during the off loading activities required to add new EDG fuel oil from a truck tanker to a Diesel Generator (EDG) fuel oil storage tank, a Technical Specification (Tech Spec) violation occurred when the appropriate Surveillance Requirements were not completed prior to the fuel oil being added to the storage tank. The Tech Spec specifies that new EDG fuel oil will be sampled and analyzed prior to addition to the fuel oil storage tanks. The fuel oil was sampled but the chemical analysis was not fully completed. Earlier that day, a truck tanker of new EDG fuel oil arrived at the site for delivery. The Plant Operator (PO) requested that a Chemistry Technician sample the tanker. The Chemistry Technician did sample the tanker, however, the PO failed to wait for the results of the chemical analysis prior to adding the fuel oil to the storage tank. The results of the analysis were completed satisfactorily following the start of the off loading activities. The cause of the event was that the PO failed to comply with the directions as specified in the appropriate procedures. The event has been discussed with the involved individual and information from the event will be provided to the appropriate Operations personnel. No previous similar events have been identified.
2771993012 | Peach Bottom 2, Peach Bottom 3 | 06/01/1993 | 07/01/1993 | 9307060287 | <strong>Technical Specification Violation when a Surveillance Test was mised on the fire protection system</strong><br /><i>Abstract:&nbsp;</i>On 06/07/93, a Fire Protection individual identified that a Surveillance Test (ST)-F-037B315-2 had not been performed within the test frequency which resulted in a violation of Technical Specification (Tech Spec) 4.14.A.4.a on 06/01/93. The cause of the event was that an insufficient degree of attention was applied by the Fire Protection individual during the review of ST Status Reports. The Surveillance Test Coordinator (STC) properly notified the Fire Protection individual with ST Status Reports and by phone that ST-F-037B-315-2 was near to exceeding its Tech Spec frequency. However, the Fire Protection individual had a mindset that the ST Status Reports and the STC was referring to a Routine Test (RT-F-037B-315-2) which had just been completed. Therefore, no actions were taken at that point due to the belief that the ST was completed. <br /><br /> ST-F-037B-315-2 is used to visually inspect Tech Spec related fire hose stations while RT-F-037B-315-2 is used to visually inspect non-Tech Spec hose stations. After discovery of the event, ST-F037B-315-2 was completed satisfactorily to ensure that all Tech Spec fire system hose stations specified in the ST were operable. The pertinent information from the event will be provided to the appropriate personnel. An evaluation will be performed on the scheduling and issuance of Fire Protection tests.
2771993013 | Peach Bottom 2 | 08/19/1993 | 09/16/1993 | 9404110327 | <strong>Technical Specification Violation when a Primary Containment Isolation System Inoperable Isolation Valve was not isolated and logged</strong><br /><i>Abstract:&nbsp;</i>On 08/19/93, while attempting to close an Isolation Valve (MO-68), the valve would not close. The Motor Control Center (MCC) was turned off to support a visual inspection of the MCC internals. The Reactor Operator (RO) attempted again to close MO-68 and it did close properly. MO-68 was stroked several times to verify valve operability. The Shift Supervisor (SSV) discussed this condition with the Shift Manager and valve status was considered to be operable. On 08/20/93, the RO attempted to close MO-68 and ft did not close. MO-68 was considered inoperable. Further investigation revealed that this condition resulted in a violation of Tech Spec 3.7.D.2 and 4.7.D.2.a. Maintenance personnel identified that an auxiliary contact was not functioning properly. The cause of the event was that insufficient trouble shooting was performed on 08/19/93 and Shift Management considered the valve operable without thoroughly identifying the cause of the valve failure. The valve's auxiliary contact was replaced. The operability section of the Operations Manual will be reviewed to determine what revisions are necessary to ensure that Managements expectations are clear regarding valve operability. The pertinent information from the event will be provided to the appropriate Operations personnel. No previous similar events were identified.
2771993014 | Peach Bottom 2, Peach Bottom 3 | 10/06/1993 | 11/04/1993 | 9311100184 | <strong>Technical Specification violation when the Main Control Room Emergency Ventilation System was Inoperable During Fuel Movements</strong><br /><i>Abstract:&nbsp;</i>On 10/06/93, a Nuclear Plant Operator (NPO) identified that the control switches for the Control Room Emergency Ventilation (CREV) system fans were in the 'OFF' position instead of 'AUTO' which resulted in a violation of Technical Specifications. There are three System Operating (SO) procedures that must be completed to fully reestablish a Normal MCR ventilation. Procedure SO-40D.7.A is used to reset the MCR high radiation trip logic. This procedure then directs the operator to perform SO-40D.1.A to restore the Normal MCR ventilation to service and to perform SO-40D.1.B to setup the CREV system for automatic operation. During this event the CO only gave the NPO two (SO-40D.7.A and SO-40D.1.A) of the three SO procedures needed. After discovery of the event, the control switches were properly aligned. The three SO procedures used to restore the CREV and MCR ventilation systems will be reviewed and revised as necessary to enhance the human factoring of these procedures. An evaluation will be performed to determine the impact of using cascading procedures for other operating tasks. Corrective actions will be implemented as appropriate. The event has been discussed with the involved NPO and CO and will be provided to the appropriate Operations personnel. One previous similar event was identified.
2771993015 | Peach Bottom 2, Peach Bottom 3 | 11/24/1993 | 12/23/1993 | 9401040088 | <strong>Technical Specification Violation occurred due to an improperly secured main stack particulate filter</strong><br /><i>Abstract:&nbsp;</i>On 12/01/93, a Chemistry Technician discovered that the Main Stack particulate and iodine filters were not properly secured in their holder. The discovery was made during the performance of a weekly Surveillance Test (ST)-C-095-857-2. This condition caused the Main Stack Particulate and Iodine filters and the Main Stack Noble Gas Monitors to be diluted and inaccurate. This is a violation of Tech Spec 3.8.4.b and 3.8.4.c. The cause of the event has been determined to be an improper securing of the Main Stack Particulate and Iodine filters. The filters were last replaced by a Chemistry Technician on 11/24/93. The filters were not properly secured as part of this evolution. An insufficient degree of attention was applied to the task by the Chemistry Technician. Following discovery of the event, the filters were changed out and gas marinelli samples were obtained to identify and quantify the nuclides in the Main Stack effluent. Analyses of these samples and other operating radiation parameters indicate that Main Stack effluent radiation levels were within expected normal limits. The involved individual has been coached and counseled. The pertinent information has been provided to the appropriate Chemistry personnel. No previous similar events were identified.
2771993016 | Peach Bottom 2 | 12/21/1993 | 01/20/1994 | 9402020321 | <strong>HPCI declared inoperable when the system isolated During surveillance testing</strong><br /><i>Abstract:&nbsp;</i>On 12/21/93, the High Pressure Coolant Injection (HPCI) system was declared inoperable during the performance of a Surveillance Test (ST). The HPCI steam Line High Flow Isolation Switch (DPIS-2-23-77) did not function as expected. The instrument was tripped to its safe condition and the HPCI system was isolated. The applicable Technical Specification Limiting Condition for Operation (LCO) was entered. It was not known at that time whether the problem was with the flow switch or the instrument calibration line. An investigation revealed that the instrument calibration line, used for flow switch calibrations, was blocked with foreign debris. The instrument calibration line is only used for calibration purposes and is isolated when the instrument is valved in and operable. Prior to manually isolating the HPCI system, both this flow switch and its redundant instrument were available and operable to isolate the HPCI system in the event of a steam line break. The instrument calibration line was flushed to clear the blockage and back filled. DPIS-2-23-77 was tested satisfactorily and the associated Tech Spec LCO was exited. Other similar instrument calibration lines were inspected and verified to be clear. Preventive Maintenance Tasks associated with these instruments will be reviewed to determine if additional actions can be incorporated to ensure that instrument calibration lines are maintained clear. No previous similar events have been identified.
2781993001 | Peach Bottom 3 | 01/25/1993 | 02/23/1993 | 9303020092 | <strong>High Pressure Coolant Injection System Being Inoperable When the Discharge Valve would not Open due to a Mis- Aligned Relay</strong><br /><i>Abstract:&nbsp;</i>On 01/25/93, the High Pressure Coolant injection (HPCI) system was declared inoperable when the HPCI pump discharge valve (MO-3-23-20) failed to open during valve stroke time testing. This condition would have prevented the HPCI system from injecting per its intended design. An investigation has revealed that a misaligned relay contact in the MO- 3-23-20 control logic prevented the valve from opening. A minor adjustment was made to the relay contact which allowed the system to be available for system operation. Following relay adjustment, MO-3-23-20 was tested satisfactorily. The cause of this event has been determined to be a misaligned relay contact. This occurred when the movable relay contact arm became dislodged from the stationary alignment pin. This allowed the relay contact alignment to slowly change with each relay operation. This condition was reproduced, however, it has not been determined yet how the movable relay contact became dislodged from the stationary alignment pin. All other DC Motor Control Centers were immediately inspected which ensured that other similar type relay contacts were aligned and the alignment pins were properly inserted. An evaluation will be performed for this and other similar type relays to identify what additional corrective actions are required. No previous similar events have been identified.
2781993002 | Peach Bottom 3 | 03/07/1993 | 03/26/1993 | 9304010205 | <strong>Automatic Scram on Reactor Water Level when a Reactor Feed Pump Tripped on High Vibrations</strong><br /><i>Abstract:&nbsp;</i>On 03/07/93 at 23% rated power, the 'C' Reactor Feed Pump (RFP) tripped and the 'B' RFP failed to respond. This caused the Reactor water level to decrease to the low level scram setpoint. Primary Containment Isolation System (PCIS) Group II/III isolations also occurred when the Reactor water level decreased. The 'A' RFP was placed in-service to restore Reactor water level. The PCIS and the Reactor Protection System (RPS) scram logics were reset. The cause of the scram has been determined to be an unexpected trip of the 'C' RFP on a high vibration condition. An investigation has been performed and concluded that a damaged vibration element in conjunction with a rough turbine shaft caused the false high vibration indication and the 'C' RFP trip. A defective controller in the 'B' RFP control logic caused the pump to fail to respond during the transient. The vibration element on the 'C' RFP was replaced and the lubrication spray nozzle was repositioned. Similar elements on the other RFPs were inspected and found to be satisfactory. The shaft roughness on the 'C' RFP will be addressed during a future outage. The defective controller on the 'B' RFP was replaced and setup. An evaluation will be performed on the defective controller to identify if additional corrective actions are necessary for other similar type controllers. This corrective actions will be based on the cause of the 'B' RFP controller failure. No previous similar events have been identified.
2781993003 | Peach Bottom 3 | 03/10/1993 | 04/07/1993 | 9304130150 | <strong>Technical Specification Violation when the Reactor was Unvented and Pressure-Temperature Data was not Obtained</strong><br /><i>Abstract:&nbsp;</i>On 03/10/93, it was discovered that the Reactor vessel head vents were closed. An Operator was immediately dispatched and identified that the backup Instrument Air Supply Valves (AO-5230A & B) were closed. Since AO-5230A & B were found closed, the head vents eventually drifted shut as pressure in the supply lines decayed away. The instrument air supply valves and the Reactor vessel head vents were immediately restored to their proper position. This condition resulted in a violation of Tech Spec because the appropriate 15 minute Surveillance Requirements were not performed when the reactor was not vented. Further investigations have determined that the operator did not fully move the control switches for AO-5230A & B to the 'AUTO' position. The control switch labels for AO-5230A & B and the same valves on the other unit will be better human factored. In addition, the sluggish switches will be inspected and corrective actions will be implemented as appropriate. The event has been discussed with the involved individuals and will be provided to the appropriate Operations personnel. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
2781993004 | Peach Bottom 3 | 07/30/1993 | 08/30/1993 | 9309080247 | <strong>Low Condenser Vacuum Scram and Primary Containment Isolation following a Recombiner Off Gas Isolation</strong><br /><i>Abstract:&nbsp;</i>On 7/30/93, after venting the Off Gas Recombiner (OGR) steam flow condensing chambers using a Special Procedure (SP-1438), a simulated low steam flow signal to the Recombiner initiated an isolation signal to the OGR. This caused Main Condenser vacuum to begin decreasing. At 0327 hours, with the Reactor at 72% power, a auto half scram signal was received due to low main condenser vacuum. Therefore, the unit was manually scrammed. An investigation has determined that the cause of the OGR isolation was the combination of a previously failed fuse from unknown causes in the 'B' OGR steam flow isolation logic and the blowing of a fuse in the 'A' OGR steam flow isolation logic due to grounding of a jumper being removed during the performance of SP-1438. Following the event, the scram and isolation logics were reset. Affected systems were restored to appropriate conditions and the blown fuses were replaced. <br /><br /> SP-1438 has been revised to ensure that fuse status is monitored. An investigation is currently underway to identify the cause of the fuse failure in the 'B' OGR logic and to determine if terminal point modifications are necessary. Design changes and/or corrective actions will be implemented as necessary. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
2781993005 | Peach Bottom 3 | 08/09/1993 | 09/03/1993 | 9309130237 | <strong>High pressure coolant injection system being inoperable due to a defective flow controller</strong><br /><i>Abstract:&nbsp;</i>On 08/09/93, the High Pressure Coolant Injection (HPCI) system was declared inoperable when the HPCI Flow Controller output signal started oscillating. The HPCI system was secured and the applicable Technical Specification (Tech Spec) Limiting Condition for Operation (LCO) was entered. An investigation revealed that the Flow Controller was providing an oscillating output signal. On 08/10/93, the Flow Controller was removed. All potentiometers and boards were cleaned. Subsequently, the Flow Controller was reinstalled, and stability testing indicated that Flow Controller tuning was required. Flow Controller tuning was then successfully performed. 08/10/93. Further reviews of the system's oscillating condition determined that the HPCI system was capable of injecting water to the reactor pressure vessel per its design intent with the existing speed oscillations. The root cause of the Flow Controller failure has not been determined, it is believed that the Flow Controller drifted out of specification. An evaluation will be performed to determine what corrective actions are required to ensure continued operability of these type Flow Controllers. In addition, the replacement of this type Flow Controller with a functionally equivalent type controller has been under evaluation. No actual safety consequences occurred as a result of this event. No previous similar events have been identified.
2781993006 | Peach Bottom 3 | 08/14/1993 | 09/03/1993 | 9309130349 | <strong>Low pressure coolant injection system being inoperable During the performance of a Unit 2 reactor water level modification</strong><br /><i>Abstract:&nbsp;</i>On 08/14/93, the Unit 3 Low Pressure Coolant Injection (LPCI) system became inoperable when a Triple Low Water Level signal was simulated on Unit 2. Per design, this signal would have defeated the auto-start logic for the "3A" and "3B" Residual Heat Removal (RHR) pumps on Unit 3. Troubleshooting revealed that the false Triple Low Water Level signal on Unit 2 came from Reactor Water Level Instrumentation (LT-72B and D) which are connected to the 2B Reference Leg. LT-72B was immediately valved out of service and equalized which allowed indicated water level to increase and the simulated Triple Low Water Level signal cleared. The cause of this event was that a simulated Unit 2 Triple Low Water Level signal occurred when the 2B Reference Leg instrumentation line increased in pressure. The instrument was isolated under a blocking clearance. Line pressure increase has been attributed to an increase in reference leg water temperature as a result of a ambient area temperature increase. Corrective actions will be implemented to ensure that the effects of area temperature changes during the Unit 3 Reactor Water Level Instrument Reference Leg modification will not cause a simulated Triple Low Water Level signal. Lessons learned from this event will be evaluated to determine the most appropriate way to remove similarly configured instrumentation from service. No actual safety consequences occurred as a result of this event.
2781993007 | Peach Bottom 3 | 08/08/1993 | 09/16/1993 | 9407060109 | <strong>Technical Specification Violation when a Suppression Chamber - Reactor Building Vacuum Breaker Surveillance Requirements was not performed</strong><br /><i>Abstract:&nbsp;</i>On 08/20/93, the Surveillance Test Coordinator (STC) identified that a Surveillance Test (ST) (S13D-7-3503-B1CR) had not been performed prior to exceeding the Technical Specification (Tech Spec) out of surveillance date. This resulted in a violation of Tech Spec 4.7.A.3.a on 08/08/93. The cause of the event was that the initial review of the proposed Tech Spec change to determine its impact on individual Surveillance Test frequencies was inadequate. After discovery of the event, S13D-7-3503-B1CR was completed satisfactorily on 08/20/93 to ensure that the instrumentation and setpoints associated with these Vacuum Breakers were operable. In addition, completion of the review of this Tech Spec Amendment verified that this was the only case where an ST was not completed within its allowable surveillance frequency. The event has been discussed with the involved individuals. The pertinent information from the event will be provided to the appropriate Site Engineering personnel to emphasize the importance of attention to detail when reviewing Tech Spec Proposals and approved Amendments. No actual safety consequences occurred as a result of this event. There were no previous similar events identified.
2781993008 | Peach Bottom 3 | 10/18/1993 | 11/05/1993 | 9311160265 | <strong>Technical Specification Violation due to Main Steam Relief and Safety Valve set point drift</strong><br /><i>Abstract:&nbsp;</i>On 10/18/93, Peach Bottom Atomic Power Station personnel identified that two of the eleven Main Steam Relief Valves (MSRV) and one of the two Safety Valves (SV) did not lift within the Tech Spec +/-1% tolerance. Two MSRVs lifted within the range of + 1.3 % to + 1.6 % of their nameplate setpoints while one SV lifted at 3.0% above its nameplate setpoint. All of these valves had been within tolerance when installed. The ability of the MSRVs and the SVs to successfully maintain a 1% tolerance is an industry wide concern. The event was caused by a small drift in the setpoint of the valves which is inherent in the valves design. Refurbished valves have been properly setup at the test facility and then installed for six MSRVs and one SV. The other SV will also be tested. In addition, a Technical Specification change request is being evaluated by PECO to address MSRV and SV setpoint tolerance relaxation. Corrective actions to resolve the concern of setpoint drift will be implemented as appropriate. No actual safety consequences occurred as a result of this event. Previous similar events have been identified.
2781993009 | Peach Bottom 3 | 11/13/1993 | 12/13/1993 | 9312200038 | <strong>High Pressure Coolant Injection System being inoperable when the discharge valve would not open due to a misaligned relay contact</strong><br /><i>Abstract:&nbsp;</i>On 11/13/93, the High Pressure Coolant Injection (HPCI) system was declared inoperable following the performance of a Surveillance Test, when the HPCI pump discharge valve (MO-3-23-19) failed to open during valve stroke time testing. This condition would have prevented the HPCI system from injecting per its intended design. Therefore, the applicable Tech Spec Limiting Condition for Operation (LCO) was entered. An investigation revealed that a misaligned relay CRA) contact in the MO-3-23-19 control logic prevented the valve from opening. A minor adjustment was made to the relay contact which allowed the system to be available for system operation. The NRC was notified via ENS at 1410 hours. Following relay adjustment, MO-3-23-19 was tested satisfactorily and the associated Tech Spec LCO was exited. The cause of this event has been determined to be a misaligned relay contact in the MO-3-23-19 control logic. An evaluation has been performed as a result of several previous similar TA relay problems and corrective action recommendations were generated to address this concern. However, the corrective actions had not been implemented yet on MO-3-23-19. Other DC MCCs which could adversely impact HPCI operability were inspected. In addition, periodic inspections of these relays will be performed until permanent corrective actions are fully implemented. Five previous similar events have been identified.
2781993010 | Peach Bottom 3 | 12/01/1993 | 12/23/1993 | 9401040096 | <strong>Technical Specification required shutdown due to a failed residual heat removal system valve</strong><br /><i>Abstract:&nbsp;</i>On 11/25/93 at 1705 hours, it was identified that the RHR System 'A' Loop Outboard Injection Valve (MO-3-10-025A) failed to fully close. On 12/01/93, Station Management decided to shut down Unit 3 since the RHR 'A' Loop Injection Valve repairs could not be completed without isolating a manual valve inside the Drywell. The cause of the event has been determined to be a bent valve stem on MO-3-10-025A. This occurred due to interferences between the in-body stationary valve components and the movable valve wedge. It is believed that as the valve wedge closed, the initial point of contact between the valve body and the wedge created a reactionary moment which bent the valve stem. This interface between the valve in-body components and the wedge was due to the machining of the valve seats over time for Local Leak Rate Test (LLRT) repairs. As the valve's in-body seats wear, the wedge is allowed to drop further into the seat. Normally the valve will fail its 'As Found' LLRT if the seats are worn too far. In this case, it appeared that while the wedge seated properly and passed its LLRT, the wedge contacted the valve body eccentrically due to abnormal valve body geometry. The RHR 'A' Loop Injection Valve was disassembled and a new valve stem was installed. An evaluation is currently underway to address MO-3-10-025A valve failure and possible generic implications. No previous events have been identified.
2781993011 | Peach Bottom 3 | 12/10/1993 | 01/07/1994 | 9401180112 | <strong>Technical Specification violation when a surveillance test was not performed within the one hour limit</strong><br /><i>Abstract:&nbsp;</i>On 12/11/93, a terminal block in the bottom of the 4KV cubicle was knocked off its mount. At 1356 hours, it was determined that this terminal block was associated with the E-322 breaker undervoltage devices and that this condition could have made these devices inoperable. After reviewing the condition and determining what Technical Specification (Tech Spec) actions were required, a Surveillance Test (ST) was initiated at 1420 hours to meet Tech Spec Surveillance Requirement 4.9. B.1. The ST was completed satisfactorily, however, the ST was not performed prior to exceeding 1456 hours. This resulted in a violation of Tech Spec 4.9.B.1. The cause of the event is improper coordination of the required Tech Spec Surveillance Requirement by the Shift Supervisor (SSV). A contributing factor was due to extra time consumed because of unnecessary steps in the ST. The ST and its associated Tech Spec Surveillance Requirement will be evaluated to identify what actions can be taken to reduce the time necessary to satisfy the surveillance requirement within the one hour Tech Spec limit. The SSV has been counselled. The pertinent information from the event will be provided to the appropriate Operations personnel. No previous similar events have been identified.
2801993001 | Surry 1 | 01/08/1993 | 01/29/1993 | 9302100236 | <strong>Reactor Trip and Safety Injection Due to Spurious High Consequence Limiting Safeguards Signal Caused by Malfunctioning Relay</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1993 at 1729 hours, with Unit 1 operating at 100% power, a reactor trip and safety injection occurred due to spurious initiation of the train 'A' high consequence limiting safeguards (Hi-CLS). The spurious signal was generated during troubleshooting by either a loose negative lead or an intermittently closing contact on relay 3/4-CLS-1A. On January 9, 1993 at 0722 hours, with Unit 1 at hot shutdown, a spurious initiation of train A safety injection occurred during testing after replacement of relay 3/4-CLS-1A. The spurious signal was caused by testing prior to removal of a temporary modification (electrical jumper). After both spurious actuations, operators used the appropriate procedures to stabilize the unit. Failed components were replaced and a root cause evaluation was conducted. An engineering evaluation will be performed to identify single point failures which can cause spurious actuations. Circuitry modifications and relay preventive maintenance will be evaluated. A drawing effort will be corrected and the event will be discussed in safety evaluation training. This report is required by 10 CFR 50.73(a)(2)(iv).
2801993002 | Surry 1 | 02/09/1993 | 03/08/1993 | 9303150055 | <strong>Unit 1 Reactor Trip During Reactor Protection System (RPS) Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At 1043 hours on February 9, 1993, with Unit 1 at 100% power and Unit 2 at 94% power, a Unit 1 reactor trip and turbine trip signal occurred when the 'A' Reactor Trip Breaker unexpectedly opened. At the time of the trip, licensee technicians were completing regularly scheduled surveillance testing on the Unit 1 'B' Train Reactor Protection System. When a technician depressed the push button to open the 'B' Reactor Trip Bypass Breaker to restore the breaker arrangement to its normal configuration, the 'A' Reactor Trip Breaker opened. The cause of the reactor trip breaker opening was a failure of the shunt trip (ST) relay on the 'A' Reactor Trip Breaker. Post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition, and the health and safety of the public were not affected. The ST relay was replaced and the defective relay has been returned to the vendor for failure analysis. This report is required by 10 CFR 50.73(a)(2)(iv).
2801993003 | Surry 1, Surry 2 | 02/13/1993 | 03/10/1993 | 9303180063 | <strong>Containment Air Recirculation System Shutdown Renders Containment Radiation Monitors Inoperable During Refueling Operations -- Violation of Tech. Specifications</strong><br /><i>Abstract:&nbsp;</i>A review of the operability requirements for the containment air particulate and gaseous radiation monitors concluded on February 13, 1993, that the monitors are rendered inoperable when the containment air recirculation system is shutdown. A subsequent review of 1992 Unit 1 refueling outage activities indicated the containment air recirculation system was shutdown during refueling operations. Therefore, Unit 1 radiation monitors 1-RM-RMS-159 and 1-RM-RMS-160 were not operable during refueling operations as required by Technical Specifications (TS) 3.10.A.2 and 3.10.A.4. No significant safety consequences or implications resulted from this event. The event was caused by inadequate design documentation of the conditions required to support the operation of the containment gaseous and particulate radiation monitors. To prevent recurrence, operations surveillance procedures which identify the required equipment for cold shutdown and refueling conditions were revised. In addition, a change to TS 3.10 will be submitted to add an action statement to secure containment purge if the automatic isolation functions become inoperable during refueling operations. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2801993004 | Surry 1, Surry 2 | 03/16/1993 | 04/14/1993 | 9304200040 | <strong>Condition Prohibited by Technical Specifications During Reactor Protection System Logic Testing</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, with Unit 1 operating at 100% power and Unit 2 in cold shutdown, it was noted that the monthly functional test of the reactor protection system logic requires blocking both trains of steam generator blowdown (SGBD) trip valves from automatic closure by an auxiliary feedwater start signal. This action resulted in a failure to satisfy previous technical specification (TS) requirements for operability of containment isolation valves. No safety consequences were created by the event. SGBD isolation would have been automatically initiated by the ATWS Mitigation Systems Actuation Circuitry (AMSAC) system or manually initiated as directed by emergency operating procedures if it had been required. The event was caused by cognitive personnel error involving a failure to adequately assess the effects of the surveillance test on TS compliance. An ongoing review of technical specification surveillance requirement implementation includes evaluating the effects of testing on operability. This report is required by 10 CFR 50.73(a)(2)(i)(B).
2801993005 | Surry 1, Surry 2 | 03/25/1993 | 04/19/1993 | 9304260171 | <strong>Two Main Control Room/Emergency Switchgear Room Chillers Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1993, at 0242 hours, Unit 1 was at 60% power and Unit 2 was in Refueling Shutdown. Main Control Room/Emergency Switchgear Room (MCR/ESGR) Chiller 1-VS-E-4C was declared inoperable following a loss of Freon when the chillers relief valve lifted. The chiller was secured immediately and a seven day action statement was entered per Technical Specification (TS) 3.23.C.1.a at 0157 hours to restore the chiller to operable status. After securing the "C" MCR Chiller for maintenance, the 1-VS-E-4B chiller was started. The Freon relief valve for the "B" Chiller also lifted and the chiller was secured and declared inoperable at 0242 hours. A six hour action statement to Hot Shutdown (HSD) on Unit 1 was entered in accordance with TS 3.0.1. Inoperability of two Main Control Room(MCR)/Emergency Switchgear Room (ESGR) Chillers was due to cognitive personnel error involving a failure to open the strainer backwash valve because of confusion over valve position indication.<br /><br /> The third chiller remained in operation and room temperatures did not increase. Past experience with a complete loss of MCR and ESGR air conditioning has shown that temperatures have not increased as rapidly as indicated in the design calculations. It is therefore concluded that no safety consequences resulted from the event. An upgrade to the chiller system is in progress adding additional chillers to increase capacity and operational flexibility..
2801993006 | Surry 1, Surry 2 | 05/13/1993 | 06/08/1993 | 9306170161 | <strong>Service Water Flow Path to Main Control Room Chillers Inoperable Due to Pipe Leak</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1993, at 1418 hours, a fire watch reported a Service Water (SW) leak in Mechanical Equipment Room (MER) four. The leak was identified to be from a two inch backwash supply line [EIIS-BI-PSP] to a Self Cleaning Continuous Backwash Strainer [EIIS-BI-STR], (1-VS-S-1A) in one of two SW flow paths to the Main Control Room (MCR) Chillers. Technical Specification (TS) 3.14.C. requires two operable SW flow paths to one operating and one operable MCR Chiller. The line and strainer associated with the leak were declared inoperable. <br /><br /> At the time of this event, TS 3.14.C had no action statement for an inoperable SW flow path, therefore a six hour LCO to Hot Shutdown was entered for Units 1 and 2 at 1418 hours per TS 3.0.1. An alternate flow path was placed into service and the action statement was exited at 1733 hours. <br /><br /> The backwash supply line was repaired following issuance of a change to TS 3.14.C. The TS change provided a 24 hour LCO allowing one flow path to be out of service for maintenance. At the time of the event the leakage was evaluated to be manageable with regard to design basis requirements. It is therefore concluded that no safety consequences resulted from the event.
2801993007 | Surry 1, Surry 2 | 04/23/1993 | 11/01/1994 | 9411090123 | <strong>Logic Channels for RCS Low Flow in 2/3 Loops Reactor Trip Not Fully Tested</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993, with Unit 1 operating at 100% power and Unit 2 at Cold Shutdown (CSD), the continuing review of Technical Specification (TS) surveillance implementation identified a missed surveillance. The Turbine Trip Inputs to Reactor Protection are required to be functionally tested prior to each start up. Periodic Test 1(2)-PT-29.3 is performed to satisfy this requirement, but does not test the circuitry to verify the turbine trip signal is supplied to Reactor Protection. On June 16, 1993, with Unit 1 and Unit 2 at 100% power, an incomplete channel calibration surveillance test of the steam generator water low low level instrumentation channels for auxiliary feedwater (AFW) pump auto-start was also identified. On August 23, 1993, with Unit 1 at CSD and Unit 2 at Hot Shutdown, it was identified that a channel check of the AFW flow rate was not performed prior to certain start ups due to a procedural deficiency. TS Table 4.1-2, Item 1, requires that the AFW flow rate channel be checked prior to each start up if not done within the previous week. The affected surveillance procedures will be changed. <br /><br /> On October 4, 1994, with Units 1 and 2 at 100% power, a test method was developed that permits the reactor protection logic channels for the reactor coolant system low flow in two of three loops reactor trip signal to be fully tested when a unit is operating above 35% power. At certain times in the past, the subject logic channels had not been fully tested before the units entered into the operating condition in which the channels were designed to actuate.<br /><br /> This report is being made pursuant to 10 CFR50.73(a)(2)(i)(B).
2801993008 | Surry 1, Surry 2 | 05/20/1993 | 06/15/1993 | 9306220384 | <strong>Fire Watch Inadvertently Discontinued as a Result of Inadequate Fire Barrier Repair Review Process</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1993, a fire watch, established as a compensatory measure for a non-functional fire barrier penetration seal, was inadvertently discontinued for a short period of time. This event occurred with Units 1 & 2 at 100% and 91.5% power. On May 12, 1993, 11 penetrations in the wall that separates the Auxiliary Building and the Unit 2 Cable Vault were found to have less than the required thickness of firestop material. The penetrations were declared non-functional, and a continuous fire watch was established at 1415 hours. Repairs on the penetrations were believed to be complete, and the fire watch was discontinued on May 20, 1993, at 0913 hours. The continuous fire watch was reestablished at 1408 hours when it was discovered, during a review of the repair documentation, that one of the nonfunctional penetrations had not been repaired. This event resulted in no safety consequences or implications since the Auxiliary Building and the Unit 2 Cable Vault are equipped with fire detection and suppression systems. This event was caused by a programmatic deficiency in the fire watch process. To prevent recurrence, the fire watch administrative process is being changed to require independent reviews to ensure that fire barriers are returned to a functional status prior to discontinuing a fire watch. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2801993009 | Surry 1, Surry 2 | 08/11/1993 | 09/07/1993 | ML09152047 | <strong>Mechanical Equipment Room #4 Fire Door Left Blocked Open Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was operating at 100% power and Unit 2 was at cold shutdown on August 11, 1993, when the Mechanical Equipment Room (MER) No. 4 door, 2-BS-DR-10, was found blocked open at 2015 hours. This condition (i.e., a nonfunctional fire barrier) had existed for a period of time in excess of that allowed by Technical Specification 3.21.B.7. 2-BS-DR-10 was blocked open by a fire watch posted at MER No. 4, as directed by the foreman, to permit observation of the room from the outside while painting activities were being performed inside. The fire watch was released by the general foreman at approximately 1730 hours and 2-BS-DR-10 was left blocked open. An operator discovered that 2-BS-DR-10 was blocked open at 2015 hours. The operator verified that the door was not being monitored by a fire watch and closed it. This event was caused by a cognitive error on the pad of contractor personnel. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2801993010 | Surry 1 | 08/21/1993 | 09/16/1993 | 9309270085 | <strong>Operation With a Non-isolable Leak on a "B" Steam Generator Channel Head Drain Line</strong><br /><i>Abstract:&nbsp;</i>At 2100 hours on August 20, 1993, with Unit 1 at 100 percent power and Unit 2 at 97.5 percent power, Unit 1 began a shutdown for planned maintenance to repair leakage on the 'B' Steam Generator (SG) channel head. An indication of Reactor Coolant System (RCS) leakage was first observed on June 25, 1993. The leakage was attributed to the SG primary manway gasket. Precautionary actions were undertaken to monitor the leakage. Plans were implemented to repair the manway. Unit 1 began a shutdown on August 20, 1993. Upon investigation, the source of the leakage was found to be a cracked weld on the upstream side of the 'B' SG channel head primary side drain valve. Technical Specification (TS) 3.1.C.4 does not allow leakage from a non-isolable fault in the primary system. A Limiting Condition for Operation (LCO), requiring that the Unit be placed in cold shutdown (CSD) within the following 30 hours, was entered at 0443 hours on August 21, 1993. A Notification of Unusual Event (NOUE) was also declared. At 0243 hours on August 22, 1993, Unit 1 was placed in CSD, and the LCO and NOUE were terminated. During this event, normal RCS inventory was maintained. Therefore, the health and safety of the public were not affected during this event. <br /><br /> This report is being made pursuant to 10CFR50.73(a)(2)(i)(B) since the station operated in a condition not allowed by TS 3.1.C.4.
2801993011 | Surry 1, Surry 2 | 09/16/1993 | 10/18/1993 | 9310250060 | <strong>Radiation Monitors Inoperable Due to Detector Ground Reference</strong><br /><i>Abstract:&nbsp;</i>Units 1 and 2 were operating at 100% power on September 16, 1993, when several spikes were noted on the recorder for the Gaseous Vents system Ventilation Vent Radiation Monitors, 1-VG-RM-131-1 and 1-VG-RM-131-2. The monitors were declared inoperable at 1515 hours. Annunciator Response Procedure 0-RMA-B4 and the preplanned alternate method of monitoring the ventilation vent were promptly initiated. The spikes were verified not to be indicative of an actual radioactive release. An investigation was initiated by Engineering, and with the assistance of the vendor, it was determined that the spikes were caused primarily by electrical cross-talk resulting from the ground reference for the 1-VG-RM-131-1 and 1-VG-RM-131-2 detectors. To correct the condition, the system's signal ground was re-referenced and a capacitor was added to 1-VG-RM-131-1 to provide an alternating current pathway for noise induced on the signal ground line. 1-VG-RM-131-1 and 1-VG-RM-131-2 were subsequently tested and returned to service on October 9, 1993, at 0437 hours. This Special Report is being submitted, pursuant to Technical Specifications, Table 3.7-6 and Section 6.2, since 1-VG-RM-131-2 was inoperable for a period in excess of seven days.
2801993012 | Surry 1 | 11/01/1993 | 11/29/1993 | 9312070320 | <strong>Safety Injection Accumulator Boron Concentration Level Less Than TS Limits for Greater Than Four Hours</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1993, with Unit 1 at 100% power and Unit 2 at 98.5% power, boron concentration in the Unit 1 Safety Injection Accumulator 'B' was found to be below the Technical Specification (TS) limit. A Limiting Condition of Operation (LCO) was entered at 2206 hours in accordance with TS 3.3.B which allows one accumulator to be inoperable for a period not to exceed four hours. The SI Accumulator 'B' was placed on recirculation from the Refueling Water Storage Tank (RWST) to increase the boron concentration. The four-hour LCO was exited at 0140 hours on October 16, 1993, when a resample of boron concentration was found to be within the TS limit. On November 1, 1993, System Engineering calculated that the Unit 1 SI Accumulator 'B' boron concentration level dropped below the TS limit approximately four days prior to the October 15, 1993 sample. Operating below the TS boron concentration limit for greater than four hours is in violation of TS 3.3.B which allows one accumulator to be inoperable for a period not to exceed four hours. <br /><br /> The SI Accumulator 'B' was continually available to deliver cooling water to the core. The accident analysis requirements for sump boron concentrations were satisfied. Therefore, no safety consequences resulted from this event and the health and safety of the public were not affected. <br /><br /> This report is being made pursuant to 10CFR50.73(a)(2)(i)(B) since the Station was operated in a condition not allowed by TS 3.3.B.
2801993013 | Surry 1 | 11/17/1993 | 12/16/1993 | 9312300190 | <strong>Volume Control Tank Level Decrease Results in Excessive Reactor Coolant System Leakage</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993, at 0945 hours, with Unit 1 at 91% reactor power and Unit 2 at Cold Shutdown, the Unit 1 Volume Control Tank (VCT) level decreased unexpectedly during an ion exchanger resin transfer. The Unit 1 Senior Reactor Operator (SRO) was notified immediately by the Reactor Operator (RO). Leakage through a two-inch manual isolation valve was diverting demineralizer effluent away from the VCT and into the resin transfer piping. The leakage was isolated promptly by closing the resin transfer isolation valve. Since the leakage was characterized as RCS leakage and exceeded 10 gallons per minute, a condition not allowed by Technical Specifications existed for a brief time. Therefore, this report is being made in accordance with 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications which occurred when Reactor Coolant System total leakage exceeded 10 gallons per minute. .
2801993014 | Surry 1 | 11/22/1993 | 12/20/1993 | 9401060061 | <strong>Delta Flux Not Logged While Alarm was Inoperable Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was operating at 88% power on November 22, 1993, when control room personnel noted that the Unit 1 calorimetric data point value generated by the Prodac 250 (P-250) computer system was not changing as expected. Instrumentation and Control Technicians investigated the discrepancy and determined that the P-250's integration and averaging program functions had failed. The P-250 was declared inoperable and Abnormal Procedure 0-AP-20.02 was initiated. The P-250 program failure rendered the 'Delta Flux Deviation' alarm inoperable. Technical Specification 3.12.B.4.d requires that delta flux be logged and assessed when this alarm is out of service. Control room personnel did not begin logging delta flux since they were not cognizant of the P-250 program failure. This event was caused by a procedural deficiency. To prevent recurrence, Abnormal Procedure 0-AP-20.02 will be revised to address a partial failure of the P-250, as well as a complete system failure. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(b) since delta flux was not logged and assessed as required by Technical Specification 3.12.B.4.d.
2801993015 | Surry 1 | 12/18/1993 | 01/13/1994 | 9401310394 | <strong>More Than One Individual Rod Position Indication Channel Per Group Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1993 at 1346 hours, Unit 1 was at 72.8% power in End-of-Life coast down and Unit 2 was at 100% power. Operations shift personnel had requested that Licensee Instrument Technicians calibrate Unit 1 Individual Rod Position Indication (IRPI) E-11. The technicians were performing Periodic Test, 1-PT-5.2, 'Analog Rod Position Instrumentation'. In order to perform the calibration, the technician had inserted the IRPI E-11 signal conditioning module with an extension card into the IRPI rack. Immediately, all control and shutdown IRPI went to zero and annunciator G-G-2, 'IRPI Power Supply Failure', was received. The technician immediately removed the card and all IRPI, except E-11, returned to normal. A six hour Limiting Condition of Operation (LCO) was momentarily entered and exited at this time in accordance with Technical Specification (TS) 3.12.E.3 which directed implementation of TS 3.0.1 due to all IRPI being inoperable. Inoperable IRPIs do not effect the operation of the control rod assemblies and all control rods remained capable of performing their intended safety function. There was no control rod movement during this event. No safety consequences resulted from this event, and the health and safety of the public were not affected. Therefore, this report is being made pursuant to 10CFR50.73(a)(2)(i)(B) since the Station was operated in a condition not allowed by TS.
2811993001 | Surry 2 | 04/20/1993 | 04/30/1993 | 9305070101 | <strong>Momentary Loss of Component Cooling Flow to Heat Exchanger Renders Residual Heat Removal Loop Inoperable - - Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>The operating loop of the Unit 2 residual heat removal system (RHR loop A) was rendered inoperable on April 20, 1993, at 2050 hours. The event occurred with Unit 2 at cold shutdown when the component cooling (CC) system flow to the RHR loop A heat exchanger (2-RH-E-1A) was inadvertently isolated. This condition resulted when CC system trip valve 2-CC-TV-209A closed. The valve actuation occurred when an electrical lead in the valve's power circuit was inadvertently determinated by station electricians. The control room annunciator for CC outlet header 1A low flow alarmed when 2-CC-TV-209A closed. Control room operators responded immediately by directing electricians to terminate the electrical lead. The lead was terminated and 2-CC-TV-209A was reopened at approximately 2051 hours. CC flow to 2-RH-E-1A returned to normal. This event resulted in no safety consequences or implications since the loss of CC flow was immediately recognized and prompt corrective actions were taken to restore it. The event was caused by a cognitive personnel error in that inadequate information was provided for use in developing tagout instructions. To prevent recurrence, procedures that control the process of de-terminating electrical leads will be reviewed and strengthened, as appropriate. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2811993002 | Surry 2 | 06/20/1993 | 07/15/1993 | 9307230337 | <strong>Unit 2 Automatic Reactor Trip Due to Low Steam Generator Water Level Coincident With Steam/Feedwater Flow Mismatch Resulting From Main Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was operating at 100% power on June 20, 1993, when Main Feedwater Pump 2-FW-P-1A tripped at 0415 hours. A Unit 2 automatic reactor trip followed at 0416 hours as a result of a low steam generator water level with steam/feedwater flow mismatch reactor protection signal from Steam Generator 2-RC-E-1A. Appropriate operator actions were taken to ensure the performance of system automatic actions and to respond to abnormal conditions. The Unit was quickly brought to a stable, no-load condition. The event was caused by the occurrence of an instantaneous electrical ground on the 2-FW-P-1A inboard motor and subsequent pump trip. A Root Cause Evaluation is being performed to determine the cause of the 2-FW-P-1A inboard motor electrical ground and to evaluate the conditions experienced following the reactor trip. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
2811993003 | Surry 2 | 08/03/1993 | 08/27/1993 | 9309030222 | <strong>Unit 2 Automatic Reactor Trip Due to Low Steam Generator Water Level Coincident With Steam/Feedwater Flow Mismatch Resulting From Spurious Closure of "A" MFRV</strong><br /><i>Abstract:&nbsp;</i>At 2005 hours on August 3, 1993, with Unit 1 at 100% power and Unit 2 at 97% power, Unit 2 experienced an automatic reactor trip. The trip occurred when the "A" Main Feedwater Regulating Valve (MFRV) unexpectedly closed, causing a feed flow/steam flow mismatch coincident with a low water level in the "A" steam generator. Reactor Protection System functions actuated as designed, and post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition, and the health and safety of the public were not affected. The cause of the closure of the MFRV was traced to an erratic power supply in the manual/automatic control station. This report is required by 10CFR50.73(a)(2)(iv).
2811993004 | Surry 2 | 08/23/1993 | 09/20/1993 | 9309280047 | <strong>Unit 2 Turbine-Generator Trip Via the Loss of Field Relay</strong><br /><i>Abstract:&nbsp;</i>At 0519 hours on August 23, 1993, with Unit 1 at 100% power and Unit 2 at 97.5% power, the Unit 2 reactor tripped due to a turbine - generator trip. Control room operators promptly initiated the appropriate emergency operating procedures. The reactor was placed in a stable, Hot Shutdown condition. The turbine-generator trip was caused by a loss of excitation field for the main generator due to a component failure in the voltage regulator (VR). During troubleshooting of the VR, a failed phase shifter card was discovered and replaced. As an additional precaution, two other cards were replaced along with the fuses between the field breaker and the firing circuit drawer. Following the trip, a fire watch notified the Shift Supervisor that sliding Fire Door 18 had shut. As a result, he could not complete his fire watch rounds of the Unit 1 Emergency Switchgear Room (ESGR) at 0523 hours, in accordance with Technical Specification 3.21. This fire door separates Unit 1 and 2 ESGRs. Following stabilization of Unit 2, an operator was dispatched and the sliding fire door was opened and relatched. During this event the health and safety of the pubic were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(2)(i)(b).
2811993005 | Surry 2 | 08/27/1993 | 09/27/1993 | 9310010127 | <strong>Reactor Trip Due to Partial Actuation of Safety Injection Master Relay During Logic Testing</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1993 at 1741 hours, with Unit 1 at Cold Shutdown, a Unit 2 automatic reactor trip occurred when both reactor trip breakers opened simultaneously. This Reactor Protection System (RPS) actuation occurred when train B safety injection master relay SIA-B partially actuated unexpectedly during monthly safeguards actuation logic functional testing. Only one of the four sets of contacts on the master relay made-up. This partial actuation resulted in a reactor trip signal which de-energized each reactor trip breakers' undervoltage trip coil. Both reactor trip breakers opened as designed. Proper procedure implementation and operator action stabilized the Unit at the Hot Shutdown condition. The Unit was subsequently brought to Cold Shutdown. The relay was replaced and tested. A Root Cause Evaluation (RCE), including additional testing, was conducted. The evaluation determined that the event resulted from relay chatter and low relay actuation and reset voltages. However, field tests could not identify a source of the voltage for the observed chatter. RCE recommendations to monitor testing for voltage sources and cover test connection jacks are being implemented. The health and safety of the public were not affected. This report is required by 10CFR50.73 (a)(2)(iv) for a Reactor Protection System actuation.
2811993006 | Surry 2 | 11/15/1993 | 12/13/1993 | 9312210406 | <strong>Unit 2 Automatic Reactor Trip Due to Low Steam Generator Level in Coincidence With Feed Flow Mismatch Following Closure of All Three Main Feedwater Regulating Valves</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1993, at 2019 hours, with Unit 1 at 95% power and Unit 2 at 95% power, Unit 2 experienced an automatic reactor trip. The trip occurred when an electrical circuit failure caused all three Main Feedwater Regulating Valves to go shut, isolating feedwater flow to all three steam generators. The resultant feedwater flow/steam flow mismatch coincident with low steam generator water levels actuated the Reactor Protection System (RPS), and the reactor trip breakers opened. The RPS functioned as designed, and post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition, and the health and safety of the public were not affected. The electrical failure was traced to a defective circuit breaker which was replaced. Three similar breakers whose failure alone could cause a reactor trip were also replaced. Additional corrective actions are under evaluation. This report is required pursuant to 10CFR50.73(a)(2)(iv).
2821993001 | Prairie Island 1, Prairie Island 2 | 01/05/1993 | 02/04/1993 | 9302110203 | <strong>Failure to Perform Hydrogen Recombiner Testing in the Sequence Specified by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>A comprehensive review of surveillance testing requirements is being performed to ensure all Technical Specification surveillance requirements are being met. This review is being made as corrective action to our Unit 1 Licensee Event Report 92-004. During this review, it was identified that our surveillance of hydrogen recombiners does not literally meet the requirements specified in Technical Specification 4.4.I, which requires that a functional test be performed every 6 months and that a resistance to ground test be performed every 18 months 'following the above required functional test.' Our procedures for testing hydrogen recombiners do not specify this order of testing. <br /><br /> When the system engineer identified the deficiency, he carried out an investigation to determine the basis for the specified order of testing, and to determine reportability of the finding. Discussions with technical people, including NRC representatives, resulted in the conclusion that there is no technical basis for the order specified in the Technical Specification. <br /><br /> On January 5, 1993, it was determined that the event is reportable since Technical Specifications were violated, though there is no safety significance attached to the violation. Procedure changes will be made.
2821993002 | Prairie Island 1, Prairie Island 2 | 01/05/1993 | 02/04/1993 | 9302110297 | <strong>Inoperability of Fire Doors Caused by Inappropriate Interpretation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1992, both units were at cold shutdown. The fire door between the Control Room and the Records Room, and the fire door between the Control Room and the operators' Study Area, had been blocked open to provide some cooling for those rooms while their normal cooling system was out of service due to cooling water header replacement. No compensatory measures had been taken; it was believed that since the Control Room side of the fire doors is continuously occupied, a fire watch was unnecessary. <br /><br /> Further discussions with NRC resulted in the conclusion that opening the doors made them inoperable and that a violation of Technical Specification 3.14.G.2 had occurred. The doors were closed and the fire barriers considered operable. Administrative procedures have been revised to include specific instructions on establishing fire watches for the doors.
2821993003 | Prairie Island 1 | 02/05/1993 | 03/08/1993 | 9303110219 | <strong>Nuclear Instrumentation System Power Range Channels Miscalibrated Due to Use of Improper Test Lead</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1993, Unit 1 was at 100% power. Surveillance procedure SP1007, Nuclear Power Range Functional Test, was in progress. The instrument technician found that the lower detector flux signal from all four Nuclear Instrumentation System (NIS) power range channels was significantly (about 10%) outside of the acceptance criterion. Investigation showed that on January 22, 1993, after the Unit 1 restart from refueling, SP1006B, NIS Power Range Axial Offset Calibration, had been performed using an improper test lead. Preliminary engineering review on February 5, 1993, indicated that the miscalibration could have resulted in some nonconservatism in the flux difference information provided to the overpower and overtemperature delta T protection channels. Based on this review, the event appeared to be reportable. All the Unit 1 NIS power range channels were recalibrated and the surveillance procedure completed satisfactorily. Procedures will be revised to preclude recurrence. Test lead labeling was improved.
2821993004 | Prairie Island 1, Prairie Island 2 | 02/09/1993 | 03/11/1993 | 9303180119 | <strong>AMSE Section XI ISI Examinations Performed with Incorrect Calibration Blocks</strong><br /><i>Abstract:&nbsp;</i>During the Fall 1992 Prairie Island Dual Unit Outage, with the plant in cold shutdown, the Authorized Nuclear Inspector noted that calibration block information was missing from the ASME Section XI ISI outage plan. Subsequent investigation showed that a number of ISI ultrasonic examinations had been performed with incorrect calibration blocks. All of the associated examinations will be evaluated for sensitivity and for coverage of required volume. Those examinations with unacceptable sensitivity or with less than required coverage will be repeated during the next refueling outage for each unit. The ISI plan will be revised to reflect correct calibration block information. ISI NDE procedures will be revised to assure that an acceptable calibration block is used and to assure that adequate examination coverage is achieved.
2821993005 | Prairie Island 1 | 02/18/1993 | 03/22/1993 | 9303260065 | <strong>Unit 1 Reactor Trip Due to Inadvertent Relay Operation Which Caused Loss of No. 12 Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1993, Unit 1 was at 100% power. Cleaning of floors in the Turbine Building was in progress. A plant services attendant was burnishing the floor in the area of Bus 12. Bus 12 supplies 4KV power to No. 12 RCP and No. 12 Feedwater Pump. While moving the machine along the end of Bus 12, a caster wheel of the machine caught in a joint in the floor. This forced the burnishing machine toward the bus and into the lower door hinge of Breaker 12-1, the offsite power supply to Bus 12. When the machine hit the door hinge of Breaker 12-1, the attendant heard the breaker operate. The attendant immediately called the control room to report the event. At 0814 the reactor had tripped; the first out annunciator received was 'One Loop Lo Flow or RCP Bkr Open.' <br /><br /> The reactor protection system responded as designed to the loss of Bus 12 and the unit was stabilized in the hot shutdown condition in accordance with plant procedures following the reactor trip. <br /><br /> Cause of the event was determined and restart accomplished in accordance with plant procedures. The unit was returned to service at 2333 hours.
2821993006 | Prairie Island 1, Prairie Island 2 | 03/25/1993 | 04/26/1993 | 9305030051 | <strong>Auto-Start of No. 121 Cooling Water Pump on Low Header Pressure While Aligned for Safeguards Operation</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1993, both units were at full power. Cooling water requirements were being supplied by No. 11 and No. 21 Motor-Driven Cooling Water Pumps. No. 22 Diesel-driven Cooling Water Pump was taken out of service for minor corrective maintenance, and No. 121 Motor-driven Cooling Water Pump was aligned for safeguards operation as required by Technical Specifications. This alignment includes closing of cooling water header valves to align No. 121 Pump to the affected header. When the maintenance on No. 22 Pump was complete, the routine surveillance test on No. 22 Pump was performed to prove operability. When No. 22 Pump was shut down, only No. 21 Pump was running to supply the affected cooling water header. The resultant decrease in system pressure was sufficient to cause No. 121 Pump to automatically start. This was a non-ESF actuation of ESF equipment. This LER is being made voluntarily.<br /><br /> The surveillance procedure contained inadequate instructions for disposition of the cooling water header valves. The procedure will be revised.
2821993007 | Prairie Island 1, Prairie Island 2 | 04/13/1993 | 09/22/1994 | 9410030082 | <strong>Discovery That Certain Valves Should Be Subject to ASME Section XI Testing</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1993 both units were at 100% power. The Design Basis Reconstitution effort for the Feedwater System revealed that certain feedwater valves required to mitigate the consequences of an accident were not included in the Prairie Island ASME Section XI Inservice Inspection and Testing Program. These valves should be classified as ASME Code Class 2 valves. <br /><br /> Subsequently, during the current development of the 3rd 10-year Interval Inservice Testing Program, we took an aggressive approach to determine any weaknesses in the current program in order to strengthen the program for the future. We reviewed violations issued against other licensees, reviewed generic discussions of industry issues, and discussed some interpretation questions with cognizant NRC Staff. As a result of this approach, we identified other ASME Code Class MC valves and six additional valves which should have been in the current program but were not. <br /><br /> An evaluation of the available data for each of these valves has been made to determine their operability. The valves will all be tested per the requirements of ASME Section XI and have been included in the 3rd 10- year interval program.
2821993008 | Prairie Island 1, Prairie Island 2 | 06/24/1993 | 07/23/1993 | 9308020069 | <strong>Containment Isolation Valve Failed Closed Due to Solenoid Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1993, Unit 1 was at 100% power. At 0357 hours, control room operators observed that valve CV-31740, Instrument Air to Unit 1 Containment, had closed. The valve could not be reopened from the control room. Cause of the valve closure was failure of a coil in its solenoid operated pilot valve. The loss of instrument air to containment resulted in several valve and damper movements, the most notable of which was letdown line isolation. At 0443, CV-31740 was reopened and held in the open position by bypassing its solenoid operated pilot valve and supplying air directly to the valve operator. At 0450, letdown was restored. <br /><br /> Operators responded to the loss of instrument air using approved procedures. An expeditious valve repair plan was instituted. CV-31740 is a containment isolation valve that closes on a containment pressure of 17 psig. The Technical Specification "shutdown action statement" had been entered, but power reduction had not yet begun when the valve repair was completed and the valve declared operable.
2821993009 | Prairie Island 1 | 07/15/1993 | 08/05/1993 | 9308120100 | <strong>Unplanned Closure of a Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1993, Unit I was operating at 100% power. At 0157, control room operators observed receipt of the annunciator "12 Charging Pump Overload Trip". Within seconds several other alarms were received (Letdown orifice isolation Valve - CLOSED, Low RCP Seal Injection Flow, Low RCP Labyrinth Seal DP) as a result of the trip of No. 12 Charging Pump. Since the pump was the only charging pump operating at the time, trip of the pump caused letdown isolation; the open letdown orifice isolation valve closed. Letdown orifice isolation valves also function as containment isolation valves. This unplanned closure of the letdown orifice isolation valve was a non-ESF actuation of ESF equipment. The operators started No. 13 Charging Pump, restoring charging flow and reactor coolant pump seal injection flow, and within 2 minutes they restored letdown. The outplant operator investigated the cause of the trip and found that the breaker for No. 12 Charging Pump had tripped. Since No. 11 and 13 Charging Pumps were available, no LCO was entered. <br /><br /> The breaker for No. 12 Charging Pump had tripped when the A phase motor lead grounded to the junction box.
2821993010 | Prairie Island 1, Prairie Island 2 | 07/29/1993 | 08/23/1993 | 9309010209 | <strong>Control Room Air Handler Out-of-Service While Surveillance Testing of a Diesel Generator Was in Progress</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1993 Unit 1 was at 100% power. At 0008, No. 121 Control Room Air Handler was removed from service for preventive maintenance. This action is in accordance with Technical Specification 3.13.A.2, which allows a 7-day Limiting Condition for Operation (LCO) to be entered. The LCO entry was logged on the control room LCO log. Later in the morning, the Unit 2 Shift supervisor was approached for approval to begin a routine surveillance test of D2 Diesel Generator, SP1037. The test procedure requires the Shift Supervisor to verify that D1 Diesel Generator and associated engineered safety features equipment are operable before beginning the test, because D2 Diesel Generator is declared inoperable during the period of the test. The Shift Supervisor reviewed Unit 1 status including the LCO log. When he read the entry regarding No. 121 Control Room Air Handler, he mistakenly thought the entry applied to No. 121 Control Room Chiller. The chiller was not ESF equipment. At 0800 the Shift Supervisor allowed the test to begin and the diesel generator was logged as inoperable. D2 Diesel Generator and No. 121 Control Room Air Handler had been inoperable simultaneously from 0800 to 1126.
2821993011 | Prairie Island 1, Prairie Island 2 | 09/03/1993 | 10/04/1993 | 9310130102 | <strong>Opening Found in Steam Exclusion Boundary</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1993 it was determined an opening had been made in the Steam Exclusion boundary that could potentially allow communication of a high energy line break (HELB) environment to a mild environment area of the Auxiliary Building, as described in Appendix I of the FSAR and USAR. The opening was in the 715 ft elevation floor. The opening was closed, and a walkdown was initiated to identify and close any other openings. An evaluation was initiated to establish whether or not design limits for an outside-of-containment HELB were exceeded, and if there was a potential impact on operability of equipment on 695 ft elevation required to mitigate the HELB event. <br /><br /> A temporarily sealed penetration between the Unit 1 Turbine Building and Bus Room 16 was identified, on September 13, 1993 as a potential steam impingement issue. A permanent impingement barrier was installed to ensure Bus 16 operability. An evaluation done later showed that the temporary seal was adequate to prevent the entry of steam into the bus room. <br /><br /> Work control processes are being reviewed for possible enhancement of identification, review and control of steam exclusion boundary openings.
2821993012 | Prairie Island 1, Prairie Island 2 | 09/08/1993 | 10/08/1993 | 9310130114 | <strong>Failure to Preform Offsite Dose and Effluent Monitor Setpoint Calculations Due to Procedural Inadequacy and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1993, the Radiochemistry Supervisor was reviewing the dose calculations for liquid and noble gas releases for the month of August 1993. During that review, he noted that the dose calculations due to radioactive releases of liquids and gases had not been completed for the month of July 1993. Further review showed that the monthly alarm setpoint calculations for liquid and airborne effluent monitors, which are normally performed at the same time as the dose calculations, were also not completed for the month of July 1993. The dose and setpoint calculations are required by Technical Specifications in accordance with methods specified in the Offsite Dose Calculations Manual. <br /><br /> Dose and setpoint calculations were performed on the July release data as soon as the oversight was detected. Those calculations verified that the previous monitor setpoints were correct and that the doses to the public were very small at less than 0.2% of quarterly and annual dose limits.<br /><br /> The monthly dose calculations and the monthly effluent monitor setpoint calculations are now being scheduled by the Chemistry Group's work scheduling program, and both calculations have also been added to the Chemistry Group's surveillance program.
2821993013 | Prairie Island 1, Prairie Island 2 | 09/08/1993 | 10/08/1993 | 9310130206 | <strong>Gaseous Effluent Sampling Requirements Not Met for a 2- day Period Due to Personnel Error and Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1993, a modification to an Auxiliary Building Ventilation Gas Monitor was begun. The Duty Chemist was notified that the monitor would be removed from service and that the building ventilation configuration would change. This notification is made to inform the Duty Chemist of the impending change in ventilation configuration so that gaseous effluent sampling methods can be adjusted to meet effluent monitoring requirements. The monitor was then isolated and its channel module power supply turned off. <br /><br /> On September 8, with the monitor still out of service, the control room operator restored the ventilation system to its normal configuration using standing operating procedures. At this change in the ventilation configuration, the Duty Chemist was not informed. <br /><br /> On September 10, it was determined that the normal ventilation configuration had been restored on September 8 without notification of the Duty Chemist. A representative sample had not been collected on the silica gel sampler for two days.<br /><br /> Procedures will be changed and training accomplished.
2821993014 | Prairie Island 1, Prairie Island 2 | 11/16/1993 | 12/16/1993 | 9312270056 | <strong>Cable Separation at Main Control Board</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1993, it was determined that control cables for redundant pressurizer power operated relief valves, found (several days earlier) to be touching behind the control board, violated criteria for physical separation of cables. The cables were repositioned and secured. Engineering evaluation concluded the cables were operable in the as-found condition. A complete inspection of the main control board was undertaken. Other instances of noncompliance with separation criteria were found. These have been analyzed and both the "as-found" and present configuration of the plant provide adequate protection for the operability of redundant equipment.
2851993001 | Fort Calhoun | 01/08/1993 | 02/08/1993 | 9302120206 | <strong>Failure to Satisfy Surveillance Requirement for Boric Acid Tank Level Check</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1993, the Operations Supervisor was reviewing maintenance to be performed on "B" Boric Acid Storage Tank (BAST) level indication (float switch LAS-253) with the Reactor Engineer. A potential problem was discussed regarding the surveillance requirements for a channel check. On review, it was identified that the BAST level surveillance was not being properly performed in that the existing surveillance test involved comparing two level indications (local and remote) from the same sensor (level bubbler), rather than comparing two independent sensors as required by Technical Specification (TS) 3.1, Table 3-2, Item 15.a. <br /><br /> The root cause of the event was determined to be an inadequate surveillance test to monitor the BAST levels. A review of plant records showed that the original 1973 surveillance test incorrectly identified the local and remote indications from the level bubblers as meeting the intent of comparing independent indications. <br /><br /> Temporary "sight glasses" have been installed to provide independent level indication at each tank. Additional actions will include a modification to control room alarm indication for low BAST level to provide individual annunciator windows for float switches LAS-260 and LAS-253 for comparison to level bubbler indications.
2851993002 | Fort Calhoun | 01/22/1993 | 02/22/1993 | 9303010164 | <strong>Inappropriate Steam Generator Low Pressure Signal Block Reset Values</strong><br /><i>Abstract:&nbsp;</i>During a review of calibration procedures for the Steam Generator Pressure Loops, it was determined that the current Steam Generator Low pressure Signal (SGLS) block reset values, for all four channels of both steam generators, were greater than that allowed by Technical Specification (TS) 2.14, Table 2-1. This TS allows SGLS to be bypassed (manually) below 550 psia, however, the block reset values were found to range from 562 to 566.5 psia. This condition has existed since the 1988-89 (Cycle 13) Refueling Outage. SGLS was not in a bypassed condition at the time of discovery of this event. <br /><br /> The root cause of this event has been determined to be improper design of the pressure indicating controllers.<br /><br /> An operability evaluation has been completed and procedures have been revised to ensure manual reset of SGLS prior to exceeding 550 psia. Additional corrective actions include revising surveillance tests and submitting a TS amendment request.
2851993003 | Fort Calhoun | 01/26/1993 | 02/25/1993 | 9303020534 | <strong>Failure to Satisfy Inservice Testing Requirement for Raw Water Pump</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1992, during the performance of the quarterly inservice test of Raw Water Pump AC-10A, as found data for pump performance was found to be in the Low Alert Range. For test values in the Alert Range, the Inservice Inspection Program Plan requires the testing frequency to be doubled until the cause of the deviation is determined and the condition corrected. On January 25, 1993, maintenance was performed and a post-maintenance test conducted on AC-10A. On January 26, 1993, during review of the performance data from the post-maintenance test, it was realized that the time limit for either performing the next inservice test (in accordance with the requirement for increasing testing frequency) or completing corrective actions, had been exceeded. An evaluation of available data and indications concluded that the pump was able to perform its design function during the period in question. <br /><br /> The root cause of this event was determined to be inadequate administrative controls. The administrative controls to ensure that the test frequency was adjusted or the corrective maintenance process would resolve the problem in a timely manner, were less than adequate.<br /><br /> Corrective actions include a change to the Station Engineering Instruction on surveillance testing, and a change to the Standing Order on conduct of maintenance.
2851993004 | Fort Calhoun | 03/01/1993 | 07/30/1993 | 9308090347 | <strong>Inoperability of Power Range Nuclear Instrumentation Safety Channel D</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1992, subchannel indication was observed to be intermittently oscillating for Power Range Nuclear Instrumentation (NI) Safety Channel A. Temporary Modification (TM) 92-078 was completed on October 31, 1992 to connect Power Range NI Control Channel A and B detectors to Safety Channels A and D respectively. On February 27, 1993, an abnormal response was noted for Channel D Axial Shape Index (ASI) in that it tracked opposite of Channels A, B and C. On March 1, 1993, it was confirmed that Channel D ASI was being calculated in reverse. Further review found that the power range NI subchannel in uts to Reactor Protection System Channel D had been reversed since completion of the temporary modification on October 31, 1992.<br /><br /> It was determined that the subchannel cables for the Control Channel B detector had been reversed prior to TM 92-078, apparently prior to initial startup in 1973. This problem was not identified when the Control Channel B detector was transferred to Safety Channel D in October 1992, due to insufficient post-TM testing and insufficient requirements for review of testing specified for TMs. <br /><br /> The Safety Channel D subchannel cables were exchanged on March 1, 1993 to correct the configuration and appropriate ASI response was verified. Additional corrective actions include revising administrative controls for post-temporary modification testing requirements. .
2851993005 | Fort Calhoun | 04/22/1993 | 05/24/1993 | 9306010147 | <strong>Seismic Design of Safety Injection & Refueling Water Tank Filter Piping</strong><br /><i>Abstract:&nbsp;</i>In March 1983, Modification MR-FC-83-046 was initiated to, in part, provide an alternate method for recirculating the Safety Injection and Refueling Water Tank (SIRWT). Over a period of several years, the modification was partially installed and several changes were pursued in response to identified concerns. During the 1992 Refueling Outage, an Incident Report was initiated to address concerns that sections of the piping associated with MR-FC-83-046 had potentially been placed in operation prior to the 1992 Refueling Outage without proper operability acceptance of the modification. On June 3, 1992, following resolution of identified concerns, the piping was Accepted for Operability. Following an engineering evaluation, it was determined that previous use of SIRWT recirculation piping associated with MR-FC-83-046 was reportable. <br /><br /> A Root Cause Analysis found that inadequate standards, policies and administrative controls led to over-reliance on personnel knowledge for the accomplishment of modifications. <br /><br /> Improved administrative controls have been implemented since initiation of MR-FC-83-046. In addition, the current process for releasing equipment for testing prior to Acceptance for Operability will be reviewed.
2851993006 | Fort Calhoun | 04/27/1993 | 05/26/1993 | 9306030201 | <strong>Failure to Maintain Continuous Fire Watch For Impaired Halon System</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1993, the Halon fire suppression system for the Switchgear Rooms was disabled to allow repair/replacement of Halon system piping. A continuous fire watch with back-up fire suppression equipment was established. On April 27, 1993 at 1941 CDT, a security officer on an hourly fire door check entered the Switchgear Rooms and noticed that the individual responsible for the continuous fire watch was not present. Computer records revealed that the individual had exited the Switchgear Rooms at 1930 CDT. Consequently, the Switchgear Rooms were without a continuous fire watch for eleven minutes, resulting in a violation of Technical Specification 2.19(8). <br /><br /> It has been concluded that the root cause of this event was personnel neglect and that the problem was isolated to this individual. The individual responsible for the fire watch at the time of the incident was a temporary contract employee. <br /><br /> The corrective action taken as a result of this event was to relieve the individual of his responsibilities, block his access to the Protected Area and terminate his services. .
2851993007 | Fort Calhoun | 04/30/1993 | 06/01/1993 | 9306090154 | <strong>Unplanned Emergency Diesel Generator Start and Reactor Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1993 at approximately 1019 CDT, with the Fort Calhoun Station in Hot Shutdown (Mode 3), a non-licensed operator was performing an independent verification of the return-to-service positions of equipment which had previously been taken out of service for maintenance. While intending to verify the installation of potential transformer fuses for Transformer T1A-1, the individual pulled the drawer with the potential transformer fuses for 4160V Bus 1A1. This resulted in a Bus 1A1 low voltage alarm, an automatic start of Emergency Diesel Generator DG-1 and load shedding of Bus 1A1 (including tripping of Reactor Coolant Pump RC-3A). Actual voltage on Bus 1A1 remained normal. The tripping of RC-3A resulted in a subsequent Low Reactor Coolant Flow reactor trip signal. <br /><br /> The causes of the event were determined to be inadequate attention to detail, inadequate labeling of the fuse drawers, inadequate caution signs and inadequate training. <br /><br /> Corrective actions will include upgrading of labeling and caution signs for 4160V cubicles and training for operators on potential transformer fuses.
2851993008 | Fort Calhoun | 05/20/1993 | 06/21/1993 | 9306280300 | <strong>Failure to Implement Surveillance Requirement for Stack Flow Indicator</strong><br /><i>Abstract:&nbsp;</i>As a result of issues discussed at a May 20, 1993 Plant Review Committee (PRC) meeting, it was determined that Technical Specification (TS) Surveillance Requirement 3.12.1(2)b(iv) had not been satisfied and that the failure to implement this Surveillance Requirement was reportable. This specification required the Laboratory and Radioactive Waste Processing Building (LRWPB) exhaust stack flow rates to be calibrated and functionally tested at a refueling frequency. This requirement was associated with TS Amendment 137 which was issued March 7, 1991. The LRWPB exhaust stack flow instrument loop was installed as a part of Modification MR-FC-88-121. <br /><br /> The root cause of this event was determined to be lack of attention to detail. The various departments and personnel involved in this event failed to review Modification MR-FC-88-121 and TS Amendment 137 in sufficient detail to ensure all required procedure updates and new procedures were identified and developed. <br /><br /> Corrective actions will include developing calibration and functional test procedures, and establishing a requirement for a verification of procedure changes which are developed to address a TS amendment.
2851993009 | Fort Calhoun | 05/24/1993 | 06/22/1993 | 9306290348 | <strong>Automatic Start of Backup Charging Pumps and Isolation of Letdown Flow</strong><br /><i>Abstract:&nbsp;</i>At 2015 CDT on May 24, 1993, with the Fort Calhoun Station operating at 100% power (Mode 1), an apparent spurious signal from pressurizer level instrumentation (LC-101X) caused both backup charging pumps (CH-1A and CH-1B) to automatically start. Both backup charging pumps are designed to start when actual pressurizer level drops below programmed level by more than three percent. Immediate and subsequent investigations indicated no such deviation existed. Letdown Isolation Valve HCV-204 subsequently closed automatically due to letdown pressure oscillations. Volume control tank and pressurizer level response was normal for the increased charging flow transient.<br /><br /> Deterioration of wiring in LC-101X is suspected to have caused the start signal. <br /><br /> A Maintenance Work Order has been initiated to inspect the wiring connections on LC-101X and an instrument loop calibration will be performed. .
2851993010 | Fort Calhoun | 06/11/1993 | 07/12/1993 | 9307200021 | <strong>Failure to Address Low Halon Tank Pressure Following Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1993, during performance of Surveillance Test GM-ST-FP-0005, "Semi-Annual Switchgear Rooms Halon Cylinders Weight and Pressure Test", one of the 14 Halon cylinders did not meet the minimum pressure acceptance criteria listed in the procedure. This unacceptable pressure value was not noticed during performance of the test. After the surveillance test was completed, the Switchgear Rooms Halon system was returned to service. The unacceptable pressure value was identified during the post-performance review of the test by the System Engineer on June 14, 1993. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) due to the failure to satisfy Technical Specification 2.19(8) between June 11, 1993 and June 14, 1993. <br /><br /> The causes of the event were determined to be the failure of the surveillance test to include the necessary steps to assign responsibility for verification of data for acceptability and failure to self-check/verify. <br /><br /> The Halon cylinder was recharged and retested on June 14, 1993. Additional corrective actions will include revising specified procedures to clarify responsibilities .
2851993011 | Fort Calhoun | 06/24/1993 | 07/26/1993 | 9308020039 | <strong>Reactor Trip on Loss of Load During Switchyard Maintenance</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1993 at 1322, the Fort Calhoun Station (FCS) experienced a reactor trip due to a Loss of Load. Work was in progress in the FCS switchyard involving Type SBFU Static Circuit Breaker Failure Relays, when a door mounted Type AR relay was inadvertently actuated. This, in turn, tripped two breaker failure lock-out relays, which resulted in opening of station output breakers and de-energized both 4.16kV non-vital buses. One non-vital bus failed to properly load shed on the loss of voltage, and as a result breakers remained closed on the bus even though the bus was de-energized. Initial Operator actions, based on Control Room indications that these breakers were closed, resulted in a short-term interruption of feedwater and condensate flow.<br /><br /> This event was determined to have resulted from lack of proper job planning, lack of a formal decision making process, incomplete communications and inadequate implementation of a procedure. <br /><br /> Corrective actions include actions to improve the conduct of work within the switchyard, and training for Operations personnel on use of all available indications in decision making.
2851993012 | Fort Calhoun | 09/23/1993 | 10/25/1993 | 9310290117 | <strong>Inadequately Sized Motor Operated Valve Power Cables</strong><br /><i>Abstract:&nbsp;</i>Engineering Analysis EA-FC-93-070 identified a condition involving five Motor Operated Valves (MOVs) which were found to have power cables that were inadequately sized to withstand sustained locked-rotor current. The condition did not affect the operability of any of the five valves because the condition did not impact the ability of the valves to perform their specified functions. However, in the event of any of the five valves failing such that it were to draw sustained locked-rotor current when called upon to operate, the valve's power cable could overheat, igniting the cable insulation and jacket. The ignition of the cable could potentially result in fires in more than one Fire Area of the plant. On September 23, 1993, the Plant Review Committee concluded that this condition was reportable. <br /><br /> Investigation of this issue identified the primary cause to be a lack of attention to detail in the design package preparation for a 1990 modification. The modification installed bypass devices for existing thermal overload protection without addressing adverse effects on circuit protection. <br /><br /> Corrective actions include enabling the existing thermal overload protection for the five valves, and evaluating long term circuit protection alternatives.
2851993013 | Fort Calhoun | 10/02/1993 | 10/29/1993 | 9311030306 | <strong>Pressurizer Safety Valve Outside Lift Setting Acceptance Criterion</strong><br /><i>Abstract:&nbsp;</i>At 1324 on October 2, 1993, during a scheduled refueling outage, it was discovered that the "As-Found" lift pressure of Pressurizer Safety Valve (PSV) RC-141 was outside its specified lift setting acceptance criterion. Fort Calhoun Station (FCS) Technical Specification (TS) 2.1.6(1) indicates that this valve is to have its lift setting adjusted to ensure valve opening at 2545 psia +/-1%. The "As-Found" lift pressure was 2596 psig, which corresponds to a drift of +2.6%. The other PSV, RC-142, was found to be within its acceptance criterion.<br /><br /> It was concluded that the root cause of this event was normal setpoint drift/scatter. <br /><br /> Corrective actions included adjusting RC-141 so that the "As-Left" lift setting was within the +/-1% tolerance range.
2851993014 | Fort Calhoun | 10/05/1993 | 12/20/1993 | 9312290257 | <strong>Failure of Power Operated Relief Valve to Open During Testing</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1993, with the Fort Calhoun Station in Hot Shutdown (Mode 3), during preparations to test Power Operated Relief Valves (PORVs) PCV-102-1 and PCV-102-2, PCV-102-1 was inadvertently opened twice. When the actual test was performed, PCV-102-1 did not open and was declared inoperable. Subsequent testing, after the valve was allowed to cool, was successful for both PCV-102-1 and PCV-102-2. On October 5, 1993, based on preliminary information regarding possible thermal binding of valve internals, it was concluded that this issue should be reported pursuant to 10 CFR 50.72 due to concerns that both PORVs could be impacted. <br /><br /> Subsequent investigation concluded that thermal binding was not involved and instead that the root cause of the failure of PCV-102-1 to complete multiple cycles was improper valve maintenance during modification work in 1984. This condition affected PCV-102-1 only. Additionally, disassembly and inspection found cracking of the main disks of both PORVs. A concern regarding venting line backpressure was also identified. <br /><br /> The PORVs have been refurbished and successfully tested. Additional corrective actions include developing an inspection, refurbishment and acceptance testing program for the PORVs, resolving the venting line backpressure concern, performing a metallurgical analysis to investigate the main disk cracking and eliminating the PORV loop seals.
2851993015 | Fort Calhoun | 11/09/1993 | 12/09/1993 | 9312200320 | <strong>Manual Emergency Boration Following Spurious Increase in Indicated Power</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1993, with the plant in Mode 5 (Refueling Shutdown) for a refueling outage, control room operators were in the process of filling the Reactor Coolant System (RCS). At approximately 0230, Wide Range Nuclear Instrumentation (WRNI) Channels A and D were observed to be rapidly cycling between 1.0 E-7% and 1.0 E-4% power. Channels B and C were not showing any unusual indications. An emergency boration of the RCS was initiated and the containment building was evacuated. Troubleshooting determined that the erratic power indications had been due to induced electrical noise. At all times during the event, shutdown margin was adequate.<br /><br /> It was determined that the cause of abnormal indication for WRNI Channel A was circuit noise induced on the extended range detector input at the pre-amplifier. In addition, it was determined that the indicated oscillations on Channel A were 'coupled' to WRNI Channel D through external counters which had been temporarily connected to the WRNI channels. <br /><br /> Corrective actions include maintenance performed on WRNI Channels A and D and revising procedures regarding connection of WRNI channels to external counters.
2851993016 | Fort Calhoun | 11/13/1993 | 12/13/1993 | 9312210023 | <strong>Unplanned Control Rod Withdrawal and Subsequent Manual Reinsertion</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1993, a surveillance test was beings performed on the Secondary Control Element Assembly Position Indication System (SCEAPIS), during a refueling outage, with the plant in Mode 5 (Refueling Shutdown). At approximately 2200, a Control Element Assembly (CEA) began to withdraw from the reactor core. A "Continuous Rod Motion" alarm was received, and a licensed operator placed the CEA mode selector switch in Off, which prevents CEA movement. During troubleshooting, Rod 31 became fully withdrawn. Rod 31 was then driven back into the core and the mode selector switch returned to Off. The reactor was then manually tripped to ensure rods were at their lower stop and to return the system to its pretest configuration. <br /><br /> Troubleshooting identified multiple electrical grounds associated with control rod drive and position indication circuitry, and a wiring deficiency. These conditions resulted in an unintended electrical circuit that energized the raise contactor for Rod 31. The root cause of the event was determined to be the lack of a ground detection system for the associated power supplies. <br /><br /> Corrective actions include troubleshooting and testing of the Control Rod Drive System and installation of ground detection for the Control Rod Drive power supply.
2851993017 | Fort Calhoun | 11/16/1993 | 12/16/1993 | 9312210402 | <strong>Time Delay Relays for Offsite Power Low Signal Found Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1993, with the plant in Refueling Shutdown (Mode 5), a System Engineer reviewing completed Offsite Power Low Signal (OPLS) calibration procedures discovered that the as-found time delays for three of four OPLS actuation relays were outside the time delay range specified in Technical Specification Table 2-1. The maximum allowable time delay is 5.3 seconds (i.e., 4.8 + 0.5 seconds). The as-found time delays for the four OPLS actuation relays were 5.3, 5.6, 5.7 and 6.7 seconds. The as-left settings following calibration of the relays were within the specifications in the calibration procedures. <br /><br /> The root cause of this event was determined to be inadequate technical review of the calibration procedures for the OPLS circuitry. The vendor manual that applies to these relays specifies how the relays are to be set, however, some of the recommended steps (involving re-checking the time delay relays against the initial time setting after the relay has been in operation) were not included in the Fort Calhoun Station calibration procedures. <br /><br /> Corrective actions include re-checking the OPLS actuation relays and revising OPLS calibration procedures.
2851993018 | Fort Calhoun | 12/06/1993 | 01/05/1994 | 9401120226 | <strong>Reactor Trip Due to Turbine Trip on Low Hydraulic Fluid Pressure</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1993 at approximately 0227 hours, the main turbine and the reactor tripped during Electro-Hydraulic Control (EHC) pump start testing. <br /><br /> The main turbine trip and resultant reactor trip occurred because of the configuration of the EHC System hydraulic fluid tubing connected to pressure switches PS-5096, PS-5097, and PS-5098, and to associated solenoid valves PS-5097-20 and PS-5098-20. The tubing configuration had been changed during the recent refueling outage by Facility Change Engineering Change Notice (ECN) 93-162. The Root Cause of this event was determined to be inadequate design of the ECN. Specifically, personnel involved in the design and review of the ECN failed to analyze the effects of increased lengths of hydraulic tubing on the operation of the EHC system. The contributing cause is inadequate pre-operational testing specified in the ECN.<br /><br /> Corrective actions include correcting the configuration of the EHC System tubing; establishment of guidance to identify which Facility Change ECNs have the potential to impact plant safety or reliability, and to specify the appropriate level of review by plant personnel for these ECNs; procedural changes to ensure proper pre-operational testing; and training for appropriate personnel.
2851993019 | Fort Calhoun | 12/09/1993 | 01/10/1994 | 9401210092 | <strong>Auxiliary Feedwater Pumps Inoperable Due to Inappropriate Testing Lineup</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1993 at 0950, while the plant was operating at 95% power, the electric and steam powered Auxiliary Feedwater (AFW) pumps (FW-6 and FW-10 respectively) were placed in a testing lineup that rendered them both inoperable for approximately 18 minutes. This occurred during the performance of Surveillance Test SE-ST-AFW-3005. Specifically, FW-10 was inoperable due to the control switch for the steam supply valve for FW-10 being out of the AUTO position, and FW-6 was inoperable due to establishment of a recirculation flow path. While personnel involved in the test had discussed manual actions that would be required to return the equipment to service in the event of an emergency, these manual actions were not outlined in the procedure. This event was determined to be a violation of Technical Specification 2.5.<br /><br /> It was determined that clear direction had not been established for declaring equipment inoperable during surveillance testing. It was also determined that a recent revision to SE-ST-AFW-3005 had added steps rendering the steam driven pump FW-10 inoperable for essentially the duration of the test. <br /><br /> Corrective actions include revising SE-ST-AFW-3005, establishing a procedure addressing equipment operability during testing, and providing training to Qualified Reviewers of procedure changes.
2851993020 | Fort Calhoun | 12/30/1993 | 02/16/1994 | 9402240222 | <strong>Ventilation Mode Requirement Not Met While Toxic Gas Monitors Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1993 at 2155, Toxic Gas Monitor YIT-6286A ran out of chemically impregnated paper tape, rendering it inoperable. On December 30, 1993 at 0015, Monitor YIT-6286B also ran out of tape and Technical Specifications thus required that the Recirculation mode of the Control Room Ventilation System be initiated within one hour, and maintained. Train 'A' of the ventilation system was placed in Recirculation mode, but it was presumed that this would not be necessary for Train 'B', due to the Train 'B' air conditioning unit being tagged-out for maintenance. At 0359, a Ventilation Isolation Actuation Signal (VIAS), generated as a part of a routine surveillance test, started the Train 'B' air supply fan, directing filtered outside air into the Control Room. At 0405, the fan was secured and Train 'B' was placed in Recirculation mode. <br /><br /> The root cause of the event was determined to be failure to complete procedural requirements. <br /><br /> Corrective actions include conducting briefings of operating crews, assessing the adequacy of the training lesson plan addressing the Control Room Ventilation System, revising the operating instruction on Control Room Ventilation System recirculation operation, and improving scheduling controls for replacement of toxic gas monitor tape.
2861993001 | Indian Point 3 | 12/04/1992 | 01/15/1993 | ML09344141 | <strong>Missed Surveillances on Radioactive Liquid Effluent Flow Rate Monitor</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1992 Indian Point 3 was at 100% power. A Quality Assurance audit identified that the Liquid Radwaste Effluent Flow Rate Measurement Device (FT-1064) had missed its quarterly surveillance test as required by Plant Technical Specifications. Further investigation determined that FT-1064 was not incorporated into the surveillance program. Surveillance requirements were established for FT-1064 by Technical Specification Amendment 51 on December 7, 1984. The root cause was personnel errors by staff members while updating the surveillance program for a technical specification amendment. The individuals responsible for ensuring the updates did not follow up upon identifying the need for a test. The reason for the lack of follow action has not been determined. Corrective actions include writing and implementing the required surveillance tests, and reviewing Amendment 51 surveillance requirements. Staff responsible for the implementation of Amendment 51 have reviewed this LER to ensure an understanding of the implication of the event and the need for attention to details.
2861993002 | Indian Point 3 | 11/25/1992 | 01/18/1993 | ML09344141 | <strong>Design Oversight Discovered That Could Result in Loss of Containment For Certain Accident Scenarios</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1992, with the unit operating at sixty-two percent power, the New York Power Authority discovered a design oversight that, under certain scenarios, could have potentially resulted in a loss of containment integrity following a small break loss of coolant accident (SBLOCA) or main steam line break (MSLB) inside containment. The loss of containment was related to the reenergizing of non-safety related equipment inside containment according to emergency operating procedures. The cause of the event was a design oversight. The exact root cause is unknown. Corrective action will be to install fuses as redundant isolation devices or provide increased sensitivity to the short time overcurrent trip units of the pressurizer heater group main supply breakers.
2861993003 | Indian Point 3 | 12/04/1992 | 01/21/1993 | ML09344141 | <strong>Missed Surveillance on Gaseous Effluent Flow Rate Monitor</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1992, with the unit operating at sixty-two percent power, the New York Power Authority discovered a design oversight that, under certain scenarios, could have potentially resulted in a loss of containment integrity following a small break loss of coolant accident (SBLOCA) or main steam line break (MSLB) inside containment. The loss of containment was related to the reenergizing of non-safety related equipment inside containment according to emergency operating procedures. The cause of the event was a design oversight. The exact root cause is unknown. Corrective action will be to install fuses as redundant isolation devices or provide increased sensitivity to the short time overcurrent trip units of the pressurizer heater group main supply breakers.
2861993004 | Indian Point 3 | 12/29/1992 | 05/28/1993 | ML09344143 | <strong>32 Auxiliary Boiler Feed Pump Inoperable due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993, the Authority concluded that a failed microswitch on No.32 steam driven Auxiliary Boiler Feed Pump (ABFP) had rendered the pump inoperable from December 3, 1992 through December 29, 1992. This condition is prohibited by Indian Point 3 Technical specification 3.4.C.1 and 2.<br /><br /> The causes of this event were a personnel error; the switch was not properly adjusted, and an inadequate surveillance test procedure; the surveillance test procedure did not verify that the microswitch had reset. <br /><br /> The Staff was trained and the surveillance tests have been revised to prevent recurrence.
2861993005 | Indian Point 3 | 12/31/1992 | 08/12/1993 | ML09344156 | <strong>Missed Periodic Inservice Tests and Faults in AMSAC System Logic, Due to Personnel Error, Place the Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1992, with the reactor at 100 percent power, a 40 second time delay in the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) logic failed to operate during the performance of a surveillance test. On two separate instances, software manipulations affecting the 40 second time delay placed AMSAC in a condition of degraded operability. On February 26, 1993, with the reactor at 97 percent power, the Authority reported that certain AMSAC system periodic inservice tests had not been performed for the last two refueling outages. A unit shutdown was initiated the same day (February 26, 1993) to correct the periodic inservice test issue. Subsequently, on March 5, 1993, with the reactor at hot shutdown, the Instrumentation and Controls department discovered a design deficiency involving the AMSAC actuation logic. Due to the 40 second time delay events, inservice test issue and design deficiency, the AMSAC system did not meet the requirements of the ATWS rule (10 CFR 50.62). The cause of these separate events is attributed to human error. Various corrective action steps have been developed to address the human error causal factor. Prior to the plant achieving criticality the AMSAC system will be restored to full compliance with our commitments to 10 CFR 50.62.
2861993006 | Indian Point 3 | 01/20/1993 | 03/03/1993 | ML09344141 | <strong>Low Pressure Steam Dump System Inoperability Due to Violation of Cable Separation Criteria by Power Supply Cable for Main Boiler Feed Pump Lubrication il Purifier</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1993, with the plant operating at 30 percent power, Indian Point 3 (IP3) Site Engineering personnel identified a condition wherein the plant's cable separation criteria was not met. A cable, identified as the power supply cable to the main boiler feed pumps lubrication oil purifier, crossed two cable trays which contained cables for the low pressure steam dump system. The cause for this event was improper installation of the main boiler feed pumps lubrication oil purifier and inappropriate determination that this installation would not adversely affect adjacent equipment. Upon discovery of this condition, the low pressure steam dump system was declared inoperable and the required compensatory action was taken. The power supply cable was removed and restored proper cable separation. The low pressure steam dump system was declared operable at 2215 hours on January 21, 1993.
2861993007 | Indian Point 3 | 02/08/1993 | 03/12/1993 | ML09344142 | <strong>Inadequate Appendix R Emergency Lighting Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1993 Indian Point Unit 3 (IP3) was at 100% power. An evaluation identified that IP3 was outside the design basis for the access/egress requirements of 10CFR 50 Appendix R section III.J. Two operator egress pathways do not have the required eight hour emergency battery lighting specified in Appendix R Section III.J. The root cause for these deficient egress pathways was a design deficiency. Appendix R plant modifications did not completely identify the specific areas for emergency lighting. Corrective actions include improved modification procedures that now address assessment of Appendix R Section III.j requirements, planned addition of fixed eight hour emergency battery lighting units in the deficient areas, and a notation will be inserted in the Appendix R operating procedures to assess procedure revisions for adequate emergency lights. Hand held eight hour rated emergency battery lighting units will be available and reserved for use during an Appendix R event until permanent lighting is installed.
2861993008 | Indian Point 3 | 07/23/1992 | 03/16/1993 | ML09344142 | <strong>Plant Heatup above Cold Shutdown With Control Room Ventilation System Administratively Inoperable Due to Failed Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1992 plant operators brought the plant above the cold shutdown condition with the control room ventilation system degraded and administratively inoperable. The cause of the degradation was that one of the two redundant filter booster fans (number 32 fan) did not provide the minimum outside air makeup flow specified in a periodic surveillance test's acceptance criteria. Additionally the system was administratively inoperable because the surveillance test was not reviewed and signed by a licensed operator in accordance with our administrative procedures. The root causes of the event were personnel error, inadequate program staffing, insufficient change management, and insufficient communications. Corrective actions include reassignment of personnel, revising the administrative procedure governing the surveillance test program, appointing a permanent surveillance test program administrator, enhancing PFM-49, "Start-up Prerequisite List," establishing departmental coordinators, and implementing an administrative procedure to clarify responsibilities for plant mode changes. The control room ventilation system was restored to operable status on December 16, 1992. Reviews of the surveillance tests have been performed and are undergoing final evaluation. Any corrective actions associated with mode changes will be resolved prior to going above cold shutdown.
2861993009 | Indian Point 3 | 01/28/1993 | 07/09/1994 | ML10049068 | <strong>Incorrect Operability Criteria for the RWST Due to Not Combining Loop Inaccuracies</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1993 a QA audit identified a non-compliance associated with surveillance test operability criteria for the refueling water storage tank lo-lo level alarms. Combined inaccuracies of the transmitter and bistables were not factored into the surveillance test operability criteria. A review of 21 surveillance tests conducted over 204 months identified five tests not satisfying "as-found" operability criteria and four tests not satisfying "as-left" operability criteria. The causes of the event were an original design that did not calculate inaccuracies and the engineers that developed the operability criteria of the original surveillance tests in 1975 did not combine inaccuracies of a transmitter and bistables in an alarm circuit. Accuracy calculations identified the five "as-found" and four "as-left" conditions. A contributing cause was an incorrect revision to the operability criteria in 1989 due to a personnel error. The criteria did not ensure operability of the required number of alarms circuits. Corrective actions include evaluating the adequacy of the instruments to provide for the specification, revising the surveillance test operability criteria, and reviewing similar surveillance tests for instrument inaccuracy concerns and multiple mode changes.
2861993010 | Indian Point 3 | 02/19/1993 | 03/26/1993 | ML09344142 | <strong>Boric Acid Transfer Pump Surveillance Test Failure</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1993 with the plant at full power, a staff member determined that the operability criteria had not been met for the surveillance test 3PT-Q38, Boric Acid Transfer Pump Functional Test, performed on February 19, 1993. Personnel error by test performers and reviewers had resulted in an incorrect operability determination. Notes included as part of the body of the test were incorrect and led the non-licensed operators performing the test to believe that the calculated values for delta pressure were adequate. Boric Acid Transfer Pumps 31 and 32 (CB) (BATP) were declared inoperable at 1235 on February 25, 1993. This condition is prohibited by Indian Point 3 technical specification section 3.2.B.2. A load reduction using normal operating procedures was commenced at 1245. An installed pressure indicator was replaced and a retest of the BATPs was performed. The pumps were declared operable at 2125 on February 25, 1993 and the load reduction was terminated.
2861993011 | Indian Point 3 | 03/19/1993 | 04/16/1993 | ML09344143 | <strong>Loss of Reactor Coolant System (RCS) level indication while in a reduced inventory condition</strong><br /><i>Abstract:&nbsp;</i>On Friday, March 19, 1993, with the plant in a cold shutdown condition, the water level in the Reactor coolant System (RCS) was drained to a reduced inventory condition to permit the testing of the Ultrasonic Level monitoring System (ULMS). The ULMS is one of two (2) RCS level indication systems required to be operable during reduced inventory conditions. During the performance of the test, the RCS level gauge being used to monitor RCS level was isolated for a short period of time to permit checking its response. This resulted in the plant having no operable indication of RCS level for that period of time while in a reduced inventory condition. Coincidental to this situation, maintenance work was proceeding on Reactor Coolant Pump (RCP) seal replacement without the plant having the required two (2) independent RCS level indication systems operable. These conditions placed the plant outside its design basis. The root causes were inappropriate actions made by several members of the plant staff coupled with inadequate communications within the plant's organization. Procedural deficiencies and engineering inadequacies were contributing factors. Corrective actions include procedural upgrades, reengineering of the RCS level indicating system, critiques with the individuals involved to provide positive reinforcement of lessons learned and dissemination of the summary of the event to the plant staff to alert the staff to its significance.
2861993012 | Indian Point 3 | 04/06/1993 | 05/07/1993 | ML09344143 | <strong>Weld Channel and Containment Penetration Pressurization Supply Line Disconnect, Caused By Personnel Error, Placed Plant Outside Design Basis.</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1993, with the plant in the cold shutdown condition, a quality control inspector found a disconnected Weld Channel and Containment Penetration Pressurization (WCCPP) supply line which leads to four lines in penetration "RR". The disconnected line resulted in a configuration where only one boundary existed between the Vapor Containment (VC) and the Primary Auxiliary Building (PAB) atmosphere. The event placed the plant outside its design basis because the Final Safety Analysis Report requires two barriers between the VC and PAB atmospheres. This condition is prohibited by Indian Point 3 Technical Specification sections 3.6.A.1 and 3.3.D.1.a. The disconnect most probably occurred during Integrated Leakage Rate Test (ILRT) preparation work for the ILRT completed on December 2, 1990. The event is attributable to human error (error in judgement) in that procedures were not followed. Maintenance reconnected the WCCPP line on April 7, 1993. Operations and Performance managers have apprised their personnel of the requirements for system configuration control and the ILRT test will be revised and reviewed for completeness. The WCCPP check off list will be revised for adequacy.
2861993013 | Indian Point 3 | 04/14/1993 | 07/15/1993 | ML09344146 | <strong>Personnel error, inattention to detail, resulted in possible failure of Fan Cooler Unit Dampers to operate.</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1993, at approximately 2000 hours, with the plant in the cold shutdown condition, the control room operators performing System Operating Procedure SOP-CB-10, "Fan Cooler Unit Operation," discovered that dampers A and B on three of the five fan cooler units (FCU) did not operate as required. As a result, in the event of an emergency, the dampers may not have assumed their fully closed post accident position. On April 23, 1993 the Authority determined that the FCUs were inoperable for an indeterminate time from July 23, 1992 to March 7, 1993, while the plant's operation varied between full power and cold shutdown. Operation of the reactor with inoperable FCUs is prohibited by Indian Point 3 Technical Specifications 3.3.B.1.b, 3.3.B.2.a and 3.3.B.3.b. The cause of this event is personnel error, inattention to detail, that resulted in a failure to include the dampers in a preventive maintenance program. The Maintenance Department will develop a preventive maintenance procedure and will include the FCU dampers in the program. The Maintenance Department will review the vendor technical manuals to ensure that vendor recommendations are being followed. The FCU dampers were cleaned, lubricated and satisfactorily retested by April 27, 1993.
2861993014 | Indian Point 3 | 04/23/1993 | 05/20/1993 | ML09344143 | <strong>Cognitive Personnel Error Resulted in an Unplanned Radiation Exposure During Disposal of Radioactive Material</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993, with the reactor at cold shutdown, a Nuclear Radwaste Utility Operator received an unplanned radiation dose of 251 mrem during the disposal of radioactive waste material into a High Integrity Container. Workers failed to comply with Technical Specifications 6.8.1 requiring that written procedures be established, implemented, and maintained; and 6.12.1 requiring that individuals in high radiation areas be provided with alarming radiation monitoring devices or Health Physics coverage according to Radiation Work Permits. The cause was cognitive personnel errors associated with communications and procedural adherence. corrective actions include: investigating the incident; communicating the incident; reemphasizing radiological protection to the plant staff; improving high radiation area postings; implementing disciplinary actions; and improving the radiation work permit program and training. During a review of the safety significance of the incident the Authority determined that, although there was a potential for a higher individual dose, it would have been less than the administrative dose limit of 1000 mrem per quarter.
2861993015 | Indian Point 3 | 04/27/1993 | 05/27/1993 | ML09344144 | <strong>Service Water System Placed in a Configuration not Controlled by Plant Operating Procedures due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1993, at approximately 1930 hours, in response to a NRC question, Operations Management determined that the service water system had been cross-connected in a configuration that was not covered by the plant's operating procedures. This action was taken to prevent damage to service water pumps that were operating with insufficient flow. The configuration existed only while the plant was in the cold shutdown condition. Indian Point 3 Technical Specification 6.8.1 requires that written procedures be established, implemented and maintained as recommended in Appendix A of Regulatory Guide 1.33. The cause for this event is an error in judgement by Operations management due to an inadequate appreciation of the requirement for procedural control of plant systems in all modes of operation. A contributing factor was inadequate procedural direction to cover the required operation. On May 8, 1993, a procedure for cross connecting the service water system headers in cold shutdown was issued with an approved safety evaluation. The Operations manager and the General Manager-Operations conducted meetings with all operations personnel to discuss compliance with operating procedures. As a result of these meetings, management decided that a policy of strict adherence to operating procedures shall be established prior to plant startup. To address the broader procedural adequacy issue, Indian Point 3 is currently implementing a procedure upgrade program.
2861993016 | Indian Point 3 | 04/28/1993 | 05/29/1993 | ML09344144 | <strong>Weld Channel and Containment Penetration Pressurization Nitrogen Backup Pressure Went Below Minimum Required by the Design Basis Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1993 at approximately 0800 hours, with the plant in the cold shutdown condition, an NRC inspector noted that the Weld Channel and Containment Penetration Pressurization (WCCPP) system nitrogen (N sub 2) backup pressure was below the minimum required by the plant operating logsheet. Based on these preliminary results the Authority concluded that the plant operated outside its design basis. The cause of this event is personnel error. A calculation to determine the minimum WCCPP N sub 2 backup pressure required to meet design basis and to validate the logsheet value was never performed. Therefore, operators did not appreciate the significance of the low N sub 2 pressure readings. The planned corrective action is to revise the conventional and nuclear logsheets to identify design basis parameters, repair WCCPP N sub 2 backup system leaks, and complete a basis document for all logsheet parameters.
2861993017 | Indian Point 3 | 04/30/1993 | 05/28/1993 | ML09344144 | <strong>Personnel Error Lead to an Inoperable Administration Building Noble Gas Monitor and Required Compensatory Technical Specification Actions were not Taken</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1993, with the reactor at cold shutdown, Radiological and Environmental Services personnel determined that the administration building noble gas monitor (R-46) had been inoperable since March 17, 1993. Because this condition had remained undetected, the compensatory action required by Indian Point 3 Radiological and Environmental Technical Specifications (RETS), Section 2.2.B and Table 2.2-1 (Action 8), had not been performed. The cause for the inoperable monitor was an out of position three way valve. The cause for the condition remaining undetected was personnel error that resulted in an inadequate procedure. The surveillance test procedure will be revised to include the sample flow test as part of the operability criteria and the calibration port lines will be capped such that inadvertent operation of this valve will not result in inoperability of the monitor. Compensatory sampling was initiated upon discovery of the inoperability. The valve was properly positioned and R-46 was retested satisfactorily and returned to service on May 4, 1993.
2861993018 | Indian Point 3 | 05/05/1993 | 06/04/1993 | ML09344144 | <strong>Missing Hemyc Blanket (Radiant Shield) As A Result of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 30,1993, at approximately 1030 hours, with the plant at cold shutdown, an NRC inspector noted an unsecured hemyc blanket (radiant energy shield). Maintenance personnel determined that the blanket was one of three blankets installed on penetration H-19. Further investigation revealed that penetration H-19 was missing all three of its required hemyc blankets. Hemyc blankets are necessary in these areas to meet 10 CFR 50 Appendix R requirements. The Authority determined that the blankets were probably missing while the plant was operating above cold shutdown. Therefore, the plant had operated in a condition outside its design basis. The cause of this event is personnel error; failure to follow procedures. The missing blankets will be replaced and an inspection will be performed to detect any other missing blankets. Maintenance and operations personnel will be counselled on the importance of following procedures and controlling the plant's configuration.
2861993019 | Indian Point 3 | 05/10/1993 | 10/06/1993 | ML09344158 | <strong>Missed Preventive Maintenance on 31, 32 and 33 Emergency Diesel Generators, Due To Personnel Error, Resulted in a Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1993, with the plant in the cold shutdown condition, maintenance personnel determined that the preventive maintenance (PM) on 33 Emergency Diesel Generator (EDG) had not been performed in accordance with the vendor recommended frequency. The recommended 12 year maintenance inspection had not been performed for all three EDGs when it was due on December 12, 1987. This is a violation of Technical Specification 4.6.A.4. The cause of the event is personnel error in judgement that resulted in misinterpretation of GE-ALCO (vendor) instructions for standby engine maintenance. Corrective actions include training of maintenance engineering and management personnel, a complete review of the vendor recommended maintenance/surveillance/testing matrix and concurrence by the vendor that this matrix is acceptable for maintaining the ALCO Diesels for standby service. The PMs on all three EDGs will be current and in compliance with the vendor recommendations prior to start-up from the present Performance Improvement Program Outage. The 12 year PM is complete for the three EDGs (33 EDG was declared operable on August 24, 1993 after its 12 year PM was completed).
2861993020 | Indian Point 3 | 05/20/1993 | 06/17/1993 | ML09344145 | <strong>Missed Preventive Maintenance On Emergency Diesel Generator Air Start System Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1993, with the plant in the cold shutdown condition, an NRC inspector noted that Indian Point 3 had not performed the vendor recommended preventive maintenance (PM) on the twelve (12) Crosby model JMBU safety relief valves used on the three emergency diesel generator (EDG) air start systems. These valves were overdue for their vendor recommended 12-year PM inspection. Technical Specification 4.6.A.4, states, "Each diesel generator shall be inspected and maintained following the manufacturer's recommendations for this class of stand-by service." The cause of this event was personnel error - inattention to detail. The Authority has counseled and will train appropriate maintenance personnel. The Authority will replace the relief valves and ensure that all the required maintenance, surveillance and testing for the EDGs are correct and complete.
2861993021 | Indian Point 3 | 06/03/1993 | 07/01/1993 | ML09344145 | <strong>Missed Reactor Coolant System Tritium Analysis Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1993, with the reactor in cold shutdown and the reactor coolant inventory at approximately 67 feet, a Senior Nuclear Chemistry Technician (SNCT) failed to sample the residual heat removal system for tritium activity weekly as required by Technical Specifications section 4.1.B and Table 4.1-2. The Chemistry Supervisors, who perform verification of sample collection and data review, failed to identify the missed sample and take appropriate corrective actions within the maximum time of ten days allowed between analyses. The cause of this event was cognitive personnel error. Contributing factors were inadequate communications and inadequate supervisory methods. The Authority has apprised the individuals involved in the event of their responsibilities and has improved supervisory oversight of tritium sample collection.
2861993022 | Indian Point 3 | 05/11/1993 | 07/06/1993 | ML09344146 | <strong>Electrical Tunnel Fire Protection Sprinkler Zone 15 Inoperable Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 5 1993, with the plant in the cold shutdown condition, Instrumentation and control (I&C) technicians determined that electrical tunnel fire protection sprinkler zone 15 had been made inoperable during the performance of a surveillance test performed on May 11, 1993. This condition remained unknown to plant personnel despite the presence of a trouble alarm on the subject zone. As a result, no compensatory action was taken as required by Technical Specification section 3.14.B.2.a. The cause of this event was personnel error. Corrective actions included apprising test personnel of the need to question system operability when systems do not respond as expected, and revising surveillance test 3PT-A13 to include new operability criteria. The electrical tunnel fire protection sprinkler zone 15 was declared operable on June 11, 1993. This Licensee Event Report (LER) also satisfies the requirement in Technical Specification section 3.14.B.2.b to provide a Special Report to the Commission when a fire protection sprinkler system has been inoperable for greater than 14 days.
2861993023 | Indian Point 3 | 06/11/1993 | 07/09/1993 | ML09344146 | <strong>Inadequate Surveillance Test, Due To Personnel Error, Caused The Inoperability Of The Control Room Toxic Gas Monitor</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1993, with the plant in the cold shutdown condition, Instrumentation and Control personnel determined that the surveillance test for the Control Room Toxic Gas Monitor, 3PT-M55, revision 8, "Toxic Gas Monitoring System Check", did not fulfill the requirements of Technical Specification section 4.5.A.5.e. As a result, those channels which monitor chlorine and ammonia in the control room atmosphere had not been functionally tested at least once every 31 days since April 17, 1989. The cause of this event is personnel error in that 3PT-M55 was improperly revised to delete requirements of the Technical Specifications. Corrective actions included revising surveillance test 3PT-M55 and committing to review a sample of procedures to determine if similar deficiencies exist. On June 11, 1993, ammonia and chlorine channels were tested satisfactorily; thereby, demonstrating the operability of the Central Control Room Toxic Gas Monitoring system.
2861993024 | Indian Point 3 | 06/09/1993 | 07/09/1993 | ML09344146 | <strong>Number 32 Emergency Diesel Generator Inoperable Due to Personnel Error Which Resulted in Exceeding The Preventive Maintenance Schedule For The Engine Governor</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1993, with the plant in the cold shutdown condition, maintenance personnel determined that the No. 32 Emergency Diesel Generator (EDG) governor had not undergone its 12 year Preventive Maintenance (PM) required by the vendor. This is a violation of Technical specification section 4.6.A.4. This condition existed from the end of the cycle 8/9 refueling outage (completed in August 1992) until June 10, 1993. The cause of this event was personnel error (cognitive error) that resulted in the installation of a governor which had not been refurbished. Maintenance engineers were counseled on the implications of the event and its relationship to regulatory requirements. Prior to startup, maintenance engineers and managers will be trained on 10 CFR 50.59 and 10 CFR 50.92 requirements. On June 10, 1993 the EDG was declared operable after installation and testing of a reconditioned governor.
2861993025 | Indian Point 3 | 06/15/1993 | 07/15/1993 | ML09344146 | <strong>Violation of the Cable Channelization Criteria in the Low Pressure Steam Dump Valve Terminal Boxes by Cross Channeling Cables Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1993, with the plant in cold shutdown, Nuclear Engineering and Design (NED) identified that the plant's cable channelization criteria were not met. The channelization deviations involve non-vital Channel II cables, inside the low pressure steam dump valve terminal boxes VU1 through VU6, which go through the barriers to the Channel I side and then are run in conduit with vital Channel I cables for the limit switches and solenoids associated with the safety related low pressure steam dump valves FCV-1206 through FCV-1211. The cause of these channelization deviations is due to personnel error. The non-vital Channel II cables were not wired in accordance with the design wiring diagram. To place the plant in compliance with the cable channelization criteria NED will provide a minor modification to reroute the non-vital Channel II cables prior to start up.
2861993026 | Indian Point 3 | 06/18/1993 | 07/19/1993 | ML09344147 | <strong>480 VAC System Lack of Coordination due to an Original Plant Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1993 at 1800 hours, with the reactor in the cold shutdown condition, Nuclear Engineering and Design (NED) identified a potential single failure in Boric Acid Heat Trace (BAHT) Panel #33 manual throwover transfer switch that could result in the loss of two safety related power supplies, Motor Control Center (MCC) MCC-36A and MCC-36B. A narrow range of fault current, occurring in the manual throwover switch for BAHT Panel #33, may result in a race to trip between MCC feeder fuses (for BAHT circuits) and upstream MCC supply breakers. The loss of both MCCs is outside the design basis for Indian Point 3 (IP3). The cause is an original plant design deficiency. Immediate action was taken to open the fused disconnect switch in cubicle 6RD at MCC-36B. An Engineering Change Notice (ECN) was generated to achieve coordination through fuse replacement. The replacement will be completed prior to the plant going above the cold shutdown condition.
2861993027 | Indian Point 3 | 06/24/1993 | 07/23/1993 | ML09344147 | <strong>Emergency Diesel Generators 31, 32 and 33 Inoperable due to Personnel Error Which Resulted in the Local Control Panels Being in a Non-Seismically Qualified Configuration</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1993 at approximately 1350 hours with the plant in a cold shutdown condition, the emergency diesel generator (EDG) system engineer determined that the local control panels for the 31, 32, and 33 EDGs did not meet seismic design requirements because they were missing fasteners used to secure the inner hinged panel to the control cabinet. Without these fasteners, the inner hinged panel could swing inside the panel during a seismic event and prevent EDG operation. Indian Point 3 personnel were unable to determine the duration of the event and therefore conservatively assumed a bounding duration of 15 years and 3 months. The cause of this event was personnel error. The Maintenance department replaced the bolts and the shift supervisor declared the 31 and 32 EDGs operable approximately 7 hours after discovery of the event. Department manager? will instruct appropriate plant personnel to report similar deficiencies identified during routine equipment walkdowns or inspections.
2861993028 | Indian Point 3 | 01/02/1992 | 11/12/1993 | ML09344159 | <strong>Fuel Storage Building Emergency Ventilation System In A Condition Prohibited By Technical Specification due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1992 with the plant at 100 percent reactor power, the Quality Assurance Department identified an error in the operability criteria for Surveillance Test 3PT-R032A, "Fuel Storage Building Filtration System" performed August 13, 1990. On August 6, 1993, New York Power Authority determined that the error resulted in a violation, between January 1989 and January 1992, of Technical Specification 4.5.A.6.b (2) which requires a minimum of 90 percent of the accident design flow rate of the Fuel Storage Building Emergency Ventilation System fans. At the time of the discovery, the system was operable and remains operable based on the results of surveillance testing since January 1992. A Temporary Procedure Change (TPC) was issued February 14, 1992 to correct the operability criteria. The cause of this event was personnel error in writing and reviewing the procedure. This event did not cause a significant increase in risk to public health and safety.
2861993029 | Indian Point 3 | 08/19/1993 | 09/16/1993 | ML09344157 | <strong>Technical Specification Violation Caused by Nonfunctional Penetration Fire Seals and Fire Barriers Due to Personnel Error When Specified Penetration Material Was Not Installed per Design Drawings.</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1993, with the plant in cold shutdown, a Nuclear Engineering and Design (NED) Fire Protection Engineer identified that two penetration fire seals and their associated fire barriers were nonfunctional. The nonfunctional fire seals are located in the walls between the 31/32 and 32/33 Emergency Diesel Generator (EDG) cells, respectively. The nonfunctionality of the seals and barriers is due to their physical configuration which does not conform to a qualified 3 hour fire rated assembly. This condition is a violation of Technical Specification section 3.14.C and has existed since the issuance of Amendment 24 to the Indian Point 3 (IP3) Operating License dated March 6, 1979. The cause of this event was personnel error in that a previous analysis of the assemblies in 1992 (for which a Special Report was sent) did not consider all possible fire effects on the assemblies. The ongoing inspection of 100% of the IP3 penetration fire seals will be completed prior to unit startup from the current plant outage to address all penetration fire seal deficiencies. In addition, a modification to the affected EDG penetration fire seals to provide a qualified 3 hour fire rated assembly will be completed prior to unit startup from the current outage.
2861993030 | Indian Point 3 | 08/20/1993 | 10/22/1994 | 9411010365 | <strong>Motor Operated Valves in an Overthurst, Outside Design Basis, Condition Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1993 at 1750 hours with the plant in cold shutdown, engineering determined that a valve overthrust condition exists for two motor operated valves (MOVs). The overthrust condition is outside design basis and existed since initial plant construction. Engineering discovered from the preliminary valve manufacturer's structural analyses that overthrust conditions potentially exists for a total of thirty MOVs. Engineering subsequently verified that of these thirty valves, two valves required replacement, four valves required modification and the others are acceptable as is. This determination was performed according to the Generic Letter 89-10 MOV program. The cause of this event was personnel error at the time these designs were performed. The Authority completed the analyses and implemented the valve modifications as required. This event had no significant effect on the health and safety of the public.
2861993031 | Indian Point 3 | 08/27/1993 | 09/27/1993 | ML09344157 | <strong>Noncompliance With 10 CFR 50.48 and 10 CFR 50, Appendix R Due to the Lack of an Approved Exemption for a Particular Postulated Fire.</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1993, the Authority determined that Indian Point 3 (IP3) was not in compliance with section III.G, of 10 CFR 50, Appendix R. On September 19, 1985, the Authority incorrectly determined the fire barrier wraps installed at the entryway to the electrical tunnels constituted compliance with the regulations and as a result withdrew an exemption request that if approved would have placed IP3 in compliance. The cause of this event is not fully determinable. The available evidence indicates that the reviewers did not perform an adequate review. The reason for this is indeterminate because the key reviewers are no longer available for interviews or do not recollect the events specifically enough. The identified deficiency was reported under 10 CFR 50.72(b)(2)(i) at 1258 hours on August 27, 1993. Corrective actions will include improvements to the process utilized for the development and review of NRC submittals and a re-submittal of the subject exemption request.
2861993032 | Indian Point 3 | 09/01/1993 | 09/30/1993 | ML09344157 | <strong>Number 31 Emergency Diesel Generator Fuel Oil Day Tank Level Indicator Inoperable Without Required Technical Specification Compensatory Actions Taken Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1993, with the plant at cold shutdown, the Emergency Diesel Generator (EDG) system engineer notified the shift supervisor that the Fuel Oil Day Tank (FODT) level indicator (LI-1136) for 31 EDG had been out of tolerance since September 1, 1993, and the technical specification required compensatory action was not implemented until September 4, 1993. The inoperable indicator did not affect the operability of 31 EDG. The cause of the event was personnel error by non-licensed nuclear plant operators in the failure to follow the logkeeping procedure. The Assistant Operations Manager met with the plant operators and shift supervisors involved to reinforce their responsibilities with logkeeping and review of logs. Also, all watch personnel have been instructed to review the Operations Directive controlling logkeeping. On September 4, 1993, the compensatory action to monitor 31 EDG FODT level using an alternate method was taken. LI- 1136 was returned to service September 6, 1993.
2861993033 | Indian Point 3 | 09/03/1993 | 10/04/1993 | ML09344157 | <strong>Failure to Amend Technical Specifications Due to Personnel Error Resulted in Plant's Emergency Diesel Generator Fuel Oil Levels Being Potentially Less Than the Minimum Required</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1993, with the plant in the cold shutdown condition, an engineering evaluation concluded that Technical Specification section 3.7.A.5, was inadequate for ensuring that the design basis minimum usable volume of 5238 gallons in each fuel oil storage tank for the emergency diesel generators (EDG) required by the Final Safety Analysis Report (FSAR) will not be violated. The plant was potentially outside its design basis from December 4, 1992 to December 24, 1992 while it was above the cold shutdown condition operating at 100 percent power. The cause for this event was personnel error by the engineers responsible for preparing and reviewing a modification to the EDG fuel oil storage tank level switches' setpoints. A Technical Specification amendment was not obtained prior to modification implementation. The corrective actions include submitting a request for an amendment to the plant's Technical Specifications, revising the operations logs to reflect the new minimum required fuel volume, briefing the engineering staff on the lessons learned, and revising the nuclear safety evaluation in the modification package which changed the EDG fuel oil storage tank level switches' setpoints.
2861993034 | Indian Point 3 | 09/10/1993 | 10/08/1993 | ML09344158 | <strong>Turbine Trip Low Auto Stop Oil Pressure Channel Not Calibrated As Required By Technical Specifications Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1993, with the plant in the cold shutdown condition, Instrumentation and Control (I&C) department personnel determined that the surveillance test for the turbine trip low auto stop oil pressure channel did not fulfill the channel calibration requirements of the technical specification. As a result, the turbine trip low auto stop oil pressure alarm and trip functions were not tested as required. The cause of the event was personnel error - inattention to detail when the surveillance test was initially written in August 1987. corrective actions include revising and performing this procedure prior to start-up, counseling personnel writing and revising I&C procedures, and ensuring surveillance tests are current and demonstrate operability prior to startup.
2861993035 | Indian Point 3 | 09/16/1993 | 10/15/1993 | ML09344158 | <strong>Weld Channel and Containment Penetration Pressurization System Outside Design Basis Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1993, with the reactor in cold shutdown, Technical Services identified an existing design flaw that could allow an automatic Safety Injection actuation signal combined with a loss of offsite power to result in the loss of the Weld Channel and Containment Penetration Pressurization System. The signal would cause the system's pressure control valves to fail in a closed position which cuts off the air supply. The design flaw is outside the design basis of the plant and has existed since initial plant startup. The cause is human error during system design and design review by the Architect Engineer. Corrective action prior to startup will be a system modification to correct this flaw. Design reviews will be performed to ensure this flaw does not exist in other plant engineered safety systems.
2861993036 | Indian Point 3 | 09/15/1993 | 05/06/1994 | ML10049068 | <strong>Improper Seismic Mounting of Damper Actuators in the Central Control Room Ventilation System Resulted in a Condition Prohibited by Technical Specifications Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1993, at approximately 1630 hours, with the plant in a cold shutdown condition and in response to a Nuclear Regulatory Commission inspector's questions, the Heating, Ventilating and Air Conditioning (HVAC) system engineer concluded that the Central Control Room (CCR) ventilation system damper actuators were not seismically mounted. This event resulted in a condition prohibited by technical specifications which requires the CCR ventilation system to be operable when containment integrity is required. This event was caused by personnel error in that the seismic design requirements of a specification were not translated into the installation. Corrective action includes assuring the seismic qualification of the damper actuators, implementing a modification to appropriately mount actuators, counseling personnel responsible for testing the system and sampling the work performed under the specification to determine if further deficiencies exist. Prior to startup the CCR HVAC system will be restored to operable.
2861993037 | Indian Point 3 | 09/28/1993 | 01/13/1994 | ML10049066 | <strong>Plant Outside Its Design Basis Due to Missing Control Power Fuses for Alternate 10 CFR 50, Appendix R Safe Shutdown Power to #32 Component Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1993, with the plant in cold shutdown condition the alternate 10 CFR 50, Appendix R power supply to 32 Component Cooling Water Pump was determined to be inoperable due to the control power fuses for the breaker. The length of time that the control power fuses were missing was not determined. The cause of the event was personnel error of indeterminant origin. The last operability verification test of the alternate feed was conducted May 18, 1983. This event has resulted in the plant being outside its design basis for an undetermined period of time back to May 18, 1983. Fuses were inserted and the component tested satisfactorily on September 28, 1993. The 10 CFR 50, Appendix R components not currently tested for operability will be verified operable prior to the plant exceeding cold shutdown. 10 CFR 50, Appendix R motor control centers that supply alternate safe shutdown power will have their fuses inspected and evaluated for adequacy prior to the plant exceeding cold shutdown.
2861993038 | Indian Point 3 | 09/30/1993 | 11/20/1993 | ML09344159 | <strong>Missing and Deficient Fire Barriers Place the Plant Outside its Design Basis Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1993, with the plant in cold shutdown, the Authority determined that the plant was not in compliance with 10 CFR 50, Appendix R, section III.G.2, in that fire barrier wrap was not installed or installed barriers were deficient for some specific plant areas. The most probable cause of the event was personnel error in that a modification performed to achieve compliance with 10 CFR 50, Appendix R, section III.G.2 was not expansive enough to envelop the three areas found deficient nor were maintenance or inspection procedures detailed enough to address deficiencies in installed wrap. Additional events were discovered during completion of field inspections. Corrective actions will include; improvements to the process utilized for development and review of 10 CFR 50, Appendix R related modifications, modifications to the deficient fire barriers to comply with 10 CFR 50, Appendix R, evaluation of a modification regarding its effect on Appendix R compliance and completion of detailed maintenance/repair and surveillance procedures for installed fire barrier wrap. Prior to startup, the Authority will achieve compliance with Appendix R section III.G.2 requirements.
2861993039 | Indian Point 3 | 10/01/1993 | 10/30/1993 | ML09344159 | <strong>Personnel Error Associated with Gaseous Radwaste Design Changes Caused a Violation of Environmental Technical Specifications and Prevented Control of Gaseous Radwaste Releases.</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1993 at approximately 1757 hours, with the reactor in cold shutdown at atmospheric pressure, the Operations department notified the NRC of a condition that could have allowed the uncontrolled release of radioactive gases to the environment. The condition resulted from the intentional bypass in 1980 and subsequent removal in 1987 of the Chemical and Volume Control System Gas Stripper-Boric Acid Evaporator packages. These actions allowed Chemical and Volume Control Sy tem Hold Up tanks to be routed to the vented outside Monitor Tanks without gas stripping. The cause of the condition was personnel error, inattention to detail. Corrective action to isolate the hold up tanks was completed at 2025 hours on October 1, 1993. corrective action to control potential releases from these vented outdoor tanks will be complete by November 30, 1993. Corrective action to amend past Semiannual Radiological Effluent Reports will be complete in February 1994.
2861993040 | Indian Point 3 | 10/07/1993 | 11/06/1993 | ML09344159 | <strong>Inadequate Surveillance Test of Control Rod Movement Placed the Plant in a Condition Prohibited by Technical Specifications Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1993, at approximately 1430 hours, with the reactor at cold shutdown, Indian Point 3 reactor engineering personnel discovered that Control Bank D was not moved as required by item 2 of Indian Point Unit 3 (IP3) Technical Specification 4.1.B, Table 4.1-3, from June 1990 to February 1993. The technical specification requirement was added June 5, 1990 but the implementing surveillance test procedure contained a precaution prohibiting testing of the controlling bank of control rods. All control rods moved as required during plant shutdown in February 1993. The cause of the event was personnel error resulting from inattention to detail. Corrective action to revise the procedure has been completed. Corrective action has been scheduled to revise the procedure used for preparation and review of surveillance procedures so that the circumstances of this LER would be considered as well as to certify that tests verify equipment operability.
2861993041 | Indian Point 3 | 10/07/1993 | 11/06/1993 | ML09344159 | <strong>Missed Penetration Fire Barrier Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>In mid August 1993, with the plant at cold shutdown and vented to atmosphere, a fire protection engineer identified six (6) penetration seals in the penetration fire barriers between the diesel generator compartments and one (1) penetration seal between the Diesel Generator Building and the Control Building that had not been inspected since before 1982. These seven penetrations were inspected and found functional as of July 22, 1993. An initial determination was made that inspection was not required by Indian Point 3 Technical specification 4.12.C.1, issued November 18, 1982. It was subsequently determined, on October 7, 1993, that the inspection was required by a more conservative interpretation of the technical specifications. The cause of the event was personnel error of indeterminate origin in the preparation of the surveillance procedure. Corrective actions will include completion of a 100% inspection of penetration fire seals, upgrading surveillance procedures and submittal of a closeout report on the inspection effort.
2861993042 | Indian Point 3 | 10/09/1993 | 11/08/1993 | ML09344159 | <strong>Emergency Diesel Generators Inoperable, Placing the Plant Outside Technical Specification Requirements, Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1993 at 1915 hours, with the plant in cold shutdown, a Senior Reactor Operator (SRO) declared all three Emergency Diesel Generators (EDGs) inoperable. The SRO made this operability determination because EDG ventilation fans in an EDG compartment were tripping on thermal overload. The fans are part of the EDG ventilation system which is required as a support system for the EDGs. The cause of the event was personnel error in that a modification implemented to replace the fan motor overloads failed to include adequate overload testing requirements. investigation results indicate that the plant was outside Technical Specification 3.7.F.4, requiring a minimum of two operable diesels, between September 20, 1993 at 0341 hours until October 8, 1993 at 1040 hours. Corrective actions include revising the modification, communicating lessons learned to engineering departments, establishing a preventive maintenance program for motors, and revising the Modification Control Manual. Prior to plant startup, a modification will be completed to assure that EDG ventilation fan and motor performance are in accordance with design basis.
2861993043 | Indian Point 3 | 10/18/1993 | 04/18/1994 | ML10049068 | <strong>Plant Outside Its Design Basis Due to Deficiencies in the Installation of Orifice Plates in the Weld Channel and Containment Penetration Pressurization System Supply</strong><br /><i>Abstract:&nbsp;</i>On October 18 and 19, 1993, with the reactor in the cold shutdown condition, Maintenance department mechanics inspected two Weld Channel and Containment Penetration Pressurization (WCCPP) system union orifice plates (FE-1128 and FE-1129), as part of the ongoing plant review of orifice plate installations. The as-found condition of these orifice plates, which had existed since initial plant startup, could cause the WCCPP system to exceed the intended leak rate following failure of the personnel hatch and/or the equipment hatch airlock door interlocks or seals. The inspection revealed deficiencies in the as-found condition of these two orifice plates. The safety related orifice inspection identified a deficiency in the as-found condition of a third WCCPP system orifice plate (FE-1124). Corrective actions include replacement of the orifice plates, a reconstitution of the design basis data for WCCPP system orifice plates, completion of the safety related orifice plates inspection task, and procedural requirements for assuring the quality of the plant is maintained in the design, installation, maintenance and training processes.
2861993044 | Indian Point 3 | 10/18/1993 | 11/18/1993 | ML09344159 | <strong>Central Control Building Heating, Ventilating and Air Conditioning System Outside Design Basis Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1993, at approximately 1840 hours with the reactor in cold shutdown at atmospheric pressure, Technical Services concluded that the as-built central control room heat loads exceeded the original design heat loads and issued significant occurrence report 93-644 to identify a reportable deficiency. This event resulted in the central control room air conditioners being outside their design basis. This event was caused by personnel error in the original design and in subsequent plant modifications. Scheduled corrective actions include: addressing safety significant design basis document open items; a modification to increase control room cooling; an evaluation to identify recommended control room heating, ventilating and air conditioning changes; and, modifications to address those recommendations. The current Modification Control Manual and design basis documents provide assurance that this type of error will not occur again.
2861993045 | Indian Point 3 | 10/23/1993 | 01/20/1994 | ML10049066 | <strong>A Failure Mode of The Central Control Room Ventilation System Damper Actuators With The Loss Of Instrument Air Resulted In A Condition Prohibited By Technical Specifications Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1993 at approximately 1000 hours with the plant in a cold shutdown condition, the Heating, Ventilating, and Air Conditioning system engineer initiated an investigation that identified the loss of Instrument Air as a failure mode of the Central Control Room ventilation system damper actuators that would result in loss of system function. Loss of this function is a condition prohibited by technical specifications. This event was caused by personnel error of an indeterminate origin during original design. The current Modification Control Manual provides assurance that this type of error will not occur again. The Authority has scheduled corrective action to address safety significant design basis document open items, add a backup gas supply to operate dampers and revise procedures for guidance on manual corrective action to damper failure.
2861993046 | Indian Point 3 | 11/02/1993 | 12/01/1993 | ML09344160 | <strong>Low Temperature for Criticality Placing the Plant Outside Design Basis Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1993, at approximately 1200 hours, with the reactor in cold shutdown, the Authority made a four hour notification under 10CFR50.72(b) (2) (i) and 10CFR50.72 (b) (2) (iii) (A) based on a review of a Westinghouse Electric Corporation letter stating that 540 degrees F is the minimum temperature (T-Average) for criticality supportable by the current licensing basis safety analyses. The Indian Point 3 (IP3) Technical Specifications do not prohibit critical operation with T- Average below 540 degrees F. The reactor has been brought critical at a temperature below 540 degrees F on several occasions between 1976 and 1987. The cause of the event was personnel error involving misjudgment and the misinterpretation of information. Westinghouse proposed Technical Specifications are apparently inconsistent with safety analyses for indeterminate reasons and the Authority failed to identify this discrepancy during routine audits and reviews of the Westinghouse cycle- specific Reload Safety Analysis Checklists (RSACs). Corrective actions include revising IP3 operating procedures, the Technical Specifications, and the Westinghouse RSAC.
2861993047 | Indian Point 3 | 11/03/1993 | 03/18/1994 | ML10049067 | <strong>Improperly Configured Containment Isolation Valves, Caused By Personnel Error, Place The Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1993, with the plant in cold shutdown and the reactor vented to atmosphere, Project Engineering Services concluded that the containment isolation valve configuration for the Chemical and Volume Control System (CVCS) Reactor Coolant Pump (RCP) seal water injection line was outside the licensing design basis. The condition was assumed to have existed since initial plant operation. The ause was personnel error of an indeterminate nature and inattention to detail. The corrective action will require Project Engineering to route seal water to the valve leak off connections prior to startup. Prior to the next refueling, Project Engineering will remove and replace or reinstall the valves in the correct orientation or file an evaluation that supports continued use of the IVSWS to pressurize the valve packing. The installed configuration of 21 Containment isolation globe valves was examined (13 are still under examination) to determine the extent of condition. Nine outboard and one inboard containment isolation valves were identified in the wrong configuration. The outboard isolation valves will be evaluated to determine acceptability. Corrective action will be taken if they are not. The line containing the inboard isolation valve is unnecessary and will be cut and capped or the valve orientation will be reversed.
2861993048 | Indian Point 3 | 01/02/1993 | 07/30/1994 | ML10049069 | <strong>Plant Outside Its Design Basis Due to Potential Single Failure of Ventilation Systems Causing Rooms With Safety Related Equipment to Exceed Design Temperatures.</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1993, with the plant in the cold shutdown condition, a concern was identified as a result of preliminary calculations and analyses performed in support of the Indian Point 3 Individual Plant Examination (IP3-IPE), that a single failure of the Control Building (CB) 15 foot elevation ventilation system could result in elevated switchgear room temperatures. This condition could cause tripping of multiple circuit breakers as a result of thermal trip of breaker control components. This event was caused by human errors of indeterminate origin during the design process. A four hour report was made to the NRC at 1547 hours on November 2, 1993 when the preliminary calculations were verified. An additional four hour report was made to the NRC at 1120 hours on February 15, 1994 to report that the extent of this condition included the CB 33 foot elevation and the Auxiliary Feedwater Pump room.<br /><br /> Corrective actions include modifications to provide control room alarms of high ambient temperatures, modifications to separate the power supplies to the two exhaust fans, upgrading the fan control components to QA Category I components and completing the IPE level 1 analysis for IP3.
2861993049 | Indian Point 3 | 11/03/1993 | 12/03/1993 | ML09344160 | <strong>Violation of Technical Specifications Due to a Failure to Adequately Test the Valves Connecting the Emergency City Water Supply to the Charging Water Pumps' Coolers</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1993, with plant in the cold shutdown condition, the Authority determined that the periodic surveillance test demonstrating the operability of the emergency city water supply to the Chemical and Volume Control System (CVCS) pumps' coolers inadequately addressed the equipment testing requirements as defined by Technical Specification section 4.1.B. and table 4.1-3, item 12. This is a violation of Technical Specification requirements. The cause of the event was due to personnel errors resulting from inattention to detail. These personnel errors involved the failure to include in the past all the valves connecting the emergency city water supply to the coolers in the test when the test was initially written and during its subsequent revisions. Corrective actions include revising and performing this surveillance test prior to plant startup.
2861993050 | Indian Point 3 | 11/15/1993 | 02/15/1994 | ML10049066 | <strong>The Plant Is Outside Design Basis Because Air Operated Solenoid Valves Can Fail On Overpressure Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>November 15, 1993, at approximately 1924 hours, with the reactor in cold shutdown, operations issued deviation event report 93-734 to identify the potential inoperability of four Service Water System solenoid operated valves affecting emergency diesel generator operation. The condition resulted from solenoid operated valves rated at less than the instrument air pressure supply and a failure mode that could cause unregulated instrument air. Subsequently, 109 additional valves subject to overpressure and one failure of a valve to vent were identified. The condition resulted from an original design deficiency and a subsequent failure to correct the error in response to regulatory feedback. The cause for both the original design deficiency and missing the opportunity to correct it was personnel error. In the first case it was inadequate knowledge while in the second it was an inadequately scoped evaluation of industry experience. Corrective actions to verify the proper setting of air regulators and to prevent recurrence is complete. Corrective actions to assess valve position and to prevent overpressurization of solenoid operated valves will be completed by startup. Corrective actions to address Generic Letter 91-15 and NUREG 1275 will be completed by May 31, 1994.
2861993051 | Indian Point 3 | 11/17/1993 | 01/09/1995 | ML10049070 | <strong>A Seismically Included Failure of A Fire Main, Caused By Personnel Error, Can Place The Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993 at approximately 1845 hours with the plant in cold shutdown condition, Site Engineering identified a 10 inch diameter fire main in the Control Building that did not seem to be supported to seismic I requirements. This was evaluated through inspection and a one hour report was made to the NRC at 1921 hours. A seismically induced break of the fire main could have resulted in flooding of the 480 volt switchgear. This was an unanalyzed condition and did not meet the Indian Point 3 (IP3) Final Safety Analysis Report (FSAR) requirement (i.e., do not allow seismically induced failures in fire protection piping to damage seismic class I components). The cause of this event was human error of indeterminate nature during the original design and installation. Compensating action was taken by isolating the header from outside the control building under administrative control. To determine extent of condition, the fire protection system was walked down in category I areas. Corrective action was taken by adding seismic class I supports to prevent seismically induced rupture of the header in the 480 volt switchgear room. The effect on the public health and safety was not significant.
2861993052 | Indian Point 3 | 11/22/1993 | 12/22/1993 | ML09344160 | <strong>Condensate Storage Tank Instrument Loops Violation of Separation Criteria, Due to Personnel Error, Place The Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1993 at approximately 1100 hours with the plant in a cold shutdown condition, Site Engineering identified redundant condensate storage tank level transmitters that were powered from the same power supply. This condition is outside the plant design basis. The cause of the event is personnel error, a misjudgment due to inadequate verification during a modification. Site Engineering will determine the extent the extent of condition reviewing control room racks with redundant instrumentation. The Authority will take additional corrective action by relocating the power supply for one level transmitter loop prior to startup, adding the power supply channel assignment to plant design drawings for control room racks with redundant instruments and updating the electrical design guide.
2861993053 | Indian Point 3 | 12/02/1993 | 01/03/1994 | ML10049066 | <strong>Technical Specification Violation Caused By Inoperable Diesel Generators 31, 32, And 33 Due To Personnel Error And Procedural Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1993 at approximately 2130 hours with the plant in a cold shutdown condition, Maintenance found flow control valves SWN-FCV-1176 and SWN-FCV-1176A inoperable during a post-work test. Operations declared all three emergency diesel generators inoperable because at least one valve must be operable to allow service water to the generators. Operations made a one hour report at 2331 (one hour late due to personnel error). The condition resulted from incorrect installation of pilot solenoid valves caused by a lack of procedural adherence due to personnel error. Contributing causes were procedural inadequacies, inattention to detail and inadequate skills. At 2135 hours, Operations restored operability (four and one half hours after inoperability). maintenance reinstalled the valves correctly and Technical Services assessed the balance of the valves for correct installation. Corrective action will require Administrative Procedure changes, new process controls (i.e., a 3 day freeze on scheduled work, monitoring of procedural conformance, night orders for Operator guidance), training on correct work practice and meetings to identify management expectations.
2861993055 | Indian Point 3 | 12/27/1993 | 07/21/1994 | ML10049069 | <strong>Inadequate 10 CFR 50, Appendix R Emergency Lighting Due to Design Deficiency Places the Plant Outside Its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1993, with the plant in cold shutdown, a reactor operator identified that there was insufficient emergency lighting to perform safe shutdown functions in two plant areas. Due to this condition, Indian Point 3 is outside its design basis based on the requirements of 10 CFR 50, Appendix R, Section III. J. The operator identified insufficient lighting to illuminate the 6.9 KV switchgear area on the 15 foot elevation of the Turbine Building and the turbine front stand on the 55 foot elevation of the Turbine Building. This event was caused by personnel error during the preparation of the original modification which installed the emergency battery lights. Corrective actions include revising the Modification Control Manual to more clearly specify testing requirements, developing a modification to correct the lighting deficiencies, completing the engineering acceptance test which identified this concern, and completing an area blackout test for manual operator actions required when the shutdown is conducted from the control room. The supplement to the LER is to report an additional deviation identified while performing the engineering acceptance test.
2871993001 | Oconee 3 | 01/26/1993 | 02/25/1993 | 9303050080 | <strong>Reactor Trip On Lost Signal Due To Technician Inattention To Details, Followed By Operator Misalignment Of Automatic Emergency Feedwater Paths</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1993, at 1005 hours, while operating at 100% Full Power, Oconee Unit 3 tripped from a Reactor Protective System anticipatory trip signal. While troubleshooting a problem in Unit 3's Power Factor meter transducer, Instrumentation and Electrical technicians incorrectly tested the voltage input of the transducer with a multimeter in the current measuring mode. This resulted in a partial loss of power to the Generator Output Megawatt meter and a false signal to the Integrated Control System. The Turbine control Valves opened in response to this false signal to recover the apparent lost megawatts. A large decrease in Feedwater Pump discharge pressure caused an Anticipated Transient Without Scram Mitigation System Actuation Circuitry actuation, starting the Emergency Feedwater pumps and tripping the Main Turbine. Main Turbine Anticipatory trip signal tripped the reactor. Post Trip response was normal. During the trip recovery, while transferring from the Emergency Feedwater to the Main Feedwater pumps, a loss of automatic initiation of both emergency feedwater flow paths resulted when both Emergency Feedwater Control Valves were not placed in "AUTO" as directed by procedure. The cause of the unit trip was Inappropriate Action (Improper Action, Lack of Attention to Detail). The cause of the second event was Inappropriate Action (Improperly Followed the Correct Procedure). Corrective actions included replacement of the blown fuses, faulty transducer, and revision of the station drawings and individual counseling to improve personnel performance.
2871993002 | Oconee 3 | 04/05/1993 | 05/05/1993 | 9305140251 | <strong>Reactor Building Emergency Hatch Outer Door Failed Open While the Inner Door Seal Was Inoperable Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1993 at 2115 hours, Oconee Unit 3 was at 100% Full Power. Maintenance personnel were preparing the Unit 3 Reactor Building Emergency Hatch (RBEH) for leak testing. When Maintenance personnel entered the RBEH they noticed the inner door had an air noise coming from around a portion of the sealing area. The inner door seal was-declared inoperable. On April 5, 1993, at 1030 hours,in preparation for inspecting the inner door seal, the outer door was opened but was not re-closed within the time allowed by Technical Specifications, due to an apparent mechanical failure of the operating mechanism. The root cause of this event is equipment malfunction. Corrective actions were to close the outer door, shim the inner door seal, and complete the testing. Planned corrective actions are to revise the preventive maintenance procedure on the RBEH and investigate and repair the mechanism.
2891993001 | Three Mile Island 1 | 01/26/1993 | 02/25/1993 | 9303020357 | <strong>BS-PS-286 (RB 30 PSIG Pressure Switch) Failure And Subsequent Entry Into Technical Specification 3.0.1</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1993 TMI-1 was operating at 100% power. Plant operations personnel were performing Technical Specification Surveillance 1303-4.14 to test the operation of the Reactor Building 30 PSIG analog channels. Pressure switch BS-PS-286 BE/PS! was declared inoperable. Because of failure to meet the redundancy requirement of Technical Specification table 3.5-1, the unit entered Technical Specification section 3.0.1 (equivalent to STS 3.0.3). Actions were taken to complete corrective measures to permit continued operation. A jumper initially installed provided normal control room indication of an actuated channel but did not completely provide an actuated channel. Further evaluation by the plant staff identified the weakness and two additional jumpers were installed to provide the proper degree of redundancy. The faulty switch was inspected, cleaned, exercised and lubricated. The deadband setting of the switch was increased and after reliable operation was confirmed, the switch was returned to service.<br /><br /> The root cause of the entry into Technical Specification 3.0.1 was the failure of BS-PS-286 during performance of the surveillance. The remaining five similar switches will be inspected and the deadbands reset as required. The Technical Specification requirements for events of this nature will also be reviewed and revised as appropriate. <br /><br /> The event is being reported per 10CFR50.73(a)(2)(i)(b).
2891993002 | Three Mile Island 1 | 01/29/1993 | 03/05/1993 | 9303110417 | <strong>Bypass Of Both Decay Heat Service Coolers Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>BYPASS OF BOTH DECAY HEAT SERVICE COOLERS DUE TO PERSONNEL ERROR<br /><br /> TMI-1 was operating at 100% power. On January 29, 1993 during the performance of a weekly procedure, not required by Technical Specifications (TS), the Auxiliary Operator (AO) failed to follow established operator work practices and established a valve lineup which caused river water to bypass both Decay Heat Service Coolers (DC-C-2A/B) simultaneously. When discovered, the proper alignment was immediately restored. The root cause of this event was personnel error.<br /><br /> TS 3.3.1.1.d requires two Decay Heat Removal Coolers (DH-C-1A/B) and their cooling water supplies, including coolers DC-C-2A/B, during plant operation. With both coolers bypassed, TS 3.0.1 was applicable. This condition is reportable under 50.73.a.2.i.B and also under 50.73.a.2.vii. <br /><br /> Bypassing both coolers simultaneously had no immediate safety significance during the event because the equipment was not called upon to be in operation. In the event of a worst case Loss of Coolant Accident, the safety systems would have fulfilled their intended function. <br /><br /> Management has reviewed this event with the affected crew. Procedures will be upgraded. Each Operating crew will review the event.
2891993003 | Three Mile Island 1 | 03/12/1993 | 04/12/1993 | 9304160154 | <strong>Reactor Coolant Pump Power Monitor Malfunction Resulting In Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1993, TMI-1 was operating at 100% power. During performance of surveillance testing for the Heat Sink Protection System (HSPS) an equipment malfunction in the Reactor Coolant Pump Power Monitor (RCPPM) 1 resulted in sending an erroneous Reactor Coolant Pump Trip signal to the Reactor Protection System (RPS). The RPS functioned normally and tripped the reactor due to a mismatch between Reactor Power and the number of running Reactor Coolant Pumps. <br /><br /> The root cause was electrical equipment failure in the Reactor Coolant Pump Power Monitor 1. The failed equipment was repaired and satisfactorily tested. The remaining RCPPM's shall be inspected and repaired as necessary to improve reliability during testing. Also, procedure enhancements to the surveillance procedure will be made to provide additional checks on equipment status before and after each switching sequence.
2891993004 | Three Mile Island 1 | 05/03/1993 | 06/01/1993 | 9306090266 | <strong>Plant Process Computer Malfunction Event</strong><br /><i>Abstract:&nbsp;</i>At approximately 0124 hours, on May 3, 1993 while TMI-1 was operating at 100% power, the Plant Process Computer (PPC) [ID/PCU] failed to initiate the Nuclear Applications Software six minute calculation. The condition continued until approximately 0720. With the Nuclear Applications Software (NAS) out of service, hand calculations for quadrant power tilt and axial power imbalance were required to be performed on two hour intervals. Since the NAS calculation of tilt/imbalance was not identified to be in an invalid condition, manual calculations of tilt/imbalance were not performed in time to satisfy the 0300, 0500 and 0700 requirements and TS sections 3.5.2.4.g and 3.5.2.7.f. were violated. The NAS was returned to service at 0730 and six minute calculations resumed. The plant was maintained at steady state full power operation during the period that the automatic calculation process on the PPC was out of service. interval calculations missed were completed using historical data. <br /><br /> Investigations have not revealed the cause of the malfunction. It is suspected that a hardware problem caused the PPC failure. <br /><br /> The event is being reported per 10CFR50.73(a)(2)(i)(b).
2891993005 | Three Mile Island 1 | 05/10/1993 | 06/09/1993 | 9306170183 | <strong>Missed Surveillance - Reactor Building Annual Inspection Due To Management Oversight</strong><br /><i>Abstract:&nbsp;</i>MISSED SURVEILLANCE - REACTOR BUILDING ANNUAL INSPECTION DUE TO MANAGEMENT OVERSIGHT<br /><br /> TMI-1 was operating at 100% power on May 10, 1993, when it was discovered that Surveillance Procedure (SP) 1301-8.1 "Reactor Building Annual Inspection" had not been performed by the required completion date of April 2, 1993. The root cause of the late surveillance was management oversight due to inadequate tracking of surveillances. The inspection revealed lightning rod damage and minor corrosion an a limited area of the Reactor Building liner plate. These findings are being scheduled for resolution in a timely manner, however neither have the potential to compromise Reactor Building integrity. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). Performance of the inspection May 10-12, 1993 revealed no significant structural degradation to the Reactor Building. There were no safety consequences associated with the late performance of the inspection. GPU Nuclear has developed a mechanism for tracking to ensure the timely completion of surveillances such as SP 1301-8.1. Improvements will be fully implemented by June 30, 1993.
2891993006 | Three Mile Island 1 | 07/01/1993 | 08/02/1993 | 9308090210 | <strong>Lube Oil Leak On EG-Y-1B Due To Inadequate Maintenance</strong><br /><i>Abstract:&nbsp;</i>At approximately 0615 hours, on July 1, 1993, while TMI-1 was operating at 100% power, an accumulation of lubrication oil was discovered in the radiator housing of the 1B Emergency Diesel Generator (EG-Y-1B) EK!. The oil leak was discovered shortly after EG-Y-1B had been shutdown from a run of approximately 20 minutes duration performed to support Engineered Safeguards (ES) system testing. The alternate Emergency Diesel Generator, EG-Y-1A, was started, loaded to 3MW and run for 20 minutes to verify operability and returned to ES standby. EG-Y-1B was removed from service and the lube oil leak repaired. The engine was tested to verify the effectiveness of the repair and returned to service. <br /><br /> Investigation identified that the oil had leaked from the lube oil filter housing FLT! during the 20 minute run of EG-Y-1B. The cause of the oil leak was determined to be maintenance related; the oil filter housing bolts had not been properly torqued. <br /><br /> The event is being reported per 10CFR50.73(a)(2)(i)(B).
2891993007 | Three Mile Island 1 | 10/08/1993 | 11/08/1993 | 9311120183 | <strong>Failure Of Pressure Isolation Valve (DH-V22B) To Seat Tightly During Plant Operation Due To Looseness Of The Hinge Mechanism</strong><br /><i>Abstract:&nbsp;</i>FAILURE OF PRESSURE ISOLATION VALVE (DH-V22B) TO SEAT TIGHTLY DURING PLANT OPERATION DUE TO LOOSENESS OF THE HINGE MECHANISM <br /><br /> TMI-1 was shutdown for the Cycle 10 Refueling Outage (10R) on October 8, 1993 when it was discovered that a condition may have existed during power operation where Pressure Isolation Valve (PIV) DH-V22B in the Decay Heat Removal (DHR) System would exceed the Technical Specification (TS) surveillance leakage limits. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition or operation prohibited by the plant's TS. Repairs to DH-V22B were completed during 10R. The hinge pins were found to have play (freedom of movement) such that the disk did not consistently seat tightly. Following repairs the disk was verified to seat properly and when tested no leakage was observed. There were no safety consequences associated with this event. With the isolation valve (DH-V4B) open, leakage from the Reactor Coolant System (RCS) would be limited by the first check valve in series (CF-V5B). PIV leakage potential will be monitored during quarterly tests where the PIVs are not isolated. An evaluation will be performed if significant leakage is noted.
2891993008 | Three Mile Island 1 | 11/03/1993 | 01/31/1994 | 9402170338 | <strong>Pressurizer Code Safety Valve Setpoints Outside Tolerance During Plant Operation Due To Inadequate Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1993 TMI-1 was at 100% power at the beginning of Operating Cycle 10 when GPU Nuclear received the vendor test report that a Pressurizer Code Safety Valve (PCSV), which had been in operation during Cycle 9, tested at pressures above the maximum valve lift setpoint required by Technical Specifications (TS). Investigations described in NRC Information Notice 91-74 have concluded that the previous vendor test procedure could introduce setpoint errors. Therefore, the setpoint may have been outside the required TS tolerance during the last fuel cycle (November 14, 1991 through September 10, 1993). This event is reportable under 50.73.a.2.i.B, as an operation or condition prohibited by the plant's TS. Reanalysis shows that Reactor Coolant System pressure would not have exceeded the safety limit if the most limiting pressure transient had occurred. The test procedure has been revised. Spare Pressurizer Code Safety Valves (PCSVs), whose actuation setpoints had previously been set using the revised test procedure, were installed prior to the startup for Cycle 10. The "As found" test results for the other PCSV in service during Cycle 9 were below the 2500 psig setpoint.
2891993009 | Three Mile Island 1 | 11/12/1993 | 12/13/1993 | 9312200319 | <strong>Motor Operator Failure Due To Improper Declutch Lever Installation</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1993, technicians were replacing declutch levers on motor operated valves. One technician requested an operability check of the first valve he worked on. The valve was placed into the manual mode and hand wheeled partially open. On the subsequent attempt to electrically stroke the valve, the motor energized but the valve did not open. It was discovered that the tripper fingers within the electric motor operator misaligned with the corresponding cams on the worm shaft also within the electric motor operator. Upon testing of other valves which had the same lever replaced it was discovered this condition existed on several of the other valves. Since the condition of the tripper finger misalignment was present to some degree on the other valves, this condition is reportable under 10 CFR 50.73(a)(2)(v).
2931993001 | Pilgrim | 01/26/1993 | 11/24/1993 | 9312030158 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to No Flow Indication During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1993, at 1004 hours, the High Pressure Coolant Injection (HPCI) System was declared inoperable and a seven day Technical Specification (3.5.C.2) Limiting Condition for Operation was entered. The HPCI System was declared inoperable because no flow was indicated at the HPCI pump flow indicating controller during a scheduled monthly operability surveillance test. All other parameters registered normal during the test. The HPCI System was returned to normal standby service during subsequent investigative and corrective action activities, which identified a blown fuse within the HPCI flow controller. An operability evaluation completed on October 4, 1993, concluded the HPCI System was capable of its intended design function even with the fuse blown. <br /><br /> The cause was a blown power supply fuse located within the flow controller. The cause of the blown fuse could not be determined. <br /><br /> Corrective action taken included replacing the blown fuse. The HPCI System was tested with satisfactory results and declared operable on January 26, 1993, at 1620 hours. While the HPCI System was declared inoperable, the applicable systems were verified operable as required by Technical Specifications. An engineering evaluation of the blown fuse resulted in planned changes in the fuse rating and addition of alarms to the plant information computer. <br /><br /> The event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1025 psig with the RV water temperature at 545 degrees Fahrenheit. This report is submitted voluntarily. The event posed no threat to the public health and safety.
2931993002 | Pilgrim | 02/25/1993 | 03/29/1993 | 9304080159 | <strong>Reactor Core Isolation Cooling System Declared Inoperable During Surveillance Testing Due to Valve Position Indication and Overload Alarm</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1993 at 1040 hours, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable because the RCIC turbine steam supply valve MO-1301-61 did not open fully and a valve overload alarm occurred during a routine surveillance test of the RCIC System. A seven day Technical Specification 3.5.D.2 Limiting Condition for Operation was entered. The direct cause was galling of the valve's stem and bonnet chamber. The galling resulted in binding during the opening of the valve and failure of the valve operator motor. The most probable cause of the galling was minimal clearance between the valve stem and bonnet chamber in combination with thermal expansion. The valve is a three inch clampseal (11G4PJ-105), rising rotating stem, y-pattern type globe valve manufactured by Conval, Incorporated. Corrective action taken included machining the galled portions of the valve stem and bonnet chamber. The valve operator motor was replaced. The RCIC System was subsequently surveillance tested with satisfactory results and declared operable at 1735 hours on February 28, 1993. The High Pressure Coolant Injection System was verified operable during the period the RCIC System was inoperable. This event occurred while at 100 percent reactor power with the Reactor Mode Selector Switch in the RUN position. The Reactor Vessel (RV) pressure was 1026 psig with the RV water temperature at approximately 537 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and this event posed no threat to the public health and safety.
2931993003 | Pilgrim | 03/01/1993 | 04/10/1995 | 9504190132 | <strong>Settings of Reactor Water Cleanup High Flow Switches Found Out of Tolerance During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1993, the two Reactor Water Cleanup (RWCU) System high flow switches were found to have trip settings greater than the Technical Specification limit (calculated at 16.6" of water) during a routine calibration. The trip setting necessary to meet the Technical Specification limit has since been re-calculated at less than or equal to 21.4" of water. Therefore, the as-found trip settings on March 1, 1993, did not result in less than the minimum number of operable instrument channels per trip system specified by Technical Specification Table 3.2.A.<br /><br /> The cause of the as-found trip settings on March 1, 1993, was setpoint drift. The switches were manufactured by I.T.T. Barton model number 288A. The switches were recalibrated with satisfactory results on March 1, 1993. The internal microswitches were later replaced and the linkages adjusted for the two high flow switches to improve repeatability.<br /><br /> The discovery occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1028 psig with the RV water temperature at 538 degrees Fahrenheit. This report is voluntarily submitted. The as-found trip settings posed no threat to the public health and safety.
2931993004 | Pilgrim | 03/13/1993 | 04/12/1993 | 9304190176 | <strong>Automatic Scram Resulting From Load Rejection at 100 Percent ReactorPower</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1993 at 1628 hours, an automatic scram resulting from a load rejection occurred during a severe coastal storm while at 100 percent reactor power. The load rejection included a trip of the Turbine-Generator, transfer of station electrical loads, and brief opening of one Main Steam relief valve. The 120 VAC safeguards Buses 'A' and 'B' de-energized. The Reactor Vessel (RV) pressure-temperature (P-T) limit was exceeded during subsequent cooldown. <br /><br /> The load rejection was caused by 345 KV switchyard insulator flashovers due to wind packed snow deposited during blizzard conditions. Corrective actions taken included an inspection of the switchyard and insulators. The cause of exceeding the P-T limit was a RV pressure increase that occurred after the HPCI System, that was being used for RV pressure control, was removed from service due to high Suppression Pool water level. The P-T condition was evaluated. The evaluation concluded the RV did not exceed the allowable limits of ASME sections III and XI. The cause of the de-energized safeguards buses was trip settings that were too low. The trip settings were subsequently increased. Other corrective or preventive actions were taken or are planned. The unit returned to commercial service at 0459 hours on March 17, 1993. <br /><br /> This event occurred near the end of the fuel cycle during power operation with the reactor mode selector switch in the RUN position. The RV pressure was 1025 psig with RV water temperature at 525 degrees Fahrenheit.
2931993005 | Pilgrim | 03/14/1993 | 04/09/1993 | 9304150056 | <strong>Automatic Closing of the Reactor Water Cleanup System Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1993 at 1051 hours, an automatic actuation occurred in the Reactor Water Cleanup (RWCU) System portion of the Primary Containment Isolation Control System (PCIS). The actuation resulted in the automatic closing of the Primary Containment System (PCS) Group 6/RWCU System isolation valves and a temporary interruption in RWCU System operation. <br /><br /> The cause for the event was a sensed RWCU System momentary high flow condition that occurred when a RWCU System suction valve was throttled. The high flow was sensed by the RWCU System flow sensor's that generated a trip signal to the PCIS/RWCU System logic circuitry. The PCIS logic circuitry was reset and the RWCU System was returned to service. The RWCU procedure will be reviewed to identify any additional changes to preclude recurrence. Changing MO-1201-85 from a gate valve to a globe valve is being evaluated. <br /><br /> This event occurred while cooling down with the reactor mode selector switch in the STARTUP position. All control rods were fully inserted. The Reactor Vessel (RV) pressure was 140 psig and the RV water temperature was approximately 340 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). The event posed no threat to the public health and safety.
2931993006 | Pilgrim | 03/15/1993 | 04/14/1993 | 9304200133 | <strong>Reactor Building-to-Torus Train 'B' Vacuum Relief System Actuation While Shut Down</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1993, at approximately 2200 hours, indications of an actuation of the Reactor Building-to-Torus Train 'B' Vacuum Relief System were discovered while shut down. The discovery occurred as a result of investigating the pressure decay rate of the air system for AO-5040B. Investigation also revealed the in-series check valve X-212B had opened. <br /><br /> The cause was negative differential pressure between the Torus atmosphere and Reactor Building atmosphere. The Torus atmosphere pressure was decreasing as a result of lowering the Torus water level. The Reactor Building atmospheric pressure was affected by the passing of a severe coastal storm. The differential pressure was sensed by the sensor that controls AO-5040B. The sensor was subsequently calibrated with satisfactory as-found results. Corrective action taken included the addition of nitrogen to the Torus atmosphere. <br /><br /> The event occurred while shut down with the reactor mode selector switch in the STARTUP position for front panel checks. The Reactor Vessel (RV) pressure was zero psig with the RV water temperature at 140 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to public health and safety.
2931993007 | Pilgrim | 03/17/1993 | 07/26/1993 | 9308050021 | <strong>Automatic Closing of the RCIC System Turbine Steam Supply Isolation Valves due to High Steam Flow Signal</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1993, at 0024 hours, an automatic Primary Containment Isolation Control System (PCIS) Group 5 actuation occurred while attempting to place the Reactor Core Isolation Cooling (RCIC) System in standby service during the performance of Procedure 2.1.1, "Startup from Shutdown". The actuation resulted in the closing of the RCIC turbine steam supply isolation valves MO-1301-16 and -17. <br /><br /> The isolation resulted from a high steam flow isolation signal while attempting to jog open the RCIC turbine steam supply valve MO-1301-16. After several attempts, valve MO-1301-16 was opened. The opening of the valve resulted in a rapid steam line pressurization and actuation of the steam flow sensors upstream of valve MO-1301-16. The inability to open MO-1301-16 on initial attempts was caused by a missing jumper that bypasses the torque switch in the opening circuit. The missing jumper was installed and MO-1301-16 was satisfactorily tested. <br /><br /> This event occurred during plant startup while at 2 percent reactor power. The reactor mode selector switch was in STARTUP position. The Reactor Vessel (RV) pressure was 130 psig with RV temperature at approximately 360 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73 subpart (a)(2)(iv) and (a)(2)(v)(D). This event posed no threat to public health and safety.
2931993008 | Pilgrim | 04/09/1993 | 05/04/1993 | 9305120031 | <strong>Failure to Perform Functional Test of Control Room High Efficiency Air Filtration System Humidistats in 1990</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1993, it was determined that the Control Room High Efficiency Air Filtration System Relative Humidity Switches (Humidistats) had not been functionally tested once-per-cycle as specified by Technical Specification 4.7.B.2.d. Specifically, the relative humidistats had not been functionally tested during the period July 1, 1988, to January 23, 1992. This period, in excess of 42 months, exceeds the once-per-cycle definition in Technical Specifications. <br /><br /> The cause was utility non-licensed personnel error in the non-performance of the functional test and subsequent review of Procedure 8.E.47.1, conducted on March 10, 1990. An Instrumentation and Control (I&C) supervisor signed-off the Master Surveillance Tracking Program for performance of the functional test when a portion of the test was not performed. Initial action taken included I&C verifying the performance of the functional test on January 23, 1992, with satisfactory as-found results. Corrective Action taken includes training for I&C Supervisor review of completed surveillance procedures. <br /><br /> The discovery occurred during power operation while at 94 percent power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1015 psig with the RV water temperature at 520 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). This event posed no threat to the public health and safety.
2931993009 | Pilgrim | 05/04/1993 | 06/02/1993 | 9306070280 | <strong>Circuit Breaker Did Not Close During Planned Bus Transfer due to Loose Control Circuit Wire</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1993, at 0230 hours, a safety-related 480 VAC load center bus that is part of a safety-related bus transfer scheme became de-energized during a planned bus transfer conducted while shut down. The related motor control centers became de-energized including the motor control center of the valves that are part of the Residual Heat Removal (RHR) System/Low Pressure Coolant Injection (LPCI) function. At the time of the event, the RHR/LPCI function was not required to be operable. The bus was re-energized at 0235 hours.<br /><br /> The cause of the bus and related components becoming de-energized was circuit breaker 52-102, that is part of the transfer scheme, not closing during the transfer. The cause of breaker 52-102 not closing was a loose wire-to-lug connection in the automatic transfer portion of the circuitry that controls the breaker. Corrective action taken included replacement of the lug. The bus transfer function was subsequently tested with satisfactory results. <br /><br /> The event occurred while shut down in a refueling outage. The Reactor Vessel (RV) head was not installed. The reactor mode selector switch was in the REFUEL position. There was no movement of a fuel assembly or fuel cask at the time of the event. This report is submitted in accordance with 10 CFR 50.73(a)(2)(vii)(D). This event posed no threat to the public health and safety.
2931993010 | Pilgrim | 05/19/1993 | 06/18/1993 | 9306280072 | <strong>Start Up Transformer Became De-energized During Testing While Shut Down</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1993, at 1328 hours, the Start Up Transformer (SUT) became de-energized during a planned calibration of turbine/generator relays, lockout test and associated annunciator verification while the plant was shutdown. The Start Up Transformer lockout relay was actuated instead of the Main Transformer lockout relay. The de-energization of the SUT resulted in designed responses including automatic actuations of the Reactor Protection System, Primary and Secondary Containment Isolation Control Systems and Emergency Diesel Generators. The Start Up Transformer was re-energized by 1421 hours. <br /><br /> The root cause of the event was utility non-licensed Electric Lab Engineer error. The engineer mistakenly actuated the wrong relay while implementing the test procedure. Corrective action taken included an immediate discussion with electrical maintenance personnel on attention to detail and self-checking. Preventive action planned includes review of the procedure for improvement to preclude recurrence. <br /><br /> The event occurred while shut down in a refueling outage. The Reactor Vessel (RV) head was installed. The reactor mode selector switch was in the SHUTDOWN position. There was no movement of a fuel assembly or fuel cask at the time of the event. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
2931993011 | Pilgrim | 05/25/1993 | 06/23/1993 | 9306290309 | <strong>Setpoint of Target Rock Relief Valves Found Out of Tolerance During Testing</strong><br /><i>Abstract:&nbsp;</i>On May 25,1993, it was determined that the initial as-found popping pressures of the pilot valves for three Target Rock two-stage main steam relief valves were not within Technical Specification limits including tolerance. The valves had been sent to Westinghouse for periodic testing during Refuel Outage (RFO) No. 9. The set pressure for the pilot valves is 1115 psig plus or minus 11 psi. The initial popping pressures of the pilot valves S/N 1040, 1025 and 1207 were 1131, 1144 and 1156 psig, respectively. <br /><br /> The cause of the out-of-tolerance popping pressures is believed to be setpoint drift. The three pilot valves were disassembled, inspected, reworked and reassembled by Target Rock Corporation personnel. None of the valves exhibited any abnormal conditions during inspection. The pilot valves satisfactorily passed subsequent certification testing. The relief valves were manufactured by Target Rock Corporation (Model No. 7567F). <br /><br /> The testing was conducted during a refueling outage with the reactor mode selector switch in the REFUEL position. The reactor power level was zero percent. This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B). The initial popping pressure posed no threat to the public health and safety.
2931993012 | Pilgrim | 05/29/1993 | 06/25/1993 | 9307010266 | <strong>Group 1 Isolation During Startup While Opening Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1993 at 0614 hours, an unplanned Primary Containment Isolation Control System (PCIS) Group 1 isolation signal occurred while opening a Main Steam Isolation Valve (MSIV) during startup. The signal resulted in the automatic closing of the related valves. The isolation signal was caused by a high Reactor Vessel (RV) water level (+48 inches). The high water level occurred while opening an MSIV that caused a swell (expansion) of RV water. The root cause of the event was licensed operator error. While attempting to equalize steam line pressures, a misunderstood communication occurred between an operator and the Nuclear Watch Engineer regarding the RV water level and RV pressure. This caused the NWE to leave the 'C' inboard main steam isolation valve open longer than planned, resulting in a relatively greater decrease in RV pressure and a corresponding rise in RV water level to the point (+48 inches) where the high water level isolation occurred. Contributing to the event was the fact that the MSIVs were opened with RV water level starting slightly higher than that directed by the applicable procedure and several manual isolation valves downstream of the MSIVs, thought to be closed, were open resulting in increased steam flow through the MSIV when opening the valve. The importance of procedural adherence and clear communication was stressed by the Chief Operating Engineer to the applicable Watch Engineer. Procedure 2.2.92 will be revised to ensure that applicable valves are checked in the event outboard steam pressure does not build up. This event occurred during a startup with the reactor mode selector switch in the STARTUP position. The control rods were in a partially withdrawn position. The RV water temperature was 350 degrees Fahrenheit and the RV pressure was 140 psig. The reactor power level was approximately one percent. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the health and safety of the public.
2931993013 | Pilgrim | 05/30/1993 | 06/25/1993 | 9307010271 | <strong>Reactor Core Isolation Cooling System Declared Inoperable Due to Turbine Speed Oscillations During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1993, at 1820 hours, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable and a seven day Technical Specification (3.5.D.2) Limiting Condition for Operation (LCO) was entered. The RCIC System was declared inoperable during a scheduled surveillance test. The RCIC System was returned to normal standby service during subsequent investigative and corrective action activities.<br /><br /> The RCIC turbine was declared inoperable due to speed oscillations that occurred after several minutes of steady operation. The cause of the oscillations is believed to be a mechanical failure of the speed control system hydraulic actuator (EG-R). The actuator was manufactured by Woodward Governor Company, part number A9903-026. The actuator was removed from service and a replacement EG-R was installed and calibrated. <br /><br /> The RCIC System was inoperable when an unplanned reactor scram occurred on May 31, 1993, at 1921 hours. The RCIC System was tested with satisfactory results, after restart from the scram, and declared operable on June 4, 1993, at 0618 hours. While the RCIC System was inoperable, the High Pressure Coolant Injection System was verified to be operable as required by Technical Specifications. <br /><br /> The event occurred during power ascension. The reactor mode selector switch was in the RUN position. The reactor power level was approximately 19 per ent. The Reactor Vessel (RV) pressure was 939 psig and the RV temperature was approximately 538 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D). This event posed no threat to the public health and safety.
2931993014 | Pilgrim | 05/31/1993 | 06/30/1993 | 9307090093 | <strong>Automatic Scram Resulting From Operation of Auxiliary Transformer Differential Relay During Power Ascension</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1993, at 1921 hours, an automatic scram occurred while at 24 percent reactor power. The event included a trip of the Turbine-Generator and transfer of the Auxiliary Power Distribution System. The scram was the result of the closing of the Turbine Stop Valves while the Turbine first stage pressure was greater than the scram bypass pressure. The Turbine Stop Valves were closing as a result of the Turbine trip. The Turbine-Generator trip was initiated by the operation of a Unit Auxiliary Transformer differential relay. <br /><br /> The operation of the relay was investigated for cause. The investigation included relay calibration, differential circuit wiring checks, Unit Auxiliary Transformer insulation resistance testing and oil sample analysis, cable insulation resistance testing, breaker testing, and performance of a test approximating the conditions existing at the time of the event. The investigation could not determine the cause for the operation of the relay. The unit returned to commercial service on June 3, 1993.<br /><br /> This event occurred during power ascension from a refueling outage with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was 940 psig with RV water temperature at 540 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
2931993015 | Pilgrim | 06/30/1993 | 07/28/1993 | 9308100126 | <strong>High Pressure Coolant Injection System Made Inoperable Due to Indicated Flow During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1993, at 0001 hours, the High Pressure Coolant Injection (HPCI) System was declared inoperable and a seven day Technical Specification 3.5.C.2 Limiting Condition for Operation (LCO) was entered. The system was declared inoperable because the pump flowrate of 4000 gpm was less than 4250 gpm during the monthly surveillance test. The system was later made inoperable for purposes of investigation. <br /><br /> The cause of the low flowrate was some foreign material that plugged a portion of the restricting orifice located in the system's full flow test pipeline. The sourc of the foreign material was most probably the Condensate Storage Tanks (CSTs). Corrective action taken consisted of the removal, cleaning, and re-installation of the restricting orifice. After the restricting orifice was cleaned and re-installed, the system was tested with satisfactory results and the LCO was terminated at 2001 hours on July 1, 1993. During the period the system was declared and made inoperable, the systems specified by Technical Specification 3.5.D.2 were verified operable. Additional corrective action being planned includes visual inspection of at least one of the CSTs for foreign material. <br /><br /> The event occurred while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1021 psig with the RV water temperature at 533 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D). The event posed no threat to the public health and safety.
2931993016 | Pilgrim | 07/19/1993 | 08/18/1993 | 9308250322 | <strong>High Pressure Coolant Injection System Pump Low Discharge Pressure Alarm Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1993, the High Pressure Coolant Injection (HPCI) System was declared inoperable because the system's pump discharge low pressure alarm was discovered to be inoperable during a monthly surveillance test of the pressure switch alarm circuit. The HPCI System was maintained in the normal standby mode. Subsequent assessment concluded the system was capable of providing its design function while the alarm circuit was inoperable. <br /><br /> The root cause of the inoperable alarm circuit was the depiction and description including a note on a Panalarm Company drawing incorporated into a modification that involved the alarm circuit. The modification inadvertently but effectively eliminated the field common connection that is part of the HPCI pump discharge low pressure alarm circuit. Corrective action taken was to re-establish the field common connection and satisfactory completion of the surveillance test on July 20, 1993. Additional action taken included a functional re-check with satisfactory results of other alarm circuits previously modified. Action being taken to preclude recurrence includes daily testing of alarm panels that are being modified. <br /><br /> The condition was discovered while at 100 percent reactor power. The reactor mode selector switch in the RUN position. The Reactor Vessel (RV) was pressure was 1020 psig with the RV water temperature at 533 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). The condition posed no threat to the public health and safety.
2931993017 | Pilgrim | 07/21/1993 | 08/13/1993 | 9308200068 | <strong>High Pressure Coolant Injection System Inoperable due to Unplanned Isolation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1993, at 1028 hours, the High Pressure Coolant Injection (HPCI) System was declared inoperable and a seven day Technical Specification (3.5.C.2) Limiting Condition for Operation (LCO) was entered. The HPCI System was declared inoperable because the HPCI turbine steam supply valves closed during a scheduled logic system functional surveillance test of the HPCI vacuum breaker isolation valves. The HPCI System was returned to normal standby service during subsequent investigative and corrective action activities. <br /><br /> The cause was utility non-licensed personnel error in not identifying the surveillance test procedure needed to be revised in accordance with changes implemented by a modification during Refueling Outage #9. Initial corrective action included securing testing and returning the HPCI System to normal standby service. The HPCI System was declared operable on July 21, 1993, at 1038 hours. Corrective action taken included performing a review to ensure all HPCI logic test procedures are in accordance with the modification. Corrective action planned includes revising the surveillance procedure. <br /><br /> The event occurred while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was 1023 psig with the RV water temperature at 545 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and (a)(2)(v)(D). This event posed no threat to the public health and safety.
2931993018 | Pilgrim | 07/22/1993 | 10/07/1993 | 9310140179 | <strong>Completion of a Shutdown Due to Reactor Coolant Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1993, at 1741 hours, a Technical Specification required shutdown was completed. A planned shutdown was initiated on July 21, 1993, at 2400 hours because of unidentified leakage of 3 gpm. Near the end of the planned shutdown on July 22, 1993, a Drywell inspection revealed the leakage to be reactor coolant pressure boundary leakage. The discovery occurred at approximately 0930 hours. Technical Specification 3.6.C.1.d specifies a shutdown if any reactor coolant pressure boundary is detected. <br /><br /> The leak was located at a weld on the Reactor Vessel drain line. The most probable cause of the weld leak was a lack of full penetration and/or fusion in a portion of the weld root pass during the weld process in 1980. The lack of full penetration and/or fusion was most likely due to the presence of water and the failure to achieve the full throat thickness in the portion of the weld that eventually leaked. A factor contributing to the cause was some physical constraints in the area where the weld is located. Stresses resulting from operational parameters and external stresses or loading aggravated this condition. Corrective action taken included a weld repair, liquid penetrant examination and hydrostatic testing. The unit returned to commercial service on July 26, 1993. <br /><br /> The discovery occurred with the reactor mode selector switch in the STARTUP position, and with the reactor power level at approximately zero percent. The RV pressure was 900 psig with the RV water temperature at 532 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73 subparts (a)(2)(i)(A) and (a)(2)(ii). The event posed no threat to the public health and safety.
2931993019 | Pilgrim | 07/22/1993 | 08/23/1993 | 9308300158 | <strong>Automatic Closing of the Primary Containment System Group 3 Isolation Valves While Shutting Down</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1993 at 1708 hours, an automatic actuation of the Residual Heat Removal (RHR) System portion of the Primary Containment Isolation Control System (PCIS) occurred while shutting down. The actuation occurred when the RHR system was being started for the shutdown cooling (SDC) mode of operation. The actuation resulted in the automatic closing of the Primary Containment System Group 3/SDC suction piping isolation valves. <br /><br /> The cause of the event was determined to be a momentary pressure transient that actuated the protective high pressure switches. The transient occurred just after the RHR pump was started and the injection valve was jogged open to initiate flow. Because the transient occurred so quickly, the high pressure alarm was not received in the Control Room. The PCIS circuitry was reset and the RHR System was satisfactorily put into service in the SDC mode of operation at approximately 1710 hours. Immediate corrective action included performing a calibration and functional test of the pressure switches with satisfactory results. Other corrective action being considered includes using a pressure switch or relay with a slower response time or possibly installing a time delay. Technical personnel are still investigating the impact of venting RHR pump suction piping. <br /><br /> This event occurred while in hot standby with the reactor mode selector switch in the STARTUP position. The reactor power level was zero percent. The Reactor Vessel (RV) pressure was nine psig, and the RV water temperature was 228 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
2931993020 | Pilgrim | 07/26/1993 | 08/23/1993 | 9308300151 | <strong>Anticipated Transient Without Scram Division 1 Pressure Transmitters Found Valved Out of Service</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1993, plant personnel found two Anticipated Transient Without Scram (ATWS) Division 1 pressure transmitters valved out of service. The transmitters were out of service for 3 hours and 18 minutes with the reactor mode selector switch in the RUN position. Technical Specification 4.2.G require these instruments to be functionally tested prior to startup. As a result of the instruments being isolated, the instrument functional test performed prior to startup was invalid. <br /><br /> Lack of procedural clarity caused this event. Plant technicians had closed the valves to the pressure transmitters during the performance of instrument backfilling Procedure 3.M.2-12.4. The backfilling procedure was unclear as to which of two isolation valves in series I&C personnel were to close for instrument isolation. As a result, the valves closest to the instrument rack remained closed. As corrective action, personnel revised Procedure 3.M.2-12.4 to clarify which valves to use for isolation. <br /><br /> Plant personnel found the pressure transmitters isolated during power operations with reactor mode selector switch in the RUN position. The reactor power level was approximately 15 percent. Reactor pressure was approximately 920 psig with reactor water temperature at approximately 537 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). This condition posed no threat to the health and safety of the public.
2931993021 | Pilgrim | 08/24/1993 | 09/22/1993 | 9309290173 | <strong>Automatic Closing of Isolation Valves During Reactor Core Isolation Cooling System Pressure Control Operations</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1993, at 1329 hours, an automatic Primary Containment Isolation Control System (PCIS) Group 5 actuation occurred while operators were using the Reactor Core Isolation Cooling (RCIC) System for reactor vessel pressure control in accordance with procedure. The actuation resulted in the closing of the RCIC turbine steam supply isolation valves and inoperability of the RCIC System. <br /><br /> The isolation resulted from a high steam flow isolation signal following a reduction in RCIC test return flow by throttling Condensate Storage Tank (CST) return valve MO-1301-53. An increase in turbine steam flow and turbine speed resulted as the RCIC control system attempted to maintain CST return flow. This steam flow increase eventually caused one high flow sensor to trip and initiate the event. The RCIC System was returned to an operable status on August 24, 1993 at 2032 hours. The High Pressure Coolant Injection System was operable during the period the RCIC System was inoperable. Engineering personnel are reviewing the high steam flow setpoint and the procedure for RCIC pressure control operations at low reactor pressure for possible improvement. <br /><br /> This event occurred during Standby conditions with reactor power less than one percent with the Main Steam Isolation Valves closed. The reactor mode selector switch was in STARTUP. Reactor vessel pressure was approximately 487 psig with reactor water temperature at approximately 467 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73 parts (a)(2)(iv) and (a)(2)(v)(D). This event posed no threat to public health and safety.
2931993022 | Pilgrim | 09/10/1993 | 10/12/1993 | 9310190157 | <strong>Loss of Preferred Offsite Power and Automatic Scram Resulting From Load Rejection at 100 Percent Power</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1993, at 1134 hours, a simultaneous loss of preferred offsite power and an automatic scram resulting from a load rejection occurred during a fast moving electrical storm while at 100 percent reactor power. The loss of preferred offsite power included an automatic start of Emergency Diesel Generator (EDG) 'B'. EDG 'A', in service for surveillance testing and loaded on its safety related bus, remained in service. The load rejection included a trip of the Turbine-Generator and opening of three Main Steam relief valves. <br /><br /> The loss of preferred offsite power and load rejection was caused by separate lightning strikes that caused the opening of switchyard breakers. One of the 345 KV switchyard air type circuit breakers (ACB 105) was struck by lightning. Corrective actions taken included a walkdown of the switchyard. Except for the replacement of an ACB 105 pressure reducing valve solenoid and surge suppression circuit, no corrective action was necessary as a result of the walkdown. The unit returned to commercial service at 0718 hours on September 12, 1993. <br /><br /> This event occurred during power operation with the reactor mode selector switch in the RUN position. The RV pressure was 1035 psig with RV water temperature at 550 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
2931993023 | Pilgrim | 09/14/1993 | 10/13/1993 | 9310220104 | <strong>Ten Percent Scram Insertion Time for One Control Rod Array</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1993, it was determined that immediate or timely action was not taken or initiated for one two-by-two control rod array that exceeded the average 10% scram insertion time acceptance criteria as a result of a surveillance test performed on November 25, 1992. A surveillance test is required by a Technical Specification that specifies testing and evaluation every 120 days of operation. <br /><br /> The cause of not taking immediate or timely action was the lack of guidance in the surveillance procedure in that the procedure did not identify or specify any action(s) to be initiated if an average 10% scram insertion time exceeded the acceptance criteria. The procedure provided guidance if the 90% scram insertion time exceeded the acceptance criteria. Corrective action planned includes revision of the procedure to provide additional guidance and action to be initiated if a scram insertion time exceeds the acceptance criteria. The cause of the subject two-by-two array exceeding the acceptance criteria was the performance of single control rod testing with an elevated scram pilot valve air header (SPVAH) air pressure. Preventive maintenance activities previously performed resulted in reduced air leakage and consequent increase in SPVAH air pressure. Corrective action planned includes a change in the setting of a pressure switch that controls Instrument Air System air pressure.<br /><br /> The condition was discovered during power operation and as a result of a surveillance test performed on November 25, 1992. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was approximately 1024 psig with the RV water temperature at 547 degrees F. The condition posed no threat to the public health and safety.
2931993024 | Pilgrim | 09/30/1993 | 10/29/1993 | 9311080260 | <strong>High Pressure Coolant Injection System Inoperable due to Inoperable Motor Operated Valve</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1993, at approximately 1400 hours, Operations personnel made the High Pressure Coolant Injection (HPCI) System inoperable based on the inoperability of DC - powered motor operated valve (MOV) MO-2301-5, the HPCI Steam Line Outboard Isolation Valve. Earlier on September 30, 1993, engineering personnel determined the valve had insufficient thrust to ensure it could close against a HPCI steam line break. <br /><br /> Engineering personnel discovered the problem with the valve thrust when Limitorque Corporation provided information to clarify published industry guidance. Based upon that published guidance the existing thrust calculations had used running efficiency versus pullout efficiency for MOVs with a safety function to close. Limitorque told engineering personnel via telephone on September 29, 1993, that running efficiency should not be used for DC-powered MOVs. Maintenance personnel subsequently modified the MO-2301-5 operator gearing in accordance with an approved modification to provide the required thrust. Diagnostic tests on the valve were satisfactory and the HPCI System was declared operable on October 4, 1993, at 0204 hours. Engineering personnel have evaluated the impact of this condition on DC-powered MOVs which were previously analyzed using the running efficiency. There were no other inoperable valves. <br /><br /> This condition was discovered with reactor power at 100 percent and the reactor mode selector switch was in RUN. Reactor pressure was approximately 1030 psig with reactor water temperature at approximately 550 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(v)(D). This event posed no threat to the public health and safety.
2931993025 | Pilgrim | 10/24/1993 | 11/22/1993 | 9312020505 | <strong>Reactor Core Isolation System Made Inoperable due to Minimum Flow Valve Position During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1993 at 0148 hours, the Reactor Core Isolation Cooling (RCIC) System was made inoperable and a seven day Technical Specification Limiting Condition for Operation (LCO) was entered. The system was made inoperable during surveillance testing when the RCIC minimum flow valve would not fully close and the turbine's control valve appeared to be binding internally. A loose wire on the minimum flow valve's circuit breaker needed to be retightened and a degraded relay within the breaker had to be replaced. The remote servo associated with the control valve was also replaced.<br /><br /> At 2355 hours during post work testing prior to declaring RCIC operable, an unplanned actuation of the RCIC portion of the Primary Containment Isolation Control System occurred due to a high flow condition. As a result, turbine steam supply isolation valves closed and the RCIC turbine tripped as designed. Post work testing was being performed to vent the hydraulic control system after replacing the control valve's remote servo. During the venting process, the isolation occurred. A procedure is being developed to post work test the turbine's hydraulic control system to preclude recurrence. The RCIC system was declared operable and the LCO cleared on October 25, 1993 at 0007 hours. The High Pressure Coolant Injection System was operable during the period that RCIC was inoperable.<br /><br /> The events occurred while at 100 percent reactor power with the Reactor Mode Selector Switch in the RUN position. The Reactor Vessel (RV) pressure was 1025 psig with the RV water temperature at 548 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and (a)(2)(v)(D). The events posed no threat to the public health and safety.
2931993026 | Pilgrim | 11/08/1993 | 12/06/1993 | 9312140134 | <strong>Low Reactor Vessel Water Level While Shutdown Resulting in Automatic Scram Signal and Containment System Isolations</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1993, at 1203 hours, a low reactor vessel level trip signal occurred at the reference level, plus 12 inches, while shut down.<br /><br /> The trip signal resulted in designed automatic responses that included a full scram signal, actuation of appropriate Primary Containment System isolation valves, and actuation of the Secondary Containment System ventilation dampers and the Standby Gas Treatment System. Operations personnel restored reactor vessel water level to normal and returned affected systems to normal service at 1230 hours on November 8, 1993. The cause of the low level trip signal was licensed operator error in failing to note the feedwater system water level instruments being utilized indicated increasing water level while safety-related instruments indicated decreasing water level. Corrective action included briefing all Operations crews on the incident and removal of the non-condensable gases by backfilling the non-safety related feedwater system reference lines. The startup procedure will be revised to require non-safety related feedwater system reference line backfilling prior to plant startup. <br /><br /> This event occurred during hot shutdown conditions with the reactor mode selector switch in the REFUEL position for pre-startup testing. Reactor vessel water temperature was approximately 253 degrees Fahrenheit and reactor vessel pressure was approximately 10 psig. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
2931993027 | Pilgrim | 11/06/1993 | 12/28/1993 | 9401040140 | <strong>Source Range Monitors Downscale Trip Setting Not Conservative to Meet Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1993, it was discovered the action statement of Technical Specification Table 3.2.C-1 (Rod Block) was not taken on at least two occasions because the downscale trip settings of more than one of the Source Range Monitors (SRMs) were not set conservatively relative to the setpoints specified by Technical Specifications. The discovery occurred as a result of utility licensed operator questioning the downscale trip settings recorded during a functional test of the SRMs for the rod block function on November 6-7, 1993. Conservative trip settings were established and another functional test was completed with satisfactory results on November 8, 1993. <br /><br /> The cause of not following the action statement was a change to the SRM functional test procedure in 1991. The procedure change incorrectly increased the SRM trip setting band. The cause of the procedure being incorrectly revised was utility non-licensed personnel error. The procedure will be revised to preclude recurrence by ensuring the trip settings are compatible with Technical Specifications. The SRM calibration procedure has been reviewed and is satisfactory. Similar procedures for the Intermediate Range Monitors and Power Range Monitors have been reviewed and are satisfactory. <br /><br /> The condition was discovered during 100 percent reactor power operation with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was approximately 1030 psig with the RV water temperature at 550 degrees Fahrenheit. The condition posed no threat to the public health and safety.
2951993001 | Zion 1 | 01/04/1993 | 02/03/1993 | 9302100008 | <strong>Declaration of a Generating Station Emergency Plan Unusual Event due to the 1A Centrifugal Charging Pump and the 1B Safety Injection Pump Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 01/03/93, Periodic Test (PT) 2I, "Centrifugal Charging Pump Tests", was performed on the 1A centrifugal charging BQ! pump to verify the pump's operability prior to taking the 1B Safety Injection (SI) BQ! pump out of service (OOS) for recirculation check valve replacement. The vibration readings were in the ALERT range which was satisfactory per the acceptance criteria. The 1B SI pump was taken OOS. <br /><br /> On 01/04/93 PT-2I was reperformed on the 1A centrifugal charging pump. Vibration readings caused the pump to be declared inoperable. Per Technical Specification 3.8.2.d, since two Emergency Core Cooling System (ECCS) BQ! pumps were inoperable, Unit 1 was required to be brought to hot shutdown and an Unusual Event was declared. <br /><br /> The cause of the centrifugal charging pump being declared inoperable was component failure. Analysis by System Materials Analysis Department (SMAD) has determined that the 2-pole IRD magnet that was used with the vibration meter to take the readings for the centrifugal charging pump has a natural frequency that resonates with the predominant vibrating frequency of the gear box. This caused the vibration reading to be higher than the actual vibration. <br /><br /> The safety significance of this event was minimal. Extensive analysis was performed and concluded that the gearbox was in fact below the ALERT range and always operable. Corrective Actions include only using a form fitted magnet on the centrifugal charging pump gearboxes, and determining that the 2 pole IRD magnet has not caused an increase in vibration readings on any other ECCS pump.
2951993002 | Zion 1 | 01/14/1993 | 02/11/1993 | 9302180132 | <strong>Missed Surveillance on the Steam Generator and Pressurizer Pressure Channel Checks</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993, at approximately 1100 hours, Unit 1 was in Mode 1 at 99 percent power. The Control Room Nuclear Station Operator (NSO) completed the Unit 1 control room rounds for 1100 hours. At 1900 hours on November 14, 1993, a NSO trainee was performing the scheduled Unit 1 control room rounds and discovered that various readings for Steam Generator and Pressurizer pressure channel checks which are recorded in Periodic Test (PT)-0, Appendix L-1, "Reactor Protection System Channel Check and ESS Instrumentation Channel Check" were not completed the previous day at 1900 hours. The Unit 1 Supervisor was notified and the rounds were completed at approximately 1910 hours, on January 14, 1993. <br /><br /> The cause of this event was personnel error. Both the NSO and the Unit Supervisor failed to self-check while performing and reviewing the control room rounds. <br /><br /> Corrective actions include counseling the NSO and the Unit Supervisor, and reviewing this event during current events training. This event has minimum safety significance.
2951993003 | Zion 1, Zion 2 | 01/21/1993 | 02/22/1993 | 9302250330 | <strong>Unconservative Low Temperature Overpressure Protection Setpoint</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1993 senior station management was informed of a potential violation of the design basis and it was determined that ENS notification was required per 10CFR50.72.B.2.i. On January 28, 1993, a letter requesting a Temporary Waiver of Compliance was submitted to the NRC requesting permission to set the low temperature overpressure protection (LTOP) system below the currently specified 435 psig at 402 and 407 psig. The different setpoints are due to the different locations of the pressure sensor instrument taps on the hot leg piping. Zion Station determined these more conservative LTOP setpoints, using correction factors appropriate for the number of pumps in operation and the RCS pressure sensor instrument tap location, to ensure compliance with the fracture toughness requirements specified by 10 CFR Part 50, Appendix G, in the event of an analyzed low temperature overpressure event. The Temporary Waiver of Compliance was granted on January 29, 1993.<br /><br /> The cause of this event is design. This event had minimal safety significance. <br /><br /> Corrective Actions include adjusting the setpoints per the Temporary Waiver, performing calculations to determine more precise setpoints and operational limitations, submitting a Technical Specification amendment, and changing appropriate operating procedures.
2951993004 | Zion 1, Zion 2 | 03/19/1993 | 04/19/1993 | 9304220057 | <strong>Two Engineered Safety Features Actuation due to the failure of two safeguards test relays</strong><br /><i>Abstract:&nbsp;</i>At 0817 on March 19, 1993, while performing Periodic Test (PT)-10-1, "Safeguards Actuation IVSW Stroke Timing", on Unit 1 Train A, Phase A isolation valves 1FCV-1W15 and 1FCV-1W17 opened unexpectedly. PT-10-1 was exited, 1FCV-1W15 and 1FCV-1W17 were returned to the closed position and the Safeguards System Engineer (SSE) was notified of the event. The SSE determined that the inadvertent actuation was due to test relay TRS10A failing to remain latched after being actuated. A work request was initiated to replace relay TRS10A. <br /><br /> At 1400 on March 22, 1993, while performing PT-10-4, "Safeguards Actuation Miscellaneous", on Unit 1 Train B, the following Phase A isolation valves closed unexpectedly: 1FCV-SS02, 1FCV-SS03, 1FCV-SS04, 1FCV-SS05, 1AOV-8149B, 1AOV-8153 and 1MOV-8100. PT-10-4 was exited, the valves were returned to their normal lineup, and the SSE was notified of the event. The SSE determined that the inadvertent actuation's were due to test relay TR1AS2 failing to remain latched after being actuated. A work request was initiated to replace relay TRIAS2. Test relays TRS10A and TRIAS2 were replaced, the affected sections of PT-10-1 and PT-10-4 were reperformed, and proper operation of relays TRS10A and TRIAS2 was verified. <br /><br /> This event caused by a component failure. The test relays failed because of a latch pin that had worked itself loose. <br /><br /> Corrective actions included inspecting all of the Unit 1 and Unit 2 latching HFA relays installed in the Safeguards System and identifying 23 out of 198 relays with loose latch pins, initiating work requests to repair the 23 relays, inspecting all HFA latching relays on a basis to be determined to identify and repair any relays whose latch may have worked itself loose during the operating cycle, and evaluating this event for Part 21 applicability.
2951993005 | Zion 1 | 05/28/1993 | 06/28/1993 | 9307060152 | <strong>Violation of Technical Specification Table 3.14-1 due to a Radiation Monitor being Out of Service without the Ventilation System being in the Proper Position.</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1993, at 0330, the Technical Support Center (TSC) SPING radiation monitor IL! was taken out of service because it high alarmed due to the presence of naturally occurring radon. Technical Specification Table 3.14-1 requires the TSC ventilation system to be placed into the recirculation mode within two hours of the failure. This action was performed by placing the control switches in the automatic position and the radiation monitor in the recirculation mode within the time allotted. <br /><br /> On May 28, 1993, at 0215, an equipment attendant was performing the required daily administrative verification when he found the TSC ventilation system returned to the normal position with all control switches in the automatic position. The cause of the TSC ventilation system being in the normal position could not be det rmined. When the control switches are in the automatic position, it is possible for the TSC SPING to switch from the recirculation mode to the normal mode if the seal-in relay for the Emergency Makeup Air Treatment System (EMATS) is reset. It could not be verified how this occurred. <br /><br /> There was minimal safety significance to this event. <br /><br /> Corrective actions include returning the TSC ventilation system to the required accident position, submitting a procedure change to Zion Radiation Procedure (ZRP) 1720-1 for the proper configuration of the TSC process radiation monitor, and reviewing ZRP 1720-1 to ensure that all radiation monitors are adequately addressed.
2951993006 | Zion 1, Zion 2 | 06/07/1993 | 07/07/1993 | 9307150014 | <strong>Train B Emergency Makeup Air Treatment System Fan Local Disconnect Switch Was Found In The Off Position.</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1993 at 1130 during a Generating Station Emergency Plan (GSEP) training class in the Technical Support Center (TSC). the TSC alarm went off. The alarm indicated a problem with either the TSC SPING radiation monitor or the TSC ventilation system. Initial investigation by the Emergency Preparedness instructor found that the Train B Emergency Makeup Air Treatment System (EMATS) fan local disconnect switch was in the off position and that both the OA and the OB EMATS fans were off, Equipment Operators verified that the system was functioning properly, but it could not be determined how the switch was turned off. <br /><br /> The cause of the Train B EMATS fan local disconnect switch being turned off could not be determined. Due to the design and location of the switch, it is believed that the switch was inadvertently repositioned. However, this could not be verified, This event had minimal safety significance. <br /><br /> Corrective Actions include turning on the Train A EMATS fan and verifying damper position, using the lock on the room where the switch is located and controlling the key, changing ZRP 1720-1, Attachment 7b, "Out of Service Surveillance Log Sheet" ORI-PR32 to clearly indicate how to properly align and verify the TSC EMATS, and determining how to reduce plant access through the TSC.
2951993007 | Zion 1, Zion 2 | 07/07/1993 | 08/03/1993 | 9308090225 | <strong>Unit 1 Reactor Trip due to a shorted Terminal on a Loop Isolation Valve Limit Switch</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1993 at 0851 during the performance of Periodic Test (PT)-5, "Reactor Protection Logic Testing". on train A, the Reactor Protection test panel pushbutton was depressed, inadvertently causing the 1B Reactor Coolant Pump (RCP) AB! breaker to trip open and Unit 1 Reactor to trip.<br /><br /> The cause of the Unit 1 Reactor Trip was component failure. Troubleshooting identified that the stem mounted limit switch for Loop Stop Isolation Valve (LSIV) 1MOV-RC8001D had a shorted lug on the limit switch contact. The safety significance of this event was minimal. <br /><br /> Corrective actions include repairing the shorted lug, verifying the state of each LSIV relay for both units, and successfully reperforming PT-5. 93007.ler1
2951993008 | Zion 1, Zion 2 | 08/30/1993 | 09/29/1993 | 9310050232 | <strong>Entry into Specification 3.0.3 due to 1MOV-SI8804A being Out Of Service for greater than seven days.</strong><br /><i>Abstract:&nbsp;</i>On 8/23/93 1MOV-SI8804A, the Residual Heat Removal (RHR) BP! System to Charging CB! Pumps Suction Isolation Valve, was taken Out of Service (OOS) for motor control center breaker inspection. When the breaker inspection was completed on 1MOV-SI8804A, the work package was not immediately cleared by the Electrical Maintenance Department. On 8/25/93, the OOS was inadvertently logged out of the Outage Editor as complete. On 8/30/93 it was discovered that 1MOV-SI8804A was still OOS, and that it had exceeded the seven day Administrative Limiting Condition of Operation (LCO). <br /><br /> The cause of this event was management deficiency. The process for tracking work on LCO related equipment was not sufficient. The safety significance to this event was minimal. <br /><br /> Corrective Actions include changing Periodic Test (PT)-14, "Inoperable Equipment Surveillance", to require a second verification of the OOS being cleared, developing a means for verifying and tracking status of all LCO work, and reviewing and clarifying expectations on the performance of control board walkdown.
2951993009 | Zion 1, Zion 2 | 10/18/1993 | 11/17/1993 | 9312010338 | <strong>Failure to Perform Off-Site Review of a 10CFR50.59 Safety Evaluation</strong><br /><i>Abstract:&nbsp;</i>On 10/18/93 it was determined that a 10CFR50.59 safety evaluation performed on 8/24/92 to keep the auxiliary building north door open during continued operation was not transmitted to the corporate off- site review group for an independent review. <br /><br /> This is a violation of Zion Station Technical Specification 6.1.7.A.1.a. This event was caused by a management deficiency. Proper administrative controls did not exist to ensure that all 10CFR50.59 safety evaluations were properly reviewed by the Off-Site Review Group. <br /><br /> This event has no safety significance. The requirement to submit safety evaluations for off-site review is only an administrative requirement to the Technical Specifications. <br /><br /> Corrective Actions include submitting the safety evaluation to off-site review, assigning one individual to transmit all safety evaluations to off-site review, and documenting in the safety evaluation log the date documents are transmitted to off-site review.
2951993010 | Zion 1, Zion 2 | 11/10/1993 | 07/25/1994 | 9407290165 | <strong>Autostart of the 1A Residual Heat Removal Pump</strong><br /><i>Abstract:&nbsp;</i>On 11/10/93 Technical Staff Surveillance (TSS) 15.6.148, "Response Time Testing of Reactor Protection and Engineered Safety Features Relays for Unit 1 - Train B", was being performed. Safeguards relay SIX3B was verified to function properly and equipment was being returned to its normal position when the 1A Residual Heat Removal (RHR) BP! pump autostarted. <br /><br /> The cause of this event is component failure. A temporary fault in the test equipment setup caused a relay to energize and start the 1A RHR Pump. Since this event did not result in damage to equipment important to safety, personnel injury, or an uncontrolled release, the safety impact of this event was minimal. <br /><br /> Corrective actions include verifying that the Bus 149, train B, Safety Injection (SI) JE! timer functions properly, revising the response time testing procedures to visually verify that the SI timer resets itself, and ensuring better shielding of cables and test equipment when attached to station equipment.
2961993001 | Browns Ferry 3, Browns Ferry 1 | 02/28/1993 | 03/29/1993 | 9304020323 | <strong>Unexpected Auto-Start of Unit 3 Diesel Generators.</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1993, at 1243 hours an unplanned actuation of an Engineered Safeguard Feature occurred when Emergency Diesel Generators (EDG) 3A, 3B, 3C and 3D automatically fast started, accelerated to full speed and rated voltage. The EDGs remained running and, because no undervoltage signal existed, did not tie onto their respective 4kV shutdown boards. <br /><br /> TVA believes the root cause of this event was an inappropriate personnel action. Specifically, the cable that connects the Unit 1 accident signal logic initiating relay to Common Accident Start (CAS) circuits in 4kV Shutdown Board 3EC was partially severed. TVA identified an area on the CAS logic cable where a sharp object struck the cable with enough force to sever one conductor and cutting into another thus, shorting the two conductors and causing the EDGs to start. <br /><br /> TVA will replace the damaged CAS logic cable. Furthermore, TVA will continue to investigate the cause of the inappropriate personnel action and if necessary, will submit a followup report.
2961993002 | Browns Ferry 3 | 12/09/1993 | 01/03/1994 | 9401210057 | <strong>An Emergency Diesel Generator Auto-started as a Result of Degraded Voltage Condition on 4kV Shutdown Caused by a Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1993, at 1840 hours CST, Unit 3 Emergency Diesel Generator (EDG) 3B automatically (auto) fast started and tied onto 4kV Shutdown (SD) Board 3EB following a transfer of 4kV Unit Board 3A from its alternate power supply to its normal supply. The EDG auto-start was the result of a sensed degraded voltage condition on SD Board 3EB. (The degraded voltage signal started EDG 3B and tripped all feeder and load breakers on SD Board 3EB.) This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in automatic actuation of an engineered safety feature. <br /><br /> The cause of the EDG auto-start was an unexpected and unforeseen failure of a primary potential transformer (PT) fuse on the 3EB SD Board bus. This failure was attributed to random PT fuse fatigue. There were no abnormalities identified in the failed fuse contacts or in the PT winding/circuitry that could have attributed to this fuse failure. <br /><br /> TVA examined the remaining three fuses on the 3EB SD Board PT circuits and found no abnormalities. The failed fuse was replaced. As a precautionary measure, the remaining three PT fuses on the affected SD Board 3EB circuit were replaced. No further corrective actions are warranted.
2981993001 | Cooper Station | 02/25/1993 | 03/18/1993 | 9303260087 | <strong>Potential For Insufficient Component Cooling During A Design Basis Accident Due To Design Discrepancies With The Service Water And Reactor Equipment Cooling Systems</strong><br /><i>Abstract:&nbsp;</i>During ongoing efforts associated with the Design Basis Reconstitution Program for Cooper Nuclear Station (CNS), several design discrepancies in the Service Water (SW) and Reactor Equipment Cooling (REC) Systems were identified. These discrepancies affected the ability to achieve the minimum required SW and REC flows to essential equipment requiring cooling during and following a design basis accident (DBA). On February 25, at 12:30 pm, both systems were declared inoperable and the 24 Hour LCO requiring plant shutdown specified in Technical Specifications was entered. At the time of entry into the LCO, the plant was operating at approximately 85 percent power (nearly 700 MWe) on end of cycle coastdown with all rods fully withdrawn. <br /><br /> Review of design and construction documentation revealed that a SW piping configuration error was made during original plant construction, resulting in Division I SW being supplied to the Division II REC Heat Exchanger, and vice-versa. While subsequent evaluations were performed by the Architect/Engineer resulting in system operational changes to compensate for the as-built condition, apparently the analyses were not sufficiently thorough to identify and resolve these concerns.<br /><br /> Compensatory measures taken to restore the SW and REC Systems to an operable status included interim procedure changes providing operator guidance and system valve alignment restrictions. Additionally, operators were briefed regarding the scenarios of concern and the necessary compensatory actions required. These actions were in effect until the plant achieved cold shutdown for the 1993 Refueling Outage which began on March 5. Prior to startup from the outage, pertinent mechanical and electrical modifications will be made to resolve the identified concerns.
2981993002 | Cooper Station | 02/02/1993 | 03/29/1993 | 9304010354 | <strong>Violation of Technical Specifications Due to Lack of Fire Watch Awareness of a Thermo-Lag Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1993, an NRC Inspector, conducting a Fire Protection inspection, interviewed a Security officer assigned as a Fire Watch in the Control Building Basement (El. 882' 6") where Thermo-Lag material is installed. When questioned about assigned duties, the Fire Watch was unaware of one of the Thermo-Lag fire barriers in the area that had been declared inoperable on June 25, 1992, in response to NRC Bulletin 92-01. As a consequence, a Notice of Violation (NOV) was issued indicating that because the Fire Watch was not in a position to monitor the inoperable Thermo-Lag fire barrier, compliance with Technical Specification requirements for a Fire Watch was not achieved. At the time, the plant was operating at approximately 95 percent power, at nearly 760 MWe, on end of cycle coastdown with all rods fully withdrawn. <br /><br /> This event occurred due to a lapse in personnel attention induced by a procedural deficiency. While supplemental information identifying the Thermo-Lag areas of concern was provided for the benefit of Fire Watch personnel, it was not specified or referred to on the Fire Watch Log. Therefore, over time, the Fire Watch who was interviewed did not maintain an awareness of the subject barrier.<br /><br /> Assigned Fire Watch personnel were re-familiarized with the Thermo-Lag areas of concern. Further, specific watch standing instructions, including a diagram of the basement area demarcating the inoperable Thermo-Lag locations, were developed. The Fire Watch procedure will be updated to ensure that Fire Watch requirements for Technical Specification impairments are addressed on the Fire Watch/Fire Watch Patrol Log. During the current refueling outage, modifications will be made that will eliminate the need for this Fire Watch station.
2981993003 | Cooper Station | 03/06/1993 | 04/02/1993 | 9304080130 | <strong>Group Isolations and Loss of Shutdown Cooling Due to Inadvertent 4160 VAC Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1993, at 3:27 am, while attempting to rack out the 4160 VAC circuit breaker for the A Core Spray pump, the feeder breaker to the 480 VAC Critical Bus 1F, located one compartment to the left, was inadvertently tripped. This caused a loss of power to the safety related Division I Motor Control Centers, resulting in a half scram, half Group 1 Isolation, half Group 2 Isolation, Group 3 isolation, Group 6 Isolation, and half Group 7 Isolation. The half Group 2 Isolation resulted in a loss of Shutdown Cooling. Shutdown Cooling was restored in approximately 33 minutes, during which time Reactor Coolant temperature increased from 170 degrees to 190 degrees Fahrenheit. The Group 3 Isolation caused a loss of Reactor Water Cleanup flow, the Group 6 Isolation isolated Secondary Containment and started one Standby Gas Treatment System train, and the half Group 7 Isolation isolated the Reactor Recirculation Sampling System. The cause of this event was personnel error by a non-licensed operator due to inadequate self-checking. <br /><br /> Meetings were held to communicate management expectations for personnel performance. The responsible operator presented a training session on the lessons learned from this event to on shift operations personnel. Procedure changes to provide additional guidance for the breaker rackout process have also been initiated. Self-checking training will be enhanced, and additional labeling and visual identification aids are being evaluated.
2981993004 | Cooper Station | 03/06/1993 | 04/02/1993 | 9304080138 | <strong>Failure to Properly Establish a Fire Seal Penetration Barrier Due to Procedural Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On March 8, at approximately 12:30 am, it was discovered that visual inspection documentation for the installation of temporary seals in two 2-inch Reactor Building exterior wall penetration conduits through which temporary power cables had been installed on March 6, was incomplete. A Fire Watch was established at 1:24 am, and the temporary seals were replaced. In accordance with procedural requirements, visual inspections of seal re-installation were performed and, at 3:07 am, the Fire Watch was secured. At the time, the reactor was in Cold Shutdown for the 1993 Refueling Outage.<br /><br /> The cause of this event is procedural deficiencies. The engineer involved on March 6 understood the procedural requirements for seal installation were applicable only to permanent seals. The maintenance and engineering procedures associated with fire barrier seals did not clearly identify the documentation requirements for temporary seals.<br /><br /> The procedural requirements associated with temporary seal installations were reviewed with the engineer involved to ensure his understanding of fire protection requirements. The procedures will be revised to ensure guidance regarding temporary seal installation is more clearly defined.
2981993005 | Cooper Station | 03/10/1993 | 04/09/1993 | 9304130197 | <strong>Excessive Primary Containment Leakage Discovered During Local Leak Rate Testing of Reactor Feedwater Check Valves</strong><br /><i>Abstract:&nbsp;</i>On March 10,1993, upon completion of the Local Leak Rate Test (LLRT) of the Reactor Feedwater check valves, the Primary Containment leak rate was determined to be in excess of 1.0 La, where La is the allowable containment leak rate. The leakage of the Reactor Feedwater check valves was too great to be accurately quantified using the available test equipment. This testing was conducted with the plant in Cold Shutdown. <br /><br /> The Reactor Feedwater check valve leakage was attributable to degraded resilient seat material, body-disc misalignment, and improper clearances of the valve internals. Additionally, draining of the piping system is restricted by the available vents and drains, potentially affecting the as-found seating of the valves. Modification and repair efforts include line-boring the valve body and disc, installing new hinge pins and bushings with tighter clearances, replacing the seating materials, and adding additional vents and drains to the system. The valve manufacturer is assisting in the evaluation, modification, and repair of the valves. These efforts were based on a review of past valve performance and investigation of the performance of similar valves at other plants. <br /><br /> LLRTs will be completed with satisfactory results prior to startup from the 1993 Refueling Outage.
2981993006 | Cooper Station | 03/16/1993 | 04/15/1993 | 9304200127 | <strong>Fire Barrier Doors Discovered Open and Obstructed Without a Continuous Fire Watch Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, at 11:00 pm, two Fire Barrier doors that provide passage from a stairwell into two safety-related pump rooms located below grade in the Southwest corner of the Reactor Building were found open and obstructed with no Fire Watch assigned. On April 10, 1993, at approximately 8:20 pm, a Fire Barrier door to the Service Water (SW) Pump Room in the Intake Structure was found open and obstructed without a Fire Watch. At the time of these events, the plant was in Cold Shutdown for the 1993 Refueling Outage.<br /><br /> The root cause for these Technical Specification violations is personnel error. Health Physics (HP) personnel blocked open one of the doors in the Reactor Building stairwell with a temporary ventilation duct. They were focused on the radiological concerns of the job in progress and failed to notice the red dot marking on the door signifying that the door was to remain in the closed position or a Fire Watch was to be stationed. <br /><br /> The other two events were the result of lapses in attention to Fire Barrier door requirements by the involved personnel. <br /><br /> Upon finding the two Reactor Building doors open and obstructed, the obstructions were removed and the doors were closed. The situation was reviewed at the outage coordination meetings and compliance with station fire protection requirements was stressed. Additionally, a roving Fire Door Patrol was initiated as a means of assuring that Fire Barrier doors were closed or that a Fire Watch was stationed. Upon discovering the SW Pump Room door open and obstructed, the obstructions were removed and the door was closed. Personnel directly involved were counseled. In order to prevent recurrence of the problems experienced, a review of the Fire Watch implementation process will be conducted, and appropriate enhancements will be made.
2981993007 | Cooper Station | 03/26/1993 | 04/22/1993 | 9305110005 | <strong>ECCS Pump Compartment Cooler Power Supply Design Deficiency Could Have Prevented Adequate Containment Heat Removal</strong><br /><i>Abstract:&nbsp;</i>Efforts associated with the Design Basis Reconstitution Program for Cooper Nuclear Station (CNS) have identified a design discrepancy in the compartment cooling for the Residual Heat Removal (RHR) pumps. This discrepancy could potentially affect the ability to maintain sufficient Low Pressure Coolant Injection flow in the event of a LOCA in the Core Spray (CS) System. In the event of a CS line break and a loss of offsite power concurrent with the failure of one division of 4160 VAC emergency power, two RHR pumps would be available to mitigate the consequences of the LOCA. The loss of 4160 VAC emergency power would result in the loss of compartment cooling for one of the RHR pumps, potentially resulting in premature failure. Thus, only one RHR pump would remain operable to mitigate the consequences of the CS line break, a condition which is not within the current licensing basis. On March 26, at 12:10 pm, this condition was determined to be reportable. With the plant in cold shutdown, a CS line break is not a credible accident and, therefore, Technical Specification Limiting Conditions for Operation were not applicable. <br /><br /> This condition is the result of design errors which occurred during the implementation of the Low Pressure Coolant Injection loop select modification in 1976. Prior to startup from the refueling outage, modifications will be made to resolve the identified concerns.
2981993008 | Cooper Station | 03/28/1993 | 04/22/1993 | 9305110007 | <strong>Loss of 4160 VAC 1G Bus During Design Change Installation Due To Inadvertent Trip Circuit Actuation</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1993, at 3:46 pm, during installation of an overvoltage relay on 4160 VAC breaker 1GS control cubicle door, 4160 VAC breakers 1BG, 1GB and 1GE were tripped due to actuation of the 1GS breaker lockout relay. The relay was inadvertently tripped when one of the three phase overcurrent (51) protective relays located on the 1GS control cubicle door actuated. The trip of the 1GB breaker resulted in the 4160 VAC 1G Bus being de-energized for approximately 10 minutes and a corresponding 1/2 Group 1 Isolation, 1/2 scram, and Groups 2, 3, 6, and 7 Isolations. Additionally, Spent Fuel Pool cooling was interrupted for an approximate five minute time frame. At the time of the event, the plant was in Cold Shutdown for the 1993 Refueling Outage.<br /><br /> The cause of the event was due to an oversight in the Design Change (DC) installation instructions. When the instructions were written, operation of the 51 relays caused by cabinet vibration or jarring during overvoltage relay installation was judged to not be a problem as 51 relay operation requires disc rotation of approximately 90 degrees to achieve contact closure. Considering relay disc rotation to not be of concern, installation instructions did not specify deenergizing the relay logic circuit until electrical installation of the overvoltage relay was to begin. <br /><br /> The step de-energizing the lockout circuit was moved ahead of the steps addressing overvoltage relay installation. The relay installations were completed in both divisions without further incident. This event will be reviewed with design engineers to emphasize the need for conservative decision making.
2981993009 | Cooper Station | 03/29/1993 | 04/28/1993 | 9305040257 | <strong>Potential Inoperability Of Solenoid Operated Valves Due To Overpressurization Discovered During Design Review</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1993, the potential for Solenoid Operated Valves (SOVs) installed in safety-related applications to be overpressurized and thereby unable to perform their safety function was identified during an evaluation being performed for Generic Letter (GL) 91-15 (NUREG 1275, Volume 6, "Operating Experience Feedback Report - Solenoid Operated Valve Problems"). The following systems and components are affected: Reactor Building emergency exhaust damper, the Standby Gas Treatment (SGT) system fan inlet vortex damper control, reactor coolant sample line primary containment isolation valves, and the solenoid pilot valves for the inboard Main Steam Isolation Valves (MSIVs). At the time of discovery, the plant was shutdown for the 1993 Refueling Outage, with the Reactor defueled and secondary containment relaxed. <br /><br /> The cause of this condition was the failure to anticipate that pressure regulators could fail open resulting in overpressurization of the solenoid valves, impacting equipment operability. A previous review of SOVs, conducted in response to Information Notice 88-24, did not investigate the use of nitrogen to the SOVs. Additionally, those SOVs identified as EPs (electric to pneumatic components) were thought to be control components rather than SOVs. Replacement of the SOVs affecting SGT and Reactor building ventilation with components qualified for a higher pressure was completed before Secondary Containment was required. Similar modifications will be made for the remaining equipment prior to the systems being required to be operable. The SOV evaluation being performed per GL 91-15 (NUREG 1275) will ensure that all SOVs subject to this failure mode in safety related applications are identified. This evaluation will be completed prior to startup from the Refueling Outage.
2981993010 | Cooper Station | 03/31/1993 | 07/21/1993 | 9307270213 | <strong>Loss Of An RPS Bus Due To A Defective Under Frequency Trip Unit Resulting In Unplanned Actuations of Several ESFs</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1993, at 2:24 am, the "B" Reactor Protection System (RPS) bus was de-energized when the two Electrical Protection Assemblies (EPAs) on the output of the RPS Motor-Generator (MG) set supplying the bus tripped for no apparent reason. Loss of the RPS bus caused a half Group 1 (Main Steam) isolation, a half Group 2 (Primary Containment) isolation, a half Group 7 (Reactor Coolant Sample) isolation, and a half Scram. Due to plant status and maintenance activities in progress, only one Group 1 and, two Group 2 isolation valves actuated. On June 21 at 8:54 am, power to the B RPS bus was again lost, resulting in the above noted ESF trips, a half Group 3 (Reactor Water Cleanup) isolation and a half Group 6 (Secondary Containment) isolation. The isolations resulted in a loss of shutdown cooling and Reactor Water Cleanup (RWCU) Systems and isolation of the Reactor Building, including actuation of the B Standby Gas Treatment (SGT) System. When these trips occurred, the plant was shutdown for the 1993 Refueling Outage.<br /><br /> A thorough investigation of both EPA units and the "B" RPS MG set control cabinet performed immediately following the March 31 trip revealed no discrepancies. The trip was evaluated as being due to a spurious cause. Following the trip of June 21, a faulty under frequency (UF) unit in the "B" RPS MG set control circuit was found. A spurious trip of this UF unit is the most likely cause of the March 31 trip. <br /><br /> Following both events, the "B" RPS bus was re-energized from its alternate source and systems were restored as needed. Following the June 21 trip, immediate action was taken to restore shutdown cooling. No change in reactor coolant temperature was noted. Since the UF units in the RPS MG sets were redundant to the UF protection afforded by the EPAs, the coils in both control circuits were jumpered. Permanent removal of the UF trip and other RPS MG set trips will be evaluated
2981993011 | Cooper Station | 03/08/1993 | 05/12/1993 | 9305180079 | <strong>Secondary Containment Surveillance Methodology Failed To Identify Leakage Path Between Secondary Containment And The Radwaste Building</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1993, at approximately 10:40 pm, with the plant shut down for the 1993 Refueling Outage, the Secondary Containment Leak Test required prior to refueling was initiated. During this test, a maximum differential pressure (d/p) between the Reactor Building and the external environment of -0.22 inches water gauge (wg) was achieved. The Technical Specification required minimum d/p is -0.25 inches wg. Maintenance was performed on various door seals, and searches were conducted for other building leakage. Several minor leaks were found and sealed. Additionally, the Heating, Ventilating and Air Conditioning (HVAC) System d/p for the Radwaste Building was adjusted from -0.1 inches wg to -0.2 inches wg. This adjustment in Radwaste Building d/p affected Reactor Building d/p, indicating an apparent direct communication pathway.<br /><br /> Further investigation into the apparent interaction between the Reactor Building and the Radwaste Building revealed that the Secondary Containment Leak Test surveillance procedure failed to verify that other building HVAC Systems did not interact with the Reactor Building. Further testing identified that the rupture seal drain line from the Drywell refueling bellows seal to the Waste Surge Tank in the Radwaste Building did not contain a loop seal. This effectively connected the Reactor Building atmosphere to the Radwaste Building through an open ten inch line.<br /><br /> Significant corrective actions taken to date have included installation of a loop seal in the bellows seal drain line and implementation of a major upgrade to the Secondary Containment test methodology. A Secondary Containment Corrective Action Plan was developed and will be completed prior to startup.
2981993012 | Cooper Station | 04/14/1993 | 05/14/1993 | 9305190267 | <strong>Violation of Primary Containment Integrity Due To Operation Of A 3/4 Inch Vent Valve During Core Spray Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1993, an engineering evaluation concluded that during plant operation, cycling of a 3/4 inch manual valve, CS-V-55, while surveillance testing the B Core Spray (CS) subsystem, violated Primary Containment integrity. CS-V-55 is the high point vent on the test discharge line that connects to the Suppression Chamber. Primary Containment integrity requires all manually operated valves not required to be open during accident conditions to be closed. At the time when this evaluation was completed, the plant was in Cold Shutdown for the 1993 Refueling Outage. <br /><br /> Venting of the test return line following local leak rate testing (LLRT) was determined to be corrective action for a 1991 nonconformance report which documented pipe support damage attributed to water hammer. In June 1992, this requirement was added to the monthly surveillance test procedure to ensue that the test return line was full prior to pump operation during surveillance testing. Engineering personnel who witness performance of the venting process estimate that the valve is open for approximately two minutes. This requirement is unique to the B CS subsystem due to the configuration of the test return line to the Suppression Chamber. <br /><br /> A procedure change is being made to eliminate test return line venting when Primary Containment integrity is required. Due to the fact that this situation resulted in violating primary containment integrity, the circumstances associated with the procedure change and attendant 50.59 evaluation and safety analysis will be reviewed during industry events training for all technical staff, operations and SORC personnel. Finally, provisions for operation of manual Containment Isolation valves under administrative control will be considered for a future Technical Specification change request
2981993013 | Cooper Station | 04/15/1993 | 05/15/1993 | 9305200111 | <strong>Safety/Relief And Safety Valve Setpoint Variance Not Within Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>While the plant was shut down for the 1993 Refueling Outage, testing of eight Safety/Relief Valves (S/RVs) and two Safety Valves (SVs) was conducted at the Westinghouse Western Service Center, Banning, California. The as-found setpoint for seven S/RVs was not within the Technical Specification limit of +/-11 psi. Additionally, the setpoint for one SV was not within the Technical Specification limit of +/- 13 psi. <br /><br /> Review of the test data indicates the S/RVs generally displayed performance characteristics typical of the industry-wide problems associated with corrosion bonding of the pilot disc. To date, the root cause and corrective action for this industry-wide problem remains unresolved. Also noted were performance characteristics typical of labyrinth seal induced friction. The failure of the safety valve is considered random setpoint drift.<br /><br /> The valves are being inspected, refurbished and satisfactorily retested before their return to the site. Nebraska Public Power District is continuing to monitor the industry-wide efforts sponsored by the BWR Owners Group to resolve the corrosion bonding setpoint drift phenomena. It is anticipated that pilot discs of an improved material selection will be installed in selected valves during the next refueling outage.
2981993014 | Cooper Station | 03/16/1993 | 05/17/1993 | 9305200344 | <strong>Service Water Throttle Valve Erosion Due To Inadequate Valve Design</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, while the plant was shut down for normal refueling, a small through-wall leak developed on the high pressure side of Service Water (SW) throttle valve SW-MOV-MO89A, Residual Heat Removal Heat Exchanger A SW outlet. The SW system was in operation in support of the A loop of shutdown cooling while the vessel was being defueled. The operating SW Booster pump was secured and allowed to "turbine" with the operating SW pump flow. This action provided sufficient flow and reduced pressure in the SW line and valve. The leak in SW-MOV-MO89A was then temporarily plugged. The leak was determined to be the result of localized flow erosion. A subsequent internal inspection of the valve identified several additional areas of localized erosion on the body and trim, although none had approached through-wall conditions. SW-MOV-MO89B, the SW throttle valve for the B RHR loop, was found to have similar erosion, although the condition was much less severe. This condition is being reported as a voluntary LER. <br /><br /> The erosion failure was due to the internal design of the valve and the suspended solids in the SW process fluid. The internal porting design caused localized vortices to be generated while the valve was operating in the throttled condition to support RHR system operation. The formation and erosive effect of the localized vortices was highly dependent on the internal geometry of the valve. The eroded areas in both valves were repaired to the applicable code requirements and the internal geometry of the body was modified to reduce future susceptibility to erosion. Additionally, more frequent ultrasonic testing will be conducted to ensure the corrective actions are effective.
2981993015 | Cooper Station | 04/20/1993 | 05/20/1993 | 9305250256 | <strong>High Pressure Coolant Injection System Design Discrepancy Resulting In A Nonconservative Difference Between Actual And Indicated Flow</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1993, during efforts associated with the Design Basis Reconstitution Program for Cooper Nuclear Station, a design discrepancy in the High Pressure Coolant Injection (HPCI) System was identified. Due to an inconsistency in the specifications for the flow orifice and the flow transmitter in the flow control system, the design flow of 4250 gpm for the HPCI system would not have been automatically attained under transient or accident conditions. <br /><br /> The flow orifice for the HPCI system was specified with a differential pressure range of 0 to 350 inches of water corresponding to a flow range of 0 to 5000 gpm. However, the associated flow transmitter was specified with a differential pressure range of 0 to 300 inches of water corresponding to a flow range of 0 to 5000 gpm. The effect of this difference is that the flow transmitter will indicate a higher HPCI flow than the actual flow sensed by the flow orifice. The HPCI flow controller, which receives input from the flow transmitter, will adjust the HPCI turbine speed to produce a pump flow of 4250 gpm as indicated by the flow transmitter. Due to this inconsistency, it is estimated that the actual HPCI flow rate would be 3934 gpm, rather than the design flow of 4250 gpm. <br /><br /> This design discrepancy was part of the original design of the Cooper Nuclear Station. The Nuclear Steam System supplier has been notified of this concern to further industry knowledge of any additional applications. Modifications will be made prior to startup from the current refueling outage to correct this design discrepancy.
2981993016 | Cooper Station | 04/22/1993 | 05/21/1993 | 9306010012 | <strong>Design Change Installation D ficiency Resulting in Control Room Emergency Bypass System Activation Failure During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1993, during performance of a surveillance test of the Control Room Ventilation (HVAC) System Radiation Monitor, RMV-RM-1, the Control Room HVAC System did not isolate and transfer to the emergency bypass mode of operation upon insertion of the particulate check source. The surveillance test was being performed as post-maintenance testing (PMT) for a maintenance adjustment made to the monitor. An investigation revealed that an On-the-Spot Change (OSC) to a design change associated with the radiation monitor, sparing two cables, had not been properly implemented. At the time when the OSC was implemented, the 1993 Refueling Outage was in progress, the reactor was defueled and the Control Room HVAC System was not required to be operable. <br /><br /> This event was caused by personnel error and inadequate design change instructions. The OSC specifically identified the cables to be spared, however, craft personnel erred during its implementation. Further, no quality control verification was specified in the OSC instructions to ensure the proper cables were lifted. <br /><br /> An OSC was implemented to correct the wiring error. The surveillance procedure was successfully performed to verify restoration of the safety function. The OSC procedure will be updated to require that standard design and installation requirements, such as implementation of quality control, be incorporated in OSCs. The contents of this LER will be incorporated into contractor craft indoctrination and training. Additionally, this event will be reviewed in industry events training for engineering, operations and station management personnel who prepare, review and approve OSCs.
2981993017 | Cooper Station | 04/28/1993 | 05/28/1993 | 9306040288 | <strong>Technical Specification Violation For Missed Fire Watch Patrols</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1993, at 3:08 pm, it was discovered that the hourly fire watch patrol for the Reactor Building as required by the Technical Specifications had not been performed during the period from 2:00 to 3:00 pm. The fire watch patrol was required because fire detection Zones 20 and 21 were inoperable due to the thermal detectors being relocated. The affected areas contain the Residual Heat Removal (RHR) system pumps and fan coil units, and the High Pressure Coolant Injection (HPCI) system pump. The fire watch patrol was being performed by temporary personnel hired for fire protection duties during the refueling outage. On May 20, while investigating this event, it was determined that the fire watch patrol also did not include the HPCI pump room. The detector in this room was also inoperable due to the relocation efforts for the detectors noted above. At the time of these events, the plant was in Cold Shutdown for the 1993 Refueling Outage. <br /><br /> The root causes for these Technical Specification violations are personnel error and an inadequate procedure. The fire watch patrol duties were being rotated between three individuals. The individual responsible for the 2:00 to 3:00 pm watch period believed the fire watch patrol was being performed by another individual. A contributing factor was the lack of a schedule delineating the responsibility for each time period. The Fire Watch/Fire Watch Patrol Log, used to implement fire watch patrols, does not provide for a listing of the specific areas requiring a fire watch patrol. The personnel directly involved were counseled. In order to prevent recurrence of these problems, a review of the fire watch patrol implementation process will be conducted, and appropriate enhancements will be made. These events and procedure enhancements will be discussed in training.
2981993018 | Cooper Station | 04/30/1993 | 05/25/1993 | 9306020351 | <strong>Standby Gas Treatment System Inlet Damper Single Failure Vulnerability Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1993, during efforts associated with the Design Basis Reconstitution Program for Cooper Nuclear Station, a potential single failure vulnerability in the Standby Gas Treatment (SGT) System was identified. The potential single failure vulnerability identified is associated with a single inlet damper in the common supply duct from the Reactor Building exhaust plenum for both trains of the SGT System. A failure of this damper to open could prevent both trains of the SGT System from performing the required safety function of maintaining the Secondary Containment at a negative pressure. This damper is designed to fail open on loss of power or loss of control air. The fail open feature is accomplished using the stored energy of a spring. Failure of this single damper in the closed position would prevent the SGT System from filtering and venting contaminated effluents through the elevated release point, and cause a possible unmonitored ground level release of radioactive material following a design basis loss of coolant or fuel handling accident. <br /><br /> This single failure vulnerability was a part of the original design of the Cooper Nuclear Station. Prior to moving fuel, or moving any load that could have affected the fuel, the inlet damper was sealed open, eliminating the single failure vulnerability. Prior to startup from the refueling outage, an evaluation will be conducted and appropriate action taken to permanently eliminate this single failure vulnerability in the SGT System.
2981993019 | Cooper Station | 05/01/1993 | 06/01/1993 | 9306100322 | <strong>Nonconservative Testing Methodology Discovered During Local Leak Rate Testing</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1993, upon evaluation of local leak rate test results, it was determined that the previously accepted methodology for performing Appendix J Type C tests for a limited number of flexible wedge gate valves could not be relied upon to be either equivalent to or more conservative than testing in the accident direction. Type C testing has previously been performed for several inboard primary containment isolation valves such that pressure was applied in a direction opposite to the accident direction.<br /><br /> The testing methodology was based on a non-conservative interpretation of past information supplied by the valve manufacturer. Information provided by the valve manufacturer indicated that testing in the reverse direction would not be expected to affect test results. Recent test results indicate that reverse direction testing of flexible wedge gate valves may not in all cases provide equivalent or conservative results. Since the testing methodology may not be equivalent or conservative, past test results may not be completely valid.<br /><br /> Testing has been conducted for those valves which have not previously been tested in the accident direction but which can be so tested. Valves which cannot be tested in the accident direction are being evaluated to determine the acceptability of the testing methodology. The manufacturer has recently been able to qualify the testing of several valves in the reverse direction using current analytical methods. Valves for which the testing method cannot be qualified will have modifications to allow appropriate testing, or exemptions from Appendix J testing requirements will be requested.
2981993020 | Cooper Station | 05/07/1993 | 06/05/1993 | 9306110047 | <strong>Hydrogen/Oxygen Monitors Not Subjected To Primary Containment Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1993, while reviewing the design and testing of the Hydrogen/Oxygen Monitoring (H2/O2) system, it was determined that the H2/O2 system had not been leak tested in accordance with the requirements of the Technical Specifications. Technical Specification 4.7.A.2 requires that an Integrated Leak Rate Test (ILRT) be conducted to verify primary containment integrity. Additionally, the monitors had not been subjected to appropriate pressure during post maintenance testing in those instances where maintenance activities breached the pressure boundary of the monitors. <br /><br /> The 1988 design change for installation of the H2/O2 monitors listed the ILRT procedure as an affected document. A records search did not locate any procedure changes which addressed testing requirements for the monitors. The monitors were routinely secured during outages; it was not recognized that this would result in the inlet and outlet solenoid operated isolation valves being closed during performance of the ILRT. Additionally, administrative controls were insufficient to ensure that the necessary post maintenance pressure testing of the monitors would be accomplished. <br /><br /> Testing of the monitors was satisfactorily conducted. Appropriate administrative controls will be established to ensure necessary testing of the monitors is performed for future maintenance and ILRT performances. A review is being conducted to verify that no similar situations exist. Other design changes will be reviewed to ensure that appropriate procedure changes have been made. The design change process has been substantially upgraded since monitor installation, including more stringent controls on the identification and processing of procedure revisions associated with new or replacement equipment.
2981993021 | Cooper Station | 05/12/1993 | 06/11/1993 | 9306170401 | <strong>Secondary Containment Integrity Requirements Not Met Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1993, at approximately 5:30 am, the Shift Supervisor (SS) determined that with Reactor Building Ventilation Exhaust Inboard Isolation Valve HV-AOV-261AV inoperable and open, Technical Specification requirements for Secondary Containment were not met. The redundant valve in the line, HV-MOV-260MV, was in the closed position and de-energized, isolating the penetration. With that penetration isolated, a Secondary Containment capability test had been satisfactorily completed prior to declaring Secondary Containment operable. However, in accordance with Technical Specifications, HV-AOV-261AV should have been closed. Subsequently, the Spent Fuel Storage Pool gates were removed and stored, and three Local Power Range Monitor assemblies were transferred from the Separator/Dryer Storage Cavity to the Spent Fuel Storage Pool. These activities have been conservatively determined to constitute movement of loads which could have potentially damaged irradiated fuel stored in the Spent Fuel Storage Pool, violating paragraph 3.7.C.1.d of the Technical Specifications. At the time, the reactor was defueled. <br /><br /> The cause of this event was personnel error. Technical Specification requirements for Secondary Containment Integrity had not been verified by the preceding SS. <br /><br /> Upon discovery of the condition, HV-AOV-261AV was manually closed. Since its air operator had been removed, it was physically blocked closed. This action established Secondary Containment Integrity as defined in the Technical Specifications. The SS who had declared Secondary Containment to be operable was counselled. A proposed change to the Technical Specifications, clarifying the requirements, will be submitted.
2981993022 | Cooper Station | 05/14/1993 | 06/10/1993 | 9306180212 | <strong>Unplanned Isolation Of 4160 VAC Bus From Emergency Station Service Transformer And Start Of Diesel Generator Number 2</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1993, at approximate 5:40 pm, actions were initiated to load test the new replacement Emergency Station Service Transformer (ESST) previously installed by a design change during the 1993 outage. Bus 1G was powered from the ESST and Buses 1A, 1B and 1F were powered from the Normal Station Service Transformer (NSST). A licensed operator was lowering the secondary voltage on the ESST to a range of 3980 to 4180 volts. Annunciator "Emergency Transformer Low Voltage" was received; however, an actual low voltage condition did not exist. The annunciation indicated that the ESST secondary voltage was too low to allow automatic transfer of emergency Buses 1F or 1G to the ESST. The operator increased the ESST secondary voltage to correct the apparent low voltage condition. After raising the voltage to 4330 volts, the undervoltage annunciator cleared. <br /><br /> The voltage of 4330 volts was above the overvoltage trip setpoint on Bus 1G; however, the ESST overvoltage annunciator originated from Bus 1F and is active only when Bus 1F is fed from the ESST. After a designed time delay of five minutes Bus 1G automatically isolated from the ESST on high voltage, and Diesel Generator No. 2 started and loaded Bus 1G. This resulted in a half Group 1, 2, 6 and 7 isolation, and a full Group 3 isolation, as designed. <br /><br /> This event was caused by human factors and unanticipated design problems. An additional input to the existing annunciator window has been provided to indicate high secondary voltage on the ESST when Bus 1G is powered from the ESST, and the existing annunciator label has been changed to more accurately describe the condition being annunciated. The annunciator and operating procedures have been updated to more clearly explain the operation of the ESST and the annunciation associated with the transformer and buses.
2981993023 | Cooper Station | 05/28/1993 | 06/28/1993 | 9307060275 | <strong>Technical Specification Violation For Insertion Of Fuel Into The Reactor Core Without All Control Rods Fully Inserted</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1993, between 2:41 a.m. and 3:02 a.m., two fuel assemblies were loaded into the Reactor core without all control rods fully inserted, in violation of Technical Specification 3.10.A.2. Four fuel assemblies had been removed and the associated control rod withdrawn to allow repositioning of a fuel support piece. The instructions to accomplish this task were revised when it became necessary to remove two additional assemblies in adjacent cells to allow the removal tool greater access to the fuel support piece. The revision to these instructions added the steps to reload the two fuel assemblies out of sequence with the step to insert the withdrawn control rod. <br /><br /> The procedure for preparation of the fuel movement instructions does not address this Technical Specification requirement. When the fuel movement instructions were revised to remove and reload the two fuel assemblies, the Technical Specification requirement to insert the withdrawn control rod was not recognized. Normal refueling uses the spiral reload technique which does not require all rods to be inserted. The personnel responsible for the preparation and review of the fuel movement instructions have been counselled. Procedural requirements will be enhanced to clarify Technical Specification requirements for fuel movement and control rod positioning. Training will be revised to discuss this event with Licensed Operators and Reactor Engineering personnel during pre-outage refueling operations training.
2981993024 | Cooper Station | 05/27/1993 | 06/28/1993 | 9307020281 | <strong>Failure To Perform A Required Surveillance Test While Shutdown Due to Ineffective Communications</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1993, while reviewing a computer generated printout of surveillance tests that had been scheduled but not yet completed, it was discovered that testing of the four Reactor Vessel Low Water Level RPS Sensors had not been completed when scheduled per the requirements of Table 3.1.1 of the Technical Specifications. The applicable LCO Action statements require, with an inoperable sensor, the affected trip system be placed in the tripped condition or all operable control rods be inserted within four hours. At the time when the test was to have been performed, the vessel was defueled. However, on May 24 at 8:11 am, following fuel reload into the vessel, Control Rod Drive (CRD) stroke testing was commenced. Since surveillance testing of the Reactor Vessel Low Water Level RPS sensors had not been completed, CRD withdrawal violated the previously indicated Technical Specification. <br /><br /> No formal method notifying the I&C Foreman of the deadline for test performance was provided by the Surveillance Coordinator. Based on work priorities in the shop, the I&C Foreman deferred the test, not realizing that its performance was required. <br /><br /> Upon discovery of the deficiency, CRD stroke testing was suspended and surveillance testing of the Reactor Vessel Low Water Level sensors was satisfactorily completed. CRD stroke testing was then resumed. To preclude similar events in the future, the Surveillance Coordinator will issue a memo with the tests provided to the I&C Shop, identifying those that are required to be performed and the scheduled due dates. This action will be re-assessed when an upgraded surveillance test scheduling software program is implemented.
2981993025 | Cooper Station | 06/18/1993 | 02/03/1994 | 9402100216 | <strong>Hydrogen/Oxygen Monitoring System Operability Concerns Due to Moisture Accumulation And Sample Pump Reliability</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1993, upon a review of past operational data, it was determined that the Hydrogen/Oxygen Monitoring (H2/O2) system may have been installed and maintained in a manner which potentially prevented it from effectively performing its post-accident monitoring functions. The H2/O2 system was installed in 1988. Occasional problems with moisture accumulation and degraded sample pump operation were noted. Inspection of the sample lines indicated that portions were installed without sufficient slope to properly drain condensate out of the lines. The sample line slope was modified in 1990 and again in 1993. To eliminate what was thought to be foreign particles which affected sample pump reliability, filters were installed in 1990. The filters were subsequently found to exacerbate condensation formation. To correct this problem, the filters were periodically removed, disassembled and the condensate dumped from the filter bowls. <br /><br /> Based on a later laboratory analysis which indicated that the pump failures were due to normal operation, and not external contaminants, the filters were removed and the pump internals upgraded in 1993. Extensive testing was conducted to verify that condensation would adequately drain from the system. In January 1994 additional modifications were made to the pumps to provide added assurance of their operability. An evaluation of H2/O2 system operability during past operating cycles, considering the effects of the conditions noted above, has concluded that the analyzers were inoperable due to the moisture intrusion problem since the filters could not have been removed and the condensate dumped in a post-LOCA environment.
2981993026 | Cooper Station | 06/18/1993 | 02/17/1994 | 9403020107 | <strong>Noncompliance With ASME Section XI Inspection And Test Requirements Associated With Safety-Related Portions Of The Service Water And Reactor Equipment Cooling Systems</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1993, it was determined safety related portions of the Service Water (SW) and Reactor Equipment Cooling (REC) system piping had not been included in the ASME Code Section XI Inservice Inspection (ISI) program as required by 10CFR50.55a(g). The requirement specified in 10CFR50.55a(g), effective February 12, 1976, states that for plants such as Cooper Nuclear Station whose construction permit was issued prior to January 1, 1971, safety related components not part of the reactor coolant pressure boundary must meet the inspection requirements for ASME Code Class 2 and 3 components. At that time, this was evaluated and considered to not apply to the SW and REC systems since they were classified as IVP, USAS B31.1.0-1967 systems in accordance with the approved CNS design basis. Consequently, since these two systems were not included in the original ISI program, the safety related portions of these two systems were never included in the ASME Section XI ISI program. The Technical Specifications require compliance with the requirements contained in Section XI of the ASME Boiler and Pressure Vessel Code. <br /><br /> The safety related portions of the SW and REC systems will be included in the ASME Section XI ISI program by the next refueling outage. In addition, other safety related non-code Class 1, 2, or 3 systems will be evaluated for reclassification regarding Section XI test and inspection. This evaluation will be completed and applicable portions of other systems will be included in the ISI program by the next refueling outage.
2981993027 | Cooper Station | 06/18/1993 | 10/21/1994 | 9410260239 | <strong>Potential Degradation of Secondary Containment Integrity Which Was Undetected Due to Preconditioning and Test Methodology Deficiencies</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. In preparation for commencement of refueling activities during the 1993 Outage, the results of Secondary Containment Leak Rate testing conducted March 8, 1993, aid not meet Technical Specification requirements of -0.25 inches water gauge (wg) under calm wind conditions. During this test, a maximum negative pressure of -0.22 inches wg was achieved. The principal contributor for this test failure was traced to a leak path through a 10- inch rupture seal drain line between the Reactor and Radwaste Buildings which did not contain a loop seal. The circumstances associated with this discovery, its root causes and corrective actions were fully addressed in LER 93-011, transmitted to NRC on May 12, 1993. When this testing was performed, the plant was in Cold Shutdown and Primary Containment Integrity was not required.<br /><br /> Because of these test results, the integrity of Secondary Containment during the prior operating cycle was questioned. The testing performed March 8 was intended as a pre-requisite for refueling activities, satisfying the requirements of paragraph 4.7.C.1.c of the Technical Specifications. The test was not performed to determine as-found conditions upon plant shutdown. However, due to the potential degradation of Secondary Containment integrity during the prior operating cycle, this report is being submitted voluntarily.<br /><br /> Extensive efforts have been undertaken to identify and eliminate surveillance test preconditioning activities such as those associated with this situation. Additionally, a review of surveillance test procedures is underway to assure that testing adequately verifies Technical Specification and USAR requirements. Completion of the surveillance test procedure review and elimination of preconditioning will enhance identification of potential problems and performance of as- found testing, providing added assurance of safety system operability
2981993028 | Cooper Station | 06/30/1993 | 07/30/1993 | 9308040279 | <strong>Two Potentially Inoperable Valves Resulting From Evaluation Of Limitorque Part 21 Notification Concerning De-Clutch Mechanism Resonance</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1993, PC-MO-233MV, the Suppression Chamber Inboard Ventilation Inlet Isolation Valve operator, and RHR-MO-MO16A, the RHR Pump A and C Minimum Flow Valve operator, were determined to be subject to a failure mode wherein the de-clutch mechanism may potentially operate if the valve operator is subject to large dynamic loadings in a narrow range of frequencies. This was discovered while reviewing a Limitorque Part 21 notification concerning seismic excitation resonance of the de-clutch mechanism. If the de-clutch mechanism operates, the valves would not function until the magnitude of the dynamic loading had decreased, potentially increasing the stroke time for the valves. The large dynamic loadings which would result in this resonance would occur during an intermediate or large break LOCA. These loadings are postulated to cease after 900 seconds and 65 seconds respectively, following which the valve would operate. <br /><br /> The plant was in the 1993 Refueling Outage at the time this condition was determined to exist. The valve operators were modified during the Refueling Outage to replace the de-clutch lever mechanism with one not susceptible to this phenomena.
2981993029 | Cooper Station | 07/08/1993 | 08/06/1993 | 9308130125 | <strong>Spurious RPS Actuation During Performance Of The ASME Class 1-N System Leakage Test</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1993, at 11:42 pm, a Reactor Protection System (RPS) scram signal was generated from two of the four Reactor Pressure-Scram switches, resulting in the scramming of partially withdrawn Control Rod 26-31. The Reactor Coolant System was pressurized to perform the ASME Class 1-N System Leakage Test in accordance with ASME Code requirements prior to startup from the 1993 Refueling Outage. In concert with this test, other activities were being performed, including replacement of instrument line excess flow check valves and scram time testing. The common sensing line for the two Reactor Pressure-Scram switches was apparently vibrated during activities associated with replacing an excess flow check valve, resulting in a minor pressure perturbation at the switches. With the Reactor at approximately 1030 psig, only a small margin existed between the Reactor Coolant System pressure and the switches' setpoint. <br /><br /> The scram was reset, and pressure testing completed without further difficulties. Procedures related to ASME Class 1N system leakage testing will be revised to require better coordination of activities in the vicinity of the High Pressure-Scram switches and sensing lines which could result in an RPS actuation.
2981993030 | Cooper Station | 07/08/1993 | 08/09/1993 | 9308160098 | <strong>Inadequate In-Service Testing Of Service Water System Check Valves Due To Flow Instrument Calibration Error And Personnel Error In Specifying System Flow Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1993, as a result of determining that the conversion of Service Water (SW) Flow Rate measured by an annubar flow monitoring device was incorrect, it was discovered that In-Service Testing (IST) of the SW Pump discharge check valves had not been performed in accordance with the requirements of Generic Letter (GL) 89-04. In accordance with the GL requirement, verification that a check valve has stroked to its full open position requires the maximum accident condition flow rate be established through the valve. However, due to the flow instrument calibration error, actual SW System flow was less than indicated by approximately eight and one-half percent. Additionally, the surveillance procedure used to verify SW Pump discharge check valve operability on a quarterly basis did not require that the maximum accident condition flow rate be established. At the time this condition was discovered, required surveillance testing in preparation for startup from the 1993 Refueling Outage was being performed. <br /><br /> The cause of the IST test deficiency was due to the flow instrument calibration error, an original design deficiency, and failure to recognize that the flow rate specified in the surveillance procedure for verifying operability of the check valves was not the maximum accident condition flow rate required by GL 89-04. <br /><br /> A revised calibration factor was developed and incorporated in the surveillance test procedure. Additionally, the procedure was revised to establish the correct SW System flow for the test and to correctly state the test acceptance criteria. Assurance of SW System check valve operability was verified prior to startup from the 1993 Refueling Outage.
2981993031 | Cooper Station | 08/30/1993 | 02/17/1994 | ML09152048 | <strong>HPCI System Inoperability Resulting From A Dislodged Motor Operated Valve Pinion Gear Key And Motor Starter Contaminants</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1993, following surveillance testing, HPCI-MO-MO20, the High Pressure Coolant Injection (HPCI) Pump Discharge valve, failed to open upon operator demand. Subsequently, at 2:25 pm, the HPCI system was declared inoperable. Investigation determined that the motor pinion gear key was dislodged from its required position, allowing the motor pinion gear to freely rotate on the motor shaft. On September 1, during post maintenance testing following repair of the valve, it again failed to properly stroke. Upon investigation, paint and metal chips were found in the starter cabinet (starter). During subsequent investigation, a paint chip was observed to fall from the vicinity of one of the contactors in the starter. <br /><br /> Operators supplied by the factory have the motor shaft staked to capture the motor pinion gear key. Motors replaced in the field require re-staking to ensure the key remains correctly positioned. Limitorque Maintenance Update 89-1 addresses this concern. Although procedures were revised to require staking, no inspection of previously rebuilt motor operators (including HPCI-MO-MO20) was conducted. The failure of the valve to close following maintenance is attributable to debris (a small paint chip) lodged in a contactor. The debris is believed to be the result of either recent modifications or inadequate cleaning during periodic maintenance. <br /><br /> HPCI-MO-MO20 and its starter were repaired, tested, and returned to service. Maintenance history was reviewed to identify operators which may have unstaked keyways, and inspections planned to verify key installations. Inspection and cleaning of essential starters and MCC cubicles (MCC) has been completed. Procedures for design changes will be revised to ensure cleanliness requirements are clearly stated. The requirements for periodic inspections and cleaning will be enhanced.
2981993032 | Cooper Station | 07/08/1993 | 10/14/1993 | 9310200249 | <strong>125 Volt Battery Disconnect Switch Fuse Failure Caused By A Manufacturing Defect Resulting In Inoperability Of The B 125 Volt Battery System</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1993, at 7:47 am, the Reactor Vessel head vent valves were closed in preparation for performance of the ASME Class 1-N System Leakage Test. Vessel pressure was subsequently increased as specified by the test procedure. Technical Specifications required both 125 Volt Battery Systems to be operable during the test. However, an investigation into an unrelated problem on July 12 revealed that at the time of the leakage test, the B 125 Volt Battery System was inoperable due to a defective disconnect fuse.<br /><br /> On August 23, when tested under load, the fuse acted intermittently, allowing only momentary current flow. Subsequent inspection by the manufacturer revealed the fuse defect to be due to a manufacturing deficiency. The solder connection between some of the fuse elements to the end bell was inadequate. The manufacturer considered the problem to be an isolated occurrence, and advised that units manufactured since June 1990 should not exhibit the same deficiency due to improved manufacturing in-process quality checks that had been instituted at that time.<br /><br /> The defective fuse was replaced and the battery was returned to service. The spare fuses that were of the same age as the failed unit were tested and determined to be satisfactory. Parallel operation of the C Chargers with the A 125V and both 250V Battery Systems was performed, indicating acceptability of the remaining installed fuses for continued operation. Subsequent in-situ resistivity measurements taken indicate that the remaining seven 125 and 250 V Battery fuses are satisfactory. No other similar fuses are installed.
2981993033 | Cooper Station | 10/11/1993 | 11/10/1993 | 9311160410 | <strong>Core Spray Valve Control Deficiency Results In Noncompliance With The Licensing Basis</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1993, at 5:13 pm, during a review of the results of analyses of the functional requirements of Core Spray minimum flow line valves CS-MOV-MO5A and 5B, it was determined that upon remote manual closure of the valves from the control room, these valves would automatically re-open if the Core Spray pump flow rate was not above the system minimum flow setpoint. It was subsequently determined that the valves did not comply with the existing licensing basis. Primary Containment was declared inoperable and the plant was placed in a Limiting Condition for Operation per Technical Specification 3.7.A.2, Loss of Containment Integrity. At 6:34 pm Primary Containment was again declared operable when a Special Order was issued directing the installation of a Plant Temporary Modification if valve closure were required. <br /><br /> The design for the control of the minimum flow line valves is a part of the original design of the Cooper Nuclear Station. The Nuclear Steam System supplier became aware of this discrepancy and issued a Service Information Letter in 1984 providing a possible enhancement to the control of these valves stating, however, they did not consider these valves to have a containment isolation function since this Core Spray piping is an extension of the containment. This modification was evaluated but not implemented.
2981993034 | Cooper Station | 10/28/1993 | 12/06/1993 | 9312130421 | <strong>Technical Specification Violation Due To Failure To Conduct Required Fire Brigade Training</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1993, Training personnel identified that Fire Brigade members from support groups (Security and others) had not received quarterly Fire Brigade training from the time the training requirements were incorporated into the Technical Specifications in 1979. A review was conducted and concluded that this condition was reportable on November 15, 1993. Additionally, on November 4, 1993, it was identified that all Operations members of the site Fire Brigade had not received the appropriate quarterly training required by Technical Specification Section 6.1.4 during the fourth quarter of 1992 or the first quarter of 1993. <br /><br /> Support personnel did not receive quarterly training due to a misinterpretation of NRC requirements. Annual training was considered to be adequate to prepare them for their designated duties. Operations personnel did not receive training within the appropriate quarter due to a scheduling deficiency resulting from inappropriate supervisory guidance. Upon discovery, quarterly Fire Brigade training was provided to Security personnel (who provide the support function). Operations personnel Fire Brigade training is presently in accordance with Technical Specification requirements. A task force investigated the causes of these problems and recommended corrective actions to prevent recurrence.
2981993035 | Cooper Station | 11/08/1993 | 05/05/1994 | 9405120026 | <strong>Both Diesel Generator Declared Inoperable Due To Incorrect Relay Setpoints Resulting From Inadequate Procedure and Implementation of Vendor Recommended Checks</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1993, at 8:46 am, Diesel Generator (DG) 1 was declared inoperable upon finding relay DG-REL-DG1(59) contacts open following DG start during performance of the monthly DG surveillance procedure. DG 2 was declared inoperable at 12:02 pm upon discovering the same indication during subsequent testing. Upon declaring DG 2 inoperable, the Limiting Condition for Operation was entered, resulting in initiation of power reduction and a Notification of Unusual Event. Following relay re-calibration and testing, DG 1 was declared operable at 5:43 pm and DG 2 at 11:35 pm. <br /><br /> These conditions resulted from an inadequate relay calibration procedure which identified neither the active contacts nor the manufacturer's recommended adjustments. When the relays were re-calibrated during the 1993 refueling outage, the possibility of testing the spare contacts was not recognized by either the procedure or involved personnel. The applicable procedures and programs are being upgraded. These relays provide a permissive to close the DG output breakers. Both diesel generators had been verified capable of automatically loading under design conditions prior to startup from the refueling outage, and although declared inoperable, could have automatically loaded upon a loss of offsite power. Irrespective of relay calibration, both DGs were capable of being manually loaded.
2981993036 | Cooper Station | 11/14/1993 | 01/03/1994 | 9403140135 | <strong>Inoperable Technical Specification Fire Doors Without Appropriate Fire Watches Resulting From Personnel Error, Training, and Procedure and Administrative Control Deficiencies</strong><br /><i>Abstract:&nbsp;</i>From November 14 through November 23, 1993, 34 Technical Specification fire doors were found to be inoperable due to industry fire protection standards for fire door installations not being met. Upon determining the doors were inoperable, fire watches were posted as required by Technical Specifications with the exceptions listed below. The necessary repairs were made or the conditions evaluated in accordance with NRC Generic Letter 86-10, inspections re-performed, and the doors declared operable. On November 15, upon identifying a fire door discrepancy, a Quality Assessment Engineer and the Fire Protection Engineer did not communicate the condition to the Shift Supervisor. The Shift Supervisor was notified and a Fire Watch posted at 9:47 am on November 16. During a tour by plant management personnel on November 17, one screw was observed to be missing from the frames of two doors at approximately 2:00 pm. The screws were replaced within the hour, however the doors were not declared inoperable and a fire watch was not established. It was subsequently determined that the door should have been inspected following screw replacement for post maintenance testing. The inspection was satisfactorily completed at 12:23 am on November 18. One individual posted as a fire watch on November 17 was subsequently determined to be not fully trained as a fire watch. <br /><br /> The causes of these events were inadequate procedures and controls, inadequate training, and personnel error. The procedure was revised to clarify inspection criteria prior to completing door inspections, and a list of qualified fire watches provided. Additional changes are planned to further clarify operability criteria, improve door maintenance, and initiate a formal fire door inspection training program. These events have also been discussed during counseling and tailgate reviews. Additional reviews are being performed to identify the underlying causes associated with the apparent programmatic weaknesses.
2981993037 | Cooper Station | 11/18/1993 | 12/20/1993 | 9312290282 | <strong>Failure to Declare the Control Room Emergency Filter System Inoperable Prior to Initiating Maintenance on a Fire Door</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1993, at 3:56 pm, a Fire Door was declared inoperable and a Fire Watch was posted in compliance with Technical Specification requirements. Subsequently, the door was removed from its hinges for maintenance without recognition of its additional function in the Control Room envelope boundary. On the next day, following completion of maintenance, the Control Room Envelope Pressurization Test was performed as part of post-maintenance testing but was unsatisfactory. At 5:20 pm on November 19, upon recognizing that the envelope was degraded, the Control Room Emergency Filter System, a single train safety system, was declared inoperable. Investigation revealed air leakage around seals on the subject door as well as two additional envelope doors. Repairs were made to the three doors on November 20, and at approximately 10:00 am the surveillance test was satisfactorily performed. Following further engineering evaluation of conditions found during the test, the system was declared operable at 2:17 pm on November 22. At the time of this event, the plant was operating at full power. <br /><br /> The cause of this event is a programmatic deficiency, in that it was not evident to Fire Protection and Maintenance personnel, nor to the Shift Supervisor, that removal of the Fire Door degraded the Control Room Envelope. Procedures and programs will be revised to ensure clear identification of all functions which each door performs. The preventive maintenance (PM) activity for inspection and replacement of Control Room envelope door seals will be upgraded to improve inspection and testing criteria. The adequacy of testing frequency and PM of the Control Room envelope will also be evaluated.
2981993038 | Cooper Station | 12/14/1993 | 01/13/1994 | 9401260276 | <strong>Unplanned Automatic Reactor Scram and ESF Actuations Due To A Feedwater Controller Failure</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1993, at 1:34 am, with the plant in operation at full power, an automatic reactor scram occurred due to low reactor vessel water level. The cause of the low water level was determined to be a failure of the Reactor Feedwater Pump (RFP) master controller. Upon receipt of annunciators associated with the feedwater system, reactor power was lowered by reducing the speed of the Reactor Recirculation (RR) Pumps. As water level continued to decrease, the B RR Pump was tripped in an effort to reduce power more rapidly, however, an automatic reactor scram occurred due to low reactor vessel water level. <br /><br /> The plant response to the transient was normal. All control rods inserted, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) Systems initiated, and Groups 2 (Reactor Coolant System), 3 (Reactor Water Clean Up System), and 6 (Primary and Secondary Containment) Isolations occurred. Normal reactor vessel water level was restored and HPCI, RCIC, and RFP B were subsequently secured. <br /><br /> The malfunction of the RFP master controller was caused by the failure of a normally energized 1/2 watt voltage dropping resistor. The most probable root cause for its failure is age related degradation. The failed master controller was replaced with a spare controller. Prior to its installation, the spare unit was visually inspected for degraded components and bench tested. Additionally, other similar GEMAC controllers in the HPCI, RCIC and Reactor Feedwater Systems were inspected for visual signs of degradation of resistors and other components. No deficiencies were found. Further corrective action to be taken includes an evaluation of GEMAC controllers for age related concerns.
2981993039 | Cooper Station | 12/14/1993 | 01/14/1994 | 9401260268 | <strong>Two Instrument Line Orifices Not Installed Due To Original Construction Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1993, while researching information concerning the design of instrumentation for the Core Spray system, it was determined that the drawings for the one inch diameter instrument lines from the Core Spray headers to CS-DPIS-43A and 43B, Core Spray System A (B) Failure - High Differential Pressure Alarm, did not indicate 1/4 inch orifices as depicted on the drawings for similar instrument lines. The design basis documents require orifices for instrument lines connected to the Reactor Coolant system which penetrate Primary Containment, to mitigate the potential consequences of an instrument line break outside Primary Containment. As the plant was shutdown at the time of this discovery, visual inspections and non-destructive examinations were conducted on December 16 which verified that the orifices were not installed. Upon review of design basis requirements for the orifices on December 17, this condition was determined to be reportable at 5:30 pm. A 10CFR50.72 notification was made at 8:38 pm. <br /><br /> This condition is the result of an original construction deficiency. Orifices were installed in the two lines on December 18 and 19, and testing subsequently completed on December 20, Documentation for other instrument lines meeting these criteria was reviewed and orifices were found to be indicated on the applicable drawings. These systems were inspected, either visually or by nondestructive examination, to ensure that orifices were installed as required. In all cases the orifices were present.
3011993001 | Point Beach 2 | 01/27/1993 | 02/26/1993 | 9303040178 | <strong>Failure of Steam Generator Sample Isolation Valve to Fully Shut</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, January 27, 1993, while performing maintenance on a radiation monitoring system data acquisition module, flow was observed in the blowdown sample line for the Unit 2, "B" steam generator. The blowdown sample isolation valves for both steam generators receive an automatic signal to close when the data acquisition module is removed from service for maintenance. However, the blowdown sample isolation valve for the "B" steam generator (2MS-2084) did not fully shut. This valve is the automatic containment isolation valve in the blowdown sample line for the Unit 2, "B" steam generator. A three hour Limiting Condition for operation was entered based on loss of containment integrity. 2MS-2084 was immediately shut and verified shut by operations personnel. The manual isolation valve (2MS-317) upstream of 2MS-2084 was also shut, thereby restoring containment integrity. The valve was repaired and satisfactorily tested two days later. There was no release of radioactive liquid to the environment as a result of this event.
3011993002 | Point Beach 2 | 03/28/1993 | 04/27/1993 | 9305040013 | <strong>Reactor Trip During Turbine Trip Testing</strong><br /><i>Abstract:&nbsp;</i>At 0145 CST on March 28, 1993, while Unit 1 was shut down for its Cycle 20 annual refueling outage and Unit 2 was operating at 100% power, a Unit 2 reactor trip occurred during performance of Technical Specification Test TS-4A, "Turbine Trip Test (Monthly), Unit 2." A Duty Operating Supervisor (DOS) was directed by the Duty Shift Superintendent (DSS) to conduct Test TS-4A. The DOS then assigned one Licensed Auxiliary Operator (LAO) to assist him in performing the evolution. Test TS-4A cautions the operator to hold the turbine test handle in the "TEST" position during the entire test to prevent an actual trip from the mechanical trip block devices. However, due to valve operation difficulties and subsequent follow-up actions, the LAO commenced opening thrust bearing Hand Valve 2EH-00065 before the DOS was able to hold the turbine test handle in "TEST." Pressure in the test line increased to the turbine trip setpoint and, because the test handle was not in the "TEST" position, the turbine stop valves shut and the turbine tripped, resulting in a reactor trip. The test was immediately terminated. Operations personnel entered Emergency Operating Procedure EOP-0, "Reactor Trip or Safety Injection." Unit 2 was subsequently returned to full power at 2220 CST on March 29, 1993. A 4-hour notification to the NRC was made at 0401 CST in accordance with 10 CFR 50.72 (b) (2) (ii).
3011993003 | Point Beach 2 | 04/09/1993 | 05/10/1993 | 9305180117 | <strong>Monthly Reactor Protection and Safeguards and Nuclear Instrumentation Systems Testing not Performed Within Required Periodicity</strong><br /><i>Abstract:&nbsp;</i>Several line items from Point Beach Nuclear Plant Technical Specifications Table 15.4.1-1, "Minimum Frequencies for Checks, Calibrations, and Tests of Instrument Channels," and one line item from Table 15.4.1-2, "Minimum Frequencies for Equipment and Sampling Tests," were not performed on Unit 2 within their required periodicity. These tests were not performed because they would have placed Unit 2 in a condition in which one spurious signal or equipment failure could have caused a reactor trip. With Point Beach Unit 1 and Kewaunee Nuclear Power Plant both shutdown for their annual maintenance and refueling outages, continued operation of Point Beach Unit 2 was essential for maintaining a stable source of off-site power to the shutdown plants. A Notice of Enforcement Discretion was granted by the Nuclear Regulatory Commission Office of Nuclear Reactor Regulation for this event.
3011993004 | Point Beach 2 | 11/02/1993 | 12/06/1993 | 9312140457 | <strong>Operability Concern For Containment Accident Fan Bearing</strong><br /><i>Abstract:&nbsp;</i>A bearing removed from Unit 2 containment accident fan W1D1 during the Fall, 1993 annual maintenance and refueling outage was identified as having a cage (retainer) made from fiberglass reinforced Type 66 nylon. This bearing was installed on fan W1D1 during the Fall, 1992 refueling outage. Discovery of the nylon cage raised a question as to whether the fan would perform its safety function during accident conditions. The bearing was replaced with one containing a bronze cage. An evaluation was performed to determine the operability of the containment accident fan with a nylon cage in the fan bearing. The evaluation provided reasonable assurance that the fan would perform its safety function under accident conditions and, therefore, was judged to be operable. A review of receipt inspection documentation associated with the bearings currently installed on all containment accident fans at PBNP confirmed that there are no containment accident fan bearings presently installed that have cages made of nylon. Although the containment accident fan was judged to be operable, this report is provided as an informational Licensee Event Report as this information may be of interest to other licensees.
3011993005 | Point Beach 2 | 11/19/1993 | 12/20/1993 | 9312300171 | <strong>Molded Case Circuit Breakers Fail Trip Tests Due To Grease Solidification</strong><br /><i>Abstract:&nbsp;</i>Prior to and during the fall 1993 Point Beach Nuclear Plant (PBNP) Unit 2 refueling outage, 80 Westinghouse Type HFA 30-amp molded case circuit breakers (MCCBs) were replaced as part of the PBNP MCCB Maintenance Program. Ten of the removed MCCBs were tested to verify proper operation in an attempt to return the MCCBs to stock. All ten of the MCCBs did not meet the tripping time requirements of Standard NEMA AB4-1991 during instantaneous current tests. A high current coordination test was conducted on the ten MCCBs along with an additional 30 MCCBs. Five of these MCCBs did not trip when subjected to a 2200 amp fault current (the instantaneous tripping point for the upstream breaker). On November 19, 1993, it was determined that with these test results and analysis of cable routings of non-safety-related loads supplied from motor control centers (MCCs) B32 and B42, a common mode failure could potentially result if two MCCBs would not clear applied faults, causing both feeder breakers to MCCs B32 and B42 to open and deenergize all safeguards loads associated with both MCCs. However, this scenario is highly improbable because the components of concern do not automatically operate and the associated cabling is normally deenergized. All identified Unit 2 MCCBs have been replaced. All but two identified MCCBs have been replaced in Unit 1. They will be replaced during the spring 1994 Unit 1 refueling outage.
3021993001 | Crystal River 3 | 03/05/1993 | 01/19/1994 | 9402020226 | <strong>Failure of Decay Heat System Cooling Control Valve Causes Cooldown Exceeding Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1993, Crystal River Unit 3 (CR-3) was in mode 4 (Hot Shutdown) and cooling down for a planned maintenance outage. After switching from steam generator cooling to decay heat removal (DH) system cooling, the cooldown exceeded the limits of Technical Specification 3.4.9.1. <br /><br /> After securing the reactor coolant system (RCS) pumps, operators, unable to establish control of the DH cooling system from the control room, dispatched an auxiliary building operator to establish manual control of the temperature control valves. While using posted vendor supplied instructions to convert from automatic to manual control, a valve unexpectedly opened causing additional RCS cooldown. An attempt was made to close the valve manually. After several minutes, the valve started to open due to damage to a stem key connecting the valve to the manual handwheel. The alternate DH train was then placed in operation, stabilizing RCS temperature. <br /><br /> The initial excessive cooling was caused by failure of a control valve controller. Additional cooling occurred when taking manual control of the valve. Damage to the valve stem key was caused by improper manual operation. The valve controller was repaired, the valve operator was modified, revised valve manual operating instructions were posted, and additional corrective actions were taken.
3021993002 | Crystal River 3 | 03/29/1993 | 05/10/1996 | 9605140381 | <strong>Switchyard Cable Failure Caused Degraded Voltage of Class 1E Electrical Busses and Actuation of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1993, Florida Power Corporation's (FPC) Crystal River Unit 3 was in MODE 5, COLD SHUTDOWN. All electrical power was being supplied via a backfeed from the 500 kilovolt (KV) switchyard. At 0151, the 500KV output breakers opened, interrupting the backfeed. Both Emergency Diesel Generators started and energized their respective Engineered Safeguards busses. <br /><br /> During the loss of one (500KV backfeed) of the two available offsite power sources, decay heat removal cooling stopped and was restarted five minutes later when the alternate source of power (230KV) reenergized the safety related busses. During the time decay heat removal was not available the 94 degree Fahrenheit (F) reactor coolant temperature increased a maximum of approximately 14 degrees F near the center of the core, while temperatures near the core barrel increased substantially less. The offsite power from the 230KV switchyard was available during the entire evolution. Salt water entered switchyard cable trenches as the result of a winter storm. <br /><br /> Salt water immersion of a degraded cable is suspected to have contributed to the cable failure, subsequent actuation of relays which opened breakers, and loss of one of two available offsite power sources. The damaged cables were replaced and other cables were tested and replaced as necessary. FPC has approved a project for control and power cable replacement and separation.
3021993003 | Crystal River 3 | 04/08/1993 | 05/10/1993 | 9305170312 | <strong>Failure to Consider Instrument Error When Specifying Safety System Operating Limits Leads To Operation Outside of the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993, Crystal River Unit 3 was in Mode 5 (COLD SHUTDOWN) for a maintenance outage. At 1335, the Nuclear Shift Supervisor was notified of a problem with the Core Flood Tank (CFT) level instrumentation. Nuclear Operations Engineering had determined that insufficient instrument error had been considered when operating limits for the CFT were selected. This created the potential that the contained volume of the CFT, as allowed by operating limits, could exceed the limits of Technical Specification 3.5.1. This report is submitted in accordance with 10CFR50.73 (a)(2)(ii)(B) as a condition outside of the design basis. <br /><br /> A modification to reset the alarm bistables has been implemented as an interim measure. A corrective action to expand the allowed margin with the improved Technical Specifications will be evaluated. Corrective action to prevent recurrence has been to implement a guideline in the design/modification process which requires consideration of instrument error in determining setback for operating limits from Technical Specifications.
3021993004 | Crystal River 3 | 04/08/1993 | 05/10/1993 | 9305180308 | <strong>Inappropriate Personnel Action Resulted In Degraded Class 1E Bus Voltage and Actuation of Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993, Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) for a planned maintenance outage. Electrical power was being supplied via backfeed from the 500 kilovolt (KV) switchyard. One of the two Class 1E electrical systems was out of service. At 1803 the 500KV breakers opened, interrupting the power backfeed. The in-service Class 1E 4160 Volt (V) bus deenergized. The "B" Emergency Diesel Generator started automatically and reenergized the bus. This report is submitted in accordance with 10CFR50.73(a)(2)(iv). <br /><br /> Decay heat removal flow was stopped for approximately three minutes during the transition of loads to the Emergency Diesel Generator. Reactor Coolant System temperature, initially 89 degrees Fahrenheit, increased approximately 4.5 degrees Fahrenheit during this period.<br /><br /> The event occurred when personnel followed an incorrect sequence for removing DC power to the 500KV breaker protective relays as a result of inadequate work instructions being used to replace a battery cell in one of the switchyard battery banks. Additional administrative controls have been established to reduce the risk of interruption of offsite power and decay heat removal. Additional corrective actions, based on the results of a Human Performance Enhancement System (HPES) analysis, will be addressed.
3021993005 | Crystal River 3 | 05/18/1993 | 06/10/1993 | 9306170362 | <strong>Lack of Isolation Device Between Safety Related and non- Safety Related Portions of a Control Circuit Results in a Condition Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1993, Crystal River Unit 3 (CR-3) was in Mode 1 (POWER OPERATION) at 100% Rated Thermal Power producing 870 Megawatts. The Nuclear Shift Supervisor was notified that the control circuit for the Makeup and Purification System letdown isolation valve (MUV-49) did not meet the electrical isolation criteria for 1E and non-1E components. MUV-49 is a containment isolation valve located outside the containment. In addition to its safety related functions, MUV-49 also has a non-safety related function to automatically close on a high temperature signal to protect the demineralizers in the letdown system. During original plant design, an isolation device was not specified for installation between the safety related and non-safety related portions of the control circuit for MUV-49, thus placing the unit in a condition outside the design basis. A modification is being developed which will install isolation devices for the non-safety related temperature control circuit. Current design standards prevent this condition from recurring.
3021993006 | Crystal River 3 | 05/20/1993 | 06/18/1993 | 9306300041 | <strong>Inadequate Modification Design Results in Degraded Seismic Capability and a Condition Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>At 1707 on May 20, 1993, Crystal River Unit 3 (CR-3) was in Mode 1 (POWER OPERATION) at 100% Rated Thermal Power producing 873 Megawatts. While performing a field walkdown of separation barriers, an inadequately secured separation barrier (an open box approximately five inches by six inches) was identified that could affect control switches for certain safety equipment on the main control board under certain seismic conditions. The equipment affected is the control switches used to throttle High Pressure Injection (HPI) flow via the HPI injection valves and their indicating lights. Adjacent control switches for the Low Pressure Injection (LPI) valves are also affected. This condition was caused by inadequate design of a plant modification. In 1990, a plant modification replaced the flow indicators directly above the separation barrier which removed the support for the barrier. A placard has been posted to restrict access to the area of the separation barriers affected. Florida Power Corporation is pursuing a plant modification to provide a secured separation barrier. Current design requirements prevent this problem from recurring.
3021993007 | Crystal River 3 | 06/28/1993 | 07/28/1993 | 9308040176 | <strong>Raised Setpoint on Pressure Regulator Leads to Operation Outside Design Basis.</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1993, Crystal River Unit 3 (CR-3) was in Mode 1 (POWER OPERATION) at 100% Rated Thermal Power producing 865 Megawatts. The hydrogen pressure regulator valve MUV-491 for the Makeup Tank (MUT) was found to be set above 10 pounds per square inch (psig). MUV-491 was reset to control at 10 psig. Engineering was notified that operating above the 10 psig setpoint was a suspected design basis issue. On June 28, 1993, the Nuclear Shift Supervisor was notified that the hydrogen pressure setpoint to the MUT had exceeded the Appendix R Design Basis. A 1985 Appendix R fire analysis postulated a spurious opening of the hydrogen addition solenoid operated control valve MUV-143 due to a fire induced short-circuit. This would place 50 psig overpressure on the MUT, possibly resulting in hydrogen entrainment in the Makeup Pumps (MUP) suction piping under certain drawdown conditions to compensate for system shrinkage during cooldown. MUV-491, a self-contained pressure regulating valve, was installed in the hydrogen addition line to maintain pressure at 10 psig to reduce this possibility without operator action. The setpoint for MUV-491 had been recently adjusted to increase the MUT pressure in order to improve chemistry parameters in the primary coolant. An Operations Study Book (OSB) Entry was made cautioning operations personnel that such actions may create unauthorized plant modifications.
3021993008 | Crystal River 3 | 07/06/1993 | 05/12/1994 | 9405180436 | <strong>Due to a Lack of Engineering Review, Motor Operated Valves With Brakes Could Fail to Perform Their Safety Function Under Degraded Voltage Conditions</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1993, Crystal River Unit 3 (CR-3) was in Mode 1 (POWER OPERATION) at 100% Rated Thermal Power producing 859 Megawatts. A High Pressure Injection suction valve was determined to be inoperable. A concern had been raised for the operability of safety related Limitorque motor operated valves (MOV) with an electrical motor brake option installed. A 1991 calculation showed that under degraded voltage conditions, valve motors will have sufficient voltage to accelerate their load, however motor brakes, which require higher voltages, may not receive sufficient voltage to release the brake. The valve therefore may not be capable of performing its safety function. This is a condition outside the design basis. The cause was a lack of engineering review for the motor brake voltage requirements. On April 11, 1994, a periodic revision to the 1991 calculation identified an additional 4 valves which may not function under degraded grid voltage coincident with accident conditions. The 1994 revision was more conservative than the original calculation and contained information unavailable in 1991. Some of the corrective actions included locking valves in place, brake removal, further analysis to assure performance of valve safety functions, and a plant modification to eliminate a valve safety function.
3021993009 | Crystal River 3 | 09/18/1993 | 10/13/1993 | 9310210115 | <strong>Reactor Coolant Pump Trip Causes Plant Transient and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1993, Crystal River Unit 3 was in MODE 1 (POWER OPERATION) at 100% power. At 2348, a high differential current alarm On September 18, 1993, Crystal River Unit 3 was in MODE 1 (POWER OPERATION) at 100% power. At 2348, a high differential current alarm for the "D" Reactor Coolant Pump (RCP) was received in the control room. Almost immediately, the "D" RCP tripped on high differential current. The Integrated Control System responded by beginning an automatic plant runback to 75% power. Approximately eight seconds later, the Reactor Protection System tripped the reactor on flux/flow/imbalance. <br /><br /> One of the Main Steam Safety Valves did not fully reseat following the trip. Personnel dispatched to the valve discovered that a non-captive release nut had rotated slightly, preventing the valve from fully seating. The valve was returned to the fully seated position following a re-adjustment and locking of the release nut. FPC determined that the RCP trip was caused by a shorted "B" phase surge capacitor, which was replaced. Several other minor plant anomalies were experienced coincident with the reactor trip and were subsequently corrected. <br /><br /> FPC is considering additional evaluations and corrective actions.
3021993010 | Crystal River 3 | 11/30/1993 | 12/22/1993 | 9401040075 | <strong>Failure to Assign Task Leads to Nonperformance of Surveillance Resulting in Entry into Technical Specification 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1993, Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION), operating at 99.8%. reactor power and generating 875 megawatts. The "B" Emergency Diesel Generator was out of service for maintenance. A routine surveillance status inquiry revealed that a weekly battery surveillance had not been performed.<br /><br /> The batteries are located at Crystal River Units 1 & 2 (CR-1 & 2), an adjacent fossil plant site, and the surveillance is normally performed by those personnel. A procedure and a calibrated instrument are delivered to CR-1 & 2 by CR-3 personnel on a weekly basis. As a result of a schedule change the CR-3 supervisor responsible for personnel assignments did not clearly assign the delivery task to any CR-3 worker, therefore the delivery was not made to CR-1 & 2 and the surveillance was not performed within the required time interval. <br /><br /> Upon discovery of the inoperable CR-1 & 2 batteries, both offsite to onsite power sources were declared inoperable. Technical Specification (TS) 3.0.3 was entered at 1311 on November 30, 1993, due to both offsite power sources inoperable concurrent with the "B" EDG inoperable. The CR-1 & 2 battery surveillance was immediately started. The surveillance was completed and TS 3.0.3 was exited at 1346 on November 30, 1993. Counselling of the shop supervisor was conducted as well as other corrective actions.
3041993001 | Zion 2, Zion 1 | 10/19/1993 | 10/06/1994 | 9410120037 | <strong>Failure to Meet "As-Found" Requirement for Total Type B and C Leak Rate</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1993, during the performance of Technical Staff Surveillance (TSS) 15.6.10E, "Type C Leak Rate Tests" on the Unit 2 penetration P-14, the Unit 2 containment isolation valve 2RC8047 failed the Type C leak rate test. The "As-Found" leakage of 306 Standard Cubic Feet per Hour, (SCFH) exceeded the acceptance criteria of 285 SCFH. <br /><br /> On October 28, 1993, during the performance of TSS 15.6.10E on the Unit 1 penetration P-14, 1RC8047 also failed the Type C leak rate test with an "As-Found" leakage of 852 SCFH. <br /><br /> The cause of this event was design deficiency. The original valves and the equivalent replacement valves had hard seating surfaces. Industry experience has shown that for containment isolation check valve locations in air and gas systems, benefits can be seen by changing from hard seats to soft seats. This was not considered during modification P22-1(2)-91-544 since the intent was to reuse the original check valves. A possible contributing cause of the check valves not seating properly was inadequate system pressure. The installed check valves are rated for 600 psig, yet are only subjected to an actual system pressure of 100 psig in this application. There was no significant increase in risk to the health and safety of the public. <br /><br /> Corrective actions include investigating the condition of the valves, replacing the valves and retesting both valves prior to each unit startup.
3041993002 | Zion 2, Zion 1 | 11/02/1993 | 12/02/1993 | 9312090128 | <strong>Missed Surveillance on the containment vent and purge radiation monitors prior to core alterations which violated Technical Specification 3.14.3.C.</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1993 during the performance of Periodic Test (PT)-0 Appendix E-2, "Operating Surveillance Checksheet", PT-17 was required to be performed. The unit operator found that PT-17 had been divided into 3 separate procedures, but PT-0 Appendix E-2 did not reference which one needed to be performed. After reviewing the procedures, the unit operator chose the wrong one to be performed and the unit supervisor approved it. On November 2, 1993, the Operating Procedure Coordinator discovered that the wrong procedure had been performed violating Technical Specification 3.14.3.C. <br /><br /> The cause of this event is personnel error. The unit supervisor did not review the selected PT for applicability. A contributing cause of this event was procedural deficiency. PT-0 Appendix E-2 did not reference the correct procedure number. The safety significance of this event was minimal. <br /><br /> Corrective Actions include updating PT-0 Appendix E-2. discussing this event with the individuals involved, and reviewing PT-0, "Surveillance Checklists and Periodic Tests", to ensure that no other procedures are incorrectly referenced.
3041993003 | Zion 2, Zion 1 | 11/29/1993 | 12/29/1993 | 9401070370 | <strong>Failure of Pressurizer Safety Valves to meet "As-Found" Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On 11-29-93 during the performance of as-found nitrogen testing on the Unit 2 pressurizer safety valves, (2RC8010A, 2RC8010B, and 2RC8010C) AB!, all three valves failed the acceptance criteria. <br /><br /> On 12-17-93, during the performance of as-found nitrogen testing on the Unit 1 pressurizer safety valves (1RC8010B and 1RC8010C), both valves failed the acceptance criteria. <br /><br /> The cause of this event was component failure. Four of the valves failed low due to foreign material (boric acid) on the valve seat, and one valve failed high, due to unknown causes.<br /><br /> Previous evaluation determined that the most limiting case for the valves that failed low was the loss of load transient. It was determined that this case was not safety significant. The valve that failed high operated at a pressure well below the system design limitation. Therefore, this case posed no additional threat to the health and safety of the public. <br /><br /> Corrective actions include disassembling, cleaning, inspecting and rebuilding the valves and then re-testing and adjusting the setpoints as necessary using steam instead of nitrogen.
3041993004 | Zion 2, Zion 1 | 07/29/1993 | 05/26/1994 | 9406010100 | <strong>Violation of the Inservice Testing Program which is required per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1993, during review of Technical Staff Surveillance (TSS) 15.6.20V-P, "In Service Testing Valve Surveillance, Power Operated Valve Testing", it was noticed that the stroke time from July 29, 1993, for valve 2MOV-CS0002 BE!, had increased by 26.3% compared to the previous stroke time. The ASME code requires that the test frequency be increased to monthly whenever the stroke time of the valve increases by 25% or more. The required increased testing was not performed in August or September.<br /><br /> The cause of the missed surveillances was personnel error. The IST coordinator failed to identify the 25% increase in stroke time, and thus did not place the valve on increased surveillance contrary to the requirements of TSS 15.6.20V-P, step 4.4. <br /><br /> The Safety Analysis maximum stroke time limit was not exceeded during the surveillance. The safety significance of this event was minimal.<br /><br /> Corrective actions include reviewing this event with the appropriate personnel to stress attention to detail, reviewing the 1993 IST program surveillances for additional deficiencies (one additional deficiency was found), revising the IST procedure, and increasing review of the program until the new program is instituted.
3051993001 | Kewaunee | 01/28/1993 | 03/01/1993 | ML11188041 | <strong>Phase-to-Phase Fault in Main Feedwater Pump Motor Causes Bus 1 and 2 Undervoltage Condition Resulting in Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1993, at 0443 hours, with the plant operating at 100% power, a large fault on main feedwater pump B motor caused an undervoltage condition on Bus 1 and Bus 2. The bus voltage dropped below the undervoltage reactor trip setpoint and initiated an automatic reactor trip. The voltage on both buses quickly recovered once the fault was isolated. <br /><br /> On January 29, 1993, during the subsequent plant startup, another reactor trip occurred at 1516 hours from 5% power. reached the low-low level reactor trip setpoint of 17% while steam generator level was being manually controlled. Problems with steam dump valve SD-11A1 (to the condenser) contributed to the difficulty in controlling steam generator level. <br /><br /> During both trips, all plant systems responded as designed. <br /><br /> Corrective actions included replacing main feedwater pump B motor with a spare and using the steam generator power operated relief valves during subsequent plant startups until the steam dump valve is repaired. Steam dump valve SD-11A1 will be repaired during the 1993 refueling outage which is scheduled to start March 5.
3051993002 | Kewaunee | 01/29/1993 | 03/01/1993 | ML11188041 | <strong>Failure of Radiation Detector Results in Actuation of Steam Generator Blowdown Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1993 at 0333 hours, the condenser air ejector radiation monitor (R-15) spiked above its high alarm setpoint. The plant was in the hot shutdown condition. As designed, the high alarm signal closed the steam generator blowdown isolation valves, and the steam generator blowdown sample isolation valves. <br /><br /> The isolation resulted from failure of the Geiger Mueller (GM) tube in the radiation monitoring circuit. A number of probable root causes for the failure were postulated. Engineering staff concluded the probable cause of tube failure was electrical damage resulting from corrosion of the electrical connections for the tube. These connections are located in a high temperature and high humidity environment. <br /><br /> The failed component was replaced and the monitor was returned to service. To prevent recurrence of this failure, the GM tube in the existing installation will be periodically replaced. <br /><br /> A modification to replace the existing radiation monitoring system is under way. The modification, as currently designed, relocates the electrical connections for this detector external to the existing environment.
3051993003 | Kewaunee | 03/06/1993 | 05/26/1994 | ML11188047 | <strong>Three Main Steam Safety Valves Found Inoperable Due To Mechanical Drift</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1993, with the plant in hot shutdown for the 1993 refueling outage, Surveillance Procedure 06-077, 'Main Steam Safety Valve Test' was performed. During the performance of the procedure it was discovered that the lift pressure of three of the ten main steam (MS) safety valves was out of tolerance; and hence, the three valves were declared inoperable. <br /><br /> The three inoperable MS safety valves were disassembled, inspected, reassembled and tested before exceeding hot shutdown after the 1993 refueling outage. The cause of the safety valve failure was not conclusively determined from these rebuilds. <br /><br /> The two valves that failed with the largest deviation from the setpoint were tested again during the 1994 refueling outage. One of theses valves failed slightly higher than its acceptance criterion on the third test. The valve's first two tests were within the acceptance criterion. Although the valve was disassembled and inspected, a root cause could not be conclusively determined. Past assembly techniques may have contributed to the 1994 failure. <br /><br /> In both cases sufficient pressure relieving capability existed to ensure the health and safety of the public at all times. This ability existed through a combination of relieving capability of the MS safety valves and the non-safety related steam relief capabilities of the system.
3051993004 | Kewaunee | 03/18/1993 | 04/15/1993 | ML11188041 | <strong>Intergranular Attack and Intergranular Stress Corrosion Cracking Results in Both Steam Generators Being Categorized as C-2</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1993, with the plant in refueling shutdown, eddy current examination of the Steam Generator (SG) tubes was completed for the 1993 refueling outage. The examination found 9 tubes in SG A and 12 tubes in SG B which were considered defective. Since one or more tubes were considered defective in each steam generator, both SGs were categorized as C-2. As required by KNPP Technical Specifications (TS), this Licensee Event Report (LER) provides the required 30 day written report to the Nuclear Regulatory Commission (NRC). <br /><br /> The majority of the SG tube degradation at KNPP is probably caused by outside diameter intergranular attack and outside diameter intergranular stress corrosion cracking (IGA/IGSCC). In accordance with KNPP's TS, all defective tubes were plugged. This increased the overall equivalent plugging percentage from 10.06 percent to 10.37 percent for the 1993-1994 operating cycle. <br /><br /> During the 1993 refueling outage, portions of 3 tubes were extracted from the B SG cold leg. These tubes will be examined by non-destructive and destructive examination techniques to determine actual tube condition relative to eddy current results. <br /><br /> The secondary side boric acid and Morpholine addition programs will continue during the 1993-1994 operating cycle to reduce the caustic environment and corrosion/erosion on the secondary side.
3051993005 | Kewaunee | 03/22/1993 | 12/29/1993 | ML11188045 | <strong>Annual Transmitter Calibration Finds a Shift in the Pressurizer High Pressure Reactor Trip Signal Initiation Due to Instrument Drift.</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1993, with the plant in cold shutdown, the pressurizer pressure transmitters were found out of tolerance (during SP 36-020A) and were subsequently recalibrated. A March 22, 1993, review of the pressure transmitter data determined that Technical Specification 2.3.a.2.A had been exceeded. TS 2.3.a.2.A requires a pressurizer high pressure reactor trip setpoint of less than or equal to 2385 psig. The March 22 review also incorporated the as found calibration data (from February 22 and 23, 1993) for the associated bistables. This review determined that a reactor trip initiation on pressurizer high pressure would not have occurred until 2405 psig. Additionally the Safety Injection block permissive of less than 2000 psig noted in Table TS 3.5-3 would have occurred at 2030 psig. <br /><br /> This event occurred as a result of instrument drift. The cause of the instrument drift may be aging of the transmitters, but the calibration method used is a more probable cause. The calibration is performed at cold shutdown and may indicate instrument drift when in fact at normal plant operating conditions the instruments are within specification. <br /><br /> Pending equipment availability and additional testing, Kewaunee may replace the pressurizer pressure transmitters' during the 1994 refueling outage. In the short term Kewaunee will continue to trend monthly pressurizer pressure transmitter loop currents in order to detect drift in the transmitters outputs. Since May of 1993, no adverse trends have been identified. If an adverse trend develops, appropriate corrective action will be taken which may include calibrating the affected transmitter(s) at power or adjusting the associated bistable setpoints.
3051993006 | Kewaunee | 03/22/1993 | 04/21/1993 | ML11188041 | <strong>Non-Conservative Low Temperature Overpressure Protection Setpoint</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1993, at 1100 hours, a potentially non-conservative condition was identified for the Low Temperature Overpressure Protection (LTOP) setpoint development. The plant was in the refueling shutdown condition with the reactor coolant system (RCS) vented. Preliminary evaluation of the LTOP setpoint calculation found the setpoint did not account for flow induced differential pressures or applicable piping losses. The LTOP system was conservatively declared inoperable until a thorough engineering review was completed. <br /><br /> This condition has existed since 1977 as a result of incomplete engineering analysis of the LTOP mitigation system. <br /><br /> The results of the engineering review and calculations were documented in a safety evaluation, which was reviewed and accepted by the Plant Operations Review Committee on April 7, 1993. This evaluation demonstrated the adequacy of the existing LTOP setpoint to prevent RCS pressure from exceeding 10 CFR 50 Appendix G limits during LTOP transients. This safety evaluation, valid through the end of operating cycle 20 (about April 1995), required the imposition of reactor coolant pump operating restrictions. <br /><br /> The operating restrictions were implemented and the LTOP system was returned to operable status.
3051993007 | Kewaunee | 03/26/1993 | 04/26/1993 | ML11188042 | <strong>Local Leak Rate "As Found" Leakage Exceeds Technical Specification Requirements Due to a Check Valve Not Seating Properly</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1993, with the plant in refueling shutdown, the local leak rate test volume associated with the reactor coolant pump A seal injection fine could not be pressurized to the required 46 psig. The test volume did not pressurize due to check valve CVC-205A not seating properly. As a result Kewaunee's total "as found" maximum pathway leakage exceeded 0.60La. For Kewaunee, 0.60La is equal to a leakage of 322,800 standard cubic centimeters per minute (sccm). The redundant seal injection line check valve indicated a leakage of 5.6 sccm. The seal injection line is a 2 inch line that supplies water to the reactor coolant pump A seals. <br /><br /> There are no safety implications associated with this event since the redundant valve had a satisfactory leak rate. Excluding CVC-205A leakage, Kewaunee's total "as found" maximum pathway leakage was 42,147.9 sccm. Kewaunee's toW "as found" minimum pathway leakage was 15,013 sccm. <br /><br /> On April 7, 1993, with the plant in refueling shutdown, CVC-205A was replaced and a retest indicated an "as left" leakage of 6.8 sccm. As of April 14, 1993, Kewaunee's total "as left" maximum pathway leakage was 8,143.4 sccm. Kewaunee is investigating the future replacement of the other seal injection check valves.
3051993008 | Kewaunee | 03/28/1993 | 04/27/1993 | ML11188042 | <strong>Machining Process Used to Manufacture the Keyway in the Yoke Bushing for Velan Globe Valves With Motor Operators Results in Valve Inoperability</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1993, with the plant in refueling shutdown, dynamic testing was completed on valves SI-208 and SI-209, the redundant safety injection to the refueling water storage tank isolation valves. During the testing it was discovered that SI-208 would not close under dynamic conditions whereas SI-209 was found to be operable. The investigation into the failure determined the valve failed to close due to a broken anti-rotational device, an "L" shaped key. Part of the key was found to be rubbing against the valve stem threads, increasing stem resistance. <br /><br /> SI-208 and SI-209 are 2 inch diameter Velan globe valves with Limitorque motor operators. On March 28 an inspection of the other 7 Velan globe valves installed in the plant found 5 of the 7 also had broken keys. An investigation into the failures found three contributing causes. In some cases the key may be bottoming out in the stem keyway when the valve is opened, shearing the key. The key is roughly machined with sharp edges resulting in unnecessary stress risers. The width of the bushing keyway is not uniform. This can overstress the key because it can result in the shorter part of the key assuming the entire load placed on the key. <br /><br /> To correct these problems, new keys were designed, which addressed the three failure mechanisms, and were installed in all 9 valves. The valves were tested and the keys were verified to be intact. The keys will be reinspected during the 1994 refueling outage.
3051993009 | Kewaunee | 04/13/1993 | 05/12/1993 | ML11188042 | <strong>Facility Outside Design Basis Due to the Unavailability of a Voice Activated Headset Connection</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1993 with the plant in the Hot Shutdown mode, a steam exclusion (SE) door was found ajar. With the SE door ajar the plant was in a condition outside of its design basis. A voice activated headset cord was run through a SE door pathway and was found in a position which may have prevented the door from fully closing. The headset cord was run through the doorway in order to perform general maintenance procedure 236-1, "Diagnostic Testing of Limitorque Motor Operated Valves using the Torque Thrust Cell." The SE door was in this condition for approximately five minutes. <br /><br /> The event was caused by the unavailability of voice activated headset connection in the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) room. A contributing factor to this event was determined to be personnel inattention to detail. <br /><br /> An evaluation is being performed to determine the need for installing a voice activated headset connection and a welding receptacle in the TDAFWP room, which would prevent the need to run cable/cord through the doorway. Additional training will also be provided on the requirements for opening a SE boundary.
3051993011 | Kewaunee | 04/21/1993 | 10/05/1994 | ML11188048 | <strong>Auxiliary Feedwater Discharge Cross Connect Valve Failed to Fully Close During MOV Dynamic Testing</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1993, at 1201 hours, with the reactor operating at 35% power, the following significant items were identified during dynamic motor operated valve (MOV) testing of auxiliary feedwater discharge cross connect valve AFW-10A: 1) the as-found setup of the actuator exceeded the manufacturer's recommended limits, and 2) the as-left setup may not fully isolate flow based on test results with similar setups. Valve AFW-10A was being tested in response to Generic Letter 89-10.<br /><br /> It was originally thought that the actuator was undersized for design basis conditions. The actuator was sized during initial system design using actuator sizing calculations which did not consider current design requirements, such as closure against full pump discharge pressures or weak link calculations. A safety analysis and 10 CFR 50.59 evaluation were initiated to determine the acceptability of modifying plant emergency operating procedures to allow the operators to stop the auxiliary feedwater pump(s) to reduce the high differential pressure across the valve and allow it to close. Danger tags were immediately placed on the valve control switches to address this concern and the procedures were revised. <br /><br /> Due to the potential generic information associated with this event, it was decided on April 26 that a voluntary LER be submitted to the NRC. Further testing and inspections during the 1994 refueling outage determined that normal valve wear created excessive valve friction losses and prevented the valve and actuator from performing properly. Similar inspection and testing will be performed on AFW-10B during the 1995 refueling outage. Also, AFW-10A will be dynamically tested to verify the 1994 dynamic test data. A periodic inspection program will be established for these valves. .
3051993012 | Kewaunee | 06/05/1993 | 07/06/1993 | ML11188043 | <strong>Unplanned Automatic Letdown Isolation Occurred During a Plant Cooldown Due to Inadequate Control of Pressurizer Level</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1993, at 0310 hours, with the plant at intermediate shutdown, a cooldown to cold shutdown was in progress. During the cooldown, an unplanned automatic letdown isolation occurred when pressurizer level dropped below the low level setpoint of 18.3%. When the cooldown was initiated, pressurizer level was at approximately 37%, two letdown orifice valves were open (allowing a letdown rate of approximately 80 gallons per minute) and both charging pumps were in manual control providing the Reactor Coolant System (RCS) with a total charging/seal injection flow of approximately 86 gallons per minute.<br /><br /> The cause of the letdown isolation was the charging and letdown system not being adequately balanced to account for RCS shrinkage. Contributing factors to the event included letdown flow being maximized for chemistry concerns and the computer alarm setpoint being marginally (0.7%) above the automatic letdown isolation setpoint. <br /><br /> As a corrective action, the computer alarm setpoint for low pressurizer level will be raised. This setpoint increase will provide greater reaction time for the operators to respond to changes in pressurizer level. Also, management will be meeting with all nuclear personnel to discuss methods for enhancing human performance.
3051993013 | Kewaunee | 06/04/1993 | 07/02/1993 | ML11188043 | <strong>Actuation of Both Motor Driven Auxiliary Feedwater Pumps Due to Feedwater Regulating Valve Failing to Completely Close and Subsequent Operator Actions</strong><br /><i>Abstract:&nbsp;</i>This report describes an unplanned actuation of the auxiliary feedwater system, which is an engineered safety feature. On June 4, 1993, with the plant in hot shutdown, an automatic actuation of both motor driven auxiliary feedwater pumps occurred. This event occurred while the plant was being shut down for a scheduled outage. Prior to the event, the B main feedwater pump had been secured while the A main feedwater pump remained running. As the demand for feedwater to the steam generators diminished, the main feedwater regulating valves automatically throttled closed. However, the A steam generator level continued to increase with the main feedwater regulating valves indicating fully closed. In order to stop the A steam generator level increase and prevent an automatic trip of the main feedwater pump at 67 % steam generator narrow range level, the operator shut off the A feedwater pump. This action caused an automatic start of both motor driven auxiliary feedwater pumps as designed. The circuitry that initiates this automatic auxiliary feedwater pump start is not an engineered safety feature. <br /><br /> The contributing causes of this event were determined to be the failure of the A main feedwater regulating valve to completely isolate feedwater flow and the operator actions taken to isolate the feedwater flow. The main feedwater regulating valve was subsequently repaired and is being monitored. Additionally, the analyses of this event will be required reading for the operations group.
3051993014 | Kewaunee | 06/18/1993 | 07/19/1993 | ML11188043 | <strong>Nuclear Instrumentation Power Range Channel Adjustment at Low Power Results in Unanticipated Deviation at Higher Power Level</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 099%. At 0428 hours on June 18, 1993, in accordance with Kewaunee's Technical Specifications, a plant shutdown was initiated when it was determined that the power range nuclear instrumentation could have allowed an overpower condition greater than the 109 % technical specification (TS) power limit. Approximately one hour later the shutdown was interrupted to allow the overpower reactor trip bistables to be conservatively reset to 100% power; this would ensure the operability of the overpower trip function. At 0730 hours, with the plant at approximately 88 % power, it was determined that, although these trips were within the USAR analyzed condition of 118 % of full power, three of the channels had exceeded the TS limit of 109 % of full power. <br /><br /> Subsequent review determined that, because of conservatism associated with the calorimetric calculation, only one channel actually exceeded the 109% TS limit; therefore, this report is being submitted to the NRC as a voluntary Licensee Event Report. <br /><br /> The contributing causes to this event were: 1) a gain adjustment (electronic signal correction) at a lower power level that caused an increased deviation at higher power levels, 2) a lack of guidance in the daily calibration surveillance procedure for the performance of gain adjustments, and 3) an unexpected drift of the overpower trip bistables.<br /><br /> Long term corrective actions include: 1) modifying the plant power range daily calibration surveillance procedure to provide detailed guidance on when to perform gain adjustments, 2) monitoring the overpower trip bistable drift, and 3) making this LER required reading for all operations and reactor engineering personnel.
3051993015 | Kewaunee | 06/18/1993 | 07/19/1993 | ML11188043 | <strong>High Radiation Area Gate Left Unsecured Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 hours on June 18, 1993, with the plant at 87 percent power, a sliding gate to the low level radioactive waste drumming area, which is a High Radiation Area (HRA), was found closed but unsecured and unattended. A Nuclear Auxiliary Operator (NAO) was performing his routine plant rounds when he found the gate (#18) unsecured and unattended. The NAO secured the gate and reported the condition to the Shift Supervisor. <br /><br /> The cause of this event has been determined to be personnel error. A plant electrician finished performing maintenance on equipment in this HRA at approximately 1130 hours. He remembers engaging the lock after exiting the HRA, but does not remember if he routed the chain through the wall-mounted metal tube prior to engaging the lock. <br /><br /> The individual involved with this incident has been counseled on the potential safety consequences of this type of error. This event will also be discussed at KNPP safety meetings, which are attended by KNPP personnel (WPSC and Contractors). Additionally, the plant's weekly newsletter, which is distributed for all KNPP personnel, will include a message emphasizing the potential impact of this event for KNPP personnel.
3051993016 | Kewaunee | 07/09/1993 | 08/09/1993 | ML11188043 | <strong>Spurious Radiation Monitor Output Signal Causes Inadvertent Closure of Steam Generator Blowdown Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>At 1014 hours on July 9, 1993, with the plant at 100% power, the steam generator blowdown and blowdown sampling isolation valves closed, as designed, on a high radiation signal from the steam generator blowdown radiation monitor (R-19). <br /><br /> The R-19 high radiation signal prompted operations personnel to closely monitor other parameters which indicated that there was no primary to secondary leak. This indication was supported by a local steam generator blowdown sample and by the results of a primary to secondary leak rate calculation, which both indicated that normal activity levels existed. After determining that there was no primary to secondary leak, R-19 was declared out of service. Additionally, R-19 blowdown isolation signals were bypassed to allow steam generator blowdown to be re-established. <br /><br /> A definitive cause of the high radiation output signal could not be determined. However, a R-19 printed circuit board was found to have an out of specification value for the level calibration and was also fining loosely in its friction socket connections. The circuit board's condition potentially generated the high radiation signal. <br /><br /> The printed circuit board was replaced. The photomultiplier tube associated with R-19 was also replaced. R-19 was returned to service on July 16, 1993.
3051993017 | Kewaunee | 09/10/1993 | 10/07/1993 | ML11188044 | <strong>Steam Generator Blowdown and Blowdown Sampling Isolation Due to Residual Radiation in Radiation Monitor 19 Housing</strong><br /><i>Abstract:&nbsp;</i>At 1437 hours on September 10, 1993, with the plant at 100% power, the steam generator blowdown and blowdown sampling isolation valves closed, as designed, on a high radiation signal from the steam generator blowdown radiation monitor (R-19). <br /><br /> Immediate actions included verifying that all automatic actuations occurred, sampling steam generator blowdown, and monitoring the condenser air ejector gas monitor (R-15). After determining that there was not a primary-to-secondary leak, R-19 was declared out of service, the blowdown isolation signal was bypassed, and steam generator blowdown was reestablished. <br /><br /> The most probable cause of the high radiation output signal was a piece of slightly radioactive sludge breaking free from the detector housing and being detected as it passed by the monitor. The buildup of slightly radioactive sludge on the R-19 detector housing resulted from a previous steam generator primary-to-secondary leak. <br /><br /> The housing of the monitor was wiped free of sludge which lowered background radiation. R-19 was returned to service at 1249 hours on September 16, 1993.
3051993018 | Kewaunee | 10/12/1993 | 11/11/1993 | ML11188044 | <strong>Failure of Agastat Relay Causes Automatic ESF Start of the Turbine Driven Auxiliary Feedwater Pump.</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1993, at 0643 hours, with the plant operating at -100% power, an unexpected automatic start of the turbine driven auxiliary feedwater pump (TDAFWP), an Engineered Safety Feature (ESF), occurred. The pump started and reached full speed as designed. The steam generator blowdown isolation valves (BT-2A, BT-2B, BT-3A, and BT-3B) closed as designed. No other alarms occurred concurrent with the automatic start. The TDAFWP was declared out of service, the control switch placed in pullout, and the associated 72 hour Limiting Condition of Operation (LCO) action statement was entered. The inadvertent start occurred as a result of a relay failure. <br /><br /> This event was caused by the failure of a time delay relay (Agastat 2400 series) in the TDAFWP automatic start circuitry. The relay is a normally energized relay; therefore, the coil in the relay has been powered almost continuously since it was installed during original plant construction. The failed relay was replaced with an identical relay from stock. The TDAFWP was returned to service at 1558 hours the same day and the LCO was exited at that time. <br /><br /> The failed relay was replaced with an identical spare. Also, an expedited review of the Nuclear Plant Reliability Data System database and the Kewaunee Operating Experience Assessment database was conducted, which revealed no generic implications associated with the Agastat 2400 series relays. Prior to this event, Kewaunee was performing an engineering evaluation to determine suitable replacements for the obsolete Agastat 2400 series relays.
3051993019 | Kewaunee | 11/04/1993 | 12/06/1993 | ML11188045 | <strong>Casting Void in Residual Heat Removal Pump Results in a Through Wall Leak</strong><br /><i>Abstract:&nbsp;</i>This report describes a violation of Kewaunee Technical Specification 3.3.b.2.B, which allows one residual heat removal (RHR) pump to be inoperable for 72 hours. The 1A RHR pump was declared inoperable at 1841 hours on November 1, 1993, with the plant at 100% power, when a through wall leak was identified on the pump's casing. Since the scheduled repair time would exceed 72 hours, Wisconsin Public Service Corporation requested and received a notice of enforcement discretion from the Nuclear Regulatory Commission prior to exceeding the 72 hour limiting condition of operation action statement. <br /><br /> The flaw, resulting in the leak, originated in a void in the pump casing wall. The void appears to have been caused by non-uniform cooling of the pump casing when it was originally cast. Service induced stresses resulted in crack propagation to the inner and outer diameters of the pump casing.<br /><br /> Corrective actions included visually inspecting the redundant pump and repairing the 1A RHR pump. The pump was repaired and returned to service prior to exceeding the extension provided in the Nuclear Regulatory Commission's notice of enforcement discretion.
3061993001 | Prairie Island 2, Prairie Island 1 | 01/04/1993 | 02/03/1993 | 9302110087 | <strong>Auto-Start of a Component Cooling Water Pump Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1993, Unit 2 was in cold shutdown for modifications. No. 21 Residual Heat Removal (RHR) Pump and No. 21 Component Cooling Water Pump were in service, providing core cooling. A licensed control room operator was using the routine operating procedure to transfer RHR to the alternate train in order to perform motor-operated valve testing. Per the procedure, the operator opened the No. 22 Residual Heat Removal Heat Exchanger Component Cooling Inlet valve, and the resulting increased flow reduced the component cooling header pressure below the pump auto-start setpoint, and at 2248 No. 22 Component Cooling Water Pump started. This was a non-ESF actuation. The operator then started No. 22 RHR Pump and completed the transfer of RHR to the alternate train per the procedure. <br /><br /> The event was caused by an inadequate procedure. The procedure assumes that both component cooling water pumps are already running but that assumption is not readily apparent to the operator. The procedure does not contain any cautions to the operator concerning the potential for pump auto-starts.
3061993002 | Prairie Island 2 | 04/13/1993 | 05/13/1993 | 9305180346 | <strong>Loss of Administrative Control of an Inoperable Containment Isolation Valve Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1993, control room operators performed surveillance procedure SP2272, Quarterly Cycling of Pressurizer Relief Tank Reactor Makeup Water and Nitrogen Control Valves. One containment isolation valve, which controls reactor makeup water to Unit 2 containment, exceeded its maximum time for closure (an ASME Section XI requirement), and was declared inoperable. The redundant containment isolation check valve was operable. To comply with Technical Specifications, the control valve was closed and its air supply was lockwired closed. Later, to improve control over the penetration, the upstream manual isolation valve was closed. <br /><br /> Later, when the System Engineer requested the control room to stroke the inoperable control valve for troubleshooting purposes, an operator was sent to restore the air supply to the control valve. He performed that action, but had misunderstood the instructions and mistakenly opened the manual isolation valve. Later, another operator making rounds discovered the manual valve open when it should have been shut. The situation was corrected. Administrative control of the penetration had been lost for about 13 hours. The redundant containment isolation check valve was operable throughout the period.
3061993003 | Prairie Island 2 | 07/19/1993 | 10/20/1993 | 9310260027 | <strong>Both Trains of Ventilation for Safeguards Electrical Equipment Secured for Several Hours Due to Inadequate Administrative Control</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1993, Unit 2 was at 100% power. A Work Request had been issued for maintenance on the supply fans for the D5/D6 building ventilation system. The D5/D6 building is a recently constructed building housing D5 and D6 Diesel Generators for Unit 2 and associated electrical equipment. At 0045 hours on July 19, both trains of the D5/D6 building ventilation system were secured per the Work Request by placing the control switches in the OFF position. After completion of the work, at 1605 hours, the control switches were returned to the AUTO position. The ventilation system had been secured for 15 hours and 20 minutes. <br /><br /> Subsequently it was determined that, absent a previous analysis to show the conditions under which the safeguards equipment in question could function as necessary without the ventilation system in service, and absent the proper guidance to the operators to enable them to return the system to service within an acceptable period of time, the safeguards equipment must be considered to have been inoperable on July 19.
3061993004 | Prairie Island 2 | 11/24/1993 | 12/27/1993 | 9401070069 | <strong>Breach in Unit 2 Containment Boundary Found During Fuel Handling</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993, Unit 2 was in cold shutdown for refueling. The Unit 2 core had been unloaded, and maintenance and testing activities were in progress. Work had begun on isolation and repair of MV-32151, No. 22 Fan-Coil Unit Cooling Water Outlet. The work request required containment fan-coil units to be isolated and drained. After draining was complete, the work request called for motor valves to be aligned for "Refueling Integrity," which establishes status of the containment boundary for fuel handling. On November 23, in preparation for core reload, equipment alignment checklist C19.9-2 was completed to establish the containment boundary for "Refueling Integrity." Core reload operations began at 1023 on November 23, 1993. At 0940 on November 24, 1993, with core reloading still in progress, air was noted coming from the open valve body of MV-32151. Investigation showed that MV-32150 was open and allowing air to flow from containment to the Auxiliary Building. MV-32150 was immediately closed manually. A similar valve was also checked and found open; it too was immediately closed manually, and "Refueling Integrity" was established.
3091993001 | Maine Yankee | 12/31/1992 | 01/21/1993 | 9302020256 | <strong>Inoperable Emergency Core Subsystems During Pump Recirculation Valve Stroke Testing</strong><br /><i>Abstract:&nbsp;</i>Maine Yankee's Operating Experience Program requires that the industry operating plant experience reports be screened for applicability to Maine Yankee. On November 16, 1992 the review of a report concerning the temporary disabling of Emergency Core Cooling System (ECCS) subsystems during valve stroke testing resulted in the determination that the report was potentially applicable to Maine Yankee and it was forwarded to the Operations Department for formal evaluation. On December 2, 1992 the Operations Department concluded that for a brief period of time, during the stroke testing of either of the normally open ECCS pump minimum-flow recirculation valves SIA-M-53 or SIA-M-54, both trains of the ECCS Low Pressure Safety Injection and Containment Spray subsystems must be considered inoperable. <br /><br /> The minimum flow recirculation valves have historically been tested on a monthly basis in conjunction with the ECCS valve tests. <br /><br /> The root cause of this event is considered to be the failure of the original Technical Specification license submittal to allow for surveillance testing of the minimum-flow recirculation valves. <br /><br /> The surveillance is required by Maine Yankee Technical Specifications. There are no exceptions in the LCO for ECCS that specifically allow this testing and recent interpretations concluded that this condition is reportable under 10CFR50.73. <br /><br /> In order to minimize the period of time during which the minimum-flow recirculation line is isolated yet tested frequently enough to provide assurance of the valve's operability, Maine Yankee has changed the frequency of the valve stroke test from a monthly basis to a quarterly basis. Maine Yankee is also evaluating the possibility of submitting a proposed Technical Specification change which would grant an exception to the ECCS operability requirements for the stroke testing of SIA-M-53 and SIA-M-54.
3091993002 | Maine Yankee | 01/21/1993 | 02/19/1993 | 9302220388 | <strong>Control Room Ventilation Trains Inoperable due to Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1993, both trains of Control Room Ventilation were declared inoperable and Technical Specification 3.0.A.2 was entered. The inoperability of both trains was a result of preventive maintenance (PM) for filter replacement, internal to "B" train air handler (AC-1B). Because of damper configuration, it is impossible to externally isolate the AC-1B air handler and maintain a recirculation path. When AC-1B is opened, both trains via FN-11A or FN-11B have direct paths to the atmosphere, bypassing the recirculation flow. <br /><br /> The consequences of this event, which will occur quarterly, is minimal since the loss of both trains is short duration (less than 1 hour - no shutdown initiated) for the PM.
3091993003 | Maine Yankee | 02/11/1993 | 03/12/1993 | 9303190265 | <strong>Expiration of DC Solenoid Pilot Valve' Environmental Qualification Service Life</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power, Maine Yankee identified two DC Solenoid Pilot Valves which had exceeded their Environmental Qualification (EQ) service life. The solenoid pilot valves are installed on the containment service air isolation valve, SA-A-138 and the containment nitrogen isolation valve, N-A-66 which close on a Containment Isolation Signal (CIS) or a Safety Injection Actuation Signal (SIAS). SA-A-138 and N-A-66 are normally shut air operated valves. <br /><br /> On February 11, 1993 at 1100, SA-A-138, and N-A-66 were declared inoperable upon discovery of the expiration of the solenoid's EQ service life. The valves were restored to operable status at 1220 by disabling them in their shut CIS/SIAS position. No solenoid failures have occurred. <br /><br /> The solenoid valves have been replaced and the EQ Program is being updated to reflect their normally energized state. A review of the EQ Program was conducted and no similar situations exist.
3091993004 | Maine Yankee | 03/08/1993 | 04/07/1993 | 9304130316 | <strong>Inoperable Fire Door</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1993 at 0630 while at full power, upper level Spray Pump Building Fire Door (FD) 103 became inoperable when heating ventilation unit HV-7 was tagged out of service for routine maintenance. Compensatory actions required by the plant's technical specifications were not implemented until the inoperable door was discovered at 0045 on March 9, 1993. When the inoperable status of the fire door was recognized, HV-7 was returned to service to rectify the condition. During the period that the fire door was inoperable, the door was closed but the differential pressure across the door exceeded the capability of the door closing mechanism to reliably latch the door. <br /><br /> The root cause of the incident is considered to be personnel error. The planned corrective action will be to place precautions in the ventilation procedures to alert operators to the fact that abnormal ventilation configurations can cause fire doors to become inoperable.
3091993005 | Maine Yankee | 03/08/1993 | 04/05/1993 | 9304120246 | <strong>Inadequate Administrative Control Of Emergency And Auxiliary Feedwater Manual Valves</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1993 at 1230 while at full power, the NRC Resident Inspector notified the control room that 5 manual valves which were necessary to assure emergency and auxiliary feedwater flow from the primary water source to the steam generators did not appear to have the administrative controls required by the plant's Technical Specifications. The 5 valves were aligned properly and controlled by procedure but due to a procedural deficiency they were not locked as required by the plant's Technical Specifications. A subsequent review of all of the valves in the emergency and auxiliary feedwater flow path identified 3 additional valves which should have been fitted with locking devices but were not. During operation at power the emergency and auxiliary feedwater flow path manual valves must be aligned and locked in the position required for reactor core energy removal.<br /><br /> The root cause of this event was a procedural deficiency. The deficiency resulted from a misinterpretation of the policy governing locked valves. The policy was subsequently clarified, but the effect of the policy clarification on the procedure governing the periodic surveillance of the subject valves was not recognized. <br /><br /> The affected valves have been locked and the controlling procedure has been revised. There was no safety significance to this event because all of the valves were confirmed to have been procedurally controlled in their proper position for reactor core energy removal.
3091993006 | Maine Yankee | 02/22/1993 | 04/09/1993 | 9304200213 | <strong>Defective Cut Off Switch Actuators (Paddles) On Reactor Trip Circuit Breakers (Type AK-25) Anti-Pumping Feature.</strong><br /><i>Abstract:&nbsp;</i>This informational LER is being submitted to describe the findings of Maine Yankee (MY) Electrical Maintenance while conducting preventative maintenance on Reactor Trip Circuit Breakers (type AK-25) on 02/22/93. <br /><br /> During the performance of MY procedure 5-77-2, INSPECTION AND REPAIR OF GENERAL ELECTRIC AK-25 REACTOR TRIP CIRCUIT BREAKERS, a defective cutoff switch actuator (paddle) was detected on a Reactor Trip Circuit Breaker. <br /><br /> The defect was identified as a broken cut-off switch actuator. The cut-off switch is part of the breaker control circuit which provides the anti-pump feature. This feature prevents repeated closure attempts if a trip signal is present during breaker closure. The breaker is tripped by other means. <br /><br /> The remaining ten RTB cut-off switches were inspected and three additional cracked actuators were discovered. Of these three, only one breaker was in service, the other two were spares. A determination was made about the operability of the breaker with the cracked paddle being able to perform it's intended function. The breaker was considered operable because the open/trip capability was not compromised. <br /><br /> The faulty switch on the breaker with the broken paddle was replaced and the trip breaker tested successfully. All RTB's were inspected for defective paddles and all cracked paddles were replaced. The root cause of the defect was determined to be cyclic fatigue. GE will also provide a written failure analysis. <br /><br /> One similar occurrence was reported by LER 83-036 that documented cracked shunt trip paddles, which is a different sub-component of the AK-25 breaker.
3091993007 | Maine Yankee | 03/14/1993 | 04/13/1993 | 9304190031 | <strong>Automatic Diverse Scram System Inoperable</strong><br /><i>Abstract:&nbsp;</i>This is an informational LER being submitted to supply information related to a condition which resulted in the plant ATWS system being degraded. The ATWS system consists of the Diverse Scram System (DSS), the Diverse Turbine Trip (DTT), and the Diverse Automatic Feedwater System (DAFWS) only the DSS portion of the system was affected. <br /><br /> On March 15, 1993 at 1400, plant personnel determined that the Automatic Diverse Scram System (DSS) had been inoperable since approximately 0015 on 3/14/93. The DSS acts as an automatic backup to the reactor protection system by interrupting power to the control rods on high pressurizer pressure. The DSS was returned to service at 1900 on March 16, 1993. <br /><br /> Maine Yankee is investigating the event utilizing Human Performance Enhancement System (HPES) methodology.
3091993008 | Maine Yankee | 04/15/1993 | 05/17/1993 | 9305190322 | <strong>Emergency Core Cooling System (ECCS) Valves Found Unlocked</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1993 plant personnel, performing a review of the service water system, found 19 open manual valves requiring locks per Maine Yankee's administration controls. This discovery was a result of an on-going program to review all ECCS valves for proper alignment and locking as required for safeguards operation. This oversight in procedure controls was due to a misunderstanding of the lube water supply requirements for service water pump operability. <br /><br /> The controlling procedures were revised and the program will continue until completed by December 31, 1993.
3091993009 | Maine Yankee | 04/08/1993 | 04/30/1993 | 9305040089 | <strong>Inoperable Emergency Core Cooling Subsystems During Pump Recirculation Valve Stroke Testing</strong><br /><i>Abstract:&nbsp;</i>Maine Yankee's Operating Experience Program requires that the industry operating plant experience reports be screened for applicability to Maine Yankee. On November 16, 1992 the review of a report concerning the temporary disabling of Emergency Core Cooling System (ECCS) subsystems during valve stroke testing resulted in the determination that the report was potentially applicable to Maine Yankee and it was forwarded to the Operations Department for formal evaluation. On December 2, 1992 the Operations Department concluded that for a brief period of time, during the stroke testing of either of the normally open ECCS pump minimum-flow recirculation valves SIA-M-53 or SIA-M-54, both trains of the ECCS Low Pressure Safety Injection and Containment Spray subsystems must be considered inoperable. <br /><br /> The minimum flow recirculation valves have historically been tested on a monthly basis in conjunction with the ECCS valve tests. <br /><br /> The root cause of this event is considered to be the failure of the original Technical Specification license submittal to allow for surveillance testing of the minimum-flow recirculation valves. <br /><br /> The surveillance is required by Maine Yankee Technical Specifications. There are no exceptions in the LCO for ECCS that specifically allow this testing and recent NRC interpretations concluded that this condition is reportable under 10CFR50.73. <br /><br /> In order to minimize the period of time during which the minimum-flow recirculation line is isolated yet test frequently enough to provide assurance of the valve's operability, Maine Yankee has changed the frequency of the valve stroke test from a monthly basis to a quarterly basis.
3091993010 | Maine Yankee | 04/08/1993 | 05/08/1993 | 9305110183 | <strong>Surveillance Testing Of ECCS Subcomponents Causes Inoperable ECCS Subsystems</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993 surveillance testing of Spray Building Exhaust Ventilation Filters resulted in the determination that, for a brief period of time, both trains of Emergency Core Cooling System (ECCS) Low Pressure Safety Injection (LPSI) and Containment Spray (CS) subsystems must be considered inoperable. <br /><br /> Bypassing and restoring Spray Building Exhaust Ventilation has been done on an infrequent basis for surveillance and maintenance activities. Securing the fans, shifting the dampers, and restoring the fans is an evolution that lasts less than one minute. <br /><br /> Technical Specification (T.S.) 3.6 C.2 requires two operable and redundant ECCS trains during power operation. There are no specific T.S. associated with the fans or filters. However, a Maine Yankee T.S. Interpretation concludes that Spray Building Exhaust Ventilation must be operable in order for LPSI and CS to be operable. Since both trains are affected by this action, entry into T.S. 3.0 A.2 is required. T.S. 3.0.A.2 is entered after the specific time frame in the remedial action is exceeded. The time required to shift the dampers is so short that no shutdown is commenced. <br /><br /> No previous LER's have been submitted by Maine Yankee for this type of event. Recent NRC interpretations concluded that entry into T.S. 3.0 A.2 is reportable under 10 CFR 50.73. <br /><br /> The cause of this event is considered to be the failure of the original T.S. license submittal to recognize the impact of testing and performing maintenance on or around the Ventilation Filters.
3091993011 | Maine Yankee | 05/26/1993 | 06/26/1993 | 9306290255 | <strong>Containment Hatch "O" Ring Maintenance Requires Entry Into Tech. Spec. 3.0.A.2.</strong><br /><i>Abstract:&nbsp;</i>At 1030 on Tuesday May 25, 1993 Nuclear Plant Operators (NPO's) completed a routine Containment Inspection in accordance with (IAW) Maine Yankee (MY) Procedure 1-200-11 CONTAINMENT INSPECTION. Following the Containment Inspection a personnel "hatch check" was performed IAW MY Procedure 3-1-13 PERSONNEL AIR LOCK DOOR SEAL LEAK TEST. <br /><br /> The "hatch check" was completed at 2230 on the same day. The integrity of the inner door of the CTMT hatch was determined to be compromised. The integrity of the outer door was determined to be sound. CTMT integrity was assured as long as the outer door was sealed. <br /><br /> On Wednesday May 26, 1993 at 1037 the CTMT hatch outer door was opened for maintenance on the inner door. TS 3.0 A.2. was entered. The time required to open and close the outer door was less than five (5) minutes so no shutdown was commenced. At 1039 the outer hatch was secured and TS 3.0 A.2. was exited. The inner hatch "O" ring was cleaned, inspected, lubricated in place, and the door was placed back in service. The outer door was reopened at 1040 and reclosed at 1041 TS 3.0 A.2. was entered and exited once again. <br /><br /> At 1130 of the same day a "hatch check" was performed on both doors IAW MY procedure 3-1-13 with satisfactory results.<br /><br /> Previous LER's have been submitted by MY for this type of event. LER 80-002 was written to describe a "hatch check" failure and LER 83-034 reported brief openings of an inner hatch while the outer hatch was inoperable. <br /><br /> The cause of this event is the failure of the "O" ring to properly seal uniformly due to the build up of dry lubricant on one area of the sealing surface.
3091993012 | Maine Yankee | 05/27/1993 | 06/27/1993 | 9306300120 | <strong>Control Room Ventilation Trains Inoperable Due to Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1993, both trains of Control Room Ventilation were declared inoperable for a brief period of time. The inoperability of both trains was a result of preventative maintenance (PM) for filter replacement, internal to "B" train air handler (AC-1B). Because of damper configuration, it is impossible to externally isolate the AC-1B air handler and maintain a recirculation path. When AC-1B is opened, both trains via FN-11A or FN-11B have direct paths to the atmosphere, which bypasses the recirculation flow. <br /><br /> The consequences of this event, which occurs quarterly, is minimal since the loss of both trains is of short duration (less than 1 hour - no shutdown initiated) for the PM.
3091993013 | Maine Yankee | 06/18/1993 | 07/18/1993 | 9307230046 | <strong>Incorrect Compensatory Action for Inoperable Fire Hose Station</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1993, with the plant at 95% power, preparations were made to isolate firemain branch cutout valve FS-289 for repair. It was recognized this work would also isolate two firehose stations required to be operable by Technical Specifications and that compensatory actions were necessary. <br /><br /> With a required firehose station inoperable, Technical Specifications require routing of additional hoses of equivalent capacity, to the unprotected area from an operable hose station, within one hour. <br /><br /> The Fire Protection Coordinator (FPC) and the Shift Operating Supervisor (SOS) responsible for isolating and tagging out the cutout valve each performed an independent review of system drawings to identify other operable hose stations for supplying the additional hoses. <br /><br /> However, in an effort to expedite the installation of the additional hoses, the FPC departed from his pre-planned hose routing and elected to use a different hose station for the alternate water supply. <br /><br /> Approximately twelve hours later, it was discovered that this hose station was inside the tagging boundary for the isolation of the branch cutout valve; and thus was itself inoperable. <br /><br /> Immediate corrective action was taken to re-route the hose to an operable station. However, for approximately 12-1/2 hours, Maine Yankee was in noncompliance with Technical Specification 3.23D. <br /><br /> The root cause of this event was human error on the part of the FPC.
3091993014 | Maine Yankee | 07/01/1993 | 08/01/1993 | 9308030254 | <strong>Inoperable Emergency Core Cooling Subsystems During Pump Recirculation Valve Stroke Testing</strong><br /><i>Abstract:&nbsp;</i>Maine Yankee's Operating Experience Program requires that the industry operating plant experience reports be screened for applicability to Maine Yankee. On November 16, 1992 the review of a report concerning the temporary disabling of Emergency Core Cooling System (ECCS) subsystems during valve stroke testing resulted in the determination that the report was potentially applicable to Maine Yankee and it was forwarded to the Operations Department for formal evaluation. On December 2, 1992 the Operations Department concluded that for a brief period of time, during the stroke testing of either of the normally open ECCS pump minimum-flow recirculation valves SIA-M-53 or SIA-M-54, both trains of the ECCS Low Pressure Safety Injection and Containment Spray subsystems must be considered inoperable. <br /><br /> The minimum flow recirculation valves have historically been tested on a monthly basis in conjunction with the ECCS valve tests. <br /><br /> The cause of this event is considered to be the failure of the original Technical Specification license submittal to allow for surveillance testing of the minimum-flow recirculation valves. The surveillance is required by Maine Yankee Technical Specifications. There are no exceptions in the LCO for ECCS that specifically allow this testing and recent NRC interpretations concluded that this condition is reportable under 10CFR50.73. <br /><br /> In order to minimize the period of time during which the minimum-flow recirculation line is isolated yet tested frequently enough to provide assurance of the valve's operability, Maine Yankee has changed the frequency of the valve stroke test from a monthly basis to a quarterly basis.
3091993015 | Maine Yankee | 07/16/1993 | 08/16/1993 | 9308190263 | <strong>Emergency Core Cooling System (ECCS) Valves Found Unlocked</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1993, as a result of a design review of the component cooling valves, Maine Yankee ascertained that 6 unlocked manual valves were critical to the proper operation of ECCS. This conclusion was a result of the final phase of a comprehensive review detailing ECCS design requirements for proper alignment and locking of valves as required by Technical Specifications. All 6 valves were in their proper position and administratively controlled. The valves were subsequently locked and controlling procedures were revised. <br /><br /> The program for identifying ECCS valves requiring locking devices is now complete for all systems. An ECCS valve database has been established that explains the basis for all ECCS valve positions to meet the intent of Technical Specifications.
3091993016 | Maine Yankee | 08/04/1993 | 09/06/1993 | 9312300176 | <strong>Multiple 480 Volt Breaker Trips Caused RMS-9 Trip Devices</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted in accordance with two other reporting requirements: <br /><br /> 1. Written report for 10 CFR Part 21 <br /> 2. Special report to the commission as required by Technical Specification 3.23 remedial action for P-4, Electric-driven fire pump, being inoperable for greater than 7 days. <br /><br /> On July 30, 1993, Maine Yankee (MY) was cooling down in preparation for refueling. At 1022 hrs. while in the transthermal condition, a 480 volt ground alarm was received and P-29D service water SW! pump P! tripped. The pump's air circuit breaker ACB! had opened, causing a SW low pressure alarm, and an operator immediately started a standby pump. <br /><br /> Normally a single ground fault will not actuate the RMS-9 device, which serves as an overcurrent protection on the breakers in the ungrounded 480 volt buses. This device was designed with long-time/short-time trip functions for motor control circuit (MCC) loads and instantaneous trip functions for motor loads, chosen to coordinate with the upstream and downstream protective devices. This coordination ensures that an overcurrent condition on a load would not result in de-energizing the entire bus or any upstream load. The RMS-9 trip device was certified by GE as a suitable replacement for the EC trip units that were originally installed in GE AK circuit breakers. The RMS-9 trip devices were installed in all AK-25 breakers at MY for both safeguards and non-safeguards 480 volt buses. There are eight AK-25 circuit breakers which control loads required to mitigate an accident. These include 4 (2 on each of two trains) service water pumps (which provide the ultimate heat sink for engineered safeguards), and 4 (2 on each of two trains) which feed various instrumentation, valves and other equipment necessary for engineered safeguards. In addition one breaker feeds an electric driven fire pump and one is the output breaker of an auxiliary diesel generator which is used to meet 10 CFR Part 50 Appendix R requirements.
3091993017 | Maine Yankee | 08/15/1993 | 09/20/1993 | 9309280168 | <strong>Emergency Diesel Generator Voltage Sensing Relay Wiring Discrepancy</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is being submitted to supply information related to the discovery of a condition which deviates from the electrical separation design criteria specified in Main Yankee's Final Safety Analysis Report. <br /><br /> On August 15, 1993 while performing refueling shutdown protective relay preventative maintenance, an emergency diesel generator output breaker voltage relay discrepancy was discovered. Further review also revealed that both the discrepant relay and the corresponding relay on the other emergency generator shared a common coil circuit ground return wire. Although the use of a common ground return wire complied with the AEC General Design Criteria when the plant was licensed and thus is within the plant's design basis, its existence represents a deviation from the electrical separation design criteria specified in Maine Yankee's Final Safety Analysis Report. <br /><br /> The cause of the event is a discrepancy in the plant's original design. A temporary modification has been implemented to provide a separate ground return path for each relay and a design change will be processed to make the change permanent. Screening criteria was developed and implemented to determine if any similar circuits shared a common ground return wire. No similar wiring problems were identified.
3091993018 | Maine Yankee | 09/03/1993 | 10/03/1993 | 9310070281 | <strong>Number of Defective Tubes in #3 S/G Greater than TS 4.10 Limit</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1993, during eddy current testing of #3 steam generator tubes, Maine Yankee found 7 defective tubes in a 688 tubes sample. Plant Technical Specifications 4.10 requires reporting of this condition. <br /><br /> The root cause of this event is considered to be general corrosion or corrosion cracking due to contaminants and stresses. <br /><br /> The inspection sample was expanded to include all unplugged tubes in #3 steam generator. <br /><br /> All defective tubes were plugged.
3091993019 | Maine Yankee | 09/28/1993 | 10/28/1993 | 9311020171 | <strong>Degraded Service Water Pump Found During Flow Rate Testing</strong><br /><i>Abstract:&nbsp;</i>On September 28,1993, while in a refueling outage, Maine Yankee determined that one of four available Service Water pumps (P-29A,B,C,D) did not deliver sufficient flow capacity to meet the design basis accident analyses. <br /><br /> Service Water flow tests were conducted on September 23, 1993 after installation and functional testing of new Service Water flow instrumentation. On September 28,1993, after analyzing the new data, it was determined that P-29B was degraded. P-29B was declared inoperable.<br /><br /> The safety significance of this event is that at power, if train A (P-29A & P-29C) is lost during a design bases accident and one B train pump, P-29D, was out of service, then only P-29B would be available to remove heat from the component cooling trains. <br /><br /> P-29B is scheduled to be overhauled. The cause of the pump degradation will be determined from overhaul results.
3091993020 | Maine Yankee | 10/12/1993 | 11/15/1993 | 9312020119 | <strong>Premature Entry Into Power Operating Condition</strong><br /><i>Abstract:&nbsp;</i>This informational LER is submitted to document events related to a deviation from the Technical Specification requirements for entry into the Power Operation Condition (condition 7). On October 11, 1993 while returning to power operations following a refueling outage, condition 7 was unintentionally entered prior to Technical Specification prerequisites for the condition being completed. <br /><br /> Entry into the Power Operating Condition (condition 7) is defined in the plant's Technical Specification as occurring when the reactor is critical and indicated power on the Power Range Nuclear Instrumentation (PRNI) exceeds 2%. At the time of the event, operators were relying on Wide Range Nuclear Instruments for power level indication and they were not aware that Technical Specifications required that PRNI be used for determining entry into the Power Operating Condition. Plant Technical Specifications also require the establishment of the three auxiliary and emergency feedwater flow paths prior to entry into the power operating condition. Prior to establishment of the final emergency feedwater flow path, 2% power as indicated on the PRNI digital volt meter was exceeded. <br /><br /> The cause of this event is a failure to recognize that plant procedures did not incorporate the technical specification definition of the power operating condition. In order to prevent recurrence, plant procedures have been revised to specify that PRNI shall be used to determine the 2% power point of entry into the Power Operating Condition, The need for providing additional guidance to operators concerning the power level indications to be observed through each segment of the operating range will also be evaluated.
3091993021 | Maine Yankee | 11/04/1993 | 12/04/1993 | 9312100075 | <strong>CEA Position Deviation Alarms Disabled</strong><br /><i>Abstract:&nbsp;</i>On 11/4/93 with the plant operating at 100% power, Control Room Operators (CRO) were conducting monthly surveillance Control Element Assembly (CEA) exercising. This was the first such monthly surveillance since startup following a refueling outage. The objective of the surveillance is to satisfy the Technical Specification (TS) requirement to verify the operability of the reed switch and pulse counting CEA position indicating systems and to verify both pulse counting and reed switch position deviation alarms. At the beginning of the surveillance, operators were aware that an intermittent malfunction had rendered the reed switch CEA position deviation alarm inoperable. <br /><br /> During the surveillance it was discovered that the CEA pulse counting deviation alarm was also inoperable. Whenever the reactor is critical, Technical Specification 3.10 "CEA Group Power Distribution, Moderator Temperature Coefficient Limits and Coolant Conditions", requires: "If the CEA deviation alarms from both the computer pulse counting system and the reed switch indication system are not available, individual CEA positions shall be logged and misalignment checked every 4 hours". The reactor was taken critical on 10/8/93. <br /><br /> Investigation determined that the rod position sensing system (RPSS) cards were removed for troubleshooting during the refueling outage on 10/1/93, thus disabling the required pulse counting system alarm functions. Since both pulse and reed CEA position alarm functions were disabled between 10/8/93 and 11/4/93 without individual CEA positions being logged and checked for misalignment every 4 hours, the plant was in noncompliance with Technical Specification 3.10 during this time frame. <br /><br /> The immediate corrective action was to reinsert the RPSS cards and restore the alarm function of pulse CEA system. <br /><br /> The CEA position indication system was operable throughout this event. Without the CEA deviation alarms, Operators would not have received immediate alarm notification if a CEA were to become misaligned. This is of minimal safety consequence since numerous other non-alarm indicators were available to alert the Operators to the misalignment. <br /><br /> An event evaluation is ongoing but suggests the root cause to be human error in failure to comply with existing administrative controls for removing RPSS cards for troubleshooting.<br /> .
3091993022 | Maine Yankee | 11/10/1993 | 11/29/1993 | 9312090019 | <strong>Control Room Ventilation Trains Inoperable Due to Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>This LER is written to provide information about preventative maintenance of control room ventilation which requires entry into Technical Specification 3.0.A.2. <br /><br /> On November 10, 1993, both trains of Control Room Ventilation were declared inoperable for a brief period of time. The inoperability of both trains was a result of preventative maintenance (PM) for filter replacement, internal to "B" train air handler (AC-1B). Because of damper configuration, it is impossible to externally isolate the AC-1B air handler and maintain a recirculation path. When AC-1B is opened, both trains via FN-11A or FN-11B have direct paths to the atmosphere, which bypasses the recirculation flow. <br /><br /> The consequences of this event, which occurs semi-annually, is minimal since the loss of both trains is of short duration (less than 1 hour - no shutdown initiated) for the PM.
3091993023 | Maine Yankee | 12/02/1993 | 05/25/1994 | 9406010085 | <strong>PCC/SCC Outside Design Basis Due to Continuous Venting Through NNS Piping</strong><br /><i>Abstract:&nbsp;</i>Maine Yankee has identified discrepancies in the operation of safety class to non-nuclear safety class boundary valves in both the Primary Component Cooling (PCC) system and Secondary Component Cooling (SCC) system. These closed loop systems provide redundant cooling for Emergency Core Cooling System components, as well as, selected non- safeguards components. In the Secondary Component Cooling system, three manual vent valves from the pump discharges and heat exchanger to the top of the vented surge tank have been procedurally throttled open when SCC was required to be operable. These SCC vent paths are through a portion of non-nuclear safety class piping. In the Primary Component Cooling system, one manual vent valve from the pump discharge line was procedurally maintained open. Operation of the systems with these vent valves open has been determined to be outside the systems' design basis. <br /><br /> The SCC and PCC systems have been operated in this fashion with no loss of functionality. Based on the potential for these systems becoming inoperable during a seismic event, Maine Yankee has administratively tagged these valves shut pending resolution of this issue. The SCC and PCC systems remain operational with these valves shut. <br /><br /> Maine Yankee is continuing to evaluate various long term actions to correct this problem, which may include upgrading the existing vent lines, or upgrading other piping to use as a continuous vent path. Maine Yankee is also developing improved guidance to provide consistent evaluations of SC/NNS boundaries.
3111993001 | Salem 2 | 12/09/1992 | 02/09/1993 | 9302170241 | <strong>2H 4KV Group Bus UF Protection Inop. Due To Mispositioned Relay Test Switch</strong><br /><i>Abstract:&nbsp;</i>From 12/9/92, until discovery at 1100 hours on 1/12/93, under-frequency (UF) protection for 2H 4KV Group Bus was unknowingly inoperable due to the bus UF relay test (knife) switch being left in the "OPEN" position following the monthly under-voltage (UV)/UF surveillance test of the bus. The Technical Specification (T/S) Action Statement was entered. The subject relay test switch is located in locked electrical cubicle 2HAD. The 2H 4KV Group Bus monthly surveillance was completed at 1317 hours (same day) (including closure of the test switch); thereby, the Action Statement was exited. The root cause of this event is personnel error due to a technician's failure to comply with a surveillance procedure. The procedure requires closing the subject test switch following testing and to "ENSURE" that all 2H Group Bus UV and UF test switches are closed. Disciplinary action has been taken with the technician involved with the 12/9/92 surveillance of the 2H Bus UF relay. This event has been reviewed by Maintenance Department management and will be reviewed with applicable department personnel. The Group Bus UV and UF monthly functional test surveillance procedures will be revised to provide for independent verification of the test switch closure. .
3111993002 | Salem 2 | 01/28/1993 | 02/26/1993 | 9303040255 | <strong>Manual Rx Trip From 100% Power Upon Trip of Both Steam Generator Feed Pumps</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 1/28/93, the low suction pressure alarm for both Steam Generator Feedwater Pumps (SGFPS) was received. Both pumps tripped on low suction pressure. A manual reactor trip was then initiated. The Unit was stabilized in Hot Standby. Prior to the loss of the SGFPS, a technician was connecting a brush recorder to the inputs and output of the Steam Generator Feed Pump (SGFP) Master Controller to troubleshoot observed spikes on all 4 Steam Generator feed flow instrument channels. The root cause of this event is equipment failure. The SGFP master controller module test jack was sufficiently loose to allow the weight of the troubleshooting lead to bring the threads of the troubleshooting test lead into contact with the module chassis. This created an electrical short between the controller signal common and chassis ground, which produced an erroneous maximum speed demand signal. Flow through the pumps then increased resulting in the low suction pressure and the pump trips. The loose SGFP master controller test jack was repaired and other jacks in the SGFP speed control loop circuitry were inspected and repaired as required. The other Hagan protection channel test connections (both Salem Units) are being checked during the protection channel monthly functional surveillance. The Hagan process channel test connections, both Salem Units, will be checked for looseness. Engineering is reviewing whether changes to the test jacks are needed to prevent event recurrence.
3111993003 | Salem 2 | 01/31/1993 | 02/26/1993 | 9303040157 | <strong>Tech. Spec. 3.0.3 Entry; Inoperability of Both Boric Acid Storage Tank's Level Indication</strong><br /><i>Abstract:&nbsp;</i>On 1/31/93, t 2220 hours, the level indicator of 21 BAST was declared inoperable due to false high level indications. 22 BAST was undergoing batching operation at the time. Therefore, Action 3 of Technical Specification Table 3.3-11 was not met, and the action associated with Technical Specification 3.0.3 was entered. Technical Specification 3.0.3 was exited on 1/31/93, at 2242 hours, upon restoration of 21 BAST level indication to service. The root cause of this event is "Design, Manufacturing, Construction/Installation" of the BAST level indication system. BAST level indication failures have been a recurring problem at both Salem Units. They have been determined to be due to bubbler tube blockage. The Unit 2 21 BAST bubbler is scheduled for cleaning. The Unit 2 22 BAST bubbler has been cleaned. The corresponding Unit 1 11 and 12 BAST's and the bubbler tubes of each tank have been inspected and cleaned. In addition, the bubbler tube nitrogen flow rates of both Salem Units have been readjusted to 3 scfh, to minimize boric acid precipitation. A design change is being developed which includes reducing BAST boron concentration. This will help minimize boron precipitation in the level indicator bubbler tubes. System Engineering is continuing to monitor BAST level indication failures to determine adequacy of current corrective action.
3111993004 | Salem 2 | 02/06/1993 | 03/05/1993 | 9303110188 | <strong>Tech Spec. 3.0.3 Entry: Inoperability of Both Turbine First Stage Pressure Channels.</strong><br /><i>Abstract:&nbsp;</i>At 2105 hours, on 2/6/93, Tech. Spec. 3.0.3 was entered due to operation outside Tech. Spec. Table 3.3-3 Action 14. Both main turbine first stage impulse pressure indication channels (PT-505 and PT-506) were indicating false readings. PT-505 and PT-506 provide turbine power input for plant control during power operation. PT-505 was indicating downscale and PT-506 was indicating upscale. This was first observed via automatic rod insertion. Rod motion was stopped by placing rod control in manual. The PT-505 and PT-506 indications returned to normal within approximately one minute following a change in the building ventilation lineup which increased ambient air temperature around the sensing line. Satisfactory channel functional checks showed the instruments operable and at 2109 hours (same day), Tech. Spec. 3.0.3 was exited. The root cause of this event is equipment failure. Sensing line protection from cold environment conditions was found to not be adequate. When this event occurred, the outside ambient temperature was less than 20 degrees F.<br /><br /> Missing insulation from the channels' transmitter sensing lines (which will be replaced) and the PT-506 heat trace had failed (which will be repaired) was identified. An Operations Department Night Order Book entry has been made to preclude chilling the PT-505 and PT-506 transmitter sensing lines. The administrative program for preparing Salem Station for Winter operation will be reviewed. Revisions will be incorporated as appropriate.
3111993005 | Salem 2 | 03/16/1993 | 04/15/1993 | 9304190317 | <strong>Reactor Trip From 100% Power Due to 22 SGFP Trip on Low Suction Pressure</strong><br /><i>Abstract:&nbsp;</i>On 3/16/93, at 1106 hour , subsequent to a 22 Steam Generator Feedwater Pump (SGFP) trip on low suction pressure, a reactor trip occurred on 24 Steam Generator (SG) low-low level. Condensate Polisher (CP) vessel regeneration was in progress. Following the reactor trip, 24 SG level increased rapidly (due to the 24BF19 valve failing open) and feedwater isolation initiated upon 24 SG level reaching the high-high level setpoint. 24 SG was then isolated. The root cause of the reactor trip is "Management/Quality Assurance Deficiency". Less than timely actions to correct a leaking CPS valve packing and failure to mitigate increasing leakage resulted in failure of a differential pressure switch. This led to the 22 SGFP trip and subsequent Reactor Trip. The failed differential pressure switch was causing premature opening of 24CP2 (Feed and Condensate Inlet Valve). A pressure transient occurred resulting in a sudden drop of SGFP pump suction pressure sufficient to actuate one of the SGFP suction pressure trips. The differential pressure switch failed due to water intrusion. An aggressive leak reduction program is in place. The circumstances surrounding the events in this LER will be reviewed with applicable station personnel for increased sensitivity to mitigation of leaks. The planning effort in support of the 24CP14 valve repair will be reviewed. Additional corrective action will be taken based on the results of this review. The failed CP System differential pressure switch and its flex conduit were replaced. The 24CP14 packing leakage will be repaired .
3111993006 | Salem 2 | 04/15/1993 | 05/13/1993 | 9305210251 | <strong>Train "A" Safety Injection System Signal During Response Time Testing.</strong><br /><i>Abstract:&nbsp;</i>At 1002 on 4/15/93, an unexpected Train "A" Safety Injection system (SI) signal occurred due to STEAM LINE DIFFERENTIAL PRESSURE when the Solid State Protection System (SSPS) Train "A" Input Error Inhibit Switch was positioned to "INHIBIT", as required by Step 8.6 of Procedure 2IC-18.4.004, "RESPONSE TIME OF SSPS LOGIC - SAFETY INJECTION, TRAIN B". The Reactor was defueled and the Safety Injection (SI) Pumps were cleared and tagged. Steam pressure transmitters were being replaced and the STEAM LINE DIFFERENTIAL PRESSURE bistables were tripped. Plant components, not cleared and tagged, functioned properly. Prior to performing 2IC-18.4-004, the status of the tripped bistables was discussed. This event resulted from the particular operating characteristics of the subject switch. Positioning the switch slowly, which occurred during this event, caused a delay between removing the signal block and disabling the inputs, which allowed the logic to initiate the SI signal. The switch is operating within acceptable tolerances. 2IC-18.4.004 will be revised, by 6/18/93, to require the SSPS train Mode Selector Switch be positioned to "TEST" prior to positioning the corresponding Input Error Inhibit Switch to "INHIBIT" and will include a caution that under certain conditions a Reactor trip signal may be initiated whenever the Input Error Inhibit Switch is positioned to "INHIBIT". In addition, other similar SSPS procedures on both units will be revised prior to their next use. Station procedures for manipulating SSPS switches will be reviewed and appropriately revised.
3111993007 | Salem 2 | 05/28/1993 | 06/25/1993 | 9307010285 | <strong>Manual Reactor Protection System Actuation Following Dropped Rods of Control Rod Bank C Group 1.</strong><br /><i>Abstract:&nbsp;</i>On 5/28/93, at approximately 1812 hours, during startup activities following completion of the unit's seventh refueling/maintenance outage, all four rods of Control Rod Bank C Group 1 unexpectedly dropped fully into the reactor core. At approximately 1814 hours, the reactor was manually tripped and the emergency operating procedure entered. The unit remained in MODE 3 (HOT STANDBY) during the entire event. This event did not affect the health and safety of the public. The rods dropped due to a degraded signal from the regulation board which caused discontinuation of firing orders to the C1 control rod group. This resulted from intermittent component failure of the Rod Control System (RCS) stationary "B" control group firing circuitry regulation card in the RCS 21AC Power Cabinet. The card was replaced restoring RCS operability for Control Rod Bank C Group 1 rods. In addition, all cards in the power cabinets have been removed, visually inspected, satisfactorily tested, and reinstalled. <br /><br /> Following NRC concurrence, Unit 2 post refueling/maintenance outage startup testing will continue. An event involving a potential RCS single failure concern (common to Units 1 and 2), identified on June 4, 1993, is being reported in a separate LER.
3111993008 | Salem 2, Salem 1 | 05/27/1993 | 08/26/1993 | 9309030268 | <strong>Rod Control System Design Basis Concern (both Salem Units).</strong><br /><i>Abstract:&nbsp;</i>During Unit 2 Reactor startup activities, following the unit's 7th refuel outage, it was determined on 6/4/93 that a postulated single failure concern existed where failure of one Rod Control System slave cycler decoder card, in conjunction with a rod motion command signal, may cause an unplanned Rod Control Cluster Assembly (RCCA) withdrawal. At 1734 hours, all control rods were inserted, the Reactor trip breakers were opened, and the Unit was stabilized in MODE 3. On 5/27/93, at 1844 hours, rod 1SA3 had withdrawn approximately 15 steps from fully inserted following a manual insertion command. Rod control power was then deenergized to fully insert the rod. The RCS single failure concern is attributed to RCS design. 1SA3 withdrew as the result of inappropriate current orders to the RCCA. Integrated circuit chips on two slave cycler decoder cards had failed due to the relay driver circuit card connector Pin No. 4 not making electrical contact with the surge suppression diode. Pin No. 4 was repaired and the slave cycler cards were replaced to restore operability of rod 1SA3. An additional corrective action was installation of suppression diodes on the rod step counters of the RCS circuitry, of each unit, to mitigate consequences of an open or bad connection on the relay driver circuit card connector pin No. 4. All Unit 2 RCS logic cards were replaced and satisfactorily tested and all RCS Power Cabinet cards were pulled, visually inspected, and retested satisfactorily. On 6/29/93 Unit 2 was taken critical.
3111993009 | Salem 2 | 06/22/1993 | 07/19/1993 | 9307280092 | <strong>ESF Actuation: Automatic Start of Motor Driven Auxiliary Feedwater Pumps.</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1993, at 0326 hours, 21 and 22 motor driven Auxiliary Feedwater (MDAFW) Pumps automatically started due to 21 and 22 Steam Generator Feed Pumps (SGFPs) tripping on low suction pressure (an Engineered Safety Feature). Both SGFPs had been running in support of Condensate System cleanup. At the time, Condensate Polishing System 24 demineralizer (DM) vessel was being restored to service. The SGFPs tripped during the tagging release of the 24 DM vessel. Investigation revealed that the reduced SGFP suction pressure was a direct result of a pressure transient induced during the 24 DM vessel tagging release. The root cause of this event is "Management/QA Deficiency". Adequate control was not maintained over concurrent testing performed during the 24 DM vessel maintenance work such that the 24CP2 arming controls remained "OPEN" and was not considered when restoring the vessel to service. A Chemistry Department troubleshooting procedure is being developed. In the interim, a temporary revision to an existing procedure was completed. <br /><br /> This procedure provides an automatic sequence that refills the vessel and details specific valve manipulation. The circumstances surrounding the cause of this event and the ways in which it could have been prevented will be reviewed with applicable Chemistry Department personnel. Also, the requirement to employ plans in support of testing/troubleshooting activities will be stressed. This event will be reviewed by the Nuclear Training Center for lessons learned.
3111993010 | Salem 2, Salem 1 | 06/29/1993 | 08/26/1993 | 9309030251 | <strong>T/S 3.0.3 Entries; More Than One Inoperable Analog Rod Position Indicator Per Bank.</strong><br /><i>Abstract:&nbsp;</i>This LER addresses Technical Specification (T/S) 3.0.3 entries due to inoperability of more than one control rod Analog Rod Position Indication (ARPI) per control rod bank. On 6/29/93, at 1200 hours, Unit 2 T/S 3.0.3 was entered for rods 1B2, 2B1, and 2B4. At 1255 hours, reactor shutdown was initiated in accordance with T/S 3.0.3. At 1345 hours, the shutdown was terminated and T/S 3.0.3 was exited after control rods 2B4 and 2B1 ARPIs were restored to specification. At 1410 hours, the T/S Action Statement was exited after rod 1B2 was restored to specification. On 6/30/93, at 0217 hours, Unit 2 T/S 3.0.3 was entered for rods 1SB2 and 1SB4. At 0259 hours, T/S 3.0.3 was exited when 1SB4 returned to specification due to thermal soak. At 0304 hours, the T/S Action Statement was exited when 1SB2 was adjusted to specification. On 7/16/90, at 2300 hours, Unit 1 T/S 3.0.3 was entered for rods 1D3, 2D1, 2D3, 2D4 and 2D5. At 2350 hours, reactor shutdown was initiated in accordance with T/S 3.0.3., On 7/17/93, at 0330 hours, the shutdown was terminated and T/S 3.0.3 was exited after rods 2D1, 2D3, 2D4, and 2D5 were restored to specification. The root cause of these events is system design. The ARPI System electronic settings experience drift due to temperature susceptibility of the system coil stacks. The signal conditioning modules of the affected rods were adjusted. System Engineering has developed an ARPI trending data base to identify problem electronic modules. The industry Rod Control User's Group has recognized an industry-wide problem with ARPI System drift. Recommendations from this group and the vendors will be used to develop appropriate action.
3111993011 | Salem 2 | 10/19/1993 | 06/15/1994 | 9406290038 | <strong>Inoperability Of Radioactive Liquid Effluent Monitors Due To Use Of Incorrect Source Decay Table Value.</strong><br /><i>Abstract:&nbsp;</i>Following calibrations in 1988, Radiation Monitoring System (RMS) channels 2R13 A,B,C were inoperable due to their efficiency being adjusted to a reduced level. The channels' alarm setpoints remained unchanged. This was caused by an incorrect Ba-133 half-life to generate standard source decay tables for these channels. 2R18, 2R19A,B,C,D, and 2R37 were also rendered inoperable in an identical manner. The incorrect Ba-133 half-life value was most likely obtained from industry reference material. Use of the incorrect value until event discovery is attributed to management deficiency with a major contributor of inadequate communication between site groups. 2R13A,B,C channels were calibrated using the correct source decay value and returned to service. operability of the other subject channels was restored in 1991. An internal notice has been issued regarding the incorrect Ba-133 half-life. Reference material has been revised to include source decay tables for TS-related channels and reference the use of controlled design basis data.
3111993012 | Salem 2 | 10/30/1993 | 11/23/1993 | 9312060021 | <strong>T/S 3.0.3 Entry; Inoperability of 21 BAST Level Indication While 22 BAST Out of Service.</strong><br /><i>Abstract:&nbsp;</i>At 0901 hours on 10/30/93, 21 Boric Acid Storage Tank (BAST) level indicator was declared inoperable due to false level indication. At the time, 22 BAST was out of service therefore, Technical Specification (TS) Table 3.3-11, Action 3, was not met, and TS 3.0.3 was entered. TS 3.0.3 was exited, at 0930 hours (same day), upon return of 22 BAST to normal lineup. This event resulted from boron blockage in 21 BAST level indicator bubbler tube. The tube was blown down and at 1051 hours (same day), 21 BAST was returned to service. The root cause of this event is design of the BAST level indication system. A design change, including reducing the BAST boron concentration to 4% to minimize boron precipitation in the tank level indicator bubbler tube, is being installed during the current Unit 1 refueling outage and is scheduled for installation on Unit 2.
3111993013 | Salem 2, Salem 1 | 12/02/1993 | 12/30/1993 | 9401110199 | <strong>Non-Valid Failure of 2C Diesel Generator with Subsequent Reactor Shutdown.</strong><br /><i>Abstract:&nbsp;</i>On 12/2/93, 2C Diesel Generator (D/G) was declared inoperable due to cracking in 3R cylinder liner. This was discovered while investigating a jacket-water leak following a successful post-maintenance operability run. The flange portion of the cylinder liner had several through-wall radial cracks and the flange had separated completely around its circumference from its cylindrical base. Repairs to the D/G could not be completed within the 72 hours allowed by Technical Specifications and on 12/3/93 a controlled shutdown was initiated and Mode 5 (cold shutdown) was entered on 12/5/93, at 1944 hours. 2C D/G was disassembled to check other cylinder liners for signs of cracking. Because 1B D/G (Salem Unit 1) was the only other Salem D/G with Canadian Allied Diesel (CAD)-supplied liners, it was disassembled and inspected. The liners of 1B D/G did not have any relevant indications. The root cause of this event is attributed to "Design, Manufacturing, Construction/Installation," as per NUREG-1022. The most plausible cause of the 3R cylinder liner failure was a combination of lack of liner flange flatness and perpendicularity, under-sized upper o-ring groove radius and possible presence of a flaw in the upper o-ring groove area. A contributor to this failure was less than adequate definition of critical characteristics at time of liner dedication (flange flatness, flange perpendicularity, and upper o-ring groove radius). All previously installed CAD liners have been removed from Salem D/Gs and replaced with ALCO liners. Appropriate changes will be made to the receipt, inspection, and maintenance activities involving D/G cylinder liners.
3111993014 | Salem 2 | 12/28/1993 | 01/27/1994 | 9402030067 | <strong>ESF Actuation & Resultant Pressurizer Overpressure Protection System Channel I Actuation.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 12/28/93, at 0850 hours, Reactor Coolant System (RCS) 22 Accumulator outlet valve 22SJ54 unexpectedly opened and injected an estimated volume of 1735 to 2640 gallons (2200 ppm boric acid) into the RCS. The resultant RCS pressure transient actuated Pressurizer overpressure Protection system (POPS) Channel I, causing Pressurizer Relief Valve 2PR1 to open at 375 psig. Highest indicated RCS pressure was approximately 372 psig. RCS pressure decreased to approximately 280 psig prior to being recovered by the Pressurizer heaters. This event occurred when test switch TS-603 was operated, per procedure S2.OP-ST.SSP-0010(Q), Solid State Protection System (SSPS) Train B Slave Relays Testing. Plant equipment responded properly to this event and TS-603 was reset to allow reclosure of 22SJ54. The root cause of this event is Defective Procedure, per NUREG-1022. S2.OP-ST.SSP-0010(Q) did not indicate that operation of TS-603 would result in opening of 22SJ54. Procedures have been revised to identify test switches which affect SJ54 valves and require that the appropriate SJ54 breaker be cleared and tagged. Integrated Operating Procedure IOP-6 (Hot Standby to Cold Shutdown) has been revised (both Units) to tag all SJ54 valve breakers when RCS pressure is less than or equal to 1000 psig. A detailed technical review of all SSPS slave relay testing procedures will be performed. Procedural inadequacy identified with IOP-6 and S2.OP-ST.SSP-0010(Q) and the procedure identified in LER 311/92-005-00, will be examined to determine if any generic implications exist.
3131993001 | Arkansas 1 | 03/05/1993 | 03/31/1993 | 9304060250 | <strong>Reactor Trip Initiated By a Turbine Trip Which Was Caused By The Occurrence Of Two Grounds On The 125 VDC System</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1993, at approximately 1414, ANO-1 experienced a reactor trip which was initiated by the Anticipatory Reactor Trip System (ARTS) as a result of a main turbine trip. The plant post trip response was normal and no major equipment malfunctions were experienced. The reactor was returned to criticality at approximately 0726 on March 7, 1993 and the main turbine generator was tied to the grid at 0345 on March 8. The trip was determined to have been caused by the simultaneous occurrence of two grounds on the 125 VDC bus D-01. One of the grounds was on the Main Feedwater Pump control circuitry and the other was on the turbine trip circuitry. The two grounds created a short and resulted in actuation of the turbine trip circuitry, causing a turbine trip which initiated a reactor trip. The turbine trip circuitry ground was caused by vibration induced fretting where the wiring entered the cabinet. No grommet was installed in the cabinet. The cause of the MFP circuit ground is unknown. The grounds were repaired and grommets installed. Turbine trip circuit wiring subject to vibration in the HP turbine area was inspected for similar conditions.
3131993002 | Arkansas 1 | 03/09/1993 | 04/02/1993 | 9304080261 | <strong>Circuit Breaker Malfunction Due To Procedural Deficiency Results In ESF Bus Being De-energized and Emergency Diesel Generator Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1993, at 1548 hours, ANO-1 was operating at 100 percent power when green train 4160 volt Engineered Safeguards (ES) and non-ES buses and the 480 volt ES load center were de-energized. During a transfer of power sources from an off-site supplied Startup Transformer to the Unit Auxiliary Transformer, the circuit breaker from the Startup Transformer did not automatically open when the circuit breaker to the Unit Auxiliary Transformer was closed. This resulted in high circulating currents due to transformer voltage differences that caused both breakers to open. An Emergency Diesel Generator started and supplied ES loads. Non-ES loads were re-powered from the Startup Transformer. The unit was run back to 63 percent power due to a condensate pump being de-energized and decreasing main condenser vacuum. Return to a normal electrical line-up occurred at 1940 hours. The circuit breaker to the Unit Auxiliary Transformer had not been completely racked up. Excessive auxiliary relay contact clearances resulted in failure to provide a signal that the breaker had closed. The root cause has been attributed to a procedural deficiency in that precautions concerning breaker racking-up evolution were inadequate. Corrective actions include procedure revisions and personnel training.
3131993003 | Arkansas 1 | 09/30/1993 | 10/27/1993 | 9311020010 | <strong>Low Pressure Injection Pump Potentially Incapable Of Performing Its Recirculation Mode Function Due To Improper Pump/Motor Coupling Which Resulted From Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1993, with the plant in cold shutdown, an engineering evaluation was completed which indicated that the "B" Decay Heat Removal/Low Pressure Injection pump (P-34B) might have been incapable of performing its recirculation mode function following a Loss of Coolant Accident (LOCA). This condition may have existed from May 24, 1993, while the plant was at power, until plant shutdown on September 9, 1993. On September 9, P-34B was declared inoperable due to high motor end bearing temperature. The engineering evaluation to determine past operability had been initiated on September 10 after identifying that the coupling hub on the pump shaft was installed approximately 0.3 16 inches too far toward the motor during the previous refueling outage (1R10). The evaluation concluded that a greasing evolution of the coupling hub on May 24, in conjunction with the coupling misalignment, created the degraded pump condition. P-34B was repaired and returned to service on September 10. The root cause of this condition was determined to be inadequate procedural guidance. Corrective actions include reviewing and revising appropriate maintenance procedures, as necessary.
3131993004 | Arkansas 1 | 10/04/1993 | 10/29/1993 | 9311010183 | <strong>Inadequate Procedural Instructions Caused A Circuit Breaker Trip Which Resulted in ESF Bus Being De-Energized and Emergency Diesel Generator Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1993, at 1647 hours, ANO-1 was in cold shutdown conditions when the red train 4160 volt Engineered Safeguards (ES) bus and 480 volt load center were unintentionally de-energized. In preparation for integrated engineered safeguards actuation system (ESAS) testing, the test leads for the red 4160 volt ES bus feeder breaker were inadvertently shorted which completed the trip circuit for the feeder breaker. This resulted in the feeder breaker opening which de-energized the red train 4160 volt ES bus and associated vital 480 volt ES load center. The emergency diesel generator (EDG) automatically started due to the undervoltage condition of the 4160 volt bus; however, the EDG output breaker failed to close. The EDG was secured. Prior to the ESAS testing, the green train had been established as the protected train, and the green train of Decay Heat Removal (DHR) was available throughout the event. The root cause of this event has been attributed to a procedural deficiency in that the instructions for the setup of the ESAS test equipment were inadequate. Corrective actions include procedure revision and discussions of lessons learned with the appropriate maintenance and engineering personnel. Trouble shooting revealed that the EDG output breaker failed to close because of a faulty latch checking switch. The output breaker was repaired and returned to an operable status.
3131993005 | Arkansas 1 | 10/14/1993 | 12/16/1993 | 9312220192 | <strong>Breaches In The Reactor Building Sump Integrity Which Resulted From An Inadequate Design Review Created The Potential For Degraded Low Pressure Injection, High Pressure Injection And Reactor Building Spray System Flows During The Recirculation Mode of Operation Following A LOCA</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1993, with the plant in cold shutdown, it was determined that the High Pressure Injection, Low Pressure Injection and Reactor Building Spray systems could have been rendered incapable of performing their design basis functions during the recirculation mode of operation following a Loss of Coolant Accident as a result of identified breaches in the integrity of the Reactor Building (RB) sump. The breaches included twenty two unscreened 6 inch long by 3 inch high split pipe openings at the base of the sump curb, four unsealed conduit penetrations in the sump screen, and two tears in the screen which could allow foreign material to enter the sump. The breaches in sump integrity occurred as a result of a modification made to the sump prior to initial power operation by the plant designer. The root cause of the condition was an inadequate review prior to modifying the sump design. Corrective actions were completed prior to startup following 1R11 to correct the deficiencies and restore sump integrity. The design change process in place at the present time is considered adequate to prevent the occurrence of similar events.
3131993006 | Arkansas 1, Arkansas 2 | 10/14/1993 | 11/12/1993 | 9311170040 | <strong>Inadequate Process For Control Of Ventilation System Charcoal Resulted In Operation Prohibited By Technical Specifications Because Samples From Each Installed Batch Were Not Obtained And Analyzed</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1993, it was discovered that testing of charcoal used in ventilation/filtration systems in both units of Arkansas Nuclear One was not being performed as required by Technical Specifications. Charcoal from multiple batches, each having a unique Certificate of Conformance, was installed; however, compliance with the sampling procedure may have resulted in only one batch being sampled and analyzed to verify iodine removal efficiency. Since the sample was not representative of characteristics of the entire filter, surveillance tests did not necessarily verify requirements. Systems involved included ventilation exhaust from Auxiliary Buildings, Reactor Buildings, Penetration Rooms, Auxiliary Building Extension, and Post Accident Sampling System Building. The root cause has been attributed to an inadequate process for control of charcoal in that representative batch sampling and control requirements were not specified. Charcoal in each system will be restored to a single batch configuration and administrative controls will be enhanced. The safety significance of samples not necessarily being representative of all installed batches has been evaluated to be minimal.
3131993007 | Arkansas 1 | 11/22/1993 | 12/21/1993 | 9312280186 | <strong>Radwaste Area Effluent Flowpath Not Continuously Monitored During Release Due to a Separated Sample Line Connection Which Resulted From Inadequate Procedural Guidance.</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1993, at approximately 1400, the radwaste area ventilation effluent flow monitor failed. Therefore, the associated gaseous effluent monitoring channel was declared inoperable. Since the Radwaste Area ventilation system was in operation, alternate sampling equipment was installed and placed in service as required by Technical Specifications. On November 22 at approximately 1430, a Chemist preparing to collect a gas sample discovered that the sample tubing was disconnected from one end of the filter cartridge. This condition resulted in the pump taking its sample from the room instead of the release path, as required. The sample tubing was immediately reconnected. The root cause of this event was inadequate procedural guidance regarding alternate sampling equipment hookup. Procedures for ANO-1 and ANO-2 were revised to include appropriate guidance for sampling equipment hookup. It was verified that no significant radioactive release occurred while the effluent flowpath was unmonitored.
3151993001 | Cook 1 | 03/30/1993 | 04/29/1993 | 9305060359 | <strong>Fuel Handling Exhaust Fan Charcoal Filter Bed Fire Alarm Inoperable Due To Moving Alarm to New Annunciator Location</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1993 new annunciators for the new Dedicated Fire Protection System (RFC-DC-12-3065) were installed in the Unit 1 Control Room. Several existing annunciators were required to be relocated in order to install the new annunciators and human factor the panels. The "Fuel Handling Exhaust Fan Charcoal Filter Fire or Abnormal" annunciator was moved as part of this process to a previously spared annunciator window. <br /><br /> The design change planning process did not identify that the annunciator was associated with Technical Specification (TS) 3.3.3.7. Even though the annunciator's electrical leads had been moved within the TS Limiting Condition for Operation (LCO) Action Statement one hour time limit, the new window's logic card was not installed, effectively, leaving the alarm function inoperable. At the subsequent operations turnover, the oncoming shift identified that two annunciator windows, one TS related and one non-TS related, did not light as expected when tested. The operators determined the problem was within the circuitry and placed the plant in the TS LCO Action Statement which requires the stationing of an hourly fire watch patrol for the area associated with the inoperable fire detection system. It was approximately eleven hours from the time the alarm was rendered inoperable until the stationing of the fire watch.
3151993002 | Cook 1, Cook 2 | 06/09/1993 | 07/09/1993 | 9307160142 | <strong>Assumptions for High Energy Line Break Not Met Due to Use of Low Temperature Thermal Links to Maintain Required Vent Area</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1993, during a review of assumptions used in environmental qualification related analyses, it was discovered that the doors to the turbine-driven auxiliary feedwater pump (TDAFP) room and the adjacent hallway, which are purposely maintained open to prevent a pressurization of the room following a postulated break of the four-inch steam supply line to the TDAFP, a High Energy Line Break (HELB), might close. The subject doors have thermal links, which could melt as the accident progressed, allowing pressurization of the TDAFP room. This situation is contrary to the assumptions used in the HELB analysis as stated in the FSAR. <br /><br /> Immediate corrective action was to block open the subject doors to ensure the design criteria venting area for a HELB was met. Long-term corrective action involves the installation of fusible links of higher temperature ratings on a selected group of fire doors. The fusible links will allow these fire doors to remain open during a potential HELB and will allow the doors to close during a fire.
3151993003 | Cook 1 | 07/02/1993 | 09/02/1993 | 9309090071 | <strong>Fire Watch Patrols not Established per Plant Technical Specifications Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1993 at approximately 1800 hours, the Unit 1 fire detection monitor alarm switch was placed and left in the "off" position. The fire detection monitor alarm switch is a cut out switch for the pyrotronics fire detection system installed throughout the unit and within various site office buildings, In the "off" position, visual and audible alarms associated with the pyrotronic fire detection zones will not alarm in the control room. However, in the event of a fire, a fire system actuation or CO sub 2 header pressurized alarm would still annunciate in the control room for the areas provided with fire suppression capabilities. <br /><br /> Spurious fire alarms had been received and reset throughout the day. The fire system is reset by turning the fire detection system control switch to "off" and then back to the "on" position. At approximately 1800 hours while resetting the fire detection system, the fire detection system control switch was inadvertently left in the "off" position. Compensatory actions required by Technical Specifications were not taken due to the control room operators being unaware of the switch being mispositioned. <br /><br /> The cause of this event is personnel error. Administrative actions have been taken with the involved personnel.
3161993001 | Cook 2 | 02/02/1993 | 03/04/1993 | 9303090565 | <strong>Technical Specification Compensatory Action not Met Due to Personnel Error After the Blocking Open of a Fire Door</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1993, with Unit 2 in Mode 1 (Power Operation), at approximately 1935 hours an employee noted that the fire door to the Pressurizer Heater Transformer Room was standing open with the safety pins installed in the door tracks. This condition makes the fire door inoperable. It was verified that there was no one in the area and the Pressurizer Heater Transformer Room was not being toured by fire watch personnel. The last time that the fire door was known to be closed was at 1422 hours on February 2, 1993, at which time the Pressurizer Heater Transformer Room was removed from a fire watch tour after some work was completed in the area. The exact time when the fire door was left open could not be determined, therefore it must be assumed that the door could have been inoperable for approximately 5 hours with no compensatory measures in place.<br /><br /> For immediate corrective action, the safety pins were pulled and the fire door was closed. <br /><br /> A technical evaluation of the condition concluded that defense-in-depth fire protection adequately protected the fire safety of the plant.
3161993002 | Cook 2 | 02/15/1993 | 03/15/1993 | 9303230208 | <strong>Condenser Evacuation System Sampling Surveillance Missed due to Personnel Error During Surveillance Test Schedule Review</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1993, during a routine review of data, a supervisor could not locate data for the Unit 2 Condenser Air Ejector (CAE) Technical Specification noble gas activity weekly surveillance. After reviewing the logbooks, it was determined that the Unit 2 CAE Technical Specification sample had not been taken. taken. The Unit 2 CAE sample was taken on February 19, 1993 at 1001 hours. No noble gas activity was detected, which is consistent with past sample results. A daily historical printout of the on-line radiation monitor was obtained which showed no abnormal readings. <br /><br /> The cause of the event was personnel error. Attention to detail and self-checking were not applied during the initial review of the surveillance test schedule. <br /><br /> Corrective action involved the sampling of the Unit 2 CAE and taking appropriate administrative action with regards to the individual's lack of attention to detail and self-checking.
3161993003 | Cook 2 | 10/16/1992 | 04/08/1993 | 9304140299 | <strong>ESF Ventilation System Filter Train Damper Control Malfunction Due to Incorrect Solenoid Installation</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1992, with Unit 2 in Mode 5 (Cold Shutdown) a problem was recognized concerning the operation/position of the Engineered Safeguards Charcoal Filter Dampers. An operator on tour discovered that the 2-HV-AES-2 (Train B) charcoal filter face dampers were closed when they should have been open. The Train-A Unit (2-HV-AES-1) had been removed from service (fan breaker was open). This condition should, by design, have automatically placed the Train-B charcoal filter in service by opening the face dampers and closing the two bypass dampers. This event was determined to be reportable on March 9, 1993, as an operation prohibited by Technical Specifications and; an event where an independent train became inoperable in a system controlling the release of radioactive material. This event was caused by a piping error on the instrument air supply to solenoid valve (2-XSO-560) which provides the control air for the damper operation. Upon actuation of a Containment Isolation Phase B (CI-B) signal, both ESF Ventilation Trains start with flow going through the associated charcoal filters. Solenoid Valve 2-XSO-560 actuates from a Train-A CI-B signal, or from the Train A fan being out of service and provides a cross-train feature to reposition the Train-B ESF Ventilation Filter Dampers. The piping and print errors were corrected. The cross-train solenoid features are being added to the CI Time Response Procedures prior to the next scheduled tests. The remaining solenoids for the AES dampers in both Unit 1 and 2 were verified to be installed correctly.
3161993004 | Cook 2 | 04/08/1993 | 05/07/1993 | 9305140071 | <strong>Exceeded Technical Specification LCO As A Result Of Inaccuracies In Control Rod Position Indication</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993 at 0245 hours with Unit 2 in Mode 1 (Power Operation) with power being increased from 56 to 100 percent rated thermal power, the Rod Position Indication (RPI) for Rods H-12 and M-8 were found to be indicating greater than twelve steps from the Demand Position Indication. With the Group Demand Position at 215 steps, the RPIs for H-12 and M-8 each indicated rod positions of 230 steps. At 0327 hours, secondary coil stack voltage measurements were completed which corroborated the H-12 and M-8 RPI. With both of these rods in the same control group, the provisions of Technical Specification 3.1.3.2 were exceeded. This required entry into Technical Specification 3.0.3, which calls for initiation of a unit shutdown within one hour. At 0416 hours, the RPI for Rod H-12 returned to within twelve steps of demand and the H-12 RPI was returned to service at 0427 hours. This allowed exit from Technical Specification 3.0.3 and entry into the Action Statement for Technical Specification 3.1.3.2. In accordance with this Action Statement, the position of Rod M-8 was verified using the movable in-core detectors every eight hours, until 2130 hours on April 8, 1993, when the M-8 RPI was within 12 steps of demand and was returned to service. The M-8 event was the result of a signal conditioning module being out-of-specification high. The H-12 event was caused by temperature dependent drift of the Linear Variable Differential Transformers, located at the top of the control rod drive mechanism, which provide input to the RPIs. This event had no actual or potential impact on the health or safety of the public.
3161993005 | Cook 2 | 04/20/1993 | 12/30/1993 | 9401180083 | <strong>10CFR50 Appendix R Cable Routing and Compliance Strategy Concerns</strong><br /><i>Abstract:&nbsp;</i>This is a follow-up report to LER 93-005-00. <br /><br /> Upon completion of certain design changes in 1986, RCS loop temperature indications and pressure indication were routed through the LSI panels to the Control Room. Thus, a potential fire which could fail all of the LSI panels WOUld also fail this indication in the control Room, thereby not complying with the requirements of 10 CFR 50 Appendix R. Such a fire was possible in any fire zone where both the normal and alternate power supply cables to the LSI panels were routed. This condition was corrected in 1990 with the completion of design changes which provided additional Control Room RCS temperature and pressure indication which was not routed through the LSI panels. <br /><br /> This update to the original LER is being submitted to appraise you of the results of the evaluations that have since been performed. The evaluations have resulted in a number of changes to the safe shutdown equipment database. However, no additional cases of non-compliance with Appendix R were identified.
3161993006 | Cook 2 | 07/10/1993 | 08/09/1993 | 9308160318 | <strong>Exceeded Technical Specification Lco Action Time Limit Due To Time Required For Repair Of Charging Pump</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1993 at 2237 hours, the West Centrifugal Charging Pump (W-CCP) was secured due to degraded performance. The following morning, troubleshooting determined that the pump was inoperable and would require maintenance. Subsequent review of the condition determined that the starting time for the inoperability should have begun when the pump was initially secured on July 6, 1993. The applicable Technical Specification Action Statement required a unit shutdown when a CCP can not be returned to service within 72 hours. In anticipation that the repairs to the pump would exceed this time limit, with Unit 2 at 70 percent Rated Thermal Power, a sixty (60) hour Exercise of Enforcement Discretion was requested. On July 9, 1993, at 1544 hours, following review by NRR and Region III staffs, the NRC granted the request. The Technical Specification 72 Hour LCO Action Statement was exceeded on July 9, 1993, at 2237 hours. The W-CCP was returned to service on July 10, 1993, at 1145 hours, following completion of operability testing. <br /><br /> A postulated failure of the W-CCP was mitigated by the availability of the redundant CCP during the period of inoperability. Exceeding the 72 Hour Technical specification Action Requirement had no actual impact on public health and safety.
3161993007 | Cook 2 | 08/02/1993 | 09/01/1993 | 9309090345 | <strong>Reactor Trip From Spurious Turbine Exhaust Hood High Temperature Trip</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1993, at 1226 hours, the Unit 2 reactor tripped as a result of a main turbine trip, caused by a spurious actuation of the Exhaust Hood High Temperature Trip Switches. Investigation revealed that eight of nine Exhaust Hood High Temperature Trip Switch setpoints were found to be significantly below the normal trip setpoint. Investigation of the event determined that the method used to calibrate the switches may have caused the setpoint to be misadjusted, and that vibration can cause a downward shift in the setpoint. These factors, combined with a slight increase in hood temperatures and vibration levels which resulted from the removal of a main condenser half from service, are believed to have caused the spurious trip. <br /><br /> To prevent recurrence, the Main Turbine Exhaust Hood high temperature turbine trip was disabled. Written instructions for a manual turbine trip on receipt of a verified Main Turbine Exhaust Hood Extreme High Temperature Alarm have replaced the defeated automatic trip. .
3161993008 | Cook 2 | 08/27/1993 | 09/27/1993 | 9310190104 | <strong>Reactor Trip From The Reactor Protection System Due To A Steam Flow/Feed Flow Mismatch Coincident With A Low Level In No. 4 Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1993, at 0502 hours with Unit 2 in Mode 1 (Power Operation) at 90 percent Rated Thermal Power, a Reactor Trip occurred from a Steam Flow/Feed Flow Mismatch coincident with a low level in the No. 4 Steam Generator. These conditions were the result of an uncontrollable speed decrease on the East Main Feed Pump (MFP) Turbine. An investigation revealed that the loss of speed control was the result of a malfunctioning Current-to-Current Repeater (I/I). I/Is were installed in both the East and West MFP Turbine speed control circuits on August 13, 1993 via a Temporary Modification (TM). This action was taken following diagnosis of a ground condition which was interfering with the transfer of the turbine speed control circuit from manual to the automatic control mode. Post modification testing and power operation following installation of the TM demonstrated that the TM had isolated the grounding problem from the speed controller and had restored proper functioning of the control circuit. Following the trip, troubleshooting of the East MFP speed control circuit found that the I/I was malfunctioning. <br /><br /> The defective I/I was replaced on August 30, 1993. Following replacement of the I/I, circuit checks revealed inconsistencies which ultimately led to a decision to remove the TM. The East and West MFP speed control circuits were returned to their original design on September 12, 1993. The control mode transfer problems caused by the ground condition are being controlled administratively. Trouble shooting of the ground and subsequent repairs are scheduled for completion during the next Unit 2 Outage of sufficient duration .
3161993009 | Cook 2 | 09/28/1993 | 10/28/1993 | 9311030333 | <strong>Technical Specification Fire Door Made Inoperable Without Proper Compensatory Action Being Taken Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1993, with Unit 2 in Mode 1 (Power Operation), at approximately 1315 hours, an employee noted that the fire door to the Unit 2 NESW Valve Area was standing open with a stanchion installed between the door and the door frame (in the doorway). This condition makes the fire door inoperable. It was verified that there was no one in the area and the NESW Valve Area was not being toured by fire watch personnel. The last time that the fire door was known to be unobstructed was at 0715 hours on September 28, 1993, at which time the Fire Brigade was in the area and performing their daily fire door tours. The exact time when the fire door was blocked open could not be determined; therefore, it must be assumed that the door could have been inoperable for approximately 6 hours with no compensatory measures in place. <br /><br /> For immediate corrective action, the stanchion was removed from the doorway. <br /><br /> A technical evaluation of the condition concluded that defense-in-depth fire protection would have mitigated any fire spread between the affected fire zones.
3161993010 | Cook 2 | 09/20/1993 | 11/13/1993 | 9311180156 | <strong>Missed Reactor Coolant System Total Gaseous Activity Sample Technical Specification Surveillance Requirement Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1993 a Unit 2 Reactor Coolant System (RCS) total gaseous activity sample, required by the plant's technical specifications, was missed due to personnel error. From a review of logged data of September 20, 1993 it has been concluded that the results recorded for the Unit 2's RCS total gaseous activity were actually Unit 1 results and that the Unit 2 RCS total activity sample surveillance requirement was not performed. An investigation has determined that the Unit 2 RCS sample was collected and prepared; however, the Unit 1 RCS sample was mistakenly counted for the Unit 2 sample. The event was reported per the plant's corrective action program on October 14, 1993. An evaluation of the Unit 2 total gaseous activity samples taken on September 17, 1993 and September 24, 1993 showed that no adverse trend existed.<br /><br /> An evaluation of the Unit 2 liquid reactor coolant sample results taken before, during and after the event corroborate the total gaseous activity evaluation that no adverse trend existed. <br /><br /> Appropriate administrative action has been taken with the involved technician.
3171993001 | Calvert Cliffs 1, Calvert Cliffs 2 | 02/02/1993 | 03/09/1993 | 9303170090 | <strong>Technical Specification 3.0.3 Entry; Loss of Control Room Air Conditioning</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1993, at 9:55 a.m., both independent Control Room Emergency Ventilation System Air Conditioning trains (CR HVACs) were declared inoperable at Calvert Cliffs and the plant entered Technical Specification 3.0.3. The No. 12 CR HVAC train was determined to be inoperable while No. 11 CR HVAC train was removed from service for scheduled routine maintenance, Immediate action restored No. 11 CR HVAC train to OPERABLE status at 10:30 a.m., 35 minutes after the start of the event. At the time of the event Units 1 and 2 were at 100 percent power. <br /><br /> The immediate cause of No. 12 CR HVAC being inoperable was determined to be insufficient system refrigerant inventory. This event did not result in any significant safety consequences.<br /><br /> Immediate corrective actions included charging No. 12 CR HVAC with additional refrigerant, performing appropriate surveillance testing and restoring it to an OPERABLE status on February 3, 1993. We are performing a detailed design review of the CR HVAC system to define guidelines for system refrigerant inventory requirements under design outdoor air temperature conditions.
3171993002 | Calvert Cliffs 1, Calvert Cliffs 2 | 02/05/1993 | 06/29/1993 | 9307020375 | <strong>Missed Surveillance Requirements Due to Software Manual Error</strong><br /><i>Abstract:&nbsp;</i>Calvert Cliffs uses the Better Axial Shape Selector System (BASSS) version 3.3 computer code. This system monitors incore Axial Shape Index (ASI) and provides various alarm functions, The software vendor discovered an error in its user's manual which the vendor uses in updating BASSS's data-input library. The error rendered one alarm function inoperable, resulting in Units 1 and 2 not fulfilling Technical Specification Surveillance Requirement 4.2.5.1. This Surveillance requires verification of incore ASI within limits every twelve hours. The cause of the user manual error was failure of the vendor's quality assurance procedures to require independent review of user's manuals. Corrective actions included manual performance of the Surveillance, correcting BASSS's data-input library, verifying BASSS operable, and reviewing applicable sections of the user manual. After issuance of the software but prior to the discovery of this event, the vendor upgraded its quality assurance procedures to require independent review of software documentation. Baltimore Gas and Electric Company has audited the Vendor's quality assurance program and found it to be satisfactory.
3171993003 | Calvert Cliffs 1, Calvert Cliffs 2 | 06/10/1993 | 07/09/1993 | 9307160080 | <strong>Dual Unit Trip Due To Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On Thursday, June 10, 1993 at 8:28:13 a.m., a flashover relay in the Calvert Cliffs switchyard actuated, causing the loss of the 500 kv "Red" bus feeding Unit 2. Unit 2 immediately tripped on low coolant flow. Unit 1 was manually tripped 25 seconds later by operators anticipating a total loss of offsite power. <br /><br /> The most probable cause of the Unit 2 trip is induced vibration of the flashover relay. The decision to trip Unit 1 resulted from the Control Room Supervisor's having concluded that a loss of offsite power was underway. <br /><br /> We will train appropriate personnel on avoiding inadvertent relay actuation. We will minimize the protective features left operative when breakers are opened for extended periods. We will evaluate improvements to operator training.
3171993004 | Calvert Cliffs 1 | 06/11/1993 | 07/08/1993 | 9307160085 | <strong>Reactor Trip Due to Turbine Trip Resulting From Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1993, Unit 1 tripped due to an automatic actuation of the Reactor Protection System (RPS). An RPS loss of load signal was generated when the turbine tripped due to a low pressure feedwater heater (FWH) high level turbine trip signal. The signal was generated because the FWH high level dump (HLD) valve handswitch was left closed during startup. The unit was at 16 percent power.<br /><br /> A cause of the event was that opening the FWH HLD valves for plant startup was not adequately proceduralized. One contributing factor was that one operating crew questioned the valves position but did not effectively follow-up on the question or pass it along to the next crew who did not detect the improper handswitch positions. Procedure changes were made to open the appropriate FWH HLD valves during plant startup. The design of the FWH high and high-high level alarm circuits was reviewed. Reactor trip and normal shutdown procedures and valve lineups will be reviewed for similar valve position problems. Troubleshooting of the FWH water level alarm circuits will be performed.
3171993005 | Calvert Cliffs 1 | 06/30/1993 | 07/30/1993 | 9308040253 | <strong>TS 3.0.3 Entered, Due to Both Containment Spray Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1993, at 2:00 p.m., Calvert cliffs Unit 1 entered Technical Specification 3.0.3 for 45 minutes because both independent Containment Spray (CS) Systems were inoperable. No. 12 CS System was inoperable for scheduled maintenance. No. 11 CS System was determined to be inoperable because the outlet valve for component cooling water supplying its shutdown cooling heat exchanger was broken. Immediate corrective action restored No. 11 CS System to OPERABLE status while the Unit was at 100 percent power. This event resulted in no public health or safety consequences. <br /><br /> The affected valve actuator had disconnected. We believe the actuator connecting linkage separated due to pivot locking plate failure. The replacement plate subsequently cracked. Similar cracked plates were found on two identical Unit 2 valves. Plate material was a sintered alloy. The cracked plates were replaced with carbon steel plates. We plan to install carbon steel pivot locking plates on similar style valves. This report satisfies 10 CFR Part 21 requirements.
3171993006 | Calvert Cliffs 1, Calvert Cliffs 2 | 10/10/1993 | 11/23/1993 | 9312060063 | <strong>Missed Surveillance on Electrical Fire Pump Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1993, Baltimore Gas and Electric Company discovered that the monthly surveillance of the electric fire pump required by Technical Specifications had passed its maximum allowed extension on October 10, 1993. The electric fire pump was therefore considered inoperable for 16 days. Also, the diesel fire pump had been removed from service on October 12-13; thus, both of the site's two fire pumps were considered inoperable for approximately 24 hours. <br /><br /> The test was missed because of personnel error. This event had no impact on safety. In addition to the surveillance test, proper pump operation is verified weekly using a shorter duration test. The immediate corrective action was to declare the pump inoperable and perform the missed surveillance. Long-term corrective action included issuing a letter of expectations to all involved personnel and a training session to stress the importance of thoroughly investigating apparent schedule discrepancies.
3171993007 | Calvert Cliffs 1, Calvert Cliffs 2 | 12/29/1993 | 12/29/1993 | 9401100164 | <strong>Performance Tests Indicate Possibility of SRW Heat Exchanger Inoperability</strong><br /><i>Abstract:&nbsp;</i>The results of recently completed thermal performance testing on our service water (SRW) heat exchangers indicate the possibility they may not have been capable of meeting their intended safety function during certain past periods of high bay temperatures. The calculated fouling plus the associated uncertainty in calculated thermal margin indicated the possibility of actual thermal performance being less than required performance. <br /><br /> The original SRW heat exchanger design calculations assumed minimum SRW flow as the most limiting case. Current calculations recognize that assuming maximum SRW flow results in higher heat transfer rates from the Containment Air Coolers to the SRW heat exchangers. The resulting higher SRW temperatures had the potential to exceed the maximum permissible SRW inlet temperature to the Emergency Diesel Generator Air Coolers. This voluntary report is submitted to share the insights we have gained from the performance tests. <br /><br /> There were no significant safety consequences resulting from this issue. The plant is currently in a safe condition with bay temperatures well below current operability limits. A variety of interim and long-term solutions are being considered to resolve the issue.
3171993008 | Calvert Cliffs 1, Calvert Cliffs 2 | 10/31/1986 | 01/04/1994 | 9401120236 | <strong>Inoperable Emergency Diesel Generators - Removal of Missile Protection</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1993, Calvert Cliffs engineers determined the removal of an Emergency Diesel Generator (EDG) room shield door could render the other Calvert Cliffs EDGs inoperable. Removal of the shield door removes tornado protection for the EDGs and a missile could impact common starting air piping and common walls. On October 31, 1986, the 11 EDG shield door was removed while Calvert Cliffs Unit 1 was shutdown for an outage. The remaining two EDGS should have been declared inoperable, but personnel were unaware of the potential missile impact. Corrective action includes generation of a maintenance procedure with appropriate precautions and the performance of an engineering review to determine if the removal of other missile barriers could create the same situation.
3181993001 | Calvert Cliffs 2 | 02/20/1993 | 03/18/1993 | 9303240181 | <strong>Pressurizer Code Safety Valve High As-Found Setpoints</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1993, Calvert Cliffs Nuclear Power Plant (CCNPP) Unit 2 was found to be in a condition outside its design basis when both Pressurizer Code Safety Valves were found with lift setpoints higher than those allowed by the Technical Specifications and above those used in the plant's safety analyses. At the time of discovery, CCNPP Unit 2 was in Hot Standby (Mode 3) with reactor coolant temperature and pressure at approximately 530 degrees Fahrenheit and 1990 PSIG. The discovery was made during surveillance testing associated with a normal shutdown preceding a scheduled refueling outage. Both valves had last been tested in March 1989. <br /><br /> Imprecision associated with the test methodology was the primary causal factor. One of the valves will be inspected by the vendor for mechanical degradation, but it is thought unlikely that this was a factor. <br /><br /> Immediate corrective action was taken to reset the valves to within specification. Refinements to the test procedure are being evaluated. Both valves will have their setpoints verified using new testing methodology prior to power operation of Unit 2 following the current refueling outage .
3181993002 | Calvert Cliffs 2 | 06/08/1993 | 07/08/1993 | 9307150106 | <strong>Inadvertent ESF Actuations While Performing Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1993, at 9:59 a.m., Calvert Cliffs Unit 2 experienced inadvertent Auxiliary Feedwater Actuation System (AFAS) and Reactor Protective System actuations during performance of Auxiliary Feedwater (AFW) System large flow surveillance testing when excessive differential pressure developed between the steam generators. At the time of the event, Unit 2 was in MODE 3, HOT STANDBY, with the Reactor Coolant System at 2250 psia and 532 degrees Fahrenheit. The main steam isolation valves (MSIVs) were shut. There were no safety consequences resulting from this event. The AFAS actuation signal immediately stopped AFW flow to the affected (lower pressure) steam generator. The cause of this event was that neither the test procedure nor the operators' assessment of the expected plant response identified the potential for the development of this plant condition. Appropriate procedure changes will be made to warn operators of the potential for this condition to occur. Both MSIVs will be required to be open during the test. Management expectations that operators identify and evaluate potential problems prior to task performance, has been re-emphasized.
3181993003 | Calvert Cliffs 2 | 06/25/1993 | 07/22/1993 | 9307280187 | <strong>Trip on Low Steam Generator Level Due to Insufficient Feedwater Addition</strong><br /><i>Abstract:&nbsp;</i>On Thursday, June 25, 1993 at 8:05 p.m., Calvert Cliffs Unit 2 automatically tripped on low level in the 21 Steam Generator (SG). Operators had noted divergent SG level oscillations with the Full Range Digital Feedwater Control System (FCS) in automatic. They took manual control with SG level at +25 inches but did not provide sufficient feedwater. The reactor tripped on low SG level. <br /><br /> The causes of this event include inadequate communication of pertinent information regarding the response of the FCS at low power, inadequate communication during shift turnover regarding a just-completed power increase, the lack of Project Team involvement at the time of the incident, and the work practices of the operations personnel involved in this incident. <br /><br /> Operations management will reemphasize expectations for the improvement of communications between operating crews. An FCS Project Team representative will be available to the Control Room for future startups and planned shutdowns until FCS performance meets expectations. We will provide classroom training to all operating crews on the details of this event.
3181993004 | Calvert Cliffs 2 | 12/02/1993 | 12/29/1993 | 9401100063 | <strong>Axial Shape Index Channel Error Due to Insufficient Troubleshooting Review</strong><br /><i>Abstract:&nbsp;</i>On Thursday, December 2, 1993, during troubleshooting in the Reactor Protective System, an error was inadvertently introduced into the Channel A upper Nuclear Instrumentation (NI) subchannel, rendering the Channel A Axial Shape Index (ASI) inoperable. The channel was subsequently brought back in service for over two hours without Technical Specification required ACTION being taken.<br /><br /> The immediate cause of this event was equipment malfunction involving either a loose NI cable connector or a malfunctioning switch. The root cause is that insufficient Post Maintenance Testing was performed prior to declaring the channel OPERABLE. <br /><br /> The NI adjustment procedure has been revised to require a check of ASI. We have reviewed this event with Maintenance and Operations personnel and are reviewing the appropriate procedure to enhance post-troubleshooting testing. We are replacing connectors similar to the ones used in this application and have replaced the malfunctioning switch.
3181993005 | Calvert Cliffs 2 | 12/03/1993 | 02/04/1994 | 9402100150 | <strong>Failure to Continuously Monitor Main Vent Effluent Iodine and Particulates</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1993, a technician found that the Unit 2 main vent iodine and particulate sampler pump was not running. This pump fulfills Technical Specification requirements to continuously sample the main vent effluent for iodine and particulates. <br /><br /> The immediate cause of this specific event was a lack of adequate self- checking by a watchstander. The root cause of the event was poor equipment design. There were no nuclear safety consequences due to this event. Immediate corrective action was to restart the pump. Actions to prevent recurrence include enhanced equipment labeling, a requirement to periodically verify pump operation and increased supervisory emphasis on the importance of self-checking. A modification is planned that will replace the sample pump with a better design that includes a control room alarm.
3201993001 | Three Mile Island 2 | 01/26/1993 | 02/23/1993 | 9303010218 | <strong>Failure to Sample PWDS Source Tank</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1993, the TMI-2 Processed Water Disposal System (PWDS) was operating in the "coupled mode" (i.e., evaporator coupled to the vaporizer) when it was determined that 221,000 gallons of water had been processed by the PWDS in the coupled mode from PWST-1 without the required periodic confirmatory sample (i.e., each 100,000 gallons) of the source tank having been taken.<br /><br /> This event was the result of both personnel error and a programmatic deficiency. Normally, the status of PWDS processing is closely tracked by the PWDS Cognizant Engineer and Plant operations shift supervision. In this event, both the PWDS Cognizant Engineer and the shift supervision failed to adequately track the volume of AGW processed and ensure the required source tank representative sample was taken and analyzed after each 100,000 gallons had been processed. The programmatic deficiency is that there is no procedural control requiring routine review of water processing progress to ensure the sample is obtained in a timely manner.
3201993002 | Three Mile Island 2 | 06/01/1993 | 06/30/1993 | 9307130156 | <strong>Failure To Obtain Weekly Tritium Grab Samples Of Chemical Cleaning Building Exhaust</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1993 during the performance of 4210-SUR-3526.01, "EPICOR Exhaust Sampling," the health physics technician observed that the sample chamber in the sampling device was essentially empty of water. The lack of water in the sampling apparatus sample chamber rendered the device inoperable, i.e., the ability to retrieve the tritium grab sample was lost. No sample was taken for the month of May, 1993 as required in the Offsite Dose Calculation Manual (ODCM, Section 3.1.J and Table 3.1-3. Upon discovery of the empty sampler, TMI Radiological Controls Field Operations and Engineering personnel conducted a review of the sample chamber changeout procedure and Tritium bubble sample technique. The root cause of the event was inadequate monitoring of the Tritium sample apparatus sample chamber operability. Specifically, the status of the Tritium sample apparatus was not inspected on a weekly basis to ensure its continued operability. Radiological Controls has initiated weekly inspections of the Tritium sample apparatus as a corrective action to preclude recurrence of this event.
3201993003 | Three Mile Island 2 | 06/07/1993 | 07/02/1993 | 9307190142 | <strong>RB PURGE WITH HP-R-225 AND HP-R-226 INOPERABLE</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1993, the TMI Maintenance foreman observed that the required channel functional test had not been performed on BP-R-226 within the required monthly surveillance interval. Subsequent investigation determined that on June 5, 1993, the TMI-2 Reactor Budding Purge was operated with HP-R-225 and HP-R-226 in an inoperable condition. HP-R-225 was out-of-service for maintenance. HP-R-226 was in an inoperable condition because the required monthly channel functional test had not been performed within the required surveillance interval. Therefore, purge of the Reactor Building on June 5, 1993, violated the control specified in the TMI Offsite Dose Calculation Manual (ODCM) Part II, Section 3.1.2.2.B.1. The root cause of this event was inadequate administrative control on the scheduling and control of a Technical Specification (Tech. Spec.) and ODCM required surveillances at TMI-2. The immediate corrective action in response to this event was the performance of the channel functional test for HP-R-226. The long term corrective action taken to preclude recurrence of this event was a change in the method by which Tech. Spec. and ODCM required surveillances for TMI-2 are scheduled and controlled.
3211993001 | Hatch 1 | 03/16/1993 | 04/08/1993 | 9304130087 | <strong>Loss Of Condenser Vacuum Results In Unplanned Manual Scram And Group 2 Primary Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On 3/16/93 at 0812 CST, Unit 1 was in the Run mode at a power level of 877 CMWT (36% rated thermal power). At that time, Operations personnel manually scrammed the reactor in response to decreasing main condenser vacuum. Vacuum began decreasing approximately 45 minutes prior to the manual scram. Operations personnel noted the decrease and investigated possible causes. They also lowered reactor power from 1267 CMWT (52% rated thermal power) to 877 CMWT in an attempt to stop the decrease. However, vacuum continued to decrease and, with vacuum at 23.2 inches Hg, the reactor was manually scrammed to avoid an automatic scram and a trip of the Reactor Feedwater Pumps on low condenser vacuum. Reactor water level decreased to two inches above instrument zero (160 inches above the top of the active fuel) immediately following the scram due to void collapse from the rapid reduction in power before being recovered with the "A" Reactor Feedwater Pump. As water level decreased to below 12.5 inches above instrument zero, a Group 2 Primary Containment Isolation signal was received on low (Level 3) water level per design. All Group 2 isolation valves closed; however, valve 1G11-F019 did not close within the required time of 15 seconds. <br /><br /> The loss of vacuum was apparently caused by component failure. The steam trap in the condensate drain line for the Unit 1 steam packing exhauster apparently stuck in the open position. This created an air inleakage flow path to the main condenser. The inleakage flow rate exceeded the capacity of the main condenser steam jet air ejector; therefore, vacuum decreased. The cause of valve 1G11-F019 not closing within its required time was apparently excessive stem friction from its packing, Corrective actions for this event include rebuilding the steam trap, repacking valve 1G11-F019, and rebuilding its actuator.
3211993002 | Hatch 1 | 04/01/1993 | 04/21/1993 | 9304270144 | <strong>Corrosion-Induced Bonding Results in Safety Relief Valve Lift Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 4/1/93, Unit 1 was in the Refuel mode with all fuel removed from the vessel. At that time plant engineering personnel notified licensed shift personnel of the results of off-site testing of the reactor pressure vessel safety relief valves (SRVs, EIIS Code JE). Five of the SRVs experienced setpoint drift in excess of the 3 percent tolerance specified by in-service testing (IST) requirements. Nine of the SRVs experienced setpoint drift in excess of the 1 percent tolerance specified by Unit 1 Technical Specifications section 2.2.A. This voluntary report is being submitted due to the potential industry interest in this event in view of the ongoing efforts to reduce setpoint drift by the Boiling Water Reactor Owners' Group (BWROG). The setpoint drift experienced was well within the analytical limits existing for reactor vessel over-pressure protection. <br /><br /> The root cause of the SRV setpoint drift in excess of the 3 percent tolerance is corrosion-induced bonding of the pilot valve disc and seat. <br /><br /> Corrective actions for this event include refurbishing the valves and continuing to participate in the BWROG efforts to resolve the SRV setpoint drift issue. In addition, a system is being installed during the ongoing Unit 1 refueling outage to provide redundant electrical actuation signals to the SRVs. A similar system has been installed on Unit 2. Since these systems provide added assurance that the SRVs will function when required, GPC does not anticipate submitting further voluntary reports on the issue of SRV lift setpoint drift.
3211993003 | Hatch 1, Hatch 2 | 04/12/1993 | 05/10/1993 | 9305170238 | <strong>Personnel Error Results In Missed Diesel Generator Technical Specifications Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 4/12/93 at 1430 CDT, Unit 1 was in its fourteenth refueling outage with all fuel removed from the reactor vessel and Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, plant personnel determined that the monthly operability test for Diesel Generator 1B had not been performed during its required performance window as required by Unit 1 Technical Specifications section 4.9.A.2.a.1 and Unit 2 Technical Specifications section 4.8.1.1.2.a. The test was due to be performed on 3/28/93 with a late date, based upon the allowed 25% grace period, of 4/4/93. It was not performed at that time because of a scheduling error. Upon determination that the surveillance had been missed, licensed Operations personnel declared Diesel Generator 1B inoperable and initiated Limiting Conditions for Operation (LCOs) 1-93-333 and 2-93-230. Operations personnel performed procedure 34SV-R43-002-1S, "Diesel Generator 1B Monthly Test," and, at 1945 CDT on 4/12/93, following successful completion of the test, declared the diesel generator operable. LCOs 1-93-333 and 2-93-230 were terminated at that time. <br /><br /> The cause of this event was personnel error. The person responsible for scheduling Technical Specifications surveillances, when changing the computer entry for the diesel generator's monthly operability test, caused the test to be rescheduled for a date after 4/4/93. He did not note this unintended change to the test due date. Consequently, the operability test was not scheduled and performed as required. <br /><br /> The involved person is aware of the causes of the error and understands how to avoid this in the future. <br /> ?
3211993004 | Hatch 1 | 04/14/1993 | 05/14/1993 | 9305190219 | <strong>Blown Fuse Results In An Unplanned Automatic ESF Actuation And An Interpretation Of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>On 4/14/93, at 0910 CDT, Unit 1 was in the Refuel mode and core reload was in progress with 23 fuel bundles loaded in the core. The "A" division of the Residual Heat Removal (RHR) System was out of service for maintenance. The "B" division of RHR was in operation in the Shutdown Cooling (SDC) mode. At that time, while performing a periodic surveillance, a licensed operator found that RHR-SDC flow was at zero. He then checked the system alignment and found that the low Pressure Coolant Injection valve (valve 1E11-F015B), which also functions as the SDC discharge valve, was closed, isolating SDC from the reactor vessel. The operator opened the valve; however, when the valve reached the full open position, it automatically reclosed. The 1D RHR pump was then secured, fuel movement was stopped, and procedure 34AB-E11-001-1S, "Loss of Shutdown Cooling," was entered. An investigation was subsequently initiated. At 1015 CDT, it was determined that the valve had closed due to a blown fuse. The fuse was replaced and the valve was reopened without incident. By 1043 CDT, the RHR system had been filled and vented and SDC had been returned to service. Reactor coolant temperature did not increase during the event. <br /><br /> The cause of the event was inadvertent grounding of a logic circuit resulting in the circuit fuse actuating. The grounding incident occurred at approximately 0745 CDT during a modification activity not associated with the RHR system. <br /><br /> Corrective actions included replacing the fuse, testing of the SDC pump, returning SDC to service, revising administrative controls, and issuing an operating order.
3211993005 | Hatch 1, Hatch 2 | 04/15/1993 | 05/15/1993 | 9305190382 | <strong>Blown Fuse Results In Unplanned, Automatic Actuations Of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 4/15/93 at 0755 CDT, Unit 1 was in a refueling outage with the reactor core partially loaded with fuel and the reactor vessel head removed. At that time, Instrument and Control technicians were performing surveillance procedure 57SV-D11-008-1S, "REACTOR BUILDING EXHAUST VENT RADIATION MONITOR INSTRUMENT FT," when fuse 1D11-A-F14B blew. This resulted in initiation of the 'B' trains of both units' Standby Gas Treatment (SBGT) Systems, isolation of the 'B' dampers of both units' Secondary Containments, and closure of several Group 2 Primary Containment Isolation System (PCIS) valves. Subsequently, when the technicians attempted to exit the procedure, the removal of a jumper resulted in initiation of the 'A' trains of both units' SBGT systems, isolation of the 'A' dampers of both units' Secondary Containments and isolation signals being sent to other Group 2 PCIS valves per design. <br /><br /> The cause of this event was a blown fuse. No reason for the fuse blowing could be found. <br /><br /> Corrective actions for this event included replacing the blown fuse, replacing several relays in the logic powered through this fuse, and examining some of the wiring in the logic which is powered by this fuse. All of these actions are complete.
3211993006 | Hatch 1 | 05/01/1993 | 05/28/1993 | 9306040055 | <strong>Engineered Safety Features Actuations Caused By Purge Dam Material In Instrument Line</strong><br /><i>Abstract:&nbsp;</i>On 5/1/93 at 1215 CDT, Unit 1 was nearing the end of a refueling outage in the Cold Shutdown mode with all control rods fully inserted. Reactor pressure was at approximately 100 psig, and reactor coolant temperature was at approximately 145 degrees Fahrenheit and increasing in preparation for the ASME XI Class 1 System Leakage Test. At that time a full Reactor Protection System actuation signal was received on a low water level signal. The low water level signal also produced a trip signal to several Group 2 Primary Containment Isolation System (PCIS) valves, per design. Licensed Operations personnel verified that actual reactor water level was not low by comparing instrumentation. Two unsuccessful attempts were made to correct the condition by filling the affected instruments' variable sensing line and performing various instrument valve manipulations. When these efforts proved unsuccessful, Instrument and Control technicians filled and vented the reference line of the affected instrumentation. While using a manual hydrostatic test pump to fill the reference line, some resistance to flow was encountered, indicating the line was partially plugged. Further pressurization, however, cleared the obstruction. The root cause of this event was pressurization of a reactor water level instrument reference leg due to blockage in the line coupled with minute leakage through instrument diaphragms or equalizing valves which permitted jet pump pressure to be felt in the reference leg. The blockage in the line is believed to have been soluble weld purge dam material used during an outage-related repair to the sensing line. Corrective actions for this event included clearing the obstruction and verifying level instrument operation. Also, the procedure controlling weld processes on pressure boundaries will be revised and the event will be discussed with personnel who perform welding.
3211993007 | Hatch 1 | 05/04/1993 | 05/21/1993 | 9305280302 | <strong>Inapproriate Jumper Placement By Plant Personnel Results In Unplanned ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On 5/4/93 at 1110 CDT, Unit 1 was in the Cold Shutdown mode with refueling outage activities in progress. At that time, several Group 2 Primary Containment Isolation System (PCIS) valves closed unexpectedly during the performance of procedure 42SV-E11-004-1S, "Residual Heat Removal Shutdown Cooling LSFT." The engineer performing the procedure inadvertently opened a contact in relay 1A71-K59 while attempting to install a jumper across the contact. This caused the PCIS logic downstream of the open contact to de-energize and Group 2 PCIS valves in the drywell pneumatics, fission product monitoring, and hydrogen and oxygen analyzer systems to close per design. Operations personnel reset the isolation signal and reopened the valves. However, at 1130 CDT, when the engineer removed the jumper on relay 1A71-K59, he inadvertently opened the contact again. As a result, the same valves closed for a second time. Operations personnel again reset the isolation signal and reopened the valves. The performance of the procedure was halted temporarily. It was resumed later that day and completed at 2055 CDT on 5/4/93 with no further incidents. <br /><br /> The cause of this event was an inappropriate action by the engineer. In an attempt to provide more secure connection points for the jumper, the engineer placed the jumper clips on the contact arm rather than the terminal screw heads. However, the force holding the contact together is not very strong; therefore, the engineer was able to push apart the contact with the tip of the jumper clip when installing and when removing the jumper. Engineering personnel who perform this type of test were made aware of the event and instructed not to install jumpers on contact arms.
3211993008 | Hatch 1, Hatch 2 | 05/05/1993 | 06/03/1993 | 9306090531 | <strong>Procedure Error and Miscommunication Result in Missed Technical Specifications Action Statement</strong><br /><i>Abstract:&nbsp;</i>On 5/5/93, at 2000 CDT, Unit 1 was in the Cold Shutdown mode and Unit 2 was in the Run mode at a power level of 1805 CMWT (74.1 percent rated thermal power). At that time, the Unit 1 Shift Supervisor determined that the Unit 1 "B" train of the Standby Gas Treatment (SBGT) system had been inoperable since 0100 on 5/2/93. On that date, Instrument and Control technicians had found a humidity controller in the SBGT system inoperable. However, licensed shift personnel were not aware that this made the "B" train of the SBGT system inoperable and thus did not initiate a Limiting Condition for Operation at that time. Concurrently, the emergency power source for the redundant train of the Unit 1 SBGT system was inoperable because of component failure. Since one train of the Unit 1 SBGT system was already inoperable due to the failed humidity controller, this invoked the Unit 2 Technical Specifications requirement that the redundant train be declared inoperable due to the lack of an emergency power source. However, since the condition was not recognized until 5/5/93, the Action statement requiring Unit 2 to be shutdown within 12 hours was missed. In addition, Unit 1 entered a condition prohibited by the Technical Specifications when it had less than the required number of operable SBGT system trains in a condition wherein Secondary Containment integrity was required. The root causes of this event were a less than adequate procedure and less than adequate communications. The calibration procedure which was in use at the time of the event did not list all the effects of removing the controller from service. Communications among involved personnel resulted in failure to identify this inadequacy. Corrective actions include revising a procedure and discussing communications with personnel in the departments involved in the event. The first action is completed; the second will be completed by 06/30/93.
3211993009 | Hatch 1 | 05/14/1993 | 06/10/1993 | 9306160133 | <strong>Blown Fuses In Reactor Protection System Cause Scram When Mode Switch Is Moved To The Run Position</strong><br /><i>Abstract:&nbsp;</i>On 5/14/93 at 0535 CDT, Unit 1 was in the Run mode at a power level of 170 CMWT (7% rated thermal power). At that time, the unit scrammed when licensed operations personnel moved the reactor mode switch to the Run position. At 0536 CDT, a Group 1 Primary Containment Isolation System (PCIS) isolation signal was received on low reactor pressure while in the Run mode. The Main Steam Isolation Valves (MSIVs) closed per design. Three seconds after receipt of the Group 1 PCIS isolation signal, operations personnel moved the mode switch out of the Run position as required by plant procedures. This bypassed the Group 1 PCIS isolation on low reactor pressure before two of the four reactor pressure switches could trip. Consequently, sufficient isolation logic was not initiated to close the remaining Group 1 PCIS valves. Reactor water level decreased to a minimum of 25 inches above instrument zero (183 inches above the top of the active fuel) due to void collapse from the rapid decrease in reactor power. Water level was restored automatically with the "A" Reactor Feedwater Pump. <br /><br /> The cause of the scram was less than adequate maintenance procedures, less than adequate post-maintenance testing, and personnel error. Because the MSIV limit switch maintenance procedures were less than adequate, it appears the replacement of the limit switches resulted in blown fuses in the Reactor Protection System (RPS). Less than adequate testing and personnel error resulted in a failure to detect the blown fuses. As a result, a scram on MSIVs less than 90% open resulted when the mode switch was moved to the Run position, arming that portion of the RPS logic tripped by the blown fuses. Corrective actions include revising procedures and disciplining personnel.
3211993010 | Hatch 1 | 05/14/1993 | 06/10/1993 | 9306160144 | <strong>Less Than Adequate Procedure Results In Unplanned Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On 5/14/93 at 1948 CDT, Unit 1 was in the Hot Shutdown mode with all control rods fully inserted and reactor pressure at 75 psig. At that time, all eight Main Steam Isolation Valves (MSIVs) closed on the unexpected receipt of a Group 1 Primary Containment Isolation System (PCIS) signal during the performance of plant surveillance procedure 34SV-B21-001-1S, "MSIV Closure Instrument Functional Test." The isolation was the result of a failure to reset partial Group 1 PCIS trips generated during the performance of the surveillance. No other Group 1 PCIS valves closed nor should any have closed given the logic tripped during the performance of the procedure. The MSIVs were re-opened and the surveillance was completed successfully at 2210 CDT on 5/14/93. <br /><br /> The cause of this event was a less than adequate procedure. Surveillance procedure 34SV-B21-001-1S did not state that Group 1 PCIS logic could be tripped by the performance of the procedure nor did it require that the tripped isolation logic be reset following the testing of each MSIV closure instrument logic channel. As a result, the operator did not reset the partial Group 1 trip following the test of the "C" outboard MSIV. A full Group 1 PCIS signal was then generated when the operator began the test of the "D" outboard MSIV. <br /><br /> Corrective actions include revising procedures 34SV-B21-001-1S and 34SV-B21-001-2S, "MSIV Closure Instrument Functional Test."
3211993011 | Hatch 1 | 05/21/1993 | 06/10/1993 | 9306160224 | <strong>Component Failure Results In Partial Group 1 Primary Containment Isolation System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 5/21/93, at 1505 CDT, Unit 1 was in the Run mode at 2436 CMWT (100 percent of rated thermal power). At that time, the setpoints for the Main Steamline Radiation Monitors (MSLRMs) were being changed in preparation for placing the Hydrogen Injection System in service. This activity requires MSLRM 1D11-K603B to be removed from service which, in turn, deenergizes one of two electro-pneumatic control valves in Main Steamline Isolation Valve (MSIV) 1B21-F028C. Prior to this, the other electro-pneumatic control valve in the same MSIV had failed and deenergized. Consequently, when the MSLRM was removed from service, both control valves were deenergized simultaneously and the MSIV closed automatically as designed. Reactor power increased to 110 percent of rated thermal power and reactor pressure increased to 1035 psig (103 percent of normal pressure). Since both of these values are less than the trip setpoints for a reactor scram, no automatic actuations occurred or were expected. At the direction of licensed personnel, the MSLRM was returned to service and the MSIV was reopened. Reactor pressure and power then returned to normal levels.<br /><br /> The cause of this event was a failed component. Specifically, one of two electro-pneumatic control valves in an MSIV failed to the deenergized state such that when the other control valve was deenergized during performance of a procedure, the MSIV automatically closed. <br /><br /> Corrective actions for this event included reopening the affected MSIV, replacing the failed component, reviewing the Nuclear Plant Reliability Data System for similar failures, and installing a system to provide control room indication of the status of the electro-pneumatic control valves in the MSIVs.
3211993012 | Hatch 1 | 06/15/1993 | 07/09/1993 | 9307210210 | <strong>Instrument Isolation Valve Packing Leak Results In An Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 6/15/93, at 1453 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent of rated thermal power). At that time, an automatic reactor scram and isolation of the inboard Group 2 Primary Containment Isolation System (PCIS) valves occurred due to a false low reactor water level signal. Control rods fully inserted as designed. As expected, actual water level decreased immediately following the scram, reaching a minimum level of 34 inches below instrument zero (124.5 inches above the top of the active fuel). At approximately 10 inches above instrument zero, an actuation of the outboard PCIS occurred on an actual low water level condition. The Reactor Feedwater Pumps (RFPs) responded to the actual low level condition and restored water level. No Emergency Core Cooling Systems actuated as a result of the low water level condition, nor were they required to actuate. Reactor pressure decreased as a result of the scram and was then controlled by the Turbine Bypass Valves at approximately 920 psig. Due to misleading level indications, level increased above the bottom of the Main Steam Lines, resulting in water intrusion into the lines. <br /><br /> The cause of the event was a loose packing nut on an instrument isolation valve becoming disengaged during an instrument calibration. This ultimately resulted in depressurization of the sensing line and a false low reactor water level signal. Corrective actions include repairing the valve, checking other similar installations on both units, performing a walkdown of system piping, and analyzing the effect of water in the Main Steam Lines.
3211993013 | Hatch 1, Hatch 2 | 10/22/1993 | 11/16/1993 | 9312010212 | <strong>Trip Of Condensate Pumps Results In Decreasing Reactor Water Level And A Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On 10/22/93 at 1744 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the condensate pumps tripped. This caused a decrease in feedwater flow to the reactor vessel and a corresponding decrease in reactor water level. At 1744 CDT, with water level at approximately 18 inches above instrument zero and decreasing, personnel inserted a manual reactor scram. Water level decreased to a minimum of 52.4 inches below instrument zero (106 inches above the top of active fuel) due to the loss of feedwater flow and void collapse from the decrease in reactor power. A Group 2 Primary Containment Isolation System signal was received at about 12.3 inches above instrument zero. All Group 2 Primary Containment Isolation Valves (PCIVs) closed. Also, the recirculation system pumps tripped, the Unit 1 secondary containment isolated, the Unit 1 and Unit 2 Standby Gas Treatment systems initiated, and the Group 5 PCIVs closed. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems automatically started when water level decreased to 35 inches below instrument zero. They restored reactor water level to greater than 12 inches above instrument zero within four minutes of the scram. All systems functioned per design. Thermal stratification led to violations of pressure and temperature and heatup rate limits. The trip of the condensate pumps appears to have been most likely caused by vibration in a condenser hotwell level instrument. This level instrument provides a trip signal to all the condensate pumps. The exact problem has not been determined. Corrective actions included trouble shooting the instrument and logic circuit and implementing a temporary modification to disable the pump trip on low hotwell level.
3211993014 | Hatch 1 | 11/11/1993 | 11/30/1993 | 9312090174 | <strong>Normal Reactor Water Level Decrease Following Planned Scram Results in Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On 11/11/93 at 0950 EST, Unit 1 was in the Run mode at a power level of 462 CMWT (19% of rated thermal power). At that time, the reactor was manually scrammed as a maintenance outage was scheduled to begin. When the manual scram was inserted, reactor water level decreased as expected due to the normal void collapse which occurs as power rapidly decreases. This is a normal response for a boiling water reactor. In this case, the level reduction reached the setpoint of some, but not all, Level 3 instrumentation. A review of the recording of the Safety Parameter Display System (SPDS) following the event showed that reactor water level barely entered the region where certain reactor water Level 3 instruments are set to trip. Three of four Level 3 instruments tripped, completing enough logic to cause inboard Group 2 Primary Containment Isolation System (PCIS) valves to close. The outboard Group 2 PCIS valves did not close, nor were they required to. No other automatic, unplanned actuations occurred. Licensed personnel confirmed that all valves which were required to close did so, and that no unexpected actuations occurred. <br /><br /> This event was caused by the normal reduction in reactor water level which followed a planned manual scram. When reactor water level reached the setpoints of reactor water Level 3 instrumentation, inboard Group 2 PCIS valves closed as designed.<br /><br /> No corrective actions were required for this event.
3211993015 | Hatch 1 | 11/28/1993 | 12/21/1993 | 9401030256 | <strong>High Pressure Coolant Injection System Experiences Momentary Inoperability Due to Power Supply Transient</strong><br /><i>Abstract:&nbsp;</i>On 11/28/93 at 1212 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent of rated thermal power). At that time, control room operators observed an annunciator alarming, "HPCI SYSTEM INVERTER CIRCUIT FAILURE." The alarm cleared in the same instant that it came on, indicating that a momentary power transient had occurred in the High Pressure Coolant Injection (HPCI) system control logic. The transient caused the HPCI system Manual/Automatic (M/A) transfer station to shift from the automatic to the manual mode. Since, in this condition, the HPCI system could not automatically initiate, it was inoperable. Licensed personnel recognized this condition immediately and returned the M/A station to the automatic mode, restoring the HPCI system to operable status. The total time during which the HPCI system was inoperable was less than 30 seconds. <br /><br /> The cause of this event was a momentary transient in the power supply for the HPCI system. The transient was sensed by the M/A station as a power interruption, and the M/A station responded per design by automatically shifting to the manual mode. The cause of the power transient has not been determined because the HPCI system is presently operable; the transient has not recurred and further investigation would require the HPCI system to be removed from service.<br /><br /> Corrective action for this event included restoring the HPCI system to operable status. This action was completed within a few seconds of the event. In addition, the HPCI system passed an operability test on 12/01/93, which included using the affected instrumentation to control HPCI operation up to rated flow and pressure. In addition, the HPCI system performed a successful automatic initiation following a scram on 12/07/93, The power supply electronics will be checked at some future time when the HPCI system is out of service.
3211993016 | Hatch 1, Hatch 2 | 12/07/1993 | 01/06/1994 | 9401130094 | <strong>Loss Of Feedwater Pump And Failure Of Recirc Pump Runback Cause Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 12/7/93 at 0602 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the unit automatically shut down on low reactor vessel water level caused by an automatic shutdown of the "A" Reactor Feedwater Pump (RFP) and a failure of the Reactor Recirculation pumps to run back to 44% speed per design. A Group 2 Primary Containment Isolation System (PCIS) signal on low reactor water level was also received, and the Group 2 Primary Containment Isolation Valves (PCIVs) closed as required. As water level decreased due to void collapse from the rapid reduction in power, the Group 5 PCIVs closed, the Unit 1 secondary containment isolated, the Unit 1 and Unit 2 Standby Gas Treatment systems initiated, the Recirculation pumps automatically shut down, and the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems initiated on low low reactor water level per design. The High Pressure Coolant Injection system did not inject to the vessel because its initiation signal cleared before the injection valve received all of its permissive signals to open. Water level decreased to a minimum of 50 inches below instrument zero (108 inches above the top of active fuel) before being recovered by the "B" RFP and the Reactor Core Isolation Cooling system. Water level was maintained greater than 24 inches above instrument zero with the "B" RFP. <br /><br /> The "A" RFP shut down due to a low RFP lube oil system pressure resulting from a loss of power to the "B" lube oil system pump. The supply breaker to the lube oil system pump inadvertently opened and de-energized the pump motor. The standby lube oil pump did not prevent the RFP trip due to pressure fluctuations in the oil header. The Recirculation system pumps did not run back due to a clogged sensing line which delayed a low RFP flow signal to the runback logic.<br /><br /> Corrective actions included testing the breaker, clearing the sensing line, reviewing the lube oil system response to a pump trip, replacing a pressure switch, and adding an automatic start signal to the lube oil pumps.
3221993001 | Shoreham | 04/29/1993 | 06/11/1993 | 9306170229 | <strong>Movement of Heavy Load on Refuel Floor Which Was Outside Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>On 4/29/93, the Shoreham Nuclear Power Station was operated outside of its design basis when a heavy load was moved in the vicinity of the Spent Fuel Pool (SFP) using a lifting attachment that did not comply with NUREG-0612. This condition violated a commitment in the Shoreham Decommissioning Plan and is reportable per 10CFR50.73(a)(2)(ii). The cause of this event was the failure to consider this lifting attachment in the original reviews performed pursuant to NUREG-0612 which identified heavy loads that would be handled over or near fuel or over safety-related equipment. The heavy load was a Refueling Jib Crane (RJC). It was moved by the Reactor Building Polar Crane using a vendor-supplied lifting attachment. In addition, this lifting attachment failed while the jib crane was suspended over the Refuel Floor causing the jib crane to fall to the floor and land between the Reactor Building hatchway and the SFP. Corrective actions included an inspection of the refuel floor, testing and inspection of the Polar Crane, procedure revisions to require Engineering, QA, management and safety representatives to be present during heavy load lifts near the SFP, procedure revisions to require rigging sketches to be prepared and to be reviewed for compliance with NUREG-0612, counseling of the personnel involved and disciplinary action.
3221993002 | Shoreham | 12/28/1993 | 01/25/1994 | 9402020031 | <strong>Fire in Primary Containment Requiring Containment Evacuation and Off-Site Fire Department Assistance</strong><br /><i>Abstract:&nbsp;</i>On 12/28/93, at 2245 hours, a fire occurred in the Reactor Building Primary Containment which required an evacuation and assistance from an off-site fire department. The fire occurred when falling slag from oxy-acetylene torch cutting entered a jet pump nozzle access window in the biological shield wall and ignited a portion of a temporary water collection system (paper towel, rope, herculite and griffolyn). This water collection system was installed to collect the potentially contaminated cooling water produced from core boring through the slightly activated bioshield wall. The Fire Brigade was activated at 2247 hours and directed people to evacuate the area. The Wading River Fire Dept. was called at 2304 and arrived at 2311 hours. The fire was declared out at 2320 hours. Eleven people reported to the First Aid Office suffering from smoke inhalation. The NRC was notified of this event at 2345 hours per 10CFR50.72 (b) (1) (vi). This event is also reportable per 10CFR50.73 (a) (2) (x). Corrective actions included suspension of work within the bioshield wall until resolution of concerns regarding egress, ventilation, emergency lighting/ communications, and personnel accountability. Also, all fire permits were temporarily withdrawn and reassessed. Finally, program enhancements and improvements in the Primary Containment work conditions have been initiated.
3231993001 | Diablo Canyon 2 | 01/30/1993 | 06/23/1993 | 9307020224 | <strong>Turbine Trip And Reactor Trip During Surveillance Testing Due To Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1993, at 2147 PST, with Unit 2 at 100 percent power, a turbine trip and reactor trip occurred during a routine surveillance test. Plant operators stabilized the plant in Mode 3 (Hot Standby) in accordance with emergency operating procedures. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on January 31, 1993, at 0009 PST. <br /><br /> The immediate cause of the main turbine trip was an inadvertent simulated low condenser vacuum signal that satisfied turbine protection logic. <br /><br /> Investigations have eliminated all but two possible root causes: personnel error or contaminated turbine lube oil. An operator holding a test lever may have inadvertently permitted the lever to move from the full-travel position, unblocking a turbine trip signal. Contaminates in the turbine lube oil may have blocked flow in an orifice, thus enabling the turbine trip. There is no firm evidence to verify or refute either possible cause. <br /><br /> Corrective actions include issuance of a Night Order Log entry for Operations personnel review, an Operations Department Incident Summary describing the event, implementation of a design change to improve performance of the surveillance test initiating in this event, and procedure revisions to clarify maintenance and testing requirements. These corrective actions resolve both possible root causes.
3231993002 | Diablo Canyon 2 | 03/04/1993 | 09/07/1993 | 9309150145 | <strong>Entry Into Technical Specification 3.0.3 Due To Auxiliary Building Ventilation System Inoperability Caused By Inadequate Work Instructions</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1993, at 1242 PST, with Unit 2 in Mode 1 (Power Operation) at 50 percent power, Technical Specification (TS) 3.7.6.1 was not met and TS 3.0.3 was entered. One train of the auxiliary building ventilation system (ABVS) was made inoperable by the closure of a manual damper during the performance of a preventive maintenance activity. Since the other train of the ABVS was already inoperable for this maintenance activity, TS 3.0.3 was entered.<br /><br /> On March 4, 1993, at 1257 PST, PG&E operators instructed maintenance personnel to reopen the manual dampers that had been closed. One train of the ABVS air flow was reestablished and the TS 3.0.3 action statement was exited.<br /><br /> The root cause of this event was determined to be personnel error, both cognitive and noncognitive, in that a clearance was changed without adequate knowledge of the task to be performed and in that the recurring task (RT) work orders contained inadequate instructions and as a result were misinterpreted. <br /><br /> The RT work orders and RT clearance instructions were revised to provide more explicit instructions. The event was discussed with Mechanical Maintenance foremen. Instructions were issued to reemphasize the need to review Design Change Memorandums when altering clearances associated with the ABVS and/or the fuel handling building ventilation system.
3231993003 | Diablo Canyon 2 | 03/11/1993 | 04/05/1993 | 9304120115 | <strong>Technical Specification 3.9.4 Requirement For Containment Equipment Hatch Closure During Refueling Core Offload Not Met Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1993, at 1416 PST, with Unit 2 in Mode 6 (Refueling), the Limiting Conditions for Operation of Technical Specification 3.9.4 were not met when a visible gap in the seal of the containment equipment hatch was identified. Core offload had been in progress and was immediately suspended. <br /><br /> On March 12, 1993, at 1615 PST, PG&E made a four-hour, non-emergency notification to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(C). <br /><br /> Immediate corrective actions taken included suspension of core offload and the installation of additional bolting on the containment equipment hatch followed by verification of hatch sealing. <br /><br /> The root cause of the event was personnel error (cognitive), failure to follow procedure. The corrective actions are to counsel personnel involved with the containment equipment hatch closure, to enhance the procedure to reduce the possibility of misinterpretation, and to brief Mechanical Maintenance personnel on the necessity for procedural adherence.
3231993004 | Diablo Canyon 2 | 03/17/1993 | 06/24/1993 | 9307020196 | <strong>Technical Specification 3.9.12 Not Met When The Fuel Handling Building Ventilation System Was Inoperable During Fuel Movement Due To Programmatic Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1993, at 1008 PST, with Unit 2 in Mode 6 (Refueling), Technical Specification (TS) 3.9.12 was not met when fuel handling building (FHB) door 258-2 was opened to mitigate an ammonia/hydrazine leak in the FHB during fuel assembly insert shuffle. <br /><br /> Opening the FHB door caused the TS 3.9.12 requirements for FHB ventilation system (FHBVS) operability to be exceeded. TS 3.9.12 requires that, with no FHBVS operable, fuel movement activities must be suspended. <br /><br /> On March 17, 1993, at 1015 PST, the Unit 2 shift foreman (SFM) was notified that the FHB door had been opened. The SFM immediately directed an assessment of the FHB pressure. The assessment determined that TS 3.9.12 FHB negative pressure requirements had been exceeded; all fuel handling activity was immediately suspended. <br /><br /> PG&E has determined that the root cause of this event is programmatic deficiency, in that hazardous material response personnel were not aware that door 258-2 was a ventilation boundary for the FHB and the associated consequences of opening it. To prevent recurrence, plant response procedure(s) will be enhanced to clarify that the SFM should be notified prior to keeping a ventilation boundary door open for more than personnel egress.
3231993005 | Diablo Canyon 2 | 04/19/1993 | 09/07/1993 | 9309150277 | <strong>Valve Disc Separated From Its Disc Nut Due To Corrosion As A Result Of A Manufacturing Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On April 19, 1993, during the Unit 2 fifth refueling cycle initial valve alignment of the chemical and volume control system (CVCS), erratic flow indication was observed while using the Reactor Coolant Pump 2-3 seal injection flow control valve CVCS-2-8369C. <br /><br /> On April 20, CVCS-2-8369C was replaced and inspected. The disc nut was found to be in good condition. However, the disc was found to be severely corroded to the extent that the disc was no longer retained by its disc nut. Similar Unit 2 valves CVCS-2-8369A, 8369B, and 8369D were replaced and inspected. CVCS-2-8369A was found to also have a corroded disc. The equivalent Unit 1 valves were determined to not constitute an operability concern. <br /><br /> The root cause of this event has been determined to be manufacturing error, in that a valve disc made of the wrong material was installed during manufacturing. <br /><br /> Since the manufacturer is no longer in business, the corrective actions to prevent recurrence included a review of the current quality program to verify that components received by PG&E are inspected upon receipt and documentation is verified to ensure the correct composition of materials and that valves are ordered under the 1986 ASME Boiler and Pressure Vessel Code, Section III, for Pumps and Valves.
3231993006 | Diablo Canyon 2, Diablo Canyon 1 | 03/10/1993 | 07/28/1993 | 9308100178 | <strong>Anchor-Darling Check Valve Bonnet Dowel Pins Not In Compliance With Design Requirements Due To Manufacturing Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary Licensee Event Report is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022.<br /><br /> On March 10, 1993, during inspection of containment spray check valve CS-2-9002A in the Unit 2 fifth refueling outage, the bonnet dowel pins indicated on the Anchor-Darling (A/D) vendor drawing were initially thought to be missing. <br /><br /> On March 17, 1993, in preparation for dowel pin installation, further investigation identified that the dowel pins were not missing from CS-2-9002A as initially thought. The dowel pins had been manufactured to an insufficient length, causing them to fall into and become flush with the bonnet surface upon opening the valve. <br /><br /> An evaluation of this condition determined that insufficient dowel pin length would not affect the operability of the valve. <br /><br /> On March 26, 1993, inspections of similar Unit 2 A/D check valves that perform safety-related functions identified another dowel pin of insufficient length. <br /><br /> All similar Unit 2 A/D check valves performing safety-related functions were returned to the correct design requirements as necessary during the fifth refueling outage for Unit 2. Inspections and necessary repairs of all similar Unit 1 A/D check valves that perform safety-related functions will be completed during the sixth refueling outage for Unit 1.
3241993001 | Brunswick 2 | 02/05/1993 | 03/08/1993 | 9303100262 | <strong>Technical Specification Requirements Exceeded When Auxiliary Reactor Building Roof Vent Radiation Monitor Was Inadvertently De-energized</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1993 at 0245 hours with both units in cold shutdown, the Unit 2 Reactor Building Roof Vent Radiation Monitor, 2-CAC-AT-1264, was declared inoperable to support plant modification design changes to the monitor. The requirements of the radioactive gaseous effluent monitoring instrumentation Technical Specification, allow continued effluent release provided continuous auxiliary sampling is established. Continuous auxiliary sampling was established at approximately 0340 hours. The auxiliary sample pump was energized by power supplied from a 120v receptacle located on the 117, elevation of the Unit 2 Reactor Building and fed through a series of extension cords. At 1648 hours, during a required walkdown to verify sample flow, the extension cord was discovered disconnected. At approximately 1707 hours, power was restored to the auxiliary sample pump and sample flow restored. The loss of power to the auxiliary sample pump occurred because those responsible for supplying power to the auxiliary sample pump did not follow plant procedure. Immediate corrective action included the restoration of power to the auxiliary sample pump. Additional corrective actions include a revision to the auxiliary sampling procedure and a review of the event with appropriate personnel. The safety significance of this event is minimal in that both units were in cold shutdown and no work activites were in progress at the time of the event which could have caused abnormal activity concentrations in the building. A review of the Unit 2 Reactor Building continuous air sample data and effluent radiation levels immediately prior to and following the event revealed that activity concentration levels were normal. Previous similar events have been reported in LERs 1-92-007 and 1-92-025. <br /><br /> ?
3241993002 | Brunswick 2 | 02/16/1993 | 03/18/1993 | 9303220252 | <strong>Inadvertent ESF Actuation During Surveillance Testing When A Test Lead Contacted Ground</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in day 301 of an outage which began April 21, 1992. At 0944 (EST), 2MST-RWCU32R, Reactor Water Cleanup (RWCU) Area High Temperature Response Time Test, was in progress. A test cable was being connected as per step 7.4.1 of the procedure. While pulling the cable, one of the test leads inadvertently contacted ground. The grounded test lead caused fuse A71-F21 in panel 2-H12-P622 to blow resulting in unexpected equipment isolations and actuations. The fuse was replaced in accordance with work request/job order 93-AGAY1. The isolation signals were reset and the valves restored to their normal line-up, Reactor Building Ventilation and Drywell purge were restored to normal operation, and 2A SBGT was returned to standby line-up. The involved Technician was counselled and a real-time training session has been conducted with the Unit 2 Instrumentation and Control Maintenance Surveillance Test Crew personnel to make them aware of this event and expectations regarding surveillance activities. I&C and Electrical Maintenance Supervisors will discuss/review this LER with their personnel prior to May 01, 1993. This event was an unnecessary challenge to safety systems as a result of personnel error. It had minimal safety significance as the equipment operated in accordance with its design. A similar event was reported in LER 2-89-019.
3241993003 | Brunswick 2 | 04/08/1993 | 05/10/1993 | 9305110313 | <strong>Missed Primary Containment Integrity Surveillance On A Body Drain Valve For The Drywell Spray Outboard Isolation Valve.</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993, with both units in cold shutdown, an engineering field inspection resulting from NRC concerns involving the surveillance of Primary Containment System Isolation (PCIS) valve vent and drain valves identified that the 2-E11-F016B, Drywell Spray Outboard Isolation Valve, was installed in the reverse direction. This configuration exposed the associated body drain valve, 2-E11-V125, to primary containment pressure and thereby requires the valve to be periodically tested in accordance with the requirements of the Technical Specification. Because the installation configuration was not incorporated in the appropriate design documents, the 2-E11-V125 valve was not included in the PCIS valve surveillance program. Corrective actions include appropriate revisions to plant documentation to ensure the proper classification and surveillance testing of the 2-E11-V125 valve and an examination of other plant installed PCIS throttle valves to ensure proper installation configuration.<br /><br /> The present configuration of the 2-E11-F016B resulted in the 2-E11-V125 being within the Appendix "J" test boundary. Testing of the 2-E11-F016B valve verified that any observed leakage was within the acceptance criteria and was included within the Primary Containment Leakage total. Therefore, the installed configuration of the 2-E11-F016B does not create the potential for increased dose to the public. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is (B) Design, Manufacturing, Construction/Installation.
3241993004 | Brunswick 2 | 03/07/1993 | 04/06/1993 | 9304120138 | <strong>Unexpected Isolation When The Wrong Fuse Was Pulled During A Clearance</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in day 320 of a dual unit outage. The Residual Heat Removal (RHR) system was operating in the Shutdown Cooling (SDC) Mode. Reactor coolant temperature was nearly equal to 97 degrees F. Placing of clearance #2-93-698 required removal of the Unit 2 Reactor Recirculation system (B32), sample line inboard isolation (F019) solenoid valve control circuit fuse, 2-A71-F13. The tag sheet and special instructions located the fuse at position F14 (i.e., 14 positions from the top of the fuse block). The Senior Reactor Operator (SRO) and the Reactor Operator (RO) discussed the requirements for pulling the fuse and directed the RO to place the clearance. The RO found what he believed to be fuse 2-A71-F13 located at position F14 and removed it at 2224. The fuse was actually 2-A71B-F15, which supplies power to the relay logic that initiates an isolation signal for the RHR SDC Inboard Suction Throttle valve. The suction valve closed when the fuse was removed, as designed. The SRO directed the RO to install the fuse and SDC was restored at 2400. The cause of this event was determined to be inadequate labeling of the fuse block and failure of the RO to count to the 14th fuse. The corrective action is to improve the labeling of back-panel fuse blocks. This event had minimal safety significance. The loss of SDC for one hour and 36 minutes resulted in an approximate one degree F increase in reactor coolant temperature. The decay heat load would have been greater had the reactor recently been shutdown from an extended run which could have resulted in a more significant event. The cause classification for this event per the criteria of NUREG-1022 is "A", Personnel Error,
3241993005 | Brunswick 2 | 03/16/1993 | 04/19/1993 | 9304200231 | <strong>Reactor Coolant Chloride Levels Could Not Be Restored Below The Limits Within 48 Hours</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, Unit 2 was in Cold Shutdown to support the outage started April 21, 1992. The B loop of Residual Heat Removal (RHR) had been placed in Shutdown cooling at 0400 on March 16, 1993. <br /><br /> At 0500, on March 16, 1993, the Reactor Coolant sample found the chloride level at .571 ppm. This is above the Technical Specification limit of .2 ppm, and actions were initiated to find the source of the chlorides and restore chemistry. The source of the chlorides was the Residual Heat Removal Service Water (RHRSW) to RHR System cross-tie. On March 11, 1993, maintenance had been performed on the inboard and outboard RHRSW injection valves. During these repairs it was noted that the normally open drain line between the RHRSW to RHR Cross-Tie was clogged and a Work Request/Job order was written. As this piping section could not drain, service water entered the piping between the inboard injection valve and the downstream check valve when maintenance testing required cycling the inboard valve. Later, when the B loop RHR was placed in Shutdown Cooling, the chlorides migrated past the check valve and were introduced into the Reactor Coolant system. Repairs have been completed for both injection valves and the clogged section of the drain line was cleared. <br /><br /> The recovery from the high chloride condition was delayed when the site experienced a Loss of Off-site Power due to the severe winter storm that affected much of the Eastern United States. At 2030 on March 18, 1993, Reactor Coolant system chlorides were restored, but this was 15 hours 30 minutes beyond the Technical Specification time limit.
3241993006 | Brunswick 2 | 05/21/1993 | 06/18/1993 | 9306290188 | <strong>Two Inoperable Control Rod Accumulators Result In Entry Into Technical Specification 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1993, Unit 2 was operating at approximately 33% power. Periodic Test (PT) 14.2.1, Single Rod Scram Insertion Times Test was in progress. Control Rod Drive (CRD) Hydraulic Control Unit (HCU) 02-23 had the charging water header valved out in accordance with the PT when a CRD Accumulator Low Pressure/High Level alarm annunciated in the Control Room at 0259 hours. The alarm was due to a high water level in HCU 06-31. With two or more Control Rod Accumulators inoperable, Technical Specification 3.0.3 was entered which required placing the Unit in a six hour to Hot Shutdown condition. The Auxiliary Operator performing PT 14.2.1 was immediately instructed to open the charging water valve for HCU 02-23. The Accumulator was returned to service at 0300 hours and Technical Specification 3.0.3 was exited. There was no intent to commence a Unit shutdown unless problems were encountered in returning HCU 02-23 to service. The excess water was drained from HCU 06-31 and the Accumulator was returned to service at 0306 hours.<br /><br /> The cause of this event is the simultaneous inoperability of two Control Rod Drive Hydraulic Control Units. Corrective actions included valving in the charging water to HCU 02-23 and draining the excess water from HCU 06-31. <br /><br /> The safety significance of this event is minimal. When the reactor vessel is at operating pressure and the scram discharge volume is at atmospheric pressure, the Control Rod Accumulator is not needed to meet scram time requirements. The Standby Liquid Control system was available during this time.
3241993007 | Brunswick 2 | 05/22/1993 | 06/21/1993 | 9306280033 | <strong>Outside Technical Specification 3.3.2 - Trip System Not Placed In Trip Condition Within One Hour</strong><br /><i>Abstract:&nbsp;</i>On May, 22, 1993, at approximately 1230 hours, while Unit 2 was operating at approximately 50% reactor power, Operations discovered that a Main Steam Line (MSL) D High Flow Trip Unit had failed downscale. The Shift Supervisor determined that establishing a tracking Limiting Condition for Operation (LCO) was the only action required by the Technical Specifications. At approximately 1925 hours, during shift turnover, a review of the tracking LCO revealed that the appropriate compensatory measures as prescribed by the Technical Specification had not been taken. At approximately 1930 hours, the appropriate Technical Specification action was established (placing the affected trip channel in the tripped condition.) The failure to implement the appropriate action resulted from misinterpretation of the Technical Specification. The cause classification for this event per the criteria of NUREG-1022 is personnel error. Corrective actions to prevent recurrence include counselling of appropriate Operations personnel on the lessons learned from this event. This event is of minimal safety significance in that other instrumentation was available to provide isolation of Main Steam Line D in the event of a line break. Previous similar events have been reported in LERs 1-90-005, 1-91-008, 1-93-004, and 1-93-007.
3241993008 | Brunswick 2, Brunswick 1 | 07/14/1993 | 08/13/1993 | 9308170089 | <strong>Core Rated Thermal Power Exceeded The Allowable Amount Due To Feedwater Flow Inaccuracy</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1993, Unit 2 was operating at an indicated power of 100% A sodium tracer injection test had been performed on July 2, 1993, to determine the calibration constants for the main steam flow elements and as part of the Brunswick power up-rate project. The preliminary results of the test, received on July 14, 1993, indicated a non-conservative inaccuracy in feedwater flow of 1.094%. This inaccuracy in feedwater flow corresponds to an increase in core thermal power of approximately 1%. At 1621 hours on July 14, 1993, Unit 2 reduced reactor power to an indicated 2405 MWth (which corresponds to an actual reactor power of <100%). Administrative controls were established to ensure core thermal power would not be exceeded. The administrative controls will remain in effect until feedwater instrumentation can be recalibrated. <br /><br /> The cause of the event is believed to be due to erosion/corrosion of the feedwater flow elements. <br /><br /> The safety significance of the event is minimal. Reviews of thermal limit calculations determined that an overpower of approximately 1% would have a negligible impact on fuel integrity. No unsafe operating conditions or transient consequences would have occurred as a result of the feedwater flow inaccuracy. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Other.
3241993009 | Brunswick 2 | 10/16/1993 | 11/15/1993 | 9311160282 | <strong>Ads Relays Energized Due To VOM Improperly Set During Performance Of An MST.</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1993, Unit 2 was operating at 100% power. Maintenance was preparing to perform Maintenance Surveillance Test (MST) 2-MST-RHR25M, Residual Heat Removal (RHR) Pump Discharge Pressure Automatic Depressurization System (ADS) Permissive Instrument Channel Calibration. A briefing was held between Maintenance and Operations and at 1315 hours, the MST commenced. During performance of the MST, the lead technician installed a Volt Ohm Meter (VOM) in panel 2H12-P628. The procedure instructs the technician to verify zero Volts Direct Current (VDC) on the VOM. The technician verified that the VOM was indicating zero but did not notice that the VOM was set on the OHMs scale rather than the VDC scale. With the VOM on the OHMs scale it acted as a jumper in the ADS Logic. At 1500 hours, the technician actuated the 2B RHR Discharge Pressure Switch completing the logic path for the "A" ADS logic. The "Auto ADS Depress Relays Energized" annunciator was received. At 1501 hours, after verifying that plant parameters were normal, the Reactor Operator inhibited the ADS logic to ensure the reactor vessel did not inadvertently depressurize. When the lead technician learned of the annunciator he immediately checked his test equipment, found the VOM set for OHMs, and informed the control room. Operations restored the ADS system to service at 1532 hours. Corrective actions included counseling the technician and discussing the event with appropriate maintenance personnel. The safety significance was minimal. The High Pressure Coolant Injection System was operable. The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3241993010 | Brunswick 2 | 10/14/1993 | 12/01/1993 | 9312100097 | <strong>Surveillances For The Steam Jet Air Ejector "A" Train Hydrogen/Oxygen Analyzer Were Not Completed As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1993, one of the two Off-Gas Hydrogen/Oxygen (H2/O2) Analyzers, each of which monitors both Steam Jet Air Ejector (SJAE) trains, was found to be inoperable. The action statement section of Technical Specification 3.3.5.9 requires that with one operable analyzer channel per train, train operation may continue provided the recombiner temperature is monitored. Without maintaining the remaining channel Operable, including maintaining its Technical Specification Surveillances current, grab samples would be required. <br /><br /> The Off-Gas Recombiner Outlet temperatures were recorded as required by the Technical Specification Action Statement, but the SJAE "A" train Daily Channel Check for the Operable H2/O2 analyzer was inadvertently discontinued due to a misinterpretation of which analyzer input fed which recorder pen. The readings were taken from the wrong recorder and therefore no valid Hydrogen readings were obtained. The equipment labeling did not provide adequate information to indicate which instruments input to which recorder pens. This resulted in the surveillance for the SJAE "A" train channel check being incomplete until the inoperable analyzer was returned to service on October 29, 1993. <br /><br /> Although the Daily Channel Check was not performed on the Operable SJAE "A" train H2/O2 analyzer it remained fully functional and would have alerted operators to any elevated Hydrogen levels via alarms during the entire occurrence. The cause classifications for this event per the criteria of NUREG-1022 is Design, Manufacturing, Construction/Installation.
3241993011 | Brunswick 2 | 11/22/1993 | 12/21/1993 | 9401040119 | <strong>Emergency Bus Feeder Breaker Trip Results In Containment Isolation Signals</strong><br /><i>Abstract:&nbsp;</i>At 1536 on November 22, 1993, Unit 2 was operating at 100% power, when the 4160 volt Emergency Bus E-4 lost its normal power feed from Balance of Plant Bus 2C. Emergency Diesel Generator #4 started and re-energized bus E-4. Due to the momentary loss of power to bus E-4 the following Engineered Safety Features (ESF) actuated as expected: <br /><br /> Secondary Containment isolated and the Standby Gas Treatment System started. 1/2 Group 1 (Main Steam Lines) signal closed Reactor Sample valve (B32-F020) Group 2 (Drywell Floor and Equipment Drains) isolated. Group 3 Div II (Reactor Water Cleanup) isolated (G31-F004). Group 6 Div II (Containment Atmosphere Control) containment monitors isolated. Group 10 Div II (Pneumatic Nitrogen) isolated. <br /><br /> The extensive investigation of the E-4 Bus Master/Slave Breaker trip did not reveal a cause for the trip. <br /><br /> During restoration of the Reactor Water Cleanup system at 1628, a momentary (did not seal-in) steam leak detection delta temperature annunciator was received and RWCU isolation valve G31-F001 (Div I) isolated. Secondary Containment temperatures were verified to be normal and no evidence of valid process signals were found. <br /><br /> These events are of minimal safety significance as the systems responded as designed. The cause classification for this event per the criteria of NUREG-1022 is Other (Unknown).
3241993012 | Brunswick 2 | 12/04/1993 | 12/30/1993 | 9401070110 | <strong>Temperature Switch Discovered Inoperable For Primary Containment Isolation System Main Steam Line High Temperature Trip</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1993, Unit 2 was operating at 100% power. Periodic Test (PT) 2.1.22B, Primary Containment Isolation System (PCIS) Main Steam Line (MSL) Area High Temperature: System B, was being performed. A temperature switch (2-B21-TS-3229B) did not operate properly during the test and the PT was completed unsatisfactorily, but with the Technical Specification (TS) requirements met. During the Shift Supervisor review, it was determined that the failure of the 2-B21-TS-3229B caused the test to be inadequate. This switch is used to perform a complete functional test for the B2 channel. When the switch failed to operate properly, the functional test was not performed and the Technical Specifications were not met. A review was performed of the previous monthly PTs and the 2-B21-TS-3230B had failed to operate properly for the previous two months (October and November). The PTs for those months had also been completed as Unsatisfactory, but with the Technical Specifications met. On December 4, 1993, operations declared that PCIS Channel B2 was inoperable and issued a temporary revision to the PT to satisfy the surveillance requirements. The B2 channel was functionally tested using the 2-B21-TS-3230B. The channel tested satisfactorily and operations declared the channel operable. The safety significance was minimal. The 2-B21-TS-3230B tested satisfactorily which proved the channel had been operable since the test had been performed satisfactorily in September. Corrective actions included revising the PT to clarify the acceptance criteria and counseling the Operators about the event. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is pe rsonnel error.
3251993001 | Brunswick 1, Brunswick 2 | 01/21/1993 | 09/16/1993 | 9309220033 | <strong>Containment Atmospheric Control (CAC) Radiation Monitors Not Seismically Qualified</strong><br /><i>Abstract:&nbsp;</i>Units 1 and 2 were shutdown. Brunswick Nuclear Plant (BNP) is committed to Regulatory Guide (RG) 1.45, Reactor Coolant Pressure Boundary (RCPB) Leakage Detection Systems. RG 1.45 describes acceptable methods of implementing General Design Criterion (GDC) 30, Quality of Reactor Coolant Pressure Boundary. GDC 30 requires that means be provided for detecting and identifying the location of the source of RCPB leakage. RG 1.45 requires at least three separate detection methods. The RG further states the leakage detection systems should be capable of performing their functions following seismic events that do not require plant shutdown and the particulate monitoring system should remain functional when subjected to the safe shutdown earthquake (SSE). On January 21, 1993, it was determined the containment atmospheric control (CAC) airborne particulate and gaseous radioactivity monitors were not seismically qualified. Modifications to the monitors and also the sump system have been implemented to conform with the RG. This event was caused by the failure to identify and clarify an inaccurate statement in the original Safety Evaluation Report. The Design Basis Reconstitution of Brunswick safety related systems will identify additional deviations, if any, and implement corrective actions. The safety significance of this event is minimal. The loss of this equipment during a seismic event would not have prevented safe shutdown of the units and other methods such as containment temperature and pressure were available to detect RCPB leakage. The NUREG 1022 cause classification for this event is "other". Past similar events were reported in LERs 1-92-006, 012, 2-92-003, 2-92-005 and 1-93-009.
3251993002 | Brunswick 1 | 01/27/1993 | 02/26/1993 | 9303020370 | <strong>480 Volt Breaker For Standby Liquid Control Pump Was Found With Undocumented Breaker Type</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1992, during the performance of Preventive Maintenance procedure OPM-BKR008, Functional Testing of Molded Case Circuit Breakers, the technicians questioned the acceptability of a circuit breaker model TEF136M1100 installed in Motor Control Center (MCC) 1XG. This breaker compartment (EG6) is for 1A Standby Liquid Control (SLC) pump and should have been type THEF rather than type TEF. <br /><br /> The breaker was replaced on December 11, 1992, with a TEC type breaker that meets the design functional requirements. <br /><br /> By January 27, 1993, review of the engineering operability impact evaluation determined that with the non-seismically qualified breaker installed the Unit had operated outside of Technical Specification 3.1.5. This was based on the fact that, in the past, the redundant 1B SLC pump had been inoperable for periods longer than 8 hours, with the type TEF breaker installed on the redundant division (1A SLC pump breaker). Research found no maintenance activities that would have installed the TEF breaker. This, along with the March 1972 date code of the circuit breaker, indicates that this was the breaker originally supplied with the motor control center. <br /><br /> This isolated event is of minimal safety significance as the breaker performed with the same characteristics as the intended type THEF.
3251993003 | Brunswick 1 | 06/09/1993 | 07/08/1993 | 9307140153 | <strong>Engineered Safety Feature Actuations Occurred During "A" Reactor Protection System Motor-Generator Trips</strong><br /><i>Abstract:&nbsp;</i>At 2151 on June 8, 1993, the "A" Reactor Protection System (RPS) motor-generator (m-g) set tripped. The trip of the RPS channel "A" bus resulted in successful Engineered Safety Feature actuations and isolations. The isolation signals affected the inboard valves, many of which were already closed as the reactor was defueled. For the recovery, the "A" RPS bus was transferred to the alternate power source and the affected systems were realigned as required by current plant conditions. <br /><br /> At 1948 on June 11, 1993, a lightning strike on the grid caused a voltage spike which resulted in a trip of the RPS channel "A" alternate supply and subsequent successful actuations and isolations. The "A" RPS channel was re-energized from the alternate power source and the systems were realigned as required by current plant conditions. The first trip occurred due to a dirty voltage adjust potentiometer (rheostat) for the "A" m-g set voltage regulator, which has been replaced. Cleaning of remaining RPS m-g set voltage adjust potentiometers will be performed, with a procedure revision submitted to incorporate cleaning as part of periodic preventive maintenance. <br /><br /> These events are of minimal safety significance as the Unit was defueled and primary and secondary containment were not required.<br /><br /> The cause classifications for these events per the criteria of NUREG-1022 are "defective procedure" for first event and "other" for the second.
3251993004 | Brunswick 1, Brunswick 2 | 02/09/1993 | 04/30/1993 | 9305060285 | <strong>Failure To Implement Technical Specification Action Statements During Reactor Protection System Relay Maintenance and Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1993, Operations personnel identified that the actions required to satisfy the Technical Specifications were not adequately established during previous periods when the Unit 1 and Unit 2 Reactor Protection System (RPS) systems had been declared inoperable. On August 11, 1992, a Limiting Condition of Operation was initiated to support replacement of the Unit 2 RPS automatic and manual trip relays. With both of the channels of the RPS trip logic inoperable, Technical Specification requires placing at least one RPS trip system in the tripped condition, locking the reactor mode switch in the shutdown position, and verifying that all control rods are fully inserted at least once per 12 hours. Contrary to this, incomplete actions as required by Technical Specification were taken in that locking the mode switch in shutdown was the only action taken. On February 9, 1993, a revision to the same Unit 2 LCO and a Unit 1 LCO were generated which did not specify the complete actions necessary to satisfy Technical Specifications. Similarly, on November 25, 1992, when the Unit 1 RPS was declared inoperable due to an expired surveillance, the complete actions as addressed in the Technical Specification were not implemented. A root cause analysis is in progress. The results of this analysis will be reported in a supplement to this LER. On February 12, 1993, following replacement and satisfactory operability testing of the Unit 2 RPS relays, the system was restored to operability. On February 24, 1993, following satisfactory performance of the Unit 1 RPS surveillance, the system was restored to operability. These events are of no safety significance in that both Units were in Cold Shutdown with all control rods fully inserted. Previous similar events were reported in LERs 1-90-005, 1-91-008, and 2-90-001. Additional information regarding the root cause of this event and corrective actions to prevent recurrence are included in the Supplemental Information section.
3251993005 | Brunswick 1, Brunswick 2 | 02/14/1993 | 06/30/1993 | 9306290250 | <strong>Reactor Building Standby Gas Treatment Throttle Valves Are Prevented From Throttling Flow To Within Technical Specification Limits By Initiation Logic And Valve Settings.</strong><br /><i>Abstract:&nbsp;</i>Both Units are in Cold Shutdown to support the Outages started on April 21, 1992. <br /><br /> On February 14, 1993, testing of Unit 1 Standby Gas Treatment (SBGT) showed that unthrottled flow of a single train would exceed the Technical Specification rated flow limit of 3300 cfm. The results of the as-found unthrottled flow for single SBGT train runs documented the 1A SBGT flow at 4050 cfm and the 1B SBGT flow at 3950 cfm. This puts the as-found flow for the individual SBGT train approximately 22% over the Technical Specification flow limit. This design deficiency affects both Units and has existed since original construction. During events initiating a Primary Containment Group 6 isolation signal the Reactor Building Intake throttle valves (D-BFV-RB and H-BFV-RB) receive a sealed-in full open signal. <br /><br /> With the flow exceeding the rated limit, the heater sizing needed to reduce humidity to 70% would not be met. Also, above the rated flow the 'residence time' of the air moving through the carbon adsorber may be less than the 0.25 seconds needed to ensure adequate adsorber 'capture time.' As indicated above, this condition is a concern when a single SBGT train fails to start and both intake throttle valves on the common suction path remain un-throttled. This issue will be resolved prior to declaring the Standby Gas Treatment Operable. <br /><br /> This design deficiency is similar to the issue reported in LER 1-92-20.<br /><br /> See Supplemental Information section..
3251993006 | Brunswick 1, Brunswick 2 | 03/02/1993 | 04/01/1993 | 9304060055 | <strong>Inoperable Fire Barrier Penetration Seals</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1993, both Units were in Cold Shutdown as part of the outage started April 21, 1992.<br /><br /> The on-going Fire Barrier Inspection program (DG-IV.0020) identified several fire barrier penetrations with fire seal application discrepancies. The Fire Barrier Inspection program was previously implemented to establish the methodology for inspection/reinspection and documentation for fire barrier configurations against specified acceptance criteria. This inspection includes visually verifying the integrity of 100% of the fire barrier penetrations, and ensuring the correctness of the Fire Barrier Index Drawings. <br /><br /> Five cable tray penetrations through the roof of the battery rooms were identified with a Delta Maid One Shot seal (insulating cement for piping) which had previously been tested only for wall seal applications. <br /><br /> Four other non-qualified penetrations, between each of the four Emergency Diesel Generator (EDG) cells and the associated fuel oil cells were noted with classification discrepancies. Although the Fire Barrier Penetration Index showed the seal design as "N/A," the analysis to justify this could not be located. <br /><br /> These items are of minor safety significance, and as reported in LER 1-92-012 the Fire Barrier Inspection program is continuing. Repair of the deficiencies is to be completed prior to the end of the present Unit 1 outage and the next Unit 2 refueling outage.
3251993007 | Brunswick 1, Brunswick 2 | 04/24/1993 | 05/24/1993 | 9305250118 | <strong>Sampling of eactor Vessel Coolant Conductivity Not Performed</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1993, Unit 1 was in refuel with the reactor defueled. At 1757 hours, the Unit 1 fuel pool gates were installed to support vessel drain down. Prior to installation of the fuel pool gates, sampling of the reactor vessel water inventory for chlorides and conductivity was being performed in accordance with the Reactor Coolant System Chemistry Technical Specification. Following fuel pool gate installation, reactor vessel water inventory sampling was terminated and the chemical sampling of the fuel pool inventory established. On April 24, 1993, Operations recognized that sampling of the fuel pool did not satisfy the intent of the specification. The reactor coolant sampling was not maintained due to a misinterpretation of the applicable Technical Specification requirements with the fuel pool gates installed. The classification for the cause of this event per the criteria of NUREG-1022 is (A) personnel error. <br /><br /> On April 24, 1993 at 1200 hours, reactor coolant chemistry sampling was reestablished in accordance with the Technical Specification. Additional corrective actions include the appropriate procedure revisions and personnel training to ensure proper and consistent interpretation and application of the Reactor Coolant System Chemistry Technical Specification. This event is of minimal safety significance in that the acquisition and analysis of one reactor coolant conductivity sample was not performed within the time allowed by the Technical Specification and that between April 22 and April 24, 1993 no activities were in progress which would have adversely affected reactor coolant conductivity and chloride levels. Additionally, the conductivity and chloride levels present in the makeup water sources to the reactor vessel during the event were verified to be well within acceptable limits. No similar events as addressed in previous LERs have been identified.
3251993008 | Brunswick 1, Brunswick 2 | 03/13/1993 | 11/24/1993 | 9312070158 | <strong>Severe Winter Storm Results in Spurious ESF Actuations and a Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1993, beginning at 1425 hours, while Units 1 and 2 were in cold shutdown, spurious Emergency Safeguard Feature (ESF) system initiations occurred on each unit. The initiations were caused by on-site electrical distribution system voltage depressions. These depressions were due to the simultaneous loss of two of four Unit 1 and one of four Unit 2 incoming transmission lines. The loss of the transmission lines was caused by high winds resulting from a severe winter storm. High winds caused a wood pole H-frame transmission line structure to fall onto an adjacent transmission line. This resulted in the loss of two of the four off-site power sources to Unit 1. Failure of the support structure also caused deflection of crossing transmission lines resulting in the loss of one of four Unit 2 off-site power sources. The failed Unit 2 off-site power source was restored at 1622 hours. During the severe weather, from 1731 to approximately 2037 hours, voltage fluctuations resulting from the loss of a third incoming line caused four additional Unit 1 ESF initiations. The third Unit 1 incoming line was restored at approximately 2155 hours. The remaining Unit 1 off-site lines were restored by March 14, 1993 at approximately 2026 hours. On March 16, 1993, as a result of the March 13 winter storm, a Loss of Off-site Power (LOOP) occurred due to excessive salt build-up on switchyard insulators. Supplement One to this LER provides the details of the Loop and updates the status of corrective actions addressed in the Corrective Action section. Supplement Two to this LER revises the corrective action regarding detection of salt deposits on switchyard components as addressed in Supplement One to this LER.<br /><br /> The cause classification for this event per the criteria of NUREG-1022 is C (external).
3251993009 | Brunswick 1, Brunswick 2 | 04/21/1993 | 05/20/1993 | 9305250135 | <strong>Design Of Standby Gas Treatment System Would Allow Operation That Would Result In System Damage If Containment Venting Were In Progress And The Unit Experienced A Loss Of Coolant Accident.</strong><br /><i>Abstract:&nbsp;</i>Both Units had been Shutdown for a dual Unit outage that began April 21, 1992. On April 21, 1993, a follow-up evaluation of a design basis documentation review of the Standby Gas Treatment (SBGT) system found that current drywell venting procedures nonconservatively use the large Containment Atmospheric Control butterfly valves (18") as the exhaust pathway through the SBGT trains to the plant stack. With this vent path, SBGT was not protected from over pressurization damage if a Loss of Coolant Accident (LOCA) occurred when the Primary Containment was being vented. Calculations show that the SBGT filters would be subjected to 5.4 psig one second after a LOCA with a maximum pressure of 23.3 psig at the filters. These pressures exceed the SBGT filter design pressure of 2.0 psig. <br /><br /> Calculations have shown that the existing 2" bypass lines, around the large CAC valves, will limit pressure at the SBGT filter inlets to 0.35 psig. The Unit 2 Operating Procedures (OPs) have been revised to require Primary Containment venting through the 2" valves when aligned through the SBGT system and the Unit 1 OPs will be revised prior to the end of the current Refueling outage. <br /><br /> This procedural deficiency (per NUREG-1022 cause classification) is of minimal safety significance as an actual LOCA has not occurred and must happen in conjunction with the limited time the Primary Containment valves are open for venting.
3251993010 | Brunswick 1 | 06/04/1993 | 07/02/1993 | 9307070401 | <strong>Hourly Fire Watch Technical Specification Surveillance Missed During Radiography</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1993, Unit 1 was in a Refuel Outage. A Fire Protection Limiting Condition for Operation (LCO) was in effect for the Unit 1 Reactor Building South Residual Heat Removal (RHR) area. At 1225 hours, a briefing was held for the planned radiography in the South RHR area. The LCO requirement for an hourly firewatch in the South RHR area was discussed. Arrangements were made for the firewatch to notify the Health Physics (HP) Technician prior to entering the South RHR area so that the radiography job could be secured and the firewatch could be escorted through the area.<br /><br /> At 1320 hours, the firewatch entered the HP field office and requested permission to make the required hourly surveillance. The HP attempted to contact the radiographers by way of the Public Address (PA) phone in the HP field office. When no contact was made, access was denied to the firewatch. The Fire Protection Auxiliary Operator and the Control Room were notified. At 1415 hours, Operations contacted the radiographers and the radiography job was secured. The firewatch then conducted the required inspection. During a post job briefing which was held with the involved individuals, it was determined that the HP office PA phone was malfunctioning.<br /><br /> The cause of the event was the failure of the HP and Operations to establish other means of communication with the radiographers. Contributing factors to this event were the malfunctioning PA phone in the HP field office and inadequate Operations involvement. The safety significance of the event was minimal. The firewatch did not enter the radiography area while the job was in progress. Had there been a fire, the radiographers would have contacted the Control Room and the fire suppression system would have actuated as required. The cause classification for this event per the criteria of NUREG-1022 is Personnel Error
3251993011 | Brunswick 1 | 09/24/1993 | 10/22/1993 | 9310290151 | <strong>Inadequate clearance boundary results in unplanned multiple control rod insertion During scram discharge volume hydrostatic test.</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1993, Unit 1 was in a refueling outage with the Reactor core defueled. A core shroud inspection was in progress and 68 of the 137 control rods in the Reactor were fully withdrawn with no blade guides installed. The Hydraulic Control Units (HCU) of the withdrawn control rods had been placed under clearance such that cooling water remained in service with only the accumulator water side de-pressurized. When the clearance was originally written, it was recognized that some minimal valve leakage past the charging header isolation valves was possible. As part of a scram discharge volume hydrostatic test a manual scram was inserted. Of the 68 control rods that had been withdrawn and placed under clearance, 39 unexpectedly inserted. An additional 11 control rods are believed to have moved inward and then settled back to fully withdrawn position. The clearance was not adequate to prevent motion of the withdrawn control rods.<br /><br /> This event is of minimal safety significance as the reactor was defueled and no control rod damage occurred. The event cause classification per the criteria of NUREG-1022 is personnel error.
3251993012 | Brunswick 1 | 09/28/1993 | 10/20/1993 | 9310270137 | <strong>Group 1 Isolation Due To Resetting Main Turbine For Testing</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in a Refuel Outage. On September 8, 1993, Maintenance began an alignment of the Electrohydraulic Control (EHC) System. This alignment required stroking the main turbine control valves. On September 26, 1993, operations shifted to a Unit Auxiliary Transformer (UAT) Backfeed line-up which closed the main generator Power Circuit Breakers (PCBs). When the main generator PCBs are closed, an EHC logic circuit automatically selects a turbine speed of 1800 RPM when the main turbine is not tripped. On September 28, 1993, Maintenance requested permission from the Shift Supervisor (SS) to continue with the EHC work. At 0920, the Reactor Operator reset the main turbine trip, enabling the 1800 RPM turbine speed select. The turbine stop valves opened in response. This action, in conjunction with a low vacuum condition in the main condenser, generated a Group 1 Isolation signal. All systems operated as designed and the main steam drain valves closed. The main steam isolation valves (MSIVs) were already closed. The cause of the event was the lack of administrative barriers in place to prevent the initiation of a Group 1 isolation during the EHC alignment. Steps were not taken to mitigate the effects of using an alternate power source during outages. The UAT Backfeed procedure did not adequately address maintenance activities requiring resetting the main turbine trip. Corrective actions include revising the UAT Backfeed procedure to provide steps to disable the automatic speed demand feature. The safety significance was minimal. All systems operated as designed. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is defective procedure.
3251993013 | Brunswick 1, Brunswick 2 | 10/16/1993 | 11/15/1993 | 9311190222 | <strong>Main Stack Wide Range Gas Monitor Failure Results in Group 6 Isolations</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1993, at approximately 0308 hours, while Unit 2 was operating at rated power and Unit 1 was in cold shutdown, the Main Stack Wide Range Gas Monitor (WRGM) failed downscale. By design, the failure of the monitor resulted in the isolation of the Containment Atmospheric Control system on both units, the isolation of the Reactor Building Ventilation system on both units, and the initiation of the unit 2 Standby Gas Treatment system. A start of the Unit 1 SGTS did not occur because the system was under clearance for maintenance. The failure was due to a blown WRGM power supply fuse. The cause of the blown fuse is indeterminate. Auxiliary stack sampling was established by 0356 hours. The Main Stack WRGM isolation override switches on each unit were placed in the override position to allow the isolations to be reset. The isolated systems were reset and restored to a normal lineup by 0405 hours. The failed fuse was replaced by 1815 hours o October 17, 1993, and the Main Stack WRGM was restarted to allow monitoring of the equipment's operation. The Main Stack WRGM was declared operable on October 18, 1993 at approximately 1012 hours. The safety significance of this event is minimal in that auxiliary stack sampling was established in accordance with the Technical Specification requirements and the affected systems and components functioned as designed. No previous similar events as reported in LERs have been identified. (The cause classification for this event per the criteria of NUREG-1022 is "other.")
3271993001 | Sequoyah 1 | 01/24/1993 | 02/23/1993 | 9303010258 | <strong>Ice Bed Monitoring Surveillance Requirement Time Interval Exceeded Because of Poor Communications</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1993, at 0218 Eastern standard time, with Unit 1 in Mode 1 operating at 100 percent power, the Unit 1 ice bed temperature recorder in the main control room (MCR) was declared inoperable. After obtaining informal readings and observing erratic recorder operation, Limiting Condition for Operation (LCO) 3.6.5.2 was entered. With the ice bed temperature monitoring system inoperable in the MCR, ice bed temperatures at the local monitoring panel inside containment must be obtained every 12 hours. However, either the MCR surveillance nor the local surveillance were completed within the required technical specification surveillance time. The cause for the missed surveillance was poor communications and failure to properly complete the surveillance package. The validity of prior control room data and the urgency of obtaining local readings were not consistently understood or communicated. The local surveillance was completed satisfactorily, and the MCR ice bed temperature recorder was subsequently replaced and declared operable. Corrective actions include review of lessons learned with Operations personnel and development of a more formal method for initiating a conditional surveillance.
3271993002 | Sequoyah 1 | 02/05/1993 | 03/05/1993 | 9303100177 | <strong>Manual Reactor Trip as a Result of a Lock-up of the Rod Control System</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1993, at 0615 Eastern standard time, during a controlled shutdown with Unit 1 in Mode 2 operating at less than one percent power, the unit was manually tripped. Before the reactor trip, a rod urgent alarm annunciated in the main control room. This prevented the rod control system from allowing movement of the control rods in either manual or automatic modes. Based on procedural guidance, the control rods were maintained in manual during maintenance evaluation of the alarm. It was subsequently determined that the reactor would soon enter Mode 3 because of the negative reactivity insertion resulting from increasing Xenon concentration with the control rods in an abnormal withdrawn position. The decision was made to manually trip the reactor. The cause of the rod control system rod urgent alarm was determined to be in the rod control system timing circuitry. A glitch in the timing circuitry could cause the multiplexing cards to operate out of sequence and cause the rod urgent alarm to annunciate. Although no hardware problems were identified, it was concluded that the most likely component to have caused the rod control system problem was the input/output alternating current amplifier board. This board was replaced with a new board.
3271993003 | Sequoyah 1 | 02/18/1993 | 03/18/1993 | 9303250145 | <strong>Reactor Trip as a Result of an Inadvertent Trip of the Exciter Field Breaker</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1993, at 1336 Eastern standard time, with Unit 1 operating at approximately 100 percent power, a reactor trip occurred as a result of the exciter field breaker opening. The breaker opened when a senior reactor operator training instructor inadvertently actuated the trip latch on the exciter field breaker during a training exercise. The unit responded as expected following the trip and the Operations crew stabilized the unit in hot standby conditions. The reactor trip occurred as a result of the instructor failing to evaluate the risks and consequences associated with conducting training activities using operating plant components. Training on energized and/or sensitive equipment has been stopped until a policy on utilizing energized and/or sensitive equipment is established. An interim policy on opening cabinets for energized equipment has been developed and communicated to site employees. Additionally, appropriate disciplinary action has been taken.
3271993004 | Sequoyah 1 | 02/22/1993 | 06/15/1993 | 9306210366 | <strong>Containment Personnel Airlock Blind Flange Leakage Causes Airlock Inoperability</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1993, it was determined that a blind flange on the Unit 1 Elevation 734 personnel airlock outer housing was leaking. During performance of a routine surveillance instruction (SI) on the airlock, a test performer noticed leakage coming from the blind flange. The leak rate was determined to be greater than the allowable containment bypass leak rate. The outer O-ring of the blind flange was discovered to be out of the machined groove and overlapping a portion of the inner O-ring. The O-rings were replaced, and the blind flange successfully passed subsequent testing. Investigation concluded that on February 16, 1993, during the performance of the SI that tests the airlock for leakage and operability, the outer O-ring slipped out of the groove during blind flange installation. An analysis determined that the increased leakage had little effect on the offsite and control room doses. In order to prevent recurrence of this event, job-planning requirements have been evaluated to ensure reliable installation of double O-ring blind flanges. <br /><br /> Revision 1 to this LER provides additional information concerning the testing methodology and revises the corrective actions.
3271993005 | Sequoyah 1 | 03/20/1993 | 04/13/1993 | 9304190178 | <strong>Inadvertent Actuation of a Containment Isolation Valve During Response-Time Testing Performance As A Result of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1993, at 1519 Eastern standard time, with Unit 1 in cold shutdown, a containment isolation valve was inadvertently actuated. The valve is the containment isolation valve for a lower compartment containment radiation monitor sample return line. An instrument mechanic (IM) inadvertently shorted test leads after verification of response time test equipment set-up. This caused a control circuit fuse to blow, resulting in the valve traveling to the closed position. The electrical short occurred when the IM was reinstalling the test leads to the back of a chart recorder after having completed chart scaling and labeling verification. The cause of the event was personnel error with a contributing factor involving access to the input terminals at the rear of the test equipment. The control power circuit fuse was replaced, and the valve was returned to the open position. The test equipment was properly connected and testing was completed without further incident. The event was discussed with the involved individual with emphasis on self-check techniques. Instrument Maintenance personnel were instructed to ensure that adequate access is provided to test equipment when setting up the equipment.
3271993006 | Sequoyah 1 | 03/18/1993 | 04/19/1993 | 9304260134 | <strong>Inadequate Technical Specification Surveillance Performance for Four Fire Protection Valves</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1993, it was determined that two containment isolation valves in the fire protection system were not verified to isolate upon receipt of a Phase A containment isolation signal as required by Technical Specification (TS) 4.6.3.2.a. It was also determined that two other fire protection system valves that isolate upon receipt of a Phase A signal were not verified to have been reopened within the timeframe specified by TS 3.7.11.2. Investigation determined that the surveillance instruction that fulfills TS 4.6.3.2.a was revised in its entirety, to incorporate a new procedure format, just before the last performance of the surveillance. This revision failed to include the fire protection containment isolation valves in the table that verifies isolation of all valves that receive a Phase A containment isolation signal and also failed to provide a step to ensure that two other fire protection valves that receive a Phase A signal were reopened within one hour as required by TSs. The condition was determined to be caused by inadequate preparation and review of the subject procedure. The individual involved was appropriately disciplined regarding performance and management expectations.
3271993007 | Sequoyah 1 | 03/24/1993 | 04/21/1993 | 9304270091 | <strong>Inadvertent Actuation of a Containment Isolation Valve as a Result of Removal of Fuses from the Wrong Circuit</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1993, at 0214 Eastern standard time, with Unit 1 in cold shutdown, a containment isolation valve was actuated when its control power fuses were mistakenly removed. The actuated valve is a containment radiation monitor isolation valve. The event occurred when an assistant shift operations supervisor (ASOS) and an auxiliary unit operator (AUO) were independently removing fuses from the vital battery boards for an approved clearance sheet. The AUO had correctly removed fuses from eleven circuits on one column of a board. While in a crouched position, he checked the fuse location for the next column, mistakenly believed that he was in the correct location, and removed the wrong fuses. The AUO realized that a mistake had been made when he questioned the ASOS on how many fuses were removed from a specific column location immediately after removal of the wrong fuses. The AUO immediately reinstalled the fuses. He then located and removed the correct fuses. The cause of the event is personnel error as a result of inadequate self-checking and improper use of verification. The involved individuals received appropriate counseling.
3271993008 | Sequoyah 1, Sequoyah 2 | 03/26/1993 | 04/23/1993 | 9305030004 | <strong>An Emergency Gas Treatment System (EGTS) Decay Cooling Valve Failed to Open as Required During a Surveillance Requirement Test Because of Miscalibrated Flow Switches</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1993, at 0706 Eastern standard time, it was determined that the flow switches controlling the operation of the emergency gas treatment system (EGTS) decay cooling valves had been miscalibrated since April 1992. The EGTS cleanup subsystem functional test was being performed when it was discovered that one of the decay cooling valves did not open. Investigation into the failure of the valve to open revealed that a flow switch was calibrated incorrectly. Further investigation revealed that because of a personnel error, incorrect scaling values had been inadvertently incorporated into the flow-switch calibration procedure in March 1992 and subsequent performance of the calibration surveillance instruction on April 1, 1992, miscalibrated the flow switch setpoints. Operation with an inoperable technical specification component is a condition prohibited by TSs. Corrective actions included revising the procedure to incorporate the correct scaling setpoints and recalibrating the switches. The EGTS cleanup subsystem functional test verifying the valve operability will be performed before entry into Mode 4.
3271993009 | Sequoyah 1, Sequoyah 2 | 04/17/1993 | 05/17/1993 | 9305250261 | <strong>Failure to Perform Technical Specification Surveillance for Three Pipe Support Snubbers</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1993, three pipe support mechanical snubbers were found to be omitted from the surveillance instruction (SI) for visual inspection. Because of the omission, the snubbers were not inspected and tested as required by Technical Specification (TS) 3.7.9. Two snubbers are located in Unit 1 containment, one each on the safety injection and chemical and volume control (CVC) systems. The third snubber is located in Unit 2 containment on the CVC system. Investigation determined that a review performed in 1983 identified the two snubbers on the CVC system as having been omitted from the SI. Based on that review, a safety evaluation was performed which concluded that operation could continue with the snubbers inoperable. Consequently, the snubbers were not added to the SI list. The third snubber had not been identified in the initial SI snubber list. This support was installed, using a typical drawing for installation, in multiple locations. The cause of the condition was misinterpretation of the 1983 safety evaluation and improper identification of pipe supports with typical snubber design drawings. The snubbers were tested and found to be acceptable. Design drawings will be reviewed to verify the SI list accuracy, and SIs will be revised as necessary.
3271993010 | Sequoyah 1, Sequoyah 2 | 04/30/1993 | 05/28/1993 | 9306080006 | <strong>Westinghouse Electric Corporation Error Results in Nonconservative Cold Overpressure Mitigation System (COMS) Setpoints</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1993, with Unit 1 defueled and the reactor head removed, and Unit 2 in Mode 5 with reactor coolant system temperature at approximately 145 degrees Fahrenheit, a problem evaluation report was written to document the potential for nonconservative COMS setpoints. Westinghouse had identified an error in the development of the calculation for the COMS setpoints. Westinghouse indicated that this error would result in an additional 74 pounds per square inch differential that must be considered in the setpoint calculation for all Westinghouse four-loop, twelve-foot core plants. A review of the Sequoyah COMS setpoint calculations indicated that insufficient margin existed in the calculation to offset this error. The root cause of this event was the failure of Westinghouse personnel to consider various factors when performing the COMS setpoint calculation. Based on plant-specific analyses performed to resolve this deficiency, Sequoyah will either apply for early use of American Society of Mechanical Engineers Materials Subcommittee approved Code Case N-514 or set administrative controls in place to ensure COMS operability.
3271993011 | Sequoyah 1 | 05/07/1993 | 06/07/1993 | 9306110273 | <strong>Failure to Establish a Fire Watch as Required by Technical Specifications in Response to Breaching a Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1993, with Unit 1 in Mode 6 for the Unit 1 Cycle 6 refueling outage, Fire Operations personnel were conducting a fire protection inspection walkdown of the auxiliary building when they discovered a fire barrier breached without the proper compensatory measures established. On May 5, 1993, the door leading to the room that houses the 1A containment spray heat exchanger was breached and the appropriate fire watch was not established. Upon discovery of the breach, the shift operations supervisor was informed, Limiting Condition for Operation (LCO) 3.7.12 was entered, and the appropriate compensatory measure was established. An investigation revealed that the door had been breached by a TVA offsite organization performing eddy-current testing on the heat exchanger. The cause of the event was determined to be lack of knowledge of SQN fire protection requirements by the TVA offsite organization and a lack of supervision of offsite personnel by SQN personnel. The Plant Manager reinforced expectations to all site organizations regarding their responsibilities for control of offsite organizations' personnel performing work activities at SQN. The eddy-current activities were completed, the fire barrier was reestablished, and LCO 3.7.12 was exited on May 10, 1993.
3271993012 | Sequoyah 1 | 10/26/1991 | 06/03/1993 | 9306080409 | <strong>Failure to Properly Identify and Plug a Steam Generator Tube That was Subsequently Determined to Exceed the Technical Specification Plugging Limit</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1993, during performance of steam generator (S/G) tube analysis, it was discovered that during the Unit 1 Cycle 5 refueling outage, an indication on the S/G No. 1, Row 24, Column 37 tube appeared not to have been properly dispositioned. This resulted in the failure to plug a tube that was subsequently (during the next refueling outage) determined to exceed the technical specification plugging limit of 40 percent of the nominal tube wall thickness. The root cause of this condition is that the eddy-current coordinator did not ensure that the task requirements and accountabilities were properly communicated to the eddy-current analyst. Therefore, the eddy-current guidelines were not followed when the identified discrepancy was resolved by the primary analyst. The corrective action is that the eddy-current procedure will be revised to require signatures of eddy-current coordinators and senior analyst in the prework instructions to ensure better communications.
3271993013 | Sequoyah 1, Sequoyah 2 | 05/14/1993 | 06/10/1993 | 9306210281 | <strong>Failure to Perform a Fire Watch Within the Timeframe Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1993, at 1315 Eastern daylight time, it was discovered that a fire watch patrol was not performed within the timeframe required by technical specifications. The fire watch patrol had been established in the diesel generator (D/G) building as a compensatory measure for a breached fire door. The fire watch evacuated the D/G building when a fire panel alarm sounded. The fire watch mistakenly believed that the alarm was the carbon dioxide actuation/evacuation alarm. The fire panel alarm was in response to smoke from welding that was in progress in the shop area of a different site building. The alarm was reset in five minutes; however, approximately 2 hours and 20 minutes elapsed before the fire watch returned to duty. The cause of the late performance of the fire watch patrol was inadequate supervision of the fire watch individual by the fire protection foreman. The fire watch patrol was subsequently reestablished. Personnel involved were counseled on their responsibilities concerning the SQN Fire Protection Program.
3271993014 | Sequoyah 1, Sequoyah 2 | 06/11/1993 | 07/12/1993 | 9307160246 | <strong>An Inadequate Ventilation Design Results in Potential Inoperability of Vital Power Equipment</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1993, at 1315 Eastern daylight time, with Unit 1 defueled and Unit 2 in Mode 5, it was determined that an inadequate ventilation design affected vital 125-volt (V) direct current (dc) equipment operability. The ventilation configuration could result in vital 125-V dc power becoming inoperable for both trains of both units from a single failure of the ventilation. The design configuration provides Train B ventilation to the Units 1 and 2 Train B 480-V board rooms. This results in one train of ventilation supplying four vital inverter and battery charger channels. Also, two of the vital battery rooms are supplied by the incorrect ventilation train. In 1991, an evaluation was performed indicating that the equipment was operable, and compensatory measures were established in the event that Train B cooling was lost. Subsequent reviews determined that the supporting logic of the evaluation may not have properly considered the use of temporary ventilation and non-1E power supplies. As a result, the design configuration of the ventilation could have impacted equipment operability. The most probable cause for the inadequate design is inadequate interdiscipline review of the initial design. The design is being modified and the new design configuration will be implemented to provide correct train ventilation to the affected equipment.
3271993015 | Sequoyah 1, Sequoyah 2 | 06/14/1993 | 07/14/1993 | 9307220275 | <strong>Diesel Generator (D/G) Start as the Result of an Incorrectly Wired Current Transformer</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1993, with Unit 1 defueled and Unit 2 in cold shutdown, Mode 5, the 1A start bus alternate feeder breaker tripped upon the start of the Unit 1 reactor coolant pump No. 1 motor. This resulted in the loss of voltage to the 1B-B 6.9 kilovolt shutdown board. The four emergency diesel generators (D/G) started and the 1B-B D/G supplied power to the 1B-B 6.9 kV shutdown board, as designed. The event has been determined to have been caused by an incorrectly wired current transformer in the alternate feeder breaker protection circuitry. Plant equipment response during this event was consistent with that specified in the Final Safety Analysis Report for a loss of offsite power event.
3271993016 | Sequoyah 1, Sequoyah 2 | 06/19/1993 | 07/19/1993 | 9307280153 | <strong>A Phase A Isolation, Auxiliary Building Isolation, and Containment Ventilation Isolation Were Manually Initiated as a Result of Fuel Assembly Failing to Remain in an Upright Position After Being Released</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1993, at 1054 Eastern daylight time (EDT), during fuel loading activities, a fuel assembly immediately tilted over after being released into position. The fuel assembly came to rest against the south core baffle plate leaning at an angle approximately 18 degrees from vertical. At 1154 EDT, a Phase A isolation, auxiliary building isolation, and containment ventilation isolation were manually initiated in accordance with abnormal operating procedures in response to the fuel-handling event.
3271993017 | Sequoyah 1, Sequoyah 2 | 06/21/1993 | 07/30/1993 | 9308060285 | <strong>Failure to Comply with Technical Specification Limiting Condition for Operation Action Statement and Notify NRC by Telephone Regarding the Auxiliary Building Fire Suppression System Being Nonfunctional</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1993, with Unit 1 in Mode 6 for the Cycle 6 refueling outage and Unit 2 in Mode 5 for a maintenance outage, it was discovered that a 24-hour telephone notification to NRC had not been carried out as required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.11.1 Action Statement (b)(2)(a). The TS requires that a backup suppression system be established and that NRC be notified any time the high pressure fire protection (HPFP) water suppression system is inoperable. A portion of the auxiliary building HPFP water suppression system had been taken out of service for a planned maintenance activity. Appropriate compensatory measures had been established. The cause of the event was personnel error because of an inadequate review of the LCO action statement. Upon discovery, the notification was made and an incident investigation was initiated. The maintenance activity was completed and the system was returned to service on July 3, 1993.
3271993018 | Sequoyah 1, Sequoyah 2 | 07/04/1993 | 07/30/1993 | 9308060308 | <strong>Diesel Generator (D/G) Start as the Result of Improper Work Order Planning</strong><br /><i>Abstract:&nbsp;</i>On July 4, 1993, with Unit 1 in Mode 6, refueling, and Unit 2 in Mode 5, cold shutdown, while performing a work order to remove a blackout relay, a loss of voltage signal to the 1BB 6.9-kilovolt shutdown board was generated. This resulted in a start signal being sent to all four diesel generators (D/Gs). The 1BB D/G was removed from service for maintenance and did not start. The 1AA, 2AA, and 2BB D/Gs started. Since an actual loss of voltage condition only existed on the 1BB shutdown board, the running D/Gs did not load onto their respective shutdown boards. The cause of this event was improper planning of the work order to replace the blackout relay. Plant equipment response was consistent with that specified in the Final Safety Analysis Report. Thus, the event did not affect the health and safety of the public. The personnel involved are being held responsible for their actions and appropriate disciplinary actions have been taken.
3271993019 | Sequoyah 1 | 07/13/1993 | 08/11/1993 | 9308180015 | <strong>Containment Isolation Resulting From a Loss of Control Air</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1993, at 1256 Eastern daylight time, the A and B nonessential control air headers were both isolated during implementation of clearance tagging. Clearance tagging was being performed to facilitate scheduled piping modifications on the nonessential control air system. Both headers were inadvertently isolated as a result of an inaccurate drawing that was used to develop the clearance boundary. The drawing continuation flag that provides the continuation reference from one drawing to another incorrectly referenced the wrong location. Nonessential air components, including some containment isolation valves, isolated. Control air was supplied to the components required to operate to ensure safe shutdown or to mitigate the consequences of an accident. Operations personnel quickly determined the cause for the loss of nonessential air, dispatched an operator to reopen some of the closed valves, and restored system air pressure. It was determined that the cause for the drawing error was personnel error. Similar systems were walked down to verify drawing continuation flags. No other drawing continuation flag errors were identified. The drawing error has been corrected.
3271993020 | Sequoyah 1, Sequoyah 2 | 06/19/1993 | 08/17/1993 | 9308230068 | <strong>Auxiliary Building Gas Treatment System Start as a Result of a Fire in the Unit 2 General Supply Fan Room</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1993, at 1135 Eastern daylight time (EDT), Operations received notification of a fire in the Unit 2 auxiliary building general supply fan room on Elevation 714. Upon notification, the auxiliary building supply and exhaust fans were stopped and Train B of the auxiliary building gas treatment system was manually initiated to prevent airborne radioactivity increases and to maintain negative pressure in the auxiliary building. A team was dispatched to the area, and it was discovered that the steam generator wet layup recirculation pump No. 4 motor was on fire. The fire was extinguished and auxiliary building ventilation was returned to normal.
3271993021 | Sequoyah 1 | 07/20/1993 | 08/18/1993 | 9308250168 | <strong>Failure to Perform a Surveillance in the Refueling Canal Because of Miscommunication</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1993, at approximately 1800 Eastern daylight time, it was discovered that a boron analysis of the refueling canal as required by Technical Specification 3.9.1 had not been performed. The boron analysis is required when the refueling canal is filled. On several occasions between July 14 and July 19, 1993, Chemistry personnel requested the status of the refueling canal from Operations. Operations reported that the canal was drained when only the transfer canal was actually drained. The cause of this event was inadequate communications between Chemistry and Operations personnel. During telephone conversations between the two groups the terms refueling canal and transfer canal were used interchangeably without the proper understanding of the terms that were being used. Therefore, Chemistry personnel considered the refueling canal to be drained and did not obtain the sample to be analyzed. A sample of the refueling canal was obtained, analyzed, and determined to be acceptable. Appropriate personnel have been informed of the potential for miscommunication, and procedures will be revised as appropriate.
3271993022 | Sequoyah 1, Sequoyah 2 | 08/05/1993 | 09/07/1993 | 9309130274 | <strong>Inability of the Auxiliary Building Gas Treatment System (ABGTS) to Perform its Intended Safety Function in the Event of an Accident</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1993, with Unit 1 in Mode 6 for the Unit 1 Cycle 6 refueling outage and Unit 2 in mode 5, it was determined that there was a potential for a situation to exist at SQN where the ABGTS could fail to effectively function as required during an accident. During an accident, the ABGTS is designed to develop and maintain a negative pressure in the auxiliary building secondary containment enclosure (ABSCE) and filter the exhausted air to prevent or minimize the release of radiation to the outside environment. To accomplish this, it is necessary for the auxiliary building general ventilation supply and exhaust fans and the fuel-handling exhaust fans to be stopped and the ABSCE isolation dampers to be closed. The control circuitry for the fans is non-1E; therefore, it is not assured that they will fail safe in the off position. The leakage of the isolation dampers with the normal supply and exhaust fans running is sufficient to negate the ABGTS design function. The failure to stop the normal ventilation fans could cause the offsite dose limits to be exceeded in approximately 90 minutes. The corrective action to ensure that the ABGTS is not negated by the leakage of the isolation dampers is to revise the appropriate emergency procedures to verify that in the event of an accident, the fans have been stopped.
3271993023 | Sequoyah 1, Sequoyah 2 | 08/19/1993 | 09/20/1993 | 9309280346 | <strong>Degradation of Fire Doors as a Result of Incorrect Door Hinge Material</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1993, with Unit 1 in Mode 6 (refueling) and Unit 2 in Mode 5 (cold shutdown), it was determined that various fire doors in the plant were installed with hinges that do not meet the National Fire Protection Association 80 requirements. Some hinges on approximately 100 fire doors were found to be fabricated from brass, bronze, or stainless steel, and not carbon steel. The condition was discovered during a fire door configuration verification where fire door, frame, and hardware inspections were being performed. Impairment permits were prepared for the affected fire doors, and appropriate compensatory action was taken. The condition was caused by insufficient information contained on the drawings that were used in the original construction procurement specification, resulting in procurement of nonsteel hinges. Work documents have been initiated, and the replacement of brass or bronze hinges is in progress. This report satisfies the special report requirements of Technical Specification 3.7.12 Action Statement (a).
3271993024 | Sequoyah 1, Sequoyah 2 | 08/24/1993 | 09/23/1993 | 9309280076 | <strong>Main Feedwater Line Break Accident Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>This event is being reported as a voluntary LER to inform the NRC staff of a condition involving the accident scenario assumptions associated with the main feedwater line-break analysis. The current feedwater line-break analysis assumes the worst-case single failure to be the turbine-driven auxiliary feedwater (AFW) pump. However, during a review of a level control valve modification, it was noted that Westinghouse Electric Corporation had considered a single failure of a motor-driven AFW pump during the Eagle 21 reanalysis in 1989. This analysis assumes that 1,070 gallons per minute (GPM) of AFW flow (410 gpm from one motor-driven AFW pump and 660 gpm from the turbine-driven AFW pump) was available. The design flow capacity of the turbine-driven AFW pump is 880 gpm. The technical specification surveillance test acceptance criteria only tests for a pump flow capacity of 440 gpm. A review of test data from the turbine-driven pump indicates that the pump's flow capacity is greater than the 660 gpm required for this accident scenario. The cause of this condition was a failure of the engineering design reviews by Westinghouse and TVA to ensure that valid assumptions were used in the analysis. Westinghouse is presently reviewing the other AFW analyses to ensure that all design assumptions have been properly verified.
3271993025 | Sequoyah 1, Sequoyah 2 | 08/25/1993 | 09/23/1993 | 9309290318 | <strong>Failure to Perform American Society of Mechanical Engineers (ASME) Section XI Bolting Inspections</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1993, with Unit 1 in Mode 6 (refueling) and Unit 2 in Mode 5 (cold shutdown), it was determined that the ASME Section XI bolting inspections of the second-stage reactor coolant pump (RCP) cartridge seal assemblies had not been performed following initial modification. Also, ASME reports and evaluations were not completed following subsequent replacement. Therefore, the requirements of Technical Specification 4.0.5 had not been satisfied. Each three-stage seal assembly was replaced with a design that changed the pressure-retaining function of the second-stage seal housing. The condition was discovered during development of a revision to the procedure that provides guidance for RCP maintenance. The cause of the condition was personnel error. The cognizant engineer responsible for modification implementation did not realize that the pressure boundary of the new seal design was different and, therefore, did not obtain the appropriate Section XI inspections for the bolts. Also, the cognizant engineer over seal replacement did not realize that the procedure specified for the work was inadequate. Program controls have been changed to require the ASME Section XI program specialist to perform an impact review on design change packages to ensure that Section XI requirements are met. The appropriate procedure will be revised to include ASME Section XI repair/replacement guidance.
3271993026 | Sequoyah 1, Sequoyah 2 | 09/07/1993 | 10/18/1993 | 9310260116 | <strong>Unqualified Coatings in Containment Exceed Design Basis Limit</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1993, it was determined that the design basis limit for unqualified coatings inside containment had been exceeded. On September 7, 1993, walkdowns were being performed on Unit 2 to identify the amount of unqualified coatings inside containment in the area that has the potential for the coatings to be transported to the containment sump. During the inspection around Reactor Coolant Pump (RCP) No. 4, it appeared that the quantity of unqualified coatings outside the boundary of the RCP motor platform screens, previously installed to prevent unqualified coatings from the RCP reaching the sump, was greater than evaluated. Upon investigation, it was determined that additional unqualified coatings on the inside of the RCP motor stand had not been evaluated. This was considered to be a problem since there are openings at the bottom of the stand that would provide a transport path for the unqualified coatings to the containment sump. The root cause for not identifying all the exposed surfaces that have unqualified coatings on the RCP is inattention to detail. A modification was initiated and implemented on Unit 2 to install screens at the openings on the RCP motor stand to prevent unqualified coatings from reaching the sump. Screens will be installed at the openings on the Unit I RCP motor stand before restart.
3271993027 | Sequoyah 1, Sequoyah 2 | 09/21/1993 | 01/21/1994 | 9402100225 | <strong>Degraded Fire Dampers as a Result of a Failure to Install the Dampers in Accordance With Design Drawings</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to provide schedule information for evaluation and resolution of degraded fire dampers. On September 21, 1993, with Units 1 and 2 in Mode 5 (cold shutdown), it was determined that some fire dampers were installed in configurations that result in a potential reduction of the damper's fire barrier capability. The condition was discovered as a result of a modification to a segment of the plant ventilation system. Upon determination that a degraded condition existed, appropriate compensatory action was taken. The condition was a result of construction personnel not following the design drawings during the initial installation of the dampers. A contributing factor was that in some cases, the design drawings did not provide specific details (bolt spacing, clearance dimensions) to ensure that the dampers were installed in a qualified fire-barrier configuration. Fire damper installations in safety-related areas are being individually evaluated for identification and correction of deficient conditions. This report satisfies the special report requirements in accordance with Technical Specification 3.7.12 Action Statement (a).
3271993028 | Sequoyah 1, Sequoyah 2 | 11/04/1993 | 12/06/1993 | 9312130384 | <strong>Containment Isolation Valves Not Verified Closed or Secured</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1993, with Unit 1 in Mode 5 for a refueling outage, Engineering personnel were performing a walkdown inside the Unit 1 reactor building. During the walkdown, personnel identified three auxiliary feedwater vent valves that were not depicted on any flow prints. The subject valves were between the containment isolation valves and, thus, part of the containment isolation boundary. Technical specifications require this type of valve to be closed and secured. Since the subject valves were not depicted on the flow prints, the valves had not been included in the administrative procedure that verifies these types of valves are closed and secured. The subsequent review of the Unit 2 configuration concluded that plug valves existed in the same location as the Unit 1 vent valves. These valves also were not verified closed and secured. The cause of this condition was an Engineering practice that allowed the installation of vent valves on instrument lines at the discretion of Engineering personnel without showing the valves on the appropriate drawing. The three AFW vent valves will be removed and the lines will be capped before the restart of Unit 1 from the current outage. The Unit 2 plug valves are closed and plugged in compliance with technical specifications.
3271993029 | Sequoyah 1, Sequoyah 2 | 11/16/1993 | 12/13/1993 | 9312270020 | <strong>Inoperable Check Valves in the Component Cooling System as a Result of a Build-up of Corrosion Products Between Valve Components.</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1993, with Unit 1 in Mode 5 (cold shutdown) and Unit 2 in power operation at approximately 100 percent power, it was determined that both units were outside their design basis as a result of eight inoperable check valves in the Unit 1 component cooling system piping upstream of the reactor coolant pump thermal barrier heat exchangers. The Unit 1 condition was discovered by radiographic inspections of the check valves. The inspections indicated that seven of eight check valves were stuck in the open position. The eighth Unit 1 valve was found to be improperly assembled. Subsequent inspection of corresponding Unit 2 check valves identified seven valves that were stuck in the open position. The cause of the condition was oxide wedging (iron oxide corrosion product buildup) between valve components (piston and bonnet). The Unit 2 valves were cleaned, reassembled, and returned to service. The carbon steel bonnets on the Unit 1 valves will be replaced with stainless steel. A Unit 2 action plan will be developed and implemented during the upcoming refueling outage to ensure check-valve operability or to replace the Unit 2 carbon steel bonnets with stainless steel.
3271993030 | Sequoyah 1, Sequoyah 2 | 12/21/1993 | 01/20/1994 | 9401280049 | <strong>Failure to Perform a Surveillance Requirement (SR) on an Essential Raw Cooling Water (ERCW) Valve</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1993, with Unit 1 in Mode 5 for a refueling outage and Unit 2 in Mode 1 operating at approximately 100 percent rated thermal power, plant personnel determined that the surveillance requirement for an ERCW valve was not being met. The valve is the supply isolation valve on the ERCW system to the OB1 and OB2 component cooling water heat exchangers. This valve is required to travel to the 35 percent open position upon receipt of a safety injection signal. Technical Specification (TS) SR 4.7.4.b.1 requires that this valve be tested once every 18 months to ensure that the valve will travel to the correct position upon receipt of a safety injection signal. The last performance of this test was in March 1990 for Unit 1 and in September 1990 for Unit 2. The root cause of this event was a personnel error in the performance of a procedure revision. As interim corrective action for Unit 2, the subject ERCW valve was opened 35 percent and the power was removed from the valve. This will ensure that the valve will be in the TS required position in the event of a safety injection signal. The applicable surveillance instructions will be revised to incorporate this SR.
3281993001 | Sequoyah 2 | 03/01/1993 | 03/31/1993 | 9304060077 | <strong>Extraction Steam Line Rupture Causes High Generator Output Voltage and Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1993, Unit 2 experienced a steam leak on the non-nuclear side of the plant. The No. 2 extraction line to the B2 feedwater heater ruptured, causing a 3- by 6-inch hole in the line. Steam escaping from the ruptured pipe flowed into the nearby main generator voltage regulator cubicle, resulting in regulator malfunction and voltage increasing to approximately 27 kilovolts (kV) (normal operating voltage is approximately 24 kV). As a result of the high voltage on the system and the inability to reduce the voltage, the reactor was manually tripped. The plant response during and after the manual reactor trip was consistent with responses described in the Final Safety Analysis Report. The root cause of this event was a programmatic failure of the erosion/corrosion (E/C) program resulting from insufficient management oversight and review of the program. Corrective actions include repair of affected piping and components; E/C program review and Engineering evaluation of other piping susceptible to erosion, including inspections and repairs/replacements; evaluation of impact of over-voltage condition on plant equipment; and review of other site technical programs.
3281993002 | Sequoyah 2 | 03/18/1993 | 08/25/1993 | 9308310278 | <strong>Containment Boundary Isolation Valves Discovered Misconfigured for an Indeterminate Reason</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1993, at approximately 2030 Eastern standard time, during the performance of a routine containment integrity surveillance, five 1/2-inch drain valves (four component cooling water system and one essential raw cooling water system) were found by the test personnel to be misconfigured. None of the valves had the required locking device installed, and two of the valves were open approximately one turn. The valves were immediately closed and locking devices were procured and installed. Investigation identified several possible causes for the condition which included procedure weaknesses and configuration control/performance/process weaknesses. Corrective actions to address these causes include procedure reviews and revisions, extensive plant configuration verification efforts, Operations performance improvement initiatives, and process improvements. Revision 1 to this LER provides additional information and revised corrective actions concerning this event.
3281993003 | Sequoyah 2 | 03/21/1993 | 04/20/1993 | 9304260069 | <strong>Inadvertent Actuation of Engineered Safety Feature Component as a Result of Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1993, at 1512 Eastern standard time, with Unit 2 in cold shutdown, a containment isolation valve was spuriously actuated as a result of equipment failure. The actuated containment isolation valve is a system process valve for the reactor coolant drain tank pump discharge line. Valve actuation was initiated by an invalid high radiation signal from a radiation monitor (RM) that does not provide an engineered safety feature (ESF) function. Investigation determined that the RM began spiking and closing the valve on November 13, 1992. Operations personnel had immediately initiated a work document on November 13, 1992, to repair the RM; the valve closure was not considered reportable. The RM spiked routinely and closed the valve between November 13, 1992, and March 21, 1993. The work document was not escalated by Operations because of the lack of sensitivity to the repetitive equipment failure. On March 21, 1993, actuation of the valve was conservatively determined to be reportable; subsequently, the work document priority was raised. Troubleshooting identified the cause of the RM failure to be a failed detector; the detector was replaced.
3281993004 | Sequoyah 2 | 03/23/1993 | 04/22/1993 | 9304270112 | <strong>Failure to Perform a Technical Specification (TS) Surveillance Instruction for Verification of Ice Condenser Chemistry Within the Required TS Timeframe</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1993, with Unit 2 in Mode 5, Chemistry personnel were preparing to perform the annually-required surveillance instruction (SI) for ice condenser chemistry when it was discovered that the surveillance interval as specified in Technical Specification (TS) 4.6.5.1 had been exceeded. The last performance of the SI was on September 21, 1991. In March 1992, a non-TS special SI that measured the boron concentration of the ice before it was blown into the ice condenser ice baskets was erroneously accepted as a completed test that satisfied TS Surveillance Requirement 4.6.5.1(b). The acceptance of the SI as a TS test caused the regular periodical SI to be rescheduled. Upon discovery of the missed surveillance, the surveillance test verifying the acceptability of the chemistry of the ice was immediately performed by the Chemistry test personnel and found to meet the acceptance criteria. The cause of this event was ineffective communication between Chemistry personnel and Technical Information Center personnel, coupled with a lack of knowledge of the rescheduling matrix by the SI test director and poor procedural guidance. The procedure governing the surveillance test program will be revised to clearly delineate the test director's and SI reviewer's responsibilities concerning the completion of the data sheets for verification of SI performance.
3281993005 | Sequoyah 2 | 10/18/1993 | 02/22/1994 | 9403090065 | <strong>Manual Actuations of the Reactor Trip Breakers as a Result of Malfunctioning Demand Step Counters</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to change the corrective action as a result of a problem encountered during the installation of electronic counters. On October 18, 1993, at 0640 Eastern daylight time (EDT); October 24, 1993, at 1149 EDT; and October 25, 1993, at 1720 EDT, with Unit 2 in Mode 3 (hot standby), the reactor trip breakers were opened as a result of demand step counter malfunctions in the Shutdown Bank "D" position. The Technical Specification (TS) 3.1.3.3 action statement requires opening the reactor trip breakers when the group demand counter is inoperable or not capable of determining demand position within plus or minus 2 steps during Mode 3 operation. In each case the demand step counter did not provide the correct step indication within the plus or minus 2-step TS requirement. Each replacement counter received preinstallation testing. No deficiencies were identified during the preinstallation testing. Investigation into the occurrences determined that the display tumblers had excessive play, resulting in improper movement of the tumblers upon receipt of an actuation signal. The defective demand step counters were found to have sequential serial numbers and were procured from one supplier. A counter from a different supplier was obtained, verified to be functional, and placed in service.
3281993006 | Sequoyah 2 | 12/03/1993 | 01/06/1994 | 9401130027 | <strong>Reactor Trip As The Result of Generator Exciter Problems</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1993, at 1055 Eastern standard time, with Unit 2 operating at approximately 100 percent rated thermal power, Unit 2 experienced a turbine trip and subsequent reactor trip. Operations personnel observed erratic indications associated with the generator excitation system. Subsequently, a generator stator cooling failure alarm actuated. This circuit starts a 45-second time delay relay that results in a turbine/generator trip. Based on these conditions, the shift operations supervisor decided to manually trip the reactor. However, before manually tripping the reactor, the generator stator cooling failure relay actuated causing the turbine/generator trip and subsequent reactor trip. The root cause of the event was the overexcitation of the generator. The overexcitation was determined to have been caused by multiple grounds in the generator exciter. The Unit 2 exciter has been replaced.
3311993001 | Duane Arnold | 02/11/1993 | 03/04/1993 | 9303150164 | <strong>Automatic Standby Diesel Generator Starts Due to Momentary Essential Bus Undervoltage During Ice Storm</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1993, with the plant operating at 100% power, both Standby Diesel Generators (SBDGs) automatically started three separate times but were not required to load. <br /><br /> The cause of each of the automatic starts was a sensed momentary under-voltage condition on both essential buses which was monitored by bus under-voltage relays that feed the SBDG start logics. The sensed momentary under-voltage conditions were caused by momentary grid disturbances during an ice storm. <br /><br /> Following verification that the essential buses were being powered from their normal sources, the SBDGs were secured and returned to standby mode. Reactor power was temporarily reduced until the weather improved. <br /><br /> This event had no effect on the safe operation of the plant.
3311993002 | Duane Arnold | 04/28/1993 | 05/21/1993 | 9306010059 | <strong>Missed Surveillance of Primary Containment Airlock Due To Different Interpretations of a Technical Specification Submittal</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1993, while the plant was operating at 95.5% power, it was determined that the testing program for the primary containment airlock was not in full compliance with the Technical Specification and 10CFR50 Appendix J requirements. Leak testing after securing the airlock had not been performed. The cause of this was different interpretations of a 1984 Technical Specification revision that was based on a 1978 submittal. <br /><br /> The historical test results, the redundant design, and the low probability of an event requiring primary containment, support the conclusion that there is no effect on safe operation. The NRC has granted Enforcement Discretion until a temporary exemption request is reviewed. The airlock will not be opened until the next plant shutdown, scheduled for July 1993. The required leak tests will be performed prior to startup from the next shutdown. The Technical Specification revision process has been strengthened and communications have been improved since 1984.
3311993003 | Duane Arnold | 05/25/1993 | 06/18/1993 | 9306290196 | <strong>Primary Containment Isolation System Half Group III Isolation due to Loss of Jumper to Terminal Continuity During Planned Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1993 the plant was operating at 88% power when a "B" side Primary Containment Isolation System (PCIS) Group III isolation occurred along with the initiation of the "B" Standby Gas Treatment (SBGT) System. This event occurred during pre-planned maintenance that had been identified as having the potential to cause the PCIS isolation and SBGT initiation. Jumper to terminal continuity was lost in a control room back panel during maintenance to install standoff jacks. Plant systems responded as expected, the PCIS isolation was reset, and SBGT was secured. There was no effect on safe operation of the plant.
3311993004 | Duane Arnold | 06/11/1993 | 07/09/1993 | 9307200004 | <strong>'A' Emergency Diesel Generator Trip While Starting During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1993, with the plant operating at 85% power, while performing the Emergency Diesel Generator (EDG) operability surveillance, the 'A' EDG tripped approximately three seconds after the initial start signal. The most probable cause was determined to be a partially latched condition of the mechanical trip mechanism, although this condition was not able to be recreated during troubleshooting efforts. The partial latching may have challenged the operability of a single EDG for a period exceeding the technical specification limiting condition for operation of seven days. Corrective actions for this event include procedural enhancements, redundant reset operations, and engine stand improvements to facilitate efficient operation of the reset lever.
3311993005 | Duane Arnold | 08/01/1993 | 11/08/1993 | 9311160305 | <strong>Main Steam Isolation Valves Have Unacceptable Leak Rate Results Due To Valve Internal Conditions</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1993, with the reactor in cold shutdown, local leak rate testing was performed on the main steam isolation valves. Two of the eight valves failed to meet the established leakage acceptance criteria. The excess leakage of the MSIVs has been attributed to the valve internal conditions. <br /><br /> The main steam isolation valves were re-machined and retested with acceptable leakage rates. This LER is submitted for information only.
3311993006 | Duane Arnold | 08/13/1993 | 09/09/1993 | 9309170043 | <strong>Unexpected Primary Containment Isolation System Partial Group 3 Isolation due to Inadequate Written and Verbal Communications</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1993 the plant was in cold shutdown for refueling when a partial Primary Containment Isolation System (PCIS) Group 3 isolation occurred. This event occurred while preparing plant systems for maintenance by de-energizing the Reactor Protection System (RPS). Although the Operating Instruction (OI) for de-energizing RPS stated that this isolation would occur, it was unexpected because operators thought that the entire isolation had been disabled by a Temporary Modification (TM) using another OI, when in fact, only part of this isolation is disabled by this OI. The purpose of the TM was not accurately stated on the TM and verbal communications between Engineering and Operations were inadequate to communicate the purpose. This event will be reviewed by Engineering, Operations, and Maintenance to stress the need for good written and verbal communications. There was no effect on safe operation of the plant.
3311993007 | Duane Arnold | 09/21/1993 | 10/15/1993 | 9310210028 | <strong>Unexpected Shutdown Cooling Isolation Due to Procedural Inadequacies</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1993, the plant was in cold shutdown for refueling when a partial Primary Containment Isolation System (PCIS) Group 4 isolation occurred ('A' shutdown cooling). This event occurred while transferring Reactor Protection System (RPS) power supply sources from the alternate source to the 'A' RPS motor generator. Isolation valves were, per procedure, deenergized open during the transfer to prevent unwanted isolations. Following the transfer, PCIS Divisions (1 and 2) were reset and annunciators PCIS GROUPS (1 through 5) ISOLATIONS were verified reset. The operator was then directed, by procedure, to reenergize the shutdown cooling suction and inject valves. Upon closing the breaker to the 'A' residual heat removal inboard inject valve, the valve went closed, isolating shutdown cooling. This occurred due to the isolation signal being locked in for this valve by design. There was no measurable increase in reactor vessel temperatures. The valve was reopened within nineteen seconds. The procedure was revised to give direction to reset the locked-in signal prior to reenergizing the valve.
3311993008 | Duane Arnold | 09/16/1993 | 10/18/1993 | 9310220201 | <strong>'B' Standby Diesel Generator Output Breaker Failure to Close</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1993, the 'B' Standby Diesel Generator (SBDG) output breaker, 1A411, failed to close during the performance of the Loss of Offsite Power-Loss of Coolant Accident (LOOP-LOCA) surveillance test. The cause was an improper clearance between the breaker plunger and the switchgear stationary auxiliary switch mechanism on the Standby Transformer feeder breaker, 1A401, to essential bus 1A4. This improper clearance disabled one of the closure permissives for 1A411. <br /><br /> The corrective actions included readjusting the gap between the breaker plunger and the stationary auxiliary switch to within the specifications intended by the breaker vendor and testing.
3311993009 | Duane Arnold | 10/05/1993 | 11/04/1993 | 9311100187 | <strong>High Pressure Coolant Injection Steam Supply Isolation Valve Tripped Its Supply Breaker Due To Inappropriate Torque Switch Setting</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, October 5, 1993 and Thursday, October 7, 1993, the High Pressure Coolant Injection (HPCI) steam supply outboard isolation valve tripped its supply breaker after the valve was completely closed. Plant operating parameters were unaffected by this event. The breaker trip is due to an inappropriate torque switch setting. HPCI was declared inoperable and the reactor startup was halted. All withdrawn control rods were reinserted. The torque switch and motor were replaced. Testing and an evaluation were performed and the torque switch was set to its optimal setting.
3311993010 | Duane Arnold | 10/26/1993 | 11/19/1993 | 9312020450 | <strong>Reactor Scram Due To Grounded Turbine Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1993, with the plant operating at 100% power, a full automatic reactor scram occurred. The scram signals were turbine control valve fast closure and average power range monitor high flux. An unknown ground at a turbine solenoid valve, combined with a momentary arc caused by maintenance on a fan in the electro-hydraulic control (EHC) cabinet in the control room, resulted in completion of the circuit to close one of the four turbine control valves. <br /><br /> All control rods inserted and vessel level dropped below the low level setpoint causing groups 2-5 primary containment isolations. Vessel level was restored and returned to normal. Reactor pressure was controlled by the turbine bypass - valves. There were no emergency core cooling system actuations and no safety relief valve openings. <br /><br /> The ground at the turbine solenoid valve was repaired and other turbine valve circuits were checked for grounds but none were found. The reactor was re-started on October 28, 1993.
3311993011 | Duane Arnold | 11/11/1993 | 12/03/1993 | 9312140334 | <strong>Loss of Control Building Chillers Due to Ineffective Setup for Low Load Conditions</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1993, both "A" and "B" control building chillers were inoperable. The "A" chiller tripped during normal operation at 1325 hours while the "B" chiller was removed from service for preplanned maintenance. Initial attempts at restarting either chiller were unsuccessful. The "A" chiller was restarted and carrying load at 1930 hours. The cause of the event was several factors concerned with chiller setpoint and freon charge balancing during cold weather operation. The chillers were rebalanced to ensure continued operation during the low load condition, while still maintaining the ability to remove design heat load. <br /><br /> This event is being reported per 10CFR50.73(a)(2)(v).
3311993012 | Duane Arnold | 11/29/1993 | 12/22/1993 | 9401060438 | <strong>Primary Containment Isolation System Half Group 3 Isolation due to a Degraded Relay Contact in the Logic System</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1993 the plant was operating at 100% power. During a surveillance test to calibrate a drywell pressure switch a half Group 3 primary containment isolation system (PCIS) isolation unexpectedly occurred. The automatic actions were confirmed and the isolation was reset. Troubleshooting found a relay that was operating properly but showed evidence of a degraded contact. On December 14, 1993 the relay was replaced. The relay was found to have a degraded contact that is considered to be the cause of the Group 3 isolation. The surveillance test was then performed satisfactorily with the new relay. This event had no effect on safe operation. The isolation functioned as designed.
3331993001 | FitzPatrick | 01/20/1993 | 02/19/1993 | 9302250238 | <strong>Identification of Inadequate Breaker Coordination Affecting Appendix R Compliance</strong><br /><i>Abstract:&nbsp;</i>INTERIM REPORT EIIS CODES ARE! <br /><br /> The plant was operating at 21.1 percent power while performing startup testing after an extended outage. During a study of the electrical distribution system for Appendix R concerns in 12/92, Engineering determined that the assumptions used by the architect engineer in the preparation of the original breaker coordination drawings were erroneous and that inadequate breaker coordination on a feeder breaker existed on a safety-related Motor Control Center (MCC) ED!. The discrepancy was due to the fact that the architect engineer assumed that if coordination existed between the largest feeder breaker and the supply breaker, then all smaller feeder breakers would also be coordinated; however, that assumption was not correct in that a smaller feeder breaker of a different type (with a different time-current characteristic) may not coordinate with the supply breaker. After review and independent verification by Engineering in 1/93, it was determined that adequate breaker coordination did not exist within two fire areas, the Cable Spreading Room and the Battery Room Corridor NA!. The NRC was notified of the Appendix R non-compliance on 1/20/93. On 1/21/93, a procedure change was made to open the feeder breaker and close the MCC supply breaker if it tripped. The feeder breaker was replaced and coordination was achieved on 1/24/93.
3331993002 | FitzPatrick | 01/27/1993 | 02/26/1993 | 9303030436 | <strong>Identification of Relay Room Ventilation System Single Failure Non-Compliance</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in! <br /><br /> The plant was operating at 32 percent power approximately 17 days after ending an extended outage. In 1980 an additional relay and an interlock circuit was added between the Relay Room carbon dioxide fire suppression (CARDOX) system KQ! and the Relay Room NA! Ventilation System VI! as part of a modification recommended by Branch Technical Position (BTP) APCSB 9.5-1, Appendix A (Guidelines for Fire Protection for Nuclear Power Plants). On 1/25/93, during a design effort to modify the ventilation system, Engineering determined there was a potential non-conformance in the existing ventilation system control circuit violating the single failure criterion in that a spurious actuation of components in the CARDOX control system could result in shutdown of redundant fans and dampers in the ventilation system. The non-conformance was verified by Engineering on 1/27/93. James A. FitzPatrick Operations and the NRC Resident Inspector were notified the same day. Alarm Response Procedures were revised on 2/3/93 to take compensatory actions upon spurious actuation. A Reasonable Assurance of Safety to continue operation was prepared and approved on 2/4/93. The cause of the condition has been determined to be design error (Cause Code B) by the engineers involved in the BTP-9.5-1, Appendix A interlock modification in 1980.
3331993003 | FitzPatrick | 02/17/1993 | 03/19/1993 | 9303230083 | <strong>Non-Safety-Related Components Connected to the Drywell Nitrogen Header Possibly Affecting Long Term Nitrogen Supply for ADS</strong><br /><i>Abstract:&nbsp;</i>EIIS codes are in !<br /><br /> The plant was operating at 100 percent power. During a review of component classifications, Engineering identified some non-safety-- related components which were connected to the drywell (primary containment) NH! safety-related nitrogen supply header LK!. During efforts to upgrade the components to safety-related in accordance with plant procedures, it was determined that certain parts within the nonsafety- related components were made of a material (Buna-N) that is not suitable for high temperature conditions. Failure of these parts during post Loss-of-Coolant-Accident conditions could result in the depressurization of the nitrogen supply header and lead to the inability to provide a 100 day supply of nitrogen to safety-related Automatic Depressurization system SB! valves, as described in the Updated Final Safety Analysis Report. Short term ADS operability is assured by nitrogen accumulators and check valves. The components were damper actuators, pressure regulators, and solenoid valves. Evaluations, calculations, and tests were performed to determine materials, failure modes, and leakage rates. A Reasonable Assurance of Safety evaluation was prepared and approved to justify operation until 2/26/93 when, during a planned shutdown, the necessary modifications were made to correct the non-conforming conditions.
3331993004 | FitzPatrick | 02/25/1993 | 03/26/1993 | 9303300220 | <strong>Low Intake Level Scram</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> On 2/25/93 at 0130 hours with the plant operating at 100 percent power, operators observed condenser SG! inlet temperature to be 58F (lake temperature was 33F). The increased temperature was apparently caused by a buildup of ice on the plant intake bar racks which restricted flow from the lake to the screenwell NN! intake. 80 of 88 intake bar rack heaters were operating. The screenwell water was being tempered by returning circulating water discharge to the intake where it mixed with lake water. As the ice blocked the intake, the amount of water flowing in from the lake decreased which caused the ratio of tempering water to lake water to increase. This caused the circulating water inlet temperature to increase. Load was reduced to 70 percent power and one circulation water pump was tripped. At 0140 hours, when the screenwell level was noted to be approximately ten feet below normal level, the reactor was scrammed. <br /><br /> A second circulating water pump was removed from service and the screenwell level returned to near normal. Computer alarm points have been established to alarm whenever the screenwell or condenser inlet temperature increases by 5 degrees F per hour. A continuous water level watch has been posted and an abnormal operating procedure has been developed to provide guidance if symptoms of icing conditions are observed.
3331993005 | FitzPatrick | 02/25/1993 | 03/26/1993 | 9303300236 | <strong>Shutdown Cooling Isolation</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> The plant was shutdown and being cooled down for a maintenance outage. At 1303 hours on 2/25/93, Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) BO! pump B was started in the shutdown cooling mode and the inboard and outboard shutdown cooling suction isolation valves closed upon initial startup of the pump. The isolation was caused by a pressure transient. When the RHR pump was started, some air in the shutdown cooling suction piping was drawn into the RHR system causing a pressure pulsation which was felt by the isolation pressure switches. On 3/11/93 at 1649 hours, with the plant shutdown and in the cold condition, the RHR shutdown cooling valves isolated when the inboard isolation shutdown cooling suction valve was opened. At the same time, with the reactor vented, the RHR suction piping high pressure alarm annunciated in the Control Room. This isolation was also caused by a pressure transient as indicated by the alarm. On both occasions, the second attempt to place the RHR system into shutdown cooling was successful. The corrective action is to revise the operating procedure to require filling and venting of the RHR shutdown cooling suction lines prior to placing the RHR system in shutdown cooling.
3331993006 | FitzPatrick | 02/26/1993 | 05/05/1993 | 9305130092 | <strong>Inoperability of Fire Pumps</strong><br /><i>Abstract:&nbsp;</i>Update Report - Previous Report Date March 12, 1993 <br /><br /> EIIS codes are in ! <br /><br /> The plant was shutdown and in the cold condition for a maintenance outage. Fire Pump KP! 76P-2 was declared inoperable due to inadequate pump discharge pressure and Fire Pump 76P-1 was declared inoperable when engine overheating was evident during a pump test. A backup source of fire suppression water was provided by a third full capacity fire pump. Fire Pump 76P-1 was replaced with a new pump and Fire Pump 76P-2 will be replaced with a new or rebuilt pump. Procedure revisions and continued trending of performance data will reduce the probability of recurrence. No similar events involving inoperability of both fire pumps have occurred at this facility.
3331993007 | FitzPatrick | 03/22/1993 | 04/21/1993 | 9304270030 | <strong>Average Power Range Monitor Thermal Trip Unit Testing Incomplete Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> On 3/22/93, during a review of surveillance testing, it was determined that the thermal power trip function of the Average Power Range Monitor (APRM) IG! was not being tested to completion because testing was performed with the instrument channel input to the Reactor Protection System (RPS) JC! bypassed which blocked the initiation of a scram signal. The plant was in the startup/hot standby mode of operation at approximately 8 percent power. Although no surveillance requirement identified in the Technical Specification was missed or violated, this event is considered reportable under the broad definition of operable which requires that systems, structures or components be shown to be capable of performing all of the intended safety functions (10CFR50.73). Procedure changes were made and testing completed prior to changing reactor mode of operation. Other neutron monitoring surveillance tests were reviewed to verify that the deficiency was an isolated event. The event was not safety significant because the Final Safety Analysis Report considered an APRM channel trip to be initiated from either the non-flow referenced neutron flux trip unit or the thermal power trip unit. The trip function of the non-flow referenced APRM trip units had been routinely tested and were operable. LER-89-008, 90-007, 90-015 and 92-032 described similar events.
3331993008 | FitzPatrick | 04/12/1993 | 05/11/1993 | 9305180080 | <strong>Failure to Perform Required Offgas Sampling</strong><br /><i>Abstract:&nbsp;</i>EIIS codes are in !<br /><br /> The plant was operating at 100 percent power on April 12, 1993. At approximately 0200 hours, a Chemistry Technician identified that the steam Jet Air Ejector (SJAE) Radiation Monitor IL! had increased to approximately 30 mr/hr from the nominal value of 15 mr/hr. A sample was immediately obtained and analyzed by the chemistry technician. Radiological Effluent Technical Specification 3.5.a.2 requires an isotopic analysis within four hours whenever the SJAE radiation monitors increase by 50 percent (excluding power level changes). A special query of computer data indicated that the increase occurred on April 11, 1993 at approximately 0200 hours (approximately 24 hours earlier). The immediate corrective action was to obtain a sample which showed that the actual radioactivity in the offgas had not increased. The failure to closely monitor changes in this parameter during periods when the readings are on the low end of the instrument resulted in the failure to identify the need to obtain an offgas sample. A review of the SJAE radiation every two hours has been added to the daily instrument surveillance (ST-40D) until a computer point can be setup to annunciate whenever the nominal steady state gas release increases by 50 percent.
3331993009 | FitzPatrick | 04/20/1993 | 02/22/1996 | 9603010227 | <strong>Low Reactor Water Level Scram Due to Feedwater Transient</strong><br /><i>Abstract:&nbsp;</i>Update report: Previous reports dated 10/25/94, 12/06/93, and 05/19/93. On 4/20/93 at 1654, while operating at 100 percent power, abrupt reduction in feedwater [SJ] flow resulted in rapidly decreasing Reactor water level. A Reactor Scram occurred at 177 inches above top active fuel. Plant operators attempted to restore reactor water level by taking manual control of the reactor feed pumps [JK], but were unsuccessful due to component failures. The event was caused by a loose electrical connection on the A Reactor Feed Pump [JK] Turbine Governor Control. The transient was compounded by a failed discharge check valve [SJ] on Reactor Feed Pump A. These failures allowed feedwater flow to be reduced and flow to be diverted causing a scram on low Reactor water level. All control rods fully inserted on the scram and plant systems responded as designed to decreasing and then increasing reactor water level. A Post Trip Evaluation was conducted to determine the root cause of the event and recommend corrective actions to prevent recurrence: The evaluation identified that the Technical Specification Pressure - temperature cooldown and heatup limit of 100 degrees per hour had been exceeded. All necessary repairs and corrective actions identified through the evaluation were completed prior to plant restart.
3331993010 | FitzPatrick | 04/20/1993 | 05/19/1993 | 9305280327 | <strong>High Pressure Collant Injection System Declared Inoperable Due to Electrical Ground</strong><br /><i>Abstract:&nbsp;</i>EIIS codes are in !<br /><br /> The plant was in hot shutdown condition with the mode switch in Refuel on 4/20/93 at 2005 hours when High Pressure Coolant Injection (HPCI) BJ! was declared inoperable due to a grounded 125 VDC electric circuit EJ! on the Turbine Steam Supply Valve, 23MOV-14. HPCI was required to be operable by Technical Specification 3.5.C. Other systems required by Technical Specification 4.5.C.1 when HPCI is inoperable were operable. <br /><br /> The ground was apparently caused by a pinched electrical wire resulting from inattention to detail when replacing the limit switch compartment cover on the valve operator following maintenance activities on or about February 26, 1993. <br /><br /> The ground was repaired and the valve post work tested satisfactorily on 4/22/93. Since the plant was in cold shutdown as of 0320 hours on 4/21/93, HPCI was no longer required to be operable. <br /><br /> LER-89-005 and LER-89-019-01 describe events where HPCI has been declared inoperable due to circuit grounding.
3331993011 | FitzPatrick | 04/22/1993 | 05/20/1993 | 9305280317 | <strong>Missed Fuel Oil Analysis</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. EIIS codes are in !!<br /><br /> The plant was shutdown and in the cold condition for a maintenance outage. Emergency Diesel Generator System EK! fuel oil DC! samples for January, February, and March, 1993 were shipped to a vendor without an approved purchase order and were not analyzed in a timely manner. On April 22, 1993, it was determined that monthly Diesel fuel oil sample analysis reports for January and February 1993 received on April 2, 1993, did not meet the Technical Specification 4.9.C.1 once a month quality check requirement. <br /><br /> The samples were shipped to the vendor on time, however, the vendor did not have a contract to perform the analysis until March 30, 1993 and the surveillance of the receipt of analysis results was inadequate. <br /><br /> The failure of the vendor to perform the analysis on time was due to a delay in obtaining a 1993 contract. In addition, personnel responsible for receiving the results of the analysis failed to initiate an emergency requisition.
3331993012 | FitzPatrick | 05/19/1993 | 12/01/1993 | 9312090288 | <strong>Shutdown Cooling Isolation</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> The plant was shutdown and being cooled down for a maintenance outage. At 1625 hours on 5/19/93, Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) BO! Pump B was started in the shutdown cooling mode and the inboard and outboard shutdown cooling suction isolation valves closed upon initial startup of the pump. The isolation was caused by a pressure transient. <br /><br /> The second attempt to place the RHR system into shutdown cooling was successful. There have been seven (7) LERs written over the past three years concerning RHR Shutdown Cooling Isolations. Based on past history and the testing performed during the 1993 Fall maintenance outage, the cause of the intermittent isolations of Shutdown Cooling is air trapped in the instrument line for 02PS-128A (Reactor Pressure >75 psig Isolation Switch).
3331993013 | FitzPatrick | 05/25/1993 | 06/23/1993 | 9306300201 | <strong>Reactor Scram During Startup Due to Neutron Monitor Spike</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> On May 25, 1993, at 2045 hours, an automatic reactor scram took place when Average Power Range Monitor (APRM) IG! E spiked while indicated power level was approximately 6 percent with the plant in the startup mode. Main Steam Line Radiation Monitor (MSLRM) IL! D had been intentionally tripped approximately 5 minutes prior to the APRM E spike after being declared inoperable due to intermittent downscale alarms. Systems performed as designed, no isolations or other engineered safety feature actuations took place and no significant reactor temperature, pressure or level transient took place. A Local Power Range Monitor (LPRM) detector spike was the probable cause of the APRM. LPRMs susceptible to spiking were tested per vendor recommendations to reduce spiking. Stronger radiation sources were placed adjacent to the MSLRM detectors to increase the detected radiation level above the downscale alarm setpoint. No previous LERs have been submitted for scrams due to APRM spikes.
3331993014 | FitzPatrick | 05/29/1993 | 12/17/1993 | 9312270062 | <strong>Incomplete Logic System Functional Testing</strong><br /><i>Abstract:&nbsp;</i>UPDATE REPORT - Previous Report Dated 6/25/93 <br /><br /> The plant was at approximately 15 percent power in the RUN mode during a normal startup power ascension. On May 29, 1993, it was determined that portions of the High Pressure Coolant Injection (HPCI) BJ! actuation logic JE! had not been periodically tested as a result of procedure deficiencies. LER-93-009 reported the initial identification of one logic test omission in the HPCI system and committed to conduct a detailed review of the HPCI logic testing as part of the corrective action. The results of the detailed review were reported in LER-93-014-00. Procedure changes were made and surveillance testing was completed in order to test all portions of the HPCI logic. Testing was completed with satisfactory results. LER-92-032, 90-007, 90-015 and 89-008 describe similar cases where surveillance testing was incomplete or missed. This supplement describes the results of test reviews conducted over the past several months and revises the surveillance procedure review schedule completion date, from December 31, 1993, (as committed to in LER-92-032), to December 31, 1994.
3331993015 | FitzPatrick | 05/20/1993 | 11/24/1993 | 9312060047 | <strong>Fire Detection Circuits which Potentially Deviate from NFPA-72D Criteria</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !. This is a voluntary LER.<br /><br /> On 5/20/93, the plant was operating at 100 percent power in a steady state condition. During a design basis reconstitution effort, NYPA Engineering identified some fire detection IC! circuit designs which potentially deviated from NFPA-72D, regarding circuit supervision. In a review of fire protection items dated 10/13/80, the NRC stated "by telephone the licensee confirmed that all new fire detection systems and all systems protecting safety-related areas meet NFPA-72D as a Class A (supervised) system." The deviations involved the main fire panels and two local smoke detection panels. An evaluation issued on 6/11/93 concluded that the Fire Detection System was operable. NYPA determined that the condition was not reportable under 10CFR50.72 or 50.73. However, since the circuit designs potentially deviated from criteria stated in correspondence with the NRC, NYPA has decided to report this condition under a voluntary LER. A full Code compliance Review is scheduled to be performed. The cause was inadequate design (Cause Code B).
3331993016 | FitzPatrick | 07/22/1993 | 08/23/1993 | 9308310040 | <strong>Liquid Radioactive Waste Discharge Without Testing the Radwaste Discharge</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in ! <br /><br /> On July 22, 1993, with the plant operating at 100% power, a source check was not performed of the Radwaste Discharge Monitor prior to discharge of Waste Sample Tank A WD! to Lake Ontario. The failure to perform the source check was discovered after the tank had been discharged (later that day). A source check was performed satisfactorily immediately upon discovery. The Radwaste Discharge Monitor alarm and trip settings were completed prior to discharge and operability verification after-the-fact proved that this was not an unmonitored release. Subsequent discharges to Lake Ontario were immediately suspended pending resolution and initiation of corrective actions to prevent recurrence.
3331993017 | FitzPatrick | 07/29/1993 | 08/30/1993 | 9309090272 | <strong>APRM Downscale Companion IRM Upscale/Inoperable Scram Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>EIIS Codes are in !<br /><br /> On July 29, 1993, at 1033 hours with the plant operating at 100 percent power and the mode switch in the Run position, an Unusual Event was declared when it was determined that the APRM Downscale, Companion IRM Upscale/Inoperative Scram was not being tested and was therefore inoperable. A plant shutdown was initiated. The 'RM Downscale Scram was tested and performed as designed. The Unusual Event was terminated at 1350 hours on the same day. Although the trips had always been calibrated and tested individually, the APRM Downscale, Companion IRM Upscale/Inoperable Scram coincident trip function had not been tested due to a misinterpretation of the surveillance requirement. This scram function exists, and is required, only in the Run mode. The IRMs are not required to be operable in Run. This misinterpretation of the trip function requirements as related to the mode switch position caused the procedural deficiency. The corrective actions included testing of the function and adding this test to the weekly surveillance, as required by Technical Specifications.
3331993018 | FitzPatrick | 08/12/1993 | 10/01/1993 | 9310070068 | <strong>Incomplete Functional Testing of Carbon Dioxide Fire Suppression System</strong><br /><i>Abstract:&nbsp;</i>The plant was operating at 100 percent power in the Run mode. During the conduct of a Fire Protection test procedure adequacy review on August 12, 1993, it was identified that portions of the Carbon Dioxide Fire Suppression System for the South Emergency Switchgear Room were not being tested by the functional test procedure. Since all Carbon Dioxide systems are similarly tested, they were declared inoperable, and fire watches posted in each affected area. The test procedure was revised and the system restored to an operable condition following satisfactory completion of testing. Evaluation of Carbon Dioxide discharge timer settings determined that the functional test procedure acceptance ranges were inappropriately based on design calculations rather than actual test results. Six timers were found set lower than the time communicated to the NRC in JNRC-78-53. An increase in the Technical Specification minimum level for the three ton Carbon Dioxide storage tank was required for the same reason. These findings are a result of inadequate procedure development and poor administrative controls. Reviews of all Fire Protection functional test procedures will be completed by 12/31/93. This event reports deficiencies similar to the testing procedure weaknesses reported in LER-93-014.
3331993019 | FitzPatrick | 09/23/1993 | 05/27/1994 | 9406020270 | <strong>Potential Design Inadequacies in the Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>This LER updates information on two previously reported conditions and describes other adverse conditions related to the Control Room Ventilation (CRV) System found in the past nine months. The plant has been operating at 100 percent power in a steady state condition except during three maintenance outages in September, November and April, 1994. As previously reported, engineering determined on 9/23/93 that an unquantified amount of unfiltered air would flow into the Control Room (through a normally open manually operated "bypass" damper) with the CRV System in the "isolate" mode of operation with a single failure, specifically, of an isolation motor operated valve (MOV) to close. An update reported that on 10/29/93 engineering identified single failure concerns in the routing of control and power cables for the CRV System fans, dampers, and isolation MOVs. The other CRV related events or conditions generally fell into four categories: single failure concerns; degraded equipment conditions allowing outside air infiltration; inadequately balanced air flows resulting in filter train flow rates that exceeded Tech Spec limits; and inaccurate design and licensing basis documentation. The causes were: inadequate design control and documentation by engineering organizations; inadequate preventive maintenance; inadequate surveillance testing; and no comprehensive CRV design basis document. The system has been returned to an operable status.
3331993020 | FitzPatrick | 09/24/1993 | 10/25/1993 | 9311010210 | <strong>Reactor High Pressure Scram Due To Turbine Bypass Valve Partial Closure</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1993, at 0709 hours, an automatic reactor scram took place when the Main Turbine Bypass Valves partially closed during the conduct of troubleshooting. Due to the potential risk of initiating a turbine trip, reactor power had been reduced, and the Main Turbine had been taken out of service to support troubleshooting an electrical ground in the Turbine Electrohydraulic Control System (EHC). The plant was at 17.5 percent power in the RUN mode with reactor pressure being controlled automatically by the Main Turbine Bypass Valves. While lifting individual leads in the Main Turbine Alarm and Trip circuit, a partial closure of the Turbine Bypass Valves occurred. The Bypass Valve partial closure caused reactor pressure to increase and an automatic scram on high reactor pressure. The event was caused by personnel error. Personnel performing the troubleshooting did not adequately verify plant response. The use of electrical drawings that did not adequately support troubleshooting contributed to the event cause. The electrical drawings will be upgraded.
3331993021 | FitzPatrick | 07/22/1993 | 10/17/1994 | 9410270362 | <strong>Motor Operator Valve Failure Due to Inadequate Brake Design Test</strong><br /><i>Abstract:&nbsp;</i>The plant was operating at 100 percent power in the Run mode. During the performance of testing on 7/22/93, the motor for 10MOV-25A, Residual Heat Removal A Side Low Pressure Coolant Injection Inboard Isolation Valve, failed due to repeated starts in the closed direction after the valve was closed. Failure appeared to be due to overheating caused by repetitive in-rush starting current. The cause was an apparent design deficiency in the selection of motor brake which was determined to be inadequately sized to prevent actuator spring pack energy release after operator torque-out and motor cut-off. This condition is reportable because with the plant in shutdown cooling operation the potential exists for common mode failure of the redundant subsystem actuator. In Shutdown cooling operation, if an isolation signal is received, a continuous, sealed in, close signal is sent to both 10MOV-25A and B, which could lead to this postulated failure and neither valve could be remotely opened for residual heat removal or vessel inventory control. Plant operators were made aware of the potential failure scenario and an operability determination was performed. A modification to the motor thermal overloads was implemented to minimize failure potential. The Authority intends to replace the motor operators during the 1995 refuel outage.
3331993022 | FitzPatrick | 10/29/1993 | 03/15/1994 | 9404190115 | <strong>Vendor Design Deficiencies Allowing Exposed Resistors in the RPS Panels</strong><br /><i>Abstract:&nbsp;</i>This is an update of LER-93-022, issued 11/29/93<br /><br /> On 10/29/93, the plant was shut down for about one week. After a series of inspections of wiring inside Reactor Protection System (RPS) panels in the Control Room, engineering determined that some of the wires between RPS scram contactors were not installed inside protective conduits as specified in notes on a vendor interconnection diagram and that eight RPS resistors were not installed inside protective enclosures. The exposed resistors (and their associated terminal blocks and wiring) could have allowed a single failure (specifically, a 120VAC hot short across an exposed wire or terminal) to bypass certain RPS relay contact actuations. Although highly unlikely, the superimposed 120VAC source could potentially prevent the automatic insertion of some or all of the control rods into the reactor core. The cause of this event appears to be inadequate design and design review (Cause Code B) by the original Nuclear Steam Supply engineering company in 1975. The resistors have since been relocated inside protective covers and the contactor wires have been relocated, eliminating the single failure design concern. A 10CFR21 notification has been made by the engineering company.
3331993023 | FitzPatrick | 11/05/1993 | 12/03/1993 | 9312090290 | <strong>Shutdown Cooling Isolation Caused by Valving Error</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1993, at 2049 hours, with the plant in cold shutdown for a maintenance outage, a reactor scram, primary containment group 2 isolation, and a shutdown cooling isolation occurred. A Group 2 isolation isolates the Reactor Water Cleanup System, Reactor Building, Primary containment and Reactor Water Sample Valves, Drywell Floor and Equipment Drains, and initiates the Standby Gas Treatment System. The low water level signal which generated the automatic action was an invalid signal which occurred while an operator was valving into service a temporary level transmitter. The transmitter was installed as part of the reactor vessel water level backfill modification (NRC Bulletin 93-03). The transmitter tubing was depressurized and partially drained after a hydrostatic test of the temporary level transmitter was completed. The event was caused by inadequate procedural control of the restoration, and failure to recognize the potential impact of placing the transmitter in service.
3331993024 | FitzPatrick | 11/16/1993 | 12/13/1993 | 9312270022 | <strong>Fire Protection Hose Station Periodic Testing Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1993, the plant was shutdown and in the cold condition with the Reactor Mode Switch in refuel. A scheduled maintenance outage was in progress. During a weekly NRC Resident inspector meeting, the inspector questioned what testing was required under the Technical Specification Table 4.12.3 heading "Flow/Hydrostatic Test (1)". Specifically does this heading require opening each hose station valve and verifying water flow. <br /><br /> Initial investigation determined that no flow testing had been performed on Fire Protection hose stations. Following evaluation, it was determined that although flow testing may not have been required in accordance with the Technical Specification basis reference documents, correspondence between the Commission and the Authority in the development of this specification identified a specific flow test. The Authority concluded on November 16, 1993, that flow testing should have been performed. The test procedure was revised and testing completed with satisfactory results.
3331993025 | FitzPatrick | 11/22/1993 | 12/22/1993 | 9401110183 | <strong>High Pressure Coolant Injection System Inoperable due to Turbine Stop Valve Failure to Close Within Required Stroke Time Limit</strong><br /><i>Abstract:&nbsp;</i>The plant was at 14.3 percent power with the reactor mode switch in run. A plant startup was in progress on November 22, 1993. An in-service test (IST) had been performed on the High Pressure Coolant Injection (HPCI) System. Test data indicated that the less than or equal to 2.0 second time interval allowed by the IST program for the closure of the HPCI turbine stop valve (23HOV-1) was exceeded by 0.08 seconds (4 percent). HPCI was declared inoperable at 1230 hours initiating a 7-day Limiting Condition for Operation (LCO).<br /><br /> The cause of the increased stroke time was determined to be hydraulic fluid residue buildup in the pilot actuated solenoid valve and ports. The valve was cleaned and rebuilt and HPCI operability restored on 11/24/93. Additional corrective actions will include reviewing preventive maintenance requirements and developing a method to prevent or minimize oil residue buildup in the pilot solenoid valve. <br /><br /> There have been no similar events where the High Pressure Coolant Injection system was declared inoperable for failure to trip within a designated IST time.
3331993026 | FitzPatrick | 12/02/1993 | 01/03/1994 | 9401120245 | <strong>High Pressure Coolant Injection Inoperable Due to Failed Master Trip Unit in the Steam Leak Detection System</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1993, at 1810 hours with the plant operating at approximately 100 percent power and the mode switch in the run position, the High Pressure Coolant Injection (HPCI) System was declared inoperable. A HPCI steam line area temperature trip unit had failed downscale. The trip unit is part of the Primary Containment Isolation system, and closes the HPCI Steam Supply Inboard Isolation Valve when high temperature in the area is sensed. The trip unit was replaced, and the HPCI system declared operable on 12/3/93 at 1240 hours.
3331993027 | FitzPatrick | 12/21/1993 | 01/20/1994 | 9403240176 | <strong>Fire Protection System Function Test Procedure Weaknesses</strong><br /><i>Abstract:&nbsp;</i>The plant was operating at 100 percent power in the Run mode. Technical Services staff had completed an initial adequacy review of the fire protection functional test procedures using improved administrative controls for guidance in their review. The review identified that heat detectors located in the Standby Gas Treatment system filter trains were not being functionally tested as required by the Technical Specifications. Additional weaknesses associated with testing of the Reactor Building fire protection water spray curtains and pre-action sprinkler systems located in the Emergency Diesel Generator and Recirculation Motor Generator rooms are also reported in order to provide a complete summary of the adequacy review. The test program was not adequate to ensure proper automatic actuation of these systems in the event of a fire. Test procedures were revised and appropriate testing completed with satisfactory results. These testing weaknesses were the result of inadequate procedure development and poor administrative controls. Improved administrative guidance which controls the development, review and revision of test procedures will prevent these types of procedure weaknesses in the future.
3341993001 | Beaver Valley 1 | 02/12/1993 | 03/12/1993 | 9303160089 | <strong>Condition Outside Design Basis - Main Steam Isolation Valve Closure Not Considered in Original Design</strong><br /><i>Abstract:&nbsp;</i>Unit One was performing an engineering analysis to support the possibility of increased steam generator tube plugging during the upcoming refueling outage. During this study, it was discovered that an inadvertent main steam isolation valve (MSIV) closure would generate a pressure transient which would result in increased loading on the main steam system piping and supports. This transient was not previously considered as a design condition for the plant. An assessment of the increased loading has shown that the established design stress limits could be exceeded, resulting in the plant being outside of its design basis. An operability assessment supports continued operation until the upcoming refueling outage. This assessment utilizes ASME Section III Appendix F faulted allowable values in accordance with Generic Letter (GL) 91-18. In addition, the plant has previously experienced inadvertent MSIV closures with no defects to the piping or supports noted. A detailed reanalysis of the steam line loading is in progress to determine the actions necessary to meet the design allowable stress limits.
3341993002 | Beaver Valley 1 | 02/12/1993 | 03/12/1993 | 9303160095 | <strong>Engineered Safety Features Actuation - Inadvertent Tripping and Automatic Starting of River Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On 2/12/93, Unit 1 was in Mode 1 at 90% power. A non-licensed operator was discussing a breaker interlock for the swing river water pump, WR-P-1C, with a trainee. The swing pump has two supply breakers, one from each train of emergency power, and a mechanical interlock system to prevent both breakers from being connected onto their respective busses simultaneously. This prevents cross-connecting the emergency busses. The train A pump (WR-P-1A) was in standby, the train B pump (WR-P-1B) was in service, and the swing pump was not in service, with both breakers removed from the breaker cubicles. The operator opened the cubicle door for the Train B supply breaker to point out the interlock. At 0912 hours, he inadvertently bumped the cell switch arm in the breaker cubicle which is located adjacent to the interlock linkage, and generated a false signal that the swing pump was connected to the Train B emergency bus. The running river water pump is designed to trip if another river water pump breaker is connected to the same emergency bus to prevent overloading the emergency diesel generators. Since WR-P-1B was running, WR-P-1B tripped and WR-P-1A automatically started on low river water header pressure as designed. The cause of this event is due to personnel error. The individual has been counseled and this event will be presented in future retraining sessions.
3341993003 | Beaver Valley 1, Beaver Valley 2 | 02/17/1993 | 03/19/1993 | 9303220318 | <strong>Control Room Habitability Air Bottle Subsystem Manually Isolated</strong><br /><i>Abstract:&nbsp;</i>On 2/17/93 at 1114 hrs, during surveillance testing on a Containment High Range Radiation Monitor, an electrical noise spike caused a spurious High Radiation Alarm on a Control Room Radiation Monitor and actuated the Control Room Emergency Habitability System. Following confirmation that the actuating signal was not valid, operators isolated the air bottle subsystem which began discharging into the control room. By manually isolating this subsystem at 1116 Hrs, the station intentionally entered Technical Specification 3.0.3. <br /><br /> After resetting the spurious high radiation signal, the Air Bottle subsystem was unisolated and the Control Room Habitability System was returned to normal system arrangement. The Station exited Technical Specification 3.0.3. at 1135 Hrs. <br /><br /> Since the Control Room Emergency Habitability System Air Bottles were isolated, this event is being reported in accordance with 10CFR50.73.a.2.i.B as a condition prohibited by Technical Specifications.
3341993004 | Beaver Valley 1, Beaver Valley 2 | 02/18/1993 | 03/19/1993 | 9303220302 | <strong>Potential Post Small Break Loss of Coolant Accident Radiological Release</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1993, Westinghouse Nuclear Safety Advisory Letter (DLW-92-701) identified a scenario in which the Volume Control Tank (VCT) outlet check valve (CH-18) could become a potential leak path outside of containment during a 2 through 8 inch small break loss of coolant accident (SBLOCA). The VCT outlet isolation valves upstream of CH-18 were considered to be the flowpath boundary valves and, the function of CH-18 was considered only to be isolation from another closed piping system. <br /><br /> Inspections of the complementary valve (2CHS-18) at Unit 2 had been completed during the last refueling outage in October 1992, and no deficiencies were noted. Although this inspection met the intent of the recommended actions in the Westinghouse letter, upon further analysis, it has been determined that a postulated failure of 2CHS-18 meets the criteria for a potential single failure which may prevent the control of a radiological release outside containment. <br /><br /> Emergency Operating Procedures for both units have been revised to diagnose the problem based on increasing VCT level and instructs operators to isolate the flowpath.
3341993005 | Beaver Valley 1 | 03/02/1993 | 04/01/1993 | 9304060057 | <strong>Degraded Charging Pump Due to Incorrect Solenoid Valve Quality Assurance Classification</strong><br /><i>Abstract:&nbsp;</i>On 3/02/93, a review identified a discrepancy in the Quality Assurance (QA) Categorization of the solenoid valve, SOV-CH-101B, used to control the cooling water flow to the Lubricating (Lube) Cooler for the 1B Charging Pump (CH-P-1B). The SOV was identified as QA Category 2 (QA-2), when in fact the SOV is used in a QA-1 application. The original SOV was replaced with a commercial grade SOV in August 1986 as a result of maintenance activities. The stock number/part number for the SOV, in 1986, was listed as QA-2 (commercial grade). Throughout the time period from August 1986 to the present, CH-P-1B was utilized as the running or standby pump. Failure of the QA-2 SOV could result in a failure of CH-P-1B due to improper temperature control of the lube oil cooler. The cause for the discrepancy in the QA Category could not be determined. CH-P-1B was taken out of service on 3/02/93 following identification of this condition. The SOV was replaced with a QA-1 SOV and the specifications were revised. CH-P-1B was returned to service on 3/13/93. Safety implications as a result of this event were minimal. A review of surveillance tests performed showed no indication of improper lube oil cooler operation.
3341993006 | Beaver Valley 1 | 04/15/1993 | 05/14/1993 | 9305190259 | <strong>Violations of Required Administrative Controls for High Radiation Areas</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1993, with Unit One in Mode Six to support the ninth refueling outage, two events occurred involving inadequate attention to technical specification requirements for high radiation areas (>100 millirem per hour). In the first event, two operators entered a posted high radiation area without a radiation monitoring device which provides a continuous indication of the radiation dose rate in the area (a meter) as required by technical specification 6.12.1.a. In the second event, two operators entered a locked high radiation area, to perform valving, and left the barrier door open, violating technical specification 6.12.2. Each of the above events is a condition prohibited by technical specifications, and is reportable in accordance with 10CFR50.73.a.2.i.B. These events are recognized as violations of technical specifications and station radiological practices. Due to the specific circumstances, the radiological consequences were not significant. In the first event, the operators who entered the high radiation area without meters did not enter any other high radiation areas during their shift and neither operator received a dose in excess of 10 millirem during the course of work. In the second event, no unauthorized personnel gained access to high radiation area while the locked barrier door was open.
3341993007 | Beaver Valley 1 | 04/23/1993 | 05/21/1993 | 9305260504 | <strong>Condition Outside Design Basis--Original Piping Did Not Conform to Design Code</strong><br /><i>Abstract:&nbsp;</i>On 4/23/93, the plant was in a shutdown condition, Mode 6 (Refueling). During corrective maintenance on piping associated with the Reactor Plant Component Cooling Water System (CCR) Heat Exchangers, it was discovered that the original design and fabrication of the piping did not meet design code requirements applicable to the construction of Unit 1 (ANSI B31.1). The installed end plates on three piping headers did not have adequate thickness. When it was determined that these headers did not meet design code, an engineering evaluation was performed based on plant conditions (Refueling, Mode 6). This evaluation concluded that the headers would maintain system integrity. Since the piping did not meet design code, this event is being reported as a condition outside design basis.
3341993008 | Beaver Valley 1 | 04/23/1993 | 05/21/1993 | 9305260502 | <strong>Check Valves Not Included in the ASME Testing Program</strong><br /><i>Abstract:&nbsp;</i>On 4/23/93, during hydrostatic testing on the train "A" Reactor Plant River Water System (RW), leakage was detected through two check valves in the chlorine injection line. Further investigation determined that these check valves, and their train "B" counterparts, were not included in the station's ASME Section XI testing program, and were not tested in accordance with Technical Specification surveillance requirement 4.0.5. An engineering analysis determined that the as-found leakage for each train did not adversely affect the ability of the RW system to fulfill its safety function. This event is being reported as a condition prohibited by Technical Specifications.
3341993009 | Beaver Valley 1 | 06/07/1993 | 07/02/1993 | 9307070325 | <strong>Unlocked High Radiation Area Barrier.</strong><br /><i>Abstract:&nbsp;</i>On 6/7/93, with Unit One Mode 5 for the ninth refueling outage, Health Physics was performing a routine radiation barrier check which verifies the integrity of the barrier and that the barrier is in place and posted. At 1740 hrs, the east ladder barrier to the solid Waste area was found open. This area is a High Radiation Area and is required to be barricaded and conspicuously posted in accordance with Technical Specification 6.12. The area was searched and no individuals were present. This barrier was previously verified locked closed during the daylight shift at 0936 hrs. A survey of the area indicated that there were no areas where the radiation levels were greater than 1000 millirem per hour, however an area that had radiation levels greater than 100 millirem per hour was present. With the barrier open, the area was still conspicuously posted as a High Radiation Area, however, it was not adequately barricaded. The barrier was not closed when personnel exited the area. All personnel that had High Radiation Area keys during this time period were interviewed. The results were inconclusive and it could not be ascertained who left the barrier open. No adverse radiological consequences resulted due to the barrier being inadvertently left open. A review of exposure records indicated that no station personnel received any abnormal dose during the time the barrier was open.
3341993010 | Beaver Valley 1 | 06/14/1993 | 07/08/1993 | 9307140005 | <strong>Missed Technical Specification Surveillance on Safety Injection Accumulator Samples.</strong><br /><i>Abstract:&nbsp;</i>On 6/14/93, Unit One was in Mode 3, Hot Standby, at 547 degrees F and 2235 psig, recovering from the ninth refueling outage. At approximately 1740 hours on 6/14/93, a review of sampling requirements, performed by a chemistry department supervisor, determined that the proper boron concentration of the A, B, and C Safety Injection Accumulators had not been verified prior to increasing Reactor Coolant System (RCS) pressure above 1000 psig, as required by Technical Specifications. RCS pressure was increased above 1000 psig on 6/9/93 at 0535 hours. Records indicated that the B accumulator was sampled with satisfactory results on 6/9/93 at 2230 hours, but the A and C accumulators were not sampled. The chemistry supervisor immediately notified the shift supervisor and directed the Shift Chemistry specialist to sample the A and C accumulators. At 1830 the sample analysis indicated that both the A and C accumulators were within the required range.
3341993011 | Beaver Valley 1 | 06/19/1993 | 07/19/1993 | 9307230069 | <strong>ESF Actuation - Letdown Isolation During Unit Startup</strong><br /><i>Abstract:&nbsp;</i>On 6/19/93 at 1050 hrs., an Engineered Safety Feature actuation (letdown isolation) occurred while synchronizing the main unit generator. At the time of the event, reactor power was 8%, and the condenser steam release valves and steam generator bypass feedwater regulating valves were in manual control due to steam generator level oscillations. During preparations for unit synchronization, steam generator pressure and reactor coolant system (RCS) temperature began to increase. The condenser steam valves were not open sufficiently to remove the necessary amount of steam to maintain stable steam generator pressure, resulting in a pressure rise. At 1046 hrs., steam generator pressure rose above the instantaneous open setpoint of the atmospheric steam release valves. Atmospheric valve operation induced an RCS cooldown, accompanied by a pressurizer level decrease. When the main unit output breakers were closed at 1048 hrs, the turbine demanded additional steam flow from the steam generators, which caused further cooling and shrinking of the RCS. Shrinkage of the RCS caused a letdown isolation at 1050 hrs, due to low pressurizer level. The plant was stabilized, and letdown was restored at 1053 hrs.
3341993012 | Beaver Valley 1 | 07/02/1993 | 07/30/1993 | 9308050126 | <strong>Reactor Startup With A Wide Range Containment Hydrogen Analyzer Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1993, with Unit 1 operating at 100% power, Hydrogen Analyzer H2A-1HY-101A was discovered to be INOPERABLE. The Hydrogen Analyzer was discovered INOPERABLE during the quarterly performance of Calibration Procedure 1MSP-46.04A-I, Containment Hydrogen Monitoring Loop H2-HY101A Calibration" when no sample flow was obtained through the analyzer. Investigation by Instrument and Control Technicians performing the calibration revealed that the flow control valves for Hydrogen Analyzer Flowmeters F2 and F3 were closed. The Technicians opened the flowmeter flow control valves and adjusted the flows to the values obtained on April 8, 1993 during the previous calibration. On July 2, 1993, the calibration procedure was successfully completed and the Hydrogen Analyzer was declared OPERABLE. Further investigation revealed that the flowmeter flow control valves were mistakenly closed on April 19, 1993, during restoration from Surveillance Procedure 1BVT 1.46.3 "Wide Range Hydrogen Monitoring System Leak Test". With the discovery of the INOPERABLE Hydrogen Analyzer, it was determined that on June 15, 1993, Unit 1 entered Operational Mode 2 with one Wide-Range Hydrogen Analyzer INOPERABLE, a violation of Technical Specifications. The redundant wide-Range Hydrogen Analyzer was OPERABLE at the time of the mode change.
3341993013 | Beaver Valley 1, Beaver Valley 2 | 10/12/1993 | 11/11/1993 | 9311160317 | <strong>Unit 1 Reactor Trip and Required Shutdown, Dual Unit Loss of Offsite Power.</strong><br /><i>Abstract:&nbsp;</i>On 10/12/93 Unit 1 was operating at 100 percent power and Unit 2 was in a refueling outage with all fuel removed from the reactor vessel. At 1507 hours, Unit 1 experienced a large loss of offsite load when ten offsite feed breakers in the Beaver Valley switchyard opened as a result of an inadvertent underfrequency system separation actuation. The load reduction caused the Unit 1 turbine to trip on mechanical overspeed and resulted in a High Flux Rate Reactor Trip. The opening of the switchyard feed breakers and the resultant Unit 1 generator trip resulted in a loss of offsite power to Units 1 and 2. Both Unit 1 Emergency Diesel Generators (EDGs), and the required Unit 2 EDG, started and supplied their required loads. Unit 1 Auxiliary Feedwater actuated due to Low-Low Steam Generator Levels resulting from the Reactor Trip. Unit 1 was stabilized using the Emergency Operating Procedures. Following realignment of switchyard breakers, offsite power was restored to both units by 1522 hours. On 10/13/93, following a Unit 1 containment inspection, a Reactor Coolant System Pressure Boundary Leak was discovered on the Loop 1A cold leg vent valve RC-27. A Technical Specification Required cooldown was initiated and Mode 5 was entered at 0304 hours on 10/14/93.
3341993014 | Beaver Valley 1 | 07/31/1993 | 11/16/1993 | 9312010003 | <strong>Missed Surveillance Due to Improper Surveillance Testing of Valve</strong><br /><i>Abstract:&nbsp;</i>On 10/21/93, a review of surveillance test results on a the Fuel Pool Heat Exchanger Reactor Plant Component Cooling Water Inlet Isolation valve, TV-1CC-128, identified that the surveillance test conducted on 7/31/93 stroked the valve to the CLOSED position. This valve is categorized as an American Society of Mechanical Engineers (ASME) Category B Valve and is required to be tested in accordance with Technical Specification 4.0.5 to the OPEN position. The valve is a passive valve and is designed to fail open on a loss of power. Testing of this valve to the CLOSED position resulted in a failure to satisfy the surveillance requirement of Technical Specification 4.0.5 and is reportable in accordance with 10CFR50.73.a.2.i.B, as a condition prohibited by the Technical Specifications. The cause for this event was personnel error. The operator performing the surveillance failed to follow the procedure. The involved individual was counseled. This event will be reviewed by all Operations personnel responsible for ASME surveillance testing. There were no safety implications as a result of this event. Subsequent testing of this valve, on 10/21/93, verified no degradation in the valve performance between the test dates.
3341993015 | Beaver Valley 1 | 11/01/1993 | 12/01/1993 | 9312090111 | <strong>Nonconformance To Technical Specification For An Isolated Reactor Coolant Loop</strong><br /><i>Abstract:&nbsp;</i>On 11/1/93 with the Unit in Cold Shutdown (Operational Mode 5), it was recognized that a Technical Specification violation occurred when power was restored to the loop isolation valves for an isolated reactor coolant loop. The 'C' reactor coolant loop had been isolated for reactor coolant pump repairs. Technical specifications require that an isolated loop must have power removed from the loop isolation valves in Mode 5. Following pump repairs, an operator was dispatched to remove the clearance from the loop isolation valves. The intended action was to remove the clearance tags, connect the breakers to the electrical bus, and maintain the breakers open (valves deenergized). At 1330 hrs, the breakers were connected to the bus, however the operator also closed the breakers, restoring power to the valves. It is a normal practice to close a breaker following reconnection to the bus. Due to inadequate work planning, the switching order which directed operator actions for clearance removal, did not state that the breakers were to remain open. Additionally, the operator removing the clearance did not read a procedural caution statement that requires the breakers to remain open. At 2015 hrs, during a procedure review to return the loop to service, a control room supervisor observed that the isolation valves were energized. Power was removed from the valves at 2025 hrs.
3351993001 | St. Lucie 1 | 01/08/1993 | 01/26/1993 | 9302020423 | <strong>Four Safety Injection header isolation valves open to their operational position due to an Engineered Safety Feature subgroup relay failure.</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1993, at 0900 hours with Unit 1 in Mode 1 at 100% power, the Assistant Nuclear Plant Supervisor noticed that two of the High Pressure Safety injection and two of the Low Pressure Safety Injection header valves on the 'B' header were open. The valves HCV-3616, HCV-3625, HCV-3626 and HCV-3645 are normally shut and are opened with a Safety Injection Actuation Signal (SIAS). Troubleshooting the cause of the valve openings showed that a subgroup actuation relay in the Engineered Safety Features Actuation System (ESFAS) actuation circuitry had failed. When it failed in its deenergized state HCV-3616, HCV-3625, HCV-3626 and HCV-3645 opened to their SIAS positions. This failure did not effect the operability of the Safety injection System. The unit remained at 100% power. <br /><br /> The root cause of the event was a failed ESFAS subgroup actuation relay. By 1230 hours the relay had been replaced and tested. The valve lineup was restored. The failed relay will be sent to a laboratory for a failure analysis.
3351993002 | St. Lucie 1 | 01/28/1993 | 02/01/1993 | 9302110279 | <strong>Inability of Emergency Core Cooling System Ventilation to maintain a negative pressure in the ECCS pump room due to a ventilation imbalance.</strong><br /><i>Abstract:&nbsp;</i>On 28 January 1993, instrumentation and Controls (I&C) personnel identified an unrecognized design condition for the Unit 1 differential pressure switches between the Emergency Core Cooling System (ECCS) pump room and the Reactor Auxiliary Building. The function of these devices is to provide an alarm in the control room when the safety related ECCS ventilation fans do not draw a sufficient negative pressure in the ECCS pump room. An I&C supervisor noted that these alarms are only enabled with a Safety injection Acutation Signal present. <br /><br /> Operations supervision recognized that the absence of this alarm was used in the ECCS ventilation surveillance procedure to verify satisfactory operation of that system as described in the Unit 1 FUSAR. A subsequent test demonstrated that the ECCS ventilation system could satisfy Technical Specification requirements for operability, but that the B train of the ECCS ventilation system could not draw a negative pressure in the ECCS pump room as outlined in the FUSAR. ECCS exhaust fan HVE-9B was declared out of service and a four hour notification of this condition was made to the NRC. On 2 February, adjustments on various ventilation dampers were made which enabled HVE-9B to be returned to service. <br /><br /> The root cause of this condition was due to a ventilation imbalanceof the various system dampers. A FPL Engineering analysis demonstrated that the ventilation sytem was able to perform its safety function without having to maintain a negative pressure in the ECCS pump room. Corrective actions: The ventilation dampers were readjusted, the A and B trains of ventilation were satisfactory surveilled, and the surveillance procedure was changed to rely on installed pressure differential indication instead of relying upon the absence of an alarm. <br /><br /> This voluntary LER is being submitted for informational purposes.
3351993003 | St. Lucie 1 | 03/31/1993 | 04/19/1993 | 9304230121 | <strong>Inadvertent Start of the 1B Emergency Diesel Generator due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1993, at 1311 hours with Unit 1 in Mode 5 for refueling, the 1B Emergency Diesel Generator (EDG) was inadvertently started. While plant maintenance personnel were installing test equipment to be used for the Integrated Safeguards Test one of the undervoltage relays located in the 1B EDG control panel was actuated, starting the 1B EDG. The 1B EDG operated as expected with no abnormal conditions observed. The 1B3 4160 VAC bus remained powered by the normal off-site source. After operators determined that the EDG had been inadvertently started the 1B EDG was secured. <br /><br /> The root cause of this event was personnel error. Utility personnel inadvertently bumped an undervoltage relay during the installation of test equipment for the Integrated Safeguards Test. <br /><br /> Corrective actions: An INPO Human Performance Enhancement System review (HPES) was performed on this event. The utility personnel were counseled. The procedure in use during this event was changed to add a precaution for installing test equipment.
3351993004 | St. Lucie 1 | 04/09/1993 | 05/10/1993 | 9305180328 | <strong>Incorrect Reactor Coolant System Low Flow Trip Setpoint results in a condition prohibited by Technical Specifications due to a Design Control Inadequacy.</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1993, St. Lucie was in Mode 6 when a typographical error was discovered by FPL Nuclear Engineering in a report used to determine the Reactor Protection System (RPS) low Reactor Coolant System (RCS) flow trip setpoint. Technical Specification 2.2.1, Table 2.2-1 states that the trip setpoint will be greater than or equal to 95% of design reactor coolant flow. The FPL Nuclear Engineering report, which described the conversion of pressure drop across the steam generators to the RPS low RCS flow trip setpoint, contained an incorrect constant. The report was subsequently transmitted to the plant staff and the Instrument and Control Department adjusted the RCS low flow setpoint. This error caused the setting of the RCS low flow trip setpoint to a value approximately 3% below the minimum 95% of design flow. This setpoint error existed since August 1988.<br /><br /> The root cause of this event was a design control inadequacy. A typographical error was made in the report transmitted to the plant staff. The error would have been discovered if the review process for the transmitted report had undergone an independent review. The Nuclear Engineering process currently in place prevents a similar event from occurring by requiring independent review of transmitted setpoints. Corrective actions for this event: An engineering evaluation was performed that concluded that the operation of Unit 1 during this time period was within the bounds of the safety analysis. A review of the procedure used to determine the Unit 2 low RCS flow setpoint verified that it did not contain a similar error. After a review of internal records, Nuclear Engineering verified that no other Unit 1 or 2 RPS setpoint changes were transmitted to the plant in error. An engineering package was developed to provide the corrected calculations for determination of the RPS reactor coolant system low flow trip setpoint. Instrumentation and Control personnel will revise appropriate procedures and install the correct trip setpoint in the Unit 1 RPS prior to entering mode 2. Prior to discovery of this event, Engineering adopted a process requiring independent review of setpoints before transmittal to the plant staff.
3351993005 | St. Lucie 1 | 05/30/1993 | 06/24/1993 | 9307010013 | <strong>Shutdown Required By Technical Specifications Due To An Unlatched Control Element Assembly Caused By Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>Unit 1 had just completed a scheduled refueling outage and was taken critical at 0430 on May 29, 1993 in preparation for low power physics testing. During the physics testing, core neutron flux asymmetries were identified that indicated one control element assembly (CEA) of dual element control element mechanism (CEDM) # 7 was potentially unlatched. Subsequent computer analysis and flux distribution modeling confirmed an unlatched inboard element of CEDM #7 as the most probable cause of the observed flux distributions. A controlled reactor shutdown was completed to satisfy requirements of Unit 1 CEA misalignment Technical Specification 3.1.3.1.f. The reactor was disassembled and ensuing inspections confirmed that the inboard element of CEDM #7 was unlatched. <br /><br /> The most likely root cause of this event was due to personnel error on the pad of contractor and plant personnel in not adequately executing CEA latching. Contractor personnel performing the latching may not have correctly evaluated the full engagement of both CEA's. Additionally, post-latching verification as indicated by the extension shaft pin position may have been inadequately performed. Both of these checks could have alerted the personnel that the CEA was not fully latched. Contributing factors include inadequate procedural guidance on methods of ensuring proper latching, human factors concerns in performing the indicator pin verifications, and lack of independent verification of position indicator pin location.<br /><br /> The corrective actions taken include: 1) CEDM #7 was inspected for damage, none was observed, and the CEA was relatched. 2) Contractor and operations personnel training and certification on the implementation of the latching procedure will be improved. 3) The CEA latching procedure is being modified to ensure proper latching. 4) Post-latching inspections will be enhanced to reinforce independent latching verification
3351993006 | St. Lucie 1, St. Lucie 2 | 09/10/1993 | 10/08/1993 | 9310130342 | <strong>Waste Gas Releases with Meteorological Instruments out of service due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On September 10, at 1120 and 1840 hours with Unit 1 at 100% power and Unit 2 at 74% power, controlled releases of the radwaste gas decay tanks were performed from Unit 2. Plant personnel were unaware that during these controlled releases the meteorological (met) tower information was invalid. On September 12, the Unit 2 Assistant Nuclear Plant Supervisor discovered that the met data was erroneous. The met tower was then entered into the out of service log and no subsequent controlled releases were made. After a review of the strip charts from the met tower, Operations and Chemistry determined that the met tower instrumentation had been out of service since September 9, at 1318. <br /><br /> The root cause of the event was cognitive personnel error by the Reactor Control Operators and the Chemistry technicians who performed the met data system daily channel checks and did not fulfill the intent of the met instrumentation surveillance procedure due to inattention to detail. A contributing factor to this event was that utility Instrument and Control specialists performed a scheduled channel calibration at the met tower and inadvertently caused the data logger to lockup and transmit the last met values without updating the data. <br /><br /> Corrective actions for this event: Operations revised procedures to enhance the control room met checks; Training will review this event with Operations, Chemistry and I&C personnel; and on September 13 at 1345 the met tower instrumentation was returned to service.
3351993007 | St. Lucie 1, St. Lucie 2 | 09/18/1993 | 10/14/1993 | 9310200290 | <strong>Three manual reactor trips to prevent equipment damage by Jellyfish influx.</strong><br /><i>Abstract:&nbsp;</i>On September 18, 20, and 22, 1993, while Unit 1 was at 100%, 63%, and 60% power respectively, a large number of jellyfish were drawn from the Atlantic Ocean into the intake canal. This condition created a large differential pressure across the intake traveling screens necessitating the removal of non-safety related circulating water pumps from service. In accordance with Off-Normal Operating Procedure 1-0620030, Circulating Water System, manual reactor and turbine trips were initiated on Unit 1 at power levels of 75%, 63%, and 11% respectively as cooling water to one of the main turbine condensers was removed from service. In each case the Standard Post Trip Actions of EOP-1 led to a diagnosis of an uncomplicated reactor trip. EOP-1 was exited and upon completing EOP-2, Reactor Trip Recovery, the Unit was stabilized in Mode 3, Hot Standby. During this time period, the safety related intake cooling water system remained in service.<br /><br /> The root cause of the event was that an abnormal influx of jellyfish was greater than the intake traveling screen system could efficiently handle. <br /><br /> Interim corrective actions for this event were: The unit was maintained at reduced power or kept offline at appropriate times to prevent equipment damage. The intake traveling screens were manned and operated as necessary with the Circulating Water Pump discharge valves throttled to minimize the jellyfish influx at the intake structure. The influx of jellyfish subsided on 29 September.
3351993008 | St. Lucie 1 | 11/01/1993 | 12/01/1993 | 9312100180 | <strong>Inadvertent Start of the 1B Containment Spray Pump due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1993, St. Lucie Unit 1 was in mode 1 operating at 100% steady state reactor power. At 0045, a licensed utility operator performing a valve stroke surveillance inadvertently started the 1B Containment Spray pump. No spray flow resulted from the pump start, which lasted approximately 4 seconds, because the header flow control valve was closed.<br /><br /> The root cause of this event was cognitive personnel error. A licensed utility operator inadvertently operated the wrong switch when attempting to cycle the containment spray valve for the stroke time surveillance. <br /><br /> The corrective actions for this event: the operator immediately stopped the pump and informed his supervisor, the individual, was counseled on the importance of self checking, Operations supervision conducted a crew conference on the aspects of self verification, training on self-checking continues to be emphasized, and a Human Performance Enhancement Review was performed. Also, an enhancement to the Unit 1 and Unit 2 Containment Spray pump control switches will be made by February, 1994. <br /><br /> This Licensee Event Report is being submitted voluntarily. The header flow control valve was closed when the 1B Containment Spray pump was started. Engineered Safety Feature logic circuitry was energized.
3351993009 | St. Lucie 1 | 11/17/1993 | 06/28/1994 | 9407070132 | <strong>Engineered Safety Features Actuation due to Spurious Subgroup Actuation Module Trip</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993, Unit 1 was in mode 1 and operating at 98% steady state power. One of four Engineered Safety Features Actuation System containment radiation measurement bistables was in trip due to maintenance. At 1336 Unit 1 experienced a trip of a single subgroup actuation module on one of two containment isolation system actuation channels. Utility licensed operators and the Instrument and Control system supervisor confirmed proper component actuation of this subgroup module. The subgroup actuation module trip was determined to be spurious and the actuation module signal reset. The subgroup actuation module was replaced as a precaution and the new module was tested satisfactorily. The actuated components were then returned to their normal position. The root cause of the containment isolation system subgroup actuation module trip was due to a spurious signal on one containment isolation system radiation monitoring channel while another channel was out of service and in the trip condition.<br /><br /> Corrective actions were: The subgroup actuation module was replaced and tested and the actuated components were reset. Repairs were completed on the previously out of service containment radiation channel and the radiation detector was replaced. The subgroup actuation module was tested by the vendor and found to be functioning correctly.
3361993001 | Millstone 2 | 12/27/1992 | 01/27/1993 | 9302040100 | <strong>Technical Specification surveillance not performed within required time interval</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1992 at 1200, with the plant in Mode 5 at 97 degrees and atmospheric pressure, it was discovered that surveillance procedure SP 2614A-3, "Weekly Checks in Mode 5 and 6" had not been performed within the specified time interval, in accordance with Technical Specification 4.0.2. The surveillance procedure verifies AC electrical facility alignment and voltage, DC electrical facility alignment and voltage and also verifies Reactor Vessel and Spent Fuel Pool water levels. The weekly surveillance procedure is required to be conducted at least every 8 3/4 days (7 days + 25% = 8 Days 18 hours). It had been ten days since the surveillance was last completed. The surveillance was immediately performed.
3361993002 | Millstone 2 | 01/07/1993 | 02/05/1993 | 9302180087 | <strong>Failure to Enter Technical Specification Action Statement</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1993, the plant entered Mode 3 at 0031. At approximately 1300, it was determined that Limiting Condition for Operation (LCO), "Accident Monitoring" para. 3.3.3.8 a. action 2 and action 3 had not been entered upon entry into Mode 3. The required data for these 2 action statements was taken immediately and the previous shifts' data was obtained from the process computer. By 1430, the scheduled surveillance procedures were completed, the instruments were determined operable and the unit logged out of the LCO Action Statement. This LER is submitted because the data, required by the Action Statement, was not taken within the required 12 hour time period.
3361993003 | Millstone 2 | 02/17/1993 | 03/17/1993 | 9303220338 | <strong>High Pressure Safety Injection Valve Not at Proper Open Position</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1993, at 0936, with the plant operating at 100% power, it was discovered that a mispositioned High Pressure Safety Injection (HPSI) valve would have rendered the Facility 1 HPSI system inoperable. This discovery was made while the Facility 2 Emergency Diesel Generator (EDG) had been removed from service to perform preventive maintenance. Operators took immediate action to restore the valve to its correct position in accordance with the time limits of Technical Specification 3.0.5. Subsequent investigation concerning the mispositioned valve resulted in the determination that since the condition existed at the start of the Facility 2 diesel outage, the requirements of Technical Specification 3.0.5 had been exceeded for a period of 1 hour and 26 minutes. <br /><br /> No further operator action was required.
3361993004 | Millstone 2 | 02/22/1993 | 07/02/1993 | 9307080246 | <strong>Reactor Trips on Steam Generator Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1993, at 0144 hours, with the plant in Mode 1 at 100% power, the 'A' steam generator atmospheric steam dump valve (ADV) failed open. During the subsequent transient plant conditions, the 'B' main feedwater pump automatically tripped on low suction pressure, and an automatic reactor trip on low steam generator water level occurred at 0151 hours. Operators then performed Emergency Operating Procedure EOP 2525, 'Standard Post Trip Actions.' All safety related equipment responded as expected and the unit was placed in a stable condition. The cause of the reactor trip was the inability to recover the water level in the 'A' steam generator following the trip of the 'B' main feedwater pump. <br /><br /> During the subsequent plant startup on February 23, 1993, at 2037 hours, with the plant in Mode 1 at 18% power, high vibration of several main turbine bearings required shutdown of the main turbine. Reactor power was quickly reduced to approximately 14% power and the main turbine was tripped at 2040 hours. During the subsequent transient plant conditions, an automatic reactor trip on low steam generator water level occurred at 2043 hours. Operators then performed Emergency Operating Procedure EOP 2525, 'Standard Post Trip Actions.' All safety related equipment responded as expected and the unit was placed in a stable condition. The cause of the reactor trip was insufficient feedwater flow to the steam generators for the existing reactor power level. <br /><br /> These events are being reported pursuant to the requirements of Paragraph 50.73(a) (2) (iv), reporting any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature System.
3361993005 | Millstone 2 | 02/22/1993 | 07/09/1993 | 9307220083 | <strong>Automatic Reactor Protection System Actuation While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1993, at 1625 hours, with the plant in Mode 1 at 100% power, it was discovered that an automatic Reactor Protection System (RPS) actuation had occurred on February 22, 1993 which had not been immediately reported to the USNRC. The USNRC was notified of this event on March 11, 1993 at 1707 hours.<br /><br /> On February 22, 1993, at 0811 hours, with the plant in Mode 3 at 0% power, Reactor Coolant System (RCS) pressure at 2267 psia, RCS average temperature at 527 degrees Fahrenheit, and all control rods fully inserted, an automatic RPS actuation occurred during an unplanned cooldown event. The cooldown caused the steam generator pressures to decrease to approximately 707 psia, which caused an automatic RPS actuation on low steam generator pressure. <br /><br /> The only automatic safety system response during the above event was the opening of the reactor trip circuit breakers. Due to personnel error, this event was not immediately reported to the USNRC pursuant to the requirements of Paragraph 50.72 (b) (2) (ii), reporting any event or condition that results in manual or automatic actuation of any Engineered Safety Feature System, including the Reactor Protection System.
3361993006 | Millstone 2 | 03/24/1993 | 04/23/1993 | 9305030003 | <strong>Structural Integrity of Service Water Supply Piping to the West 480V Switchgear Room Coolers</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1993, at 1800 hours with the plant at 100% power it was determined that the service water supply piping to switchgear room coolers X-181A and X-181B did not meet the structural integrity requirements of Technical Specification 3.4.10. <br /><br /> During the unit's refueling outage, service water piping inside the West 480 V Switchgear Room had been modified to facilitate the installation of new coolers. All of the pipe welds inside the switchgear room were completed and all code required final visual inspection were satisfactorily performed by December 30, 1992. However, the hydrostatic test was deferred until service water pipe replacement located outside the room were completed. Concurrent with the piping work, the turbine was placed on-line on January 13, 1993, revealed a small leak under hydrostatic pressure. With the plant on-line, a code repair was not feasible due to the potential for a plant trip caused by welding in the area of sensitive electrical equipment. Therefore, a relief request was submitted on February 24, 1993. During USNRC review of the relief request, it was determined that TS 3.4.10 was applicable and that the structural adequacy was in question since the leak was discovered during a hydrostatic test. <br /><br /> Enforcement discretion for TS 3.4.10 was verbally granted by the USNRC on March 25, 1993. An Engineered Clamp which provides enhanced structural integrity for the affected weld joint was installed on March 31, 1993. Millstone Unit 2 logged out of the enforcement discretion on March 31, 1993, at 1532 hours.
3361993007 | Millstone 2 | 03/29/1993 | 04/28/1993 | 9305060222 | <strong>Diesel Generator Parallel Operations</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1993 at 1350 hours with the plant at 100% power and normal operation, the determination was made that the paralleling of an emergency diesel generator with the grid while the other diesel generator is not operable is unsatisfactory. Synchronizing the only operable diesel generator with the grid, makes that diesel generator susceptible to faults on the grid that can disable the diesel generator. <br /><br /> This is being reported as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Technical Specification section 3.8.1.1 requires the operable diesel generator to be started, within one hour and at least once per eight (8) hours thereafter, when the other diesel generator is inoperable. The requirement of loading (parallel to grid) the diesel generator each time it was started was added to support vendor recommendations. The vendor recommendation was made as a general good practice to avoid buildup of residue in exhaust ports, that could create a fire hazard. <br /><br /> Procedures have been changed to clarify that the operable diesel generator must not be paralleled with the offsite power system (grid) whenever the other diesel generator is inoperable. <br /><br /> Changes to Technical Specification LCO 3.8.1.1 are planned to reflect current NRC guidance and corresponding Technical Specification requirements at other similar plants. <br /><br /> Similar Events: none
3361993008 | Millstone 2 | 05/05/1993 | 09/02/1993 | 9309090412 | <strong>Charging Pumps Inoperable Due to Low Control Power Voltage</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1993, at 1045 hours with the plant at 100% power and normal operation an Engineering Evaluation determined the electrical starter for the "A" "B" (aligned to the facility Z2 power supply) and "C" Charging pumps could have insufficient control power (120 volt AC) during a degraded voltage condition, and fail to start the Charging pumps. The Charging pumps in question have long lengths of cable which increases the resistance of the control circuit, and thus reduces the available voltage for the starter. <br /><br /> This is being reported as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This condition is only a concern during a degraded grid voltage condition, which is higher than the level two bistable trip setpoint for a Loss of Normal Power (LNP). If an LNP was to occur, which starts and loads the Diesel Generators, the control power returns to normal levels and is no longer a concern. <br /><br /> Immediate response was to provide administrative controls which identified the operating configuration that would ensure the minimum Technical Specification requirements for the Charging System are satisfied.<br /><br /> Between June 7, 1993, and July 13, 1993, testing of the Motor Control Center controllers with simulated conditions to match actual installed conditions proved all components, except the "C" Charging Pump, would start under degraded grid voltage conditions. <br /><br /> The long term solution is to install an interposing relay within the "C" Charging Pump control circuit. This modification will reduce the voltage drop across the cabling, and provide sufficient voltage at the starter relay coil. <br /><br /> Similar Events: 76-42
3361993009 | Millstone 2 | 05/06/1993 | 06/04/1993 | 9306100282 | <strong>Radiation Monitor 6038 Inlet and Outlet Isolation Valve Found Shut</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1993, at 0100 hours, with the plant operating in Mode 1 at 100 percent power, the inlet and outlet skid mounted isolation valves to radiation monitor RM-6038 for the Reactor Building Component Cooling Water (RBCCW) system were found shut. The closed valves were discovered by a Plant Equipment Operator investigative the cause of no flow through two sample flow indicators for the radiation monitor. Immediate operator action was to open the inlet and outlet isolation valves and notify the Control Room. Chemistry was then requested to sample the Reactor Building Component Cooling Water (RBCCW) for possible radioactive contamination. None was found. <br /><br /> It was determined that Radiation Monitor RM-6038 had been isolated for three days without any grab samples taken and analyzed, as required by plant Technical Specifications. The root cause of the event was procedure noncompliance during the performance of the calibration procedure for Radiation Monitor RM-6038 by Instrument and Control (I&C) personnel. This occurred when I&C notified Operations that RM-6038 was returned to service, but mistakenly left the skid mounted valves in the closed position. The personnel involved have been counseled as to the importance of procedure compliance and the procedure used to calibrate RM-6038 has been enhanced to prevent future recurrence. In addition, the Instrument and Control Department is going to review and edit other radiation monitoring procedures and enhance them as required to ensure this error will not be repeated in similar procedures. No safety related equipment was affected. This event is reportable pursuant to 10CFR50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications.
3361993010 | Millstone 2 | 10/29/1993 | 11/23/1993 | 9312060023 | <strong>MP2 Failure to Perform ASME Leakage Test</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1993, at 1030 hours, with the unit in Mode 1, 100% power, the unit failed to perform a post work ASME leakage test on valve 2-CH-223. This event was discovered during the close out review of the automated work order (AWO) for the maintenance activity performed on the valve. The retest block of the AWO specified that a leakage test was required, however, no specific reference was made to the ASME leakage test in accordance with Engineering procedure number 21218 as required in the ASME Section XI Repair/Replacement Plan. When the valve was restored to service, Operations performed a leakage test in accordance with the retest portion of the AWO. This resulted in a failure to perform the leakage test using a qualified VT-2 inspector and the failure to perform the required ASME documentation required for leakage tests. Upon discovery of the error, the leakage test was repeated in accordance with ASME requirements and found to be satisfactory.
3361993011 | Millstone 2 | 10/07/1993 | 11/02/1993 | 9311100198 | <strong>Underrated Emergency Diesel Generator Air Start Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1993, at 1830 hours with the unit in Mode 4 (Hot Shutdown), the 'B' Emergency Diesel Generator (EDG) was declared inoperable due to an underrated air start solenoid. At the time of discovery, the unit was in its 55th hour of a 72 hour action statement. Technical Specification Action Statement (TSAS) 3.8.1.1, action (a) was entered on October 5, 1993, at 1011 hours, due to corrective and preventative maintenance performed on the 'A' EDG. During post maintenance retesting, the 'A' EDG remained inoperable due to a slow start on one of its two redundant air start trains. Upon discovery of the underrated solenoid on the 'B' EDG, the unit was placed under TSAS 3.8.1.1 action (d), two inoperable EDGs. Preparations were immediately undertaken to place the plant in Mode 5 (Cold Shutdown). On October 8, 1993, at 0215 hours, the 'A' EDG was returned to service after satisfactory repairs to its starting air "Grove-Flex" valve. The unit re-entered TSAS 3.8.1.1 action (a) for the remainder of the 72 hours which began on October 5, 1993. The underrated solenoid was replaced at 0955 hours and the unit logged out of the TSAS. It should be noted that during this condition, at least one EDG and at times both of the EDGs were available though not OPERABLE by Technical Specification definition due to its redundant air start systems.
3361993012 | Millstone 2 | 05/24/1993 | 07/23/1993 | 9308030024 | <strong>Turbine and Reactor Trip During Mussel Cook (Thermal Backwash)</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1993, at 0943 hours, with the plant in Mode 1 at 100% power, a reactor trip occurred due to a turbine trip. The turbine trip was caused by high generator stator cooling water temperature resulting from mussel cooking (thermal backwash) operations on the 'B' condenser waterbox. During the subsequent transient, a malfunction caused the 'A' feedwater regulating valve to stay at approximately 56% open which caused the #1 steam generator water level to increase to the high level setpoint. The reactor operator tripped the running feedwater pump based on the high steam generator water level. Steam generator water levels were subsequently controlled using the auxiliary feedwater system, Operators performed Emergency Operating Procedure 2525, "Standard Post Trip Actions." All safety related equipment, with the exception of the main feedwater regulating valves, responded as expected and the unit was placed in a stable condition. During the event investigation subsequent to the trip, it was discovered that during the mussel cook, Reactor Building Closed Cooling (RBCCW) temperatures momentarily exceeded 85 degrees F which potentially resulted in the plant being outside of its design basis. RBCCW temperatures immediately returned to normal.<br /><br /> These events are being reported pursuant to the requirements of Paragraph 50.73(a)(2)(iv) and Paragraph 50.73(a)(2(ii)(B) reporting any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature System including the Reactor Protection system and to report an event or condition that potentially resulted in the nuclear power plant being in a condition outside the design basis of the plant.
3361993013 | Millstone 2 | 06/03/1993 | 07/02/1993 | 9307080096 | <strong>Reactor Trip on High Pressurizer Pressure</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1993, at 1624 hours, with the plant in mode 1 at 100% power, the main turbine generator Electro-Hydraulic Control (EHC) system initiated a signal that caused the main turbine to rapidly, decrease load. The sudden load drop caused an increase in pressurizer pressure, resulting in a reactor trip. The EHC signal has been attributed to spurious relay actuations as a result of operations within the EHC cabinet.<br /><br /> Operators performed Emergency Operating Procedure EOP 2525, "Standard Post Trip Actions" and all safety related equipment performed as expected. <br /><br /> This is being reported pursuant to requirements of Paragraph 50.73(a)(2) (iv), reporting any event or condition that resulted in manual or automatic actuation of any, Engineered Safety Feature system, including the Reactor Protection System (RPS).
3361993014 | Millstone 2 | 07/14/1993 | 01/24/1994 | 9402040171 | <strong>Technical Specification Surveillance Not Performed Within Required Time Interval</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1993, at 1200 hours, with the plant in Mode 1, 100% power level, it was discovered that surveillance procedures SP 2608C-1, 'Post Incident Recirculation System Operability Test,' and SP 2610F-1, 'PORV Block Valve Operability Test,' had not been performed within the specified time interval in accordance with Technical Specification 4.0.2. SP 2608C-1 verifies the Facility 1 post incident recirculation fan can be started by the operator from the Control Room and that it operates for at least 15 minutes. SP 2610F-1 verifies that the block valve can operate through one complete cycle of full travel and valve position indication is available in the Control Room. These quarterly surveillance procedures are required to be conducted every 3 months, not to exceed a maximum of 115 days ((92 days + 25%) = 115 days). SP 2608C-1 and SP 2610F-1 had been previously performed on March 1,1993. Upon discovery of the missed surveillances, they were immediately performed.
3361993015 | Millstone 2 | 09/13/1993 | 11/23/1993 | 9312060029 | <strong>Shutdown Due to Feedwater Block/Bypass Valve (2-FW-38A&B and 2-FW-42A&B) Inoperability</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1993, at 1700 hours, with the plant in Mode 1, 100% power, during a review of operating experience information, it was discovered that the actuator motor brakes on feedwater motor operated valves (MOVs) 2-FW-38A&B and 2- FW-42A&B might not release at design undervoltage. This could prevent closure of the valves, which is credited in the Main Steam Line Break analysis. An engineering investigation was immediately initiated to determine operability of the feedwater valves. <br /><br /> On September 14, 1993, at 1915 hours, with the plant in Mode 1, 100% power, Millstone Unit 2 (MP2) was shutdown due to inoperability of feedwater MOVs 2-FW-38A&B and 2-FW-42A&B. The engineering investigation had determined that the feedwater MOVs were susceptible to failure of the actuator motor brakes to disengage during design basis undervoltage conditions. Engineering began pursuing a design change that would return the valves to operability. <br /><br /> On September 18, 1993, at 1400 hours, with the plant in Mode 4, 0% power, it was discovered that feedwater MOVs 2-FW-38A&B and 2-FW-42A&B had been operated to thrust levels which exceeded the thrust allowables. Engineering review of a recently acquired weak link analysis determined that the maximum thrust allowables previously provided by the valve vendor, and specified in MOV Program calculations, were not conservative.<br /><br /> As a result of the above, the motor brakes were removed. In addition, valve modifications were performed and tested to ensure adequate performance. No further action is required.
3361993016 | Millstone 2 | 07/29/1993 | 01/10/1994 | 9401280071 | <strong>Inconsistency Between Safety Analysis and Plant Operating Procedures</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1993, at 1620 hours, with the plant operating in Mode 1 at 100% power, a reportability determination was made concerning the analysis for a boron dilution event. The result of this analysis and plant operating procedures placed conflicting requirements on the operation of the Shutdown Cooling (SDC) system. <br /><br /> The October 1988 boron dilution event analysis required a minimum SDC flow of 2450 gallons per minute (gpm) in modes 4 and 5. Plant operating procedures require the SDC flowrate to be less than 1500 gpm to prevent vortexing at the SDC suction line when in mode 5 and with the Reactor Coolant System (RCS) drained to the centerline of the reactor vessel hotleg. <br /><br /> The boron dilution event was reanalyzed. The following assumptions were changed: <br /><br /> The number of operable charging pumps was changed from 3 to 2 for RCS cold leg temperatures less than 300 degrees Fahrenheit.<br /><br /> The shutdown margin requirement for mode 5 was increased from 2% delta k/k to 3.6% delta k/k. <br /><br /> The revised analysis requires no SDC flowrate restrictions for modes 4 and 5, and a minimum SDC flowrate of 950 gpm in mode 6.
3361993017 | Millstone 2 | 07/01/1993 | 08/03/1993 | 9308100003 | <strong>Possible Inoperability of Power Operated Relief Valve Blocking Valves</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1993, with the reactor in Mode 1, at 100% power, discussions with NRC Representatives, relative to implementation of NRC Generic Letter 89-10, identified that manufacturer's design valve factors, used in determination of operability of the Power Operated Relief Valve (PORV) Blocking Valves, 2-RC-403 and 2-RC-405 prior to Operating Cycle 12, may not have been sufficiently conservative. Preliminary results from NRC and industry test programs indicate some gate valves require more force to close than had been assumed by the manufacturer's valve factor. Use of the manufacturer's design valve factors led to a conclusion that these valves were operable When they may not have been able to close to isolate a stuck open PORV at design basis conditions. The possible effects of using a non-conservative valve factor are tempered by other conservatisms in the calculations. Design changes and testing performed during the refueling prior to Operating Cycle 12 provide assurance that the valves are capable of fulfilling all design basis functions during Operating Cycle 12 and subsequent cycles. This report is filed for information only.
3361993018 | Millstone 2 | 08/05/1993 | 10/15/1993 | 9310220007 | <strong>Letdown Isolation Valve 2-CH-442, Leakage Above 1.0 GPM</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1993, at 1439 hours, with the plant in Mode 1 at 100% power, Letdown Manual Isolation Valve 2-CH-442 (nonisolatable from the Reactor Coolant System) developed a leak which exceeded the Technical Specification Limiting Condition for Operation (LCO) 3.4.6.2, Reactor Coolant System "unidentified" leakage limit of 1.0 gallon per minute. No attempt was made to quantify this leakage as "identified" leakage. The Technical Specification Action Statement requires that the leakage rate be reduced to within limits within 4 hours or be in Cold Shutdown within the next 36 hours. Operations personnel immediately began a controlled plant shutdown utilizing Operating Procedure, OP 2205, "Plant Shutdown," and Abnormal Operating Procedure, AOP 2568, "Reactor Coolant System Leak." On August 6, 1993, at 0933 hours, the plant was in Mode 5, 19 hours after the controlled shutdown was initiated. During the controlled plant shutdown there were no challenges to the plant safety systems. All other systems and controls remained operable during this time period. This event is being reported pursuant to the requirements of Paragraph 50.73(a)(2)(i), the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
3361993019 | Millstone 2 | 08/12/1993 | 09/10/1993 | 9309170019 | <strong>Reactor Trip Due to Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1993, the plant was operating in Mode 2. At 13:44 a reactor trip occurred due to low Steam Generator (SG) level. Approximately one hour prior to the trip the plant had entered mode 2 (reactor critical) and SG levels were being maintained by one auxiliary feedwater pump. Reactor power had just been increased to 2% and preparations were being made to start a main feedwater pump and begin the turbine warming process. Following the reactor trip Emergency Operating Procedure EOP 2525, Standard Post Trip Actions, was performed. All safety related equipment responded as expected, and the unit was placed in a stable condition.
3361993020 | Millstone 2 | 10/04/1993 | 11/02/1993 | 9311100194 | <strong>Switchgear Room Cooling and RBCCW Systems Found To Be Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1993, at 1310 hours with the plant shutdown and in Mode 4, it was determined by review of the Service Water System analysis that the Switchgear Room Cooling System and the Reactor Building Closed Cooling Water (RBCCW) System were outside their plant design basis. <br /><br /> Calculations performed in response to NRC Generic Letter 89-13 (GL 89-13) showed that during both (1) a Safety Injection Actuation Signal (SIAS) without Loss of Normal Power (LNP) or (2) a seismic event without an LNR the AC Vital Switchgear Rooms could reach 112 degrees F, which is above their design basis temperature of 104 degrees F. Upon discovery of the increased room temperatures, electrical analysis was performed to demonstrate that the subject equipment remains operable to a temperature of 122 degrees F. <br /><br /> The GL 89-13 analysis also showed that the peak RBCCW heat exchanger outlet temperature would increase from its design basis temperature of 104.5 degrees F to 114 degrees F during normal shutdown cooling. As with the switchgear cooling system, additional calculations were performed to demonstrate that the RBCCW equipment remains capable of performing its intended safety function. <br /><br /> Final Safety Analysis Report (FSAR) Change Requests have been initiated to reflect these changes..
3361993021 | Millstone 2 | 08/27/1993 | 09/27/1993 | 9310050311 | <strong>PORV Block Valves Found Outside Their Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1993, at 22:00 hours, with the plant in Mode 1 at 100% power, 572 degrees Fahrenheit (F), and 2260 psia, an engineering evaluation determined that the Power Operated Relief Valve (PORV) block valves (2-RC-403 and 2-RC-405) were not capable of closing against their Design Basis differential pressure (D/P) of 2250 psi. However, the block valves were deemed operable because an engineering analysis showed them capable of shutting against a D/P of 1880 psi. This capability was believed to enable the PORV block valves to perform their intended safety function of isolating a stuck open PORV<br /><br /> On September 1, 1993, at 21:22, with the plant in Mode 1 at 100% power, 572 degrees F, and 2260 psia, the PORV block valves were declared inoperable. An engineering review identified that the valves may be unable to perform their design basis safety function of isolating a stuck open PORV during certain postulated scenarios if the guidance contained within the applicable operating procedures (OP), abnormal operating procedures (AOP), and emergency operating procedures (EOP) was followed. <br /><br /> The immediate operator action was to enter Technical Specification Action Statement 3.4.3.b. Both PORV block valves were closed and power was removed from both valves. This prevented the PORVs (2-RC-402 and 2-RC-404) from providing overpressurization protection. Overpressurization protection continued to be provided by the pressurizer code safety valves.<br /><br /> The engineering review considered preliminary data obtained from the Electric Power Research Institute (EPRI) Performance Prediction Program for a valve of the same size and manufacturer, and of similar design to the Millstone Unit No. 2 PORV block valves. This data indicated that the assumptions used for previous evaluations of PORV block valve operability may have been non-conservative. The initial engineering assessment concluded that the PORV block valves would continue to re-energize and attempt to close until ultimately closing when RCS pressure dropped below 1880 psia. Further review identified that there was insufficient evidence to assure that the valves would have been able to close under all operating and accident conditions. On September 3, 1993, following procedure changes restricting operator closure of the PORV block valves until RCS pressure decreases to less than 1800 psia, the PORV block valves (2-RC-403 and 2-RC-405) were declared operable and returned to service.
3361993022 | Millstone 2 | 09/03/1993 | 01/05/1994 | 9401190015 | <strong>Auxiliary Feed Water Suction Header Operability and ISI Program Omission</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1993, at 1500 hours, with the Plant operating in Mode 1, 100% power, it was determined that a make-up water line connected to the Auxiliary Feed Water (AFW) pump suction header may not have been seismically qualified. At 2132 hrs on September 3, 1993, the affected auxiliary feedwater suction header was isolated and Technical Specification Action Statement (TSAS) 3.7.1.2.a. was entered. On September 4, 1993, it was decided to consider the AFW suction header inoperable, due to an inability to seismically qualify the 3" make-up line. This event was reported at 1605 on September 4,1993. Following completion of design modifications, the TSAS was exited at 1800 hours on September 5, 1993. As a result of this finding the ISI Program was reviewed. On September 10, 1993 a preliminary review identified a possible omission in the ISI Program. On September 16, 1993 with the Unit in Hot Shutdown, Mode 3, it was determined that hangers associated with the AFW suction lines were inadvertently excluded from the ISI inspection program. An immediate inspection of the hangers was performed in accordance with Technical Specification 4.0.3. At 0929 on September 17, 1993, it was determined that the hanger surveillance could not be completed in the 24 hours allowed by 4.0.3 and a plant cooldown to Mode 4 was commenced. Subsequent inspection and review concluded that subject hangers were operable and the AFW lines had in fact remained operable at all times. An independent review of the ISI Program was completed to ensure that no other portions of the code required inspection boundaries had been excluded. A portion of the main steam piping was also determined not to be included in the ISI Program. No additional examinations were required to be performed as a result of this omission.<br /><br /> On October 20, 1993, a decision was made to change the ISI boundary for the AFW system based on a review of the ISI Plan. As a result of this change, two hangers were added to the ISI component list. These hangers were satisfactorily inspected.
3361993023 | Millstone 2 | 08/30/1993 | 06/19/1997 | 9706250237 | <strong>Leakage Through Letdown Valves 2-CH-089 and 2-CH-515</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1993, at 1315 hours, with the Unit in Mode 1 at 100% power, it was noted that 20 to 30 gallons per minute of letdown was flowing through Letdown Isolation Valve 2-CH-089 with the valve indicating closed. On June 25, 1993, at 1300 hours, with the Unit in Mode 1 at 100% power, it was noted that 40 gallons per minute was flowing through Letdown Isolation Valve 2-CH-515 with the valve indicating closed. On August 30, 1993, an engineering analysis performed to assess the consequences of leakage through valves 2-CH-089 and 2-CH-515 concluded that leakage from the reactor coolant system to an area outside of containment could occur. These valves, along with 2-CH- 516, are installed in series and provide Containment Isolation and/or Letdown isolation following receipt of a Safety Injection Actuation Signal or Containment Isolation Actuation Signal. Additionally, a review performed in 1996 identified that the potential leakage through valve 2-CH-089 would have exceeded the Reactor Coolant System leakage assumptions made in the Appendix R analysis during the first 4 hours of a fire in Fire Area R-1 (Control Room, Cable Vault and portions of the Auxiliary Building). Recent As-Found testing identified these valves as having been improperly set and would not adequately isolate against Normal Operating System Pressure (NOSP).<br /><br /> The cause of this event was an inadequate program to ensure that facility procedures clearly address all design basis functions. <br /><br /> To correct this condition the affected valves will be readjusted to ensure they will close against NOSP. Procedures will be revised to ensure proper valve control parameters are specified and verified following valve maintenance.
3381993001 | North Anna 1 | 01/17/1993 | 02/10/1993 | 9302170309 | <strong>Personnel Hatch Outer Door Escape Lock Equalization Valve Not Fully Closed As Required For Containment Integrity During Core Alterations Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1993, at 2230 hours with Unit 1 in Mode 6 (refueling) the equalization valve for the personnel hatch outer door escape lock was discovered open during core alterations. This valve is required to be closed for containment integrity per Technical Specification 3.9.4.c.1 when the personnel hatch is used for access during core alterations. All operations involving core alterations were immediately suspended and the equalization valve was closed. A 4 hour report was made to the NRC at 0028 hours on January 18, 1993, pursuant to 10 CFR 50.72 (b) (2) (iii) (c). This event is reportable pursuant to 10CFR50.73 (a)(2)(v)(C). <br /><br /> The cause of the event has been attributed to personnel error. Administrative controls in place to preclude the inadvertent operation of the personnel hatch emergency escape lock did not prevent the equalization valve from being opened. <br /><br /> No significant safety consequences resulted from the event because any release of radioactivity from this event had a fuel handling accident occurred is bounded by previously calculated accident analysis assumptions. Therefore, the health and safety of the public were not affected at any time during this event.
3381993002 | North Anna 1 | 01/20/1993 | 02/04/1993 | 9302100278 | <strong>Pressurizer And Main Steam Safety Valve Setpoints Out Of Tolerance Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1993, with Unit 1 in mode 6 (Refueling), the "as found" set pressures for one Pressurizer Safety Valve and two Main Steam Safety Valves (MSSVs) were found to be outside the setpoint tolerances allowed by Technical Specifications 3.4.2, 3.4.3.1 and 3.7.1.1, respectively. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for conditions prohibited by Technical Specifications 3.4.2, 3.4.3.1 and 3.7.1.1. <br /><br /> The safety valves were sent to Wyle Labs for testing to ensure conformance to Technical Specifications requirements. The "as found" set pressures for one Pressurizer Safety valve and two MSSVs were found to be outside Technical Specification tolerances. In addition, leakage was noted from one Pressurizer Safety Valve and fifteen MSSVs following "as found" testing. <br /><br /> The safety valves will be repaired and readjusted to be within the correct setpoint tolerance allowed by Technical Specifications. <br /><br /> This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time during this event.
3381993003 | North Anna 1 | 01/22/1993 | 04/09/1993 | 9304150039 | <strong>Emergency Diesel Generator Load Sequencing Timer Setpoint Drift Due To Poor Repeat Accuracy Of The Agastat 2400/7000 Series Timers</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1993, with Unit 1 in Refueling, Mode 6, it was determined during Emergency Diesel Generator load sequencing timer testing that three Control Rod Drive Mechanism cooling fans had timers that drifted outside their setpoint tolerance listed under Technical Specification (TS) Table 4.81. In addition, a containment recirculating air fan timer was found outside its setpoint tolerance. On January 26, 1993, a standby primary grade water pump timer was found outside its setpoint tolerance. On March 26, 1993, with Unit 1 in Cold Shutdown (Mode 5), it was discovered that on March 5, 1993, the 1 "A" Component Cooling (CC) Pump had two timers with the "as found" setpoint tolerance outside the limits listed under TS Table 4.8-1. These conditions are prohibited by the TS, and are reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event is setpoint drift due to poor repeat accuracy of the Agastat 2400/7000 series time delays. The CC pump timers were replaced with solid state timers during the current Unit 1 refueling outage.<br /><br /> Engineering performed an evaluation to review the impact that setpoint drift of timers would have on the operation of the EDG load sequencing scheme and determined that no significant safety consequences resulted from this event. Therefore, the health and safety o the public were not affected at any time due to this event.
3381993004 | North Anna 1, North Anna 2 | 02/15/1993 | 03/05/1993 | 9303150003 | <strong>Containment Particulate And Gaseous Radiation Monitors Inoperable Due To No Containment Air Recirculating Fans Operating During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1993, at 1300 hours with Unit 1 defueled it was noted that the containment gaseous and particulate radiation monitors become inoperable when no containment air recirculating fans are operating. The monitors must be operable for the containment purge and exhaust isolation system to be operable when in Mode 6 during core alterations per Technical Specification (TS) 3.9.9. The monitors are also required by TS 3.4.6.1 in Modes 1 through 4. The radiation monitors, RM-RMS-159/160, continuously draw a sample from containment atmosphere via an isokinetic nozzle in the recirculating air ring duct. However, when no fans are operating a representative sample of containment air is not obtained. During the current refueling outage the fans were secured thereby rendering the radiation monitors inoperable. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the event is an inadequate initial review of the containment gaseous and particulate radiation monitor operating conditions which failed to identify that at least one containment air recirculating fan must be in operation to support the operability requirements of RM-RMS-159/160. <br /><br /> No significant safety consequences resulted from the event because additional containment radiation monitors were operable and available to detect increasing radiation levels. Therefore, the health and safety of the public were not affected at any time during this event.
3381993005 | North Anna 1 | 02/19/1993 | 03/09/1993 | 9303150242 | <strong>Loss Of 1H Emergency Bus Due To Feeder Breakers Tripping Open Upon Degraded Voltage Auxiliary Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1993, at 1530 hours with unit 1 defueled the 1H 4160 volt emergency bus was de-energized as a result of the 1H emergency bus feeder breakers tripping open. The 1H emergency diesel generator had been removed from service to prevent an unnecessary start while calibrating the 90 percent degraded voltage sensing relays. Upon completing the calibration two of three normally energized auxiliary relays failed to reset when they were energized. As a result the circuit interpreted this action as a degraded voltage condition on B and C phases which caused the feeder breakers to trip open causing a loss of power to the 1H emergency bus. The 1H emergency bus was energized at 1647 hours. A four hour report was made to the NRC pursuant to 10CFR50.72(b)(2)(ii). This event is reportable pursuant to 10CFR50.73(a)(2)(iv). <br /><br /> The cause of the event is component failure of two degraded voltage auxiliary relays. <br /><br /> No significant safety consequences resulted from the event because the 1J 4160 volt emergency bus was energized and remained fully operable throughout this event. Therefore, the health and safety of the public were not affected at any time during this event.
3381993006 | North Anna 1, North Anna 2 | 02/25/1993 | 03/22/1993 | 9303260138 | <strong>Previously Unidentified Potential Loss Of Coolant Accident, Emergency Core Cooling System Leakage Path To Environment During Recirculation Mode Of Operation Due To Inadequate Initial Design</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1993, at 1954 hours with Unit 1 defueled and Unit 2 in Mode i (100 percent power) a four hour report was made to the NRC pursuant to 10CFR50.72 (b) (2) (iii) (C) due to the confirmation of a previously unidentified potential post-LOCA, Emergency Core Cooling System (ECCS) leakage path to the environment during the recirculation mode of operation. Failure of the check valve between the volume control tank (VCT) and the suction of the High Head Safety Injection (HHSI) charging pumps could result in the pressurization of the seal water heat exchanger by the low head safety injection (LHSI) pump discharge. The relief valve on this line discharges to the VCT which in turn relieves to the liquid waste system which could ultimately overflow to the auxiliary building sump. This condition is reportable pursuant to 10CFR50.73 (a) (2) (v) (C). <br /><br /> The cause of the condition was an inadequate initial design which failed to identify the potential leak path.<br /><br /> No significant safety consequences resulted from the condition. Compensatory actions to prevent a release to the environment are available. The ECCS operability is not compromised. Therefore, the health and safety of the public were not affected at any time during this condition.
3381993007 | North Anna 1 | 03/08/1993 | 04/05/1993 | 9304120051 | <strong>Unanalyzed Condition Concerning The Containment Equipment Hatch Structure Modification Due To An Inadequate Design Basis Tornado Load Fabrication Analysis</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1993, at 1709 hours with Unit 1 defueled a four hour report was made to the NRC pursuant to 10CFR50.72 (b)(2)(i) because of the Steam Generator Replacement Project (SGRP) modifications to the Unit 1 containment equipment hatch work platform which did not include design basis tornado loads in the analysis. If the modification failed during tornado loads the existing equipment hatch platform could collapse and a portion of the missile protection outside the equipment hatch door which protects the emergency personnel escape hatch would be lost. This condition existed since March 1992 when the platform modifications were completed while Unit 1 was operating in Mode 1 at 100 percent power. This event is reportable pursuant to 10CFR50.73 (a)(2)(ii)(A). <br /><br /> The cause of the event was personnel error. An inadequate review of the original design calculations, by the contracted architect engineers, failed to identify that design basis tornado loads were required in the analysis for the equipment hatch platform modifications.<br /><br /> No significant safety consequences resulted from the event because the equipment hatch platform and modifications were not subjected to any tornado wind loads. Therefore, the health and safety of the public were not affected at any time during this event.
3381993008 | North Anna 1, North Anna 2 | 03/16/1993 | 04/09/1993 | 9304150023 | <strong>Missed Surveillance To Functionally Test The Reactor Coolant System Loop Stop Valve Position Limit Switch Inputs To The Solid State Protection System And Manual Safety Injection Switch Input To The Reactor Trip And Bypass Breakers Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, with Unit 1 in Mode 6, Refueling, and Unit 2 in Mode 1, 100 percent power, the continuing evaluation of Technical Specification surveillance requirements, being performed as a corrective action reported under LER 50-338/92-007-00, identified a missed surveillance. Functional testing of the Reactor Coolant System (RCS) loop stop valve did not verify the position limit switch inputs to the Solid State Protection System (SSPS). Upon further evaluation, it was also determined that the Safety Injection (SI) functional test did not verify that all four reactor trip and bypass breaker circuits receive a signal from each of the two manual SI switches. Technical Specification 4.0.3 was invoked permitting the required test within 24 hours on the manual SI switches for Unit 2. These conditions are prohibited by TS and are reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the missed surveillances is personnel error resulting in failure to develop adequate procedures to fully test component circuitry. <br /><br /> No significant safety consequences resulted from these conditions because the investigation of the loop stop valve condition on unit 2 proved the limit switch inputs are functional and performance of the Unit 1 functional test verified operability. Also, no credit is taken for the manual Engineered Safety Feature functional test of the SI input to the reactor trip breakers in the plant's safety analysis. Therefore, the health and safety of the public were not affected at any time during this event.
3381993009 | North Anna 1 | 03/20/1993 | 04/08/1993 | 9304120239 | <strong>Cold Leg Safety Injection Line Flow Below Technical Specification Requirements Due To Overly Restrictive Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1993, with Unit 1 in Mode 6 (Refueling), while performing the High Head Safety Injection (HHSI) flow balance test, it was determined that the "as-found" cold leg branch line flows were below the Technical Specification (TS) requirements. Technical Specification 4.5.2.h.1.a requires that the sum of the two lowest branch line flows, to be at least 384 gpm. Using the single most limiting HHSI pump, the sum of the two lowest existing branch flows was 381 gpm. This event is a condition prohibited by the plant Technical Specifications and is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of this event is a TS allowable flow rate that is too narrow to be consistently met with instrumentation uncertainties associated with the ultrasonic flow measurement that must be used during surveillance testing. The TS value of 384 gpm is conservative with respect to existing safety analysis values. <br /><br /> When the flows were discovered to be less than the TS required values, the Safety injection cold leg throttle valves were adjusted such that the "as-left" two lowest flow branch lines equaled 396 gpm. <br /><br /> No significant safety consequences resulted from this event because the safety analysis requires a minimum flow rate of 359 gpm. Thus, Peak Clad Temperature would have remained well within the 2200 degrees F limit of 10CFR50.46 during the postulated limiting small break loss of coolant accident. Therefore, the health and safety of the public was not affected at any time during this event.
3381993010 | North Anna 1 | 03/23/1993 | 04/07/1993 | 9304130155 | <strong>Engineered Safety Feature Actuation During Reactor Protection And Engineered Safety Feature Response Time Testing Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1993, at 1032 hours with Unit 1 in Mode 5, cold shutdown, the Unit 1 'A' Service Water Pump (1-SW-P-1A) started unexpectedly during performance of Unit 1 Reactor Protection and Engineered Safety Feature (ESF) Train A Slave Relay Time Response Testing. Since the 1-SW-P-1A is part of the ESF system and starting this component was not preplanned, this event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as an automatic actuation of an ESF component. The SW pump was promptly secured and returned to normal standby status. A four hour report was made to the NRC pursuant to 10CFR50.72(b)(2)(ii). <br /><br /> The cause of the event was inadequate procedure. The periodic test (PT) diagram did not identify all cables and wires as they appear in the SSPS output cabinet. During the performance of the time response testing an electrical lead, not listed in the PT, had not been properly lifted to defeat the automatic start of 1-SW-P-1A. This resulted in the pump starting when the slave relay was energized during testing. <br /><br /> No significant safety consequences resulted from the event because the pump started as designed when the ESF slave relay was energized. Therefore, the health and safety of the public were not affected at any time during this event.
3381993011 | North Anna 1 | 04/03/1993 | 04/21/1993 | 9304270246 | <strong>Engineered Safety Feature Actuation Of Reactor Trip And Bypass Breakers Opening During Solid State Protection Testing Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1993, at 2107 hours with Unit 1 in Mode 5, cold shutdown, the Unit 1 "B" Reactor Trip and "A" Bypass breakers opened after receiving an automatic reactor trip signal when the "A" Steam Generator (SG) level reached its setpoint limit of 18 percent on two of three channels. The automatic reactor trip signal was an expected actuation for the SG draining evolution in progress. The opening of the breakers was not expected since they were believed to have been defeated during performance of the Train "A" Reactor Protection (RPS) and Engineered Safety Feature (ESF) Logic Channel functional test which was occurring simultaneously. The breakers are part of the ESF system and tripping them was not preplanned. As such, the event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as an automatic actuation of an ESF component. A four hour report was made to the NRC pursuant to 10CFR50.72 (b)(2)(ii). <br /><br /> The cause of the event was personnel error. Communication of actions necessary to prevent the "B" Reactor Trip and "A" Bypass breakers from opening prior to receiving the reactor trip signal was untimely. <br /><br /> No significant safety consequences resulted from the event because the rod control system was removed from service prior to receiving the trip signal and the actuation was of no safety significance. Therefore, the health and safety of the public were not affected at any time during this event.
3381993012 | North Anna 1 | 04/08/1993 | 04/27/1993 | 9305100096 | <strong>Engineered Safety Feature Actuation Where The Main Steam Trip Valves Closed On The Generation Of A Main Steam Line Isolation Signal Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993, at 0257 hours with Unit 1 in Mode 4, hot shutdown, a main steam line isolation signal was generated, causing the main steam trip valves to close, as a result of simultaneously blowing down two steam flow transmitter sensing lines. Flow transmitter sensing line blow down is performed to remove any condensation and/or non-condensable gas. The blowdown evolution resulted in a high steam flow signal on one of two protection channels on two of three main steam lines coincident with low low reactor coolant system average temperature or low steam line pressure which initiated the main steam trip valve isolation signal. A four hour report was made to the NRC pursuant to 10CFR50.72 (b) (2) (ii). This event is reportable pursuant to 10CFR50.73 (a) (2) (iv) as an automatic actuation of an Engineered Safety Feature (ESF) component. <br /><br /> The cause of the event was personnel error due to communications and self check inadequacies. Upon receiving the notification to blow down the sensing lines a second time adequate self check techniques were not employed to ensure only one transmitter sensing line was worked at a time. <br /><br /> No significant safety consequences resulted from the event because all components functioned as required for the ESF actuation. In addition, there was no actual transient in progress. Therefore, the health and safety of the public were not affected at any time during this event.
3381993013 | North Anna 1, North Anna 2 | 04/14/1993 | 04/27/1993 | 9305100085 | <strong>Missed Surveillance To Functionally Test Entire Circuitry For Manual Phase "A" Isolation Switches And Safety Injection Interlock For "H" & "J" Bus Undervoltage Protection Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1993, at 0930 hours with Unit 1 in Mode 1, 50 percent power, and Unit 2 in Mode 1, 100 percent power, the continuing evaluation of Technical Specification (TS) surveillance requirements, being performed as a corrective action reported under LER 50-338/92-007-00, identified additional missed surveillances. Portions of two manual Phase "A" isolation switch circuitry were not functionally tested as required by TS. The action of TS 4.0.3 was entered for both units to allow testing within 24 hours. Testing was completed and the actions were cleared at 1712 hours for Unit 1 and 1703 hours for Unit 2. It was also determined, on April 15, 1993, that a portion of the safety injection interlock to the "H" and "J" Bus undervoltage protection circuitry was not being functionally tested as required by TS. The action of TS 4.0.3 was entered at 0800 hours and testing was completed with the actions cleared at 1345 hours for Unit 1 and 1405 hours for Unit 2. These conditions are prohibited by TS and are reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event was personnel error resulting in failure to develop adequate procedures to test the entire component circuitry. <br /><br /> No significant safety consequences resulted from these conditions because subsequent testing determined the affected circuitry was capable of performing the required functions. Therefore, the health and safety of the public were not affected at any time during this event.
3381993014 | North Anna 1 | 04/11/1993 | 05/06/1993 | 9305140256 | <strong>Entry Into Mode 3 With The Steam Driven Auxiliary Feedwater Pump Inoperable Due To An Incorrect Speed Control Setting Following Annual Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1993, at 0130 hours with Unit 1 in Mode 1, 30 percent power, the as found speed setting of the steam driven auxiliary feedwater (AFW) pump, 1-FW-P-2, was discovered to be below its required limit during pump operability testing. As part of the normal start-up sequence a flow test was performed to demonstrate AFW System operability prior to entering Mode 3. Operability testing of 1-FW-P-2 cannot be performed until sufficient steam pressure is available. Therefore, TS 4.0.4 is not applicable to 1-FW-P-2. in addition, after entering Mode 3 on April 8, 1993 and before the incorrect speed setting of 1-FW-P-2 was discovered, the 1H Emergency Diesel Generator (EDG) was removed from service for periodic testing. This condition rendered the emergency power source for the "A" motor driven AFW pump temporarily inoperable. The EDG was returned to service within the time required by Technical Specifications. Inoperability of 1-FW-P-2 is prohibited by TS 3.7.1.2 since TS 3.0.4 is applicable and is reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event was personnel error as a result of failing to follow procedure. Self check of procedural step evolution's was inadequate.<br /><br /> No significant safety consequences resulted from the event because 1-FW-P-2 was tested and restored to operable status within the 72 hour action statement of entry into Mode 3. Therefore, the health and safety of the public were not affected at any time during this event.
3381993015 | North Anna 1, North Anna 2 | 04/27/1993 | 05/07/1993 | 9305140186 | <strong>Missed Surveillance On Portions Of The Containment Pressure High High Protection Channel Circuitry Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1993, at 0931 hours with Unit 1 in Mode 1, 100 percent power, and Unit 2 in Mode 5, Cold Shutdown, the continuing evaluation of Technical Specification (TS) surveillance requirements, being performed as a corrective action reported under LER 50-338/92-007-00, identified an additional missed surveillance. Specifically, portions of the containment pressure channels that input to Containment Spray-High High Pressure were not being tested during the monthly channel functional test. A review of the Type "A" test, performed on March 31, 1993 for Unit 1, indicated that the pressure channels functioned as designed. Therefore, additional testing was not required. Unit 2 testing was satisfactorily completed at 0950 hours on April 27, 1993. This condition is prohibited by Technical Specifications 4.3.2.1.1 Table 4.3-2 and is reportable pursuant to 10CFR50.73(a) (2) (i) (B).<br /><br /> The cause of the event was personnel error resulting in failure to develop adequate procedures to test the entire component circuitry during initial TS implementation.<br /><br /> No significant safety consequences resulted from these conditions because subsequent testing determined the affected circuitry was capable of performing the required functions. Therefore, the health and safety of the public were not affected at any time during this event.
3381993016 | North Anna 1, North Anna 2 | 05/09/1993 | 05/27/1993 | 9306080014 | <strong>Containment Hydrogen Analyzer Inoperable For Greater Than 30 Days Due To A Disconnected Pressure Switch Sensing Line As A Result Of Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1993, with Units 1 and 2 in Mode 1, 100 percent power it was discovered that a containment hydrogen analyzer pressure switch (PS-3) sensing line was disconnected in the local panel. with the sensing line disconnected the flow through the analyzer would be altered in a manner that would invalidate the sample analysis. This condition would render the analyzer inoperable. The TS action for an inoperable analyzer was entered at 0700 hours on May 9, 1993. Subsequently, the pressure switch was calibrated and the sensing line was reconnected. The Technical Specification action was cleared at 1430 hours on May 9, 1993. An investigation could not determine the exact cause for the disconnected sensing line but it is believed to have occurred following the last calibration in February 1993. As such, the allowed 30 day outage time for one of the shared analyzers required by TS 3.6.4.1.a was exceeded. Further review identified the Unit 2 containment hydrogen analyzer was removed from service for calibration in March 1993. However, the Unit 2 analyzer was returned to service prior to the 7 day limit of TS 3.6.4.1.b for two inoperable analyzers. The condition is prohibited by TS and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> The cause of the event is personnel error resulting in an inoperable analyzer. <br /><br /> This event posed no significant safety implications since alternative means were available to sample containment hydrogen levels throughout the event. Therefore, the health and safety of the public were not affected at any time.
3381993017 | North Anna 1, North Anna 2 | 06/16/1993 | 07/08/1993 | 9307160166 | <strong>Containment Hydrogen Analyzer Heat Trace Channel Calibration Not Performed On A Staggered Test Basis As Required By Technical Specifications Due To Inadequate Implementation Of Technical Specification Amendment</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1993, with Units 1 and 2 in Mode 1, 100 percent power, the continuing evaluation of Technical Specification (TS) surveillance requirements, being performed as a corrective action reported under LER 50-338/92-007-00, identified that the containment hydrogen analyzer channel heat tracing calibration was not scheduled and performed in accordance with TS 4.6.4.1. The TS 92 day Staggered Test Basis requires that one train of heat trace be tested at least every 46 days in an alternating fashion. However, the periodic test procedure was not being performed on a Staggered Test Basis. The condition is prohibited by TS and is reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event is inadequate implementation of TS Amendment No. 64 and No. 49 associated with the Three Mile Island (TMI) action item concerning Containment Hydrogen Monitor. <br /><br /> This event posed no significant safety implications because the periodic tests verified operability of both trains of heat tracing. The previous scheduling frequency of every 92 days had minimal safety implications. Therefore, the health and safety of the public were not affected at any time.
3381993018 | North Anna 1 | 10/16/1993 | 10/26/1993 | 9311030344 | <strong>Missed Surveillance on the Performance of the Calorimetric Heat Balance</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1993, with unit 1 at 100% power (Mode 1), a missed surveillance was identified at 1841 hours because the daily calorimetric periodic test had not been performed within 24 hours + 25% surveillance extension in accordance with Technical Specification (TS) 3.3.1.1, Table 4.3-1. Upon discovery of the event, the action of TS 4.0.3 was entered, and a calorimetric periodic test was satisfactorily performed at 1843 hours. The event is reportable pursuant to 10 CFR 50.73 (a) (2) (i) (B) as a condition prohibited by TS 3.3.1.1. <br /><br /> The cause of the event was personnel error due to inattention to detail. <br /><br /> No significant safety consequences evolved as a result of this event because the power range NI did not require adjustments as a result of the calorimetric periodic test performed at 1843 hours. Therefore, the health and safety of the public were not affected during the event.
3391993001 | North Anna 2 | 03/22/1993 | 04/13/1993 | 9304190255 | <strong>Inoperable power range nuclear instrument due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On March 22,1993, with Unit 2 at 100 percent power (Mode 1) it was identified that a condition outside the actions of Technical Specification (TS) 3.3.1.1, Table 3.3-1 Action 2(a) existed in that a power range nuclear instrument channel was inoperable for greater than one hour without being placed in trip. The channel calibration tests had been completed on power range NI channels N 41 and N 42 and returned to service. While returning power range NI channel N 43 to service following the calibration test it was noted that the delta flux indication for power range NI channel N 42 was not in agreement with the other three power range NI channels. Further evaluation determined that the detector input signal cables for power range NI channel N 42 which are disconnected from the upper and lower power range NI drawers during the calibration test had been inadvertently reversed and reconnected to the wrong drawers. This event is reportable pursuant to 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the event was personnel error due to an inadequate self check and inadequate independent verification. <br /><br /> No significant safety consequences resulted from this event because the minimum number of operable power range NI channels required by TS 3.3.1.1, Table 3.3-1 was maintained. Therefore, the health and safety of the public was not affected at any time during this event.
3391993002 | North Anna 2 | 04/16/1993 | 08/12/1993 | 9308190098 | <strong>Automatic Reactor Trip Initiated From A Turbine Trip Due To An Over Excitation Of The Main Generator</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1993, at 0717 hours with Unit 2 in Mode 1, 100 percent power, an automatic reactor trip occurred as a result of a turbine trip. Emergency procedures were entered and immediate actions were performed. Subsequently, the operating crew became concerned with the reactor coolant system (RCS) cooldown when temperature decreased to approximately 540 degrees F. To reduce the Steam Generator feedwater addition rate and stabilize the RCS temperature the ATWS Mitigation System Actuation Circuitry was reset and the Auxiliary Feed Water (AFW) pumps were secured before steam generator levels were restored above the automatic start setpoint. Defeating the automatic start capability of the AFW pumps is prohibited by Technical Specifications. A 4 hour report was made to the NRC at 1055 hours pursuant to 10CFR50.72 (b)(2)(ii) & (iii)(A). The event is reportable as an Engineered Safety Feature System actuation pursuant to 10CFR50.73 (a)(2)(iv) & (v). <br /><br /> The cause of the turbine trip/reactor trip was a malfunction in the main generator voltage regulator circuitry. The cause of defeating the AFW system during the event was a result of personnel error.<br /><br /> No significant safety consequences resulted from the reactor trip because reactor protection safety systems responded as designed. Disabling the AFW pumps did not present a significant safety consequence because the heat sink was maintained throughout the event. Therefore, the health and safety of the public were not affected at any time during this event.
3391993003 | North Anna 2 | 04/24/1993 | 05/12/1993 | 9305180359 | <strong>Manual Reactor Trip Initiated Due To Excessive Main Feedwater Regulating Valve Oscillations</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1993, at 0530 hours with Unit 2 in Mode 1, 71 percent power, a manual reactor trip was initiated due to erratic feedwater flow indications to the "C" Steam Generator, abnormally high vibration alarms for the "B" Reactor Coolant Pump, and suspected water and steam leakage from the "C" Main Feedwater line. Emergency procedures were entered and immediate actions were performed. All Engineered Safety Feature system equipment responded as designed. At 0602 hours an "Alert" was declared, based on Shift Supervisor judgment, in accordance with Emergency Plan Implementing Procedures and the required notifications were made. A 1 hour report was made to the NRC at 0620 hours pursuant to 10CFR50.72 (a) (ii) (3). At 0816 hours with the unit in a stable condition the "Alert" classification was down graded to a Notification Of Unusual Event (NOUE). The NOUE was terminated at 1045 hours on April 24, 1993. The event is reportable pursuant to 50.73 (a) (2) (iv). <br /><br /> The cause of the event has been attributed to the inherent instabilities with the design of the main feedwater regulating valve and positioner controls. <br /><br /> No significant safety consequences resulted from the main feedwater concerns because auxiliary feedwater was available and provided cooling to the steam generators throughout the event. Therefore, the health and safety of the public were not affected at any time during this event.
3391993004 | North Anna 2 | 09/02/1993 | 09/28/1993 | 9310040283 | <strong>Inoperable Reactor Coolant Pump Trip Circuit Due to a Potential Single Failure</strong><br /><i>Abstract:&nbsp;</i>At 1410 hours on September 2, 1993, with Unit 2 in Mode 1 at 71% power, it was determined that two out of three cables for the Reactor Coolant Pump (RCP) bus Underfrequency (UF) Reactor Trip channels were located on the same neutral cable tray along with other neutral cables. A single failure on the neutral cable tray could have disabled both channels and defeated a valid RCP bus UF Reactor Trip Signal because the UF sensors are designed in an energize to actuate configuration. One channel was declared inoperable and placed in trip per Technical Specification (TS) 3.3.1.1 Table 3.3-1. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(v)(A) for an event or condition that alone could have prevented fulfillment of a system needed to shut down the reactor. A four-hour report was made to the NRC at 1530 hours on September 2, 1993 in accordance with 10 CFR 50.72 (b)(2)(iii)(A). <br /><br /> The cause of the event was inadequate initial plant design. <br /><br /> No significant safety consequences evolved as a result of this event because the minimum number of operable channels per TS 3.3.1.1 Table 3.3-1 were maintained. The health and safety of the public were not affected at any time during the event.
3391993005 | North Anna 2 | 09/09/1993 | 10/04/1993 | 9310080128 | <strong>Emergency Diesel Generator Load Sequencing Timers Outside Setpoint Tolerance</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1993 at 1340 hours, with Unit 2 in cold shutdown (Mode 5), during Emergency Diesel Generator (EDG) load sequencing timer testing, the "3A" Auxiliary Feedwater Pump timer was found outside its setpoint tolerance as specified in Technical Specification (TS) Table 4.8-1. The timer was reset and successfully re-tested. On September 20, 1993 at 1125 hours, with Unit 2 in Refueling (Mode 6), during EDG load sequencing timer testing, a timer associated with a Control Rod Drive Mechanism (CRDM) cooling fan was found outside of its setpoint tolerance listed in TS Table 4.8-1. The timer was reset and successfully re-tested. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) for a condition prohibited by the Technical Specifications. <br /><br /> The cause of the event was setpoint drift of the Agastat 2400/7000 series timer relays.<br /><br /> Engineering performed an evaluation to determine the impact of the timer setpoint drift. The evaluation determined that there would be no impact on the operation of the EDG load sequencing scheme. Therefore, the health and safety of the public were not affected at any time.
3391993006 | North Anna 2 | 09/21/1993 | 10/19/1993 | 9310270059 | <strong>Steam Generator Tube Defects</strong><br /><i>Abstract:&nbsp;</i>During the 1993 Unit 2 refueling outage, Steam Generator (S/G) tube inspections were performed using the standard eddy current bobbin probe and rotating pancake coil probe. The results of the tests showed that greater than one percent of the tubes in service in each of the three S/Gs had pluggable indications. Per Technical Specification (TS) 4.4.5.2, "C" S/G was classified as C-3 at 0930 hours on September 21, 1993, "A" S/G was classified C-3 at 1015 hours on September 22, 1993, and "B" S/G was classified C-3 at 1310 hours on September 25, 1993. All tubes with pluggable indications were taken out of service. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (v) (c). Four-hour reports were made to the NRC in accordance with 10 CFR 50.72 (b) (2) (i) and TS 4.4.5.C at 1135 hours on September 21, 1993, for "C" S/G, at 1107 hours on September 22, 1993, for "A" S/G and at 1334 hours on September 25, 1993, for "B" S/G. <br /><br /> The primary cause of the tube degradation is believed to be primary water stress corrosion cracking and stress corrosion cracking originating in the outside diameter of the tube. <br /><br /> No significant safety consequences evolved as a result of the event because the number of tubes plugged in each S/G is below the Safety Analysis tube plugging limit. Therefore, the health and safety of the public were not affected as a result of the event.
3391993007 | North Anna 2 | 10/14/1993 | 04/25/1994 | 9405030273 | <strong>High Head Safety Injection Flow Below Technical Specification Minimum</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1993, with Unit 2 in Mode 5 (Cold Shutdown), during High Head Safety Injection (HHSI) flow balance testing, the 'as-found' cold leg branch line flow was found to be below the Technical Specifications (TS) minimum requirement. The sum of the branch line flows, excluding the highest flow rate, is required by TS 4.5.2.h to be greater than or equal to 359 gpm. However, the sum of the two lowest measured branch flow rates was found at 356 gpm. The cold leg Safety Injection throttle valves were adjusted so that sum of the two lowest flow rates was equal to 384 gpm.<br /><br /> On November 8, 1993, concerns were identified about the flow balancing data due to instrument inaccuracies. All three charging pumps were twice declared inoperable, and TS 3.0.3 was entered. At 1402 hours on November 9, 1993, seal injection flow was decreased to allow two charging pumps to meet the requirement of the TS, and TS 3.0.3 was exited. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications.<br /><br /> The primary suspected cause of the event is previously unaccounted for uncertainties in the Unit 2 HHSI flow balance measurements due to adverse system piping geometry's.<br /><br /> No significant safety consequences evolved as a result of this event because a previous analysis has shown that the existing HHSI branch flows are within the design basis limbs. Therefore, the health and safety of the public were not affected.
3411993001 | Fermi 2 | 01/04/1993 | 02/03/1993 | 9302110200 | <strong>HPCI Inoperable Due To Failed Relay</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1993 at 1711 hours, annunciator 2D60, "High Pressure Coolant Injection (HPCI) Turbine Exhaust/Exhaust Drain Valve Not Fully Open" annunciated. There was no HPCI related surveillance or work in progress. Operators followed the applicable sections of the Alarm Response Procedure (ARP). All HPCI valves were verified to be in their proper position. Technical assistance was obtained to fully investigate this alarm and determine the implications on HPCI operability. <br /><br /> The investigation showed that the coil of E4100M092, "HPCI Turbine Exhaust Valve Open Relay," was deenergized. This differed from the normal logic configuration. The logic which feeds this coil was found to be energized with the coil deenergized. With this relay deenergized, the HPCI Steam Admission Valve (E41-F001) is prevented from opening electrically by either an automatic or manual demand. Failure of this relay would have prohibited the HPCI system from operating on a valid demand signal. Based on the failure of this relay, the system was declared inoperable at 1911 hours, January 4, 1993. Relay E4100M092 was replaced, post maintenance testing was successfully completed and the HPCI system restored to operability at 0320 hours, January 5, 1993.<br /><br /> The root cause of the event was attributed to component failure based on failure analysis. A contributing cause was the omission of this relay from the Agastat Preventative Maintenance (PM) program, which would have ensured that the relay was replaced prior to failure. Corrective actions included placing relay E4100M092 in the PM program for continuously energized Agastat relays, generating a PM event to change out the relay and performing a review of all safety related Agastat relays to ensure that all energized relays are properly identified in the PM program.
3411993002 | Fermi 2 | 01/14/1993 | 02/15/1993 | 9302220181 | <strong>HPCI Failure to Start</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1993 at 1351 hours, the High Pressure Coolant Injection System (HPCI) failed to start on a simulated auto injection signal during the performance of surveillance 24.202.01, "HPCI Pump Time Response and Operability Test at 1025 psi". The surveillance was suspended. Because surveillance 24.202.01 requires HPCI injection valve E41F006 to be deenergized in the closed position the Technical Specification Limiting Condition for Operation (LCO) had already been entered at 1313 hours with the HPCI system declared inoperable. <br /><br /> HPCI failed to start due to a loss of supply voltage to the governor control system. This was caused by a failed voltage dropping resistor (E41K204). The resistor drops voltage from the 130 VDC bus to 48 VDC. The failed resistor was replaced with an identical resistor. The surveillance was performed satisfactorily, HPCI was declared operable, and the LCO was cleared at 0230 hours on January 15, 1993.
3411993003 | Fermi 2 | 01/19/1993 | 02/18/1993 | 9302230139 | <strong>Technical Specification Required Recorder Discovered Not To Be Qualified</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1993, while performing modifications on the plant simulator, technicians encountered problems during the installation of pressure recorder T50-R802B, "Division 2 Drywell and Torus Pressure." The technicians determined that the recorder did not meet the purchase order description for simulator application. Subsequent investigation found that the recorder intended for the simulator had been installed in the main control room. Installation of the simulator recorder in the main control room occurred on September 25, 1992 during the third refuel outage. <br /><br /> An engineering analysis concluded that although the simulator recorder installed in the main control room met most of the specifications for this application, it could not be seismically qualified through analytical methods. Thus, on January 19, 1993, it was concluded that the recorder could not be considered OPERABLE per Technical Specification section 3.3.7.5 when the plant entered MODE 2 (Startup) following the third refuel outage on November 4, 1992. <br /><br /> The simulator recorder installed in the main control room was replaced with the proper recorder on January 7, 1993. An investigation concluded that the cause of this event was a procedural deficiency. Inattention to detail by those involved was cited as a contributing factor. Procedure changes will be implemented. Lessons learned will be discussed in Technical Staff and Managers Training and in training sessions for those directly involved.
3411993004 | Fermi 2 | 02/19/1993 | 03/19/1993 | 9303220272 | <strong>Automatic Reactor Shutdown on Turbine Trip Due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1993, Circulating Water Pump number 3 was removed from service for performance of Preventive Maintenance PM!. Electrical Maintenance personnel were to perform procedure 35.318.017, "Inspection and Testing of Multi-Contact Auxiliary Relays". An electrician located and connected his test equipment to the incorrect relay which resulted in the loss of 4160 VAC bus 69J. Circulating Water Pumps number 1 tripped and 2 de-energized, and their discharge valves de-energized in the open position. Circulating Water Pumps 4 and 5 continued to operate. However, their discharge was partially re-directed through Circulating Water Pumps 1 and 2 in the opposite direction. Because of inadequate cooling water, Condenser pressure began to increase. The Main Turbine tripped on high Condenser pressure. At 2102 hours, an automatic Reactor Protection System shutdown was initiated by the Main Turbine control valve fast closure trip signal. The Reactor shutdown and all safety systems responded properly. <br /><br /> The root cause of this event was determined to be personnel error. The electrician did not verify that he was on the proper relay before connecting and energizing his test equipment. The General Supervisor of electrical maintenance discussed the importance of self checking and verification with electrical maintenance personnel. An accountability meeting was held. Training for electricians on self checking and trip relays will be reviewed.
3411993005 | Fermi 2 | 02/25/1993 | 03/29/1993 | 9304020138 | <strong>ESF Actuation Due to Failed Indicating Lamp</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1993, a Shift Technical Advisor (STA) replaced a burned-out indicating lamp for a 130 VDC power circuit (circuit #31) on a local panel in the relay room. As he was screwing the replacement lamp into the socket, the lamp shattered as it contacted the socket base. A short in the new lamp caused a fault that blew the upstream feeder positive and negative circuit fuses resulting in a loss of power to seven 130 VDC branch circuits, specifically causing closure of the Primary Containment Pneumatic Supply Outboard Isolation Valve T49-F468. All affected systems responded to the loss of power as designed. Division II Emergency Equipment Cooling Water System was declared inoperable. The fuses were replaced, the circuits were re-energized and all systems were restored in approximately 1 hour and 24 minutes. <br /><br /> During subsequent investigation, an engineering review of the circuit design indicated that the fuse in circuit #31 was inappropriately selected for fuse coordination at high fault current. A faster acting fuse would have prevented opening of the upstream feeder circuit fuses and would have prevented valve T49-F468 from closing. <br /><br /> Plant personnel will be cautioned on the replacement of control power indicating lamps. Also, the design of safety related control power distribution circuits will be reviewed for proper fuse coordination.
3411993006 | Fermi 2 | 03/04/1993 | 04/05/1993 | 9304080235 | <strong>Inoperable EPAS Due To Missed Channel Functional Test Required Per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1993, it was determined that test procedures used to perform channel functional tests of Reactor Protection System (RPS), Electrical Protection Assemblies (EPAs) were incorrect. The procedure failed to trip the EPA breakers as required by Technical Specification surveillance requirements. Because the EPAs had not been properly tested as required by Technical Specification 4.8.4.4 all eight EPAs (A,B,C,D,E,F,G,H) were declared inoperable. <br /><br /> Technical Specification 4.0.3 permits 24 hours to complete the surveillance requirements of section 4.8.4.4 before implementing the action requirements of section 3.0.3. The EPAs were successfully tested and declared operable within 6 hours. <br /><br /> Investigation showed that channel functional tests and channel calibrations of the undervoltage, overvoltage and underfrequency EPA trip functions did not actually trip the EPA breaker. The defective procedures were 42.610.02 and 42.610.04, Division I and II RPS, EPA Calibration/Functional Testing, respectively. <br /><br /> The cause of this event was attributed to a defective procedure. A review of other electrical surveillances was conducted and verified that no other similar problems existed. The affected procedures will be revised to include steps necessary to satisfy channel functional test requirements per Technical Specification requirements.
3411993007 | Fermi 2 | 04/20/1993 | 05/20/1993 | 9305270022 | <strong>Reactor Trip on Intermediate Range Monitor Upscale During Reactor Pressure and Feedwater Transient.</strong><br /><i>Abstract:&nbsp;</i>April 20, 1993, with the reactor at 510 psig during startup, a control room operator noticed that the main steam manifold pressure control system was unexpectedly switching between the "A" and "B" regulators when the Electric Governor Trouble Alarm actuated and the turbine bypass valves opened approximately 40 percent. Reactor pressure began to decrease and reactor water level increased due to increased void fraction resulting from the increased steam flow. The increased void fraction also led to a decrease in reactor power. When control room operators began to gradually close the bypass valves, reactor water level decreased. As water level decreased through the normal operating band, feedwater flow automatically increased. The addition of cold feedwater caused reactor power to increase until the reactor automatically tripped on Intermediate Range Monitor upscale. All safety systems responded properly. <br /><br /> This event occurred because leakage past a threaded adapter allowed steam and water to leak into an instrument cabinet which contained the pressure transmitters used to control main steam manifold pressure, causing failure of these transmitters. The cause of the event was personnel error in that a threaded adapter used to install temporary test equipment for startup monitoring did not match the fitting into which it was threaded. Training will be conducted on this event to reinforce the need for control of contractor activities.
3411993008 | Fermi 2 | 05/19/1993 | 06/18/1993 | 9306240284 | <strong>Technical Specification Instrument Powered from Improper Electrical Outlet</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1993, while conducting a walkdown of the installation of Engineering Design Package (EDP) 11264, it was discovered that recorder T50-R802A, "Division 1 Drywell and Torus Pressure" was powered from a utility service outlet. On May 19, 1993 it was determined that this 120 VAC utility service outlet would deenergize on a loss of off-site power signal and is not designed to automatically re-energize following Emergency Diesel Generator Loading. Investigation concluded that the recorder had been powered from the improper source since startup from the third refuel outage. <br /><br /> Recorder T50-R802A could not be considered OPERABLE as required by Technical Specification section 3.3.7.5 from the time the plant entered MODE 2 (Startup) November 4, 1992 until May 19, 1993. During this time period the Division 2 recorder was INOPERABLE from November 4, 1992 until January 7, on April 19, 1993, and again from May 11 through May 16, 1993. <br /><br /> The cause of the event was attributed to personnel error associated with implementation of the EDP. Recorder T50-R802A was subsequently plugged into the proper outlet. Labelling of utility service outlets in the main control room has been completed. Lessons learned will be incorporated into training programs and plant procedures..
3411993009 | Fermi 2 | 07/26/1993 | 08/25/1993 | 9308310133 | <strong>Emergency Equipment Cooling Water Start During Service Water Temperature Transient.</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1993 at approximately 1015, control room operators noticed increasing temperatures for heat loads cooled by General Service Water (GSW). Because drywell pressure was increasing due to increasing temperature, drywell venting was initiated. Emergency Equipment Cooling Water/Emergency Equipment Service Water (EECW/EESW) was manually started to supplement Reactor Building Closed Cooling Water (RBCCW), primarily for drywell cooling. The cooling provided by the EECW system reversed the drywell pressure increase. At 1032 as drywell pressure continued to decrease, drywell venting was terminated and a drywell to suppression chamber vacuum breaker opened briefly as expected. <br /><br /> At 1050 a valve connecting the circulating water (CW) pond with the GSW intake was found open, diverting 95 degree water from the CW pond to the GSW system. This had caused the temperature increase in the GSW system. <br /><br /> At 1052 the valve was reclosed, and by 1100 plant temperatures were returning to normal. The EECW/EESW subsystems were shutdown and returned to standby by 1253. <br /><br /> The valve opened when a painter, thinking that the control switch was an enclosed 120V electrical outlet, pushed the open lever to "open the enclosure". The switch for this valve is mounted on an I-beam near the wall and had no identification label. The switch is now labelled, and the valve is now deenergized to prevent unintentional operation.
3411993010 | Fermi 2 | 08/13/1993 | 09/13/1993 | 9309170264 | <strong>Reactor Automatic Shutdown Following a False High Water Level Trip of the Main Turbine Generator</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1993, while performing routine reactor building rounds, a Nuclear Power Plant Operator (NPPO) removed some tape from the valve handle on a manifold to instrument B21-R004B "Reactor Vessel Division 2 Pressure Indicator". While removing the tape residue, the NPPO noticed a pressure spike on instrument B21-R004B and heard the scram pilot valves vent. He called the main control room and was informed that an automatic reactor shutdown had occurred. <br /><br /> An investigation determined the cause of the event to be personnel error. The NPPO inadvertently unseated an instrument calibration/vent isolation valve while removing the tape residue from the valve handle. This induced a pressure transient into an instrument header shared by other instruments. A false high reactor water level signal caused the main turbine generator to trip off. Closure of the main turbine generator control valves initiated a reactor scram. <br /><br /> A lessons learned meeting was conducted. Signs have been posted on instrument racks H21-P004/P005 warning of the sensitivity of these instruments. Lessons learned will be incorporated into the licensed and non-licensed operator training program.
3411993011 | Fermi 2 | 08/24/1993 | 09/23/1993 | 9309280268 | <strong>Inadvertent Isolation of B31-F016A Due to Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1993 prior to a planned transfer of power from Reactor Protection System (RPS) "B" Bus to its alternate power supply, two jumpers were installed in relay room panel H11-P623 per a system operating procedure. These jumpers were installed to prevent the closure of the B31-F016A and B, Outboard Reactor Recirculation Seal Purge Valves. At 0251 hours, after the transfer of power, a Nuclear Supervising Operator (NSO) noticed a loss of position indication for B31-F016A. The valve was verified closed by local observation. <br /><br /> It was determined that B31-F016A went closed due to a blown fuse in the control logic which contained the jumpers. The fuse was replaced, B31-F016A was opened and seal purge flow to the reactor recirculation pump was restored. The most probable cause of the fuse blowing is grounding of the B31-F016A jumper when it became disconnected during the verification process. The root cause of this event was a design deficiency which did not allow secure installation of jumpers. Corrective actions included the installation of star lugs on all jumper locations for this evolution to allow for more positive connection to the terminal strip.
3411993012 | Fermi 2 | 09/06/1993 | 10/06/1993 | 9310180097 | <strong>High Pressure Coolant Injection System Suction Swap from the Condensate Storage Tank to the Torus.</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1993 preparations were being made to pump down the suppression pool using torus water management system (TWMS). The suppression pool level had increased due to identified leakage. At 0929 hours, the "HPCI Suction Transfer Torus Level High" alarm was received and High Pressure Coolant Injection (HPCI) suction re-aligned from the condensate storage tank (CST) to the suppression pool. The HPCI suction transferred when instrument E41N662B tripped at a setpoint of +2 inches of torus level. <br /><br /> Discrepancies between E41 (HPCI) & G51 (TWMS) instruments were the root cause of the HPCI suction transfer. Control Room torus level indications were +0.8 inches on TWMS indicator G51R402, which is the only narrow range indication in the control room, and +1.8 inches on the E41 (HPCI) instrumentation on the Emergency Response Information System (ERIS) computer for the average of suppression pool level indicators E41N662B and D. The ERIS indication was +2.1 inches on E41N662B and +1.6 inches on E41N662D for the individual channels. <br /><br /> A calibration was performed on the TWMS instrumentation (G51N402 and G51R402). A work request was written to calibrate the HPCI instrument loop (E41N062 and E41N662 B and D). This calibration will be performed during RF04.
3411993013 | Fermi 2 | 09/17/1993 | 10/18/1993 | 9310220179 | <strong>Manual Reactor Scram due to Maintenance Breach of Reactor Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1993 an inadvertent breach of the Reactor Feedwater System occurred during a planned reactor shutdown with the reactor at 17% power. Maintenance personnel had begun work on the No. 5 North Feedwater Heater Level Control valve, N22-F415A, located on the discharge side of the heater drain pump prior to the establishment of the proper plant conditions. As a result, control room operators manually scrammed the reactor in order to shut down the feedwater system and isolate the system leak. All plant systems performed as expected and all leakage was contained within the plant. <br /><br /> The cause of the event was personnel error in failing to follow established work control practices. Poor communications, weaknesses in the implementation of the Work Control Process, and modification to the planned schedule of work contributed to this event. Corrective actions will include discipline administered in accordance with plant policy, counseling of those involved and training of appropriate plant personnel.
3411993014 | Fermi 2 | 12/25/1993 | 04/25/1994 | 9404290114 | <strong>Automatic Reactor Shutdown Following Failure of the Main Turbine</strong><br /><i>Abstract:&nbsp;</i>On December 25, 1993 at 1315 hours an automatic reactor shutdown occurred when the main turbine tripped off line. The turbine generator tripped when the mechanical overspeed device was activated. This was due to high vibration levels and was not due to an actual overspeed condition. The turbine generator unit and associated support systems sustained significant damage. All safety systems and isolations performed as designed during the event. An Unusual Event was declared at 1352 hours. This was upgraded to an Alert at 1357 hours. A fire at the main generator brush rig area was extinguished by the plant fire brigade using hand held extinguishers. <br /><br /> The cause of the high turbine vibration was due to the failure of the number 9 blade, on the 8th stage, turbine end of the low pressure section number 3. The root cause of this failure continues to be under investigation. <br /><br /> Turbine/generator repairs will be determined based on the results of the investigation. Other corrective actions needed to return the plant to power operation are being formulated and implemented.
3411993015 | Fermi 2 | 12/26/1993 | 04/21/1994 | 9404260165 | <strong>Failure of Reactor Recirculation Pump B Discharge Valve B3105-F031B to Close</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1993 at 0520 hours while preparing to place Division 2 of the Residual Heat Removal RHR! system into service for the Shutdown Cooling SDC! mode of operation, valve B3105-F031B, the "B" loop recirculation pump discharge valve, failed to fully close. The plant was brought to Cold Shutdown within the 24 hours as required by the applicable Technical Specification Action Statement and SDC was established using division 1 RHR. On December 28, maintenance personnel inspected the valve's limit switch compartment and found three wires from the torque switch to the limit switch broken at the crimp of their respective lugs. The three wires were relugged and reconnected. On December 29, at 0235 hours the valve was successfully stroked and declared operable. <br /><br /> The root cause was determined to be the coincident natural frequency of the wire bundle and the valve's yoke, in conjunction with the pump operating speed causing the vibration induced fatigue observed.<br /><br /> Corrective actions include changing the resonant frequency of the wire bundles by restraining or retraining the bundles, using a more flexible wire, changing procedures, and training.
3441993001 | Trojan | 10/08/1992 | 02/17/1993 | 9302230261 | <strong>Personnel Error to Properly Seal a Fire Barrier Penetration Leads to a Non-Functional Three Hour Fire Barrier Penetration</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1992, the Trojan Nuclear Plant was operating at 100 percent power. Plant personnel conducting the eighteen month fire barrier surveillance required by Trojan Technical Specification (TTS) 3/4.7.9, "Penetration Fire Barriers," determined that a sleeved conduit penetration did not have an internal seal (between conduit and sleeve). Further investigation by engineering personnel concluded that the penetration was not a TTS-related penetration. On January 18, 1993, during review of discrepancies identified during the 1992 fire barrier surveillance, it was determined that the penetration was a TTS-related penetration. A design drawing error had led to the earlier incorrect conclusion. The penetration is in the wall separating the elevator equipment room from the adjacent corridor on elevation 611 of the Control Building. Compensatory measures required by TTS 3/4.7.9 were implemented within one hour of the discovery. The root cause of this condition is personnel error, failing to seal adequately a three hour fire barrier penetration. Corrective actions included repairing the penetration, correcting the design drawing, and adding the barrier to the barrier inspection program. This report is being submitted to fulfill the reporting requirements of 10 CFR 50.73(a)(2)(i) and as the Special Report required by TTS 3/4.7.9.
3441993002 | Trojan | 02/09/1993 | 03/11/1993 | 9303180036 | <strong>Deficiency in Penetration Fire Seals Results in a Degraded 3-Hour Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1993, the Trojan Nuclear Plant was shut down and defueled. It was discovered that the seals for Fire Barrier Penetrations 2121 and 2122, in the walls of a vertical pipe chase located in the 45 foot elevation of the Auxiliary Building, did not meet 3-hour fire barrier ratings. The seals close the openings made for small conduits penetrating one of the pipe chase walls. The seals were being inspected to resolve discrepancies noted during a recent periodic fire barrier surveillance. It was determined that both seals were grouted, flush with the inside of the pipe chase, to a depth of 2-1/2 to 3 inches instead of the six inches required to provide a 3-hour fire rated barrier. The pipe chase is located in an open area of the Auxiliary Building which contains the Service Water Booster Pumps and the Component Cooling Water Pumps. The cause for this penetration deficiency was an error at the time of penetration identification and tagging. This was performed several years ago when penetrations in Appendix R fire barriers were originally identified. A fire patrol was established when it was determined that the penetration seals did not meet 3-hour fire rating requirements. The fire patrol remained in place until February 16, 1993 when the seal repairs were completed.
3441993003 | Trojan | 05/31/1993 | 06/24/1993 | 9307020239 | <strong>Lightning Strike Causes Undervoltage Condition and Results in Emergency Diesel Generator Start from Non- Engineered Safety Feature Signal</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1993, plant electrical loads for the permanently defueled Trojan Nuclear Plant were being supplied from the Trojan switchyard via the Startup Transformers. A lightning storm was in progress and was causing transmission system disturbances. At 1928, a lightning strike resulted in a momentary undervoltage condition on the distribution system grid, which was sensed by a non-Engineered Safety Feature relay on the secondary side (12.47 KV) of a plant startup transformer. The relay actuated and caused an automatic start of the "A" Emergency Diesel Generator. The Emergency Diesel Generator did not load since the bus it supplies remained energized throughout the event. No corrective actions are necessary.
3441993004 | Trojan | 10/18/1993 | 11/16/1993 | 9312070192 | <strong>Deficient Calibration Method for Emergency Diesel Generator Day Tank Level Instrument Causes Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1993, the Trojan Nuclear Plant was in the defueled condition due to a permanent plant closure decision. A verification of Emergency Diesel Generator (EDG) fuel oil day tank level transmitter and mechanical level indication accuracies revealed level indication errors between 2.1 and 8.4 inches (high). The inaccurate level indications, which were used to verify compliance with Trojan Technical Specification (TTS) tank level requirements, resulted in B EDG day tank levels below the TTS limit during a one month period in 1990 while the plant was in modes 1 through 4. Both EDGs were required by TTS to be operable during this period. The cause of the errors was inadequate calibration instructions for a level transmitter and an error in the mechanical level indication that had existed since plant construction. Corrective actions include modifying the calibration instructions, recalibration of the mechanical level indications and hanging a tag on the control room level transmitter indication alerting operators to the level error.
3461993001 | Davis-Besse | 02/17/1993 | 03/19/1993 | 9303220375 | <strong>Unlocked High Radiation Area Door</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1993 at approximately 1600 hours, it was discovered that the door to the emergency airlock vestibule (door 360) was not locked. Since the emergency airlock itself is not maintained locked, door 360 provides the locked barrier to the high radiation area inside containment. As such, this event violated Technical Specification (TS) 6.12.2 which requires high radiation areas to be provided with a locked door to prevent unauthorized entry. It was subsequently determined that door 360 had been unlocked since approximately 1922 hours on February 17, 1993, with the plant in Mode 1 at approximately 73 percent power, when work associated with performance of TS Surveillance Requirement 4.6.1.3 was completed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i) as a condition prohibited by the TSs. <br /><br /> Door 360 was locked February 19, 1993 at approximately 1600, restoring compliance with TS 6.12.2. The lock on door 360 is unique. Security and radiation protection personnel have been trained on the proper operation of the lock. A sign which describes the proper method for locking door 360 will be installed near the door.
3461993002 | Davis-Besse | 04/22/1993 | 05/20/1993 | 9306010038 | <strong>Mode 4 Entry with Make-up Pump No. 1 Inoperable (TS 3.0.4 Violation)</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1993, at approximately 2057 hours, the unit entered Mode 4 (from Mode 5) with Makeup Pump 1-1 functional but electrically inoperable and Reactor Coolant System (RCS) pressure approximately 250 psig. This is a violation of Technical Specification 3.0.4 which prohibits mode changes unless Limiting Conditions for Operation are met without reliance on Action Statements. <br /><br /> Prior to Mode 4 entry, Makeup Pump 1-1 was declared operable with the close power fuses for breaker AC105 intentionally removed. The fuses allow remote closure (i.e., from the control room) of breaker AC105 for Makeup Pump 1-1. The decision to leave the fuses removed was an attempt to provide additional safety margin against a potential low RCS temperature overpressure event. <br /><br /> On April 24, 1993, at approximately 0049 hours, the condition was identified and the close power fuses were installed. Training on makeup pump operability, including required reading of this Licensee Event Report, will be completed by July 1, 1993.
3461993003 | Davis-Besse | 05/20/1993 | 06/17/1993 | 9306280126 | <strong>Reactor Trip - Loss of ICS Tave Input</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1993, at 1138 hours, the plant experienced a trip from approximately 102% power. Loss of continuity between a fuse and fuseholder resulted in a loss of power to an auxiliary relay in the Non-Nuclear Instrumentation (NNI) System. This caused a loss of the selected RCS average temperature (Tave) input to the Integrated Control System (ICS). The ICS Tave input failed to zero VDC indicating that the RCS average temperature was approximately 570 degrees F. Normal RCS average temperature is 582 degrees F. To compensate, the ICS Tave integral increased Reactor Demand, withdrawing control rods and increasing reactor power. In an attempt to reduce reactor power, operators took manual control of ICS and decreased the Steam Generator/Reactor Demand signal. The primary reactor operator overreacted and lowered demand too far. Primary to secondary heat flow became unbalanced as feedwater flow followed the lowered demand, but reactor power did not decrease due to the low Tave input. As feedwater flow decreased, RCS pressure increased. The reactor tripped on high RCS pressure. <br /><br /> The faulty fuse cap and fuse were replaced and other NNI fuse holders and fuses were inspected. The plant was returned to service on May 21, 1993 at 1308 hours.
3461993004 | Davis-Besse | 04/28/1993 | 07/26/1993 | 9308050217 | <strong>Mode 2 Entry with Auxiliary Feedwater Train 2 Inoperable (TS 3.0.4 Violation)</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1993, at 1212 hours, during startup from the eighth refueling outage (8RFO), the plant entered Mode 2 with the auxiliary feedwater pump turbine main steam line crossover check valve MS735 in the open position. Valve MS735 is required to close in order to maintain functionality of auxiliary feedwater pump turbine (AFPT) 2 in the event of a high energy line break (HELB) upstream of the valve. A subsequent engineering evaluation could not verify that valve MS735 would have closed under such conditions. As such, this constitutes a violation of Technical Specification 3.0.4.<br /><br /> It is believed that check valve MS735 stayed in the open position following system testing which was performed prior to entry into Mode 2. Valve MS 735 remained open due to valve packing load. A modification was made during 8RFO which replaced check valve MS735 with a new valve having an external shaft and packing. The design report for the modification stated that a packing friction load up to 60 ft-lbs could be expected. Testing verified that approximately 40 to 45 ft-lbs of torque on the valve stem are required in order to initiate valve motion in either direction. This was not properly analyzed during the design modification process. <br /><br /> Valve MS735 was closed at approximately 1500 hours on April 28, 1993, thereby returning AFPT 2 to operable status.
3461993005 | Davis-Besse | 10/08/1993 | 11/08/1993 | 9311120231 | <strong>Reactor Trip Due to Momentary CRD Trip Confirm Signal</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1993, at 0843 hours, with Control Red Drive (CRD) trip breaker testing in progress, the reactor tripped from 97 percent Rated Thermal Power (RTP). The trip was initiated by a momentary CRD Trip Confirm signal which caused the Integrated Control System (ICS) to initiate the Rapid Feedwater Reduction (RFR) and Main Feedwater Block Valve (MFWBV) closure. This resulted in feedwater flow being reduced by approximately forty percent while the Reactor was still at full power. The feedwater flow upset caused the Reactor Coolant System (RCS) pressure to increase rapidly until it reached the high pressure trip setpoint where the Reactor Protection System (RPS) tripped the reactor. The post-trip response of the plant was normal with no major problems.<br /><br /> The momentary CRD Trip Confirm Signal was caused by a degraded power supply in the CRD System Logic Cabinet No. 1. Excessive Alternating Current (AC) ripple on the Direct Current (DC) power supply output caused a CRD logic protection circuit to change state and actuate the CRD Trip Confirm Signal. The degraded power supply and CRD logic protection circuit were replaced prior to restart.
3461993006 | Davis-Besse | 10/15/1993 | 11/12/1993 | 9312020542 | <strong>Containment Air Cooler Service Water Valves Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1993, at 1646 hours, with the plant in Mode 1 at 100 percent power, Technical Specification (TS) 4.0.3 was entered due to missed Surveillance Requirement (SR) 4.7.4.1.a for Containment Air Cooler (CAC) Service Water (SW) inlet valves. Containment was entered, the valves were verified in the open position satisfying the SR and TS 4.0.3 was exited on October 15, 1993, at 1906 hours.<br /><br /> Position verification of the CAC SW inlet valves has not been performed during power operations since February, 1989, when these valves were removed from the Davis-Besse locked valve program. The valves were considered secured in position for purposes of meeting SR 4.7.4.1.a by virtue of the containment being locked and inaccessible during Modes 1 through 4. This position was questioned during the NRC Service Water System Operational Performance Inspection (SWSOPI). Toledo Edison rereviewed the treatment of the CAC SW inlet valves and concluded that position verification should have been performed every 31 days or the valves should have been locked. <br /><br /> This event is being reported as a condition prohibited by Technical Specifications under the provisions of 10CFR50.73(a)(2)(i)(B).
3461993007 | Davis-Besse | 11/12/1993 | 12/13/1993 | 9312200341 | <strong>Plant Operated Outside Design Basis Due to Isolation of No. 1 Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1993, at approximately 0500 hours, Auxiliary Feedwater (AFW) System Valve AF 608 was removed from service for preventive maintenance and Motor Operated Valve (MOV) testing. AFW System Valve AF 608 provides isolation of the AFW System to No. 1 Steam Generator and is also a containment isolation valve. Upon removing AF 608 from service, actions associated with Technical Specifications (TS) 3.7.1.2.a and 3.7.1.7, for the AFW System and the Motor Driven Feedwater Pump (MDFP), respectively, were entered. In addition, valves AF 3870 and AF 3871 were closed and power vas removed from their actuators, and Motor Driven Feedwater Pump Valve FW 6398 was closed to comply with TS 3.6.3.1., Containment Isolation Valves. Following completion of maintenance and testing, the affected systems were returned to their normal status and the appropriate TSs were subsequently exited. Following completion of the maintenance, a review of the AFW System configuration during the maintenance activity concluded that neither train of the AFW System, nor the MDFP were capable of feeding No. 1 Steam Generator in the event of a main feedwater or main steamline break on No. 2 Steam Generator. This is inconsistent with the assumptions for AFW System availability in the plant accident analyses. This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition outside the plant design basis.
3461993008 | Davis-Besse | 12/21/1993 | 09/30/1994 | 9410110211 | <strong>Manual Initiation of Emergency Ventilation Due to High Airborne Activity</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1993, at 1315 hours, with the Reactor operating at approximately 100 percent Rated Thermal Power, Chemistry personnel initiated a sample of the Make-up Tank (MUT) gas space. Plant Engineering and Chemistry personnel were evaluating the correlation between the concentration of dissolved gases contained in the reactor coolant and the concentration of hydrogen and nitrogen in the MUT gas space. At 1319 hours a high alarm signal was received in the control room from the Radioactive Waste Area Ventilation Exhaust Radiation Monitor RE5405. The Radwaste Area Supply and Exhaust fans automatically stopped and ventilation dampers changed position as designed. Emergency Ventilation System (EVS) Trains 1 and 2 were manually started. Initial notification to the NRC of the manual initiation of an Engineered Safety Feature was made on December 21, 1993 at 1737 hours. Starting the EVS in a non-ESF mode in accordance with regular reactor operating procedures has since been evaluated as non-reportable. This LER is therefore redispositioned as a voluntary report due to the number of diverse aspects of the event which generated significant generic interest. This event had no direct impact on the health and safety of the public or plant personnel. The dose due to the release was a very small fraction of the regulatory limits.
3461993009 | Davis-Besse | 12/22/1993 | 01/21/1994 | 9402030065 | <strong>Entry into T.S. 3.0.3 due to Inoperable Control Room Emergency Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On December 21, 1993 during performance of the monthly surveillance test (DB-SS- 03042) the Control Room Emergency Ventilation System (CREVS) Train 2 was declared inoperable due to excessive bearing noise. Technical Specification (TS) Action 3.7.6.1 was entered at 2131. On December 22, 1993, work commenced to repair the Train 2 fan bearing. To obtain access to perform repairs, the workers had to step over the Train 1 and 2 refrigerant pressure sensing lines. While work was being performed, one of these lines was bumped and a minor Train 1 refrigerant leak developed. The leak was discovered at 1146 and the line was subsequently crimped to prevent further refrigerant loss. Train 1 was declared inoperable and TS 3.0.3 was invoked. The sensing line was repaired, but not before commencement of a plant power reduction and declaration of an Unusual Event at 1245. The State of Ohio and local counties were notified of the event at 1249 and the NRC was notified at 1305. <br /><br /> The CREVS Train 1 was declared operable at 1357 after the sensing line was repaired and the applicable surveillance test performed. With the CREVS Train 1 restored, TS 3.0.3 was exited and the Unusual Event was terminated. Workers were counseled about the event, a temporary shield was placed over the sensing lines and CREVS Train 2 was repaired. The CREVS Train 2 was declared operable at 0305 on December 24, 1993.
3481993001 | Farley 1, Farley 2 | 06/07/1993 | 07/23/1993 | 9307280180 | <strong>Reactor Coolant Pump Undervoltage/Underfrequency Circuitry</strong><br /><i>Abstract:&nbsp;</i>In 1993, Southern Nuclear Operating Company (SNC) conducted a Self-Initiated Safety System Assessment (SSSA) of the Reactor Protection System (RPS) modeled after the Safety System Functional Inspections conducted by the NRC. On June 7, 1993, as a result of the SSSA, SNC determined the Reactor Coolant Pump (RCP) Undervoltage (UV) and Underfrequency (UF) portion of the reactor trip system, and the Turbine Driven Auxiliary Feedwater Pump (TDAFP) autostart signal from RCP bus undervoltage, contained a design deviation. The deviation was with respect to the single failure criterion requirements of IEEE-279 (1971) and the fail safe requirement of 10 CFR 50 Appendix A General Design Criteria (GDC) 23. <br /><br /> The SSSA found that the RCP UV and UF circuitry uses energize-to- actuate components, with two of three channels powered from one Turbine Building (TB) battery and the third channel powered from the other TB battery. For RCP UV or UF, the RPS logic requires two of the three channels to actuate in order to initiate either a reactor trip or a TDAFP automatic start. Thus, a loss of the particular TB battery (a single failure) which supplies two channels would preclude the RPS from sensing a RCP bus UV or UF condition since only one channel would have power. The purpose of the RCP UV and UF reactor trip is to protect against a complete loss of RCS flow event. The RCS low flow reactor trip has been confirmed by Westinghouse analysis to be adequate to provide the primary protective function such that DNBR limits would not be exceeded. In addition, the UV portion of the circuitry provides an autostart to the TDAFP that is an anticipatory signal. Steam Generator low low level is the primary start signal to the TDAFP. The existing condition does not prevent the RPS from completing the safety function of the system. The design deviation will be corrected.
3481993002 | Farley 1, Farley 2 | 08/12/1993 | 09/10/1993 | 9309150132 | <strong>Diesel Generator Fuel Oil Storage Tank Level Indicators</strong><br /><i>Abstract:&nbsp;</i>On 08-12-93 SNC determined that Technical Specification (T/S) 3.8.1.1.c had been violated. This T/S requires each independent Diesel Generator (D/G) Fuel Oil Storage Tank (FOST) to contain a minimum of 25,000 gallons of usable fuel. <br /><br /> The review of events leading to the T/S violation was initiated when on 07-07-93 four of the five D/G FOST level indicators failed as the result of a lightning strike. As a result of these failures, the levels in the D/G FOSTs were taken manually using a dipstick while the remote level indicators were being repaired. Following measurement of the D/G FOSTs using the dipstick method, inconsistencies were noted between the dipstick readings and the remote level indications recorded prior to the instrument failures. Subsequent investigation determined the technique used for calibrating the FOST level indicators was in error. This error caused the indicators to be nonconservative and resulted in not maintaining the required level. <br /><br /> The T/S minimum volume of 25,000 gallons was at this time believed to have been met with a remote level indication of greater than or equal to 71% for each tank. Based on reviews and calculations that were performed after 07-07-93, the minimum required level indication should actually have been 71.2% to 75.6% depending on the specific FOST. For the approximate two year time period for which data were reviewed, two of the FOSTs had one date, and one of the FOSTs had two dates on which the T/S limit for that tank was not met due to these instrument errors. On no occasion were these dates the same, and the minimum total available fuel on any of these dates was calculated to be approximately 139,000 gallons. This exceeds the 125,000 gallons that would be available in five FOST's at the T/S minimum. Based on these facts, it was determined that the health and safety of the public was not affected.
3481993003 | Farley 1, Farley 2 | 09/23/1993 | 10/22/1993 | 9310260345 | <strong>Control Room HVAC housing causes breach of Control Room pressurization boundary.</strong><br /><i>Abstract:&nbsp;</i>On 09-23-93 at 1400, Southern Nuclear Operating Company (SNC) recognized that the Control Room pressurization boundary had been affected by maintenance that was in progress on the A train Control Room (C/R) Air Conditioner (A/C). It was determined that the Technical Specification (T/S) requirement to be able to maintain the C/R at a positive pressure of greater than or equal to 1/8 inch water gauge relative to the outside atmosphere could not be met due to openings in the C/R Air Conditioner housing and duct-work. <br /><br /> Maintenance on the A train A/C was in progress to locate and repair a refrigerant leak in the system. The work involved removing the condenser end bells which required that access panels/doors in the A/C housing and duct-work be removed/opened. The A/C housing and duct-work forms a part of the C/R pressurization boundary and with the access panels/doors removed or open, the B train C/R Pressurization Unit was unable to maintain the required pressure. Work on the A train C/R Air Conditioner was stopped and the access panels/doors were restored to normal within approximately 30 minutes. This action reestablished the C/R pressurization boundary integrity and thus the ability to meet the T/S requirement for maintaining a positive C/R pressure. <br /><br /> Since the C/R Air Conditioner is shared between the two units, this event also affected Unit 2. Unit 2 was operating at 87 percent power.
3521993001 | Limerick 1, Limerick 2 | 01/09/1993 | 02/01/1993 | 9302100014 | <strong>PCRVICS Actuations During Performance of a Surveillance Test Procedure as a result of Inadequate Implementation of Previous Corrective Actions.</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1993, an inadvertent actuation of an underfrequency relay resulted in a trip of the '1A' Reactor Protection System (RPS) inverter output circuit breaker which caused a loss of power to the '1A' RPS/Uninterruptible Power Supply power distribution panel. This loss of power resulted in automatic actuations of the Primary Containment and Reactor Vessel Isolation Control System, and other various Engineered Safety Features. Instrumentation and Controls (I&C) personnel reset the underfrequency relay and reclosed the breaker thereby restoring power to panel 1AY160. All remaining isolations were reset 35 minutes after the trip. The cause of this event was the inadvertent actuation of an underfrequency relay during performance of a Surveillance Test (ST) procedure as a result of jarring. This problem had previously been identified but previous corrective actions were less than adequate and failed to prevent this occurrence. Procedure ST-8-036-320-1 did not contain cautions to alert performers of the sensitivity of the underfrequency relay to any jarring motion. Responsible I&C and Nuclear Maintenance Division work group foremen will complete the review of appropriate procedures for potential plant impact prior to their performance. A request to engineering has been initiated to determine whether any requirements exist for performance of ST-8 procedures. In the interim a Temporary Change will be made to appropriate procedures to alert performers of the potential for actuation of the underfrequency relay.
3521993002 | Limerick 1 | 02/06/1993 | 03/03/1993 | 9303100050 | <strong>Closure of a Primary Containment Isolation Valve in the Instrument Gas System due to a faulty Microswitch within a Pressure Differential Switch.</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1993, during the Main Control Room shift turnover, a Reactor Operator identified that the normally open Unit 1 long term gas supply to the Automatic Depressurization System (ADS) Primary Containment Isolation Valve (PCIV) was in the closed position. Operations personnel declared the PCIV inoperable, and troubleshooting of the PCIV was initiated. An evaluation concluded that the PCIV closed sometime between 2300 hours on February 5, 1993, and 0710 hours on February 6, 1993. This event is a recurrence of an identical event which occurred on December 9, 1992, and was reported in LER 1-92-018. The cause of the PCIV closure was identified to be the result of a faulty microswitch internal to a pressure differential switch (PDS). The microswitch and the PCIV handswitch were replaced. The PDS and PCIV were then successfully tested in accordance with a Surveillance Test (ST) procedure. Based upon the acceptable ST results, the PCIV was declared operable. The consequences of this event were minimal. A review of the test records for identical operating PDSs in the Plant and a review of the Nuclear Plant Reliability Data System were performed. No similar problems were identified, and therefore, we conclude that the faulty microswitch internal to the PDS is an isolated occurrence. Since the PDS and the handswitch are the only instruments that can directly cause closure of the PCIV, the refurbishment of the PDS should prevent the recurrence of a similar event.
3521993003 | Limerick 1, Limerick 2 | 03/03/1993 | 03/30/1993 | 9304060051 | <strong>A condition prohibited by Technical Specifications in that the Toxic Gas Detection System was inoperable for the detection of ammonia since initial installation.</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1993, the 'A' and 'B' Toxic Gas Analyzers were declared inoperable since the analyzers would not respond to the presence of ammonia in adequate time to allow operators 120 seconds to don Self Contained Breathing Apparatus (SCBA) as specified in the Limerick Generating Station Updated Final Safety Analysis Report. The condition has existed since original construction. The Main Control Room (MCR) ventilation was placed in an isolated mode such that analyzer response time was within acceptable limits until the analyzers were declared operable in the normal mode of operation. The consequences of this event were minimal since the operators would have had sufficient time to detect the odor of ammonia, don SCBA and initiate a manual isolation of the MCR ventilation system in accordance with approved procedures. The cause of this event was an original hardware deficiency in that the analyzers were not capable of alarming the presence of ammonia within the required response time. A contributing cause of this event was less than adequate testing of the analyzers prior to initial startup. On March 6, 1993, the analyzer flush times were reduced to lower the overall analyzer response time while maintaining analyzer operability. This new response time limit was determined using known values of wind speed and building wake effects rather than the estimated values used in the original design calculations. The reduced flush time has been incorporated into the site procedures..
3521993004 | Limerick 1 | 04/05/1993 | 05/05/1993 | 9305140076 | <strong>Primary Containment and Reactor Vessel Isolation Control System Actuation Resulting From Personnel Error During performance of a Surveillance Test Procedure.</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1993, at 0900 hours, while performing Unit 1 Surveillance Test (ST) procedure ST-2-026-624-1, "NSSSS-Refueling Area Ventilation Exhaust Duct Radiation-High; Division II A, Channel C Functional Test (RISH-26-1K610C)," a station Instrumentation and Controls (I&C) technicians inadvertently caused a Unit 1 'A' channel Refuel Floor high radiation isolation signal. The isolation signal resulted in automatic actuation of portions of the Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature (ESF). The isolation signal resulted in the automatic closure of Primary Containment H2/O2 Combustible Gas Analyzer Sample Line Isolation Valves SV-57-133, 183, and 191. Main Control Room (MCR) personnel verified all appropriate isolations. The actual and potential consequences of this event were minimal and there was no release of radioactive material to the environment as a result of this event. The cause of this event was personnel error in that an I&C technician manipulated incorrect equipment during performance of the ST procedure. The contributing components of this personnel error included less than adequate self-checking and failure to utilize repeat back during procedure performance. The involved technician was counseled on the importance of self-checking and proper communications. All I&C technicians are currently being given a newly implemented On the Job Training module on self-check and self-verification. I&C supervision have increased field observations of technicians to ensure that the principles of self-checking are being implemented.
3521993005 | Limerick 1, Limerick 2 | 04/23/1993 | 05/21/1993 | 9306020185 | <strong>Missed Technical Specifications Surveillance Requirement due to Personnel Error During Procedure Revision.</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993, at 1200 hours, we determined that a Technical Specifications (TS) Surveillance Requirement (SR) had not been satisfied for TS Section 3.8.2.1, 'D.C. Sources-Operating,' and the associated TS ACTION were not taken in the specified time period. It was determined that Surveillance Test (ST) procedures for Units 1 and 2 had been revised to remove the requirement that battery cell-to-cell and terminal connections be verified tight (by checking the torque values against the vendor required values); the ST procedures then only required a visual inspection and resistance test. Upon discovery of the condition on April 23, 1993, at 1200 hours, the plant entered TS Section 3.0.3 and TS SR 4.0.3. All 2400 affected battery cell-to-cell and terminal connections were verified as found to be tight within the 24 hour extended surveillance period allowed by TS SR 4.0.3, thereby precluding a plant shutdown. The actual and potential consequences of this event were minimal. Upon inspection, all 2400 affected battery cell-to-cell and terminal connections were sufficiently tight to ensure operability of the D.C. Sources. Additionally, visual inspections as well as resistance checks performed during the previously performed ST procedures did not indicate any abnormal conditions. The cause of this event was personnel error in that the requirement to verify tightness of connections was removed from the affected ST procedures. The affected ST procedures will be revised prior to their next performance to include proper direction for verification of tightness for cell-to-cell and terminal connections.
3521993006 | Limerick 1 | 05/06/1993 | 06/07/1993 | 9306150042 | <strong>Engineered Safety Feature Actuation Resulting from a Reactor Water Cleanup (RWCU) System Isolation due to High 'A' RWCU Pump Room Temperature.</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1993, at 1320 hours, a Group III Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) isolation signal occurred, an Engineered Safety Feature (ESF), initiating a Reactor Water Cleanup (RWCU) system isolation. The PCRVICS isolation signal was initiated when the Steam Leak Detection System (Division 1) detected high temperatures in the 'A' RWCU pump room above the 135 degrees F trip setpoint. The increase in the pump room temperature was due to removal of normal Reactor Enclosure (RE) Heating Ventilation, and Air Conditioning (HVAC) system from service for maintenance. The consequences were minimal and reactor coolant conductivity and purity remained well within the required limits. The cause was the result of a combination of several factors. First, the normal RE HVAC system was secured for maintenance prior to the isolation, and created a high temperature condition in the 'A' RWCU pump room. Secondly, the improper location of a steam leak detection temperature probe resulted in inaccurate high ambient room temperature representation. Thirdly, the RE HVAC system failed to restart to reduce the 'A' RWCU pump room temperature, due to a faulty fan motor breaker. The faulty breaker was replaced and the RE HVAC system was repaired and returned to operation. A work request has been initiated to relocate the temperature probe. The cause of the faulty fan motor breaker is currently under investigation.
3521993007 | Limerick 1 | 05/16/1993 | 06/21/1993 | 9306280320 | <strong>This LER reports a condition prohibited by Tech. Spec. (TS) in that a Primary Containment Isolation Valve was inoperable and the required TS ACTION was not taken due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1993, a section of Surveillance Test (ST) procedure ST-6-059-200-1, "PCIG Valve Test," which includes obtaining the stroke time of the Primary Containment Isolation Valve (PCIV) XV-059-141D, was identified by the Operations Surveillance Test Scheduler (OSTS) to be out of surveillance (OOS). Operations personnel were notified and the affected PCIV was declared inoperable. The ST procedure section was satisfactorily performed, and the PCIV was declared operable on May 21, 1993. The ST procedure and the PCIV had been OOS for a time period of 5 days and 74 minutes. Plant personnel were unaware that the ST procedure was OOS, and this resulted in the failure to comply with Technical Specifications (TS). The actual and potential consequences were minimal in that the PCIV was verified to be operable, and would have functioned as designed had an accident or operating transient occurred. The cause of this event was personnel error in that the Shift Technical Advisor (STA) incorrectly cancelled the ST procedure from a work order (WO). Contributing factors were that the WO had inadequate instructions, and an incorrect overdue date was assigned to the ST procedure. A detailed review of all open Unit 1 and Unit 2 Operations Department ST procedures was performed and no additional discrepancies were identified. The OSTS will ensure that explicit instructions and correct overdue dates are included in WOs when an incomplete ST procedure is involved. A letter has been issued to appropriate plant personnel which discusses this event.
3521993008 | Limerick 1, Limerick 2 | 06/27/1993 | 07/30/1993 | 9308040290 | <strong>Manual actuation of the Standby Gas Treatment System and Unit 1 Reactor Enclosure Recirculation Sys. following a motor failure in the normal Reactor Enclosure Ventilation Sys.</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1993 1 a main Control Room (MCR) annunciator alarmed indicating that the outside atmosphere to Unit 1 Reactor Enclosure (RE) negative differential pressure had decayed. An operator, dispatched to the local RE fan controls, observed the odor of burnt electrical insulation and discovered that the 'B' RE exhaust fan motor breaker had tripped as had the normal RE ventilation. Normal RE ventilation could not be restored since the standby RE exhaust fan was out of service. MCR operators took prompt actions to re-establish the required RE negative differential pressure by manually initiating the 'B' train of the Standby Gas Treatment System, the 'B' train of the Unit 1 Reactor Enclosure Recirculation System, and a Unit 1 RE normal ventilation system isolation. The manual actions taken constituted a valid manual Engineered Safety Feature actuation. The consequences of the event were minimal. The cause of the event is an unexpected failure of the 'B' RE exhaust fan motor due to a short in the windings. The motor is undergoing further inspection. The 'B' RE exhaust fan motor has been replaced and further corrective actions are pending the results of the motor inspection and evaluation. There have been no previous failures of this type of motor at Limerick Generating Station.
3521993009 | Limerick 1, Limerick 2 | 08/10/1993 | 09/09/1993 | 9309130199 | <strong>PCRVICS Actuations During Performance of a Surveillance Test Procedure as a Result of Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1993, at 0921 hours, an inadvertent actuation of an underfrequency relay resulted in a trip of the Unit 1 'B' Reactor Protection System (RPS) inverter output circuit breaker which caused a loss of power to the '1B' RPS/Uninterruptible Power Supply power distribution panel. This loss of power resulted in automatic actuations of the Primary Containment and Reactor Vessel Isolation Control System, and other various Unit 1 and Common Plant Engineered Safety Features. Instrumentation and Controls (I&C) personnel reset the underfrequency relay and Operations personnel reclosed the breaker thereby restoring power to the panel. All remaining isolations were reset within 37 minutes after the trip. The cause of this event was the inadvertent actuation of an underfrequency relay due to personnel error during performance of a Surveillance Test (ST) procedure. A test jumper was inadvertently left connected to the underfrequency relay test plug during testing, due to a lack of attention to detail. The I&C Technicians involved in this event were counseled regarding self-check principals and on the need for attention to detail. Additionally, a revision to enhance the ST procedure, and training to all I&C Technicians which reinforces self-check principals are planned.
3521993010 | Limerick 1 | 08/20/1993 | 12/23/1993 | 9401100156 | <strong>Actuation of the PCRVICS, an ESF, after a Reactor Enclosure exhaust plenum radiation monitor spuriously tripped.</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1993, at 2043 hours, the '1D' Reactor Enclosure (RE) Heating Ventilation and Air Conditioning (HVAC) exhaust plenum high radiation monitor spuriously tripped. This resulted in various Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations, Engineered Safety Features. The isolation signal closed various Primary Containment sampling and block valves. At 2103 hours Operations personnel reset the radiation monitor and the PCRVICS isolation signal and returned all affected valves to their normal positions. The actual consequences of this event were minimal. The affected PCRVICS isolation valves repositioned and functioned as designed in response to the isolation signal. Cable/connector integrity, sensor converter/detector performance, and power supply/capacitor performance have been evaluated as potential causes of this event. All equipment was found to be within expected performance criteria. The cause of this event could not be determined and has been attributed to a random spurious trip. The radiation monitor has not tripped since the occurrence of this event.
3521993011 | Limerick 1, Limerick 2 | 09/07/1993 | 10/07/1993 | 9310150195 | <strong>Partial Loss of Offsite Power that Resulted in a Unit 1 SCRAM and Various ESF Actuations on Unit 1, Unit 2, and Common Systems.</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1993, a loss of one of the two independent station offsite power supplies occurred. The 10 Station Auxiliary Bus Feeder Breaker opened and locked out due to an overcurrent condition when a bus feeder cable was struck during excavation work. All affected electrical buses transferred. The partial loss of power caused several Engineered Safety Feature actuations including fast starts of four Emergency Diesel Generators. The Unit 1 D114-G-D Feeder Breaker failed to reclose. The D114-G-D Feeder Breaker failure caused a Unit 1 Feedwater System anomaly which resulted in a reactor SCRAM on low water level. All safety systems functioned as designed. Unit 2 continued to operate at full power. The root causes of the 10 Station Auxiliary Bus trip are inadequate control of non-routine work processes, unclear supervision and worker expectations, and inadequate control of excavations including inadequate shoring procedural guidance. A primary casual factor of the Unit 1 reactor SCRAM was the Feeder Breaker failure. Corrective actions include the establishment of an excavation coordinator, a revision to the excavation procedure, the communication of management expectations, and a Feeder Breaker Diagnostic Testing Program.
3521993012 | Limerick 1 | 09/22/1993 | 10/21/1993 | 9311030239 | <strong>Failure to comply with Technical Specifications Section 3.7.7 in that a one hour firewatch inspection was not performed due to cognitive personnel error.</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1993, the established firewatch inspection for an area containing an inoperable fire barrier was not performed within the time required by the ACTION statement of Technical Specifications (TS) Section 3.7.7, "Fire Rated Assemblies," thereby resulting in a condition prohibited by TS. The actual consequences of this event were minimal in that a fire did not occur during the time period in which the area containing the inoperable barrier was not firewatched. Had a fire occurred, operable fire detection in the area would have automatically initiated to alert the Main Control Room personnel to dispatch the Fire Brigade. The primary cause of this event was personnel error in that the specifically designated Security Force Member (SFM) failed to perform the assigned inspection. A secondary cause was management oversight and a procedure deficiency in that a "Special Order" was ,not issued to instruct the SFM of the required inspection. The SFM was counseled on attention to detail, and appropriate disciplinary action was administered. All SFMs were briefed on this event and the requirements of attention to detail. Appropriate procedural revisions have been completed to require that a "Special Order" be issued whenever a deviation in the Firewatch Patrol occurs.
3521993013 | Limerick 1 | 10/26/1993 | 02/14/1994 | 9403020003 | <strong>LER and Special Report Concerning the Failure of the D14 Emergency Diesel Generator to Start During its Monthly Operability Test Run.</strong><br /><i>Abstract:&nbsp;</i>On 10/26/93, the D14 Emergency Diesel Generator (EDG) failed to start during its monthly operability test. One of the 2 redundant Starting Air Systems (SAS) (1D2) was out of service at the time due to a leaking solenoid valve. The leaking solenoid valve in the 1D2 SAS was replaced and the D14 EDG was successfully retested on 10/27/93. Investigation revealed that the 1D1 SAS distributor cam was mistimed due to inadequate procedural direction and verification during maintenance. The distributor cam was realigned and on 11/15/93, the D14 EDG was successfully tested using only the 1D1 SAS. Between 9/28/93, (the last successful D14 run) and 10/27/93, the D14 EDG would not have started since the 1D2 SAS was out of service while the 1D1 SAS distributor cam was mistimed. Since this condition was not observable until the subsequent start attempt, required TS ACTIONs for an inoperable EDG were not taken. No event requiring the D14 EDG to operate occurred, and the 3 remaining EDGs were operable. Inspections of the SAS for the remaining 7 Unit 1 and 2 EDGs were performed, and no problems were identified. Procedures will be revised to ensure proper cam timing.
3521993014 | Limerick 1, Limerick 2 | 10/05/1993 | 12/10/1993 | 9312200215 | <strong>Condition prohibited by Tech. Spec. (TS) in that the Spray Pond was inoperable due to a missed TS Surveillance Requirement as a result of personnel error.</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1993, at 2300 hours, Main Control Room (MCR) operators determined that Technical Specifications (TS) Surveillance Requirement (SR) 4.7.1.3.c had not been satisfied earlier on that day and a condition prohibited by TS existed. To support an Emergency Service Water (ESW) system flow verification test, the 'A' Residual Heat Removal Service Water (RHRSW) pump and the 'C' ESW pump were in service with the 'A' spray network in service. Later on the same day, MCR operations personnel performed the normally scheduled monthly D11 Emergency Diesel Generator (EDG) operability test. This test resulted in an automatic realignment of the spray network valves at 0902 hours and terminated flow to the 'A' spray network which was not recognized by the MCR operators. The piping above the frost line was later drained by 2400 hours an October 5, 1992, as required by TS SR 4.7.1.3.c thereby restoring the spray pond to operable status. The consequences of this event were minimal in that the piping was not in danger of freezing. The primary cause of this event was personnel error resulting from a less than adequate pre-job briefing. A contributing factor included an inadequate review of the impact of the D11 EDG test. Management's expectations on pre-job briefings and proper reviews was re-emphasized.
3521993015 | Limerick 1 | 10/29/1993 | 11/24/1993 | 9312060017 | <strong>LER Concerning an Unplanned Isolation of Several Primary Containment Isolation Valves, an Engineered Safety Feature Actuation, due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1993, a Main Control Room (MCR) Reactor Operator (RO) inadvertently grounded a test jumper during the performance of a surveillance test, causing a circuit breaker to trip open. This loss of power caused various Primary Containment Isolation Valves (PCIV) to go closed, an Engineered Safety Feature (ESF) actuation. Power was expeditiously restored by closing in the circuit breaker and the PCIVs were returned to their normal positions. There were no adverse consequences as a result of the PCIV closures. The PCIVs and the affected systems performed as designed. This event was caused by personnel error, in that, the preparation for this activity by the RO was less than adequate. Contributing factors included the lack of pre-staged banana jacks, and the lack of equipment and supplies in the MCR for this type of activity. Corrective actions include counselling of the RO, the installation of banana jacks in appropriate locations in the MCR, the availability of a jumper installation kit, and the dissemination of information regarding this event to all Operations personnel.
3521993016 | Limerick 1 | 11/15/1993 | 12/15/1993 | 9312210177 | <strong>Primary Containment and Reactor Vessel Isolation Control System Actuation Causing Isolation of the Reactor Water Cleanup System due to a leaking pressure relief valve.</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1993, at 0848 hours, a valid actuation of Group III of the Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature (ESF), occurred resulting in the isolation of the Reactor Water Cleanup (RWCU) system. The PCRVICS isolation signal was initiated by Divisions 1 and 4 of the Steam Leak Detection System which detected actual high temperatures in the RWCU system regenerative heat exchanger (RHX) room. The RWCU system isolated as designed. The steam was filtered within the Reactor Enclosure. The reactor coolant conductivity increased but remained within specified limits during the entire event. The cause of the high area room temperature was a leaking pressure relief valve on the tube side of the RHX. The major causal factor of the leaking relief valve is suspected to be thermal effects on the valve due to the operating temperature of the RHX. The relief valve was replaced, and the RWCU system was returned to service at 0414 hours on November 16, 1993. Until other long term corrective actions are evaluated and implemented, this valve and the corresponding Unit 2 valve will be included in the Preventative Maintenance Program, and will be replaced once every operating cycle.
3521993017 | Limerick 1, Limerick 2 | 07/05/1993 | 01/12/1994 | 9401270012 | <strong>Condition prohibited by Technical Specifications (TS) in that a Special Report for an inoperable Seismic Monitoring System was not submitted within the TS time period.</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1993, during a review of a modification to upgrade the Seismic Monitoring System (SMS), the SMS system manager identified that the Triaxial Response Spectrum Analyzer (TRSA) instrument of the SMS had been inoperable since May 26, 1993, and a Special Report had not been submitted.within 10 days pursuant to the requirements of Technical Specifications (TS) 3.3.7.2. The Special Report should have been issued by July 5, 1993; however, the report was not submitted until December 23, 1993, thereby constituting a condition prohibited by TS. No seismic events have occurred while the TRSA has been inoperable. The failure to submit the report was due to a mis-interpretation of the TS Section 3.3.7.2. On September 9, 1992, the SMS was declared inoperable due to an inoperable SMS instrument, and a Special Report was submitted on October 16, 1992. Since the SMS was already inoperable, the action of declaring the SMS inoperable was not re-performed on May 26, 1993, when the TRSA became inoperable. The TS LCO had been interpreted to cover the entire SMS and not just an individual instrument. Corrective actions include the issuance of an electronic voice mail message and a Reportability Training Bulletin, and a revision to the Reportability Reference Manual.
3521993018 | Limerick 1 | 12/06/1993 | 01/27/1994 | 9402030037 | <strong>Emergency Diesel Generator Fuel Oil Samples not analyzed within the Technical Specification specified time period.</strong><br /><i>Abstract:&nbsp;</i>On 12/29/93, samples of fuel oil off-loaded to the Unit 1 D14 and D11 Emergency Diesel Generator (EDG) storage tanks were found delivered to the off site laboratory and neither sample had been analyzed for eight fuel oil properties as required by a Technical Specifications (TS) Surveillance Requirement (SR). The D14 sample had been obtained on 10/28/93, and the D11 sample had been obtained on 11/03/93. The TS SR had not been performed within the 31 day SR time limit and the associated TS ACTIONs had not been taken resulting in a condition prohibited by TS. operations personnel declared the two EDGs inoperable until the samples were analyzed and the results indicated that both fuel oil samples were within the acceptable range for all parameters. The oil samples were preliminarily analyzed prior to being off-loaded per a separate TS SR, further analyzed on 12/29/93, and met the TS required limits. The primary cause of this event is a less than adequate process to ensure the TS required analyses are completed within the TS required time. A receipt acknowledgement mechanism and new procedures for analysis of the TS parameters will be implemented. Additionally, the personnel involved in the transport of the samples will be instructed on the importance of having the samples promptly delivered to the laboratory.
3531993001 | Limerick 2 | 01/03/1993 | 01/25/1993 | 9302030037 | <strong>Reactor SCRAM and ESF actuations resulting from an Electrohydraulic Control system transient coincident with a Balance of Plant battery ground due to an indeterminate cause.</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1993, the Unit 2 reactor shut down automatically on high pressure after a transient in the Electrohydraulic Control (EHC) system occurred coincident with a Balance of Plant (BOP) battery ground alarm. Following the reactor SCRAM, reactor water level momentarily decreased to -37.9 inches causing the Reactor Core Isolation Cooling (RCIC) system to initiate, various Primary Containment and Reactor Vessel Isolation-Control System (PCRVICS) isolations to occur, and a Reactor Enclosure Secondary Containment isolation. These are Engineered Safety Feature (ESF) actuations. The reactor shut down on high pressure as designed, and all control rods fully inserted. The RCIC system initiated but did not inject since the signal was not present long enough to have other injection valve 'open' permissives satisfied. The ESF actuations functioned as designed and the affected systems were expeditiously restored, thereby preventing any adverse impact on other plant systems. Following recovery from the SCRAM, Unit 2 entered Operational Condition 2 (Startup) on January 6, 1993, at 2307 hours. The cause of the EHC system transient and coincident BOP battery ground could not be established. While the unit was in operation, monitoring equipment was installed on the EHC system to provide information if a similar transient occurred. Tests on the EHC and BOP battery systems are currently being performed during the Unit 2 Refueling Outage, which began on January 23, 1993, and any related problems identified will be corrected during this outage.
3531993002 | Limerick 2 | 01/19/1993 | 05/20/1993 | 9305260070 | <strong>Improperly Connected Wires in a Circuit Breaker caused an Emergency Diesel Generator to be inoperable and a Violation of Technical Specifications to occur.</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1993, the D24 Emergency Diesel Generator (EDG) failed to pass Surveillance Test (ST) procedure ST-1-092-114-2 because certain loads were not shunt tripped from the D24 safeguard bus when a simulated Loss of Coolant Accident (LOCA) signal was initiated. During troubleshooting on January 25, 1993, a loose wire was discovered in circuit breaker D244-R-E-15 and a lifted wire was discovered in circuit breaker D244 D-6-28. The wires were restored to their normal position and a portion of procedure ST-1-092-114-2 was performed to verify appropriate loads were shunt tripped following a simulated LOCA signal. This event resulted in a condition prohibited by Technical Specifications (TS) Section 3.8.1.1 because the associated TS ACTION statements were not implemented within the required time period. Actual consequences of this event were minimal in that there was no event requiring the D24 EDG to perform its design function. The wire in the D244-R-E-15 circuit breaker is believed to have come loose at a plug connection during repairs made to enhance electrical separation between electrical divisions. Procedures S93.0.A and S93.0.C were revised on April 2, 1993 and March 31, 1993 respectively to alert workers of the potential for wires becoming loose during removal and restoration of plug connections on circuit breakers similar to D244-R-E-15. During troubleshooting on March 5, 1993 wires were found in circuit breaker D224-R-C-03 that were improperly connected. This caused the D22 EDG to fail procedure ST-1-092-112-2. This condition is being voluntarily reported because a condition prohibited by TS could have occurred.
3531993003 | Limerick 2 | 02/13/1993 | 03/11/1993 | 9303180169 | <strong>Engineered Safety Feature Actuations Resulting From a Spurious Division 2 Loss of Coolant Accident Signal due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1993, while the Unit was shutdown for refueling, an inadvertent Division 2 Loss of Coolant Accident (LOCA) signal was initiated. The LOCA signal was generated during the performance of a surveillance test, when an Instrumentation and Controls (I&C) technician was self-verifying instrument valve positions for a reactor water level differential pressure (dP) transmitter. The I&C technician inadvertently opened, then quickly re-closed, two isolation valves to the high pressure side reference leg head chamber. The two valves are utilized for calibration purposes only. The I&C technician mistakenly thought that the two valves were supposed to be open. The inadvertent LOCA signal caused various plant systems and automatic Engineered Safety Features to actuate automatically as designed. The actuations included the start of the 'B' Core Spray (CS) pump and subsequent injection, opening of the 'B' Low Pressure Coolant Injection Valve, the start of the D22 Emergency Diesel Generator, and various Primary Containment Valve isolations. All systems and components functioned as designed in response to the inadvertent LOCA signal. All isolation signals were reset and the affected systems were expeditiously restored, thereby preventing any adverse impact on other plant systems. The cause of this event was cognitive personnel error. The corrective actions include counseling of the I&C technician, and dissemination of management expectations to all I&C personnel.
3531993004 | Limerick 2 | 03/03/1993 | 03/30/1993 | 9304060044 | <strong>Inadvertent Emergency Diesel Generator start as a result of personnel error from misunderstood verbal communications During performance of a procedure.</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1993, while Operations and Technical Section personnel were performing Surveillance Test (ST) procedure ST-1-092-112-2, "D22 Diesel Generator 4KV SFGD Loss of Power LSF/SAA and Outage Testing," performance of a procedural step out of sequential order resulted in premature start of the D22 Emergency Diesel Generator (EDG). This inadvertent EDG start constituted actuation of an Engineered Safety Feature (ESF). Operations Shift Supervision was immediately notified and directed that the D22 EDG be realigned to the 101 offsite source bus to carry load. The D22 EDG was secured per the ST procedure using the EMERGENCY SHUTDOWN push button. The actual consequences of this event were minimal and there was no release of radioactive material to the environment as a result of this event. This type of inadvertent start had minimal detrimental effects on the EDG, such as thermal cycling and wear, because the EDG had been operating at steady state conditions earlier during performance of the ST procedure. The cause of this event was personnel error during performance of the ST procedure in that verbal communications were misunderstood by the test director. This event was communicated to all Technical Section personnel by memorandum on March 17, 1993 to reinforce Management's expectations regarding procedure use and proper communication techniques.
3531993005 | Limerick 2 | 03/26/1993 | 04/22/1993 | 9304260266 | <strong>Reactor SCRAM and PCRVICS actuation resulting from a closure of the Main Turbine Stop Valves due to air entrained in the Main Turbine Electro Hydraulic Control system.</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1993, during performance of a Surveillance Test procedure, a Unit 2 reactor SCRAM occurred in response to an inadvertent closure of the Main Turbine Main Stop Valves (MSVs). The reactor SCRAM was followed by a Main Turbine trip. Reactor water level decreased to +12.5 inches as expected, and various Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations occurred, however, no PCRVICS valve movements occurred. The Reactor Core Isolation Cooling system and the High Pressure Coolant Injection system received spurious initiation signals, but neither system injected into the reactor vessel. The reactor shutdown automatically and all control rods fully inserted as designed. Operations personnel successfully controlled the plant shutdown using the appropriate plant procedures. Unit 2 was returned to power operation on March 28, 1993. An investigation included that the MSV closures resulted from air entrapment in the Main Turbine Emergency Trip System (ETS) which is supplied by the Electro Hydraulic Control (EHC) system. The primary cause of the air entrapment was a procedure deficiency which did not adequately identify when to vent air from the ETS/EHC systems. A contributing factor to the cause was that orifices required to mitigate the effects of air in the ETS/EHC systems had not been installed. As a result of this event, a procedure revision was made, the required orifices were installed, and additional evaluations of this event are planned.
3531993007 | Limerick 2 | 06/17/1993 | 07/19/1993 | 9307280096 | <strong>Spurious Closure of a Traversing Incore Probe system explosive shear valve, a Primary Containment Isolation Valve, due to an indeterminate cause.</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1993, Main Control Room (MCR) Operations personnel received alarm indications that the Unit 2 'B' Traversing Incore Probe (TIP) system explosive shear valve had either spuriously fired and closed or was inoperable. This shear valve is one of two Primary Containment Isolation Valves (PCIV) on the TIP tubing. MCR Operations personnel then de-activated the second (i.e., redundant) unaffected PCIV and declared the 'B' TIP shear valve inoperable. The redundant PCIV is a ball valve downstream of the 'B' TIP shear valve. On June 22, 1993, plant personnel confirmed that the 'B' TIP shear valve firing mechanism had spurious y activated, constituting an Engineered Safety Feature actuation., Replacement of the 'B' TIP shear Valve was then performed. The 'B' TIP shear valve was then declared operable and returned to service. The actual and potential consequences of this event were minimal. The TIP detector was fully retracted and in its shield chamber, and the 'B' TIP ball valve was fully closed prior to and during this event. The cause of the 'B' TIP shear valve firing and closure is indeterminate. The integrity of the 'B' TIP shear valve including its associated firing circuit and cable were tested and inspected and no abnormalities were identified. Reviews of industry events were performed and no similar events could be identified. We have concluded that this event is an isolated occurrence, and therefore, no long term corrective actions are planned to be implemented.
3531993008 | Limerick 2 | 07/12/1993 | 07/30/1993 | 9308040294 | <strong>Missed Technical Specification Surveillance Requirement on fire Rated Assemblies due to Personnel Error During procedure preparation</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1993, we determined that a Technical Specification (TS) Surveillance Requirement (SR) had not been satisfied for TS Section 3.7.7, "Fire Rated Assemblies," and the associated TS ACTIONs were not taken within the specified time period. We determined that the Surveillance Test (ST) procedure required that upon failures in visual inspection of penetration seals, additional sampling of 10% of the same seal type must be performed. This is not in agreement with the TS requirement to perform an additional 10% sampling of each type of penetration seal upon any visual inspection failure. The ST procedures performed in July, 1990 and May, 1991 contained visual inspection seal failures. However, additional sampling was not performed and all penetration seals on Unit 2 should have been declared inoperable in July, 1990. The actual and potential consequences of this event were minimal. The cause of this event was a personnel error in that the technical requirement from TS SR 4.7.7.1(c) was misinterpreted during preparation and review of Revision 0 of the ST procedure, resulting in a less than adequate ST procedure. The investigation revealed that an acceptable ST procedure, with no inspection failures, was performed in February, 1993. Therefore, no additional sampling is required to ensure seal operability. The ST procedure will be revised prior to the next performance to require additional inspection of each seal penetration type, following failure of penetration seal visual inspections.
3531993009 | Limerick 2 | 07/16/1993 | 08/13/1993 | 9308190078 | <strong>An inadvertent Primary Containment and Reactor Vessel Isolation Control System actuation (High Pressure Coolant Injection System Isolation) due to a failed Rosemount Transmitter.</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1993, at 1228 hours, the High Pressure Coolant injection (HPCI) system steam supply line outboard primary containment isolation valve isolated due to an inadvertent HPCI steam line high steam flow isolation signal. Isolation of this valve is controlled by the Primary Containment and Reactor Vessel Isolation Control System which is an Engineered Safety Feature. The isolation signal was the result of an unexpected failure of differential pressure transmitter, PDT-055-2N057B (Rosemount, Model No. 1153DB6PAN0016). The cause of the transmitter failure is currently under investigation. The consequences of this event were minimal and there was no release of radioactive material to the environment. The HPCI system isolated as designed in response to the isolation signal. All other Emergency Core Cooling Systems were operable at the time of the event to mitigate the consequences of an accident. Following troubleshooting, the transmitter was replaced and the HPCI system was declared operable at 0720 hours on July 17, 1993. Corrective actions to prevent recurrence, if necessary, will be determined based on the results of the failure analysis by the manufacturer. A supplement to this report will be submitted if any significant results are identified from the failure analysis.
3531993010 | Limerick 2 | 07/21/1993 | 10/14/1993 | 9310210077 | <strong>This LER reports a condition prohibited by Tech Specs in that a Primary Containment Isolation Valve was inoperable and the required ACTION wasn't taken due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>In May 1993, the Reactor Core Isolation Cooling (RCIC) system barometric condenser vacuum pump discharge valve, HV-049-2F002, was declared inoperable due to a problem with the valve during testing. The valve was then declared operable on July 21, 1993. On September 9, 1993, Operations was notified that a stroke time surveillance requirement (SR) may not have been performed prior to declaring the valve operable. The valve was satisfactorily tested at 1705 hours on September 9, 1993. Subsequent investigation revealed that the SR had not been satisfied. The valve was inoperable between July 21 and September 9, 1993, and the Technical Specifications (TS) Actions were not taken. The actual and potential consequences of this event were minimal in that the operability of the RCIC system was not affected, and the valve would have performed its intended isolation function. The cause of this event was personnel error in that the ,Shift Supervisor failed to review outstanding SRs prior to declaring the valve operable. A review of all Operations Department out of surveillance ST procedures was performed and no discrepancies were identified. This event will be reviewed with Shift Supervision to ensure that a review of all applicable SRs is performed prior to declaring equipment operable.
3541993001 | Hope Creek | 02/18/1993 | 04/22/1993 | 9304260256 | <strong>Technical Specification noncompliance - surveillance test missed on High Pressure Coolant Injection Isolation System Delta T channel.</strong><br /><i>Abstract:&nbsp;</i>On 2/16/93, Instrument and Controls technicians performing a monthly functional test for a High Pressure Coolant Injection (HPCI) Isolation System delta T channel A5 noted that the channel under test was in bypass condition. The technicians notified their supervisor who determined that the A5 channel specified in the functional test had been placed in bypass during the previous refuel outage and the alternate A2 channel was placed in service as the primary channel at that time. On 2/18/93, review of the surveillance status of both channels, the supervisor recommended to the Senior Nuclear Shift Supervisor (SNSS - SRO licensed), that the A5 channel should be placed in service as primary and the A2 channel bypassed as the surveillance testing on A2 had not been completed. The SNSS concurred and the A5 channel was placed in service returning the isolation system to operable status. Review of test data following discovery of the missed functional test and data acquired from a channel calibration test performed during the period indicates that the channel had remained functional for the period. Procedures will be revised to identify all actions required to place a spare channel in service.
3541993002 | Hope Creek | 03/23/1993 | 04/21/1993 | 9304260220 | <strong>Technical Specification noncompliance - Missed In Service Test required by Technical Specification 4.0.5.</strong><br /><i>Abstract:&nbsp;</i>On 3/23/93, during a review of outage work orders, operations department personnel discovered that required post maintenance retest activities were not performed for several valves which were repaired during the outage. The retest activities are required following maintenance to meet the in service test requirements of technical specification 4.0.5. The retest activities which were specified on the work order did not list all the procedures required to fulfill the in service inspection requirements. Each of the valves were stroked to verify full travel and remote position indication was verified, however, the valve stroke time was not recorded. The valves were fully tested at their next scheduled 92 day interval shortly after the unit was returned to service. The valve stroke times recorded during the regular surveillance were within allowable values to meet operability requirements. Scheduling errors resulted in the overdue quarterly test. Planning personnel did not verify that each retest procedure, designated on the work order, addressed the valves which were worked during the outage. Corrective actions include establishing new recurring tasks when valve testing frequency changes are required for individual component testing and verifying that specified retest activities include all components being returned to service.
3541993003 | Hope Creek | 05/13/1993 | 06/09/1993 | 9306170141 | <strong>Engineered Safety Feature Actuation - Emergency Diesel Generator start due to loss of offsite power on 2 of 4 Vital Busses</strong><br /><i>Abstract:&nbsp;</i>On Thursday, 5/13/93, at 1757, a plant transient was initiated when a 13.8 KV pothead, located on a transformer feeder in the 13.8 KV ring bus, failed inducing a voltage drop and phase differential relay actuation. The relay actuation opened the normal feeder breakers to two vital busses and three non 1E busses which were being fed from the failed bus section, and initiated a close (fast transfer) signal on the alternate feeds for the busses. The non 1E busses transferred successfully; however, the two 1E alternate infeed breakers tripped open as the feeder voltage was below the required value needed for breaker closure. The two emergency diesel generators received valid start signals, loaded onto the busses, and all required loads for a loss of power (LOP) condition were sequenced on the busses. Non vital loads such as a primary and secondary condensate pump, a reactor recirc pump and two reactor feedpumps tripped as a result of the voltage transient. The plant stabilized at approximately 48% reactor power with the "A" & "C" diesel generators powering two of four vital busses. The root cause of the event was attributed to a failed pothead in the 13.8 KV switchyard. Corrective actions to replace the failed pothead were completed and the 13.8 KV bus section was restored. Additional corrective actions to provide additional monitoring of switchyard equipment are under evaluation and/or implementation.
3541993004 | Hope Creek | 05/16/1993 | 06/14/1993 | 9306170411 | <strong>ESF Actuation - Reaction SCRAM From EHC Component Failure</strong><br /><i>Abstract:&nbsp;</i>On 5/16/93 a component failure in the Electrohydraulic Control (EHC) System resulted in a Generator/Turbine Trip and Reactor SCRAM on Reactor High Pressure. The transient occurred while testing the No.2 Turbine Stop Valve during the Weekly Turbine overspeed Protection Surveillance. Operating pressure exceeded 1037 psig and reactor water level reached -5 inches. Lo Lo Set pressure was reached and "P"&"H" safety relief valves (SRV) cycled open once. Plant systems and components responded as expected. The root cause was attributed to a failed Agastat relay on an EHC control card. corrective actions included troubleshooting and replacement of specific components. The EHC System was monitored and valve testing was repeated successfully during plant startup prior to exceeding 30% power.
3541993005 | Hope Creek | 08/14/1993 | 09/14/1993 | 9309170041 | <strong>High Pressure Coolant Injection System inoperable due to torque switch roll pin failure on the Injection valve motor operator</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1993 at 1650 hrs, control room personnel removed the High Pressure Coolant Injection System (HPCI) from service to perform a scheduled quarterly In Service Test (IST) valve stroke procedure, OP- IS.BJ-0101(Q). During performance of the test, the BJHV-F006 (High Pressure Coolant Injection Valve discharge to Core Spray) did not stroke full open under test conditions. The Nuclear Control Operator (NCO-RO licensed) initiated an open signal overriding the test open circuit and the valve fully opened. When the valve was tested in the closed direction it traveled to the full close limit; however, shortly after reaching full closed, the valve thermal overload protection device tripped. The NCO notified the Senior Nuclear Shift Supervisor (SNSS-SRO licensed) who determined that the HPCI system should be secured to initiate corrective maintenance repairs on the valve. The discharge valve to core spray was isolated. Although the system was declared inoperable, the discharge flowpath to the feedwater system and the HPCI pump and turbine remained available for injection via the feedwater system. The root cause of the failure was identified as a failed roll pin in the motor operator torque switch assembly. The torque switch was replaced and tested satisfactorily on 8/19/93.
3541993006 | Hope Creek | 09/09/1993 | 10/06/1993 | 9310150045 | <strong>Single condition which could have affected the operation of multiple Safety Systems - misoperation of cooling water isolation valves for diesel generators and Emergency Core Cooling system room coolers</strong><br /><i>Abstract:&nbsp;</i>On Monday, September 6, 1993, while clearing and tagging a diesel generator room cooler isolation valve, the equipment operator noticed that the redundant room cooler valve was not open with the room cooler fan running. The Senior Nuclear Shift Supervisor (SNSS -SRO licensed) was notified and instructed maintenance department personnel to fail open the isolation valve prior to tagging the redundant room cooler valve. When maintenance personnel opened the valves to restore cooling to the diesel room, the equipment operator attempted to fail open the redundant cooler isolation: however, it too failed to open. Maintenance personnel were again dispatched to investigate the failure and attempt to open the valve. The SNSS decided to fail open at least one room cooler isolation valve in each diesel compartment to ensure room cooling would be available in the event any diesel generator would start. Subsequent to the initial event it was decided to perform weekly stroking of all room cooler valves to ensure their continued operability as no sticking or reduced stroke times were observed at the increased stroke frequency. The root cause of the valves sticking was attributed to the combination of excessive force generated by the actuator due to high supply air pressure and infrequent valve operation. Corrective actions include reducing the actuator air pressure, continued monitoring of the valves to verify proper operation with the reduced supply air pressure, and reviewing this incident with engineering personnel responsible for preparation of design change packages.
3541993007 | Hope Creek | 10/26/1993 | 11/22/1993 | 9312020428 | <strong>Condition Prohibited by Plant Technical Specifications, Entry into Technical Specification 3.0.3 due to both Control Room Emergency Filter Systems being declared inoperable.</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, October 26, 1993, Operations and Maintenance Department personnel were in the process of returning the "A" Control Room Ventilation System (CRVS) to service following a scheduled maintenance outage. At approximately 2233, operations personnel began operational testing of the Safety Auxiliaries Cooling System (SACS) Room Cooler Fans which operate in conjunction with the Control Room Chilled Water System. When the SACS room cooler fans associated with the "A" CRVS were removed from service following testing, the room cooler fans associated with the in service "B" CRVS were returned to service. Approximately two minutes after the "B" system fans were started the "B" CRVS tripped. At 2235 the Senior Nuclear Shift Supervisor (SNSS - SRO licensed) entered Technical Specification 3.0.3 due to both Control Room Ventilation Systems being out of service. A review of the control room alarm chronolog and local alarm panel did not indicate any cause for the trip of the "B" CRVS. As the SACS room cooler fans had just been started prior to the trip it was assumed that one of the fans may have tripped on low flow and subsequently tripped the CRVS. Both SACS room cooler fans were restarted and after they had run successfully for several minutes the CRVS were returned to service. At 2250, the "B" Control Room Ventilation System was declared operable and Technical Specification 3.0.3 was exited. Subsequent investigation determined the cause of the CRVS trip was a failed damper actuator on the suction of the "B" Control Equipment Room Fan, rather than the SACS room cooler fan. The actuator was repaired and tested Sat. Additional testing is scheduled to determine the root cause of the actuator failure.
3541993008 | Hope Creek | 11/01/1993 | 11/22/1993 | 9312090056 | <strong>Engineered Safety System actuation - Invalid High Pressure Coolant Injection System isolation due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1993, during performance of a High Pressure Coolant Injection (HPCI) steam Leak Detection surveillance test, an isolation signal initiated the closure of the HPCI inboard isolation valve. The Instrument and Controls technician (I&C tech - non licensed) performing the surveillance, immediately terminated testing when he realized an actual isolation signal occurred, which is not an expected result for the test. The tech contacted the Nuclear Control Operator (NCO - RO licensed) who verified all proper actuations occurred and reset the isolation logic. The Steam supply was reopened and HPCI was returned to a standby lineup. The Senior Nuclear Shift Supervisor (SNSS - SRO licensed), after determining the source of the isolation, permitted the test to be completed. The testing was performed satisfactory with no further incidence. The root cause of this event was inattention to detail and improper self checking. The I&C tech has been counseled in regard to attention to detail and proper self checking. This incident will also be reviewed with other maintenance department personnel who perform similar test activities. Additionally, this surveillance procedure and other similar procedures will be revised to perform a logic disabled verification following test switch manipulation.
3541993009 | Hope Creek | 11/09/1993 | 12/08/1993 | 9312160297 | <strong>Engineered Safety System actuation - Invalid start of "B" Residual Heat Removal Pump During surveillance testing due to test equipment malfunction.</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1993, during performance of a functional test of the Emergency Core Cooling system initiation logic, an invalid actuation signal resulted in a start of the "B" Residual Heat Removal Pump. The Nuclear Control Operator (NCO - RO licensed) contacted the Instrument & Controls technician (I&C tech - Non-licensed) and directed the I&C tech to terminate testing when the pump started. The NCO then verified that no valid initiation signals were present, secured the pump and returned it to a standby lineup. The I&C tech returned to the control room and notified the Senior Nuclear Shift Supervisor (SNSS -SRO licensed) that he suspected the logic tester in use had failed resulting in the invalid actuation signal. The contacts of the NORMAL/TEST function switch of the logic tester were verified to be closed with the logic tester set to the NORMAL (contacts open) position. The test was completed satisfactorily using a different logic tester. The root cause of this event was attributed to a faulty mode switch on the ECCS logic tester. Corrective actions include a mode switch position verification, using a digital multimeter prior to installing the tester during surveillances, and replacing the toggle switch on all ECCS testers every three years.
3541993010 | Hope Creek | 11/09/1993 | 12/08/1993 | 9312150348 | <strong>Condition Prohibited by Plant Technical Specifications, Entry into Technical Specification 3.0.3 due to both Control Room Emergency Filter Systems being declared inoperable.</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, November 9, 1993, the "B" Control Room Ventilation System (CRVS) tripped due to a spurious high motor winding temperature being sensed on the "B" chiller unit. The "A" CRVS was undergoing an Instrument and Controls surveillance test which was terminated to place the "A" CRVS in service. The Control Room Operator (NCO - RO licensed) started the "A" CRVS and dispatched an Equipment Operator (NEO - non- licensed) to perform a routine inspection of the equipment following the start. The NEO reported back to the control room that the linkage which operates the chiller compressor inlet vane was broken, and requested that the chiller be removed from service. With both Control Room ventilation systems inoperable, Technical Specification 3.0.3 was entered at 2108. The Senior Nuclear Shift Supervisor (SNSS -SRO licensed) instructed maintenance personnel to remove the linkage swivel from the "B" chiller to replace the failed linkage swivel on the "A" chiller. The linkage on the "A" chiller was restored, the "A" CRVS was returned to service and Tech Spec 3.0.3 was exited at 2125. At 2355 the NEO performing a routine tour of "A" chiller noticed the linkage was again broken; however, as the chiller was running at normal load maintaining chilled water temperature within the normal operating band it was decided to leave it in service. At 0030 the "B" chiller was placed in service, following installation of a new swivel, and the "A" was removed from service for similar repair. Two unrelated root causes were identified in this event. The broken swivel was attributed to design deficiency. The high motor temperature trip was attributed to loose connectors in the control cabinet. Corrective actions included replacement of the swivel and installation of new connectors in the control cabinet.
3541993011 | Hope Creek | 11/21/1993 | 12/20/1993 | 9312300013 | <strong>Engineered Safety System Actuation - service water pump start due to an invalid refuel floor high radiation signal.</strong><br /><i>Abstract:&nbsp;</i>On Sunday, November 21, 1993, at 0220 hours, control room personnel received indication of a failure on the "C" reactor building exhaust (RBE) radiation monitoring channel- The Nuclear Shift Supervisor (NSS- SRO licensed) contacted the shift Instrument and Controls technician (I&C tech - nonlicensed) to investigate the cause of the "loss of counts" indication on the channel. The I&C tech and NSS proceeded to investigate the malfunction. During the course of troubleshooting the "C" RBE channel, which inops the "C" Refuel Floor Exhaust (RFE) channel and provided 1 input to the 2 of 3 logic (expected system response), an unrelated failure of the "A" RFE channel resulted in completing the 2 of 3 logic causing an invalid actuation of the primary containment isolation system (PCIS) at 0306 hours. The radiation monitoring system was returned to a normal configuration, the invalid actuation was reset and all systems which responded to the PCIS signal were returned to a normal lineup. The root cause of this event was attributed to equipment failures in each of the RMS channels. Corrective actions included replacing the failed preamp cards in the two affected channels and sending the failed preamp cards to the vendor for failure analysis. Additionally this event will be reviewed with maintenance and system engineering controls personnel.
3541993012 | Hope Creek | 12/01/1993 | 12/30/1993 | 9401070142 | <strong>Engineered Safety System Actuation - Manual reactor scram due to severe arcing on main generator exciter brush assembly.</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, November 30, 1993, at 2100 hours, the equipment operator (NEO -nonlicensed) performing routine equipment inspections noticed sparking on the main generator exciter brushes. The nuclear shift supervisor (NSS - SRO licensed) and shift electrician were notified and inspected the exciter brushes both confirming that the sparking was excessive and immediate corrective actions were required. Additional off-duty personnel from system engineering and maintenance were called in to determine the cause of the sparking and whether the brush change should be attempted. After verifying normal current readings on the collector ring, it was determined that the brush was worn and replacement should be attempted. When the electrician pulled the brush assembly the remaining brushes on that ring began to spark violently. An immediate recommendation was made by system engineering to take the generator off line. Control room personnel were notified who reduced reactor recirculation flow to minimum and inserted a manual scram. All immediate operator actions following the scram were appropriate and all plant systems functioned normally. The root causes of this event were attributed to inadequate inspection guidelines and different style brushes being supplied by the vendor under the same part number. Corrective actions include revising the monthly inspection procedure, performance of additional weekly inspections and removing the incorrect style brushes from stores.
3611993001 | San Onofre 2 | 02/04/1993 | 03/08/1993 | 9303120154 | <strong>Main Steam Safety Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1434 on February 8, 1993, an engineer notified the Operations Shift Superintendent that Main Steam Safety Valve (MSSV) 2PSV-8411 was inoperable due to the insulation having been removed from the valve body. Since the removal of the insulation may cause the setpoint to shift, the MSSV was conservatively considered inoperable. Action was immediately initiated to restore the insulation. The action statement for an inoperable MSSV was entered which required a reduction in the Linear Power Level-High Setpoint to 98.6% within four hours as required by Technical Specification (TS) 3.7.1.1. The MSSV insulation was reinstalled at approximately 1500 and the MSSV was declared operable at 1632 after the valve body temperature had stabilized. <br /><br /> Subsequent investigation determined that the insulation had been removed on February 4, 1993, at approximately 1400 to provide access for investigation of a leak on the discharge flange of the MSSV. <br /><br /> As a corrective action, a warning will be added to the computerized San Onofre Maintenance Management System (SOMMS) concerning the need to declare the MSSV inoperable if the insulation is removed. A formal root cause evaluation will also be performed which may result in additional corrective actions.<br /><br /> This event had no safety significance since sufficient steam pressure relieving capacity existed to prevent exceeding 110% of the design pressure.
3611993002 | San Onofre 2 | 02/25/1993 | 03/29/1993 | 9304010309 | <strong>125 VDC Chargers 2B001 and 2B002 Inoperable Due to Incorrect 10 CFR Part 21 Evaluation</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1993, with Unit 2 in Mode 1 at 100% power, following replacement of all the reactor balance circuit boards of Unit 2 125 VDC battery charger 2B001, it was discovered, during review of replacement part documents, that an August 14, 1989 10 CFR Part 21 report, "C&D Battery Chargers," might be applicable to the replacement parts and might affect the TS Surveillance 4.8.2.1.c.4 minimum required charger current. Three chargers, (2B001, 2B002, and 3B004) were identified to be potentially affected by the Part 21 report. <br /><br /> On February 25, 1993, at approximately 7:40 pm, charger 2B001 was tested and did not meet the TS Surveillance 4.8.2.1.c.4 required current limit. Since chargers 2B001 and 2B002 each might be affected, and charger 2B002 had not been tested, both were declared inoperable. (Charger 3B004, which had three circuit boards replaced, was also declared inoperable pending testing.) As TS 3.8.2 does not provide an action statement for the condition where more than one battery charger is inoperable, TS 3.0.3 was invoked. A temporary waiver of compliance was sought and verbally approved at 8:30 pm on February 25, 1993. The temporary waiver of compliance was exited at 9:43 pm on February 25, 1993, when battery charger 2B001 was restored to operable status.<br /><br /> The cause of this event has been attributed to an incorrect 10 CFR Part 21 evaluation. <br /><br /> The affected chargers were adjusted to above the Technical Specification required amperage of 300 amperes and all warehouse in-stock reactor balance circuit boards were quarantined. Planned corrective actions include: 1) post installation testing will be required when reactor balance circuit boards are installed, 2) revision of the original 10 CFR Part 21 evaluation, and 3) procedures will be enhanced appropriately based on the revised 10 CFR Part 21 review
3611993003 | San Onofre 2, San Onofre 3 | 07/30/1993 | 11/12/1993 | 9311300085 | <strong>Pressurizer Pressure Bypass Removal Setpoint - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary Licensee Event Report (LER) involving the discovery of a plant setpoint that was not in conformance with the most conservative interpretation of the Technical Specification (TS) requirements associated with the Low Pressurizer Pressure Trip (LPPT) setpoint. However, existing operations administrative controls prevented a violation of the TS. As a result, the condition described in this LER had no safety significance and did not pose a threat to the health and safety of the public.<br /><br /> This condition resulted because several TS notes contain conflicting requirements for the LPPT setpoint. Edison has not been able to determine the root cause of this event due to the passage of time (the conflicting notes have existed for approximately 10 years). <br /><br /> Edison has reset the LPPT setpoint to be in compliance with the most conservative interpretation of the TS notes. Edison also reviewed similar setpoints and found no additional discrepancies. Edison has submitted proposed TS changes to clarify the TS notes and eliminate the conflicting requirement.
3611993004 | San Onofre 2 | 08/02/1993 | 09/01/1993 | 9309080272 | <strong>Incomplete Once-A-Shift Operations Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1993, at approximately 1900, during a review of Technical Specification (TS) shift surveillances, it was determined that some portions of a shiftly surveillance had not been performed. This shiftly surveillance had been successfully performed on August 1 at 2105, and on August 2 at 2030, with all systems found OPERABLE. Therefore, all systems were, in fact, OPERABLE during this period and there was no safety significance to this event.<br /><br /> SCE Operations procedures explicitly require that the entire surveillance procedure is to be used, and any inapplicable steps marked "N/A". Contrary to this requirement, the operator failed to verify that the procedure copy used to perform the surveillance was complete, resulting in only 2 of 22 items being surveilled. Further, the normal review and approval of this procedure by the Control Operator and Control Room Supervisor failed to identify the incomplete surveillance. The root cause of this event was cognizant personnel error on the part of: (1) the operator (utility, licensed) who performed this surveillance; and, (2) the two supervisors (utility, licensed) who had oversight responsibilities over the operator, and who reviewed and approved the incomplete surveillance. <br /><br /> As corrective action, the three plant operators involved have been counselled regarding the use of procedures. This event is also being reviewed by all plant operators.<br /><br /> A review of previous LER's did not reveal any similar events.
3611993005 | San Onofre 2, San Onofre 3 | 08/10/1993 | 09/07/1993 | 9309130249 | <strong>Improper Configuration Of The Units 2 And 3 Main Steam Isolation Valve (MSIV) Enclosure Blowout Panels</strong><br /><i>Abstract:&nbsp;</i>On 7/15/92, with Units 2 and 3 in Mode 1 at 100%- power, a management walkdown identified that some retaining bolts of the Main Steam Isolation Valve (MSIV) enclosure blowout panels NF, DR! were either missing, broken, or improperly engaged. These steel panels on the roof and walls of the MSIV enclosure are secured closed by bolts to assure that the panels remain closed during a tornado to function as missile barriers. The bolts are also designed to fail in tension to relieve internal pressure during a main steam or feedwater line break. A comparison of the as-built with the various as-found configurations and a subsequent evaluation of the adequacy of the as-found configurations was concluded on 8/10/93. The evaluation concluded that the affected panels may not have remained closed in the event of a tornado and may not have, therefore, protected components in the enclosure from tornado missiles. Specifically, 9 panels at Unit 2 and 12 panels at Unit 3 (of the 14 panels per unit) were affected. Each of the 4 MSIV enclosures (2 per unit) house steam and feedwater isolation valves and atmospheric dump valves. <br /><br /> The missile barrier function of the panels is a passive design feature. Applicable maintenance procedures did not provide direction which was adequate to assure proper installation of the panel retaining bolts, following maintenance or removal for access. Additionally, the original panel bolt design is susceptible to damage during bolt removal and installation as well as occasional failure subsequent to installation. <br /><br /> The blowout panels were restored to operability on 9/30/92. Appropriate procedures were modified to assure the as-built configuration is maintained. The MSIV blowout panel fastening system will be evaluated and enhanced as appropriate. Other similar blowout panels will be assessed. A probabilistic risk assessment of the condition conservatively determined the increase in core damage frequency to be about 5E-9 per year per unit. This increase in risk is negligible and of no safety consequence.
3611993006 | San Onofre 2, San Onofre 3 | 09/08/1993 | 10/07/1993 | 9901270110 | <strong>Licensing Basis For Units 2 And 3 Auxiliary Feedwater Piping Tornado-Generated Missile Barriers Not Fully Met</strong><br /><i>Abstract:&nbsp;</i>By letter dated 11/24/80, SCE committed to protect the Auxiliary Feed Water (AFW) system from all tornado-generated missiles listed in the FSAR. On 9/8/93, during the resolution of calculation concerns raised by an SCE internal audit, SCE determined that missile barriers for portions of the AFW pump suction and miniflow lines did not satisfy their initial design criteria for tornado-generated missiles. On 9/8/93, at 1349 PDT, SCE conservatively provided a non-emergency four-hour report to the NRC in accordance with 10 CFR 50.72(b)(2)(iii). SCE later determined that the existing AFW piping barriers met the Standard Review Plan (SRP) acceptance limit for probability of damage from tornado-generated missiles. <br /><br /> SCE submitted Revision 0 of this LER as a voluntary report. SCE has since found a few additional cases where plant components were not protected from all design basis tornado-generated missiles and is updating this LER accordingly. SCE has submitted Amendment Application Nos. 138 and 122 to the NRC for approval to revise the licensing basis for tornado-generated missile barrier protection.
3611993007 | San Onofre 2, San Onofre 3 | 09/21/1993 | 10/21/1993 | ML09152030 | <strong>Calculated Peak Fuel Clad Temperature</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1993, at approximately 1600 PST, with units 2 and 3 at 98% power, it was determined that a non-conservative error had been made in the input to the original Large Break Loss of Coolant Accident (LBLOCA) analysis for Units 2 and 3 which affected the calculated peak fuel cladding temperature (PCT) . Combustion Engineering (CE) discovered that the input value used for paint thickness on some carbon steel structures inside the containment had been incorrectly entered as 0.00524 ft instead of the correct value of 0.000524 ft. With the paint thickness input error corrected, the resulting PCT value was 74 F higher than indicated by the original calculation. This increase resulted in a calculated PCT for Units 2 and 3 Cycle 7 which exceeded the 2200 F PCT allowed by 10CFR50.46. <br /><br /> The cause of the incorrectly calculated PCT was a data input error made by CE for the containment paint thickness used in the original LBLOCA analysis. This was identified and corrected during the Unit 3 Cycle 7 reload analysis of the LBLOCA event. It is not possible at this time to determine the exact cause of this data input error due to the length of time since the original analyses was performed in 1977.<br /><br /> The existing LBLOCA analysis for San Onofre was reevaluated by CE with the paint thickness input corrected and a LHR limited to 13.5 Kw/ft. This new analysis has confirmed that the Peak Clad Temperature would remain below 2200 F and that the LBLOCA analysis remains bounding. SCE has administratively reduced the maximum allowed linear heat rate (LHR) from 13.9 Kw/Ft to 13.4 Kw/Ft. <br /><br /> There is no safety significance to this event since the LHR at San Onofre has never exceeded 13.4 kw/ft. A thorough engineering review of core performance data, as measured by the COLSS, has found no instance in which San Onofre Units 2 or 3 has exceeded an LHR of 12.8 Kw/ft, including measurement uncertainties. Therefore, had the postulated LBLOCA occurred during past operating cycles, the actual PCT would not have exceeded 2200 F.
3611993008 | San Onofre 2, San Onofre 3 | 10/22/1993 | 11/22/1993 | 9312060242 | <strong>Inoperable Waste Gas System Monitor</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1993, with the Waste Gas Holdup System operating, the sample blower for the hydrogen/oxygen monitors for the Waste Gas Surge Tank (WGST) was inadvertently turned off and remained off for approximately 11 hours. This caused one channel of the gas monitoring system to be inoperable. Because the remaining channel of the hydrogen/oxygen monitors was not aligned to, the WGST during this period and the required 4 hour grab samples were not taken, this constituted a condition prohibited by Technical Specification 3.3.3.9, action b. <br /><br /> The day shift Radwaste Operator, believing the hydrogen/oxygen monitoring system was misaligned in that he believed that the blower should not be running, inappropriately turned off the WGST sample blower and did not communicate this manipulation to his command function supervisor in the Control Room. The night shift Radwaste Operator discovered the sample blower off while completing a daily surveillance. <br /><br /> The causes of this event were inadequate system knowledge on the part of the day shift Radwaste Operator, lack of a clear definition of the role of the Radwaste Supervisor, and inadequate communication between the Radwaste Supervisor and the day shift Radwaste Operator.<br /><br /> The operator involved in this event has been specifically retrained in the operation of the hydrogen/oxygen monitoring system. Edison will give additional on-the-job training on this system to the other operators who were qualified with this operator. In addition, Edison has reviewed the Qualification Guide and Lesson Plan for the Waste Gas Holdup System and determined they provide an adequate knowledge base for system operation. Edison will develop and promulgate a written policy on the authority and responsibilities of the Radwaste Supervisor. <br /><br /> The WGST hydrogen and oxygen concentrations were within their Technical Specification limits both before and after the event. During the period in which the WGST blower was off (and the hydrogen/oxygen monitors inoperable), no system evolutions were performed that could have caused the relative concentrations of hydrogen and oxygen to change. Therefore, there was no safety significance to this event
3611993009 | San Onofre 2, San Onofre 3 | 10/25/1993 | 01/04/1994 | 9401120135 | <strong>Inadequate Control Of Watertight Doors</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1993, Edison conservatively concluded, based on preliminary information, that the failure to have had a formal program to control watertight barriers, may have resulted in instances in the past of unacceptable configurations of watertight barriers. On November 24, 1993, a preliminary LER was submitted notifying the NRC of this discovery and that Edison's final engineering safety significance assessment for having various open watertight barrier combinations was ongoing. This LER provides the results of the engineering assessment which was discussed in detail in the R. M. Rosenblum (Edison) to B. H. Faulkenberry (NRC) letter dated December 23, 1993.<br /><br /> In response to an NRC inspector inquiry (discussed in NRC Inspection Report Nos. 50-206, 361, 362/93-29, dated November 4, 1993), and as a conservative action, Edison immediately took steps to clear and close the affected watertight barriers, and initiated administrative controls for opening watertight barrier configurations. Edison is also developing a formal program for controlling watertight barriers. <br /><br /> Edison completed a safety significance evaluation for having had these watertight barriers open as it relates to possible adverse cross-train interactions. This safety significance evaluation assessed each of the watertight barrier design functions. The assessment concluded that having the watertight barriers temporarily open had little safety significance. For the most significant of the event cases analyzed (pipe rupture with flooding), the net increase in core damage frequency (as determined by probabilistic risk assessment) was conservatively determined to be 3.7E-9. Details of Edison's safety significance evaluation are contained in a letter from R. M. Rosenblum (Edison) to B. H. Faulkenberry (NRC) dated December 23, 1993. <br /><br /> A review of previous LER's did not reveal any similar events.
3611993010 | San Onofre 2, San Onofre 3 | 11/22/1993 | 12/22/1993 | 9401040313 | <strong>Configuration Of Containment Sump Cover Plate</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary Licensee Event Report (LER) for a condition involving the containment emergency sump cover plates for Units 2 and 3. With Unit 2 in Mode 1 at 98% power and Unit 3 in a refueling outage, inspection of the Train A sump compartment of both Units identified an irregular (6' maximum) annular gap surrounding the 8' Reactor Coolant System Low Temperature Overpressure Protection (LTOP) relief discharge line which penetrates the horizontal steel cover plate of the sump compartment. As a conservative measure, the Unit 2 Train A Emergency Core Cooling System was declared inoperable pending an engineering assessment of the identified conditions. A debris limiting collar was promptly installed around the LTOP pipe penetration of the Unit 2 Train A sump cover plate. A final engineering assessment has concluded that both sump Trains were operable even without the Train A debris limiting collar, and that the as-built configuration of the sumps is consistent with Regulatory Guide 1.82, Revision 0, 'SUMPS FOR EMERGENCY CORE COOLING AND CONTAINMENT SPRAY SYSTEMS'. Edison is providing this voluntary report due to industry interest in sump-related issues, and to close out the 4-hour report of November 22, 1993 which noted the conservative declaration for Unit 2 Train A.
3611993011 | San Onofre 2 | 11/30/1993 | 12/28/1993 | 9401050031 | <strong>Reset Of Low Steam Generator Pressure Setpoint In Mode 1</strong><br /><i>Abstract:&nbsp;</i>With the unit in Mode 1, a Control Room Supervisor exercised misjudgment while trying to diagnose and correct an apparent anomalous pressure setpoint indication by directing the Control Operator (CO) to depress a reset pushbutton to lower the displayed value of a low steam pressure setpoint. The display was reading high due to a faulty meter. The CO depressed the pushbutton. The reading on the faulty meter did not change, but the setpoint for the other steam generator decreased to a value below the minimum allowed by the Technical Specifications (TS). This setpoint decrease was not noticed until the next scheduled shiftly surveillance. Because the setpoint remained below the TS minimum longer than allowed without compensatory action, this condition is reportable. Corrective actions included restoring the low setpoint to its proper value, repairing the faulty meter, and counseling the operators.
3611993012 | San Onofre 2, San Onofre 3 | 01/26/1994 | 02/25/1994 | 9403040169 | <strong>Motor Control Center Control Circuit Voltages</strong><br /><i>Abstract:&nbsp;</i>During a 1989 NRC Safety System Functional Inspection (SSFI) of the electrical systems at San Onofre Units 2 and 3, the NRC noted inadequacies in electrical distribution system design calculations. In response to this NRC observation, Edison committed, by letter dated April 24, 1990, to prepare new, formal electrical distribution system design calculations. Because the 120 VAC Motor Control Center (MCC) control circuit voltage calculations are dependent on the other calculations, they were the last of the electrical distribution calculations to be prepared. <br /><br /> In November 1993, during preparation of the MCC control circuit voltage calculations, Edison identified several circuits where the available voltage may not have been adequate to ensure automatic component actuation under worst case post-accident loading concurrent with minimum switchyard voltage conditions. On January 26, 1994, Edison conservatively concluded that, the alternate power source for the MCC control circuits for 2HV9303, the Containment Emergency Sump Train A outlet valve, and 3HV4713, the discharge control valve for Train A Auxiliary Feedwater pump may not always provide sufficient voltage to ensure automatic component actuation.<br /><br /> Technical Specification 3.8.1.1, 'A.C. Sources,' requires two physically independent circuits between the offsite network [FK] and the onsite Class 1E distribution system. Because 2HV9303 and 3HV4713 may not have operated with the alternate power source, Edison is conservatively reporting this condition in accordance with 10CFR50.73(a)(2)(i).
3621993001 | San Onofre 3 | 01/16/1993 | 02/16/1993 | 9302230133 | <strong>Automatic Turbine/Reactor Trip Due To Main Generator Stator Ground Protection Actuation Caused By Water Intrusion</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1993, Unit 3 was operating at 75% power with a heavy rain storm occurring. At 1641, the Main Generator tripped on a stator ground protection signal, causing a turbine/reactor trip. The plant was stabilized in Mode 3 at normal temperature and pressure at approximately 1715. <br /><br /> Rain water leaked down from the turbine deck into the main generator terminal enclosure, which contains the transition from the main generator conductors to the isophase bus. The water accumulated on some insulating material and provided a low resistance path from the exposed B phase conductor to ground, actuating a Main Generator/Main Turbine trip signal. <br /><br /> Additional sealing was provided for the Main Generator terminal enclosure to minimize the possibility of rain water intrusion, and the insulating material was replaced. SCE will evaluate whether additional measures can be taken to minimize the possibility of rain water intrusion into the Main Generator components. <br /><br /> There is no safety significance to this event since all Reactor Protection System components operated as designed.
3621993002 | San Onofre 3 | 03/09/1993 | 04/08/1993 | 9304120282 | <strong>Missed Daily Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>At approximately 0700 on March 9, 1993, with Unit 3 in Mode 1 at 100%; power, it was discovered that a Technical Specification (TS) surveillance required to be performed at least once per 24-hours had not been performed. The surveillance was subsequently performed at 0740 on March 9, 1993. The interval between completed surveillances was 3 hours and 10 minutes greater than the TS surveillance interval plus the allowable extension permitted by TS 4.0.2. <br /><br /> The cause of the event was an error by control room operators. The Assistant Control Operator (ACO) became distracted by other control room activities and failed to perform SO23-3-3.26 as scheduled. The Control Operator (CO) and the Control Room Supervisor (CRS) review all completed surveillances and check them against a list of required surveillances on a Technical Specification Surveillance Control Sheet (TSSCS). The CO initials the TSSCS indicating completion of each surveillance. Due to lack of verification by the CO and assumptions made by the CRS during the review process, the discrepancy was not identified. <br /><br /> As a corrective action, the personnel involved in this event have been counseled. In addition : 1) refresher training will be conducted for all licensed operators to emphasize management expectations with regard to performance and review of surveillances and 2) a change will be implemented to the TSSCS such that the operator actually performing the surveillance will now initial for completion.<br /><br /> There was no safety significance to this event since the delinquent performance of SO23-3-3.26 demonstrated that applicable TS components met their associated TS requirements and therefore remained operable.
3621993003 | San Onofre 3 | 05/27/1993 | 06/28/1993 | 9307020332 | <strong>Inoperable Containment Isolation Valves Due To Inadequate Motor-Operator Switch Settings</strong><br /><i>Abstract:&nbsp;</i>As the result of ongoing analysis and testing in accordance with Generic Letter (GL) 89-10, "Safety-Related Motor-Operated Valve Testing and Surveillance," SCE identified three containment isolation valves which had motor-operator switch settings that were non-conservative compared to those established by our GL 89-10 Motor-Operated Valve (MOV) program. Corrective action was taken to lock these valves in their OPERABLE position as required by the Technical Specifications. SCE will revise the MOV switch settings of these valves in accordance with SCE's MOV switch setting calculation program.
3621993004 | San Onofre 3 | 07/05/1993 | 08/03/1993 | 9308110133 | <strong>Reactor Trip Due To A Loss Of Vacuum</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1993, at 1943, Unit 3 tripped from 100% power, when the instrument air tubing supplying air to the Main Turbine Gland Seal Steam Spillover Valve Actuator failed. In accordance with the design of the valve, the loss of instrument air pressure to the valve caused the valve to fail open. The resulting loss of turbine gland steam pressure caused a Loss of Vacuum Turbine Trip and Reactor Trip. Emergency Feedwater Actuation occurred as expected due to Low Steam Generator Levels following the Reactor Trip from full power and the Auxiliary Feedwater System operated as designed. <br /><br /> The root cause of the instrument air supply tubing failure was a fatigue induced material failure. Corrective Actions include: 1) replacing the failed Instrument Air tubing, and 2) inspecting the tubing for Unit 2 and 3 Turbine Gland Steam supply and spillover valves.
3621993005 | San Onofre 3 | 11/30/1993 | 02/18/1994 | 9403080162 | <strong>Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1993, with Unit 3 in Mode 6 at 0% power, Edison completed an evaluation of a Non-Conformance Report for Train A Component Cooling Water System (CCW)CC! valve 3HV6371. During Motor Operated Valve Analysis and Test System (MOVATS) testing in April 1992, Edison had noted high running current for 3HV6371, and had scheduled the valve for maintenance during the next refueling outage. Prior to completing this maintenance, during a stroke test on January 19, 1993, 3HV6371 failed to open. The valve had been successfully passing its quarterly surveillance testing, including the last test (November 1992) before it failed in January 1993. In accordance with Technical Specification (TS) 3.6.3, "Containment Isolation Valves," the valve was secured in its safety related actuated position (open). When the valve was disassembled during the Cycle 7 refueling outage starting in November 1993, 3HV6371 was found to be incorrectly assembled. Specifically the upstream valve skirt was inverted. Therefore, Edison has conservatively concluded that 3HV6371 was inoperable in excess of the out of service time limits of TS 3.6.2.3 and TS 3.6.3 and therefore is reportable in accordance with 10CFR50.73 (a) (2) (i) (B). <br /><br /> The cause of the inoperability of 3HV6371 was the inverted upstream skirt which ultimately lead to the January 19, 1993 failure of the valve. 3HV6371 was correctly assembled, tested and determined operable during the Cycle 7 refueling outage in November 1993. Separate from this event, in January 1990, Edison upgraded the training provided for this type of valve, and, in July 1990, upgraded the associated maintenance procedure. <br /><br /> Edison has confirmed that sufficient containment cooling components were operable to ensure containment pressure and temperature design limits could be maintained. Therefore, there was minimal safety significance to this event.
3621993006 | San Onofre 3 | 12/13/1993 | 01/12/1994 | 9401260265 | <strong>Reactor Protection System actuation During Mode 3</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1993 at 2106, with the plant in Mode 3 at 0% power, during preparation for low power physics testing, control operators (utility/licensed) tripped reactor coolant pump (RCP) 3P002 [AB] after being notified of irregular pump operation by personnel monitoring the pump locally. As expected, the reactor tripped on a valid reactor protection system (RPS) [JC] actuation generated from all four 'Reactor Coolant Flow-Low' channels for steam generator (SG) E088 [HX]. All of the reactor trip breakers opened as designed. Because a valid RPS actuation occurred, this event is reportable in accordance with 10CFR50.73 (a) (2) (iv).<br /><br /> The cause of the reactor trip was the manual trip of RCP 3P002. No corrective actions are necessary as a result of the RPS actuation. The RCP was stopped because the rotating assembly was rubbing a carbon bushing at the top of the seal package. To return the RCP to service Edison realigned the lower motor radial bearing assembly, repositioned and secured the bearing shoes within the bearing assembly, and installed a new pump seal package. All systems functioned as designed when the RCP was stopped. Additionally, the Technical Specification requirements for RCPs and Reactor Coolant Loops in operation remained satisfied after RCP 3P002 was stopped. Therefore, there was no safety significance to this event.<br /><br /> ?
3621993007 | San Onofre 3, San Onofre 2 | 11/28/1993 | 04/26/1994 | 9405040099 | <strong>Roto Test Switch Bolt Failure, Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1993, with Unit 3 in Mode 5 in a refueling outage, during Engineered Safety Features [JE] testing, Unit 3 Emergency Diesel Generator (EDG) [EK] 3G002 output breaker tripped. Emergency Diesel Generator 3G002 tripped because the output breaker had closed but immediately reopened on high differential current signal. Edison investigated and determined that a Roto test switch (RTS-2) [EA] terminal bolt had failed which had caused the EDG 3G002 output breaker to reopen. An Edison root cause evaluation of this failure concluded that the terminal bolt failed due to a manufacturing defect. <br /><br /> While this event is not reportable in accordance with 10CFR50.73, Edison is submitting a voluntary report due to potential industry interest. <br /><br /> On November 29, 1993, Edison replaced RTS-2 for Unit 3 EDG 3G002. Emergency Diesel Generator 3G002 was tested satisfactorily and declared operable on December 1, 1993.
3641993001 | Farley 2 | 02/05/1993 | 03/04/1993 | 9303100186 | <strong>Inadvertent Safety Injection Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 2-5-93, preparations were being made for Unit 2 entry into mode 4 after a cold shutdown outage. At 0344 on 2-5-93, an inadvertent 'A' train safety injection (SI) occurred during the performance of FNP-2-STP-33.0A, "Solid State Protection System Train A Operability Test". The control room responded to the inadvertent actuation and subsequently terminated the SI and returned the Engineered Safety Features (ESF) systems to their pre-SI alignment. All ESF equipment functioned properly in response to the 'A' train SI signal.<br /><br /> During performance of the surveillance test procedure (STP) with the plant in Mode 5, the lights on the Bypass and Permissive panel should illuminate when the low pressurizer pressure safety injection and low steamline pressure safety injection signals are blocked. When attempting to block these signals the operator noted the lights did not illuminate. He incorrectly concluded this was the correct response and failed to communicate this observation to other crew members and correct the problem before proceeding to the next step of the procedure. FNP has concluded that the failure to block the safety injection signals as designed was due to the misoperation of the block-reset hand switches. <br /><br /> This event was caused by cognitive personnel error. The individual involved in this event has been disciplined for failure to use self-verification techniques and to effectively communicate with other members of his crew. As an enhancement all STP-33.0 series procedures have been revised to include the expected Bypass and Permissive Panel lamp indication based on plant conditions. This incident will be covered in licensed operator requalification training.
3641993002 | Farley 2, Farley 1 | 02/11/1993 | 03/12/1993 | 9303220012 | <strong>Missed Technical Specification Surveillance on the TDAFWP</strong><br /><i>Abstract:&nbsp;</i>As a result of a self assessment on the Reactor Protection System, at 1550 on 02-11-93, it was determined that the actuation of two B train slave relays for the Unit 2 Turbine Driven Auxiliary Feedwater Pump (TDAFWP) had not been verified within the last 18 months. These relays initiate the TDAFWP start on undervoltage on two out of three reactor coolant pump buses and the start on steam generator low-low water level on two out of three steam generators. The verification of this function is part of the required surveillance testing associated with Technical Specification (T.S.) 4.7.1.2. <br /><br /> Surveillance Test Procedures (STPs) tested only an A Train initiated start every 18 months (not separate A and B Train initiations); however, other procedures have tested a B Train initiated start at least once every 36 months. <br /><br /> FNP-2-STP-33.1 was modified to test the B Train initiated start while in mode 1. This was completed satisfactorily at 1914 on 02-11-93, at which time the Unit 2 TDAFWP was declared operable. It was determined that credit could be taken for B Train surveillance on Unit 1 based on FNP-1-STP-246.18, 'TDAFWP Response Time Test', which was performed on 11-28-92. <br /><br /> Surveillance test procedures for the testing of Unit 1 and 2 TDAFWP automatic starts from the B Train signals have been revised.
3641993003 | Farley 2 | 11/12/1993 | 11/22/1993 | 9312020299 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted in accordance with Technical Specification 4.4.6.5.a to report the number of tubes plugged, repaired or designated F* in each steam generator, and in accordance with Technical Specification 4.4.6.5.c to report the results of steam generator tube inspections which fall into Category C-3. <br /><br /> During the Unit 2 Ninth Refueling Outage, eddy current inspections were performed on one hundred percent of the available tubes in all three steam generators. As a result of this inspection a total of 129 tubes in service during Cycle nine (1.38 percent of the total number of tubes inspected), were found to be defective, which requires inspection results to be classified as Category C-3. A total of 145 previously plugged tubes were returned to service by sleeving or current data analysis. As a result of this inspection 227 tubes were designated F*. Following these actions, the equivalent tube plugging percentage in each steam generator is : 8.68 percent in 2A, 5.41 percent in 2B, and 7.23 percent in 2C. This results in an overall equivalent tube plugging of 7.11 percent.<br /><br /> In addition to the required tube plugging and sleeving, several ongoing programs have been established to reduce the probability of future tube degradation.
3641993004 | Farley 2 | 12/02/1993 | 12/21/1993 | 9312300205 | <strong>Reactor Trip on Steam Generator Low-Low Level following a Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At 2233 on December 02, 1993, with the Unit in Mode 1 operating at approximately 5 percent reactor power, the reactor tripped due to a low-low water level in the 2C steam generator (S/G) following a turbine trip and feedwater isolation. <br /><br /> The turbine/generator had been ramped down to between 60 and 70 megawatts in preparation for a turbine overspeed test. At this time reactor power was being maintained at approximately 20 percent power with load being maintained by the main generator in combination with the steam dumps. After the main generator output breakers were opened, S/G level and feedwater flow oscillations occurred. The operators were unable to maintain S/G levels due to the steam generator feed pump speed control maintaining an excessive/erratic pressure differential across the feed regulating bypass valves as a result of a speed controller card failure. <br /><br /> The level in the 2B S/G rose to the point that turbine trip and feedwater isolation signals were generated. With feedwater isolated, the S/G levels decreased. The operators began simultaneously feeding the S/G with auxiliary feedwater at the maximum attainable rate to maintain levels, and began inserting the control rods to reduce reactor power and return the Reactor Coolant System average temperature to the program value. Within approximately 1.5 minutes of the turbine trip/feedwater isolation, the reactor tripped on low-low level in the 2C S/G.
3661993001 | Hatch 2, Hatch 1 | 01/01/1993 | 01/22/1993 | 9301250222 | <strong>Short Circuit Causes Trip Of RPS Bus "B" And Unplanned Engineered Safety Feature System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 1/1/93 at 1330 CST, Unit 1 and Unit 2 were in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, Unit 2 Reactor Protection System (RPS) bus "B" lost power when the "B" Motor/Generator (M/G) Set, its normal power supply, tripped. This caused a loss of power to the "B" channels of the RPS, Process Radiation Monitors, Neutron Monitoring System, Primary Containment Isolation System (PCIS), and Offgas Radiation Monitoring System. These systems tripped on loss of power per design resulting in a half-scram in RPS channel "B", closure of various PCIS valves, isolation of the Unit 2 secondary containment, initiation of the Unit 2 Standby Gas Treatment System, and actuation of the pressurization mode of the Main Control Room Environmental Control System. All systems functioned per design given the loss of power to the RPS bus. Licensed operations personnel immediately restored power to RPS bus "B" via its alternate supply. RPS bus "B" was returned to its normal power supply and all affected equipment was restored to its normal configuration by 1400 CST. <br /><br /> The cause of this event was a momentary perturbation on RPS bus "B" caused by a short circuit in one of the loads supplied by the bus. The short circuit apparently caused a momentary undervoltage condition to be sensed by the RPS bus undervoltage protection relay. The undervoltage relay tripped the "B" RPS M/G Set per design causing a loss of power to the "B" RPS bus. <br /><br /> Corrective actions for this event include removing the short circuit and investigation of adding a time delay to the RPS bus protection relays.
3661993002 | Hatch 2 | 01/26/1993 | 02/02/1993 | 9303190232 | <strong>"As-Found" Primary Containment Integrated Leakage Rate Test Failure</strong><br /><i>Abstract:&nbsp;</i>On 1/26/93, Unit 2 was in the Run mode at 2436 CMWT (approximately 100 percent of rated thermal power). An Integrated Leakage Rate Test (ILRT) of the Unit 2 primary containment had been previously performed on November 6-7, 1992 during the tenth refueling outage. The as-left containment leakage rate was found to be 0.8858 weight percent per day, which was within the Technical Specification limit of 0.9 weight percent per day (.75La). Subsequent to the outage, the Architect Engineer (A/E) compiled the local leakage rate testing (LLRT) results, which determine the leakage rate improvements, and calculated the 'as found' containment integrated leakage rate. The 'as found' leakage rate was determined to be 1.3357 weight percent per day. This was in excess of the Technical Specification limit of 1.2 weight percent per day (La). The ILRT report was subsequently completed by the A/E and submitted for management review on 1/14/93. On 1/26/93, in reviewing the report, plant management determined that the excessive 'as found' integrated containment leakage rate represented a reportable condition. No corrective actions were required at this time since the leakage rate had been previously restored to the appropriate Technical Specification limit prior to restart from the refueling outage. The cause of the event was degradation of components comprising the primary containment boundary, in particular, those comprising the boundary for penetration X-222B. Corrective actions included repairing valves and replacing a flange gasket.
3661993003 | Hatch 2 | 04/07/1993 | 05/03/1993 | 9305140271 | <strong>Personnel Error Results In A Condition Prohibited By The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 04/07/93 at 0103 CDT, Unit 2 was in the Run mode at a power level of 938 CMWT (38.5% rated thermal power). At that time, licensed shift personnel were performing Control Rod Drive (CRD) system scram time testing in accordance with Unit 2 Technical Specifications section 4.1.3.2.a which requires the testing to be completed prior to exceeding 40% rated thermal power. Per procedure 34GO-OPS-001-2S, "PLANT STARTUP," reactor power was being maintained below 40% in order to comply with the specification. When licensed personnel prepared to test control rod 26-31, they expected that fully withdrawing the rod might cause thermal power to increase to a level very close to 40%. Therefore, they slowly withdrew the rod a few notches at a time while observing the Average Power Range Monitors. The monitors, which have strip chart indication, appeared to indicate approximately 40%. By the time the rod had been fully withdrawn, however, the plant's Process Computer indicated that thermal power had actually reached 40.71%, violating the requirement of the specification. Licensed personnel then scrammed the rod, and thermal power decreased to approximately 38.3%. <br /><br /> The root cause of this event is personnel error on the part of the licensed superintendent of shift. The plant startup procedure stated that the testing should normally be performed at 35% rated thermal power. However, the plant was operated at a higher power level (38.5%) with the result that when rod 26-31 was fully withdrawn, core thermal power increased to 40.71%.<br /><br /> Corrective actions for this event included counseling the licensed superintendent of shift. Also, the plant startup procedure will be revised by 7/16/93 to provide improved administrative control of reactor power.
3661993004 | Hatch 2 | 04/19/1993 | 05/18/1993 | 9305280281 | <strong>Group 2 Primary Containment Isolation System Valve Closes During Procedure Performance</strong><br /><i>Abstract:&nbsp;</i>On 4/19/93 at 1305 CDT, Unit 2 was in the Run mode at a power level of 1370 CMWT (56.2% rated thermal power). At that time, Group 2 Primary Containment Isolation System valve 2E51-F008, Reactor Core Isolation Cooling (RCIC) System Steam Supply Line Isolation Valve, unexpectedly closed. Instrument and Controls (I&C) personnel were performing a functional test on Analog Transmitter and Trip System (ATTS) trip unit 2E51-N657A, RCIC Steam Line Differential Pressure Instrument, per surveillance procedure 57SV-SUV-011-2S, "ATTS Panel 2H11-P925 Channel FT&C," at the time the valve closed. This trip unit provides an isolation signal to valve 2E51-F008 on steam supply line high differential pressure. A functional test of this isolation function was in progress at the time the valve closed; however, Operations and I&C personnel verified the logic had been configured as required by the surveillance procedure to prevent the isolation signal from actually closing the valve. With no other reason for the closing of valve 2E51-F008 apparent, licensed Operations personnel reopened the valve at 1318 CDT.<br /><br /> The cause of this event could not be determined. The logic was confirmed to be configured as required by the procedure to prevent the valve from closing, the logic drawings were reviewed to ensure the procedure was technically correct, and the actions of the I&C technicians performing the functional test were reviewed to ensure they correctly followed the procedure. No problems were found in any of these areas. Finally, the test was performed again with no changes having been made to the procedure; the test was run successfully and the event did not recur. No corrective actions were taken because the cause of the event could not be determined.
3661993005 | Hatch 2 | 05/21/1993 | 06/10/1993 | 9306180329 | <strong>Personnel Error Results In Unplanned Insertion Of Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On 5/21/93 at 1939 CDT, Unit 2 was in the Run mode at a power level of 1581 CMWT (approximately 65 percent of rated thermal power). At that time, licensed Operations personnel were performing surveillance procedure 34SV-C71-005-2S, "TURBINE CONTROL VALVE FAST CLOSURE INSTRUMENT FUNCTIONAL TEST." This procedure tests the "RPT" logic which causes a trip of the Reactor Recirculation Pumps in the event of a Main Turbine trip above 30 percent power. The procedure requires opening a test switch to disable the RPT trip while each Main Turbine Control Valve (TCV) is cycled. Per the procedure, the licensed operator should have disabled the "A" logic using the "A" test switch. Instead, he mistakenly moved the "B" test switch, disabling the "B" logic which was not being tested and leaving the "A" logic active. Subsequently, when the TCV in the "A" logic channel was closed per the procedure, the RPT logic was satisfied, and both Reactor Recirculation pumps tripped per design. Licensed operators immediately inserted a manual scram as required. Reactor water level decreased following the scram as expected, producing a second scram signal and closure of the Group 2 Primary Containment Isolation System valves. Water level was restored from a low point of 161 inches above the top of active fuel by the Reactor Feedwater Pumps. No Emergency Core Cooling Systems injected, nor were any required to do so. The cause of this event is a personnel error on the part of a licensed operator. Specifically, he manipulated the wrong test switch while performing a surveillance. Subsequent movement of the TCV being tested completed the logic required to produce a trip of the Recirculation Pumps. Corrective actions for this event included temporarily removing the involved operator from licensed duties and subjecting him to formal discipline under the Company's Positive Discipline Program. <br /> ?
3661993006 | Hatch 2 | 07/21/1993 | 08/18/1993 | 9308250035 | <strong>Less Than Adequate Procedure Results In Inoperable Reactor Coolant Pressure Boundary Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 7/21/93, at 1800 CDT, Unit 2 was in the Run mode at a power level of 2046 CMWT (85 percent rated thermal power). At that time, licensed personnel were notified that valves 2B31-F019 and F020 could not be fully closed against reactor pressure by use of normal motive power. These valves are air operated, normally open, spring to close valves that provide isolation capability for a three-quarter inch diameter reactor coolant sample line. The valves function as Primary Containment Isolation System (PCIS) valves and Reactor Coolant Pressure Boundary (RCPB) isolation valves. As RCPB isolation valves, pursuant to 10 CFR 50, Appendix A, General Design Criterion 55, they should be capable of closing against normal operating pressure. Based on previous local leak rate testing results, the valves would isolate the Primary Containment in the event of a design basis accident. By 2035 CDT, outboard valve 2B31-F020 had been de-activated and mechanically secured in the closed position. The cause of the condition was less than adequate procedural controls resulting in the valve actuators being set up improperly. Corrective actions include isolating the affected penetration, developing a procedure, reviewing similar valve applications, and properly setting up the valves during the next outage of sufficient duration.
3661993007 | Hatch 2 | 08/25/1993 | 09/23/1993 | 9309290347 | <strong>Relay Interaction Results In Unplanned Actuation Of Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On 08/25/93 at 1705 CDT, Unit 2 was in the Run mode at a power level of 2071 CMWT (85 percent rated thermal power). At that time, a surveillance of the High Pressure Coolant Injection (HPCI) system steam supply line pressure sensor was being conducted. This sensor is one of two instruments which provide isolation signals to the HPCI steam supply valve on low steam supply line pressure. Both instruments are required to trip in order for the steam supply valve to close. In this event, only one instrument was tripped per the surveillance; nevertheless, the steam supply valve automatically closed. With the steam supply valve closed, the HPCI system was rendered inoperable. When no cause for the isolation could be found, licensed personnel reset the isolation signal and reopened the steam supply valve, restoring the H CI system to operable status by 1730 CDT.<br /><br /> The cause of this event could not be conclusively determined. However, a possible cause is a spurious signal due to electrical interaction (noise) between adjacent relays in the same Analog Transmitter Trip System (ATTS) Control Room panel. The possibility for personnel error during performance of the surveillance was carefully evaluated and was determined not to be a contributing factor in this event. <br /><br /> Corrective actions for this event include restoring the HPCI system to operable status, inspecting the involved Control Room panel, and monitoring the panel using a computerized transient recorder. These actions are complete. In addition, off-site engineering is investigating the potential for electrical interaction causing the event.
3661993008 | Hatch 2 | 11/03/1993 | 11/30/1993 | 9312090182 | <strong>Turbine Stop Valve Failure Results In High Pressure Coolant Injection System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 11/3/93, at 0030 EST, Unit 2 was in the Run mode at 2064 CMWT (85 percent rated thermal power). At that time, it was determined that the High Pressure Coolant Injection System (HPCI, EIIS Code BJ) Turbine Stop Valve (TSV) was bound in the open position. In this configuration, the HPCI system was rendered inoperable. The TSV was subsequently repaired and the HPCI system was returned to service at 1830 EST, on 11/5/93 following successful testing of the system. <br /><br /> The cause of the TSV binding was galling of the disc guide surfaces. The valve bonnet guide and disc guide ring surfaces were found to be galled to the extent that no clearance existed between the disc and guide, resulting in the binding. The cause for the galling could not be conclusively determined. No debris was found in the valve internals that could have caused the galling, No other problems were identified with the valve. Corrective actions included reconditioning the bonnet guide and disc guide ring surfaces.
3661993009 | Hatch 2 | 11/08/1993 | 12/03/1993 | 9312090232 | <strong>Leak On Core Spray System Valve Results In Entry Into Technical Specifications Section 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 11/8/93 at 0856 EST, Unit 2 was in the Hot Shutdown mode with reactor pressure at 360 psig and the "A" loop of the Residual Heat Removal (RHR) system being aligned and warmed for the shutdown cooling mode. At that time, the "B" loop of the Core Spray system was declared inoperable as Operations personnel began establishing a clearance to isolate the "B" Core Spray system injection check valve, 2E21-F006B. The bonnet pressure seal area on the valve was allowing reactor coolant to leak; therefore, the valve had to be isolated in order to stop the leak and allow repair of the pressure seal area. Since the "A" loop of RHR was being aligned for the shutdown cooling mode, it had previously been declared inoperable for its low pressure coolant injection (LPCI) function. With one loop of Core Spray and one loop of the LPCI function of RHR inoperable, the plant was in a condition not addressed by the Limiting Conditions for Operation or action statements of the Unit 2 Technical Specifications. <br /><br /> Consequently, the unit entered Unit 2 Technical Specifications section 3.0.3 which required the unit to be in the cold shutdown condition within 30 hours. By 2155 EST on 11/8/93, the unit reached the cold shutdown condition thereby satisfying the requirements of Unit 2 Technical Specifications section 3.0.3. <br /><br /> The cause of this event was a leak in the bonnet pressure seal area of valve 2E21-F006B. With the "A" loop of RHR being aligned for shutdown cooling, the "B" loop of the Core Spray system had to be rendered inoperable in order to isolate the bonnet leak, a reactor coolant leakage path. This required entry into Unit 2 Technical Specifications section 3.0.3.
3661993010 | Hatch 2 | 11/08/1993 | 12/03/1993 | 9312090226 | <strong>Spurious Radiation Monitor Trip Results In Automatic Actuation Of Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On 11/8/93 at 1620 EST, Unit 2 was in the Hot Shutdown mode with reactor pressure at approximately 60 psig. At that time, the nitrogen atmosphere in the drywell was being vented to support a personnel entry for maintenance purposes. A licensed plant operator performing a routine panel inspection in the control room observed an extinguished indicator light on a Drywell radiation monitor. When the indicator light did not respond after changing the bulb, he tapped on the face of the monitor to ensure the bulb was securely seated in its socket. This action apparently induced sufficient noise in the monitor's detection circuit to produce a spurious trip. The trip resulted in the isolation of four drywell and suppression pool vent and purge valves. The operator immediately reset the trip on the radiation monitor. Licensed personnel then confirmed that no valid cause existed for these valves closing, and reopened the valves by 1625 EST. <br /><br /> The cause of this event was apparently electronic noise induced by an operator tapping on the radiation monitor. A contributing factor to the event is calibration drift in the radiation monitor which caused its status indicator light to be extinguished. The radiation monitor detected the calibration drift as an electronic "trouble" which caused the monitor to extinguish the indicator light. <br /><br /> The radiation monitor was recalibrated and returned to service. In addition, operations personnel will receive training on this event, which will be completed by 12/24/93.
3661993011 | Hatch 2, Hatch 1 | 12/20/1993 | 01/13/1994 | 9401250300 | <strong>Blown Fuse Results In Unplanned Automatic Actuations Of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 12/20/93 at 0945 EST, Unit 2 was in the Run mode at a power level of 2070 CMWT (85 percent rated thermal power) and Unit 1 was in the Run mode at a power level of 2387 CMWT (98 percent rated thermal power). At that time, technicians were performing a surveillance procedure to test the refueling floor vent radiation monitor instruments. This procedure requires the installation of jumpers in the "A" logic to prevent an automatic actuation of the Standby Gas Treatment (SBGT) system. After jumpers were installed on the contact side of relay 2D11A-K80 in trip auxiliary unit 2C51A-Z2A, fuse 2D11A-F14A blew on the coil side of this relay. Since this fuse supplies control power to both the "A" and "B" division logic systems, equipment associated with the "B" division received a start signal, initiating the "B" division SBGT system, closing the outboard Secondary Containment dampers, and actuating various outboard Group 2 Primary Containment Isolation System (PCIS) valves. Technicians then halted the surveillance. When the jumpers were removed, the same equipment associated with the "A" division also actuated. <br /><br /> The cause of this event has not been determined. The circuit in which the jumpers were placed is electrically independent from the circuit in which the fuse blew.<br /><br /> Corrective actions for this event included examination of relays from this and two previous similar events. Other corrective actions included reviewing the procedure which was in use at the time of the event and increasing the size of the fuse in the affected circuit. All these actions are complete. In addition, the affected circuits and wiring will be traced and verified during the next refueling outage.
3681993001 | Arkansas 2 | 05/13/1993 | 06/11/1993 | 9306170163 | <strong>Configuration Control Error Results in Technical Specification Required Action For One Inoperable Reactor Vessel Level Monitor Not Being Accomplished</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1993, ANO-2 discovered that one channel of the Reactor Vessel Level Monitoring System (RVLMS) had been inoperable since the probe was replaced in October 1992. During installation of RVLMS probes in 1986, polarity of conductors from some sensors in each of the two instruments was determined to be reversed from the intended design configuration. To correct this condition, polarity of wiring in the cabinets was changed and a note added to cabinet drawings. Replacement probes were purchased with the original design sensor polarity. The drawing note was not incorporated into the procedure for probe replacement. When both probes were replaced during October 1992, post-installation testing did not verify sensor polarity. Subsequent monthly surveillance checks did not detect the condition because the sensors indicated "Wet" (or "Invalid" with Reactor Coolant Pumps in operation) with the Reactor Coolant System filled. The cabinet wiring has been changed to restore operability of the RVLMS channel. The condition is reportable as an operation prohibited by Technical Specifications since required actions for one RVLMS channel being inoperable were not accomplished. The root cause of the condition is attributed to a configuration control error. Corrective action includes drawing and procedure revisions.
3681993002 | Arkansas 2 | 10/22/1993 | 11/22/1993 | 9312080008 | <strong>Inadequate Containment Sump Integrity Caused By Initial Construction Deficiency Results in The Potential For High Pressure Safety Injection And Containment Spray Systems To Be Degraded In The Recirculation Mode Due To Foreign Material Intrusion</strong><br /><i>Abstract:&nbsp;</i>During a containment inspection with the reactor operating at 100 percent power on October 22, 1993, it was discovered that containment sump integrity was inadequate to prevent entry of foreign material. Following a Loss of Coolant Accident, during the recirculation mode, this foreign material could enter the High Pressure Safety Injection (HPSI) and/or Containment Spray Systems and potentially degrade the system performance. Seven holes were found in the base of the sump that would have permitted water to pass into the sump without being screened. These holes were located in the masonry grout below the sump screen assembly. Within an extension of the allowable outage time of Technical Specification 3.0.3 approved by the Nuclear Regulatory Commission, repairs were completed in an expeditious manner to restore sump integrity. The root cause of the condition was determined to be an inadequate initial construction implementation of the sump design basis. Corrective actions include enhancement of sump inspection criteria. The condition has been determined not to have represented an undue increase in the risk to the public health and safety. Current procedures are adequate to prevent recurrence of similar conditions.
3691993001 | McGuire 1, McGuire 2 | 03/02/1993 | 04/02/1993 | 9304060153 | <strong>Technical Specification Required Surveillances Were Not Performed Due To Test Circuit Wiring Error Because Of Vendor Fabrication Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1993, McGuire Component Engineering personnel received informal notification from the NRC Resident Inspector identifying a problem discovered at Byron and Braidwood Nuclear Stations. An error in the wiring of the Westinghouse supplied Solid State Protection System (SSPS) was discovered during maintenance at Byron Nuclear Station. The wiring termination drawings which agreed with the as found condition were also in error. The wiring error resulted in the inability to properly test portions of the Engineered Safety Features (ESF) actuation and logic instrumentation channels to verify Phase B Containment isolation logic path. Upon examination, the Component Engineering personnel discovered the same problem existed at McGuire Nuclear Station. Consequently, both Units entered Technical Specification (TS) 4.0.3 to complete surveillances on the effected equipment. A minor modification and associated work orders were issued to correct the wiring error and complete equipment testing. The modifications and testing were completed on March 2, 1993 and both Units exited TS 4.0.3. Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power at the time the event was discovered. This event is assigned a cause of Vendor Fabrication Deficiency since the equipment and associated drawing were supplied in an incorrect condition.
3691993002 | McGuire 1 | 02/17/1993 | 03/19/1993 | 9303220293 | <strong>Technical Specification Required Surveillances Were Not Performed Correctly Due to Omission Of Relevant Information Because Of Deficient Written Communication</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1993, McGuire Component Engineering personnel received an Operating Experience (OE) report documenting a problem discovered at South Texas Nuclear Station, Unit 1. The OE report stated that a surveillance review task force had discovered a portion of the Containment Spray (NS) system channels between the process instrumentation and the Engineered Safety Features (ESF) actuation and logic instrumentation that was not being properly tested. Upon examination, the Component Engineering personnel discovered the same problem existed at McGuire. Consequently, McGuire Units 1 and 2 entered Technical Specification 4.0.3 to complete surveillances on the affected equipment. The required testing was satisfactorily completed on February 17, 1993, at 1700. Both Units exited Technical Specification 4.0.3. Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power at the time the event occurred. This event is assigned a cause of Deficient Written Communication due to relevant information being omitted from the surveillance test procedures. The individuals developing the test procedures did not recognize the significance of the test points used to verify continuity of NS circuitry. The circuits in question were subsequently verified and appropriate procedural changes will be implemented to ensure proper verification of continuity during future surveillance tests.
3691993003 | McGuire 1, McGuire 2 | 04/01/1993 | 05/03/1993 | 9305120052 | <strong>Train B Of The Control Room Ventilation System Was Past Inoperable Resulting In A Technical Specification Violation Due To A Possible Fabrication/Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1993, Mechanical Maintenance (MM) personnel were performing work order 93015150, and procedure MP/0/A/7450/16, VC Filter Removal and Replacement. Air in leakage was detected at an expansion joint on the Control Room Air Handling Unit, Train B, of the Control Area Heating Ventilation and Air Conditioning (VC) system. The insulation was removed from the ductwork by MM personnel, who determined that there was air being drawn in at four locations beneath an angle iron brace used to support the duct. The immediate corrective action performed by MM personnel was to caulk around the angle iron brace and duct to prevent any further air in leakage. Mechanical Nuclear Engineering personnel, tasked with resolving the operability question, determined the VC system to be past inoperable due to the existing air in leakage rate which exceeded the maximum assumed rate for the dose calculations. The existing in leakage rate would produce dose calculations exceeding the 10CFR50, GDC-19 limits. Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power at the time of discovery. This event has been assigned a cause of Possible Fabrication/Installation Deficiency because the angle iron brace was not properly installed. Permanent repairs to seal the duct will be made.
3691993004 | McGuire 1, McGuire 2 | 05/13/1993 | 06/11/1993 | 9306170128 | <strong>Both Trains Of Control Room Ventilation Were Inoperable Resulting In A Technical Specification Violation Attributed To Equipment Failure Due To Unknown Cause.</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1993, at 1140, Operations personnel declared Train 'B' of the Control Room Ventilation (VC) system inoperable. This was done in accordance with PT/1/A/4403/08, Nuclear Service Water (RN) Train 1B Flow Balance. At 1255, Train 'A' Chilled Water (YC) chiller for the VC system tripped due to a High Bearing Temperature alarm. At this time, both trains of the VC/YC system were inoperable requiring entry into Technical Specification (TS) 3.0.3. Immediate steps were taken to accelerate the completion of the RN Flow Balance and return the Train 'B' chiller to service. At 1314, the Train 'B' chiller was started and TS 3.0.3 was exited. Emergency Work Order 93034579 was also issued to troubleshoot the problem with the Train 'A' chiller. The investigation into the problem with the Train 'A' chiller revealed a faulty temperature sensor contact in the chiller motor module. The module was replaced and the chiller was returned to service at 2255. Unit 1 was in Mode 6 (Refueling) at 0% power and Unit 2 was in Mode 1 (Power Operations) at 100% power at the time of this event. This event is assigned a cause of Equipment Failure/Malfunction due to an unknown cause. There are no further actions planned.
3691993005 | McGuire 1 | 06/12/1993 | 07/12/1993 | 9307220218 | <strong>Unit 1 Experienced A Manual Reactor Trip As A Result Of An Equipment Failure Due To An Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1993, Operations personnel were commencing Reactor start up on Unit 1, from refueling outage 1EOC 08. The unit was approaching initial criticality. Zero Power Physics Testing was in progress. At approximately 0244, the Operations unit supervisor noticed a lashing General warning light emitting diode (LED) and Rod Bottom LED for Control Rod L-13 of Shutdown Bank C on the Digital Rod Position Indication (DRPI) system display unit. The Operator Aid Computer Program General 76, which displays control rod position and other pertinent data, was accessed for additional information by Control Room personnel. The information indicated that the rod position for rod L-13 was 'unreliable'. Operations personnel manually tripped the Reactor at 0245, on June 12, 1993 and immediately implemented procedure EP/1/A/5000/01, Reactor Trip or Safety Injection, and transitioned to procedure P/1/A/5000/1.3, Reactor Trip. The four hour notification was made to the NRC on June 12, 1993, at 0343, as directed by procedure RP/0/A/5700/10, NRC Immediate Notification Requirements. All systems operated as required. Unit 1 was in Mode 2 (Startup) at the time for this event. This event has been assigned a cause of Equipment Failure due to the failure for the L-13 field cable between Data Cabinet B and the bulkhead for undetermined reasons. The field cable has subsequently been replaced.
3691993006 | McGuire 1 | 05/26/1993 | 06/25/1993 | 9306300264 | <strong>A Failure To Comply With Technical Specification Action Statement Occurred Due To A Technically Deficient Procedure.</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1993, Operations and Systems Engineering personnel were performing the Unit 1, Train B, Engineered Safety Features (ESF) actuation test in accordance with procedure PT/1/A/4200/09A, ESF Actuation Periodic Test. While in the re-alignment phase of the test, at approximately 1530, Control Room (CR) personnel discovered that the sample blower for radiation monitor (EMF) 1 EMF-43B was off. 1 EMF-43B monitors the B Train Control Room Ventilation System (VC) air intakes. With the sample blower off, 1 EMF-43B is considered inoperable. Technical Specification (TS) 3.3.3.1 requires a VC air intake to be isolated within one hour if it has an inoperable EMF. Investigation by CR personnel revealed that 1 EMF-43B had been inoperable for approximately 1 hour and 52 minutes, without the VC air intake being isolated. Investigation also revealed that the same EMF had been inoperable for approximately 1 hour and 35 minutes earlier in the day, during a different portion of the ESF test. Investigation further showed that the A Train portion of the test had most likely rendered 1 EMF-43A, which monitors the A Train VC intake, inoperable on May 25, 1993. Failure to isolate the VC air intakes with the EMFs inoperable constitutes a condition prohibited by TSs, and is therefore reportable. Unit 1 was in Mode 5, (Cold Shutdown) at the time of the event. This event was caused by a Technically Deficient procedure. Corrective actions will include revising the Unit 1 and Unit 2 test procedures, to prevent reoccurrence.
3691993007 | McGuire 1 | 07/05/1993 | 08/04/1993 | 9308050027 | <strong>A Technical Specification Required Surveillance Was Not Performed Because Of An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1993, the Work Control Specialist in charge of monitoring the McGuire Preventative Maintenance/Periodic Testing (PM/PT) program, discovered that the PM/PT functional verification tests for Reactor Protection (IPE) system Trains A and B, showed the same due date. Technical Specifications (TSs) require that these tests be performed on a frequency of 62 days such that both trains are tested on a staggered basis. The due dates should be 31 days apart for the PM/PTs. Upon investigation, the Specialist discovered the computer program had failed to properly update the PM/PTs after both were performed on May 22, 1993, at the end of Unit 1 EOC08. Therefore, the required test on one of the IPE trains had not been performed as required on the 31 day stagger. A work order was generated and testing was satisfactorily completed on IPE system Train A at 1200, on July 5, 1993. Unit 1 was in Mode 1 (Power Operation) at 100 percent power at the time the event occurred. This event is assigned a cause of Inappropriate Action because personnel reviewing the computer program did not properly test the part of the program used for updating the PM/PTs. All other such tests were verified to be within TS requirements and appropriate changes will be made to the computer program to ensure proper updating of future PM/PTs.
3691993008 | McGuire 1, McGuire 2 | 10/21/1993 | 12/10/1993 | 9312210091 | <strong>The Decay Heat Removal System Was Past Inoperable Due To A Possible Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1993, Instrumentation and Electrical (IAE) Personnel were performing preventive maintenance (PM) on a Unit 1 Refueling Water Storage Tank (FWST) level instrument. The PM was to be performed using IAE procedure IP/0/A/3050/13B, Refueling Water Storage Tank Level Transmitter Verification, and called for pressurizing the low pressure (LP) side of the transmitter, to verify that the transmitter is not failed high. The IAE specialist performing the work was unable to pressurize the LP side. Subsequent troubleshooting revealed a loose fitting inside the transmitter cabinet. The IAE specialist tightened the loose fitting and completed the verification successfully. The loose fitting technically rendered both trains of the Decay Heat Removal (ND) system inoperable. This event is assigned causes of possible inappropriate action and inappropriate action. corrective actions for this event will include changes to the IAE procedure for verification to ensure that the integrity of the entire LP side of the transmitter is verified semiannually. Unit 1 was in Mode 4, Hot shutdown at the time of this event.
3691993009 | McGuire 1 | 11/06/1993 | 12/06/1993 | 9312140176 | <strong>Unit 1 Reactor Trip/Turbine Trip On Over Temperature Delta Temperature Resulting From An Equipment Failure (Inadvertent Action) Of The Emergency Trip Solenoid Due To An Unknown Cause.</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1993, at 0220:14, while operating in Mode 1 (Power Operation) at 100 percent power, Unit 1 experienced a Reactor Trip/Turbine Trip on Over Temperature Delta Temperature (OTDT). The initiating event was a large loss of turbine load caused by Turbine Governor and Interceptor Valve closure. The unit was stabilized in Mode 3 (Hot Standby) and an investigation into the cause of the valve closure was conducted. While a suspected cause was developed, it could not be confirmed. A decision was made to proceed with restart, and continue testing circuits monitoring generator and switchyard breaker position. During restart, a problem with the Interceptor valves was discovered. Both the Overspeed Protection Control (OPC) solenoid valves and a Train B Emergency Trip (ETC) solenoid valve were replaced and the Unit was returned to Mode 1 at 0405 on November 7, 1993. This event has been assigned a cause of Equipment Failure/Malfunction due to an unknown cause. Immediate corrective actions were to replace the three solenoid valves associated with the OPC header prior to returning the unit to service. Planned corrective actions include an evaluation of potential changes to the flush methods used on the Electro-Hydraulic High Pressure Fluid system. Also an evaluation of possible equipment modifications/replacements will be performed in conjunction with other problems identified with the OPC and ETC solenoid valves.
3691993010 | McGuire 1, McGuire 2 | 11/11/1993 | 12/11/1993 | 9312200202 | <strong>A Potential Exists For The Loss Of The Residual Heat Removal System As A Part Of The Emergency Core Cooling System Because Of A Design Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1993, Westinghouse issued a nuclear safety advisory letter concerning the operation of the Residual Heat Removal (ND) system as part of the Emergency Core Cooling System (ECCS). The letter addressed the potential for degradation of the ND pump performance due to vapor binding of the ND pump suction piping during accident conditions while the unit is in a normal startup sequence. Specifically, if the suction piping of the ND system is not cooled down prior to the system being removed from service, the piping may be voided when aligned for standby readiness. On October 8, 1993, Problem Investigation Process (PIP) 0-M93-0971 was initiated to address these concerns. On November 11, 1993, it was determined that the ND system had been past inoperable due to the postulated scenario. This scenario is possible during modes 3 (Hot Standby) and 4 (Hot Shutdown) if cooling of the ND pump suction piping is not performed. This event is assigned a cause of Design Deficiency due to the failure to consider the system/component interaction. Both units were in Mode 1 (Power Operation) at 100 percent power at the time of the event discovery. Corrective actions include procedural changes to ensure cooling of the suction piping prior to aligning for standby readiness.
3691993011 | McGuire 1 | 11/15/1993 | 12/16/1993 | 9403080044 | <strong>Unit 1 Diesel Generator 1B Was Past Inoperable Due An Equipment Malfunction Resulting In A Technical Specification Violation.</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1993, Instrumentation and Electrical (IAE) personnel were performing preventive maintenance (PM) on the Diesel Generator (DG) 1B Fuel oil Storage Tank level instrument 1FDLS5150. The PM required a calibration check of the level gauge. This work was performed according to procedures IP/0/B/3204/01A, FD (DG Fuel oil) System Storage Tank Level Indicator Calibration, and IP/0/A/3204/01, Calibration Procedure For Barton Model 288A And 289A D/P (Differential Pressure) Switch. At approximately 1200, it was determined by IAE personnel that the level gauge was out of tolerance, in a non-conservative direction. The fuel oil level was 4500 gallons below the Technical Specification (TS) required minimum of 39,500 gallons. On November 16, 1993, 7000 gallons of fuel oil was delivered and added to the 1B Fuel oil Storage Tank bringing the level in the tank above the required 39,500 gallons. This event has been assigned a cause of Equipment Failure/malfunction due to the malfunction of the 1B DG Fuel Oil Storage Tank gauge. Unit 1 was in Mode 1, Power Operation, at 100 percent at the time of this discovery. As a result of this event, Unit 1A and Unit 2A and 2B DG Fuel Oil Storage Tank gauges were checked. As part of the corrective actions, the DG fuel oil storage tank level gauges will be replaced on Units 1 and 2.
3691993012 | McGuire 1 | 12/06/1993 | 01/05/1994 | 9403230008 | <strong>Unit 1 Turbine Driven Auxiliary Feedwater Pump Automatically Started Because Of Inappropriate Actions.</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1993, while operating in Mode 1 (Power Operation) at 100 percent power, Unit 1 experienced an inadvertent Engineered Safety Features (ESF) actuation when the Turbine Driven Auxiliary Feedwater (TDCA) Pump automatically started. Operations personnel were performing a valve stroke timing test for valve 1CA-48B, CA Pump Number 1 To Steam Generator 1C Control, as required by procedure PT/1/A/4252/03B, CA Train B Valve Stroke Timing - Quarterly (TD Pump Flowpath). During performance of the procedure, Operations Technician A was placing a jumper on terminal B-21R in the CA Pump 1B Control Panel. Technician A inadvertently placed the jumper on terminal B-22R directly below terminal B-21R. When the jumper was placed on terminal B-22R, a path to ground was created and the control power fuses for the associated valves were blown. Loss of control power to these valves caused them to move and subsequently started the TDCA Pump. The ground path is speculated to have been initiated by an exposed wire end on the test lead used. Causes of Inappropriate Action have been assigned to this event. Planned corrective actions include the rework of test points to allow use of a safer type test lead, check of test leads and jumpers to assure good electrical integrity, and review of the circumstances of the event with appropriate personnel.
3701993001 | McGuire 2 | 02/22/1993 | 03/24/1993 | 9303290279 | <strong>A Unit 2 Manual Reactor Trip was Initiated as a Result of Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1993, at 0046, Unit 2 Control Room personnel reported hearing a sound resembling the 'harmonic vibrations' associated with the feedwater lines when operating at reduced load. The Senior Reactor Operator (SRO) directed the Reactor operator at the Controls (ROATC) to check the position of the Feedwater Control Valves. The ROATC discovered the Steam Generator (SG) 'C' feedwater flow was low and decreasing even though the controller output was increasing. A Turbine Generator load reduction was begun to compensate for the reduced feedwater flow. When the SG level approached the trip setpoint, the SRO instructed the ROATC to manually trip the Reactor which in turn caused an automatic Turbine trip. Subsequent investigation revealed that valve 2CF-20 (SG 'C' Feedwater Control Valve) failed to open on demand due to a signal air leak in the valve positioner pneumatic relay. Unit 2 was operating in Mode 1 (Power Operation) at 100 percent power at the time of the event. A cause of Equipment Failure has been assigned to this event. Corrective actions include replacement of all Feedwater Control Valve positioner pneumatic relays. In addition, a group of Nuclear Generation Department personnel previously working with the Secondary Valve Reliability Team are accelerating their review of problems associated with the Feedwater Control Valves in order to identify and correct the underlying causes.
3701993002 | McGuire 2 | 03/09/1993 | 04/05/1993 | 9304060158 | <strong>A Unit 2 Manual Reactor Trip was Initiated Due to an Equipment Failure.</strong><br /><i>Abstract:&nbsp;</i>A Unit 2 manual Reactor Trip was initiated by Operations Control Room Personnel after receipt of alarms indicating a low and decreasing feedwater (CF) flow to Steam Generator (SG) 2B. Control Room personnel assumed manual control of valve 2CF-23, Steam Generator 2B Main Feedwater Control Valve, and attempted to increase CF flow to SG 2B. The attempt was unsuccessful. As the SG water level approached 45 percent, the Senior Reactor Operator instructed the Reactor Operator at the Controls to manually exercise Reactor Trip Breakers A and B. The Reactor was tripped at 0416 on March 9, 1993. The manual Reactor trip was followed by an automatic Turbine Trip. Operations personnel immediately began recovery efforts. Unit 2 was operating in Mode 1 (Power Operation), at 100 percent power at the time of the event. An investigation revealed that the inner metallic bellows in the valve positioner relay for valve 2CF-23 failed as a result of fatigue cracking, causing the valve to close resulting in a loss of CF flow to SG 2B. Corrective actions included the replacement of all Unit 2 CF valve positioner relay bellows with relays which incorporate viton elastomer diaphragms as opposed to metallic bellows.
3701993003 | McGuire 2 | 03/22/1993 | 04/22/1993 | 9304280103 | <strong>A Manual Actuation of an ECCS Pump Due to a Leak on the Charging Header Caused by a Construction/Installation Deficiency and a Management Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1993, at 1450, Mechanical Maintenance shift personnel were attempting to repair a broken instrument hanger associated with the Chemical and Volume Control System charging header pressure instrument. The maintenance personnel were working under work order 93003839, task 2. This task required the instrument root valve to be isolated, prior to the work being performed. This was not done. During the work, a 1/2 inch Parker Hannifin instrument tube fitting failed which created a leak of approximately 80 gallons per minute. Operations personnel implemented procedure AP/2/A/5000/10, NC System Leakage Within The Capabilities Of The Charging Pump, to respond to the leak. The leak was isolated by a Radiation Protection Specialist, within 13 minutes. Due to indications found during repair of the failed fitting, this event is assigned a cause of Construction/Installation Deficiency, because the fitting was not properly swaged. This event is also assigned a cause of Management/Quality Assurance Deficiency due to the breakdown in the work control process, and a cause of Improper Action. The immediate corrective action for this event was to have Instrument and Electrical personnel repair the leak. Additionally, a team of Station Management personnel assembled to define and identify the process to determine whether this event may indicate a generic station problem with compression fittings. Unit 2 was operating in MODE 1 (POWER OPERATION) at 100 percent power at the time of the event. This event is reportable due to the manual starting of a Charging Pump.
3701993004 | McGuire 2 | 07/25/1993 | 08/24/1993 | 9308300341 | <strong>A Technical Specification Was Violated As A Result Of The Past Inoperability Of Valve 2RV-80B Due To An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1993, Operations test personnel performed procedure PT/2/A/4200/01C, isolation Valve Leak Rate Test, on containment penetration M385, as required by Surveillance Requirement 4.6.1.2, of Technical Specification 3/4.6.1. When Operations test personnel attempted to pressurize the penetration volume, isolated by valve 2RV-79A, Upper Containment Ventilation (VU) Supply Containment Isolation Outside, and valve 2RV-80B, VU Supply Containment Isolation Inside, test results indicated leakage. Work orders (WOs) 93052735 and 93052737 were issued on valves 2RV-79A and 2RV-80B, respectively, to investigate the source of the problem. It was determined by Mechanical Maintenance personnel that the problem existed with valve 2RV-80B. Maintenance personnel discovered the travel stop bushing had been covered with insulation material and tape to avoid personnel injury, thereby preventing the valve from completely closing. The insulation material and tape were removed and the leak test was successfully performed. Unit 2 was in Mode 6 (Refueling) at the time of this event. This event has been assigned a cause of Inappropriate Action because the action taken by station personnel to avoid personnel injury was not the best alternative. System Engineering personnel will evaluate placing a stem cap on valve 2RV-80B. System Engineering personnel will also take the lead in arranging for valve 2RV-80B to have caution stripes painted on the non-moving parts of the actuator, to alert station personnel of the potential safety hazard.
3701993005 | McGuire 2 | 07/31/1993 | 08/30/1993 | 9309090003 | <strong>Initiation Of A Blackout Signal Resulting In An Emergency Safety Features Actuation Resulting From An Inappropriate Action.</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1993, Operations (Ops) personnel attempted to reinstall a potential transformer (PT) fuse associated with the Unit 2 Train B 4.16KV Emergency Power Source. While trying to install the fuse it broke and a replacement fuse was not available. A decision was made to substitute a 1 Amp fuse in the interim for the required .5 Amp fuse to facilitate Diesel Generator break-in runs. Work Order (WO) 93053534 was written to get the 1 Amp fuse installed and have it replaced with the correct size fuse when received. When the correct size fuse was received, Ops personnel replaced it. While trying to complete the WO, the Instrumentation and Electrical Maintenance (IAE) Supervisor discovered the need for a Quality Control (QC) inspection. A Senior Reactor Operator (SRO), the IAE Supervisor, and a QC Inspector went to check the fuse and perform the required inspections. The SRO opened the wrong PT compartment simulating a Blackout signal thus initiating a Load Sequencer actuation. Unit 2 was in No Mode (all fuel removed from the core) at the time of this event. This event is assigned a cause of Inappropriate Action. This was due to Failure to Adhere to Policies, Directives, or Management Procedures and Lack of Attention to Detail. Corrective Actions include revising the drawings to clearly indicate the PT's location, installing better labels on the compartments, communicating the event to Station Personnel emphasizing the need for Self Verification and good communication, and defining the roles of Ops and IAE as it relates to operations versus maintenance.
3701993006 | McGuire 2 | 08/30/1993 | 09/30/1993 | 9310040289 | <strong>A Unit 2 Secondary Side Steam Generator Leak Caused an Increase in Lower Containment Pressure Which Resulted in s Technical Specification Required Shutdown snd Subsequent Engineered Safety Features Actuation snd Inadvertent Mode Change</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1993, at 0030 with Unit 2 in Mode 3 (Hot Standby) at full temperature and pressure, a vendor attempted to repair a pipe cap leak downstream of Steam Generator 2A Shell Drain Valve. While attempting to remove the pipe cap in a controlled manner, the pipe cap blew off resulting in a significant discharge of feedwater and slight burns to the back of one vendor employee's legs. Lower Containment pressure increased to approximately 0.45 psig. Almost immediately, the Lower Ice Condenser Inlet Doors opened, as designed, allowing the steam to pass through the ice, and limiting the pressure. The temperature of the primary system was lowered to Mode 4 (Hot Shutdown) in an attempt to reduce the leak to a point at which it could be capped. After achieving Mode 4, the primary system temperature was improperly allowed to rise. This caused the unit to change from Mode 4 to Mode 3. The ejection of the pipe cap is assigned a cause of Inattention To Detail due to incorrect reassembly of a valve following maintenance, and Failure to Follow Procedures due to improperly performing a post maintenance test. The inadvertent mode change is assigned a cause of Inappropriate Action due to the operator failing to recognize the approach to the Mode 3 temperature limit and not taking the necessary actions to prevent re-entering Mode 3.
3701993007 | McGuire 2 | 09/27/1993 | 10/27/1993 | 9311020036 | <strong>Unit 2 Shutdown Because of Unidentified Reactor Coolant System Leakage Greater Than Technical Specification Limits Caused By Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1993, at 1640, an Unusual Event was declared and Unit 2 commenced load reduction to comply with Technical specification 3.4.6.2, Reactor Coolant System Operational Leakage. Leakage calculations indicated that unidentified leakage was greater than 1 gallon per minute (GPM). Appropriate notifications were made as specified by procedures RP/0/A/5700/01, Notification Of Unusual Event, and RP/0/A/5700/10, NRC Immediate Notification Requirements. Unit 2 entered Mode 3 (Hot Standby), at 1913. During a subsequent Reactor Building surveillance, valve 2NC-14, Reactor Coolant System Letdown to Regenerative Heat Exchanger Number 2, was found to have an approximate 0.5 GPM leak from the valve. An evaluation of the situation was conducted and a decision was made to commence cool down for entry into a previously planned Steam Generator tube repair outage. The necessary repairs to valve 2NC-14 were made during this outage. This event is assigned a cause of Equipment Failure. Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time the leakage was discovered.
3701993008 | McGuire 2 | 12/27/1993 | 01/26/1994 | 9402080199 | <strong>A Unit 2 Reactor Trip Occurred Due To A Loss Of Offsite Power Caused By A Possible Unanticipated Environmental Interaction, Vendor Fabrication Deficiency, Deficient Documentation, Inadequate Surveillance Program, And An Inappropriate Action.</strong><br /><i>Abstract:&nbsp;</i>On December 27, 1993, Unit 2 experienced a loss of bus line 2B due to a failed insulator. This was followed by a failure of the Unit 2 Turbine Generator to runback. Bus line 2A subsequently tripped on an overcurrent condition. A Reactor Trip occurred at 2207 due to a Power Range High Flux Rate Signal, followed by a Turbine Generator trip and the opening of the 2A Generator breaker. This resulted in a loss of Unit 2 offsite power. The subsequent cooldown resulted in a Safety Injection and Main Steam (SM) line isolation at 2214. Valve 2SM-5, SM Isolation Valve Steam Line B, failed to close fully, resulting in the 2B Steam Generator emptying. Control Room personnel declared an Unusual Event at 2222. As a conservative measure, OPS Control Room personnel activated the Technical Support Center, Operations Support Center, and staffed the Emergency Operations Facility. Offsite power was restored to Unit 2 at approximately 2343. Causes of Possible Unanticipated Environmental Interaction, Vendor Fabrication Deficiency, Deficient Documentation, Inadequate Surveillance Program, and Inappropriate Action are assigned to the event. Unit 2 was in Mode 1 (Power Operation) at 100 percent power, prior to the event. Corrective actions included repairs to the failed SM isolation valve and replacement of the failed bus line insulator. Unit 2 returned to Mode 2 (Startup) operation on January 6, 1994, at approximately 2200.
3731993001 | LaSalle 1 | 01/05/1993 | 02/04/1993 | 9302100442 | <strong>Instrument Spike With Resulting Division II Low Pressure Coolant Injection Pump Start And 1A Diesel Generator Start Due to A Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1993 Unit 1 was in Operational Condition 4 (Cold Shutdown). At 0809 hours during the performance of LaSalle Operating Procedure LOP-NB-01 'Reactor Vessel Leakage Test,' 1B and 1C Low Pressure Coolant Injection System (LPCI) (RH) (BO) pumps and 1A Diesel Generator (DG) [EK] received an automatic start signal. The cause of the initiation signal was a spike on an instrument with a common sensing line to level transmitters. The spike was large enough to cause the associated reactor vessel level instrumentation to actuate on low level 1 (-129' Reactor Water Level). <br /><br /> LPCI injection into the reactor did not occur because reactor pressure at the time of the event was 1040 psig, above the injection permissive setpoint for the Residual Heat Removal (RHR) Pumps. <br /><br /> The spike on the sensing line was created when an Instrument Maintenance (I.M.) Department Control System Technician (CST) returned to service a temporary gauge used for monitoring pressure during LOP-NB-01. <br /><br /> Immediate corrective action included the Nuclear Station Operator (NSO) verifying correct Reactor level and pressure for the present system configuration, resetting the initiation signals, and shutting down both LPCI Pumps and 1A DG. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature System.
3731993002 | LaSalle 1 | 01/26/1993 | 02/25/1993 | 9302250210 | <strong>Unit 1 Manual Scram Due To 'A' SRV Being Stuck Open Due To Duct Tape Being Over The Actuator's Air Valve Manifold Exhaust Port</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1993 Unit 1 was in Operational Mode 1 (Run) at 18 percent power. <br /><br /> During the performance of LaSalle Operating Department Surveillance, LOS-MS-R2, 'Main Steam Safety Relief Valve Manual Cycling Test for Conditions 1, 2 or 3', Unit 1 Safety Relief Valve (SRV) 'A' (EPN 1B21-F013A) failed to close when operated by the Nuclear Station Operator (NSO). Several attempts were made to close the SRV but were unsuccessful. Upon the Shift Engineer's authorization, the reactor was manually scrammed, per LaSalle Operating Abnormal Procedure LOA-NB-02, at 2320 hours. The reactor mode switch was placed into the Shutdown position and scram recovery actions were initiated. 'A' SRV closed at 2334 hours, with no deliberate NSO action. Reactor pressure, at this point, had decreased to 340 psig. Other procedural actions were then taken to place the reactor into a Cold Shutdown condition. <br /><br /> Subsequent investigations revealed that 'A' SRV was pneumatically locked into a partially open position. This was caused by duct tape blocking the pneumatic operator's Air Valve Manifold Exhaust Port. The SRV was able to open but air was not allowed to exhaust and therefore the SRV would not fully close. The duct tape eventually ripped away from the port, allowing air to exhaust and thus closing the SRV. <br /><br /> This event is reportable to the Nuclear Regulatory Commission per the requirements of 10CFR50.73(a)(2)(iv) any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature (ESF) and 10CFR50.73(a)(2)(i)(A) completion of any Nuclear Plant Shutdown required by Technical Specification.
3731993003 | LaSalle 1 | 01/29/1993 | 02/26/1993 | 9303020379 | <strong>Reactor Core Isolation Cooling System Barometric Condenser Condensate Pump Failure And Discharge Flow And Turbine Speed Problems</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1993, at 0505 hours, while Unit 1 was in Operational Condition 1 (Run), at 20% power, the Reactor Core Isolation Cooling Turbine (RCIC) Barometric Condenser Condensate Pump, 1E51-C004, failed during a planned RCIC System run per LaSalle Special Procedure, LLP-92-193. Uneven brush wear, overheating that caused a burnt brush contact surface, and heavy carbon-graphite film build-up found on the commutator caused the motor to stop running. The motor commutator was cleaned, the brushes were replaced, and the pump was then operated satisfactorily. <br /><br /> On January 30, 1993 at 1905 hours, following successful repairs to the RCIC Barometric Condenser Condensate Pump, the RCIC System was started and approximately twenty five minutes into the surveillance, the RCIC System experienced a sudden decrease in discharge flow, discharge pressure, and turbine speed. The cause was attributed to loose wire connections on the RCIC Ramp Generator Signal Converter Terminal. <br /><br /> The two connections at the Ramp Generator Terminal were fastened securely. The remaining cables at the Ramp Generator Terminal and the Electronic Control Box Terminal were verified to be fastened securely. <br /><br /> The RCIC System was re-started on January 31, 1993, and the system was returned to service on February 1, 1993, at 0330 hours.<br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3731993004 | LaSalle 1 | 02/10/1993 | 03/12/1993 | 9303170196 | <strong>Unit 1 Reactor Core Isolation Cooling Inoperable Due To The Inboard Isolation Valve Failure Due To A Breaker Trip On Thermal Overloads</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1993 Unit 1 was in operational condition 1 (Run) at 85% power following the fifth refueling outage. At 1650 hours, while attempting to open the Reactor Core Isolation Cooling System Inboard Isolation Valve 1E51-F063 its circuit breaker tripped on thermal overloads. This occurred during restoration of the RCIC System after preplanned preventative maintenance. <br /><br /> The RCIC Steam Line was isolated for planned maintenance which required the Inboard Steam Isolation Valve 1E51-F063 to be closed. When returning RCIC to normal, the 1E51-F063 breaker tripped on thermal overload when an open signal was sent to the valve. <br /><br /> The RCIC System was declared inoperable and containment integrity was maintained by closing the RCIC Outboard Isolation Valves 1E51-F008 and 1E51-F064 and taking them out of service. Unit 1 shutdown was initiated at 2000 hours on 02/13/93. <br /><br /> Maintenance Departments performed repairs to the valve and found a broken disc retainer pin. This was replaced, the valve was tested, and RCIC was declared operable. <br /><br /> A Generating Station Emergency Plan (GSEP) Unusual Event was declared at 2000 hours on 2/13/93 because of a unit shutdown due to Technical Specification 3.7.3. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function) and 10CFR50.73(a)(2)(i) due to the completion of a nuclear plant shutdown required by Technical Specification.
3731993005 | LaSalle 1 | 02/22/1993 | 03/24/1993 | 9303290172 | <strong>High Radiation Door Violation Due To Security Computer Problems</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1993 Unit 1 was in Operational Condition 1 (Run) at 87% power. Two High Radiation Doors, #52 and #213, were found to be unsecured (open). <br /><br /> On February 18, 1993 the Security Uninterruptabe Power Supply (UPS) was found on alternate power feed. Attempts were made to transfer back to the normal power supply. When this could not be accomplished a work request was generated to correct the problem. Troubleshooting per this work request revealed a blown fuse on the 'C' phase output of the static switch. <br /><br /> At approximately 1230 hours on February 22, 1993 Electrical Maintenance Department (EMD) replaced the fuse. After replacing the fuse, the UPS was re-energized and placed on normal supply per LOP-IS-01. The inverter carried the load for less than 5 seconds when the new fuse blew and the UPS auto-transferred to the alternate feed. Coincidental with the auto-transfer of the UPS, another fuse failed in a multiplexer cabinet. The multiplexers are "information hubs" between the door card readers and the Security Computer System. During this same time period several High Radiation Doors Alarmed on the Security Computer System. Security notified Radiation Protection (RP) Shift Supervisor, so the RP Department could physically verify the doors status. There was a communication problem and only 12 of the 14 doors that had alarmed were inspected. <br /><br /> At approximately 1511 hours a High Radiation Door was found to be unsecured and RP was contacted. This was Door 52 and was one of the 14 doors that had alarmed at 1230 hours but not verified closed. Door 52 was verified secured after the RP Technician ensured no one in the area. At 1705 hours Security questioned RP concerning the status of door 213 which was still in alarm status. The RP Department immediately responded, found the door opened slightly, and secured the door after verifying no one in the area. <br /><br /> The loss of control of a High Radiation Door is a violation of Technical Specification 6.1.1.2. This is reportable to the Nuclear Regulatory Commission as a Licensee Event Report pursuant to 10CFR50.73(a)(2)(i) due to a High Radiation Barrier being unsecured (condition prohibited by the plant's Technical Specifications).
3731993006 | LaSalle 1 | 02/16/1993 | 03/18/1993 | 9303220242 | <strong>Group 1 Isolation Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1993 Unit 1 was in operational condition 4 (Cold Shutdown) at 0% power. At 1452 hours a Group I isolation occurred due to the reinstallation of the Servo Amplifier Demodulator Indicator (SADI) Boards with low condenser vacuum condition, while the Main Turbine was reset and speed selected for 1800 rpm.<br /><br /> The Instrument Maintenance Department (IMD) was verifying the calibration of the Primary Speed Circuit Low Valve Gate per LIP-EH-24. A precaution of this procedure recommends removal of the SADI Boards per LIP-EH-28 "Methods of Preventing Valve Movement (EHC System)" in order to prevent undesired turbine valve movements. The procedures do not contain information concerning the potential of causing a Group I isolation. Following the completion of LIP-EH-24, the turbine is left in a reset condition with 1800 rpm selected and the SADI Boards removed. When the SADI Boards were installed with a speed selected, the associated turbine valves attempted to open. This resulted in a Group I isolation due to low condenser vacuum with turbine valves not full closed. Normally the EHC calibrations are performed during refuel outages where the Group I isolations are bypassed by operating procedures. The IMD Technicians, therefore, do not have to be concerned with generating isolation signals during the calibration. In this case, IMD was performing calibrations during a forced outage in which the isolations were not bypassed. <br /><br /> The cause of this event was inadequate directions within the procedure. The appropriate information was not contained in the procedure to ensure the turbine is tripped. The procedure will be revised. <br /><br /> This event is reportable as a License Event Report pursuant to 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature.
3731993007 | LaSalle 1 | 02/26/1993 | 03/26/1993 | 9303250077 | <strong>Unit 1 Reactor Core Isolation Cooling Inoperable Due To The Inboard Isolation Valve Failure Due To A Breaker Trip On Thermal Overloads</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1993 Unit 1 was in operational condition 1 (Run) at 100% power following the fifth refueling outage. At 1223 hours, while attempting to open the Reactor Core Isolation Cooling (RCIC)System Inboard Isolation Valve 1E51-F063 its circuit breaker tripped on thermal overloads. This occurred during testing of the RCIC 1E51-F063 valve. <br /><br /> The RCIC Steam Line testing was being performed to recreate conditions of the previous failure on February 10, 1993. The 1E51-F063 breaker tripped on thermal overload when an open signal was sent to the valve. <br /><br /> The RCIC System was declared inoperable and containment integrity was maintained by closing the RCIC Outboard Isolation Valves 1E51-F008 and 1E51-F064 and taking them out of service. Unit 1 shutdown was initiated at 2000 hours on 02/27/93. <br /><br /> The cause of this event was due to hydraulic lock in the bonnet of the 1E51-F063 valve. <br /><br /> Maintenance Departments performed repairs to the valve and replaced the broken disc retainer pin with a stronger material. Elimination of hydraulic lock was accomplished by the addition of holes drilled into the upstream disc. The valve was tested and RCIC was declared operable. <br /><br /> A Generating Station Emergency Plan (GSEP) Unusual Event was declared at 2000 hours on 2/27/93 because of a unit shutdown due to Technical Specification 3.7.3.<br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function) and 10CFR50.73(a)(2)(i) due to the completion of a nuclear plant shutdown required by Technical Specification.
3731993008 | LaSalle 1 | 03/07/1993 | 04/06/1993 | 9304120100 | <strong>Inadvertent Group 8 Isolation During Return to Service Due to A Reactor Core Isolation Cooling System Division 2 Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1993, Unit 1 was in Operational Condition 2 (Startup) at 0% power. At 0529 hours, the Reactor Core Isolation Cooling System (RCIC, RI) received a Division 2 (inboard) isolation signal on RCIC high stress line flow. At the time of the event, the RCIC Steam Line Inboard Isolation Warmup Bypass Valve 1E51-F076 was being throttled open to warm up the RCIC steam line. <br /><br /> The RCIC steam line isolation was not a valid high steam flow signal. Shortly after the Inboard Isolation Warmup Valve lifted off of its seat, a pressure increase occurred, and the Division 2 Inboard RCIC Steam Isolation Valves 1E51-F076 and 1E51-F063 received an isolation signal due to a high steam flow signal.<br /><br /> The Outboard Isolation Valve, 1E51-F008, was open at the time of the isolation signal, and it remained open during the isolation. LaSalle Special Test, LST-93-033, was being performed to verify operability of the Inboard Isolation Valve. RCIC System piping integrity was verified and the isolation logic was reset. Warming up of the RCIC System proceeded with no further incidents.<br /><br /> Because of the off-normal temperature and pressure of the RCIC Steam Line for performance of the special test at the time of the high steam flow instrument actuation, this incident is considered isolated and a recurrance should not occur.<br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature (ESF).
3731993009 | LaSalle 1 | 03/02/1993 | 03/31/1993 | 9303290295 | <strong>Fire Barrier Inoperable Greater Than Seven Days Due To Corebores Not Being Resealed</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 2, 1993 at 2145 hours with Unit 1 in Operational Condition 4 (Cold Shutdown), Operations personnel discovered three open corebore penetrations in the floor of the three Hour Fire Rated Assembly. The Floor Slab is located in the Balance-of-Plant Cable Area at elevation 731' Auxillary Building (AB) Fire Zone 5B13 and was found while performing general plant inspections. <br /><br /> The three six inch diameter corebores were drilled in order to run cables into the Demodulator Panel 1PLG3J. However, the corebores were never used or sealed. All cabling to the panel enters 1PLG3J from the top. These open corebores were not detected during the initial Unit I Fire Barrier Integrity Inspection because the corebores were concealed by a piece of material at the base of and inside panel 1PLG3J. Their location from the 710' Turbine Building (TB) elevation below (Fire Zone 5C11) is obstructed by cable trays and pipes. <br /><br /> An Hourly Fire Watch was established (Fire Impairment #50-93) at 2145 hours on March 2, 1993 in accordance with LaSalle Technical Specification 3.7.6. Work requst No. L21897 was written to have the corebores filled with grout. The corebores were sealed in accordance with this work request and the barrier was declared operable on March 8, 1993 at 0730 hours.<br /><br /> This event is reportable to the Nuclear Regulatory Commission as a Licensee Event Report pursuant to 10CFR50.73(a)(2)(i) due to the Fire Rated Assembly being inoperable (a condition prohibited by LaSalle Technical Specifications 3.7.6).
3731993010 | LaSalle 1 | 04/14/1993 | 05/14/1993 | 9305190310 | <strong>Diesel Generator Cooling Water Pump Automatically Tripped Due To Trainee's Unfamiliarity of Specific Equipment</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1993, Unit 1 was in Operational Condition 1 (Run) at 90 percent power. At 0843 hours, while starting the 1B Diesel Generator during LOS-DG-M3, '1B(2B) Diesel Generator Operability Test', the 1E22-C002 Diesel Generator (DG) Cooling Water Pump auto-tripped on magnetic overload. <br /><br /> The DG Cooling Water Pump automatically started when the DG speed increased above 150 rpm. While manually controlling engine speed per the surveillance procedure, the diesel engine speed dropped below the 150 rpm DG cooling water pump shutdown setpoint as a trainee pulled back on the injector control lever causing the DG Cooling Water Pump to shut off. The Diesel Generator speed was subsequently increased using the injector control lever, giving a second start signal to the cooling water pump Receipt of the start signal with the pump still coasting down caused excessive current inrush and the pump breaker tripped on magnetic overload. The 1B DG was shutdown.<br /><br /> The 1B DG and High Pressure Core Spray Systems were declared inoperable, and appropriate actions to meet Technical Specifications were initiated. <br /><br /> This Event is reportable per 10CFR50.73(a)(2)(v) due to the loss of a Safety System.
3731993011 | LaSalle 1 | 04/23/1993 | 05/21/1993 | 9305240332 | <strong>Manual Scram Due to Disconnected Linkage on Valve Positioner on a Heater Drain Valve</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993 Unit 1 was in Operational Condition 1 (Run) at 99 percent power. At 0833 hours, the '12A' Low Pressure Feedwater Heater (LP Heater) High Level Alarm was received in the Control Room, followed by auto isolation of the 'A' LP heater string. The loss of feedwater heater(s) procedure was entered and reactor power reduction to 900 MWe was immediately started.<br /><br /> At 0835, the '12C' and '12B' LP heaters alarmed on high level followed by auto isolation of the 'C' and 'B' strings. The LP heater bypass valve, 1CB007, was opened. In anticipation of a low reactor water level condition and the possibility of entering Reactor Instability Region, the Shift Engineer directed a manual scram. <br /><br /> Cause of the event was a disconnected feedback linkage on the 1HD065A valve positioner due to a loose jam nut. The exact cause of the jam nut not being tight is not known. <br /><br /> Instrument Maintenance training is being changed and a tailgate session will be conducted to include the lessons learned from this event. Air supply for the 11 and 12 heaters emergency drain valves has been isolated as an interim measure. A query will be made to the industry for similar events associated with this type and model control valve positioner. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) due to the manual scram.
3731993012 | LaSalle 1 | 07/02/1993 | 07/30/1993 | 9308030176 | <strong>Reactor Core Isolation Cooling System Declared Inoperable Due to Associated Bus Voltage Dropping Below Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1993, Unit 1 was in Operational Mode 1 (Run) at 99.7% power. At 1329 hours, a 250 VDC bus (121Y) undervoltage alarm was received. Locally, the 250 VDC battery charger (1DC03E) output was observed to have failed to zero (0) amps. <br /><br /> For the Reactor Core Isolation Cooling (RCIC, RI) System to be operable, Technical Specification 4.7.3.d.1.a requires the bus 121Y voltage to be greater than or equal to 250V and that the battery charger be operable. Since neither of these conditions were satisfied, the RCIC System was declared inoperable and a 14 day timeclock was started (per Technical Specification 3.7.3).<br /><br /> Locally, the 250 VDC battery charger timer was cycled. The charger output then returned to normal.<br /><br /> The cause of this event was loss of continuity of a timer contact on the 250 VDC battery charger. <br /><br /> System Engineering will investigate the feasibility of permanently bypassing the battery charger timer.<br /><br /> The safety consequences of this event were minimal, since the High Pressure Core Spray (HPCS) System was fully operational.
3731993013 | LaSalle 1 | 07/27/1993 | 08/16/1993 | 9308200110 | <strong>Primary Containment Isolation System Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1993 at 2010 hours Unit 1 was in Operational Condition 1, Run at 100% power when a partial Group 7 isolation was received. The isolation was the result of a failed coil in relay 1B21H-K78. <br /><br /> The failed coil caused the logic associated with the K78 relay to trip, generating the partial Group 7 isolation. The entire Group 7 isolation was not received due to electrical separation between the Inboard Isolation Logic and the Outboard Isolation Logic. <br /><br /> The safety consequences of the event were minimal. The Primary Containment Isolation System logic is normally energized, deenergize to actuate. When the coil failed, a short circuit was created which dropped logic voltage, deenergizing the logic.<br /><br /> Work Request L23678 was written and the failed relay was replaced and successfully functionally tested.
3731993014 | LaSalle 1, LaSalle 2 | 08/27/1993 | 09/24/1993 | 9309280086 | <strong>Lack of Automatic Trip of The Mechanical Vacuum Pump on Main Steam Line High Radiation Due To An Inadequate Pre- License Change Review</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1993, Units 1 and 2 were at full power (Unit 2 was in coast down at the end of Cycle 5). A 10 CFR 50.59 evaluation was performed to evaluate a pre-licensing change. This evaluation resulted in the identification of an Unreviewed Safety Question (USQ).<br /><br /> Determination of the USQ was based on a General Electric Co. (GE) analysis dated August 25, 1993. The GE Analysis indicated that the Standard Review Plan (SRP) limits for dose consequences for the design basis control rod drop accident (CRDA) will be exceeded if the mechanical vacuum pump continues to run during the accident. <br /><br /> The only accident or transient which requires the Mechanical Vacuum Pump and associated isolation valve to trip on Main Steam Line high radiation is the control rod drop accident, because this action reduces the rate of activity release from the condenser to the environment following the accident. The safety significance of the lack of the mechanical vacuum trip since the licensing of LaSalle Units 1 and 2 is minimal because: <br /><br /> 1. The GE analysis verified that the CRDA dose consequences are less than 10CFR Part 100. <br /><br /> 2. Compensatory actions were implemented to immediately trip the Mechanical Vacuum Pump on Main Steam Line high radiation. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(ii)(B) due to a condition outside the design basis of the plant.
3731993015 | LaSalle 1, LaSalle 2 | 09/14/1993 | 10/12/1993 | 9310210020 | <strong>Unit 1 Scram and Loss of Off-Site Power Due to Bus Duct Water Intrusion</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1993 Unit 1 was in Operational Condition 1 (RUN) at 100% power. At 1147 hours the System Auxiliary Transformer (SAT) experienced a differential current auto-trip due to water intrusion in the 4.1 kV ductwork and a fast transfer of loads to the Unit Auxiliary Transformer (UAT) occurred. During the bus transient, the 4.1 kV bus experienced lower than normal voltage. This low voltage condition caused the Feedwater Control System for the 1B Turbine Driven Reactor Feed Pump (TDRFP) to lock up. This caused speed and flow to decrease to zero. The 1A TDRFP was unable to make up the loss in flow, and the reactor scrammed on low reactor water level. Following the Scram the UAT was lost when the Generator separated from the Grid. This resulted in a loss of offsite power. All three diesel generators auto started and picked up the busses.<br /><br /> Reactor water level was restored and controlled initially by Reactor Core Isolation Cooling (RCIC), and later by Low Pressure Core Spray (LPCS). Reactor pressure was controlled by RCIC and the Safety Relief Valves (SRV). Due to a failure of the 1B Reactor Protection System (RPS) Motor Generator isolations were unable to be recovered initially. The Unit was later placed in Cold Shutdown. <br /><br /> This event is being reported pursuant to: <br /> 1. 10CFR50.73(a)(2)(i)(B) due to not meeting the limiting condition of operation (LCO) of Technical Specification 3.4.4. <br /> 2. 10CFR50.73(a)(2)(i)(C) due to deviating from plants Technical Specifications per 50.54(x) when LaSalle General Plant Abnormal Procedures (LGA) LGA-CM-01 and LGA-VP-01 were invoked. <br /> 3. 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System (ESF) and the automatic actuation of RPS.
3731993016 | LaSalle 1 | 10/22/1993 | 11/19/1993 | 9312020177 | <strong>Reactor Core Isolation Cooling Declared Inoperable Due to Loss of Power to Governor Control</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1993 at 1157 hours the Reactor Core Isolation Cooling (RCIC)BN! System experienced a decrease in Electric Governor (EG-M) Control Voltage, and Ramp Generator Signal Converter (RGSC) Voltage. The change in EG-M Control and RGSC voltages led to a decrease in Pump Flow, Turbine Speed, and Pump Discharge Pressure. This transient occurred while RCIC was operating in the full flow test mode per LaSalle Operating Surveillance LOS-RI-Q5 "Reactor Core Isolation Cooling System Pump Operability, Valve InService Tests In Condition 1, 2, 3, and Cold Quick Start". Unit 1 was in Condition 1 at 100% power. RCIC was already inoperable due to surveillance testing. <br /><br /> A team was organized to determine the root cause for the system failure. The team members included personnel from the Instrument Maintenance Department, System Engineer, System Engineering Associates, and General Electric. <br /><br /> The root cause for the transient was determined to be tarnished contact surfaces of the Tracking Control Relay 1E51-AK049. <br /><br /> Consequences of this event were minimal since the High Pressure Core Spray, (HP)BG! and other Emergency Core Cooling Systems were fully operable. <br /><br /> Work Request 125278 was written and the Electrical Maintenance Department replaced the Tracking Control Relay 1E51-AK049. The RCIC System was re-started per LOS-RI-Q5, and operation continued successfully for 2 hours. The system was shutdown and RCIC was declared operable on 10/29/93 at 1024 hours. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety function).
3731993017 | LaSalle 1 | 10/27/1993 | 11/24/1993 | 9312020436 | <strong>Technical Specification Surveillance Not Performed Within Required 30 Days Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1993, Unit 1 was in Operational Condition 1 (Run) at 100%. At 0800 hours it was determined that a required Technical Specification Operating Surveillance LOS-PC-Q1, "Primary Containment Isolation Valves Operability Test and Inservice Inspection For Conditions 1, 2, and 3", was not performed within the required 30 days for 1RE026 valve. <br /><br /> The root cause of this event is personnel error. LaSalle Station Operating Department has a dedicated individual who is responsible for scheduling, updating, and tracking the completion of all required operating surveillances. Much of the scheduling is performed and tracked via a computer program. As an aid in scheduling future surveillances, the computer determines surveillance due and critical dates based on the start date of the last performed surveillance. The person entering the data inadvertently entered the finish date instead of the start date. Immediately upon the realization that the critical date had expired (approximately 0800 on 10/27/93), LOS-PC-Q1 was performed to stroke time the 1RE026. <br /><br /> Site Quality Verification (SQV) will perform an effectiveness review of the Surveillance Program to determine if previous corrective actions have been proper and effective. <br /><br /> Safety significance was minimal as Unit 1 Primary Containment integrity would have been assured in the event of an accident since this valve would have isolated well within the 15 second maximum closure time required by Technical Specifications. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i) due to a condition prohibited by the plant's Technical Specification.
3731993018 | LaSalle 1 | 12/05/1993 | 12/30/1993 | 9401120207 | <strong>Closure of Primary Containment Isolation Valves Due to A Failed Logic Card</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1993, at 1902 hours, a half scram and several expected isolations or half isolations occurred. At the time, both Reactor Protection System (RPS) buses were powered from their respective motor-generator (MG) sets.<br /><br /> The half scram was caused by a trip of an Electric Power Monitoring (EPM) Assembly for the 1A RPS MG set. The exact cause of the trip could not be determined due to indication failure on the EPM Assembly. After the 1 'A' RPS Bus was placed on its alternate supply, the half scram was successfully reset and all systems which isolated were placed back in service. <br /><br /> The cause was a failed logic card. A failure analysis on this card will be performed.<br /><br /> This event is being reported in accordance with the requirements of 10CFR50.73 (a) (2)(iv) due to the actuation of an Engineered Safety Feature (ESF).
3731993019 | LaSalle 1 | 12/04/1993 | 12/28/1993 | 9401100188 | <strong>Missed Technical Specification Surveillance Due to Misinterpretation</strong><br /><i>Abstract:&nbsp;</i>At 1715 hours on December 4, 1993, LaSalle County Station Unit 1 entered Technical Specification 3.4.2, Action a., due to the inoperability of two (2) Safety/Relief Valves (SRVs) 1B21-F013B and 1B21-F013J. Commonwealth Edison requested Enforcement Discretion from Technical Specification 4.0.3 for these SRVs to be granted to allow continued unit operation until approval of an exigent Technical Specification amendment. <br /><br /> The amendment requested that valves 1B21-F013B and 1B21-F013J be exempted from the requirements of Technical Specification 4.0.3 until the sixth refueling outage (L1R06) or the first Cold Shutdown prior to L1R06, whichever comes first. The two SRVs are scheduled to be setpoint tested during the sixth refueling outage. <br /><br /> Until these valves are setpoint tested, compensatory actions include operators being trained that the 2 SRV's safety mode actuations are potentially affected by setpoint drift. Steps are being taken to determine the correct ASME Section XI interpretation and revise any required programs or procedures. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) due to a missed Technical Specification Surveillance.
3731993020 | LaSalle 1, LaSalle 2 | 11/29/1993 | 12/28/1993 | 9401100011 | <strong>Unit 1 and 2 VR Containment Isolation Due to Loss of Reactor Protection System Bus Power</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1993 Unit 1 was in Operational Condition 1 (Run) and Unit 2 was in Operational Condition 4 (Cold Shutdown). At 0328 hours a half scram and several expected isotations or half isolations occurred on Unit 2. Additionally, the Reactor Building Systems Secondary Containment Isotation Dampers closed and the Standby Gas Treatment System autostarted on both units. At the time, the Unit 2 'A' Reactor Recirculation Pump was being started while the Unit 2 B Reactor Protection System (RPS) Bus was powered from the alternate power supply. <br /><br /> This half scram was caused by an uridervottage trip of an Electric Power Monitoring CEPM) assembly for the RPS alternate power supply. White transferring power to the normal RPS power supply at 0337 hours on November 29, 1993, a Unit 2 full scram was caused by overtravel of the RPS transfer switch with no subsequent effect on Unit 1. <br /><br /> The scram was successfully reset and all systems which isotated or auto-initiated were placed back in service.<br /><br /> This event is being reported in accordance with the requirements of IOCFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature (ESF).
3741993001 | LaSalle 2 | 02/22/1993 | 03/22/1993 | 9303230161 | <strong>RCIC High Flow Isolation Static-O-Ring (SOR) Failure Due To A Torn Diaphragm</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1993, at 0245 hours while Unit 2 was in Operational Condition 1 (Run) at 96% power, Reactor Core Isolation Cooling (RCIC) Steam Line High Flow Isolation Switch PDS 2E31-N013AA was found with an apparent ruptured diaphragm. The failure was found during the performance of LaSalle Special Test, LST-93-012, "Unit 2 Steam Line High Flow RCIC Isolation Calibration." <br /><br /> The switch functions to provide a Division 1 (Outboard) isolation of the RCIC Steam Line in the event of a high flow condition, which is an indication of a break in the RCIC Steam Line. The switch was rendered inoperable due to the diaphragm rupture, therefore the Division 1 isolation from this switch was not available. During this event the Division 2 (Inboard) isolation from PDS 2E31-N013BA was available and would have provided system isolation through the Inboard Isolation Valves 2E51-F063 and 2E51-F076. <br /><br /> The RCIC System was declared inoperable on February 22, 1993 at 1010 hours as a result of the failed differential pressure switch. The High Pressure Core Spray System was available throughout this event. <br /><br /> A replacement switch was characterized, installed, calibrated, and functionally tested satisfactorily. The RCIC System was declared operable February 23, 1993 at 1100 hours. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of safety system function). <br /> ?
3741993002 | LaSalle 2 | 02/23/1993 | 03/25/1993 | 9303290157 | <strong>Insufficient Flow of the Reactor Core Isolation Cooling System During Quartly Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1993 Unit 2 was in Operational Condition 1 (Run) at 100% power. At 1625 hours the Reactor Core Isolation Cooling (RCIC) System Turbine was started in accordance with LOS-RI-Q5, "Reactor Core Isolation Cooling System Pump Operability, Valve In Service Tests in Conditions 1, 2, & 3, and Cold Quick Start". Following a successful system startup, pump flow increased to 500 gpm and turbine speed to 3300 rpm, at 665 psig discharge pressure. The required system flow of 600 gpm could not be obtained. The system was declared inoperable and entered into the Degraded Equipment Log on February 23, 1993 at 2220 hours. The cause of the degraded flow and speed was attributed to an inoperable RCIC Turbine Control Box. <br /><br /> At the time the High Pressure Core Spray (HPCS) System and the other Emergency Core Cooling Systems (ECCS) were fully operable.<br /><br /> The RCIC System was immediately declared inoperable. There were no adverse consequences due to this event. The RCIC Turbine Control Box was replaced and LaSalle Special Test LST-92-185, "RCIC Control Calibration Test" was performed satisfactory. The RCIC System was restarted on February 24, 1993 per LaSalle Operating Procedure LOP-RI-06, "Controlled Start of the Reactor Core Isolation Cooling System in the CST Test Mode" to verify proper operation of the turbine controls. <br /><br /> The system was later tested successfully per LOS-RI-Q5. The RCIC system was returned to service on February 25, 1993 at 0245 hours. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3741993003 | LaSalle 2 | 05/24/1993 | 06/23/1993 | 9306300020 | <strong>Inadvertant ESF Actuations Due to Personnel Error During Performance of Instrument Surveillance</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1993 Unit 2 was in Operational Condition 1 (Run) at 100 percent power. At 0524 hours a Division 1 Emergency Core Cooling System (ECCS) Initiation Signal was received. <br /><br /> At the time of the initiation the Instrument Maintenance Department (IMD) was performing LIS-NB-404A 'Unit 2 Reactor Water Level 1 ECCS Division I Initiation and Level 2 RCIC Initiation Instrument Channels A & C Monthly Functional Test'. <br /><br /> The Unit 2 Low Pressure Core Spray Pump, the 2A Low Pressure Core Injection Pump, and the Unit 0 Emergency Diesel Generator automatically started due to the initiation. Due to plant conditions at the time of the event, the Unit 0 Emergency Diesel Generator did not load to the bus, nor did either the Unit 2 Low Pressure Core Spray Pump or 2A Low Pressure Core Injection Pump inject into the Reactor Vessel.<br /><br /> Immediate corrective actions were taken by the Operating Department to verify the initiation signal was invalid and to secure the involved plant equipment. An investigation was performed and the cause of this event was determined to be an inappropriate action taken by the Instrument Technician performing the LIS-NB-404A surveillance.<br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature (ESF).
3741993004 | LaSalle 2 | 06/04/1993 | 07/02/1993 | 9306300243 | <strong>Reactor Scram Due to Low Charging Header Pressure</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1993 Unit 2 was in Operation Condition 4 (Cold Shutdown) at 0% power. At 2037 hours the Operations Department was performing control rod cycling in preparation for startup when an unexpected Control Rod Drive (CRD) Low Charging Water Header Scram was received. <br /><br /> The Operations Department was in the process of replacing the CRD Pump Suction Filter. This process requires that the Standby Suction Filter be placed on-line prior to valving out the on-line Pump Suction Filter. Approximately five minutes -after placing the Standby Suction Filter on-line the CRD Drive Filter DP HI Alarm was received. One minute later the LO Charging Water Header A1/81 Scram Alarm was received followed by the LO Charging Water Header A2/62 Alarm. Since the mode switch was in REFUEL, ten seconds after receiving the A2/B2 LO Charging Water Header Alarm a SCRAM signal was generated. <br /><br /> The cause of this event is the mechanical process which allowed crud or foreign material to pass through the suction filter, and to be deposited on the drive filter. The crud deposit caused the filter to plug thus creating a large pressure drop. This pressure drop allowed pressure in the charging header to be reduced below the scram setpoint causing a reactor scram signal to be generated. <br /><br /> The main concern of this event is an operational concern that would arise if the filter element became detached as a result of this event. This investigation revealed that the drive filter while experiencing some degradation maintained it's integrity. The filter element was removed from it's casing and no evidence of disintegration of the filter element was observed. The process of cleaning and reusing the suction and drive filters will be examined for possible elimination. Also, station procedures will be revised to include steps for flushing the suction filter piping prior to bringing the standby filter on-line to eliminate crud build-up.
3741993005 | LaSalle 2, LaSalle 1 | 08/02/1993 | 08/26/1993 | 9309030366 | <strong>2A Diesel Generator Air Start System Below 200 PSIG Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1993 both Units 1 and 2 were in Operational Condition 1 (Run) at 100% power. At approximately 1401 hours the 2A Diesel Generator (DG)LC! Air Receivers were reported to be at 192 psig, which is below the Technical Specification requirement of 200 psig. The 2A DG was declared inoperable. The 1A DG had already been declared inoperable at 0545 hours on July 31, 1993, when it was removed from service for a planned bearing inspection of the DG Cooling Water Pump. <br /><br /> Since the Limiting Condition for Operation (LCO) for Technical Specification 3.8.1.1.b could not be met, Technical Specification 3.0.3 was entered.<br /><br /> An Equipment Operator (EO) was immediately dispatched to the 2A DG Room. At 1412 hours, the 2A DG Air Receivers were restored to a pressure greater than 200 psig. The 2A DG was declared operable at 1412 hours on August 2, 1993. Technical Specification 3.0.3 was exited within one hour so no power reduction was required. <br /><br /> The cause of this event was equipment failure of the 2A DG Discharge Relief Valve, 2DG048B and the 2A DG Starting Air Isolation Check Valve, 2DG049A. The safety significance of the event was minimal. <br /><br /> This event is reportable to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(v)(A) due to a decrease in safe shutdown capability.<br /> ?<br /> DOCUMENT ID 93
3741993006 | LaSalle 2, LaSalle 1 | 08/18/1993 | 09/14/1993 | 9309210225 | <strong>Diesel Generator Cooling Water Pump Breaker Failure Due to Unknown Reasons</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1993, at approximately 1930 hours with Unit 1 and Unit 2 in Operational Condition 1 (RUN) at 100% and 87% power respectively, the Unit 2 Nuclear Station Operator (NSO) was attempting to mix the Suppression Pool using the Low Pressure Core Spray (LPCS, LP)(BM) system per LaSalle Operating Procedure LOP-LP-04. The Suppression Pool temperature was elevated due to heat input from steam leaking past some Safety Relief Valves (SRV). When the LPCS Pump was manually started (and allowed to run 3 minutes), the Common Diesel Generator Cooling Water Pump failed to auto start as designed. The Common Diesel Generator Cooling Water Pump is part of the LPCS motor cooling and also provides cooling water for the area cooler for LPCS and RCIC. <br /><br /> One hour later the Cooling Water Pump was manually started from both Unit 1 and Unit 2 control circuits successfully. After initial troubleshooting was performed, the LPCS Pump was started and the Cooling Water Pump successfully auto started as expected. <br /><br /> Failure of the Cooling Water Pump to auto start could not be recreated. It is hypothesized that an auxiliary contact on the breaker had high resistance across one of the contacts. However, operation of the breaker prior to troubleshooting eliminated any evidence of the high resistance, thus making it impossible to determine the root cause of breaker failure. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(v) due to loss of Unit 2 Reactor Core Isolation Cooling Systems.
3741993007 | LaSalle 2 | 09/01/1993 | 09/30/1993 | 9310060198 | <strong>Failure of SDV Level Transmitters to Meet Technical Specification LCO Due To A Procedure Missing Caution</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1993, at 1700 hours, with the Unit 2 Mode Switch in Run and reactor power at 81%, the LaSalle Instrument Maintenance Department was performing an Instrument Surveillance on the Control Rod Drive (CRD) Scram Discharge Volume (SDV) Level Transmitters when the transmitters were found to actuate outside of the Technical Specification Limiting Condition for Operation (LCO).<br /><br /> This was the first scheduled calibration surveillance performed after initial installation (February 1992). <br /><br /> The cause of the Level Transmitters being out of calibration was due to a column of trapped water in the sensing lines acting against the reference leg isolation diaphragm, which led to incorrect initial calibration after installation. The source of this trapped water was the hydrostatic testing performed on the newly installed instrument sensing elements of the SDV. <br /><br /> The safety consequences of this event is the loss of one set of redundant level switches on the SDV. These level switches provide the scram signal to the Reactor Protection System when the SDV fills up. <br /><br /> Immediate corrective actions were to calibrate the level transmitters to within the acceptable Technical Specification range. <br /><br /> To prevent recurrence LIS-RD-203 will be revised to verify that the SDV instrument reference leg is drained and vented prior to performance. <br /><br /> This is reportable pursuant to 10CFR50.73(a)(2)(vii) redundant equipment inoperable due to a safety system interaction.
3741993008 | LaSalle 2 | 10/22/1993 | 11/19/1993 | 9312020173 | <strong>Inadvertant ESF Actuations Due to Personnel Error During Performance of Instrument Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1993 at 2100 hours with Unit 2 in Operational Condition 5 (Refuel) and defueled, Instrument Maintenance (IM) Personnel were performing surveillance LIS-NB-216 'Low Pressure Excess Flow Check Valve Refuel Operability Test (EFCV)'. At approximately 2102 hours, a Division I Emergency Core Cooling System (ECCS) initiation signal was received and the Unit '0' Diesel Generator (0DG01K)(DG)[EK] automatically started. <br /><br /> Immediate corrective actions taken by the Operating Department were to verify that the initiation signal was invalid and to contact the IMD personnel working on LIS-NB-216 and instruct them to stop work. Operating Department secured the Unit '0' DG and closed injection valves 2E21-F005 (LP) (BM) and 2E21-F042A (RH) (BO). <br /><br /> The cause of the Division I ECCS initiation and the Unit '0' DG start was due to IMD Personnel error in testing EFCV 2B21-F382 instead of the correct EFCV 2B21-F380. <br /><br /> This event is reportable pursuant to 10CFR50.73 (a) (2) (iv) due to an automatic actuation of an Engineered Safety Feature.
3741993009 | LaSalle 2 | 12/24/1993 | 01/20/1994 | 9402020198 | <strong>Reactor Water Cleanup High Differential Flow Isolation Due To Filter/Demineralizer Operations During Startup</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1993, at 0520 hours Unit 2 was in Operational Condition 2 (Startup) at 1% power following a Maintenance outage. The Reactor moderator temperature was 317 degrees F and Reactor Water Level was being controlled using Reactor Water Cleanup (RWCU) System blowdown to the main condenser. <br /><br /> Operations personnel were in the process of placing a RWCU filter/demineralizer on line. As the Flow Control Valve for the 2B RWCU filter/demineralizer was opened, the RWCU System isolated on High Differential Flow. <br /><br /> Following the Primary Containment Isolation System (PCIS) Group V Isolation, Operations performed a system walkdown. There were no leaks or other system abnormalities identified during the walkdown. <br /><br /> The cause of the event was a High Differential Flow condition that occurred white placing the RWCU filter/demineralizer on line with Slowdown Flow going to the main condenser and the unit not at rated conditions. The High Differential Flow Instrument is calibrated for rated conditions. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv).
3741993010 | LaSalle 2 | 12/25/1993 | 01/19/1994 | 9402020206 | <strong>Reactor Core Isolation Cooling System Declared Inoperable Due To Loss Of Power From Malfunctioning Tracking Control Relay</strong><br /><i>Abstract:&nbsp;</i>On December 25, 1993, at 2250 hours, the Reactor Core Isolation Cooling (RCIC), 2E51-F045 Dynamic Votes Test was being performed to verify the closing capability of the RCIC Inboard and Outboard Testable Check Valves, 2E51-F066 and 2E51-F065 following a vessel injection, and full closure of the RCIC Steam Supply Valve, 2E51-F045, against rated vessel pressure. <br /><br /> Upon opening of Valve, 2E51-F045 and the RCIC Injection valve, 2E51-F013, an initial speed peek of approximately 1800 RPM, was observed. The turbine speed then decreased to 600 RPM, and remained at that value. Pump flow at the time of the event was less than 100 GPM. The required system flow of 600 GPM could not be obtained. An investigation was performed by System Engineering and General Electric.<br /><br /> The cause for Turbine Speed of 600 RPM and pump flow of less than 100 GPM was attributed to failure of the Tracking Control Relay 2E51-AK049. The relay contacts either did not close due to armature binding or closed but developed a high resistance that simulated an open circuit across the contacts. <br /><br /> During this event the High Pressure Core Spray (HPCS) System and the other Emergency Core Cooling Systems (ECCS) were fully operable.<br /><br /> Work requests were written for investigation and repair. Proper operation of the limit switch at the steam supply valve was verified and the Tracking Control Relay 2E51-AK049 was replaced. <br /><br /> The RCIC System was re-started per LOS-RI-Q5, and after successful completion of the surveillance, RCIC was declared operable on December 28, 1993, at 2000 hours. <br /><br /> This event is reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73 (a)(2)(v) due to RCIC being declared inoperable (loss of a safety system function).
3821993001 | Waterford 3 | 03/04/1993 | 04/01/1993 | 9304260241 | <strong>Rx Trip Caused by Age-Related Loss of Inverter and Protection System Power Supply</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1993 at 2045, Waterford 3 was operating at 100% power when a reactor trip occurred as a result of two nearly simultaneous power supply failures. The failures deenergized elements of two channels of the Plant Protection System (PPS) which satisfied the coincidence logic and resulted in the reactor trip. <br /><br /> The first failure appears to be the result of age-related degradation of a frequency detection card in a static uninterruptible power supply. The second power supply was lost when its supply breaker opened during the subsequent electrical transient. Further analysis indicates that several of the power supply output capacitors were degraded.<br /><br /> In addition to replacing failed components, corrective action will include review of other applications of this equipment and the addition of periodic checks to identify power supply degradation. Since the PPS "failed safe," as expected, and generated the required reactor trip, this event posed no risk to the health and safety of the public.
3821993002 | Waterford 3 | 06/15/1993 | 07/15/1993 | 9307200258 | <strong>Reactor Trip Caused By Failure of FWCS Feed Flow Square Root Extractor</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1993, at 1604 hours, Waterford 3 was operating in Mode 1 at 100% power when the reactor tripped due to a high Steam Generator level caused by the failure of the Feedwater Control System (FWCS). <br /><br /> The root cause of this event was the failure of the square root extractor in the feedwater flow circuit for FWCS #1. The failure caused calculated feedwater flow to drop to zero and generated a high demand signal from FWCS #1 which, in turn, caused the #1 Feedwater Regulating Valve to go fully open and overfeed the #1 steam generator.<br /><br /> Corrective action for this event includes, in part, replacement and analysis of failed components, review of alarm set points (two expected alarms were not received during the event), operator training, and reevaluation of Feedwater Control System troubleshooting practices. This event posed no risk to the health and safety of the general public or plant personnel. Similar events include LER's 85-041, 87-008, 89-013, and 91-013.
3821993003 | Waterford 3 | 08/31/1993 | 10/01/1993 | 9310060346 | <strong>Dry Cooling Tower Sump Rad Monitor Setpoint Incorrect Due to Inadequate Shift Turnover</strong><br /><i>Abstract:&nbsp;</i>From August 31, 1993, to September 3, 1993, liquid waste containing Iodine 131 was intermittently released from Dry Cooling Tower Sump (DCTS) '1' to the 40 Arpent Canal. The associated radiation monitor high alarm setpoint was set higher than the setpoint allowed by the Offsite Dose Calculation Manual (ODCM). When radioactivity levels reached the ODCM allowed value, the release did not terminate automatically. However, a calculation was performed that provides reasonable assurance that the concentrations of radioactivity released did not exceed 10CFR20 limits. The root cause of this event is an inadequate shift turnover complicated by inappropriate assumptions by count room personnel. Count room personnel knew that the DCTS '1' waste contained Iodine 131 but took no action because they believed the waste was being sent to a waste tank. Interim measures were established to assure that DCTS releases are accomplished with an appropriate radiation monitor setpoint. The count room turnover procedure will be revised to provide additional instructions on the information that should be recorded in turnover documents. The health and safety of the public were not compromised during this event.
3821993004 | Waterford 3 | 09/13/1993 | 08/31/1994 | 9409060190 | <strong>Containment Spray Isolation Valve, CS-125A Failure to Stroke Open</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1993, it was discovered that the containment spray header isolation valve, CS-125A, would not open following an ESFAS subgroup relay surveillance. A high differential pressure was discovered to exist across the valve after a containment spray pump run. The failure to stroke was determined to be caused by a high differential pressure across the valve, created by a pressure surge on pump start. The pressure surge was caused, in part, by pockets of air entrained within the piping. This resulted in a condition whereby the valve would not open consistently. <br /><br /> Corrective actions for this event include, in part, analysis of the B train of containment spray and similar systems for applicability to this event, installation of additional vent valves on the A train of containment spray, venting of containment spray piping, and finally maintaining CS-125A in the open position, via Technical Specification Amendment 86 and appropriate procedural changes. This event posed no risk to the health and safety of the public.
3821993005 | Waterford 3 | 10/07/1993 | 11/08/1993 | 9311100306 | <strong>Motor Pinion Gear Keys For SDC Valves Not Staked Due To Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1993 at 1125, Waterford 3 was operating at 100% power when it was discovered that the second of two motor-operators for the shutdown cooling suction line isolation valves was not in the configuration specified by the actuator manufacturer because the key which connects the motor pinion gear to the motor shaft was not staked to the motor shaft as required. <br /><br /> This condition was the result of an inadequate procedure in that maintenance procedures did not contain the information provided by Limitorque in Maintenance Update 89-1. <br /><br /> Corrective action for this condition included staking the two motor pinion gear keys. In addition, appropriate procedures will be revised to require that the motor pinion gear key be staked to the motor shaft. <br /><br /> This event posed no risk to the health and safety of the public.
3821993006 | Waterford 3 | 10/19/1993 | 11/18/1993 | 9312010219 | <strong>TS 3.0.3 Entered Due to Both Wet Cooling Tower Water Basins Less Than 97% Full</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1993, at 1829 hours, Operations discovered that both Ultimate Heat Sink (UHS) Wet Cooling Tower (WCT) water basins were less than 97% full. In consequence, Operations declared both trains of UHS inoperable and entered Technical Specification (TS) 3.7.4b. Also, those systems affected by UHS were declared inoperable and their associated TS Action Statements entered per procedure. TS 3.0.3 was entered because the condition was not addressed by all of the associated action requirements. <br /><br /> The root cause of this event is failure to follow procedure in that Isolation Valve CMU-1131 was allowed to remain deviated open instead of locked closed. Operations closed CMU-1131 at 1842 hours. By 1858 hours the level in WCT water basin 'A' had been restored to greater than 97% full and TS 3.0.3 was exited. Shift Supervisors will brief their shifts on this event. Operations will develop a Case Study on this event that stresses procedural compliance expectations. WCT Basin Hi Alarms will no longer annunciate in the control room. This event did not compromise the health and safety of the public.
3821993007 | Waterford 3 | 12/07/1993 | 01/06/1994 | 9401120273 | <strong>Chemistry Samples Not Analyzed Due To Procedural Non- Compliance</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1993, Waterford SES, Unit 3 was operating at 100% power when it was discovered that the Technical Specification (TS) Surveillance Requirement to analyze the Secondary Coolant System for specific activity had not been met within the specified periodicity. <br /><br /> The samples were analyzed at 1122 and 1139 and exceeded TS Requirements by 8 hours 3 minutes and 8 hours 17 minutes respectively. The root cause of this event is procedural non-compliance coupled with poor work practices by the Shift Chemistry Technician. <br /><br /> Corrective action includes training and counseling of the responsible Technician. The sample results indicated that no activity was present; therefore, this event did not compromise the public health and safety. Similar LERs include LER 87-030-01 and LER 88-007.
3821993008 | Waterford 3 | 12/08/1993 | 01/06/1994 | 9401120305 | <strong>TS 3.0.3 Entered Due to Zero Independent Essential Services Chilled Water Loops Operable</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1993, at 1209 hours, Essential Services Chilled Water (CHW) Chiller 'A' tripped. At that time, Chillers 'AB' and 'B,' the 'B' Train of CHW, and those systems affected by that train were inoperable. As a result, Operations declared the 'A' Train of CHW and those systems affected by that train inoperable and entered their associated Technical Specification (TS) Action Statements. Concurrently, TS 3.0.3 was entered because the Technical Specifications do not provide explicit action requirements when two trains of CHW are inoperable. The plant was in TS 3.0.3 for approximately 59 minutes. <br /><br /> Given that Chiller 'B' was out of service, the root cause of this event is that Chiller 'A' tripped when a loose connection caused CHW Pump 'A' to trip on motor overloads. The 'B' Train was out of service at the time to repair a large refrigerant leak on Chiller 'B.' A contributing cause is that Chiller 'AB' was inoperable due to a cycle timer failure. The cycle timer was replaced. The appropriate procedure will be revised to accentuate tightness checks on the connections between the CHW pump motor starter and the overload block. This event did not compromise the health and safety of the public.
3821993009 | Waterford 3 | 11/15/1993 | 01/18/1994 | 9401260153 | <strong>PSV Setpoints Found Out of Tolerance Due to Errors Introduced When Establishing Setpoints</strong><br /><i>Abstract:&nbsp;</i>On November 15 and 16, 1993, Waterford 3 was informed that off-site testing had revealed that the as-found setpoints of the two valves which had been installed as pressurizer safety valves during the fifth operating cycle were outside of the allowable tolerance (+/-1%). <br /><br /> Waterford 3 believes that this condition may have resulted from an inability to adequately control some of the many variables present in the pre-installation "jack-and-lap" process. Waterford 3 has revised the safety valve testing procedure to require steam set pressure verification when the jack-and-lap process is used. <br /><br /> Action to prevent recurrence of this event includes an evaluation of a change to the Waterford 3 Technical Specifications to increase the as-found setpoint tolerance to +/-3%. This event did not compromise the health and safety of the public or plant personnel. Previous occurrences of this condition are discussed in this report. There have been no similar LER's.
3821993010 | Waterford 3 | 12/18/1993 | 01/18/1994 | 9401250284 | <strong>Late in Conducting LCO Action for CEAC Out Of Service</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1993, Waterford SES Unit 3 was operating in Mode 1 at 100% power complying with Limiting Condition for Operation (LCO) ACTION 6.a of Table 3.3-1 for Technical Specification (TS) 3.3.1. The LCO was entered because one Control Element Assembly Calculator (CEAC) was inoperable. ACTION 6.a states that operation may continue for seven days provided that at least once per four hours each CEA is verified to be within seven inches of all other CEAs in its group. Operations had been performing this required action, but was 74 minutes late for one of the time intervals. Not taking action during the specified time interval resulted in a noncompliance with the TS per TS 3.0.2.<br /><br /> The root cause of this event was inadequate attention to detail. Corrective action for the event included immediately conducting the required action and debriefing of the parties involved in accordance with the Improving Human Performance Program. During the interval that the verification was late, it was determined that all of the applicable CEAs had not moved since the last verification. As a result, this event did not compromise the health and safety of the public. Similar LERs include 91-012 and 92-011.
3821993011 | Waterford 3 | 12/20/1993 | 01/19/1994 | 9401260131 | <strong>Two of Three CEA Position Indications Inoperable Due to Weak Man-Machine Interface</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1993 at 0705 Waterford 3 was operating at 100% power when it was discovered that CEA positions were not updating on the PMC. It was determined that this situation had existed since 1325 on December 19, 1993. Reed Switch Position Transmitter 1 (RSPT 1) for CEA 34 was declared inoperable on August 16, 1992, thus making 2 of 3 CEA position indicators for CEA 34 inoperable. After discovering this condition, Technical Specification 3.1.3.2 was entered and the multiplexor was checked and found to be operational. At 0724 a CEA Initialization was performed to reset the CEA values. At 0731, the PMC was verified to be updating CEA positions. <br /><br /> The root cause of this event is a weak man-machine interface in that, while performing a CEA initialization, the PMC displays updated CEA positions after they are entered leading the operators to believe that the process was completed successfully. <br /><br /> Corrective action for this event includes an enhancement to the PMC's CEA processing which will include an initialization flag check on 5 minute intervals. Additionally, operators will be trained on CEA initializations.
3871993001 | Susquehanna 1, Susquehanna 2 | 02/01/1993 | 03/03/1993 | 9303090499 | <strong>ESF Actuation Due to Electrical Transient When Radwaste Electrical Transformer Failed</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1993 at 1125 hours, with Unit 1 operating at 100% power in Condition 1 and Unit 2 in Condition 4, invalid ESF actuations occurred on both Units on the Containment Gas Analyzer and Containment Instrument Gas Systems. A Load Center Transformer OX340 underwent an electrical failure. As part of the electrical transient that followed, ESF actuations as well as other plant equipment was affected in both Units. Plant safety was not impaired by the ESF actuations or other effected equipment. The cause of the occurrence was attributed to water intrusion into the transformer enclosure. Condensation from an overhead HVAC duct migrated into the transformer enclosure and fell directly onto the transformer core and coils. The cause of the ESF actuations and other plant perturbations was the direct result of the electrical transient the OX340 failure induced on the 13.8 KV and 480 V electrical systems. The event was determined reportable per 10CFR50.73(a)(2)(iv) due to the unplanned ESF actuations. Electrical load centers and power supplies were cross-tied as necessary and the affected systems were restored. The transformer will be replaced and a moisture deflector or moisture barrier will be installed above the transformer to prevent future condensation intrusions. The HVAC process air data will be collected and evaluated to determine the cause of high humidity and subsequent condensation. There were no safety consequences or compromises to the health or safety of the public.
3871993002 | Susquehanna 1 | 01/22/1993 | 02/22/1993 | 9302250306 | <strong>Instrument Fitting Leak Repair Required Entry into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>At 1255 hours on January 22, 1993, with Unit 1 in Condition 1 at 100% power, repair of a leak on the valve manifold for reactor water level switch LIS-B21-1N031D necessitated entering Technical Specification LCO 3.0.3. The leaking fitting was on the reference leg side of the reactor water level instrument. Because of recent heightened awareness of the effects of reference leg leaks on reactor water level indication (Generic Letter 92-04) and radiological contamination concerns, the need to repair the leak and enter the LCO 3.0.3 ACTION was reinforced. LIS-B21-1N031D provides initiation signals to Core Spray Division II, Residual Heat Removal Low Pressure Coolant Injection (RHR LPCI) Division II, High Pressure Coolant Injection (HPCI), Automatic Depressurization System (ADS) and Reactor Core Isolation Cooling (RCIC; non-ECCS system). The ACTION of Technical Specification LCO 3.3.3.b requires that the associated inoperable trip system be placed in the tripped condition within 1 hour or declare the associated ECCS inoperable. Since placing the trip system in the tripped condition would result in the actuation of the ECCS systems, the associated ECCS systems were declared inoperable, which required entry into LCO 3.0.3 when the ECCS Technical Specification 3.5.1 actions could not be met. Repairs were made and LCO 3.0.3 was cleared at 1523 hours on January 22,1993.
3871993003 | Susquehanna 1, Susquehanna 2 | 03/29/1993 | 04/28/1993 | 9305070162 | <strong>Postulated Events Could Result in Exceeding the Plant's Electrical Design Basis</strong><br /><i>Abstract:&nbsp;</i>At 1000 hours on March 29, 1993, with Unit 1 in Condition 1 at 90% power and Unit 2 in Condition 1 at 100% power, engineering evaluations concluded that two postulated accident scenarios could render Class 1E equipment inoperable. Namely, the loss of one offsite power source prior to or concurrent with a specifically sized line break of either a main steam line or recirculation pump discharge line inside containment could have resulted in the overlapping starts of ECCS and other plant equipment. The overlapping starts of the equipment could suppress voltage long enough to result in transfer of Class 1E power from the remaining offsite power source to the Emergency Diesel Generators (EDG). Upon Class 1E power transfer to the EDGs, the Emergency Service Water Pumps, which supply cooling water to the EDGs and other safety-related equipment, would, trip and not automatically restart, per design. Since the design basis assumes no operator action for 10 minutes, degradation of the EDGs could have occurred. The postulated events represented a condition outside the design basis of the plant and were reported pursuant to 10CFR50.72. Action was taken to defeat the auto restart feature of the non-safety related load, thus eliminating the potential for the postulated events. Training describing the postulated scenarios, as well as the modification to defeat the auto restart feature of the non-safety related load, was completed for all on-shift licensed operations personnel. Further engineering evaluation subsequent to the 10CFR50.72 report concluded that the second postulated scenario did not result in the plant being in a condition outside its design basis.
3871993004 | Susquehanna 1 | 04/23/1993 | 05/19/1993 | 9305260168 | <strong>Isolation Logic Relay - Operation Prohibited by Technical Specification During Retest</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993, at 0810 hours with Unit 1 in Condition 1 at 100% power, Relay B21H-K51 was replaced in the Main Steam Isolation Valve logic due to possible failure. In order to perform the required functional and operability testing, the affected trip system was taken out of the tripped condition required by Technical Specification 3.3.2 Action Statement b. With the trip system out of the tripped condition, the Action Statement was no longer met and Technical Specification 3.0.3 was entered. Entry into Technical Specification 3.0.3 constitutes operation prohibited by the Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). Taking the trip system out of the tripped condition did not create a significant degradation in the Station's ability to protect the health and safety of the public. Changes with respect to Technical Specification 3.0.3 will be pursued as part of the NRC generic Technical Specification Improvement Program. A preventative maintenance procedure for that type of relay in the MSIV isolation logic will be developed.
3871993005 | Susquehanna 1 | 06/22/1993 | 07/16/1993 | 9307270031 | <strong>Fire Barrier Not Installed On Conduit As Required</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1993, with Unit 1 at 100% power, it was determined that a conduit requiring fire barrier wrap was not wrapped. The Technical Specification ACTION STATEMENT was entered and appropriate compensatory measures were taken. The cause of the conduit not being wrapped was an error on the drawing utilized to identify those conduits requiring wrapping. The error occurred during a design change package revision by the Architect/Engineer in 1980. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications in that the required ACTION STATEMENT had not been complied with for at least some periods of time during the past several years. This condition is considered an isolated occurrence with no generic implications. A plant modification has been initiated to wrap the subject conduit.
3871993006 | Susquehanna 1, Susquehanna 2 | 05/26/1993 | 06/25/1993 | 9306300203 | <strong>Failure To Correct Instrument Drift Condition Within Tech Spec Required Action Time</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1993, an evaluation of an Emergency Diesel Generator (EDG) fuel oil storage tank level instrument's location, function and tolerance, and a review of surveillance test documentation from December 19, 1991 through July 20, 1992 concluded that a noncompliance with the plant's Technical Specifications occurred. Namely, a calibration check performed on July 20, 1992, via a corrective maintenance work authorization, determined that the level indicating instrument for the 'C' EDG fuel oil storage tank had drifted in a nonconservative direction. The work authorization had been initiated on December 23, 1991 to investigate why a low level alarm was present when the tank level indicated greater than the low alarm level setpoint. Due to a lack of clear understanding of instrument design and tolerance, improper direction in the alarm response procedure, and improper prioritization by the work groups involved, the work authorization was not implemented until July 20, 1992. The evaluation concluded that several times during the period from December 19, 1991 to July 20, 1992, the fuel oil tank fuel volume may have been less than the Technical Specification required minimum volume by up to approximately 200 gallons. The instrument was recalibrated and verified to indicate properly. Training was conducted to stress the importance of timely identification and proper prioritization of plant problems. The associated alarm response procedure was revised to require the addition of fuel oil to the storage tank upon receipt of the low level alarm and operating procedures are being enhanced to provide clarification of actual levels when alarms are received and the margins to Tech Spec limits at those levels and to utilize the higher accuracy alarm instruments during tank filling evolutions.
3871993007 | Susquehanna 1, Susquehanna 2 | 06/11/1993 | 09/11/1995 | ML09152032 | <strong>Potential Plugging Of ECCS Suction Strainers By Containment Debris</strong><br /><i>Abstract:&nbsp;</i>A voluntary LER was initially submitted to provide the NRC with preliminary results of PP&L actions upon identification of the ECCS suction strainer issue. This supplement addresses PP&L's corrective actions to the concern. PP&L has assessed the impact on ECCS suction strainers of debris, corrosion products and fibrous materials that may become dislodged as a result of a pipe break in containment, and has confirmed the operability of the ECCS systems. This evaluation was performed under our Engineering Deficiency Report Program. Various sources of debris (fibrous insulation, coating material, corrosion products) existed in containment and could be drawn to the suction strainers of the ECCS pumps during inventory make-up and containment cooling functions. Many uncertainties were evaluated to assess this condition including: 1) pipe break cone of influence; 2) amount of insulation damage; 3) transport of material to wetwell; 4) insulation effects on strainer flow; and amount of other foreign material in the containment. Actions to address this concern included: removal of fibrous insulation from HELB areas, testing to characterize the debris threat to strainer blockage, reduction in the amount of unqualified paint in containment, quantification of corrosion products on the structural steel in the wetwell, and establishment of a comprehensive analysis of containment debris effects. Additionally, containment installation and coating procedures now contain requirements reducing the potential of ECCS suction strainer blockage.
3871993008 | Susquehanna 1 | 07/12/1993 | 11/02/1995 | 9511070250 | <strong>Reactor Scram Following Turbine Trip On High Vibration</strong><br /><i>Abstract:&nbsp;</i>At 1635 hours on July 12, 1993, with Unit 1 operating at 100% power, a reactor scram occurred, per design, when the Main Turbine tripped. All major equipment operated per design during the transient, Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The reactor scram was caused by a turbine control valve fast closure that resulted from a turbine master trip actuation. The turbine master trip was caused by Main Turbine high vibration as a result of failure of two turbine blades on the 'C' Low Pressure Turbine. The turbine blade failure was caused by electrical system torsional induced vibration. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned ESF actuation occurred when the RPS initiated an automatic reactor scram following turbine control valve fast closure with power greater than 24%. The plant was safely shut down and there were no safety consequences or compromise to public health or safety during this incident, nor would there have been under different initial operating conditions. This transient was within the bounds of a turbine trip as analyzed in Chapter 15 of the FSAR. Repairs were made to the turbine and an inertia ring was installed, at the manufacturer's recommendation, to minimize the potential for high cycle fatigue as a result of excited torsional vibrations. Subsequent inspections, testing, torsional test reports for both (Unit 1 and Unit 2) Susquehanna units and analytical results all reinforced the initial 8/12/93 root cause conclusion and the corrective actions taken.
3871993009 | Susquehanna 1 | 08/25/1993 | 09/20/1993 | 9309280142 | <strong>Unplanned ESF Actuation - Primary Containment Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>At 0015 hours on August 25, 1993, with Unit 1 in condition 4 at 0% power, a Drywell Vent primary containment isolation valve failed closed. Investigation revealed the cause of the event to be a failed solenoid on the valve actuator. The event was determined to constitute an unplanned ESF actuation and is reportable per 10CFR50.73(a)(2)(iv). No ESF logic was involved or challenged. The valve failed to the closed position which is the position required for it to fulfill its design safety function, had it been needed. Thus, there were no safety consequences or compromise to public health or safety. Further laboratory analysis was performed on the failed solenoid. The analysis concluded that the solenoid coil wire insulation had failed, resulting in the turns of the coil wire shorting together. This was the only such failure of a solenoid coil of this model installed at Susquehanna. The solenoid was replaced.
3871993010 | Susquehanna 1, Susquehanna 2 | 08/16/1993 | 09/13/1993 | 9309170085 | <strong>Loss Of Fire Detection/Suppression - Operation Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1993, a severe lightning storm in the area of the site caused numerous spurious alarms in the Simplex Fire Protection System and disabled a transponder which locked in two alarms and rendered the fire suppression system in two areas inoperable. With fire barriers already inoperable due to Thermo-lag fire rating issue (LER 92-015-00), continuous fire watches were required. Sufficient manpower was not available for all affected areas within one hour; thus, all available firewatch personnel were assigned roving fire watch duties. The cause of the event was an apparent lightning strike disabling a transponder card in the Simplex system. This event was determined to be reportable per 10CFR50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications in that the required action of establishing a continuous fire watch was not accomplished within one hour as required. The failed transponder card was replaced and system operability restored. Previous improvements to the system to minimize the effects of surges from lightning strikes have proven to be adequate since no similar events have occurred in the past several years.
3871993011 | Susquehanna 1, Susquehanna 2 | 09/12/1993 | 02/08/1996 | 9602150010 | <strong>1A201 4KV Bus Momentarily De-energized - Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1993, with Units 1 and 2 in Condition 1, an unplanned invalid ESF actuation occurred on Unit 1 when the 1A ESS bus momentarily de-energized during the monthly degraded voltage channel functional surveillance test. This power interruption resulted in the following actuations and isolations: 'A' Emergency Diesel Generator start, Division 1 RIPS 'A' 1/2 scram, Division 1 Nuclear Steam Supply System Shutoff isolation, Reactor Building Ventilation isolation and start of CREOASS and SBGT systems, and automatic swap from A to B of various operating equipment. System response was verified to be proper and once the bus was restored to its normal power supply, all affected equipment was restored to its normal alignment. No specific root cause could be determined. However, based on the investigation, it was most likely caused by a misoperation of one of three (or combination thereof) components in the undervoltage test circuit (i.e. test switch, blocking relay, or timing relay). This event was determined to be reportable per 10CFR50.73(a)(2)(iv) as an unplanned invalid ESF actuation. There were no safety consequences or compromises to the public health or safety during this event. The switch and relays were tested satisfactorily and the surveillance was re-performed satisfactorily. A modification to provide a positive means of confirming the blocking of a breaker trip signal prior to inserting the trip signal will be implemented on both Unit 1 and Unit 2.
3871993012 | Susquehanna 1 | 09/24/1993 | 10/25/1993 | 9311030356 | <strong>Operation Prohibited by Technical Specifications - Entry Into 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1993, at 0102 hours with Unit 1 at 100% power, Emergency Core Cooling Systems Low Reactor Pressure Permissive Switch (PIS-B21-1N021D) was found in the tripped condition with the low pressure side bellows leaking transducer fluid. This switch provides inputs to the Core Spray (CS) system and the Residual Heat Removal (RHR) system logics. Control Room Operators then reviewed the actuation logic for both systems and declared division II of Core Spray inoperable and division II of RHR Low Pressure Coolant Injection (LPCI) inoperable. Technical Specification 3.5.1 for Emergency Core Cooling Systems (ECCS) could not be met in this configuration and Technical Specification 3.0.3 was entered as a failure to meet LCO 3.5.1. Technical Specification 3.0.3 was entered as of the time of the failure of PIS-B21-1N021D. Power reduction toward Startup was commenced at 0255 hours. Efforts to replace switch PIS-B211N0321D were pursued concurrently with power reduction. The switch was replaced and successfully tested and returned to Operable prior to reaching the time limits in Technical Specification 3.0.3. At 0743 hours LCO 3.0.3 was exited and reduction of Reactor power was stopped at 23% power. The cause of the switch failure could not be determined at this time and will be returned to the manufacturer for further analysis. There was no compromise to the health and safety of the public due to this event.
3871993013 | Susquehanna 1 | 09/21/1993 | 10/20/1993 | 9310250295 | <strong>Unplanned ESF Actuation - Primary Containment Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>At 1750 hours on September 21, 1993, with Unit 1 operating at 100% power, the Reactor Core Isolation Cooling steam line isolated during the performance of excess flow check valve testing. RCIC was in a standby alignment at the time of the event. RCIC steam supply inboard isolation valve HV-149-F007 closed isolating the RCIC steam supply and generated a RCIC turbine trip signal closing the trip and throttle valve HV-150-012. All systems functioned as required following the instrument channel trip on logic 'B' high differential pressure which was being tested at the time of the event. RCIC was reset and was OPERABLE at 1803 hours. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned Engineered Safety Feature (ESF) actuation occurred when the RCIC steam line containment isolation valve automatically closed. The subject valve is used for primary containment isolation in the event of an accident. The valve automatically repositioned to the closed position which is the required position for it to fulfill its design safety function, had it been needed. There were no safety consequences or compromise to public health or safety during this incident, nor would there have been under different initial operating conditions. The most probable cause is believed to have been the repositioning of the applicable instrument isolation valves too rapidly during restoration from the test. The surveillance test was attempted again and was successfully completed at 2006 hours with no further problems. For added assurance, the surveillance was again performed on September 22, 1993 and the test was successfully completed at 0600 hours. As action to prevent recurrence, I&C personnel will review this event at a shop meeting with emphasis on the significance of proper instrument valving operations.
3871993014 | Susquehanna 1 | 09/28/1993 | 10/27/1993 | 9311030343 | <strong>Operation Prohibited by Plant's Technical Specification 3.9.1</strong><br /><i>Abstract:&nbsp;</i>At 0950 hours on September 28, 1993, with Unit 1 in Condition 5, Refueling, at 0% power, the Refuel position one-rod-out interlock was declared inoperable and Technical Specification Limiting Condition for Operation (LCO) 3.9.1 was entered for the purpose of performing Technical Specification Surveillance Requirement 4.9.1.2, one-rod-out interlock testing. Technical Specification 3.9.1 states that when the reactor mode switch is locked in the Refuel position, a control rod shall not be withdrawn unless the one-rod-out interlock is OPERABLE. However, in order to verify OPERABILITY of this interlock, a control rod must be withdrawn. Therefore, when the reactor mode switch was placed in the Refuel position and a control rod was withdrawn for performance of Surveillance Requirement 4.9.1.2 on September 28, 1993 in the Refueling condition, an operation prohibited by the plant's Technical Specifications occurred. The cause of this event was attributed to procedural non-compliance by Operations personnel. Inconsistencies between operating procedures and a structural inconsistency in Technical Specification 3.9.1, Reactor Mode Switch were contributing causes to this event. Corrective actions include: reviewing this event with all Operations personnel to emphasize the importance of procedural compliance; procedure revisions to ensure consistency; and pursuit of a change to Technical Specification 3.9.1 to relieve the inconsistency contained therein.
3871993015 | Susquehanna 1 | 10/05/1993 | 11/30/1993 | 9312090010 | <strong>Administratively Inoperable Refueling Platform Used to Move Fuel.</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1993, at approximately 1900 hours with Unit 1 at 0% power, it was determined that the Unit 1 Refueling Platform main hoist had been used to offload 38 fuel bundles from the Unit 1 Reactor while the main hoist interlocks were administratively inoperable. The above determination was made on 10/31/93 while Engineers were reviewing two previously issued Significant Operating Occurrence Reports. Main hoist interlocks were not tested immediately following the replacement of a grapple head rendering the main hoist administratively inoperable. The Unit 1 Refueling Platform main hoist loaded interlocks would have performed as required with the hoist loaded with a fuel assembly. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. Since the main hoist interlocks would have performed as needed when the main hoist was loaded with a fuel assembly, the condition did not create a degradation in the Station's ability to protect the health and safety of the public and/or plant personnel. Insufficient Operability testing that was chosen after replacing the grapple head was the cause of the event. Surveillance testing procedures and Refueling Platform work instructions have been revised. The event has been reviewed with appropriate personnel.
3871993016 | Susquehanna 1 | 11/05/1993 | 12/06/1993 | 9312140141 | <strong>Condition Prohibited By Plant's Technical Specifications Sections 4.9.1.2 and 4.9.1.3</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1993, with Unit 1 in Condition 5 at 0% power, Operations Support staff personnel discovered a surveillance inadequacy while revising a surveillance test procedure. Specifically, it was found that the procedure for verification of the reactor mode switch refuel position interlocks did not require that a second licensed operator (or other technically qualified Unit Staff member) verify that all control rods remained fully inserted when the mode switch was placed in the Startup position during performance of the test. Since the procedure did not require a second person verification, a second qualified person did not perform the verification. This constituted a condition prohibited by the plant's Technical Specifications. The cause of this incident was a procedural inadequacy caused by Operations support staff oversight at the time the surveillance test procedure was developed and during subsequent revisions. Although the exact cause for the oversight could not be determined, it is believed that a contributing causal factor was failure to verify that the surveillance procedure completely matched the scope of the Technical Specification requirements. The Unit 1 Surveillance procedures have been revised to require that a second licensed operator verify all control rods remain fully inserted while the mode switch is in the Startup position and training was conducted for Operations personnel. The respective Unit 2 surveillance test procedures will be similarly revised prior to the Unit 2 6th refuel outage scheduled to commence in March 1994. In addition, the checklist which is used when conducting reviews of surveillance procedure revisions will be enhanced to add a line item to verify that the procedure completely matches the scope of the Technical Specification requirements.
3881993001 | Susquehanna 2 | 01/14/1993 | 02/12/1993 | 9302180234 | <strong>Momentary Loss of 120 VAC Instrument Power Resulted in Invalid ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>At 0625 hours on January 14, 9 with Unit 2 in Condition 1 at 100% power, the alarm for Instrument AC Panel 2Y226 Power Failure was received in the control room. Approximately three to five minutes later, additional alarms and invalid Engineered Safety Feature (ESF) actuations occurred as containment isolations of the Reactor Water Cleanup System, 'B' Loop of Containment Atmosphere Control and Drywell Floor Drain Sump lines. Non-ESF trips of the 'B' Containment Hi Rad Monitor and the 'B1' Containment Rad Monitor Pump and an auto swap of the Containment Instrument Gas 150 pound header to its backup nitrogen bottles also occurred. The cause for the initial Instrument AC Panel 2Y226 Power Failure alarm and the momentary voltage dip to the subject loads on Panel 2Y226 was attributed to failure of a rectifier on the Loss of Voltage Relay located in Panel 2Y226, and was considered to be an isolated failure. The relay was replaced. System response to the momentary voltage dip of the 120 VAC power was per design and there were no safety consequences or compromise to public health or safety as a result of the event.
3881993002 | Susquehanna 2, Susquehanna 1 | 01/13/1993 | 02/11/1993 | 9302220256 | <strong>Fire Doors Inoperable - Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993, with Unit 2 in Condition 1, several fire doors failed the six-month surveillance procedure acceptance criteria due to excessive gaps around doors. It was determined that the timeliness in reporting these failures was not within the required time and that the gap deficiencies had existed for some time. In addition, four Technical Specification fire doors were not included in the daily and six-month surveillance procedures and thus were not surveilled. Appropriate LCO action statements were entered and compensatory fire watches were established. The causes of this event were personnel error, procedural inadequacy, and drawing discrepancies., This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications in that required LCO action was not taken within the allowed time frame for inoperable Technical Specification components and Technical Specification surveillances were not performed. The subject fire doors will be repaired. The six-month surveillance procedures have been revised to more clearly specify acceptance criteria as well as to more clearly identify notification requirements when inoperable fire doors are discovered. This revision also included adding the fire doors to the procedure which were not included during this procedure performance. The daily surveillance procedures and the drawing which lists fire doors will be revised to include these doors also.
3881993003 | Susquehanna 2 | 06/03/1993 | 07/01/1993 | 9307060309 | <strong>4.16KV Bus Undervoltage Relays Not Channel Checked</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1993, with both Units at 100% power, it was discovered that the Unit 1 4.16kv bus undervoltage relays were not channel checked while Unit 1 was in the defueled condition. Since the Unit 1 4.16kv buses supply Engineered Safety Feature (ESF) equipment common to both Units, Technical Specification Surveillance requirements 4.3.3.1-1, 5.b and 5.c were not being met for Unit 2 during those times when Unit I was defueled (2nd through 6th refueling outages) and Unit 2 was in conditions 1, 2, 3, 4 and 5. This condition is reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause of the condition was attributed to a procedural inadequacy with the Unit 1 Shiftly Surveillance Operating Log. The procedure did not recognize that the Unit 1 4.16kv bus undervoltage relays were required to be channel checked in the defueled condition for the common ESF equipment powered by those buses. This condition did not create a degradation in the Station's ability to protect the health and safety of the public. If the Unit 1 4.16kv buses would have experienced an undervoltage condition while Unit 1 was in the defueled condition, the Unit 1 relays would have functioned properly or Operations personnel would have become aware of the condition through other means. The Shiftly Surveillance Operating Log was revised to correct the condition. A review of Operations Unit specific surveillances that check common equipment will be conducted to ensure no other reportable conditions.
3881993004 | Susquehanna 2 | 05/24/1993 | 06/23/1993 | 9306290315 | <strong>Operability Testing Following Instrument Leak Repair Required Entry Into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1993, at 2305 hours, with Unit 2 in Condition 1 at 100% power, repairs were completed on a leaking fitting on the reference leg of reactor vessel level switch LIS-24221C. This level switch provides signals to the containment isolation logic for Drywell Cooling, Reactor Building Closed Cooling Water and Containment Instrument Gas systems. In order to perform the required functional and operability testing, the affected trip system was taken out of the tripped condition required by Technical Specification 3.3.2 ACTION b. With the trip system out of the tripped condition, ACTION b. was no longer met and Technical Specification 3.0.3 was entered. Entry into Technical Specification 3.0.3 constitutes an operation prohibited by the Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). Since redundant instrumentation for Drywell Cooling Isolation Logic remained operable, there were no safety consequences or compromise to public health or safety as a result of the entry into LCO 3.0.3. This condition was cleared following return of the switch to operable status. Changes with respect to Technical Specification 3.0.3 are being pursued as part of the NRC generic Technical Specification Improvement Program.
3881993005 | Susquehanna 2 | 09/08/1993 | 10/07/1993 | 9310130065 | <strong>Operation Prohibited By Technical Specification - Untimely Hydrogen Sample</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1993, at 1725 hours with Unit 2 in Condition 1 at 47% power, the required hydrogen sampling of the condenser offgas treatment system was not completed within four hours of the previous sample as required by Technical Specification 3.3.7.11 action 110. This Technical Specification requires grab samples to be collected at least once per 4 hours and analyzed within the following 4 hours when the required in-line hydrogen analyzers are inoperable and the main condenser offgas treatment system is in service. Eight grab samples of the offgas treatment system were satisfactorily taken and analyzed. The next sample was due at 1725 hours on 9/8/93 and the Chemistry Technician assigned to perform the sampling was unable to complete the task because a pressure indicator which is utilized to determine the sample volume was found inoperable. The failed pressure indicator was investigated and replaced. Additionally, Operations evaluated the offgas treatment system parameters and at 1855 hours on 9/8/93, the hydrogen analyzers were returned to operable status and action 110 of Technical Specification was exited. The cause of the pressure indicator failure was due to a loose connection within the indicator dial. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. This condition did not create a significant degradation in the Station's ability to protect the health and safety of the public. Actions to prevent recurrence include a comprehensive evaluation of the hydrogen analyzers and determining if improvements to the existing system can be made.
3881993006 | Susquehanna 2 | 11/06/1993 | 12/06/1993 | 9312160364 | <strong>Main Steam High Flow Switch Testing Required Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1993, at 1323 hours with Unit 2 in Condition 1 at 100% power, the 'A' Main Steam Line high flow switch (FIS-B21-2N006B) lower switch assembly was replaced due to erratic indication. During replacement of the flow switch lower switch assembly, the trip function of the switch was placed in the tripped condition. At 1437 hours, in order to perform the subsequent functional and operability testing, the affected trip function was removed from the tripped condition. Technical Specification 3.3.2 Action Statement b required that the inoperable channel be placed in the tripped condition within 1 hour. With the high flow switch administratively inoperable and the trip function not in the tripped condition, Action Statement 3.3.2.b was no longer met and Technical Specification 3.0.3 was entered. Entry into Technical Specification 3.0.3 constitutes an operation prohibited by the Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). The required Operability testing was completed and Technical Specification 3.0.3 was exited at 1450 hours on 11/06/93. Replacing the high flow switch lower switch assembly did not create a significant degradation in the Station's ability to protect the health and safety of the public. The lower switch assembly was found with a worn micro switch actuating arm roller. Changes with respect to Technical Specification 3.0.3 will be pursued as part of the NRC generic Technical Specification Improvement Program.
3881993007 | Susquehanna 2 | 11/10/1993 | 12/10/1993 | 9312160289 | <strong>Unplanned ESF Actuation Due to Spurious Auto-Transfer of HPCI Suction Valves</strong><br /><i>Abstract:&nbsp;</i>At 2127 hours on November 10, 1993, with Unit 2 in Condition 1 at 100% power, the High Pressure Coolant Injection (HPCI) system pump suction automatically swapped from the Condensate Storage Tank (CST) (normal suction) to the Suppression Pool during performance of Instrument and Controls (I&C) Section surveillance testing. All equipment functioned per design. No HPCI system initiation or injection occurred and no other system components were affected. The cause of this event was a procedure inadequacy. The surveillance test procedure did not provide adequate detail for lowering the water level in a float chamber-type level switch. This resulted in an I&C work crew (who had not previously performed this specific evolution) opening an instrument isolation valve to the Suppression Chamber to attempt to drain the float chamber, vice draining to a rad container via a test connection drain. When the isolation valve was opened, the combination of a high water level in the instrument being tested and a pressure differential between the Suppression Chamber and the instrument float chamber resulted in sufficient level increase in an adjacent instrument chamber (which is in parallel with the chamber of the instrument being tested) to cause the actuation. The HPCI system was restored to normal standby alignment. Corrective actions include revising the procedure to include necessary details for properly draining the instrument, reviewing the event with I&C personnel and reviewing similar, related procedures and adding additional details where appropriate.
3881993008 | Susquehanna 2, Susquehanna 1 | 11/24/1993 | 10/02/1996 | 9610070220 | <strong>Condition Prohibited By Plant's Technical Specifications Section 4.3.3 and 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1993 with Unit 2 in Condition 1 at 100% power and Unit 1 defueled in Condition 5 at 0% power, a review of degraded grid modifications and post-modification testing completed during the Unit 1 7th refueling outage was being performed. During this review it was discovered that the Unit 2 93% degraded grid auxiliary load shed signal to the Unit 1 auxiliary load shed circuitry had not been tested following completion of circuitry modifications during the current Unit 1 7th refueling outage. This resulted in Unit 2 having been operated in a condition prohibited by the Technical Specifications in that the portion of the 93% 4.16 KV ESS Bus undervoltage protection scheme which ties to Unit 1 had not been declared OPERABLE. Furthermore, since all four Unit 2 4.16 KV ESS Buses were affected, entry into LCO 3.0.3 was required for Unit 2 and this also constitutes a condition prohibited by the Technical Specifications. The cause of the event was related to programmatic deficiencies associated with the modification process. Actions to prevent recurrence include: a review of two modification procedures to assure appropriate involvement of System Engineering personnel in the modification process; issuance of a procedure to provide guidance to system engineers on their role and responsibilities during the modification process; a revision to a modification design specification that requires evaluation of Technical Specification impacts (not only Technical Specification changes) as a specific design consideration; and training that emphasizes the importance of Technical Specification reviews as part of the modification process.
3881993009 | Susquehanna 2 | 12/10/1993 | 01/10/1994 | 9401180101 | <strong>Unit Shutdown Due to Drywell Unidentified Leakage Exceeding Limits</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1993, at 0217 hours with Unit 2 in Condition 1 at 15% power, Unit 2 completed a shutdown required by the plants' Technical Specifications after unidentified Drywell leakage exceeded the Technical Specification 3.4.3.2 limit of five gallons per minute and the limit of two gallons per minute increase within any four hour time period. The cause of the event was due to leakage from a cracked Reactor Building Closed Cooling Water (RBCCW) pipe on the outlet from the internal heat exchanger of the 2A Reactor Recirculation Pump. The pipe crack occurred at a welded section of the pipe just above where the piping enters the 2A pump cover. The most probable cause for the pipe crack was determined to be fatigue coupled with a preferential galvanic corrosion of the weld area with respect to the base metal. In addition, the analyzed stresses were highest on the 2A outlet piping at the connection of the Reactor Recirculation Pump because of the piping support configuration. As a result of the cracked pipe, a weld - overlay of the cracked area was implemented and a pipe support was added to the RBCCW 2A Recirculation Pump heat exchanger outlet in order to reduce the stresses at the cracked area. This condition, however, did not create a significant degradation in the Station's ability to protect the health and safety of the public and/or plant personnel. The excessive Drywell leakage was not the result of primary coolant loss. The RBCCW leakage did not adversely affect the Reactor Recirculation pump/motor temperatures.
3891993001 | St. Lucie 2 | 01/08/1993 | 02/05/1993 | 9302110293 | <strong>Missed Surveillance for Safety Injection Tank Sampling Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 8, at 0500 a Reactor Control Operator (RCO) filled the 2A1, 2A2, and 2B2 Safety injection Tanks (SITs) and subsequently notified Chemistry. A Chemistry technician sampled two of the SITs per the required surveillance but failed to sample the third. On January 8,1993, at 2300 the Unit 2 Assistant Nuclear Plant Supervisor discovered that the sampling of the 2A1 Safety Injection Tank had not been performed by Chemistry within the required time interval after filling the tank. Using the 25% maximum allowable extension permitted by Technical Specification (TS) 4.0.2, the latest time at which the sampling could have been performed on time was January 8, at 1230. <br /><br /> The root cause of the event was personnel error by a Chemistry technician responsible for the sampling. When informed by Operations that specific SITs have been filled it is the responsibility of the Chemistry department personnel on shift to sample these SITs for the required boron concentration per TS 4.5.1.1.b. In addition, there was a failure on the part of the control room personnel to realize that one of the three filled SITs had not been sampled when Chemistry notified them that two SITs were within specification. <br /><br /> Corrective actions were; 1) Perform the 2A1 SIT surveillance. 2) Create a status board by which Chemistry can insure that the appropriate SITs have been sampled. 3) The Chemistry personnel involved were counselled. 4) Operations personnel have been counselled. 5) A Human Performance Evaluation System evaluation was subsequently conducted whose findings agree with this report.
3891993002 | St. Lucie 2 | 12/01/1992 | 02/26/1993 | 9303050185 | <strong>Missed Surveillance on Reactor Coolant System Pressure Isolation Check Valves Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 30, 1993 St. Lucie Unit 2 was in Mode 3 implementing the Plant Heatup Procedure OP 2-0030121. As part of this procedure, the Safety Injection (SI) headers were recirculated causing six Reactor Coolant System (RCS) pressure isolation check valves to be exercised. These valves are then required to be tested per Technical Specifications. The Technical Staff was advised of this and the valves were subsequently tested satisfactorily within the required time interval. A Technical Staff supervisor realized that there was not an adequate procedurally addressed method to ensure performance of surveillance requirements of this evolution during heatups. A review was initiated to address past startups to ensure this requirement had not been previously missed. On February 3, 1993 a Technical Staff pump and valve specialist performing the review discovered only two instances on 12/1/92 and 12/7/92 in which the required surveillances of the RCS pressure isolation check valves had not been performed within the appropriate time interval during past plant heatups. <br /><br /> The root cause of the missed surveillances was procedural deficiency. There was no note or caution in the Plant Heatup Procedure as exists in the Prestart Check-Off List on the necessity of testing the valves as required by Technical Specification 4.4.6.2.2.d. <br /><br /> The corrective actions were to ensure current surveillance requirements on the SI header check valves were met satisfactorily and to change the Plant Heatup Procedure OP 2-0030121 to identify the surveillance requirements following recirculation of the SI headers during plant heatup. This event is not applicable to Unit 1 due to differences in design.
3891993003 | St. Lucie 2 | 02/01/1993 | 03/03/1993 | 9303090376 | <strong>Discharge from the Safety Injection Tanks to the Reactor Coolant System due to Personnel Error while Shutdown.</strong><br /><i>Abstract:&nbsp;</i>On 1 February, 1993 St. Lucie Unit 2 was in Mode 5 and preparing for a normal plant cooldown and depressurization. Operations personnel were performing a stroke time test of the Safety Injection Tank (SIT) discharge valves. The SIT discharge valves were shut at the start of this test because the SITs are not required to be operable in Mode 5. After the stroke testing was complete the four SIT discharge valves were erroneously left open. When the Reactor Coolant System (RCS) was intentionally depressurized below the SIT pressure of 260 psia, approximately 2200 gallons of SIT inventory was transferred to the RCS. Operators noted the increase in pressurizer level and stopped the plant depressurization. The open SIT discharge valves were determined to be the cause, and they were shut and de-energized. The normal cooldown and depressurization was then completed. <br /><br /> The root cause of this event is personnel error. While cooling down and depressurizing the plant an operator erroneously placed the SIT discharge valves in a position contrary to that required by plant conditions. A contributing factor is that the cooldown and depressurization procedure was not specific on what was required for 'as left' valve position after the SIT valve test. <br /><br /> The corrective actions taken include: 1) to place the plant in the required condition by closing the SIT discharge valves, 2) update valve stroke data sheet to clarify which procedure is used for the valve position required after testing, 3) change the cooldown procedure to clarify the SIT discharge valves post test position, 4) Operations supervision counselled the personnel involved in this event on the importance of understanding plant conditions.
3891993004 | St. Lucie 2 | 03/02/1993 | 03/31/1993 | 9304060099 | <strong>Pressurizer Instrument Nozzle Leakage Due to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1993 utility personnel discovered water dripping onto the floor in containment near the pressurizer. Operations maintained the plant in Mode 5 with the pressurizer solid to determine the leakage source. A visual inspection revealed the four upper instrument nozzles were leaking at the entry fitting to the pressurizer. The scope of the investigation was expanded to include the lower instrument water space nozzles on the pressurizer as well as the Reactor Coolant System (RCS) hot leg nozzles as they were all part of an earlier replacement of the same heat number. No other instrument nozzles showed any indication of leakage. On March 4, 1993, following drain down of the pressurizer, work was begun to inspect the upper steam space instrument nozzles and pressure boundary welds in conjunction with the vendor, Combustion Engineering. Liquid Penetrant and Eddy Current Tests were performed on the nozzles and weld areas which revealed axial cracking in the four steam space nozzles extending into the surrounding weld area. <br /><br /> The root cause of leakage escaping from through wall cracks in the affected nozzles was diagnosed as Primary Water Stress Corrosion Cracking (PWSCC). The axial orientation of the cracks and their origination in the nozzle material is consistent with previous industry experience with Inconel 600 instrument nozzles. Cracking of this nature is not considered to present a significant safety risk due to slow rates of propagation and minimal expected leak rate. <br /><br /> The corrective actions were: 1) Replacement of the cracked nozzles with a material more resistant to PWSCC. 2) Performed a visual inspection of nozzles of the same heat number in the RCS. 3) Nuclear Engineering evaluated the life expectancy of the remaining nozzles to ensure adequacy for continued operation. 4) Future visual inspections of selected instrument nozzles will be performed.
3891993005 | St. Lucie 2 | 01/12/1993 | 04/18/1994 | 9404250003 | <strong>High Reactor Coolant Pump vibration resulting in a controlled Unit shutdown due to a cracked shaft</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1993, vibration levels began to increase on the 2A1 reactor coolant pump. The 1X (synchronous speed) and 2X (2 times synchronous speed) vibration levels increased at the upper motor, 1X and 2X phase angles wandered, and the orbit exhibited a non-uniform shaft rotation. Overall vibration levels continued to trend upwards. At 2315 on January 12th, a controlled plant shutdown was commenced at a vibration level of 15 mils and increasing. A root cause team was assembled and subsequently developed a detailed inspection plan. Disassembly of the reactor coolant pump and inspection of the pump shaft revealed two cracks just above the hydrostatic bearing. Upon replacement of the pump internals the 2A1 reactor coolant pump was restarted with satisfactory vibration readings. The unit was returned to Mode 1 on April 1, 1993. <br /><br /> The cause of the 2A1 reactor coolant pump high vibration was the result of a growing circumferential crack in the pump shaft. The root cause of the crack initiation was the use of seal injection on an idle reactor coolant pump. <br /><br /> The corrective actions as a result of this event were: 1) Unit 1 and Unit 2 operating and emergency procedures have been revised to limit the use of seal injection to Design Basis Events and isothermal conditions experienced during reactor coolant system fill and vent. 2) Replaced the motor rotor assembly on the 2A1 reactor coolant pump. 3) Replaced the motor upper radial bearing assembly (shoes, adjusting bolts), upper and lower thrust bearing shoes, reset the upper and lower radial and thrust bearing clearances. 4) Installed a new pump rotating element and seal. 5) The defective pump rotating element was sent to an off-site examination facility for non-destructive examination and subsequent metallurgical examination of the crack area. 6) New vibration probes were installed to monitor all Unit 1 and Unit 2 reactor coolant pump shafts. This voluntary Licensee Event Report is being submitted for industry informational purposes.
3891993006 | St. Lucie 2 | 05/13/1993 | 06/14/1993 | 9306160342 | <strong>Inadvertent Start of the 2B Emergency Diesel Generator During Safeguards Relay Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1993, at 1920 hours with Unit 2 in Mode 1 at 100% power, Instrument and Control (I&C) personnel were performing the 'Engineered Safeguards Relay Test' procedure OP 2-0400053 in coordination with the Unit 2 Operating crew. Operations had set up the initial test conditions including control isolation of the 2B Emergency Diesel Generator (EDG) from the Engineered Safety Features Actuation System (ESFAS). Instrument and Control technicians then connected a multifunction test meter across an ESFAS relay contact which provides an EDG start and injected a trip test signal to check this circuit's actuation. When the I&C supervisor did not obtain the desired results he informed the Assistant Nuclear Plant Supervisor that Operations personnel could 'reset' following the test. Operations restored the plant to normal including taking the EDG normal/isolate switches back to the normal position thereby unisolating the 2B EDG from the ESFAS. Approximately one minute later the 2B EDG started and performed as expected for an automatic safeguards actuation. The 2B EDG was immediately secured and the safeguards relay testing was stopped pending investigation of why the EDG had started. <br /><br /> The root cause of the unplanned start of the 2B EDG was due to personnel error. The I&C supervisor intended to perform the test again and only intended for Operations to reset the ESFAS signals to restore the initial test conditions. However, based on previous communications following each test, Operations understood the reset request as that the test was complete and that they could secure from the test conditions. A contributing factor was a lack of procedural guidance for repeating or securing the test conditions. <br /><br /> Corrective actions: 1) Personnel performing the test were counseled on communications. 2) The safeguards relay testing was completed satisfactorily.3) OP2-0400053 will be changed to ensure test equipment is removed prior to restoring plant equipment. 4) A Human Performance Enhancement Review was conducted and the conclusions incorporated in this report. 5) Training on this event will be provided for appropriate plant personnel.
3891993007 | St. Lucie 2 | 05/21/1993 | 03/16/1995 | 9503200203 | <strong>Manual Reactor Trip After Simultaneous Dropping of Control Element Assemblies due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1993, St. Lucie Unit 2 was manually tripped from 72% power by utility-licensed operators approximately ten seconds after seven Control Element Assemblies (CEA's) fully inserted into the core. The dropped CEAs were confirmed by the presence of rod bottom lights, CEA reed switch position transmitter indication, and decreasing reactor coolant system average coolant temperature. Standard Post Trip Actions were carried out and the unit was placed in a stable condition in Mode 3. <br /><br /> Initial investigation revealed that several CEA power supply breakers were open and/or fuses blown which was indicative of an electrical fault. Subsequently, two grounded CEA cables associated with CEA's 54 and 61 were discovered in electrical penetration D-1 to the containment shield building. The root cause of the electrical grounds was investigated and could not be confirmed. However, a probable failure scenario is that mechanical damage to the conductor's insulation occurred during the fabrication and/or installation of the conductor bundle. <br /><br /> Corrective Actions for this event: 1) Isolated grounded conductors in electrical penetration D-1 and relanded affected CEA cables to available spare penetration modules in penetration D-1, 2) Replaced the subgroup breaker associated with subgroup sixteen and individual disconnect breakers for CEA's 8, 54, 60, and 61, 3) Performed an Engineering Evaluation on multiple CEA drops and effects on Departure from Nucleate Boiling Ratio and Local Power Density which concluded that no Specified Acceptable Fuel Design Limits (SAFDL) were exceeded, 4) During the 1994 Unit 2 refueling outage, penetration D-1 was inspected, and the grounded modules were replaced. 5) A local leak rate test on penetration D-1 was performed with satisfactory results, and 6) The failed components were examined by the equipment vendor and an independent laboratory for root cause analysis.
3891993008 | St. Lucie 2 | 11/02/1993 | 12/01/1993 | 9312100179 | <strong>Manual Reactor Trip Due To High Gas Temperatures In The Main Generator Caused By A Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1993, St Lucie Unit 2 was in Mode 1, operating at 45% power. At 0443 hours the control room annunciator for the main generator hydrogen system panel actuated. Utility licensed operators checked the hydrogen gas temperatures and saw that the average cold gas temperature was increasing. Before any attempts to reduce the hydrogen gas temperatures could be initiated, the average cold gas temperature reached the limit in the off-normal procedure. At 0447 hours, in accordance with Off-Normal Operating Procedure 2-200030 'Main Generator', a manual reactor and turbine trip were initiated. Standard Post Trip Actions were performed as per EOP-1. Safety function status checks were performed as per EOP-2 Reactor Trip Recovery and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause for the increase in the main generator hydrogen gas temperatures was due to the operation of the turbine cooling water system with two turbine lube oil coolers lined up to receive turbine cooling water flow and only one turbine cooling water pump available. The turbine cooling water operating procedure permits the isolation of one lube oil cooler that is not in use to maximize flow to those cooling systems in service. Based on plant conditions at 45%, utility licensed operators decided to maintain both turbine lube oil coolers in service. <br /><br /> Corrective Actions for this event: 1) Plant personnel verified that the turbine lube oil cooling system configuration was the cause for the event by reproducing system conditions just prior to the trip. 2) Utility operators isolated a turbine lube oil cooler. 3) The generator vendor verified that the hydrogen gas temperatures experienced during this event would not adversely affect the main generator. 4) I&C verified that the turbine cooling water and component cooling water temperature control valves were operating properly. 5) The plant operating procedure will be enhanced to clarify requirements for operation of the turbine cooling water system.
3951993001 | Summer 1 | 01/12/1993 | 02/11/1993 | 9302180059 | <strong>Reactor Trip Due To High Positive Rate</strong><br /><i>Abstract:&nbsp;</i>At approximately 0854 on January 12, 1993, the reactor tripped from 100% power on positive flux rate on all four power range channels. With no work being performed on generator protective relays or in the switchyard, a generator backup auxiliary time delay relay spuriously actuated and opened the transformer high side oil circuit breaker (OCB 8902). When it opened, the generator was left supplying only the balance of plant (BOP) busses through the generator breaker. The instantaneous loss of load caused a rapid generator speed increase which resulted in bus frequency increasing to approximately 62.5 hertz. The reactor coolant pumps (RCP), powered from the BOP busses, increased reactor coolant system (RCS) flow. The increased flow caused a reduction core differential temperature, which increased core water density. This, combined with the large negative moderator temperature coefficient at end of life, caused a neutron flux increase and a reactor trip occurred. <br /><br /> The reactor protection system responded as designed. When the generator breaker opened with OCB 8902 already open, there was no backfeed available to the BOP busses and they were deenergized. At 1039 the BOP busses were reenergized. "A" RCP was started at 1113 terminating natural circulation of the RCS. <br /><br /> The cause of the spurious actuation of the generator backup auxiliary time delay relay is unknown; however, the auxiliary time delay relay, along with another relay of the same type, and the generator backup protection relays that feed a signal to the auxiliary time delay relay were replaced.
3951993002 | Summer 1 | 03/18/1993 | 09/27/1993 | 9310050259 | <strong>Steam Generator Tube Eddy Current Results - Category C-3 Applied</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1993, at approximately 1037 hours, the preliminary results of the seventh inservice eddy current examination of the Virgil C. Summer Nuclear Station Steam Generators (SGs) were obtained. The planned examinations included 100% of the available (i.e., unplugged) tubes in each SG hot leg tubesheet, utilizing Motorized Rotating Pancake Coil Eddy Current Testing. A 100% Bobbin Coil inspection of the full length tubing (Tube End Cold to Tube End Hot) was also performed. The results indicated that since more than 1% of the inspected tubes in each SG were defective, a C-3 inspection category, per Technical Specification 4.4.5.2, applied. When the first SG (SG B) entered Category C-3, a prompt notification was made to the NRC Operations Center in accordance with the requirements of Technical Specification 4.4.5.5.c and 10CFR50.72(b)(2)(i). <br /><br /> As a result of the inspections performed during the seventh refueling outage, plugs were installed as follows: SG A-181, SG B-255 and SG C-212. <br /><br /> The Category C-3 tube degradation is localized in the tubesheet area and is the result of Primary Water Stress Corrosion Cracking (PWSCC). In addition, a number of tubes experienced Outer Diameter Stress Corrosion Cracking (ODSCC) in the tube support and flow distribution baffle plate areas. Tube plugging was completed on April 9, 1993. Three tubes were pulled to confirm the degradation mechanism in the flow distribution baffle plate area. Extensive examination and analysis of the pulled tubes was then performed to determine the exact cause of the degradation.
3951993003 | Summer 1 | 06/28/1993 | 07/28/1993 | 9309090184 | <strong>Personnel Error Places Purge System Outside the Provisions of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1993, at 0440 hours, approval was granted by the control room to remove Atmospheric Radiation Monitor RMA-2 from service to allow the performance of preventive maintenance. A Removal and Restoration Checklist (R&R) was entered and logged in the control room documenting that RMA-2 was out of service. The status of RMA-2 was discussed and included as part of turnover to the oncoming shift which was completed at approximately 0730 hours. <br /><br /> Soon after turnover was completed, the Reactor Building pressure alarm annunciated indicating the pressure was approaching the low pressure limit allowed by Technical Specifications. At 0745, the control building operator opened purge supply valves PVG-6056 and 6057 and started purge supply fan XFN-95 to increase reactor building pressure without consulting System Operating Procedure (SOP) 114, Reactor Building Ventilation System. Shortly after the valves were opened, another control room operator noticed the valves were open and pointed out that the valves should be closed due to RMA-2 being out of service. The fan was stopped and the valves were closed at 0748. Action 17 of Table 3.3-3 states that plant operation may continue provided the containment purge and exhaust valves are maintained closed. Opening the valves with RMA-2 out of service constitutes operation outside the provisions of Technical Specifications. <br /><br /> Radiation levels inside containment were normal and remained steady during the three minutes the valves were opened. Therefore, this event resulted in no safety consequences. <br /><br /> Operations management has communicated to all operations personnel the importance of proper procedural usage and stressed the usage level requirements defined in Station Administrative Procedure (SAP) 123, Procedural Use and Adherence (Revision - 1).
3951993004 | Summer 1 | 06/29/1993 | 08/30/1993 | 9309130226 | <strong>Missed Surveillance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 0800 hours on June 29, 1993, Operations personnel identified a noncompliance with the surveillance requirements of Technical Specification 4.3.2.1, Table 4.3-2.2.b in that XVG03005B-SP had not been stroked from its associated relay during the performance of the required surveillance testing, due the lack of power available to the valve. The personnel involved failed to note this as a test discrepancy during the performance or review of this test. <br /><br /> Plant safety was not compromised by the missed surveillance. The appropriate procedure was performed on June 29, 1993, which confirmed that the valve was fully functional and capable of performing its intended safety function. <br /><br /> Operations personnel have taken part in a discussion of the importance of the post-test review process required and proper documentation of test discrepancies.
3951993005 | Summer 1 | 12/03/1993 | 12/30/1993 | 9401100051 | <strong>Partial Phase 'A' Containment Isolation Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1993, during the performance of B train Solid State Protection System (SSPS) slave relay testing in accordance with Surveillance Requirement 4.3.2.1 for ESF Actuating System instrumentation, a problem was identified when the slave relay continuity lamps failed to light. A Maintenance Work Request was generated. The troubleshooting plan called for the technician to place the test switch from the "test" position to the "operate" position to verify normal voltage. When the switch was cycled, an unexpected actuation of the slave relays caused a partial Phase 'A' containment isolation at 1143 hours. This actuation meets with the reportability requirements of 10CFR50.73(a)(2)(iv). <br /><br /> Operations personnel immediately contacted the technicians performing the troubleshooting and had them terminate further action while they restored the components which had activated during the partial Phase 'A' signal. <br /><br /> The partial Phase 'A' isolation did not affect the continued safe operation of the plant, and all components were restored to their normal state within approximately one hour. <br /><br /> Further investigation of this event has determined the SSPS drawing (1MS-42-036-27c-12), utilized in development of the troubleshooting plan, did not accurately reflect the present design of the SSPS. It appears that the design of the SSPS had been modified in 1984 without the proper revisions being made to impacted drawings. <br /><br /> Following this event, a detailed review was conducted of all modifications affecting SSPS. This review resulted in the identification of three drawings needing revision. This action was completed by December 6, 1993.
3971993001 | Columbia | 01/13/1993 | 05/11/1994 | 9406130009 | <strong>Inoperable Suppression Pool Cooling Due To Potential Waterhammer</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993, a Licensing Engineer determined that both trains of Suppression Pool Cooling (SPC) of the Residual Heat Removal (RHR) System (RHR "A" AND "B") were inoperable on August 6, 1990. This represented a condition that could have prevented the RHR System from performing its SPC, Suppression Pool Spray (SPS), and Drywell Spray (DWS), and Low Pressure Core Injection (LPCI) safety functions. On December 22, 1992, engineering evaluations concluded that water hammer could fail the train of RHR in SPC/SPS due to a Loss of Power (LOP) coincident with a Loss of Coolant Accident (LOCA). Further review revealed that both trains were again operated concurrently: once in 1991 and twice in 1992. Per the Emergency Plans, these incidents also represented Unusual Events (UE). <br /><br /> A night order was issued immediately to declare any loop of RHR in SPC or SPS mode inoperable and enter the appropriate Technical Specification Action Statements (TSAS). <br /><br /> The root causes included: 1) management methods that failed to identify this problem during review of a 1987 NRC Information Notice (IN), and 2) failure to follow procedures which led to inappropriate two train operation of SPC.
3971993002 | Columbia | 01/21/1993 | 06/11/1993 | ML09152050 | <strong>Reactor Scram Due To Low RPV Level As A Result Of Loss Of Reactor Feedwater Pump Caused By An Inadvertent Actuation Of The Deluge System</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1993, at 0948 hours, a low Reactor Pressure Vessel (RPV) level reactor scram was initiated by the Reactor Protection System (RPS) in response to an actual low water level condition. The low RPV level was caused by a 'high thrust bearing wear' trip of the Reactor Feedwater (RFW) Pump 1A turbine. The trip signal was generated as a result of wetted vibration sensing circuitry caused by an inadvertent actuation of the RFW Pump Room 'A' fire protection deluge system. The remaining RFW pump was unable to supply enough water to maintain RPV level above the reactor scram setpoint. This was due to the failure of the Reactor Recirculation (RRC) Pump Flow Control Valves to automatically reposition (runback) to reduce reactor power and steam flow to within the capacity of one RFW pump.<br /><br /> The immediate corrective action was prompt response by the Plant Operators to bring the plant to a safe shutdown condition in accordance with approved Plant Operating Procedures. <br /><br /> Three root causes for this event have been identified: <br /><br /> 1. Personnel/work practices error causing the inadvertent actuation of the RFW Pump Room 'A' fire protection deluge. <br /><br /> 2. Management methods/work organization planning effort in that there was no method in the painting prejob planning process to provide the painters with precautionary information relating to sensitive equipment.<br /><br /> 3. Plant equipment/design configuration and analysis error in that the RFW Pump Room fire protection manual discharge stations are not well suited for an industrial machinery environment. <br /><br /> This event posed no threat to the safety of the public or plant personnel.
3971993003 | Columbia | 01/21/1993 | 02/22/1993 | 9303020003 | <strong>Inadequate Coordination Of Primary Undervoltage Bus Transfer Logic And Overcurrent Protection Results In Potential Loss Of Offsite Power And Delayed Emergency Power Source Availability</strong><br /><i>Abstract:&nbsp;</i>At approximately 1215 hours on January 21, 1993, it was determined that a deficiency involving coordination of protective relays associated with the AC electrical distribution system could result in plant operation that was not within the plant design bases. Under certain AC electrical distribution system alignments a fault on either 4.16 KV vital bus could have resulted in unavailability of both offsite power sources and delayed powering of the nonfaulted 4.16 KV vital bus from its associated Emergency Diesel Generator (EDG). WNP-2 has not experienced a bus fault that resulted in a loss of offsite power and/or delayed synchronization of the EDGs due to inadequate breaker coordination. Consequently, the conditions described in this report did not have an adverse affect on safe operation of the plant, or the health and safety of plant personnel or the general public.<br /><br /> The root cause of this condition was a deficiency involving inadequate analysis of undervoltage and overcurrent protective features on the vital 4.16 KV AC electrical distribution system. As corrective action, delay times associated with this breaker coordination problem were revised. Additionally, the Bus Short Circuit Current Calculation and the Relay Coordination Calculation will be reviewed and updated.
3971993004 | Columbia | 01/27/1993 | 02/26/1993 | 9303020544 | <strong>Improperly Seated Fuses Could Have Caused A Loss Of Residual Heat Removal Capability During A Seismic Event</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1993, a Design Engineer determined that two inadequately installed fuses (F03-2 and F04-2) caused Division 2 of the Residual Heat Removal (RHR) System to be inoperable. This condition could have prevented the RHR System from performing its safety function during the time when Division 1 of RHR was also inoperable. A seismic event may have dislodged the fuses. A review determined that the fuses could have been in this configuration since Plant startup. These discrepancies were found during performance of the Plant Fuse Walkdown Program, which was initiated in part to identify these types of deficiencies.<br /><br /> The fuses were properly reseated in their fuse clips. <br /><br /> The root cause was improper installation of the fuses. <br /><br /> No further corrective actions were identified because formal controls for fuse replacement now exist and the Fuse Walkdown Program is meeting management expectations. <br /><br /> The safety significance of this event is negligible because the probability of a seismic event occurring coincident with the opposing division of RHR being unavailable is low. This condition posed no threat to the health and safety of Plant personnel or the public.
3971993005 | Columbia | 02/02/1993 | 03/04/1993 | 9303100200 | <strong>Inadequate Documentation And Review Of Operability Status Results In Unavailability Of Wetwell Purge Exhaust Valve During Required Conditions</strong><br /><i>Abstract:&nbsp;</i>At 1557 hours on February 2, 1993, it was identified that the plant had entered into an Operational Condition where the Wetwell Purge Exhaust Valves were required to be operable without performing Technical Specification required maintenance. Technical Specification Surveillance Requirement 4.6.1.8.2.b specifies that these valves are to be secured closed, and maintenance performed during the next plant cold shutdown if their leakrate is greater than 0.05 La. The valves were secured shut after their leakrate was measured to be greater than 0.05 La on November 23, 1992. However, the plant entered Operational Condition 4 (cold shutdown) on January 21, 1993, and was later restarted on January 28, 1993 without performing valve maintenance. <br /><br /> This event had two root causes. The primary cause was technical inaccuracies in documents written to document the failed LLRT on November 23, 1992. The secondary cause was required verifications that were not adequately performed. As corrective actions, the affected valve was repaired, procedures regarding preparation, review and use of LCO/INOP Status Sheets will be revised, required reading will be provided, and expectations regarding review of deficient conditions involving Technical Specification required equipment and systems will be communicated to Control Room Supervisors and Shift Managers. WNP-2 did not experience an event that required use of the affected valves during the period when their leakrate exceeded limits. Consequently, this condition did not have an adverse affect on safe operation of the plant, or the health and safety of plant personnel or the general public.
3971993006 | Columbia | 02/06/1993 | 03/08/1993 | 9303120166 | <strong>Manual Reactor Scram Initiated Due To Reactor Recirculation Pump Trip While Operating In The Area Of Increased Awareness</strong><br /><i>Abstract:&nbsp;</i>At 0947 hours on February 6, 1993, control room operators at WNP-2 initiated a manual scram after the Reactor Recirculation Pump 1A (RRC-P-1A) tripped during an attempt by the operators to transfer the pump from slow speed to high speed (15 Hz to 60 Hz). During the pump shift, RRC-P-1A tripped, leaving the unit in single recirculation loop operation while operating in the Area of Increased Awareness. A manual reactor scram is the required response to this event, in accordance with PPM 4.12.4.7, 'Unintentional Entry Into the Region of Potential Core Power Instabilities'. <br /><br /> After inserting the manual scram to exit the prohibited area, the immediate corrective action was the prompt response by the operators to bring the plant to a safe shutdown condition in accordance with approved plant procedures. <br /><br /> The root cause is that the risks and consequences associated with a change were not adequately reviewed or assessed. A second root cause for this event has been categorized as a component was not operated within the component design parameters in that the power level and feed flow conditions, at which the transfer to high speed was attempted were not within the acceptable parameters to satisfy to logic circuitry. As a corrective action the RRC system operating procedure was changed. Contributing factors were the operating constraints placed on the plant as a result of the power oscillation event which resulted in the RRC pump shift attempt at the lower power level. Abstract (Cont'd) The event posed no threat to the health and safety of either the public or plant personnel.
3971993007 | Columbia | 02/10/1993 | 06/11/1993 | 9306170319 | <strong>Reactor Scram And High Pressure Core Spray (HPCS) System Suction Valve Transfer Due To Loss Of A Reactor Feedwater Pump Caused By A Failure Of The Turbine Governor Control System</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1993, at 1727 hours, a low Reactor Pressure Vessel (RPV) level reactor scram was initiated by the Reactor Protection System (RPS) in response to an actual low water level condition. The low RPV level was caused by the loss of Reactor Feedwater (RFW) Pump 1B due to a loss of turbine governor control. <br /><br /> At 1730 hours, steam was observed at the entrance to RFW Pump Room "B", and at 1739 hours, the steam supply to the RFW Pump 1B turbine was isolated. An Unusual Event was declared at 1750 hours to enhance increased awareness of plant personnel. Investigation of the steam in the pump room determined the source to be an RFW Pump 1B suction side relief valve and pump casing drain line. <br /><br /> At approximately 1800 hours, an unplanned Engineering Safety Features (ESF) automatic High Pressure Core Spray (HPCS) suction valve switchover occurred due to an actual high Suppression Pool water level. The high water level resulted from Main Steam Relief Valve (MSRV) discharge to the Suppression Pool during manual actuation for RPV pressure reduction. <br /><br /> The immediate corrective actions were prompt response by Plant Operators to bring the plant to a safe shutdown condition, and to restore HPCS suction to the normal configuration.<br /><br /> The root cause of this event was less than adequate evaluation of corrective actions to prevent recurrence of RFW pump turbine governor actuator connector pin corrosion and failure. Further corrective actions will perform a failure analysis of the connector and implement action(s) to eliminate the connector pin corrosion. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
3971993008 | Columbia | 02/11/1993 | 06/11/1993 | 9306170347 | <strong>Logic System Functional Test Requirements For Emergency Bus Undervoltage Logic Not Fully Implemented Due To Inadequate Procedure Development</strong><br /><i>Abstract:&nbsp;</i>At approximately 1054 hours on February 11, 1993, it was determined the method used to demonstrate operability for Division 1, 2, & 3 emergency power bus primary undervoltage protection logic circuits was not fully adequate to satisfy Technical Specification requirements. Operability of these circuits must be demonstrated periodically by performance of a Logic System Functional Test (LSFT). LSFT requirements were not fully implemented for portions of the primary undervoltage logic due to inadequacies in the existing test method. <br /><br /> The root cause of this deficiency was inadequate provisions for review and evaluation of surveillance procedure suitability during initial development of the Technical Specification Surveillance Testing Program. As corrective action procedures were established to satisfy the primary undervoltage logic LSFT requirement, and functional testing of the undervoltage logic was performed. Additionally, a project to improve Technical Specification Surveillance Program implementation is in progress. Operability of those portions of the primary undervoltage logic that were not adequately verified previously has been demonstrated by testing. Consequently, the condition described in this report did not have an adverse effect on safe operation of the plant, or the health and safety of plant personnel or the general public.
3971993009 | Columbia | 02/17/1993 | 07/02/1993 | 9307090007 | <strong>Existence Of Noncondensible Gases In The Reference Leg Of Reactor Pressure Vessel Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1993, after a period of engineering review and evaluation, plant management concluded that the existence of noncondensible gases in the reference leg of Reactor Pressure Vessel (RPV) Instrumentation could have affected the point at which a RPV Level 3 isolation occurred. This actuation is required in response to a postulated RHR pipe crack and would have delayed a Nuclear Steam Supply Shutoff System (NS**4) Groups 5 and 6 isolation. <br /><br /> As an immediate corrective action credit was taken for an existing flood watch to assure a leak would be detected and any flood could be terminated. Further corrective actions include procedure changes and training to provide plant operators with information on how to recognize the noncondensible gas problem and to describe actions to be taken if the conditions are observed. Boiling Water Reactor Owners Group (BWROG) activities associated with this problem are being tracked to provide a short and long-term solution to this issue. <br /><br /> Testing completed by the Electric Power Research Institute (EPRI) for the BWROG in April 1993, indicates that the impact of noncondensible gases could, under postulated accident conditions, effect the RPV Level 3 isolation actuation setpoints to a greater extent than previously known. Observations during the WNP-2 shutdown for refueling on May 1, 1993, did not reveal significant degassing. Observed level indication deviations on May 1, 1993, did not meet the unacceptable notching criteria of six inches offset for two minutes or longer duration. <br /><br /> The root cause of this event was a design deficiency. The RPV level instrumentation designer did not recognize the impact of noncondensible gases in the system. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971993010 | Columbia | 03/04/1993 | 04/13/1994 | 9404190155 | <strong>Technical Specification Surveillance Improvement Project Identification Of Nonconforming Conditions</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1993, the first condition of noncompliance with WNP-2 Technical Specifications was identified as part of a Technical Specification Surveillance Improvement Project (TSSIP). This two-year project was recommended by a Supply System Quality Action Team formed as a corrective action of LER 91-013-02. The TSSIP revises and broadens the scope of the Surveillance Procedure Verification Program completed in May 1991. <br /><br /> A total of 24 reportable problems identified by this process are described in this LER. All 24 items relate to failure of procedures to fully implement WNP-2 Technical Specification surveillance requirements. This LER reports the initial findings of the TSSIP surveillance procedure review process. Based upon previous experience with the Surveillance Procedure Verification Program, it is likely that additional reportable items will be identified. A supplement to this LER will be submitted on an approximate monthly basis, or as necessary, to describe future reportable items.<br /><br /> Immediate and further corrective actions include, but are not limited to, entering Technical Specification Action Statements, additional testing, Plant Procedure changes, Technical Specification changes, and design changes.<br /><br /> The root causes for these events include less than adequate barriers and controls for program changes and less than adequate test procedures, directives/requirements, and design. The general root cause has been determined to be less than adequate management control of the Surveillance Test Program. The safety significance of each item and the whole surveillance program was evaluated and it has been concluded that this event had potential safety significance.
3971993012 | Columbia | 03/11/1993 | 04/09/1993 | 9304130102 | <strong>Main Turbine Bypass Valves Not Operable Per Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1993, a System Engineer learned that the fast open function of the Main Turbine Bypass Valves (BPV) was not operable between 25 % and 35 % reactor thermal power as required by the Technical Specifications. This condition was the result of an inappropriate setpoint in the Digital-Electro-Hydraulic (DEH) Turbine Control System. The System Engineer was verifying the DEH setpoints when this condition was identified. <br /><br /> No immediate corrective actions were required because the Plant was above 35% power and the BPVs were operable. <br /><br /> The root cause was less than adequate surveillance procedures because they did not comply with the Technical Specifications. <br /><br /> Engineering evaluations will be performed to determine the appropriate actions required to comply with the Technical Specifications. <br /><br /> The safety significance of this event is negligible. The safety limits to prevent fuel failure from critical heat flux under design basis conditions were not violated nor would they have been under accident conditions. This condition posed no threat to the health and safety of Plant personnel or the public.
3971993013 | Columbia | 03/18/1993 | 05/12/1993 | 9305140245 | <strong>Loss Of Containment Integrity Due To Original Design Errors And Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1993, and April 12, 1993, design efforts were identified by Supply System engineers working in the Component Safety Classification (CSC) and Design Requirement Document (DRD) Programs. These are ongoing design basis reconstitution programs that provide a detailed review of WNP-2 design. The CSC Program uses an Electric Power Research Institute (EPRI) Guideline based methodology to establish and document the technical basis for the safety classification of each safety-related component. The DRD Program provides a documented reference to system level design requirements and functions. <br /><br /> The root cause for these events was deficiencies in original plant design. <br /><br /> Immediate and further corrective actions include, but are not limited to, entering Technical Specification Action Statements and taking compensatory action, additional testing and maintenance, Plant Procedure changes, Technical Specification changes, design reviews, and design changes.
3971993014 | Columbia | 03/25/1993 | 09/01/1993 | 9309080187 | <strong>Inadequate Backup Overcurrent Protection For Containment Penetrations</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1993, an Electrical Engineer found five electrical lighting circuits associated with Primary Containment that were not turned off during plant operation and did not have adequate backup overcurrent protection. This condition could cause failure of the impacted Primary Containment electrical penetrations. This problem was discovered as part of an Electrical Calculation Improvement Program being carried out by Engineering at WNP-2. All circuits entering Primary Containment must be properly protected with primary and secondary overcurrent protection or shut off procedurally during power operation. It was found that procedures did not address shutting off five circuits that feed 120 volt receptacles within containment. The backup protection to these circuits was found to be too large to protect the containment penetrations. Additional inadequate penetration overcurrent protection conditions were found on August 3, 1993, during performance of Further Corrective Action Number 4. The penetration conductors and supported equipment were declared inoperable.<br /><br /> Immediate action was taken by opening the breakers feeding the five involved electrical circuits. <br /><br /> The root cause of this event was a less than adequate design analysis using inaccurate and incomplete documentation.
3971993015 | Columbia | 03/31/1993 | 04/30/1993 | 9305060318 | <strong>High Pressure Core Spray Inoperability Caused By Inadequate HPCS Pump Room Cooler Flow</strong><br /><i>Abstract:&nbsp;</i>At approximately 0714 hours on March 31, 1993, with the plant operating in Mode 1 at 97.5% power, WNP-2 commenced a reactor shutdown and declared an Unusual Event (UE). The reactor shutdown was a result of the High Pressure Core Spray system (HPCS) being inoperable from low Service Water (SW) flow through HPCS pump room cooler RRA-CC-4, coincident with the Reactor Core Isolation Cooling system (RCIC) being inoperable since March 18, 1993. with these two systems inoperable, Technical Specification 3.0.3 was applicable, which forced the shutdown and subsequent declaration of the UE. <br /><br /> Immediate corrective actions for this event included: 1) reperforming and approving an engineering calculation to demonstrate HPCS operability at a lower HPCS pump room cooler flowrate, 2) revising the HPCS-SW flow balancing surveillance to specify the newly calculated, lower flowrate, and 3) rebalancing flow through the HPCS-SW system. <br /><br /> The apparent cause for this event was a system/component deficiency. <br /><br /> There was no safety significance associated with this event. During the time that the HPCS system was considered inoperable, the HPCS system was able to perform its safety function.
3971993016 | Columbia | 03/31/1993 | 04/30/1993 | 9305070183 | <strong>Containment Atmosphere Control (CAC) System Bypass Leakage Not In Compliance With The Technical Specifications Due To Less Than Adequate Procedures/Corrective Action Followup</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1993, at 0115 hours, during the performance of Plant Procedure (PPM) 7.4.6.6.1.3C, 'Hydrogen Recombiner 1A Flow Instrumentation,' a plant control room operator noticed that Containment Atmosphere Control (CAC) System primary containment isolation valves CAC-V-4 and CAC-V-6 were open. This condition opened a path between the drywell and the wetwell through the CAC 'A' hydrogen recombiner skid and, as a result, the containment drywell-to-suppression chamber bypass leakage limits were exceeded. During the course of the surveillance, a jumper was installed (as directed by procedure) which allowed for the energization of relays associated with containment isolation valve control power, causing the valves to open automatically. <br /><br /> As an immediate corrective action, at 0134 hours the valves were closed by removing the jumper and the shift manager directed that the surveillance be suspended. In addition, at approximately 1500 hours on March 31, 1993, the Plant Operating Committee (POC) directed that the shift manager suspend all activities pertaining to the CAC System and an Incident Review Board (IRB) was convened. <br /><br /> The causes of this event are: 1) less than adequate procedures, 2) less than adequate corrective action followup for a related problem, and 3) technical inaccuracies in the Scheduled Maintenance System (SMS). Further corrective actions include: 1) reviewing maintenance surveillance procedures associated with the CAC System, 2) providing counselling on corrective action closeout, and 3) modifying the SMS process to provide for a consistent method for designating plant conditions. <br /><br /> This event did not affect the health and safety of either the public or personnel.
3971993017 | Columbia | 04/26/1993 | 05/26/1993 | 9306010332 | <strong>Fire Damper Seismic Qualification Concerns Identified In 1985 Through 1987 Were Not Reported</strong><br /><i>Abstract:&nbsp;</i>At 1350 hours on April 26, 1993, it was discovered that fire damper seismic qualification concerns were identified in 1985 through 1987, but not reported. A seismic event could have caused the failure of fire dampers WMA-FD-6, WMA-FD-52 and WMA-FD-54 to remain open. These fire dampers must remain open to provide Division 2 Heating, Ventilation and Air Conditioning (HVAC) cooling to the Control Room and the Critical Switchgear Room. The sash type chains and chain end fastening clips, used to hold the fire dampers open, could not be seismically qualified, and could have failed during a seismic event.<br /><br /> Two root causes for this event have been identified: (1) The failure to include fire dampers on the Safety-Related Mechanical (SRM) list; and (2) the failure to rereview a Nonconformance Report (NCR) for reportability following a scope and intent change. <br /><br /> No corrective actions are required. All fire dampers were modified for seismic qualification in 1987, and programs are currently in place to prevent recurrence of the programmatic problems.
3971993018 | Columbia | 04/28/1993 | 05/28/1993 | 9306030259 | <strong>Spent Fuel Pool Makeup Not Adequate To Mitigate Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1993, the WNP-2 Management Review Committee (MRC) concluded its review of a problem associated with the Fuel Pool Cooling (FPC) system and decided it was a reportable event. Previously, on April 23, 1993, a plant support engineer discovered a design condition that could have impacted the plant's ability to mitigate the consequences of an accident. In the event of a Loss Of Coolant Accident (LOCA), the Service Water system (SW) must be able to supply emergency makeup water to the Spent Fuel Pool (SFP). Makeup is normally supplied by the Condensate Storage and Transfer system, a non-safety-related system. Without makeup, water in the pool would have continued to evaporate until the Fuel Pool Cooling system (FPC) pump tripped. This would have resulted in eventual fuel pool boiling. Vapors generated by the elevated Spent Fuel Pool temperature would have condensed, flowed to the bottom of the Reactor building, and caused a loss of the Emergency Core Cooling (ECCS) pumps due to flooding. Service water would not have been immediately available because manual isolation valves SW-V-75AA and BB are presently closed, and access to these valves was analyzed to be restricted during post-LOCA conditions.<br /><br /> Immediate corrective action included performing an analysis to verify the feasibility of continued, safe operation until the next refueling outage, which began on April 30, 1993. <br /><br /> Further corrective actions included performing engineering calculations and revising plant documents to justify continued closure of manual isolation valves SW-V-75AA and BB during normal plant operations.
3971993019 | Columbia | 05/10/1993 | 06/09/1993 | 9306170223 | <strong>Engineered Safety Features (ESF) Isolations And Actuations Due To A 500 KV Load Break Disconnect (LBD) Failure</strong><br /><i>Abstract:&nbsp;</i>At 1115 hours on May 10, 1993, during the annual Maintenance and Refueling Outage, a loss of off-site 500 KV power occurred that resulted in plant critical AC electrical loads being supplied by the 115 KV Backup AC source. At the time, plant loads were being supplied by the off-site 500 KV South Bus via the backfeed configuration through Main Transformers E-TR-M1, E-TR-M3 and E-TR-M4; and Normal Auxiliary Transformers E-TR-N1 and E-TR-N2 (see Figure 1). The loss of power was caused by a failure of 500 KV South Bus Inductive Reactor Load Break Disconnect (LBD) 4909 during routine load voltage control by the Bonneville Power Administration (BPA) System Dispatcher. The loss of power resulted in load shedding from the Critical Switchgear E-SM-7 and E-SM-4 buses, Emergency Diesel Generator (DG) 1 and 3 automatic starts, an automatic transfer of E-SM-7 to Backup Transformer E-TR-B, an RPS full scram (all control rods were already fully inserted) and multiple Engineered Safety Features (ESF) isolations.<br /><br /> Plant Operators responded to this event by restoring RHR Loop 'A' Shutdown Cooling at 1144 hours and resuming all plant systems to normal lineup status by 1315 hours.
3971993020 | Columbia | 05/11/1993 | 06/10/1993 | 9306210062 | <strong>Improper Scheduling Of Main Steam Relief Valve (MSRV) Position Indicator Testing</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1993, a system engineer determined that the Main Steam Safety/Relief Valve (MSRV) position indicators have not always been demonstrated operable prior to entry into Mode 2 as required by Technical Specification 3/4.3.7.5. The root cause of this event was less than adequate written documents in that the procedures did not satisfy the surveillance requirements for entry into the applicable Modes, and the three MSRV Specifications are inconsistent. The MSRV position indication testing methodology has been changed to support testing prior to entry into Mode 2 in order to meet the Technical Specifications as written. In addition, a Technical Specification amendment request will be submitted to make the three applicable requirements consistent. Since other methods of detecting open MSRVs are available, this event had no safety significance or affect on the health and safety of the public.
3971993021 | Columbia | 05/14/1993 | 06/14/1993 | 9306180314 | <strong>Containment Atmosphere Control (CAC) System Water Accumulation And Potential Containment Bypass</strong><br /><i>Abstract:&nbsp;</i>On May 14 and June 2, 1993, followup actions resulting from a recently completed Supply System Safety System Functional Inspection (SSFI) discovered two problems with the Containment Atmosphere Control (CAC) system. The first problem that was discovered was a potential for water accumulation in the CAC system's low-point piping containing flow orifices and flow control valves. The water could affect the ability to measure and control flow in the system. The second problem discovered was a bypass of Secondary Containment in the event of a single failure in the Standby Service Water (SW) system that supplies scrubber water to the CAC system operating during post Loss Of Coolant Accident (LOCA) conditions. Post-LOCA, Primary Containment gas could escape to the environment via the failed SW system and thus bypass the Secondary Containment. <br /><br /> No immediate corrective actions were required because the CAC system and Primary Containment are not required to be operational in Mode 5. <br /><br /> The root cause for both events was inadequate original analysis of the system design. <br /><br /> Further corrective actions to alleviate possible water accumulation during prolonged CAC system operation, post-LOCA, following accident conditions included installation of drains in the lowest elevations of CAC system piping. To alleviate the Containment bypass issue, further corrective actions included providing procedural instructions to trip the appropriate CAC subsystem if its corresponding service water supply becomes unavailable.
3971993022 | Columbia | 05/24/1993 | 07/14/1994 | 9407190333 | <strong>Two Control Rods Were Withdrawn With Their Scram Accumulators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1993, two control rod withdrawal events were identified as having violated Technical Specifications. Previously, on May 24 and 25, 1993, during the annual Maintenance and Refueling Outage, Control Rods '10-11' and '26-35,' respectively, were withdrawn with their scram accumulators inoperable. The scram accumulators were inoperable because their associated water level switches had failed Surveillance Procedure PPM 7.4.1.3.5.2, 'Scram Accumulator Pressure Detection CC/Level Detection - CFT/CC.' Withdrawing a control rod with its scram accumulator inoperable is contrary to WNP-2 Technical Specification 3.1.3.5.<br /><br /> Immediate corrective action by Plant Operators was to disarm Hydraulic Control Units (HCUs) '10-11' and '26-35' hydraulically. <br /><br /> The root causes for this event were: (1) the Shift Managers failed to fully evaluate Technical Specification requirements and actions to assure compliance, and (2) the methods used to indicate the status of HCU and control rod maintenance and testing activities were not sufficiently effective to coordinate the concurrent activities.
3971993023 | Columbia | 06/05/1993 | 07/01/1993 | 9307080390 | <strong>Improperly Supported Instrument Flexible Conduit</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1993, it was concluded in a reportability evaluation that flexible conduit associated with pressure switches MS-PS-48A and C were not seismically supported. These pressure switches provide a permissive to allow remote manual opening of upper drywell (containment spray valves RHR-V-16A and 17A. The containment spray function is a mode of Residual Heat Removal (RHR) operation that provides supplemental containment cooling during postulated post accident conditions. This event was not safety significant.<br /><br /> The root cause of this event was improper construction instructions. Other instrumentation racks were walked down to identify similar conditions. The unacceptable conditions found have been corrected. Because the root cause of this condition was a construction/startup modification control process that has changed significantly since the time this problem occurred (1983), no further corrective actions are planned. This event posed no threat to plant personnel or the public.
3971993024 | Columbia | 06/15/1993 | 07/15/1993 | 9307220303 | <strong>Containment Instrument Air System Actuation During System Restoration</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1993, the Containment Instrument Air (CIA) system was returned to service following scheduled containment drywell to wetwell bypass leakage rate testing (BLRT). The CIA system restoration was not performed in accordance with the BLRT procedure. CIA restoration was expedited to support testing of the Main Steam Isolation Valves. The restoration was performed in a sequence other than that required by the BLRT procedure and resulted in an Engineered Safety Feature (ESF) actuation of the CIA backup nitrogen bottle programmer. One root cause of this event was a personnel effort in that self checking was not applied. The individual responsible for the coordination of the CIA system restoration has been counseled in expectations for procedural adherence. The second root cause was a deficiency with the BLRT procedure. The BLRT test procedure will be strengthened to prevent CIA programmer actuations. The author and reviewer of the BLRT procedure deviation will be counseled on the need to perform a thorough review with a questioning attitude and when possible to review proposed procedure changes with the appropriate system engineer. Since the CIA system and supported equipment were not required to be operable at the time of this event, this event had no safety significance.
3971993025 | Columbia | 06/15/1993 | 07/15/1993 | 9307220304 | <strong>Engineered Safety Feature (ESF) Actuation Caused By Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>At approximately 1850 hours on June 15, 1993, a Group 1 Nuclear Steam Supply Shutoff System (NS**4) isolation occurred during the performance of a Technical Specification surveillance test associated with the Turbine Throttle Valves. The test involved calibration of position switches on the valves associated with the NS**4 logic. During shutdown conditions there is no main condenser vacuum. The NS**4 logic is configured in a manner where exercising each Turbine Throttle valve to the open position initiates a half Group 1 isolation. During the surveillance test a second Throttle Valve was opened without resetting the (NS**4) logic after testing the first valve. This resulted in a Group 1 isolation which is considered an ESF actuation. <br /><br /> The root cause of this event was a procedural deficiency. <br /><br /> Immediate corrective action was taken to stop work on the surveillance and investigate the cause. Further corrective action was taken to change the surveillance procedure to require a reset of the logic after the switches on each valve are calibrated. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
3971993026 | Columbia | 06/19/1993 | 07/19/1993 | 9307280103 | <strong>Failure To Complete Weekly Battery Surveillance Requirements Within The Allowed Technical Specification Interval Due To A Scheduling Oversight</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1993, at 0611 hours, WNP-2 failed to comply with Technical Specification Surveillance Requirement 4.8.2.1.a for all safety-related batteries. Surveillance Procedure PPM 7.4.8.2.1.20, 'Weekly Battery Testing,' satisfies the surveillance requirements for all plant safety-related batteries. The procedure was not completed within the required seven day interval plus 1.75 days (25% maximum allowable extension per Surveillance Requirement 4.0.2). The battery surveillance procedure was last completed on June 10, 1993, at 1211 hours, with the next completion due no later than 0611 hours on June 19, 1993. However, the surveillance procedure was not completed until June 19, 1993, at 1837 hours. This resulted in all plant safety-related batteries being technically inoperable from 0611 hours to 1837 hours on June 19, 1993, for failing to comply with Surveillance Requirement 4.0.2. The associated Technical Specification Action Statements were not entered as the battery surveillance procedure was in progress. Surveillance Requirement 4.0.3 permits an action requirement delay of up to 24 hours to complete a delinquent surveillance. <br /><br /> The immediate corrective action was the initiation and successful completion of PPM 7.4.8.2.1.20 on June 19, 1993, at 1837 hours. <br /><br /> The root causes of this event were less than adequate Technical Specification surveillance tracking methods and personnel error. Further corrective actions include counseling of responsible Electrical Maintenance Shop personnel and Technical Specification Surveillance Program changes. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
3971993027 | Columbia | 08/03/1993 | 09/01/1993 | 9309080006 | <strong>Reactor Scram During MSL High Radiation Channel Calibration</strong><br /><i>Abstract:&nbsp;</i>At 0539 hours on August 3, 1993, during performance of a surveillance procedure to calibrate Main Steam Radiation Indicating Switch MS-RIS-610D, the reactor unexpectedly scrammed from 100% power due to a full isolation of the Main Steam Isolation Valves (MSIVs). The isolation was due to higher than normal steam flow through three of the main steam lines. <br /><br /> Control Room personnel immediately implemented the Emergency Operating Procedures to stabilize the plant in a safe shutdown condition. Additionally, shift management declared an Unusual Event (UE) to promote increased awareness on the part of plant operating staff. <br /><br /> There were three root causes of the MSIV isolation/r actor scram: self-checking not applied, job scoping not thorough, and post-maintenance testing inadequate. Further corrective action consisted of performing a failure analysis on a failed MSIV component and determining the operability of all of the MSIVs. <br /><br /> This event posed no threat to the safety of the public or plant personnel.
3971993028 | Columbia | 09/23/1993 | 10/25/1993 | 9310290064 | <strong>Failure To Analyze A High Energy Line Break Located Outside Primary Containment</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1993, with the reactor in MODE 1 at 100% power, a programmatic engineering review of high energy line break (HELB) analysis to confirm consistency between Leak Detection (LD) system capabilities and HELB analysis assumptions identified an unanalyzed HELB. The WNP-2 Final Safety Analysis Report (FSAR), Section 3.6, indicates that HELBs were analyzed for environmental effects, specifically temperature and humidity. However, the programmatic engineering review determined that these environmental effects were not analyzed for a postulated break in a four-inch Reactor Water Cleanup (RWCU) system line RWCU(5)-3. The break is open to the Reactor Building environment.<br /><br /> Engineering immediately performed an operability evaluation for the unanalyzed HELB conditions and determined that the plant could continue to operate safely. Further corrective action consists of finalizing revisions to Supply System HELB analysis and requesting permanent exclusion of the postulated break. <br /><br /> The root cause of this event was less than adequate design analysis and review of design analysis by the architect engineer. There were no contributing causes to this event. <br /><br /> This event posed no threat to the health and safety of the public or plant personnel.
3971993029 | Columbia | 08/05/1993 | 11/05/1993 | 9311100114 | <strong>Steam Line Flow Element Sensing Line Pinhole Leak</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1993, with the plant in Mode 3 (Hot Shutdown) a system engineer discovered a small steam leak of reactor coolant located upstream of the 'A' Inboard Main Steam Isolation Valve inside the Primary Containment. The steam flow was from an unisolatable pinhole leak at a flow element sensing line weld. <br /><br /> Control Room personnel immediately initiated a plant cooldown from Mode 3 to Mode 4 (Cold Shutdown) W allow repair of the leak. <br /><br /> The root cause of the steam leak was a weld defect. A defect introduced into the root of the weld during installation served as the initiation point with subsequent crack propagation due to fatigue. <br /><br /> The weld crack was repaired on August 6, 1993. <br /><br /> This event posed no threat to the safety of the public or plant personnel.
3971993030 | Columbia | 10/28/1993 | 08/19/1994 | 9408310137 | <strong>Missing Cable Tray Covers Discovered During The Electrical Power Raceway Walkdown</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1993, with WNP-2 in Mode 1 (Power Operations) at 100% power, the Supply System found seven locations where electrical raceway cable tray covers were not installed in accordance with electrical separation design criteria. These cable tray cover deficiencies were found during electrical power raceway walkdowns being conducted to identify noncredited Thermolag installations. At the conclusion of the walkdowns on June 23, 1994, a total of 166 locations were found with missing cable tray covers or other deficiencies, such as gaps or holes in the cable tray covers. <br /><br /> Cable tray covers provide physical independence of redundant safety-related circuits. The absence of these covers violates WNP-2 electrical separation design criteria. A failure induced fire in an open power cable tray could produce faults in nearby safety-related electrical cables, resulting in a loss of a redundant safety function. <br /><br /> The cause of this event was inadequate management methods to identify and resolve cable tray and conduit electrical separation problems. <br /><br /> Corrective actions included: establishing fire tours of affected areas, correcting cable tray deficiencies, incorporating as-built information into the design data base, developing methods for design configuration control and feedback of as-built information into the design data base, training of plant personnel, and review and walkdown of a sample of recent plant design changes to verify that electrical separation related mistakes are not recurring.
3971993031 | Columbia | 11/09/1993 | 01/07/1994 | 9401210063 | <strong>Main Control Room HVAC High Temperature Condition During A DBA</strong><br /><i>Abstract:&nbsp;</i>At 1200 hours on November 9, 1993, with the reactor at 100% power, an engineering evaluation determined that the Main Control Room HVAC system will not maintain control room temperature below the design basis limit of 104 degrees Fahrenheit following a Design Basis Accident (DBA). This postulated event involves extreme warm-weather conditions with only the Standby Service Water system available for heat removal. The potential to exceed this design temperature limit is based on current knowledge of Standby Service Water system fouled cooling coil UA values. <br /><br /> Upon discovery, a PER was written to document the potential design analysis concerns. Further corrective actions include revising the applicable procedure to maintain control room temperature below its design limit and reviewing other components utilizing service water to ensure appropriate fouling and cooling water temperatures have been considered. <br /><br /> The root cause of this event was inadequate design margin in the original design including a failure to account for cooling-coil fouling. A contributing cause was a less than adequate process for factoring fouling considerations into the original and subsequent design calculations. <br /><br /> Although this condition does not presently affect plant operability, the design basis temperature could have been exceeded during past summers coincident with design basis accident conditions.
4001993001 | Harris | 03/08/1993 | 04/07/1993 | 9304120271 | <strong>Surveillance test procedure deficiency resulting in failure to a equately verify instrument inverter breaker alignment.</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1993, while performing the weekly surveillance test for the on-site power distribution system, a procedural deficiency was identified related to the operability verification for the 7.5 Kva instrument inverters. Technical Specifications (TS) require that the instrument inverters be 'connected to their 125-volt DC Bus'. To satisfy this requirement, breaker alignment and voltage indication verifications have been performed. Operators performing the March 8, 1993 surveillance test noted that the procedure did not verify the position of the inverter backup DC supply breakers and therefore did not specifically satisfy the TS requirement. Based on this, a determination was made that TS operability had never been adequately verified and that a TS violation existed. The cause of this event was an oversight during the procedure revision process that occurred in 1986. Immediate corrective actions included verifying that the backup DC supply breakers were closed on all four instrument inverters. In addition, the surveillance test procedure was revised to include position verification for these breakers.
4001993002 | Harris | 03/30/1993 | 04/29/1993 | 9305040167 | <strong>Entry into Technical Specification 3.0.3 due to failure of AH-92A Fan, concurrent with inoperable B-train Essential Services Chilled Water Chiller.</strong><br /><i>Abstract:&nbsp;</i>On March 30 1993 at 1052 hours, Operations personnel discovered a bearing failure on Fan AH-92A and promptly secured it. This fan provides cooling air for safety related Motor Control Center MCC 35A. Concurrently, the B-train Essential Services Chilled Water Chiller was under clearance and inoperable for periodic maintenance which renders MCC 35B inoperable. This combination resulted in a loss of cooling for both MCC 35A and 35B, which requires entry into Technical Specification 3.0.3. Immediate corrective actions included restoration of the B-train ESCW Chiller and removal of the clearance. This took approximately 23 minutes and TS 3.0.3 was exited at 1115. The cause of this event was the failure of the outboard bearing on Fan AH-92A. Possible reasons for this bearing failure include improper maintenance activities, or the installation of a faulty bearing, both of which took place ten days earlier on March 20, 1993. Additional analysis is being performed to help determine the cause of the bearing failure. The Air Handling unit was returned to service on April 1, 1993. <br /><br /> This condition constitutes a TS violation and is being reported in accordance with 10CFR50.73 (a) (2) (i) (B).
4001993003 | Harris | 03/31/1993 | 08/23/1993 | 9309020200 | <strong>Containment Vacuum Relief System design deficiency resulting in Technical Specification violation.</strong><br /><i>Abstract:&nbsp;</i>On March 31 1993, during a routine procedure review, Operations personnel discovered a possible design deficiency in the Containment Vacuum Relief System. Technical Specification (TS) 3.6.5 provides operability requirements for the system and refers to the differential pressure (D/P) across containment as 'containment less atmospheric pressure'. The D/P transmitters at Harris that provide input for the automatic vacuum relief actuation were identified to actually sense D/P from containment to the Reactor Auxiliary Building (RAB), rather than outside atmospheric pressure. Due to the fact that the RAB is maintained at a slight vacuum (nominally -.125 ' H sub 2 O), the automatic actuation would not have occurred until the required setpoint, plus .125' H sub 2 O was reached. During subsequent system walkdowns it was also discovered that the D/P transmitters that provide indication in the Main Control Room, which are used to satisfy TS 3.6.1.4, are configured in the same manner. Following evaluation by plant and corporate engineering groups these conditions were determined to constitute a TS violation and are being reported in accordance with 10CFR50.73 (a)(2)(i)(B). Interim corrective actions were to decrease the automatic relief actuation setpoint and monitor actual containment to outside atmospheric pressure from alternate indications. A modification that rerouted the sensing points to outside of the RAB was completed on August 20, 1993 to provide permanent corrective actions.
4001993004 | Harris | 04/13/1993 | 05/12/1993 | 9305180360 | <strong>Two Control Room Ventilation dampers were not tested within their required surveillance interval, which resulted in a Technical Specification violation.</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1993 Technical Support personnel discovered that Control Room Ventilation System valves 1CZ-19 and 1CZ-20 had not been tested within their quarterly surveillance test interval as required by Technical Specifications (TS). On several occasions since plant startup, dampers CZ-D19 and CZ-D20 were mistakenly stroked instead of the valves. The cause of these occurrences was personnel error on the part of Operations personnel performing the quarterly tests and inadequate review and trending of test data results by ISI personnel in the past. An additional factor that contributed to the error was poor human factors considerations relate to the numbering and labeling of ventilation system components on the main control board. Corrective actions included the development of two Operations Night Orders which outlined the error and re-emphasized the importance of strict procedure compliance and attention to detail. The test procedure was also revised to include a clarifying statement and training for Operations personnel will be conducted. An evaluation will be performed and appropriate enhancements will be made to the labeling scheme on the main control board. Recent improvements have been made to the ISI review process, including a more thorough evaluation of test data results and the incorporation of data point trending plots. These improvements contributed to the identification of this error. Additional improvements are being evaluated that will enhance the ISI program to ensure timely resolution of discrepancies identified during the review process.
4001993005 | Harris | 04/28/1993 | 05/28/1993 | 9306040120 | <strong>Technical Specification 3.0.3 entry due to closing the CSIP cross connect valves for stoke testing, with the "B" CSIP inoperable.</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1993, the 'B' Charging/Safety Injection Pump (CSIP) was removed from service due to excessive seal leakage and suspected internal damage. On April 26, following replacement of the pumps rotating element, a Justification for Continued Operation (JCO) was approved to provide an acceptability evaluation for the repaired 'B' CSIP. On April 27, the pump was started for testing and the results appeared to confirm the assumptions made in the JCO. On April 28, the 'B' CSIP was declared operable and placed in service. Shortly afterwards, an in-service stroke test was performed on the CSIP discharge cross connect valves. During this testing the valves were closed for less than one minute. <br /><br /> On April 29, it was discovered that an error had been made during the review and evaluation of pump acceptance test results, which rendered the test unsatisfactory and invalidated the JCO operability assumptions. <br /><br /> Based on this, the pump should not have been declared operable and for the <1 minute time period that the cross connect valves were closed during testing, the plant was in Technical Specification (TS) 3.0.3, due to not having an operable Emergency Core Cooling Supply flow path. Immediate corrective actions were to restore the 'C' CSIP and remove the 'B' CSIP until additional testing could be performed to validate its operability. The root cause of this event was personnel error during the 'B' CSIP acceptability evaluation process and subsequent operability justification. This condition constitutes a TS violation and is being reported per 10CFR50.73 (a)(2)(i).
4001993006 | Harris | 05/17/1993 | 06/06/1993 | 9306220281 | <strong>Automatic sampling device did not function During release of the Secondary Waste Sample Tank, resulting in a Technical Specification surveillance violation.</strong><br /><i>Abstract:&nbsp;</i>On May 17 and May 31, 1993, during the performance of weekly operability checks, problems were discovered with the automatic sampling device on the Secondary Waste Sample Tank (SWST) effluent line. On both dates, it was determined that this sampler had not functioned as required during releases from the SWST. Technical Specifications (TS) require continuous sampling of this effluent stream while releases are in progress, to provide a weekly radioactivity composite. This composite sample is used as a backup to the normal radiation monitor and due to the fact that the monitor was in service during each SWST release, analysis of this sample water is not required. In both instances the release line up was immediately secured and the effluent stream was verified to have no detectable radioactivity levels.<br /><br /> The sampling device malfunctions were caused by a failure in the units electronic counter. Corrective actions included replacing this counter with a modified model and ensuring that similar discrepancies do not exist in other automatic samplers. <br /><br /> This condition constitutes a TS violation and is being reported per 10CFR 50.73 (a) (2) (i) (B).
4001993007 | Harris | 05/23/1993 | 08/23/1993 | 9309010100 | <strong>Unplanned Engineered Safety Feature Actuation when "B" Emergency Diesel Generator started on loss of power to the 1B-SB Safety Bus.</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1993 the Startup Transformer to Auxiliary Bus E supply breaker 121 failed to open automatically when the corresponding Auxiliary Transformer supply breaker 122 was closed. This resulted in both transformers feeding the same bus. After troubleshooting, recommendations were made and action taken to manually open breaker 121. Upon opening breaker 121, emergency bus B-SB supply breaker 125 opened on interlock resulting in deenergizing of the B-SB bus and automatic start and loading of the 'B' Emergency Diesel Generator (EDG). The Auxiliary Feedwater System turbine driven and 'B' motor driven pumps started at this point, as required and were subsequently secured to stabilize steam generator levels. A Containment Ventilation Isolation Signal also occurred during the transient due to the failure of a radiation monitor supply power fuse. Breaker 121 failed to automatically open due to a misaligned Mechanism Operated Cell (MOC) switch in breaker 122, which defeated the auto-open interlock. The cause of this event was determined to be insufficient and procedural controls to ensure that the MOC switch was properly aligned following maintenance. <br /><br /> Corrective actions will include training, procedure revisions and enhancements to ensure proper MOC switch alignment in applicable breakers. This event is being reported per 10CFR50.72(a)(2)(iv) as an unplanned actuation of an Engineered Safety Feature.
4001993008 | Harris | 05/25/1993 | 06/24/1993 | 9306290214 | <strong>Technical Specification violation due to improper wiring in a containment penetration current limiting breaker.</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1993, an electrical wiring discrepancy was identified in a breaker that serves as a containment penetration conductor overcurrent device. The electrical supply for the Reactor Head Cable Bridge Hoist has two 15 ampere breakers wired in series outside containment that satisfy the requirement for a primary and secondary overcurrent protective device. During an independent engineering review, it was discovered that the secondary breaker was not terminated in line to the cable bridge hoist and could not have performed its protective function. This condition constitutes operation outside of Technical Specifications and is being reported per 10CFR50.73 (a)(2)(i). <br /><br /> Immediate corrective actions included securing power to the bridge hoist by turning the operable breaker off. This action ensures that no current will pass through the containment penetration until the secondary breaker is properly wired. The cause of this event was an oversight during installation and wiring of these breakers during initial plant construction. Additional corrective actions included proper wiring of this breaker and an investigation to determine if any similar conditions exist at other containment penetrations.
4001993009 | Harris | 06/22/1993 | 07/21/1993 | 9307300104 | <strong>Technical Specification violation due to Axial Flux Difference logging error.</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1993 at 0846, the plant process computer (Emergency Response Facility Information System - ERFIS) was declared inoperable to allow for software upgrade modification. This rendered Axial Flux Difference (AFD) Monitor inoperable. Technical Specifications (TS) require logging AFD hourly for the first 24 hours after declaring the AFD monitor inoperable and every 30 minutes thereafter. At 0900, Operators began hourly AFD logging per the AFD Operations Surveillance Test (OST-1070). At 0930 on June 22, the logging frequency was not changed to a 30 minute interval as required by the OST and TS. Instead, Operators continued to log AFD hourly until the error was detected at 2300 on June 23, 1993. <br /><br /> The cause of this event was personnel error on the part of the control room operators performing the manual AFD logging. Corrective actions include counseling the involved individuals, revising OST-1070 to require logging AFD at 30 minute intervals immediately upon declaring the AFD monitor inoperable, and disseminating information related to this event to other operations personnel. <br /><br /> This condition constitutes a TS violation and is being reported per 10CFR50.72(a)(2)(i)(b)
4101993001 | Nine Mile Point 2 | 01/05/1993 | 10/28/1993 | 9311040145 | <strong>Actuation of Engineered Safety Feature (ESF) due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1993 at 1124 hours, with the reactor at 100 percent power and the mode switch in the 'RUN' position (Operational Condition 1), Nine Mile Point Unit 2 (NMP2) experienced a loss of power to the Division II 4160 Volt Alternating Current (VAC) Emergency Switchgear (2ENS*SWG103), resulting in an actuation of Engineered Safety Features (ESF). The loss of power to the switchgear resulted in the following: 1) an auto start of the Division II Standby Emergency Diesel Generator (2EGS*EG3); and 2) an auto start of the Standby Gas Treatment System (GTS). The operators immediately verified reactor parameters were stable, 2EGS*EG3 had started, and GTS had auto initiated. The switchgear was repowered from its alternate offsite power source and 2EGS*EG3 and GTS were returned to standby. <br /><br /> A similar non-reportable event occurred on August 17, 1993. <br /><br /> Troubleshooting following this event revealed the root cause was radio frequency interference. The corrective actions were updated to the new root cause and include eliminating the use of radios in the switchgear rooms, and evaluating use of an external time delay circuit to prevent spurious trips of the breaker.
4101993002 | Nine Mile Point 2 | 02/21/1993 | 03/23/1993 | 9303290233 | <strong>Technical Specification Violation as a Result of Relay Reorientation due to Personnel Error and Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1993 at approximately 1400 hours, it was discovered during instrument and Control (I&C) surveillance testing that Nine Mile Point Unit 2 (NMP2) had been operating outside of Technical Specification requirements. Specifically, during performance of electrical preventive maintenance on January 23, 1993, two relays had been removed from their socket bases and reinstalled without the appropriate post-maintenance testing or proper installation verification to ensure the relay contacts would function properly. This action caused Technical Specifications 3.4.3.2d (Reactor Coolant System Leakage) and 3.5.1.a.1 (Emergency Core Cooling Systems) Limiting Conditions for Operation (LCO) to be exceeded. For the duration of this event the reactor mode switch was in the "RUN" position (Operational Condition 1) with the plant operating at approximately 100 percent rated thermal power. <br /><br /> The root causes of this event were personnel error due to improper relay installation and inadequate written communications during procedure development. Contributing causes to this event are lack of knowledge of relay characteristics and a failure to fully understand post-maintenance test requirements. <br /><br /> The immediate corrective actions were to restore the relays to their original as-tested condition, verification of relay operability and review of similar relay installations to ensure no other untested relay contacts were utilized in safety-related circuits. Additional corrective actions include: 1) revising relay removal/installation procedures; 2) requesting training on relay installation; 3) generating a Lessons Learned Transmittal; 4) reviewing maintenance procedures for similar problems; and 5) counseling electricians on the importance of self-checking and attention-to-detail.
4101993003 | Nine Mile Point 2 | 07/09/1993 | 08/09/1993 | 9308160168 | <strong>Violation of Technical Specification Surveillance Requirement Due to an Inadequate Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1993, the Operations Department determined that Nine Mile Point Unit 2 (NMP2) had operated outside of Technical Specification Surveillance Requirement 4.6.1.1.b from initial plant startup in the Spring of 1987 until March 1993. Specifically, manual vent, drain, and test valves on primary containment penetrations of the Residual Heat Removal System (RHS) and the Reactor Core Isolation Cooling System (ICS) were not verified to be closed at least once per 31 days as required by the Technical Specification Surveillance Requirement. These valves are required to be closed during accident conditions. At the time of this determination, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 100 percent rated thermal power. <br /><br /> The root cause of this Technical Specification Surveillance Requirement violation is inadequate technical review in preparing the original surveillance procedure. Contributing causes were deficient engineering design basis documentation, specifying the valves required to be verified closed, and inadequate control of revisions to the engineering document. <br /><br /> Corrective actions consisted of revising the surveillance procedure, verifying the closed position of the valves, and revising the engineering documentation. Processes involving technical accuracy of engineering lists, revisions to surveillance procedures and timeliness of response to discrepancies are being further evaluated.
4101993004 | Nine Mile Point 2 | 04/23/1993 | 05/21/1993 | 9306010218 | <strong>Surveillance Test not Performed per the Requirements of Appendix J due to Cognitive Error</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993 at 1100 hours, with the reactor at 100 percent power with the mode switch in RUN (Operational Condition 1), it was determined that Nine Mile Point Unit 2 (NMP2) was not in compliance with Technical Specification (TS) 4.6.1.2.d. An independent review of the NMP2 10 CFR 50 Appendix J Program revealed that metal expansion bellows incorporated into drywell penetrations for the Traversing Incore Probes (TIP) had been Type A tested versus Type B tested. <br /><br /> The root cause of this incorrect surveillance test is a cognitive error, that identified the bellows for Type A testing, without first securing an exemption from 10 CFR 50 Appendix J. <br /><br /> Corrective actions for this event included: 1) initiating a Deviation Event Report to track the issue, develop root cause, and precipitate effective corrective actions; 2) including penetrations 2NMT*Z31 A, C, D and E in 10 CFR 50 Appendix J Type B testing; 3) completing an Engineering Operability Determination; 4) preparing a schedular exemption request to permit delaying Type B testing of the TIP bellows until the next refueling outage; 5) performance of a physical examination of the expansion bellows; and 6) preparing an update to the Updated Safety Analysis Report to reflect the correct testing requirement as described in Appendix J.
4101993005 | Nine Mile Point 2 | 08/04/1993 | 09/02/1993 | 9309080284 | <strong>Technical Specification Violation Caused by Inadequate Surveillance Testing due to Inadequate Change Management</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1993, at approximately 1615 hours, it was discovered that Nine Mile Point Unit 2 (NMP2) was operating outside of a Technical Specification requirement to leak test Primary Containment isolation valves in accordance with 10 CFR 50 Appendix J. Specifically, four Containment Hydrogen Recombiner inboard isolation valves were non-conservatively tested in the direction opposite that which the valves would be exposed to during performance of their safety function. At the time of discovery, the mode switch was in the 'RUN' position (Operational Condition 1) with the plant at 100 percent rated thermal power. <br /><br /> The root cause of this event was determined to be inadequate change management. <br /><br /> The immediate corrective actions included commencing a shutdown until enforcement discretion could be obtained. Ultimately, an engineering Safety Evaluation was implemented to permit compliance with Technical Specifications. Additional corrective actions include: 1) updating source documentation; 2) correcting the inadequate procedures and conducting LLRTs of the valves; and 3) addressing the untimely review and resolution of this discrepancy. Improvements to the modification process were previously completed.
4101993006 | Nine Mile Point 2 | 09/16/1993 | 10/13/1993 | 9310200224 | <strong>Potential Common Mode Failure of Standby Gas Treatment System Charcoal Filter Adsorbers</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1993 at 1700 hours, with Nine Mile Point Unit 2 operating in Mode 1 at 100 percent power, it was determined that the charcoal filter adsorbers utilized as integral components of the Standby Gas Treatment System (GTS) had the potential for a common mode failure. <br /><br /> During routine surveillance testing on September 8, 1993, the Division II Standby Gas Treatment Filter GTS*FLT1B failed the bypass leakage criterion of less than 0.05 percent as specified in the Technical Specification. Visual inspection indicated that a significant area of the mesh portion of one of the six compartments was exposed.<br /><br /> As a result of this finding, Division I was also visually inspected on September 10, 1993. Although the Division I filter exhibited incipient indications of a similar degradation, the separator mesh was not exposed to the same extent as it had been in the other train. However, it was felt that Division I could have failed the Technical Specification criterion of 0.05 percent. Division I was declared inoperable, filled, tested satisfactory, and then declared operable. <br /><br /> The cause of the event has been determined to be inadequate written communication in the vendor manual. The analysis of the event determined that each filter train had sufficient efficiency to support the assumptions used to demonstrate compliance with 10CFR100 dose limits in the event of a design basis accident (DBA).<br /><br /> Corrective actions were to add charcoal to the safety related filter systems, to complete a satisfactory surveillance test on the GTS filters, and to initiate changes to the vendor manuals.
4101993007 | Nine Mile Point 2 | 11/03/1993 | 12/01/1993 | 9312100003 | <strong>Violation of Technical Specifications Found During a Verification of Engineering Design Basis Documents</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1993, the Operations Department determined had operated outside of Technical Specification 3/4.8.4, 'Electrical Equipment Protective Devices,' and its associated Surveillance Requirement since initial plant startup in the Spring of 1987. Specifically, three (3) AC circuits that penetrate the primary containment were not de-energized in Operational Conditions 1, 2 and 3 as required by Technical Specifications, and they were not verified to be de-energized at least once every 24 hours as required by the Technical Specification Surveillance Requirement. At the time of this determination, NMP2 was in the refueling condition (Operational Condition 5). <br /><br /> The root cause of this Technical Specification violation was determined to be inadequate work practices. The architect/engineer who prepared the list of 'Primary Containment Electrical Penetrations and Penetration Conductors Which are not Required During Reactor Operation and are Protected by De-energization,' failed to perform self-checking to ensure the completeness of this list. The list was prepared for inclusion into NMP2's Technical Specifications prior to initial plant startup.<br /><br /> Corrective actions include adding circuit 2SCA-PNL406 Bkr #9 to the procedure, 'List of Controlled Lists,' and to the USAR Table, 'Primary Containment AC Circuits De-energized. ' The Operations Surveillance Procedure to verify primary containment AC circuits de-energized has been revised to include circuit 2SCA-PNL406 Bkr #9. Outboard cables 2RCSANC528 and 2RCSBNC538 from panel 2SCI-PNLC104 switch #27 and switch #28 have been disconnected outside of primary containment by determinating the cables. Other Technical Specification tables which contain lists provided by the architect/engineer have been reviewed to verify their completeness.
4101993008 | Nine Mile Point 2 | 11/07/1993 | 12/01/1993 | 9312100002 | <strong>Engineered Safety Feature Actuations due to a Partial Loss of Offsite Power Caused by a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1993 at 1656 hours, Nine Mile Point Unit 2 (NMP2) experienced a partial loss of offsite power while transferring power supplies to one of the normal 13.8 KiloVolt switchgear. Specifically, the offsite switchyard breaker for Line #5 opened, causing a loss of power to the Division I emergency switchgear. This loss activated several Engineered Safety Features including: automatic start signal and loading of the Division I Standby Emergency Diesel Generator; automatic isolation of normal Reactor Building Ventilation; and automatic start of the Standby Gas Treatment System. Also, Shutdown Cooling was lost when the power supply to the Residual Heat Removal pump was lost. The plant was shutdown with the mode switch in 'REFUEL' (Operational Condition 5). The reactor vessel head was removed and the reactor cavity was flooded. <br /><br /> The root cause of this event is personnel error caused by poor work practices and inadequate self-verification techniques when two wires were improperly installed in the current transformer circuit. A contributing cause was inadequate post-maintenance testing. <br /><br /> Immediate corrective actions included verifying required actions occurred and placing the plant in a stable condition. Further corrective actions include: 1) performing additional functional testing of the Line #5 breaker wiring; 2) emphasizing proper work practices with personnel involved; 3) ensuring that the enhanced post-modification testing is performed when Line #6 breakers are replaced; and 4) requiring a technical review of relevant switchyard modifications.
4101993009 | Nine Mile Point 2 | 11/08/1993 | 12/02/1993 | 9312130376 | <strong>Engineered Safety Feature Actuations Resulting From a Loss of Power to RPS and PCIS Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0036 hours on November 8, 1993, Nine Mile Point Unit 2 (NMP2) experienced a full reactor scram signal, various Division I Primary Containment Isolation System (PCIS) actuations, and an automatic start of the Standby Gas Treatment System (GTS). Specifically, Uninterruptible Power Supply 2VBB-UPS3A was inadvertently de-energized causing a loss of power to the Reactor Protection System (RPS) and PCIS. At the time of the event, NMP2 was shut down in a refueling outage with the mode switch in 'Refuel' (Operational Condition 5). The reactor vessel head was removed, the reactor cavity was flooded, and the Neutron Monitoring System was in a non-coincident logic. <br /><br /> The root cause of this event is personnel error due to inadequate evaluation of plant impact. A contributing cause was an inadequate use of resources.<br /><br /> The immediate corrective actions included determining the cause for the loss of power to 2VBB-UPS3A and re-energizing the UPS. The scram signal was reset, a tripped temperature switch bypassed, and Shutdown Cooling restored. Additional corrective actions include: 1) counseling the operators involved; 2) verifying a generic weakness does not exist; 3) stressing management expectations and requirements for conduct of operations; and 4) conduct seminars for Station Shift Supervisors.
4101993010 | Nine Mile Point 2 | 11/08/1993 | 12/08/1993 | 9312160175 | <strong>Inoperability of High Pressure Core Spray System Due to an Equipment Deficiency, Inadequate Managerial Methods and Poor Work Practices</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1993 at approximately 1704 hours, a condition was discovered that could have prevented the Nine Mile Point Unit 2 (NMP2) High Pressure Core Spray (HPCS) System from performing its safety function. Specifically, a deficiency in the HPCS System injection valve motor contactor would have resulted in the valve failing to perform its intended safety function during a degraded voltage condition. On November 17, 1993 at approximately 0445 hours, while implementing a corrective action to address this contactor issue, a second condition was discovered which could have prevented die NMP2 HPCS System from performing its intended safety function. Specifically, the tap setting on the transformer controlling voltage to the HPCS motor control center was such that lower than adequate voltages could have been supplied to HPCS loads during a degraded voltage condition. At the time of both discoveries, the mode switch was in the "REFUEL" position (Operational Condition 5) with the plant at 0 percent rated thermal power. These conditions have existed since initial plant operation. <br /><br /> The root cause of the contactor condition was determined to be an equipment deficiency with a contributing cause of inadequate managerial methods. The root cause of the incorrect tap setting was determined to be poor work practices. <br /><br /> The corrective actions included replacing the deficient contactors with contactors of a different design and restoring the transformer tap setting to the original design setting to increase the voltage available to the HPCS loads.
4101993011 | Nine Mile Point 2 | 11/19/1993 | 12/20/1993 | 9401030215 | <strong>Reactor Scram and ESF Actuation Caused by Poor Work Organization and Planning</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1993 at 0337 hours while performing reactor vessel hydrostatic leak testing, Nine Mile Point Unit 2 (NMP2) received a Division 11 Redundant Reactivity Control System (RRCS) initiation signal, and a Division 11 Emergency Core Cooling System (ECCS) initiation signal. This caused a Division 11 Alternate Rod Insertion (ARI), a trip of the 'A' reactor recirculation pump, a Division 11 Emergency Diesel Generator (EDG) start, and a start of Residual Heat Removal (RHR) pumps 'B' and 'C'. The reactor was in mode 4 (Cold Shutdown) with one control rod fully withdrawn for scram time testing, reactor vessel level a Reactor approximately 457', and reactor pressure at approximately 1000 psig. At 0338 hours, a Reactor Prot ection System (RPS) full reactor scram signal was received due to a high level in the Scram Discharge Volume (SDV). <br /><br /> The root cause of this event was poor wor k organization and planning. The variable leg instrument root valve was closed prior to isolating instruments on the affected instrument line. The process of valving a level transmitter out of service then caused a hydraulic perturbation in the reference leg instrument line, initiating the Division II RRCS and ECCS signals. <br /><br /> Corrective actions include direction for Instrument and Control (I&C) personnel to review maintenance work packages that could affect plant instrumentation. Maintenance and Operations personnel will receive training in this event. The Work Planning Guide has been revised and other procedure changes will be evaluated.
4101993012 | Nine Mile Point 2 | 12/04/1993 | 12/30/1993 | 9401120202 | <strong>Reactor Scram Caused by a Turbine Trip Resulting From an Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>At 2018 hours on December 4, 1993, Nine Mile Point Unit 2 (NMP2) experienced an Engineered Safety Feature actuation. Specifically, an automatic reactor scram occurred caused by a turbine generator trip. At the time of the event, the reactor mode switch was in the "RUN" position (Operational Condition 1) with the plant operating at approximately 100 percent of rated thermal power.<br /><br /> The root cause of this event was equipment failure, which caused a generator runback and turbine trip. <br /><br /> The immediate corrective action was to respond to the reactor scram and turbine trip in accordance with plant operating procedures. Follow up corrective actions included: 1) determining the cause for the turbine trip; 2) replacing the faulty flow switch; 3) checking flow switch calibration every 18 months; 4) attempting to isolate the source of the foreign material in the failed component; and 5) sampling Stator Water for filterable impurities periodically. <br /> ?
4121993001 | Beaver Valley 2 | 01/26/1993 | 02/25/1993 | 9303020427 | <strong>Design Stress For The Auxiliary Feedwater System Exceeded Due To Water Hammer</strong><br /><i>Abstract:&nbsp;</i>On 1/26/93 at 1720 hours, the results of extensive engineering analysis of previous plant events identified that the stress on the Auxiliary Feedwater (AFW) piping to the 'C' Steam Generator, for combined water hammer and seismic events, exceeded the design stress allowables. It has been hypothesized that the 'C' AFW line has been subjected to water hammer due to steam pocket formation (voiding) and steam bubble collapse. There have been two events at Beaver Valley Power Station Unit 2 since it went operational in 1987 that have been attributed to water hammer. The location of the inside containment AFW check valves (inside CV's) and piping layout have the potential to cause voiding (see Figure 1). The inside CV's are located near the main feedwater lines causing the piping upstream to be at elevated temperatures. The inside CV's are also at a higher elevation than the AFW supply tank minimum water level. If the inside CV's leak rate is less than the outside CV's, the AFW piping will depressurize causing voiding upstream of the inside CV's due to elevated temperatures. AFW automatic actuation with unthrottled flow to a voided AFW line is the main concern for water hammer. There were minimal safety implications as a result of this event. The mechanical snubbers were replaced with new hydraulic snubbers with a higher load rating.
4121993002 | Beaver Valley 2 | 01/30/1993 | 03/01/1993 | 9303040201 | <strong>Reactor Trip and Safety Injection Due To Comparator Card Failure In A Main Steam Pressure Channel</strong><br /><i>Abstract:&nbsp;</i>On 1/30/93, with the Unit at 92 percent power, the bistables for Loop 'A' Channel II main steam pressure were in a tripped condition for transmitter replacement. At 0124 hours, the Loop 'A' Channel III main steam pressure transmitter experienced a fuse failure which tripped the bistables for that channel, generating a Low Steamline Pressure Safety Injection (SI) signal. The SI signal caused a reactor trip and SI flow to the reactor coolant system. Operations personnel entered Emergency operating Procedure E-0 and the plant was stabilized in Hot Shutdown. The emergency diesel generators started as designed, but did not load due to the availability of offsite power. The auxiliary feedwater pumps automatically started and supplied feedwater to the steam generators. All other SI equipment operated as designed. The cause for this event was a comparator card power supply failure in the 'A' Channel III main steam pressure circuit. This tripped the bistables for that channel, which in conjunction with the tripped bistables for Loop 'A' Channel II, resulted in a SI and reactor trip signal. There were no safety implications as a result of this event. The SI equipment including the emergency diesel generators, standby high head charging pump, auxiliary feedwater pumps, standby service water pump and the associated valves all actuated to their design positions.
4121993003 | Beaver Valley 2 | 02/05/1993 | 03/08/1993 | 9303110344 | <strong>Steam Generator Blowdown Isolation on High Blowdown Tank Level</strong><br /><i>Abstract:&nbsp;</i>On 2/5/93, with the Unit at 100 percent power, the steam generator blowdown (SGBD) system was being returned to service following the completion of a surveillance procedure on the SGBD radiation monitor. Local adjustments in SGBD flow were in progress to place the SGBD demineralizers in service. The SGBD tank level was within the normal operating level with the level control valve in automatic operation. The level control valve was then placed in manual and repositioned from 80% closed to 40% closed. At 1004 hours, the SGBD system isolated due to high level in the SGBD tank. When the isolation occurred the level indicator in the control room was showing the tank level to be approximately 4 inches below the isolation setpoint. This isolation is considered an Engineered Safety Features (ESF) component actuation by a non-ESF signal. The cause for the valve closure was an actual high level condition in the blowdown tank. This occurred due to discrepancies between the actual tank level and indicated tank level. It has been determined that the level transmitters, for the alarm and control functions, were not compensated for normal operating temperature and pressure. There were no safety implications as a result of this event. The steam generator blowdown isolation valves closed as designed on high level in the steam generator blowdown tank.
4121993004 | Beaver Valley 2 | 03/02/1993 | 04/01/1993 | 9304060247 | <strong>Steam Generator Blowdown Isolation While Troubleshooting DC Ground</strong><br /><i>Abstract:&nbsp;</i>On 3/2/93, Unit #2 was experiencing a 130 volt ground on DC-BUS-2-1. Procedure 2OM 39.4F, Clearing Grounds (125 VDC Busses 2-1 and 2-2), was in progress. The Nuclear Shift Supervisor and the Assistant Nuclear Shift supervisor discussed which circuits could be tested to locate the origin of the ground. They decided that breaker 8-1 on Panel DC2-07, power supply to 2MSS-SOV-105A Auxiliary Feedwater Pump Steam Valve, could be tested. By design, 2MSS-SOV-105A fails open when its supply breaker is opened. Consideration was given to the fact that as 2MSS-SOV-105A opened, a sudden surge of steam may cause the next, in series, valve to pop open. This, in turn, would start the Steam Driven Auxiliary Feedwater Pump. In order to prevent this, it was decided to isolate the trip throttle for the steam driven pump while the circuit was being tested. What was not realized was that when 2MSS-SOV-105A opens, with the plant in its current configuration, it completes the logic to initiate a Steam Generator Blowdown Isolation. At 0028 hrs. Breaker 8-1 on panel DC2-07 was opened to test that circuit. 2MSS-SOV-105A opened, as expected, and the Steam Generator Blowdown Outside Containment isolation valves automatically closed. This isolation is considered an unplanned Engineered Safety Features component actuation. There were no safety implications as a result of this event.
4121993005 | Beaver Valley 2 | 03/04/1993 | 04/02/1993 | 9304080219 | <strong>Potential for Inadequate Core Cooling Flow During Hot Leg Recirculation</strong><br /><i>Abstract:&nbsp;</i>The Westinghouse Electric Corporation recently notified Duquesne Light Company of an issue related to supplying sufficient flow to the reactor coolant system to maintain adequate core cooling following a postulated loss of coolant accident (LOCA). A Duquesne Light engineering evaluation of this information determined that inadequate core cooling could exist due to the postulated single failure of a motor operated valve (MOV) in the low head safety injection (LHSI) system. Approximately fourteen (14) hours following a large break LOCA, the safety injection system is transferred from the cold leg recirculation mode to the hot leg recirculation mode. This is performed to terminate boiling and to prevent boron precipitation in the core. During the realignment of the LHSI system, failure of the discharge MOV to open would prevent LHSI flow to the hot legs. If the operators did not restore the LHSI flow to the cold legs, and if the break was located on a hot leg (such that full high head safety injection (HHSI) flow did not reach the core) then adequate core cooling could not be assured. In order to prevent this situation, the emergency procedures have been revised to direct the operators to immediately restore cold leg recirculation flow from the LHSI system if hot leg flow can not be established.
4121993006 | Beaver Valley 2 | 03/12/1993 | 04/12/1993 | 9304150031 | <strong>Engineered Safety Feature Components Actuation Due to De- energization of the 1G 4KV Bus.</strong><br /><i>Abstract:&nbsp;</i>On 3/12/93, an automatic closure of the Steam Generator Blowdown Outside Containment isolation valves and an automatic realignment of the contiguous area ventilation from unfiltered to filtered exhaust occurred during a test of the Emergency Response Facility Diesel Generator. The diesel generator was connected to the 1G 4KV bus and loaded to approximately 300 KW. While the operator was adjusting the power factor, the diesel generator output breaker tripped on ground overcurrent. The normal supply to the 1G 4KV bus also tripped, leaving the bus momentarily de-energized and locked out. This caused the 480 Volt busses J and K, and L and M, to automatically tie together. The voltage disturbance then caused several radiation monitors to momentarily go into high alarm, resulting in the steam generator blowdown isolation and ventilation realignment. This event is categorized as an unplanned automatic repositioning of Engineered Safety Feature components. There were no safety implications as a result of this event. The diesel generator was shut down and normal power was restored to the 1G 4KV bus. The radiation monitors were reset. The Steam Generator Blowdown system was restored to its normal configuration and the contiguous area ventilation was restored to its normal exhaust path.
4121993007 | Beaver Valley 2 | 04/05/1993 | 04/30/1993 | 9305060176 | <strong>Inadequate Testing of Reactor Trip Breakers</strong><br /><i>Abstract:&nbsp;</i>On 4/5/93, with the Unit at 100% reactor power, a review of Information Notice 93-15 identified a deficiency in the testing of the reactor trip breaker manual shunt trip circuitry. Technical Specification (TS) Surveillance Requirement 4.3.1.1.1, Table 4.3-1, Item 1 requires independent testing of the reactor trip breaker shunt trip and undervoltage trip circuitry. The surveillance procedure utilized to satisfy this requirement failed to independently test the manually actuated shunt trip circuitry. This surveillance procedure was in effect since initial Unit startup in 1987. The cause of this event is a deficient procedure. A Discretionary Enforcement request was approved, permitting continued unit operation until the next entry into Operating Mode 3. The surveillance procedure was revised to include an independent check of the manual shunt trip circuitry. There were minimal safety implication as a result of this event. The Solid State Protection System was verified to indirectly energize the shunt trip coil, upon manual actuation, through testing conduced by Instrument and Control personnel. Testing of the automatic actuation of both the undervoltage and shunt trip circuitry was properly included in station procedures and was available at all times.
4121993009 | Beaver Valley 2 | 09/02/1993 | 09/30/1993 | 9310040410 | <strong>Failure to Calibrate Radiation Monitor Velocity Probes</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1993, a review of the Maintenance Work Request (MWR) history for five Technical Specification gaseous effluent monitoring instrumentation channels that use velocity probes for process flow rate indication revealed that the probes associated with gaseous effluent radiation monitors for the Waste Gas Storage Vault (2RMQ-RQ303) and Condensate Polishing Building Vent (2HVL-RQ112) were not calibrated during the last 18 month interval as required by Technical Specification Surveillance requirement 4.3.3.10. Since the velocity probes associated with the gaseous effluent radiation monitors for the Waste Gas Storage Vault and Condensate Polishing Building Vent were not calibrated within the required Technical specification Surveillance interval, the probes were declared inoperable on 9/2/93 at 1200 hours and the appropriate Technical specification Action statements were implemented. <br /><br /> Since methods in the Offsite Dose Calculation Manual (ODCM) assume maximum possible flow via these gaseous effluent pathways, there were no safety implications associated with the missed surveillances. <br /><br /> This event is being reported in accordance with 10 CFR 50.73.a.2.i.B.
4121993010 | Beaver Valley 2 | 10/04/1993 | 11/03/1993 | 9311090105 | <strong>Reactor Coolant RTD Insulation Breakdown</strong><br /><i>Abstract:&nbsp;</i>On 10/4/93, an inspection of a previously failed reactor coolant loop resistance temperature detector (RTD) identified deteriorated electrical insulation. RTD's are used to monitor reactor coolant loop temperature and provide inputs to the reactor control and protection system. The inspection found that the insulation on the wiring internal to the RTD instrument head had deteriorated. The deterioration was to the point where the insulation had burned away from the wires, shorting out the terminals. Additional inspections of the RTD's on the remaining reactor coolant loops showed evidence that these RTD's were also exposed to overheating, but the deterioration to the insulation was less severe. The elevated temperatures resulted from improper thermal insulation installation in the area where the RTD's penetrate the Reactor Coolant System piping. Safety implications due to this event were minimal. Failure of the inservice RTDs would have been detected during power operation, allowing corrective action to be implemented promptly. Since the RTD wiring was exposed to temperatures exceeding design, this event is being reported as a condition outside the component design basis in accordance with 10 CFR 50.73.a.2.ii.B.
4121993011 | Beaver Valley 2 | 10/06/1993 | 11/05/1993 | 9311100182 | <strong>Containment Closure Defficiency During Refueling</strong><br /><i>Abstract:&nbsp;</i>On 10/06/93, with Unit 2 in Refueling Mode 6, core off load was in progress with containment ventilation flow isolated. At 0935 hours, a construction supervisor performing a safety tour through the East Cable Vault heard air flow coming from an electrical penetration. An improperly installed temporary seal on a spare electrical penetration was leaking air from Containment (CNMT) into the cable vault. The penetration was used to route temporary cable for steam generator tube inspection equipment in CNMT. Using air operated equipment inside CNMT created a gradual increase in CNMT pressure, resulting in a pressure differential between CNMT and the cable vault. Construction Supervision promptly contacted the control room and refueling personnel ceased fuel movement. With fuel movement halted, the CNMT ventilation dampers were opened at 0957 hours equalizing the pressure differential and eliminating the air leakage. The penetration was subsequently sealed and tested. The cause of this event was the incomplete installation of a temporary seal on a spare penetration through the primary containment building.
4121993012 | Beaver Valley 2 | 11/06/1993 | 12/06/1993 | 9312130369 | <strong>Emergency Diesel Generator Sequencer Circuit Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 11/04/93, a test to verify the automatic loading capability, on a Safety Injection Signal (SIS), for the 2-1 Emergency Diesel Generator (EDG) failed. The Unit was in Cold Shutdown at the time of the testing. The test verifies that all loads will deenergize on the respective safety-related emergency busses and that the EDG sequencer circuitry will automatically load safety-related loads at specified time intervals, following starting of the EDG. On 11/06/93, the 2-2 EDG also failed its respective test for automatic loading capability. The cause of the test failures was the misoperation of a digital (microprocessor based) solid state timer associated with the Load Sequencer circuitry. An inductive voltage surge was produced by the deenergization of auxiliary relays within the Load Sequencer circuit during the SIS reset of sequencer operation. This caused the timer to misoperate resulting in the failure of the sequencer. Voltage suppression diodes were added to the auxiliary relays within the sequencers' circuit to eliminate the voltage surge. This event constituted a common mode failure which could have safety implications during an event involving a loss of offsite power and safety injection actuation. Operator action may have been required to manually sequence Emergency Diesel Generator loads.
4121993014 | Beaver Valley 2 | 11/29/1993 | 08/02/1994 | 9408050153 | <strong>Required Plant Shutdown Due to Inoperable Steam Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On 11/29/93, with the Unit in Hot Standby (Operational Mode 3) and the reactor trip breakers open, it was determined that maintenance activities on the steam driven auxiliary feedwater pump would not be completed within the ACTION statement requirements of Technical Specification (TS) 3.7.1.2. The steam driven auxiliary feedwater pump, 2FWE*P22, had been declared inoperable at 0516 hours on 11/26/93 for maintenance on the steam supply valves. Since additional maintenance on the valves and governor became necessary and could not be completed prior to expiration of the action statement for an inoperable steam driven auxiliary feedwater pump, a plant cooldown was initiated at 0325 hours on 11/29/93. In accordance with the Emergency Preparedness Plan, an Unusual Event was declared at 0328 hours, due to the required plant cooldown to Hot Shutdown. The Unusual Event was terminated following entry into the Hot Shutdown mode at 1005 hours on 11/29/93. The cause for this event was improper reassembly of 2MSS*SOV105A, and a stem failure on 2MSS*SOV105D. The governor problems were due to incorrectly sized buffer springs and stem corrosion. There were minimal safety implications as a result of this event. The motor driven auxiliary feedwater pumps remained operable throughout this event. Reactor core decay heat level was low due to having been shutdown for a refueling outage.
4121993015 | Beaver Valley 2 | 12/05/1993 | 01/04/1994 | 9401190005 | <strong>Oxygen Analyzers Inoperable Due to Closed Inlet Valve</strong><br /><i>Abstract:&nbsp;</i>On 12/05/93 at 1921 hours, with the Unit in Hot Shutdown, operations personnel received a 'High Oxygen Concentration' alarm associated with the Gaseous Waste System Oxygen Analyzers. An investigation identified that the Oxygen Analyzers Inlet Header Isolation Valve, 2GWS-306, was closed. The valve was returned to its normally open position and the High Oxygen Concentration alarm cleared. Technical Specification 3.3.3.10 requires the Oxygen Analyzers to be operable during Gaseous Waste Storage Tank filling evolutions. If the analyzers are inoperable, grab samples are required when filling the tanks. Computer trend logs were reviewed and it was identified that there were elevated oxygen levels, (0.9 percent as compared to a normal 0.5 percent value), for the preceeding three days. The investigation could not identify when 2GWS-306 was shut. The Gaseous Waste Storage Tanks were filled on 11/27/93, and it is assumed that 2GWS-306 may not have been open during this evolution. Since the oxygen analyzers were apparently inoperable, and no grab samples were taken during the filling of the storage tanks, the ACTION statement of Technical Specification 3.3.3.10 was not complied with. This is reportable in accordance with 10CFR50.73 a 2 i.B. There were minimal safety implications as a result of this event. The highest oxygen levels identified, 3.3 percent, were below the explosive threshold values.
4121993016 | Beaver Valley 2 | 12/09/1993 | 01/07/1994 | 9401120109 | <strong>Inadvertent Deactivation of CIA Signal From Two Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 12/09/93, with the Unit at 30 percent reactor power, operations personnel were performing a surveillance test on a containment isolation valve. The valve failed to close and was declared inoperable at 0557 hours. The associated outside containment isolation valve was closed and deenergized in accordance with Technical Specification 3.6.3.1. On 12/10/93 at 0943 hours, it was discovered that one train of Containment Isolation Phase 'A' (CIA) signal had been inadvertently defeated from two outside containment isolation valves. This unintentional defeating of the CIA signal occurred when the outside containment isolation valve circuit was de-energized on 12/09/93. The cause for this event was personnel error. The control room staff failed to adequately review the breaker load list when deenergizing the breaker for the outside valve used to isolate the penetration. The breaker load list identified the additional CIA circuits powered from the referenced breaker. A temporary modification was implemented which restored the CIA input signal to the two affected valves. There were minimal safety implications as a result of this event. One of the two valves was in its normally closed position, and the remaining valve was capable of manual closure. Additionally, the inside containment isolation valves were operable throughout this time frame.
4131993002 | Catawba 1, Catawba 2 | 02/25/1993 | 04/05/1993 | 9304130424 | <strong>Technical Specification 3.0.3 Entered Due To Inoperable Pump Discharge Valves</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1993, at 1431 hours, with Unit 1 in Mode 1, Power Operation, at 100 percent power, and Unit 2 in No Mode, Defueled, 'B' train Nuclear Service Water (RN) System pump discharge valves (1(2)RN38B) failed to open during RN pump start. At 1745 hours, Unit 1 entered Technical Specification (TS) 3.0.3 due to both trains of RN being inoperable due to 'A' train having a potential for similar problem. At 2205 hours, valve 1RN38B was declared operable and Unit 1 exited TS 3.0.3. Failure of the RN pump discharge valves to open has been attributed to a lack of detailed information in the motor operated valve (MOV) torque switch setup procedure, sizing variables that are possibly inadequate for these specific applications and/or a potentially degraded valve subcomponent. Corrective actions include adjusting valve settings for both Unit 1 and Unit 2 valves, evaluating similar valves in other applications, and further Engineering evaluation and testing. During this event, Operations failed to perform a Power Availability Test within one hour of declaring the Diesel Generators inoperable due to RN being inoperable. This resulted in a TS Surveillance being missed. The missed TS Surveillance is attributed to policy guidance that was not well defined or understood. Corrective actions included performing the TS Surveillance, developing a TS Interpretation, and training.
4131993003 | Catawba 1, Catawba 2 | 02/17/1993 | 03/18/1993 | 9303220270 | <strong>Technical Specification Required Surveillance Not Performed</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1993, Catawba Component Engineering personnel received an Operation Experience (OE) report documenting a problem discovered at South Texas, Unit 1. The OE report stated that a surveillance review task force had discovered that the portion of the containment Spray (NS) system channels between the process instrumentation with the Engineered Safety Features (ESF) actuation and logic instrumentation was not being properly tested. Upon examination, the Component Engineering personnel discovered that same problem existed at Catawba. The required testing was satisfactorily completed on February 18, 1993. Unit 1 was in Mode 1, Power Operation, at 100 percent power at the time the event was discovered. Unit 2 was in No Mode, Defueled. This event is assigned a cause of Deficient Written Communication due to relevant information being omitted from the surveillance test procedures because individuals developing the test procedures did not recognize the significance of the test points used to verify continuity of NS circuitry. The circuits in question were subsequently verified. Procedure changes will be implemented to ensure proper verification of continuity during future surveillance tests.
4131993004 | Catawba 1 | 03/05/1993 | 04/05/1993 | 9304130328 | <strong>Missed Technical Specification Surveillance of AC Offsite Power Sources</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1993 at 2301 hours, with Unit 1 operating in Mode 1, Power Operation, at 100 percent power, Technical Specification (T/S) surveillance requirement 4.8.1.1.1a was missed when AC offsite power sources were not verified operable within one hour of the Unit 1A Diesel Generator (D/G) being declared inoperable. The Train A D/Gs were inoperable due to a hydro alignment on the Nuclear Service Water (RN) system. The oncoming shift noticed they had not received turnover on the next required T/S surveillance and verified the operability of AC offsite power sources on March 6 at 0920 hours. The root cause of this incident is attributed to deficient work practices, in that the required verification was not performed. A contributing cause of this incident is deficient written communication, information concerning actions to be performed when a D/G is declared technically inoperable was not addressed in the appropriate procedure. Corrective actions include informing other shifts about this incident and procedure revisions.
4131993005 | Catawba 1, Catawba 2 | 03/01/1993 | 04/01/1993 | 9304060262 | <strong>Technical Specification Test Deficiency Due To Manufacturer Fabrication</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1993, Unit 1 was in Mode 1, Power Operation, and Unit 2 was in No Mode, Defueled. A Nuclear Regulatory Commission Resident Inspector notified Component Engineering that Solid State Protection System (SSPS) wiring errors had been found at facilities with similar equipment. On March 2, at 1200 hours, it was determined that wiring for the SSPS Train A, Phase B Containment Isolation logic test circuit for both units was incorrect although the manufacturer documentation was correct. Unit 1 entered the 24 hour action statement under Technical Specification 4.0.3, Limiting Conditions For Operation And Surveillance Requirements. Work requests were initiated to correct the wiring and to verify operability of the logic circuits. Unit 1 SSPS was corrected and tested by 1645 hours. Unit 2 was corrected and tested on March 9 at 1415 hours. The manufacturer's representative has distributed an information notice to address these wiring problems. This event was attributed to a manufacturer fabrication deficiency.
4131993006 | Catawba 1 | 06/12/1993 | 03/01/1994 | 9403160053 | <strong>Reactor Trip Due To Blown Fuse In Intermediate Range Channel</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1993, a Unit 1 Reactor (Rx) Trip occurred at 1042 hours while shutting down to make repairs in the Main Condenser. Unit 1 was in Mode 2, Unit Startup, at Hot Zero Power, on the way to Mode 3 via control rod insertion, when an automatic Rx trip was initiated by the Intermediate Range (I/R) Channel N35 Hi Flux Rx Trip Bistable. This signal was generated by the loss of control power voltage to N35 caused by a blown fuse. Main Feedwater (CF) System isolation occurred immediately upon Rx Trip due to Rx Coolant (NC) System Average Temperature being below 564 degrees F. Both Motor Driven Auxiliary Feedwater (CA) System Pumps were manually started to reinitiate NC cooldown. CA flow was throttled to control NC cooldown. Pressurizer (Pzr) pressure and level had already decreased significantly before the trip; the subsequent cooldown, caused by CA, resulted in a decrease of Pzr level below 17 percent which initiated letdown isolation. Letdown was restored approximately nine minutes later when Pzr level and pressure were recovered. The cause of the blown fuse was determined to be a combination of two factors: 1) control power in rush capacity problem and 2) an intermittent internal failure of the detector high voltage power supply. Corrective actions included replacing the power supply and replacing all control power fuses with a type that has a much higher in rush current capacity.
4131993007 | Catawba 1 | 03/15/1993 | 04/14/1993 | 9304190249 | <strong>Engineered Safety Feature Actuation Due to An Unexpected System Interaction</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1993, at 1501 hours, an unexpected Engineered Safety Feature (ESF) Actuation occurred on Unit 1 while in Mode 1, Power Operation. Upon receipt of a spurious signal, Auxiliary Feedwater (CA) System Motor Driven Pumps (MDP) 1A and 1B started simultaneously. The Steam Generator Blowdown (BB) system and the Steam Generator sampling portion of the Nuclear Sampling (NM) system isolated as designed. Component Engineering (CE) investigated this incident and determined that the spurious signal originated in the final output relays of the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC). Corrective action included securing the CA Motor Driven Pumps, realigning BB and NM valves, and the replacement of the two final output relays of the AMSAC system in Unit 2. Planned corrective action includes the replacement of the two final output relays in the Unit 1 AMSAC system during the next unit outage and a review to determine if Struthers-Dunn 219 type relays are used in other areas of the station which may be susceptible to high vibration.
4131993008 | Catawba 1 | 07/18/1993 | 08/17/1993 | 9308250013 | <strong>Reactor Trip and Auxiliary Feedwater System Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On July 18 at 2031 hours, with Unit 1 in Mode 1, Power Operation at 100% power, a Reactor Trip occurred due to low-low level in Steam Generator (S/G) 1A. Engineering was replacing a backup processor in the Digital Feedwater Control System (DFCS). As the processor was inserted the redundant processor failed, causing Main Feedwater (CF) and all S/G controls to swap to Manual and several Control Room (C/R) indications for S/G 1A to be driven to zero. This led C/R Operators to believe CF flow was lost, therefore they opened a CF valve to restore flow. When a S/G 1A High High Level Alert annunciator was received, CROs realized flow had not been lost and began to close the CF valve. The resulting transient caused the low-low S/G 1A level and Reactor Trip. On July 19 at 0030 hours, with Unit 1 in Mode 3, Hot Standby, Engineering was restoring the DFCS when an Auxiliary Feedwater System autostart occurred. The output control card (QAM) for CF Pump 1A speed control had swapped to its backup QAM. Upon reset to the primary QAM, with the backup in manual mode, a positive step change occurred causing CF Pump 1A to trip due to high discharge pressure. These incidents are attributed to Equipment Specification/Manufacture due to special installation instructions that were not provided. Corrective actions include a review of failure modes for DFCS, a review of spare DFCS parts, and procedure revisions.
4131993009 | Catawba 1 | 09/23/1993 | 10/25/1993 | 9311020139 | <strong>Technical Specification 3.0.3 Involving Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1993, at 1322 hours, with Units 1 and 2 in Mode 1, Power Operation, at 100% power, Technical Specification (T/S) 3.0.3 was entered due to both trains of the Control Room Ventilation (VC) and Chilled Water (YC) Systems being inoperable. Train 'B' of the VC/YC System was declared inoperable on September 22 at 0110 hours for preplanned preventive maintenance. On September 23, at 1322 hours, T/S 3.0.3 was entered when YC chiller 'A' tripped due to an inadvertent internal conductor removal during the completion of a Nuclear Station Modification. Subsequent corrective action re-terminated the conductor and the chiller was restarted at 1342 hours. After an engineering review of the event and Instrument and Electrical (IAE) Quality Control inspection of the re-termination, T/S 3.0.3 was exited at 1504 hours. This event is attributed to failure to adequately perform self-checking/independent verification to ensure the correct internal conductor was being removed from service. Corrective action included additional training for the technicians involved in the event and a communication of the event to other IAE technicians along with recommended action to prevent recurrence. Planned corrective action includes a review of the event by the site Human Performance Enhancement System (HPES) group and a site wide notification of this event to inform station personnel and to reiterate the importance of self-checking/Independent Verification.
4131993010 | Catawba 1, Catawba 2 | 11/23/1993 | 12/22/1993 | 9312300173 | <strong>Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1993, at 1000 hours, Unit 1 status was No Mode, for refueling outage 1EOC7 and Unit 2 was in Mode 1, Power Operation, 100% power. Station management determined, after reviewing station procedures and Technical Specifications, that the Technical Specification test interval for the surveillance in Section 6.8.4 was not met. A program to reduce external leakage from those systems outside containment that could contain highly radioactive fluids during a serious transient or accident was developed. During implementation of the program, the support group included the 25% grace period allowed in Technical Specification 4.0.2 to the test interval. The grace period is not allowed for this particular surveillance located in Technical Specification 6.8.4. The root cause of this incident is attributed to less than adequate management direction due to Technical Specification 4.0.2 being improperly applied to Section 6.8.4. Corrective actions include procedure changes and a review of Technical Specifications to determine if 4.0.2 is inappropriately applied to other sections of Technical Specifications.
4131993011 | Catawba 1 | 12/20/1993 | 01/19/1994 | 9401280082 | <strong>Technical Specification Surveillance Interval Exceeded</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1993, with Unit 1 in Mode 5, Cold Shutdown, Component Engineering determined that the Technical Specification (T/S) 3/4.7.8 surveillance interval for snubber visual inspections had been exceeded. The latest allowable completion date for the accessible snubber visual inspections, including the twenty-five percent allowable extension per T/S 4.0.2, was November 20, 1993. Mechanical Maintenance personnel performing the inspections were not aware of the latest allowable completion date since it was not specified on the Work Order. Upon notification of the T/S violation, Maintenance personnel expedited the snubber inspections; all inspections were complete on December 21, 1993. All snubbers were determined to be operable. This incident is attributed to document use practices. The surveillance inspection interval for T/S 3/4.7.8 was revised in 1991 per Amendment 88 (Unit 1) and Amendment 82 (Unit 2). Catawba Station Directive (S.D.) 2.1.7, Final Safety Analysis Review (FSAR) and T/S Amendment Processing and Interpretation, was not adequately followed which resulted in model work orders not being updated to reflect the change in the snubber T/S surveillance interval. Corrective actions include the revision of model work orders associated with T/S 3/4.7.8 to include the revised surveillance inspection interval to ensure tracking via the Work Management System (WMS), review/ enhancements of S.D. 2.1.7, and a review of T/S changes to assure required documents were revised following T/S changes.
4131993012 | Catawba 1 | 12/25/1993 | 01/24/1994 | 9402080213 | <strong>Unit 1 Entered Mode 3 With Inoperable Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On December 25, 1993, at 1546 hours, Unit 1 entered Mode 3, Hot Standby, from Mode 4, Hot Shutdown, following refueling outage 1EOC7 with the Turbine Driven Auxiliary Feedwater Pump (CAPT) inoperable. Two of the Main Steam Supply System (SA) valves to the CAPT had been previously tagged closed for maintenance. Unit 1 Operations shift personnel were aware of the SA valve tagout. The Unit 1 Operations shift reviewed the Technical Specification (T/S) along with the associated T/S Interpretation and concluded that entry into Mode 3 was allowable. On December 26, the SA valves were opened and the CAPT was successfully tested. This event has been attributed to incorrect use of T/S and T/S Interpretations. Corrective actions include review and revision of associated T/S and T/S Interpretations, issuance of an operator update referencing the causes of this event, and an evaluation of Operation procedures to determine if hold points are necessary to prevent reccurence.
4141993001 | Catawba 2 | 02/21/1993 | 03/23/1993 | 9303290202 | <strong>Unit 2 Essential Auxiliary Power System Blackout Due To Missed Procedure Step</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1993, at 0957 hours, Unit 2 status was No Mode, Defueled, for refueling outage 2EOC5. The 4160 V Essential Auxiliary Power System (EPC) Train B (ETB) was powered from Unit 1 through alternate feeder SATB. Diesel Generator (D/G) 2B was removed from service for scheduled maintenance. During performance of the D/G 2B Load Sequencer timer calibration test, a procedure step placing the sequencer in the test mode was inadvertently missed. When the test sequence was initiated, a blackout resulted. On February 22, at 0955 hours, problems with the Train B Control Room Area Ventilation (VC) System required that Train A be placed in service. However, the Train B fans continued to run since the sequencer latch circuit was not reset after sequencer initiation. Case 2 of AP/2/A/5500/07, Loss of Normal Power, did not require resetting the sequencer latch circuit. After the circuit was reset, Train A VC was placed in service. This event is attributed to work practices in that the test procedure was not followed properly. The procedure steps that places the sequencer in test were missed. Subsequent corrective actions included removing power to the sequencer and restoring power to 2ETB. Planned corrective actions include revisions to procedures associated with the D/G sequencer, and to determine if caution signs inside the sequencer cabinets are necessary.
4141993002 | Catawba 2 | 03/31/1993 | 04/29/1993 | 9305050090 | <strong>Engineered Safety Feature Actuation When Steam Dump Valves Opened</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1993, at approximately 0858 and 2123 hours, two unexpected Engineered Safety Feature (ESF) Actuations occurred on Unit 2 while in Mode 2, Startup. A third ESF actuation occurred on April 1, 1993 at approximately 0921 hours, while in Mode 1, Power Operation, at 15 % power. The ESF actuation, P-12 (Lo Lo Tave), occurred when two banks of valves in the Steam Dump System opened thus bringing average Reactor Coolant System (NC) temperature (Tave) below P-12 setpoint of 553 degrees F. Control Room Operators took immediate action to close the Steam Dump Valves each time. Due to a P-12 actuation that occurred in 1992, monitoring equipment had been installed on the Steam Pressure Controller to help identify the cause of future spurious P-12 actuations. Data from the monitoring equipment indicated a problem with a power supply card and pressure transmitter. Therefore, this incident is attributed to a degraded subcomponent. Corrective actions included replacement of the power supply card and pressure transmitter.
4141993004 | Catawba 2 | 01/31/1993 | 10/25/1993 | 9311020178 | <strong>Ice Condenser Door Opened Due To Residual Heat Removal System Transient</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1993, at 0644 hours, Unit 2 was in Mode 4, Hot Shutdown. Control Room Operators noted a decrease in Reactor Coolant (NC) Pressurizer level and an increase in Pressurizer Relief Tank (PRT) level while placing Residual Heat Removal (ND) System Train A in service. Failure of a ND vent line weld released water into the Containment Building in addition to a ND relief valve that was opening prematurely to die PRT. An Ice Condenser (NF) door open annunciator that initiated and immediately cleared during this event was not determined to be an Emergency Safeguard Feature (ESF) actuation. The Ice Condenser door opening was later determined to be reportable. Investigation of die vent line determined a weld had been damaged by vibration during previous water hammer events. Subsequent corrective actions included weld replacement in the affected area and evaluation of die broken section of pipe. Planned corrective actions include modification of ND vent valve piping. The Ice Condenser door opening event was not reported due to an inadequate policy/procedure. Planned corrective actions include determination of reporting requirements, procedure changes and associated training. This Licensee Event Report is a revised Station Report that is being submitted due to additional evidence that the NF door had opened.
4161993001 | Grand Gulf 1 | 01/11/1993 | 02/10/1993 | 9302170160 | <strong>No Licensed SRO in Control Room During Operational Condition 1</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1993 at approximately 0050 CST, a disturbance was heard outside of the control room. The sounds of distress were thought to be a woman calling for help.<br /><br /> Two of the three licensed reactor operators (RO), along with the licensed senior reactor operator (SRO) went to the control room door to investigate the matter. The remaining RO stayed at the reactor controls. The SRO stepped into the stairwell to intervene in the disturbance. After the SRO was in the stairwell, the control room operator at the door stepped back into the control room and allowed the door to close. The control room was without an SRO for approximately 5 minutes. Plant conditions did not change during the time the control room was without an SRO. Therefore, this occurrence did not compromise the health and safety of the public.
4161993002 | Grand Gulf 1 | 03/22/1993 | 04/22/1993 | 9304270173 | <strong>Primary Containment Penetration Over Current Protection Not Tested</strong><br /><i>Abstract:&nbsp;</i>During a review of design drawings, it was determined that two electrical circuits installed through a containment electrical penetration were not identified as being associated with plant Technical Specifications. As a result, no functional test of the circuit breaker protection was documented. Upon discovery of the condition, the breaker supplying power to the crane, along with the breaker for its control power were taken to the open position. A nonconformance report was initiated to document this condition. The protective devices were tested in accordance with approved plant procedure and an evaluation was performed to determine if a potential for a degraded condition existed. The results of the test verified proper operation of the protective devices. The electrical circuits were installed in accordance with a design change package in 1986. Penetration overcurrent protection was installed in accordance with the requirements of Regulatory Guide 1.63. However, reviews did not identify that the breaker protective devices should have been included in the plant's Technical Specifications. The above electrical circuits will be added to the applicable table to ensure all requirements are met.
4161993003 | Grand Gulf 1 | 03/24/1993 | 08/12/1993 | 9308160346 | <strong>Loss of Single Train Safety System Function</strong><br /><i>Abstract:&nbsp;</i>Grand Gulf Nuclear Station (GGNS) Division III standby service water (SSW C) system pump motor failed on March 24, 1993 The failure occurred approximately five and one-half hours into the weekly eight hour recirculation run. SSW C provides cooling water for the high pressure core spray (HPCS) pump room coolers and Division III standby diesel generator. <br /><br /> The cause of the motor failure was investigated by the motor manufacturer. This investigation determined that the motor stator end windings apparently were moving during motor start-ups. The end winding movement likely caused a turn-to-turn electrical short which subsequently caused a phase-to-phase short in the motor windings The motor had an estimated total run time of twenty-five hundred hours The suspected cause of the motor failure was initially reported as an apparent phase-to-phase or phase-to-ground short in the motor. The motor was reconditioned by the manufacturer An NPRDS report was submitted for the failed motor. <br /><br /> All safety related equipment operated as designed. Safety and health of the general public were not compromised by this event not compromised by this event
4161993004 | Grand Gulf 1 | 05/17/1993 | 06/16/1993 | 9306230242 | <strong>Topaz Inverter Failure Results in Isolation of Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1993, the Inboard Containment Isolation Valve which supplies steam to the Reactor Core Isolation Cooling (RCIC) System automatically isolated. The isolation is attributed to the erratic behavior of a division 2 trip unit inverter. The associated trip units generated trip signals to several division 2 card files. This resulted in the RCIC System actuating and immediately isolating. RCIC did not inject into the vessel. Vessel level remained within normal operating limits during this occurrence. Operations personnel declared RCIC inoperable and the appropriate technical specification actions were taken. The malfunction of the inverter did not degrade the ability of other safety systems to perform their intended functions. The health and safety of the public were not compromised during this occurrence.
4161993005 | Grand Gulf 1 | 06/08/1993 | 07/08/1993 | 9307150195 | <strong>Reactor Core Isolation Cooling Steam Pressure Instrumentation Not Properly Surveilled</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1993 during a review of Westinghouse response time test results, it was indicated that the response time test for the Reactor Core Isolation Cooling (RCIC) low steam pressure isolation instrumentation was invalid. The Westinghouse process noise ('white noise') method had been used for the response time testing during the last three test. RCIC was declared inoperable and the pressure instrumentation was tested using the hydraulic ramp method. The test was successfully completed and RCIC was restored to operable status. The white noise method will not to be used for response time testing for the subject instrumentation. No safety functions or components were compromised as a result of this condition. Therefore the condition did not adversely impact the health and safety of the public.
4161993006 | Grand Gulf 1 | 07/20/1993 | 10/22/1993 | 9310270248 | <strong>Update to Reactor Core Isolation Cooling Steam Supply Isolation Due to an Invalid Temperature Signal</strong><br /><i>Abstract:&nbsp;</i>On July 20 and July 21, 1993, an annunciator was received in the control room. The annunciator specified a high temperature in the Residual Heat Removal system equipment room. As a result of the invalid temperature signal, the outboard steam supply valve for the Reactor Core Isolation Cooling system isolated. The invalid temperature signal was generated due to the failure of an equipment room differential temperature switch. A preliminary investigation was performed and revealed an inadequate wiring connection in the failed switch. Based on subsequent tests, it appears that the component malfunction was not caused by the connection. It appears that the failure of the Riley temperature switch generated an erroneous high temperature signal to the isolation logic. GGNS is in the process of replacing failed temperature switches with a newer model. The health and safety of the public were not compromised at any time during this incident.
4161993007 | Grand Gulf 1 | 07/23/1993 | 12/03/1993 | 9312170080 | <strong>Update to Violation of Operating License Condition 2.C.(38) Control Room Envelope</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1993, plant personnel were in preparation to perform a functional test of the Control Building Fire Detection System as required by GGNS Technical Requirements Manual. The test is performed at least once per 184 days. In order to test two of the nine required smoke detectors, the associated access panel had to be removed. Prior to the start of the applicable portion of the surveillance, it was noted that the access panel was a part of the control room envelope boundary. Opening this panel would introduce an open area of approximately 576 square inches which would exceed the allowable opening area. Introducing an opening of this size would have required a review by the Plant Penetration Coordinator. This review had not been performed. Therefore, this portion of the surveillance was not performed. A subsequent review was performed to identify prior tests which have opened the access panel without the proper reviews. Even though each performance of the test violated the OL Condition, only three cases were cited to substantiate prior violations of the OL Condition. Neither in-the-field personnel nor control room personnel realized that the access panel was a part of the envelope boundary. Plant personnel did not regard the access panel as a penetration. They were unaware that this type opening should be controlled by plant procedures governing work on penetrations. The procedure governing the functional test did not reference the penetration control procedure which would have caused personnel to perform a more in-depth evaluation of the opening of the access panel. Labels were placed on control room envelope boundary access panels. Additionally, plant personnel were trained on the event via the required reading program.
4161993008 | Grand Gulf 1 | 09/13/1993 | 10/13/1993 | 9310190119 | <strong>Reactor Scram Due to Actuation and Injection of High Pressure Core Spray</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1993 during normal plant operations, an actuation of the High Pressure Core Spray system occurred. Reactor vessel water level increased to high water level scram setpoint. Reactor water level decreased to approximately -36 inches and was restored by the Feedwater system. The plant was stabilized in accordance with plant procedures. A subsequent investigation revealed that the HPCS initiation was the result of low water level signals from the C and G channels of HPCS level instrumentation. It is believed that flow impingement as a result of a displaced jet pump mixer caused perturbations in the HPCS level instrumentation. The unit was required to shut down due to an inoperable jet pump. Additional information associated with the jet pump malfunction will be submitted in an upcoming submittal. This report also serves as a Special Report pursuant to GGNS Technical Specification 3.5.1.h. The HPCS actuation and injection did not degrade the capability of any safety related plant system. Therefore the health and safety of the public were not compromised as a result of this occurrence.
4161993009 | Grand Gulf 1 | 09/28/1993 | 04/15/1995 | 9504190082 | <strong>Update to Completion of TS Required Reactor Shutdown due to Jet Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>During plant startup on September 28, 1993, operations personnel increased core flow to support a power ascension. At approximately 77 percent core flow, personnel observed oscillations on several plant level instruments which were indicative of a displaced jet pump mixer. The jet pump was declared inoperable. GGNS TS 3.4.1.2 requires all jet pumps to be operable while in OPERATIONAL CONDITIONS 1 and 2 or be in HOT SHUTDOWN within 12 hours. The action statement was entered at 0500 on September 28, 1993. The mode switch was placed in shutdown at approximately 1641. <br /><br /> Visual inspection of the # 10 jet pump, revealed a displaced mixer assembly. The jet pump mixer, along with the ram's head, was propelled out of its diffuser and came to rest against an adjacent jet pump assembly. A portion of the failed beam was retrieved and tested to determine the failure mechanism. Test results indicated that the beam failed due to IGSCC. <br /><br /> The failure of the jet pump did not significantly impact the ability to mitigate the consequences of an accident because all plant ECCS systems were available during OPERATIONAL CONDITION 1 to provide sufficient makeup to maintain adequate vessel level in the event of a loss of vessel inventory. The health and safety of the public were not compromised as a result of this condition.
4161993010 | Grand Gulf 1 | 10/04/1993 | 02/14/1994 | 9402280050 | <strong>Loss of Shutdown Cooling and ESF Actuation During Unit Outage Due to Class 1E Bus Voltage Oscillations</strong><br /><i>Abstract:&nbsp;</i>Automatic closure of Grand Gulf Nuclear Station's (GGNS) residual heat removal (RHR) system containment isolation valve 1E12F008 occurred while RHR B was operating in shutdown cooling mode. This automatic closure resulted in RHR B pump tripping. 1E12F008 is the outboard isolation valve on the common suction line for RHR A and RHR B. The closure signal was generated when voltage fluctuated on the Division I Class 1E 125 vdc bus due to a faulty current limiting card in one of two full capacity battery chargers, thereby causing relays to deenergize and initiation of engineered safety features (ESF) equipment.<br /><br /> Investigation determined that the event was caused by failure of a current limiting card in the battery charger. The investigation also identified that written communications failed to identify a precaution which contributed to the event. The faulty current limiting card was replaced. The appropriate procedures were modified to warn of precautions and limitations of the affected plant equipment. An NPRDS report was submitted for the faulty card. Maintenance history of the battery chargers was also reviewed.<br /><br /> Loss of shutdown cooling events have occurred previously at GGNS due to causes unrelated to this event. LER 90-023, LER 90-022, LER 89-004, LER 87-021, and LER 87-020 discussed details of those events. A similar ESF actuation due to loss of power to the bus as a result of a failed inverter was discussed in LER 85-038. <br /><br /> Safety related equipment with exception of charger 1A4 operated as designed. Safety and health of the general public were not compromised by this event.
4161993011 | Grand Gulf 1 | 10/07/1993 | 02/04/1994 | 9402170147 | <strong>Loss of Shutdown Cooling and ESF Actuation During Unit Outage Due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>Automatic closure of Grand Gulf Nuclear Station's (GGNS) residual heat removal (RHR) system containment isolation valve 1E12F009 occurred while RHR B was operating in shutdown cooling mode, This automatic closure resulted in RHR B pump tripping. 1E12F009 is the inboard isolation valve on the common suction line for RHR A and RHR B. Additional ESF systems actuated as a result of this event. The closure signal was generated when station operators manually opened the feeder breaker to the alternate power supply for Class 1E distribution panel 1Y85. <br /><br /> Immediate corrective actions included briefing Operations personnel on the event. Issuance of a standing order to require that an information tag be placed on the inverter barrel switch and the alternate source feeder breaker when the inverter is switched to its alternate power supply. Signs were also placed on the alternate power source supply breakers. These signs give appropriate details for inverter verification which would be required prior to the opening of the breakers. <br /><br /> A similar ESF actuation and loss of shutdown cooling event occurred at GGNS just three days prior to this event, but was caused by a faulty battery charger. LER 90-023, LER 90-022, LER 89-004, LER 87-021, and LER 87-020 discussed details of previous loss of shutdown cooling events at GGNS. A similar ESF actuation due to loss of power to the bus as a result of a failed inverter was discussed in LER 85-038. <br /><br /> Safety related equipment operated as designed. Safety and health of the general public were not compromised by this event.
4161993012 | Grand Gulf 1 | 10/14/1993 | 02/25/1994 | 9403040356 | <strong>Spurious ESF Actuation of Secondary Containment Isolation Valves During Unit Outage</strong><br /><i>Abstract:&nbsp;</i>Automatic actuation of an engineered safety feature (ESF) system occurred at Grand Gulf Nuclear Station (GGNS) on October 14, 1993. Secondary containment isolation valves closed automatically upon receipt of an apparent spurious isolation signal. <br /><br /> Immediate investigation did not determine the cause. Subsequent investigation determined the most probable cause of the actuation was inadvertent operation of relay 1B21K17A. This determination was based on review of electrical and control system drawings for equipment that actuated. The wiring and connections in panels 1H13P623 and 1H13P871 will be inspected as plant conditions permit. Repairs will be made as necessary. Relay 1B21K17A had been replaced in November 1990 as a preventive measure based on service life. Operating history revealed no previous spurious operation of the relay. <br /><br /> Safety related equipment operated as designed upon generation of the isolation signal. Safety and health of the general public were not compromised by this event.
4161993013 | Grand Gulf 1 | 10/24/1993 | 11/25/1993 | 9312030220 | <strong>Inadvertent Actuation of Drywell Purge Compressor</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1993 plant personnel were preparing to perform a repetitive maintenance task for the Division 2 Combustible Gas Control System (CGCS) [BB]. This evolution required the normal electrical line-up to be altered by opening the breaker for the Division 2 drywell purge compressor and removing the fuse for the CGCS control logic. Due to inadequate communications, the fuse was removed prior to opening the breaker, which deenergized the system control logic and resulted in an automatic start of the purge compressor. The compressor started and ran for approximately two minutes. The system was reset and placed in standby. The cause of this occurrence is failure to follow procedure. Involved personnel were counselled and other operations personnel were informed of the incident. A plant deficiency report was written to document this event and evaluate any further action which would enhance this process. The plant was in Mode 5 and the CGCS was not required to be operable at the time of occurrence. The initiation of the drywell purge compressor did not pose any undue risk to the health and safety of the public. The system ran for approximately two minutes and did not degrade the ability of other safety systems to perform their intended function.
4161993014 | Grand Gulf 1 | 10/27/1993 | 04/15/1994 | 9404200211 | <strong>Update to Pressure Boundary Leakage Due to Thermowell Failure</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1993, plant personnel identified a leak from the thermowell associated with the temperature element for the suction of the 'B' reactor recirculation water pump. Evaluations determined the thermowell had a through-wall leak. The thermowell was replaced and retested satisfactorily. The remaining reactor recirculation thermowells were inspected and no evidence of leakage was identified. Based on subsequent reviews, it was concluded that the most probable cause of failure is flow-induced high cycle low stress fatigue. The current design will be evaluated to determine if redesign is necessary. The failed thermowell did not place the plant in an unanalyzed condition. The leakage that would be experienced in the event of complete failure of the thermowell would have been well within the bounds of the GGNS accident analyses. The failure did not degrade any systems needed for emergency core cooling. Therefore the health and safety of the public were not compromised.
4161993015 | Grand Gulf 1 | 11/08/1993 | 03/08/1994 | 9403140317 | <strong>ESF Actuation While Troubleshooting Control Room Alarm</strong><br /><i>Abstract:&nbsp;</i>Automatic actuation of a Grand Gulf Nuclear Station (GGNS) engineered safety feature (ESF) system occurred on November 8, 1993. Automatic startup of the drywell purge compressor occurred while station electricians were troubleshooting a system annunciator for the Division I purge compressor. <br /><br /> Investigation determined that the root cause of the event was inadequate preparation for the troubleshooting efforts to correct the alarm. Adequate review of electrical prints should have revealed the incorrect wiring of a purge compressor control relay following calibration. The wiring was corrected and the alarm functioned properly. <br /><br /> Restoration requirements for the calibration were deficient. Specific guidance will be developed for this relay calibration as a result of this event. In addition, this condition was reported under the plant's quality deficiency program via QDR 93-0268. All identified deficiencies will have corrective actions developed as appropriate under the quality deficiency program.<br /><br /> Safety related equipment operated as designed upon generation of the isolation signal. Safety and health of the general public were not compromised by this event. .
4161993016 | Grand Gulf 1 | 11/08/1993 | 03/08/1994 | 9403140340 | <strong>ESF Actuation While Performing Surveillance</strong><br /><i>Abstract:&nbsp;</i>Automatic actuation of a Grand Gulf Nuclear Station (GGNS) engineered safety feature (ESF) system occurred on November 8, 1993. Automatic closure of containment isolation valves occurred while station and contract personnel were performing a functional surveillance of its control system. While connecting a recorder, the grabber end of the recorder lead contacted a terminal which caused the circuit's power supply fuse to open. Closure of multiple containment isolation valves ensued when the fuse opened.<br /><br /> Investigation determined that this actuation was a result of not having implemented corrective actions determined necessary as a result of a previous identical event. Test jacks were installed following this event. In addition, Operations and Maintenance departments developed a review plan for installation of test jacks. Discussions were conducted with Maintenance I&C supervisors to reinforce the necessity of adequately briefing technicians for work assignments. In addition, all station I&C technicians have reviewed the event. <br /><br /> Safety related equipment operated as designed upon generation of the isolation signal. Safety and health of the general public were not compromised by this event.
4161993017 | Grand Gulf 1 | 11/26/1993 | 12/23/1993 | 9401030273 | <strong>Reactor Core Isolation Cooling System Not Operable As Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>While commencing unit startup following the sixth refueling outage, iron concentration exceeded EPRI guideline limits for feedwater. Operations personnel were performing appropriate portions of the reactor core isolation cooling (RCIC) surveillance when reactor pressure exceeded the limit specified by GGNS Technical Specification (TS) 3.7.3 with RCIC inoperable. This resulted in noncompliance with TS 3.0.4. <br /><br /> The licensed operator in charge of unit startup had not ordered that control rod movements be ceased soon enough. A contributing factor was that the digital pressure gauge used for monitoring the reactor pressure actually indicates steam pressure for the high pressure turbine first stage. This gauge indicates pressure at about five to eight psig less than steam dome pressure. Other pressure indications on the same control room panel are more difficult to monitor. <br /><br /> Personnel involved in the event were counseled. The need for increased awareness during unit startup was re-emphasized to operators along with discussion that a fast unit startup should not be a priority. The startup procedure did not specify actions to be taken when feedwater chemistry is out of specification and contained inadequate instructions for suspension of control rod movements so that compliance with TS 3.0.4 is maintained. An additional enhancement being considered is that the condensate and feedwater systems be put in their water chemistry cleanup cycles earlier as part of the unit startup evolution in order to preclude the limitations of out-of-spec feedwater. <br /><br /> Health and safety of the general public were not compromised by this event.
4161993018 | Grand Gulf 1 | 12/13/1993 | 01/12/1994 | 9403140376 | <strong>Reactor Core Isolation Cooling Steam Supply Isolation Due to an Invalid Temperature Signal</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1993, an annunciator was received in the control room. The annunciator specified a high temperature in the Residual Heat Removal system equipment room. As a result of the invalid temperature signal, the outboard steam supply valve for the Reactor Core Isolation Cooling system isolated. The invalid temperature signal was generated due to the failure of an equipment room differential temperature switch. It appears that the failure of the Riley temperature switch generated an erroneous high temperature signal to the isolation logic. Switch connections were checked and no problems were identified. The faulty switch was replaced. GGNS is in the process of replacing failed temperature switches with a newer model. The health and safety of the public were not compromised at any time during this incident.
4161993019 | Grand Gulf 1 | 11/22/1993 | 09/01/1994 | 9409120016 | <strong>Voluntary Report on Potential Common Mode Failure of Anchor Darling Valves in Safety Related Systems</strong><br /><i>Abstract:&nbsp;</i>Plant maintenance personnel were preparing to perform static diagnostic testing of a high pressure core spray (HPCS) system globe valve when the valve yoke failed catastrophically. The yoke cracked 360 degrees circumferentially in the necked transition region. The yoke is one piece cast carbon steel. Disassembly of 1E22F011 revealed that the valve disc and disc nut had separated from the stem, thereby causing an internal interference condition. The interference condition subjected the valve to overthrust conditions beyond its design limits during the closing stroke. <br /><br /> The failed valve was inspected for effects of the overthrust operation. The valve was reworked by replacing the yoke and other components. Two other similar valves were inspected and found to have the threaded disc/disc nut connection loosening. Affected valves will be modified by installation of two pins to secure the threaded disc/disc nut connection. <br /><br /> The pinning of the disc/disc nut should preclude future similar events due to this failure mechanism. The manufacturer reported that newer model valves feature a pinned disc/disc nut assembly. <br /><br /> This LER is being submitted as a voluntary report to describe the potential that previous corrective actions may not have been sufficient to address disc-to-stem separation for some valves. General Electric issued Service Information Letter 435 in 1986 to address the potential of disc separation and other characteristics of HPCS valves. This incident did not impair the ability of any system to perform its safety function, but some facilities may have susceptible valves whose failure would have potential safety consequences. Health and safety of the general public were not compromised by this event.
4231993001 | Millstone 3 | 01/26/1993 | 02/25/1993 | 9303040114 | <strong>Failure to Verify Testing of NIS Inputs Into Westinghouse 7300 Process Control System Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1430 hours on January 26, 1993, while in Mode 1 at 100% power, a procedure deficiency in the testing of the Nuclear Instrumentation System (NIS) upper and lower Flux circuit input to the Westinghouse 7300 Process Controls System was identified. During a review of vendor start-up manuals and surveillance procedures. Instrumentation and Controls personnel discovered that the signal path from the NIS Axial Flux circuit input into the Westinghouse 7300 Process Control System was not periodically tested under any Instrumentation and Controls surveillances. Testing of this circuit is required by Plant Technical Specifications. Upon notification of the testing deficiency, Unit 3 Operations entered the appropriate Limiting Condition for Operation (L.C.O.) <br /><br /> The root cause of the event is a procedural deficiency. The procedure associated with the NIS Axial Flux circuit input into the Westinghouse 7300 Process Control System does not verify that the circuit is adequately tested. <br /><br /> Changes were incorporated into the applicable surveillance procedures and the NIS inputs were satisfactorily tested the 'as-found' condition. <br /><br /> This review process is part of a continuing effort to identify and correct overlap deficiencies in existing procedures as a result of the concerns of LER 91-025, dated September 10, 1991.
4231993002 | Millstone 3 | 02/07/1993 | 05/07/1993 | 9305140059 | <strong>Common Mode Failure of Control Room Envelope Pressurization System</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1993, at 1938 hours with the plant in Mode 1 at 100% power the A Train Control Room Pressurization System failed its 18 month pressurization surveillance test. On February 6th the B Train had initially failed its surveillance test. An investigation revealed two potential common mode failures and both trains were declared inoperable pending further investigation. <br /><br /> The first potential common mode failure is freezing of the pressure regulating valve caused by moisture in the air banks. The second common mode failure is pressure oscillations within the control room envelope which cause the differential pressure to periodically fall below the .125 in wg acceptance criteria for brief periods of time. <br /><br /> The immediate corrective action was to place the Control Room in filtered recirculation in accordance with Technical Specification 3.7.8.b.1. The B Train surveillance was satisfactorily performed after a throttle valve was opened further. The air banks were purged and refilled with dry air to reduce the dewpoint.
4231993003 | Millstone 3 | 03/29/1993 | 04/28/1993 | 9305050174 | <strong>Inadequate Testing of Slave Relays</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1993, at 2000 hours with the plant in Mode 1 at 100% power, a deficiency in the surveillance procedures for testing slave relay actuations was discovered. The deficiency was related to inadequate slave relay testing, of Air Operated Valves (AOVs) for Auxiliary Feedwater Pump alternate suction, Demineralized Water Storage Tank path to the Auxiliary, Feedwater Pump Isolation Valves, and the Auxiliary Feedwater Pump Discharge Crossover valves. In addition, one of the contacts from this relay eliminates a time delay for an Emergency Diesel Generator start when an Emergency Bus Degraded Voltage Condition occurs. The discrepancy, was discovered during a Unit 3 Operations Department drawing review. Operations Department personnel discovered that these AOVs are actuated during a Containment Isolation Phase-B (CIB). These AOVs are driven by,a slave relay, which had not been verified through the slave relay operability testing procedure. Testing of this relay is required by Plant Technical Specifications. A task force was assigned and additional testing deficiencies were identified, <br /><br /> The root cause of this event was determined to be a management deficiency during the procedure development. During test development neither an individual nor a group was assigned to ensure that department procedures were integrated to test all circuits and components receiving actuation signals. <br /><br /> Upon notification Unit 3 Operations entered the appropriate Limiting Condition for Operations (LCO). Actions were taken to ensure that proper testing was conducted. All components tested satisfactorily in their "as found" condition.
4231993004 | Millstone 3 | 03/31/1993 | 08/31/1993 | 9309090435 | <strong>Reactor Trip Due to Electro-Hydraulic Control Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>At 0103 on March 31, 1993, with the plant in Mode 1 at 100% power, a turbine valve closure resulted in a reactor trip followed by a turbine trip. <br /><br /> Turbine valve closure was the result of a faulty power supply in the Electo-Hydraulic Control (EHC) system. With the exception of a steam generator code safety valve not completely reseating, the plant responded normally to the transient. <br /><br /> Extensive trouble shooting determined that a power supply in the EHC system was faulty and caused the turbine valves to close. The faulty power supply was replaced. As action to prevent recurrence, the power supplies in the EHC system will be replaced or refurbished on a 10 year period. <br /><br /> Subsequent investigation determined that the steam generator safety valve which did not completely reseat had an incorrect lower adjustment ring setting. Additional inspection revealed that 7 other safety valves also had incorrect settings. Three of these valves indicated that they lifted and reseated during the transient. The other four valves did not open. <br /><br /> The root cause of the improper settings was inadequate work control by the vendor. Crosby Valve and Gage Company, who performed maintenance on the safeties, conducted an investigation and determined that their personnel inadvertently used the wrong procedure to set the lower adjustment rings.
4231993005 | Millstone 3 | 05/20/1993 | 06/18/1993 | 9306280209 | <strong>Inadequate Overlap Testing</strong><br /><i>Abstract:&nbsp;</i>On May, 20, 1993 at 1400 with the plant in Mode 1 at 100%, the Cold Over Pressure Protection System (COPPS) was declared inoperable due to inadequate surveillance testing. The surveillance requirement is a monthly test of the circuit from the sensor up to but not including valve operation. However, only the portion of the circuit from the sensor to the input relays to Solid State Protection System were tested at this frequency. The discovery was made by the task force reviewing overlap testing issues. This task force was established as a corrective action to Licensee Event Report 93-003. Four other inadequate surveillance tests were discovered in the next twelve days.<br /><br /> The root cause of the event was a management deficiency in that a comprehensive approach to testing was not implemented during procedure development at plant start up. While the exact circumstances of the inadequate tests were different, they all indicate that unusual conditions were not always considered during procedure development. A broader overview of testing may have detected these deficiencies. <br /><br /> The immediate corrective action was to declare the affected component or system inoperable and enter the appropriate Limiting Condition for Operation (LCO) Action Statement. All in service components have been tested to confirm operability. <br /><br /> As action to prevent recurrence, the overlap task force will continue to look for other situations where inadequate testing exists. The task force's charter is to review overlap testing for reactor trip and Engineered Safety Features actuations. In addition, the task force will recommend methods for implementing a comprehensive approach for current test development.
4231993006 | Millstone 3 | 05/25/1993 | 06/21/1993 | 9306300144 | <strong>Inadequate Surveillance Testing of High Pressure Safety Injection Check Valves</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1993 at 1730 with the plant in Mode 1 at 100%, two High Pressure Safety Injection (SIH) discharge check valves were declared inoperable due to inadequate testing. The In Service Test (IST) Manual specified a quarterly partial stroke test of the two valves. The discovery was made during a review of the SIH system by the Reliability Centered Maintenance group. <br /><br /> The apparent root cause of the event was personnel error. A planned relief request to delete the requirement to test these valves was never submitted but the surveillance procedure was changed based on a verbal commitment. <br /><br /> The immediate corrective action was to declare the two valves inoperable. A test was written and performed to demonstrate operability of the valves within the time allowed by surveillance requirement 4.0.3. This test will be performed on a quarterly basis as required. <br /><br /> As action to prevent recurrence, the need to verify that surveillance procedure changes reflect actual changes to the IST manual is being reinforced with the Operations and Engineering Departments. Additionally, an audit of the IST manual will be performed to ensure that all testing requirements are incorporated in surveillance procedures.
4231993007 | Millstone 3 | 06/11/1993 | 07/09/1993 | 9307200173 | <strong>Reduction in Emergency Diesel Generator Fuel Oil Storage Capacity</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1993, at approximately 1044, in Mode 1 at 100% power, plant management concluded that the reduction in available Emergency Diesel Generator (EDG) fuel oil supply below the capacity discussed in the Safety Evaluation Report and Final Safety Analysis Report constituted an event outside the design basis of the plant. Storage tank capacity was reduced from a 3-1/2 day EDG run time, to slightly greater than 3 days. The two tank storage capacity to support 7 day operation of a single EDG was reduced to slightly greater than 6 days. The day tank storage capacity was reduced from 1-1/2 hours to 3/4 of an hour. The reduced capacity resulted from revised calculations and were not the result of physical modifications. <br /><br /> The root cause of this event is inadequate design interface. <br /><br /> No immediate corrective actions were required and the EDGs are considered operable. <br /><br /> A proposed License Amendment will be submitted by August 31, 1993. A temporary fuel oil tanker is being utilized to provide approximately 7,000 gallons of additional fuel oil, pending issue resolution. <br /><br /> By July 31, 1993, guidance to order fuel oil, and to initiate a load shedding evaluation, will be incorporated into the emergency response procedures. A re-evaluation of the loss of coolant accident and loss of off-site power load shedding calculation will be performed by October 31, 1993, to demonstrate the ability to extend EDG run times.
4231993008 | Millstone 3 | 06/14/1993 | 07/09/1993 | 9307220022 | <strong>Main Steam Valve Building Temperature Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1993, at 1200 with the plant in Mode 1 at 100%, one channel of the Electrical Environmentally Qualified (EEQ) temperature monitor (datalogger) for the Main Steam Valve Building was found to be indicating improperly. The discovery was made by a Plant Equipment Operator (PEO) while on routine rounds. Further investigation determined that when the datalogger had been upgraded on May 28, 1993, two channels had been assigned to the same detector.<br /><br /> The root cause of this event was personnel error. The technician assisting in the upgrade of the datalogger incorrectly entered part of the software. As a result, two channels were assigned to the same sensor. A line by line review of the software by the vendor and the technician did not detect the error. Subsequent retest did not detect the error either, despite the fact that a 27 degree Fahrenheit difference existed between 'as found' and 'as left' data. <br /><br /> The immediate corrective action was to declare the channel inoperable and begin logging temperature manually to satisfy the surveillance requirement. <br /><br /> As action to prevent recurrence, the technicians and supervisor involved have been counseled on work control and importance of performing retests. First line supervisor's responsibility for technical review of results of retests has been reinforced.
4231993009 | Millstone 3 | 06/17/1993 | 10/29/1993 | 9311040195 | <strong>SLCRS Potentially Inoperable in Past Cold Weather Periods</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1993, at 1055 hours with the plant in Mode 1 at 100% power, the plant determined that the Supplemental Leak Collection and Release System (SLCRS) may have been inoperable during certain cold weather periods in the past. <br /><br /> This determination was based on the temperature induced pressure gradient phenomena involving the containment Enclosure Building. As outdoor air temperature decreases and building elevation increases the net differential pressure decreases. This phenomena was not accounted for in the plants SLCRS Technical Specification acceptance criteria since the differential pressure was measured at lower elevations and not corrected.<br /><br /> No immediate corrective action was required. SLCRS operation has been verified to meet draw down pressure requirements for the most probable worst case cold weather temperature differentials.
4231993010 | Millstone 3 | 07/07/1993 | 08/06/1993 | 9308120095 | <strong>Reactor Trip to Turbine Interlock Not Adequately Tested</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1993, at 1010 with the plant in mode 1 at 100%, the Reactor Trip (P-4) input to the Turbine Trip portion of the Engineered Safety Features Actuation System (ESFAS) was declared inoperable due to inadequate surveillance testing. Limiting Condition for Operation (LCO) 3.0.3. was entered. The surveillance requirement is a TRIP ACTUATING DEVICE OPERATIONAL TEST (TADOT) on an 18 month basis. However, four isolators which provide the contacts to the turbine trip circuit were not included in the test. The discovery was made by the task force reviewing overlap testing issues. This task force was established as a corrective action to Licensee Event Report 93-003. <br /><br /> The root cause of the event was a management deficiency in that a comprehensive approach to testing was not implemented during procedure development at plant start up. A broader overview of testing may have detected this deficiency. <br /><br /> The immediate corrective action was to write and perform a test to verify operability of the previously omitted portion of the circuit. <br /><br /> As action to prevent recurrence, the overlap task force will continue to look for other situations where inadequate testing exists. The task force's charter is to review overlap testing for reactor trip and Engineered Safety Features actuations. A surveillance test procedure will be developed to test the isolators and their associated contacts on the required frequency.
4231993011 | Millstone 3 | 07/31/1993 | 08/30/1993 | 9309090353 | <strong>Main Steam Safety Valve Lift Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1993 at 2100 with the plant in Mode 3 (Hot Standby), ten of twenty Main Steam Safety Valves did not lift within the tolerance allowed by Technical Specifications. (One of the ten did not lift within +/-3% of the setpoint.) The discovery was made during the plant shutdown for a refueling outage. <br /><br /> The root cause of this event is unknown. Setpoint drift is a problem that has occurred previously but the cause has not been determined. <br /><br /> No immediate corrective action was required because the plant was already in Hot Standby and the setpoint for the Power Range Neutron Flux High Trip was already reduced to 10%. However, all ten valves were reset and verified to be within the required tolerance. <br /><br /> As action to prevent recurrence, the unit is pursuing relaxation of the +/- 1% tolerance to +/- 3%. This would have caused nine of the ten valves to be within this specification.
4231993012 | Millstone 3 | 08/05/1993 | 11/15/1993 | 9312020306 | <strong>"A" Train of Service Water System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1993 at 1730 with the plant in Mode 5, a piece of plywood was discovered in the "A" train of the Service Water System. Two days later another piece was discovered in another part of the "A" train. This had the potential to make the "A" train inoperable. No actual flow obstructions were observed. The plywood was discovered during inspection of the Service Water System at the beginning of the unit's refueling outage. <br /><br /> A root cause analysis determined that inadequate work planning by the Construction Department was the root cause of the event. The differences between the area around the tee and other work areas were not accounted for in specifying the cleanness class to be maintained inside the pipe.<br /><br /> To prevent recurrence during the recently concluded refueling outage, attention to the introduction of large objects and the close out inspection of the Service Water System was increased. <br /><br /> Additionally, the following actions are planned:<br /><br /> - all plant personnel who write work orders or function as job supervisors will be instructed that strict compliance with existing work control requirements is expected.<br /><br /> - all Construction job supervisors will be instructed to improve documentation of actual work performed on work orders.
4231993013 | Millstone 3 | 09/01/1993 | 09/27/1993 | 9310040319 | <strong>Reactor at Power Permissive Bistable Set to Incorrect Value</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1993 at 1500 with all fuel removed from the core, an engineer determined that the Reactor at Power Permissive (P-10) bistable reset function had been calibrated lower than the Allowable Value specified by Technical Specifications. The bistable trip function was calibrated consistent with the Technical Specification Setpoint at all times. <br /><br /> Because the plant was already shutdown, no immediate corrective action was required. <br /><br /> The inappropriate action in this event was submission of Technical Specifications with mutually exclusive conditions for the P-10 interlock. <br /><br /> The fact that P-10 performs an interlock function on both trip and reset makes it a unique situation. This led to confusion during original procedure development and subsequent reviews. This contributed significantly in failure to address the problem earlier.
4231993014 | Millstone 3 | 09/03/1993 | 11/12/1993 | 9312020263 | <strong>Train A of Supplemental Leak Collection and Release System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1993, at 1100 with all fuel removed from the core, it was determined that a delayed start of the Train A Auxiliary Building Filter fan during surveillance testing was caused by an inherent design characteristic of the flow switch in the fan control circuit. The flow switch is physically located at the Train B fan to sense opposite train air flow. Due to the design of the flow switch, the fan was not permitted to start immediately after a Loss of Power (LOP). The actual test failure occurred on August 28, 1993 during LOP testing. The delay was repeated twenty four hours later during the Engineered Safety Features/Loss of Power test.<br /><br /> The root cause of this event was a lack of understanding of the flow switch response to a Loss of Power event. <br /><br /> All safety related ventilation systems which utilize these flow switches were analyzed and a design change has been completed to provide an uninterruptable power source to the various flow switches. <br /><br /> Subsequent events on October 13 and October 17 revealed additional design problems in the Auxiliary Building Ventilation System. <br /><br /> To prevent recurrence, a task force was formed to enhance the design of the Auxiliary Building Ventilation System to better support the Supplemental Leak Collection and Release System. A complete failure modes effects analysis on these ventilation systems was performed by the task force. No design changes were required to correct issues identified by this analysis. A Technical Specification change to extend the draw down time requirement to 2 minutes was submitted. <br /><br /> This supplemental report is being issued to report the subsequent events.
4231993016 | Millstone 3 | 10/01/1993 | 10/29/1993 | 9311050158 | <strong>Plant Outside Design Basis Due to Improper Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1993, with the plant in Mode 5, it was determined that a non-conservatism existed in the analysis for one of the plant's licensing basis accidents. Under a new, conservative scenario postulated by Westinghouse for the Inadvertent Emergency Core Cooling System (ECCS) Actuation at Power event, the pressurizer could fill, leading to the pressurizer safety valves opening and relieving water Since the valves are not designed to relieve water, it is postulated that they would not close, thereby leading to a non-isolable small break loss-of-coolant-accident (SBLOCA) through the pressurizer safeties. This violates the plant's design basis in that a Condition II event (Inadvertent ECCS Actuation at Power) could lead to a Condition III event (SBLOCA) without any independent events occurring. <br /><br /> The root cause of this event was a technical error that resulted in assumptions being used in the Inadvertent ECCS Actuation at Power event analysis that were not conservative with respect to pressurizer overfill. A Justification for Continued Operation (JCO) has been developed and reviewed to allow startup from the current refueling outage. Westinghouse will reanalyze this accident by April 1, 1994.
4231993017 | Millstone 3 | 10/06/1993 | 11/02/1993 | 9311100199 | <strong>Inadequate Response Time Testing</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1993, at 1600 with the plant in Mode 5, the RESPONSE TIME test for Turbine Trip on high/high Steam Generator Level (P-14) portion of the Engineered Safety Features Actuation System (ESFAS) was determined to be inadequate. The RESPONSE TIME of the turbine trip slave and interposing relays and isolators was not measured. The discovery was made by the task force reviewing overlap testing issues. This task force was established as a corrective action to Licensee Event Report 93-003. <br /><br /> Further investigation revealed that interposing relays for the Main Steam Isolation Valves (MSIVs) in the Main Steam Isolation circuit were not included in RESPONSE TIME testing. <br /><br /> The root cause of the event was a management deficiency in that a comprehensive approach to testing was not implemented during procedure development at plant start up. A broader overview of testing may have detected this deficiency. The immediate corrective action was to modify the surveillance procedure to measure the RESPONSE TIME of the previously omitted components. As action to prevent recurrence, the overlap task force will review previously reported cases of inadequate overlap testing to ensure that the RESPONSE TIME testing for these components is correct.
4231993018 | Millstone 3 | 10/10/1993 | 11/02/1993 | 9311100200 | <strong>Continuous Fire Watch Improperly Removed</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1993, at 1300 with the plant in Mode 5, the Shift Supervisor discovered that a required continuous fire watch had not been posted in the East Switchgear Room since September 21, 1993. The discovery was made during review of an automated work order at the completion of work on an associated fire assembly. <br /><br /> The root cause was inappropriate management decision. Several shift supervisors did not use the required method of tracking justification of fire watches when additional duties were assigned to the established fire watch. <br /><br /> As immediate corrective action, the proper fire watch was verified to be in place.<br /><br /> As action to prevent recurrence, the Operations Department Manager directed all Shift Supervisors to ensure that they comply with all configuration management requirements.
4231993019 | Millstone 3 | 10/19/1993 | 11/18/1993 | 9312010078 | <strong>Lifting of Pressurizer Safeties Above the Allowed Tolerance Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1993, Wyle Laboratories notified Northeast Utilities of out of tolerance test results on two previously installed Pressurizer Safety Valves. The safety valves are required by Technical Specifications to be operable with a setting of 2500 psia +/- 1 percent (2475 - 2525 psia) during Modes 1, 2, and 3. Bench testing at Wyle Laboratory revealed one valve lifted at 2467 psia initially, at 2499 psia on the second test and at 2493 psia on the third test. The other safety lifted at 2533 psia, 2566 psia and 2579 psia during its three lift tests. The third safety valve was within the required tolerance. The out of tolerance safety valves had been installed from February 1991 to August 1993. Since the valves were not installed in the plant when the event was discovered, no immediate operator action was required. <br /><br /> The root cause for the safety valves lifting at pressures outside the 1 percent tolerance is setpoint drift. A search of NPRDS indicates the problem of setpoint drift is common to the industry. A Technical Specification change is being submitted to allow +/- 3 percent tolerances for as found conditions. Use of a 3% tolerance for as found conditions is acceptable for the following reasons: <br /><br /> - it is in compliance with AMSE Sections III and XI, <br /><br /> - a slightly higher stress on the discharge piping would occur due to the higher lift pressure. However, a review of the stress analysis for this piping determined that sufficient margin exists for this increased stress.
4231993020 | Millstone 3 | 11/01/1993 | 12/01/1993 | 9312100157 | <strong>Mode Change Without Verification of Equipment Operability</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1993, at 1300 with the plant in MODE 3, a Shift Supervisor reviewing work orders discovered that the plant had entered MODE 2 without retesting the 'B' Hydrogen Recombiner and had entered MODE 4 without retesting several containment isolation valves. The valves were the outboard containment isolation valve for the 'A' steam generator blowdown sample line, the inboard containment isolation valves for the 'B' and 'C' steam generator steam header drain lines and the outboard containment isolation valve for the 'C' steam generator blowdown line. The discovery was made during routine review of automated work orders which required retest. <br /><br /> The apparent cause was a programmatic deficiency. An efficient method to track MODE dependency of retests does not exist. <br /><br /> As immediate corrective action, the components were verified to be OPERABLE by performing the required retests. In addition, another review of open work orders was conducted to ensure no other similar conditions existed. <br /><br /> As action to prevent recurrence, methods to more efficiently track retest performance are being investigated.
4231993021 | Millstone 3 | 11/06/1993 | 01/28/1994 | 9402040179 | <strong>Reactor Coolant Pump Oil Collection System Not Seismically Mounted</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1993, at 0932 with the plant in MODE 1 at 7% power, the seismic mountings of three drain nozzles in the Reactor Coolant Pump Oil Collection System were determined to have been inadequate since plant start-up. The discovery was made during an evaluation of potential problems identified as part of a review of stress calculations for the system. The calculations were being reviewed as part of a design change. <br /><br /> The apparent cause of this condition was inadequate review of calculations from a condition in 1988. This led to the incorrect conclusion that the system was adequately supported. <br /><br /> After the potential for high nozzle loadings was identified on October 6, 1993, plant management decided to repair the affected portions of the system while an operability determination was underway. These repairs were completed prior to entry into MODE 1. No further immediate corrective action was required.<br /><br /> As action to prevent recurrence, procedural changes have been made to improve the control of: design inputs, the release of design information from calculations, and review of seismic qualifications.
4231993022 | Millstone 3 | 12/19/1993 | 01/18/1994 | 9402010178 | <strong>Unlocked Manual Containment Isolation Valve Due to Equipment Interface</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1993, at 0850 with the plant in MODE 1 (Run) at 100% power, a manual containment isolation valve was discovered unlocked. The valve was found closed but not locked as required. The valve is one of two manual containment isolation valves on a Hydrogen Recombiner (HCS) two-inch supply line. <br /><br /> The root cause of the condition is an interface design/equipment condition resulting in a personnel error. The padlock that was in place was determined to be not securely locked, although it previously had appeared and felt locked due to the locking cap holding the shank of the lock securely against the padlock body.<br /><br /> As immediate corrective action the valve was verified to be in the required closed position, the padlock was securely locked, and all other valves in the hydrogen recombiner building were verified to be securely locked as required. As action to prevent recurrence, the padlocks have been replaced with long-shank padlocks, which cannot be held in the apparent locked position by the locking cap, without being fully locked.
4231993023 | Millstone 3 | 12/23/1993 | 01/21/1994 | 9402040174 | <strong>Boron Dilution Event Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1993 at 2205 hours, with the plant in MODE 1 at 100% power, a reactor power transient occurred which slightly exceeded 102% of the licensed thermal power limit of 3411 MWth. The transient resulted from a 6-minute boron dilution, when a boric acid transfer pump stopped running while in a manual makeup mode. The operating shift immediately reduced power by decreasing turbine load, stopping dilution flow, commencing RCS boration, and utilizing manual rod control, thus minimizing the transient. An engineering review was initiated to determine the significance of the event. It was determined on January 6,1994, that 102% was exceeded, and the NRC was promptly notified via telephone, as required under Operating License Condition 2.F. The transient was bounded by the analyzed boron dilution transient for Mode 1. The event was well within the operators' ability to respond as evidenced by the operators stopping the transient prior to any automatic protective functions being required. No automatic protective functions were required or actuated. The root cause was program failure - procedural deficiency. Procedures were followed, but they were not adequate to preclude the dilution event. As action to prevent recurrence, procedures have been revised to caution operators, and change the method of boration and makeup.
4241993001 | Vogtle 1 | 03/03/1993 | 03/24/1993 | 9303310141 | <strong>Valve Mispositioning Results In Inoperability Of Both ECCS Subsystems</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1993, while removing one train of the residual heat removal system from service for testing, a valving error caused the opposite train to be inadvertently removed from service. As a result, both subsystems of emergency core cooling were inoperable for a period of approximately 4 minutes. During this time, the unit was operated in a condition prohibited by the Technical Specifications (TS), a condition outside of its design basis, and a condition that alone could have prevented the emergency core cooling system from mitigating the consequences of an accident.<br /><br /> The causes of this event were personnel errors by the operators responsible for closing the valve and verifying that the correct valve was closed. Corrective actions include personnel discipline and conducting shift briefings to advise other personnel of the event.
4241993002 | Vogtle 1 | 03/13/1993 | 04/02/1993 | 9304060007 | <strong>Tech. Spec. 3.0.3 Entry Due To Pressurizer Code Safety Valves Lift Setpoints Out Of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1993, while in Mode 3 (Hot Standby) during a plant shutdown for refueling, personnel were performing surveillance testing of pressurizer code safety valves (PSVs). The lift setpoint for valve 1PSV-8010B was found to be in excess of the Technical Specification (TS) allowable limit, and the unit shift supervisor (USS) entered the TS limiting condition for operation (LCO). Testing proceeded and the lift setpoint for a second pressurizer valve, 1PSV-8010C, was also found to be in excess of the TS limit. The USS entered TS 3.0.3 since there is no action statement for more than one PSV being out of service in Mode 3. Operation per TS 3.0.3 was exited at 0648 EST, when the unit entered Mode 4 (Hot Shutdown) as the unit cooled down for a planned refueling outage. <br /><br /> The cause of this event was two PSVs with lift setpoints in excess of the TS limit. The PSVs have been sent to a vendor for testing and adjustment of the setpoints.
4241993003 | Vogtle 1 | 03/16/1993 | 04/09/1993 | 9304130228 | <strong>Loss Of Residual Heat Removal Due To Inadvertent Closure Of RHR Pump Inlet Valve</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, Unit 1 was in cold shutdown for a refueling outage, and personnel were preparing to test a design change installed in the process protection system. While troubleshooting an indication on the trip status light board, which was affected by the change, a circuit card was pulled and a suction isolation valve to the operating residual heat removal pump closed. Operators saw indications of the closing and had the valve reopened within 2 minutes. During this time, the reactor coolant system temperature rose from 160 degrees F to 161 degrees F due to core decay heat. <br /><br /> The cause of this event was inadequate reviews of the affected circuitry prior to removing the circuit card. A technician and his foreman had performed these reviews, but had failed to identify all the components affected by the circuit card. The technician and foreman involved have been counseled regarding the importance of adequate reviews.
4241993004 | Vogtle 1 | 04/10/1993 | 05/03/1993 | 9305110097 | <strong>Engineered Safety Feature Actuation System Sequencer Operation Is Initiated During Testing</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1993, personnel were testing the Train A engineered safety features actuation system (ESFAS) sequencer. New circuit cards had been installed as a followup corrective action to LER 50-424/1992-002. During the test, the sequencer caused the Train A 4160-volt bus to open the normal incoming feeder breaker (causing a loss of power to the bus), shed its loads, and initiate the undervoltage loading sequence. Components actuated as designed, and operators in the control room responded by stopping equipment started by this engineered safety feature actuation.<br /><br /> The cause of this event was a design flaw in a circuit card not affected by the card replacements. Investigation found that a protective filter allowed a small portion of a test signal to pass. This small portion of the test signal initiated the load shed. However, it was shown that this condition existed only during testing with a specific circuit board configuration and would not have affected sequencer operation during normal use. The affected circuit cards in both the Train A and Train B sequencers were modified to shorten the initiating test pulse. Both cards were reinstalled, and testing was completed successfully.
4241993005 | Vogtle 1 | 04/11/1993 | 04/26/1993 | 9305040139 | <strong>Containment Ventilation Isolation Due To Improper Radiation Monitor Actuation Setpoints.</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1993, at 1824 EDT, the reactor upper internals were raised inside of the water filled reactor cavity prior to placement of the upper internals into the reactor vessel. This evolution reduces the shielding and increases the proximity of the internals to the containment building area radiation monitors. Therefore, a subsequent rise in background radiation occurred as expected. However, the actuation setpoint for initiating a containment ventilation isolation (CVI) had not been raised as required by procedure, resulting in a high radiation alarm and a CVI. Unit operators determined that only expected levels of radioactivity were detected, and the actuation setpoints for these radiation monitors were reset by 1951 EDT.<br /><br /> The cause of this event was a cognitive personnel error by the unit shift supervisor (USS) in not ensuring that the actuation setpoints for the radiation monitors were raised prior to moving the reactor upper internals. The USS was disciplined regarding the importance of procedural compliance.
4241993006 | Vogtle 1 | 04/18/1993 | 05/17/1993 | 9305280270 | <strong>Safety Injection Initiated During Slave Relay Testing</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1993, while in cold shutdown, the solid state protection system (SSPS) mode selector switch was taken to 'Operate' in order to support slave relay testing. Immediately, the SSPS processed a safety injection (SI) signal due to low pressurizer pressure and low steamline pressure. At the time that the mode selector switch was taken to 'Operate,' SI actuation should have been blocked. However, due to work in progress that affected the pressurizer pressure instrumentation channels, automatic unblock permissive conditions were present. Control room operators recognized the inadvertent SI signal and responded to reduce injection flow and restore the normal charging system flowpath. Because this actuation had resulted in emergency core cooling system discharge to the RCS, and operators had returned the unit to normal operation, a Notification of Unusual Event was both declared and terminated at 0824 EDT. <br /><br /> The cause of this event was a personnel error on the part of the control room team for allowing the SSPS to be returned to service when a SI signal would not be blocked. Contributing to this was the large number of activities occurring as restoration of plant systems took place following the refueling. The crew did not fully evaluate the impact of other maintenance activities on this procedure. The team was reminded to request assistance when operational questions arise and/or to take sufficient time for review prior to changes in the configuration of plant systems.
4241993007 | Vogtle 1 | 04/25/1993 | 05/18/1993 | 9305250353 | <strong>Manual Reactor Trip During Low Power Physics Testing Due To Negative Reactivity</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1993, low power physics testing was being conducted following unit refueling. Personnel were interchanging control rod banks as a part of rod worth testing, alternately stepping in control bank D and stepping out shutdown bank B. When reactivity changes reached 20 percent millirho (pcm) during the process, the reactor engineer (RE) would advise the reactor operator (RO) to stop the insertion or withdrawal in progress. At 0835 EDT, while stepping in control bank D, the RE observed reactivity go offscale low. Control rod movement was discontinued as personnel investigated the reason for the reactivity excursion. Unable to determine the cause for a larger than normal negative reactivity insertion and suspecting a dropped rod, a manual reactor trip was initiated at 0859 EDT, as required by procedure, for excessive negative reactivity. <br /><br /> The cause of this event was a personnel error on the part of the RE in not advising the RO to stop rod movement in a timely manner. There was no dropped rod, and the test was subsequently completed satisfactorily. The RE was counseled regarding the importance of close attention to reactivity during the rod worth test. This incident will be discussed in future reactor engineering training.
4241993008 | Vogtle 1 | 05/03/1993 | 05/28/1993 | 9306040162 | <strong>Reactor Trip Due To Loss Of Turbine Electrohydraulic Control Fluid Pressure</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1993, at 0406 EDT, a turbine/reactor trip occurred due to low electrohydraulic control (EHC) system pressure. The main feedwater (MFW) system isolated and the auxiliary feedwater (AFW) system actuated, as designed. Control room personnel observed the actuations and stabilized the steam generator (SC) water levels. Normal unit operation resumed in Mode 3 (Hot Standby). <br /><br /> The direct cause of this event was a failure of the 'A' EHC pump, along with the failure of the standby EHC pump to auto start at the correct pressure. The combination of the two failures prevented the EHC pumps from properly maintaining EHC pressure. The 'A' EHC pump pressure compensator was found to intermittently stick in the unloaded condition.<br /><br /> Additionally, the standby pump automatic start pressure switch was out of calibration, causing the pump to start at a pressure lower than required to maintain EHC pressure above the trip setpoint. The defective pump was replaced, and the low EHC pressure standby pump auto start pressure switch was calibrated and adjusted to the correct setpoint.
4241993009 | Vogtle 1 | 07/28/1993 | 08/23/1993 | 9308300305 | <strong>Reactor Trip During Maintenance Due To Low Pressurizer Pressure Signal</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1993, technicians replaced pressurizer pressure transmitter 1PT-457 after it had displayed signs of failure. Following calibration, personnel initiated action to place the new transmitter in service by opening the transmitter's isolation valve, prior to pressurizing the sensing line and transmitter. This caused the pressure in the sensing line, which is shared with transmitter 1PT-458, to drop low enough to trip the 1PT-458 bistable for low pressurizer pressure. Because the bistable for 1PT-457 was already tripped due to the transmitter being out of service, the required 2 of 4 logic for a reactor trip now existed and a trip occurred at 2350 EDT. Upon recovery from the reactor trip, normal unit operations resumed in Mode 3 (Hot Standby). <br /><br /> The cause of this event was a cognitive personnel error on the part of the technicians and their foreman in not returning 1PT-457 to service in accordance with procedural requirements. Certain steps in the procedure that would have ensured that the sensing line and transmitter were pressurized were omitted during performance of the evolution. The technicians and foreman involved were disciplined and reminded of the importance of procedural compliance.
4241993010 | Vogtle 1, Vogtle 2 | 09/09/1993 | 10/04/1993 | 9310140181 | <strong>Inadequate Relay Testing Results In Inadequate Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1993, an instruments and controls (I&C) foreman was reviewing a Unit 2 maintenance work order and discovered that certain solid state protection system (SSPS) input relays were not adequately tested per Technical Specification surveillance requirements. The relays are part of a circuit which provides cold overpressure protection while the unit is shut down. The unit shift supervisor (USS) was advised of the potential relay problem and a limiting condition for operation (LCO) was entered when Unit 2 entered Mode 4 (hot shutdown) at 1730 EDT. The maintenance work order was implemented, and at 1745 EDT, the affected relays were tested satisfactorily. <br /><br /> The cause of this event was that the original scoping of the surveillance test, performed during initial plant startup, failed to identify that the affected SSPS input relays were not included as part of the circuit testing. The appropriate procedures will be changed to include the necessary testing. The affected Unit 1 SSPS input relays will be tested when the unit is in Mode 3 (hot standby), prior to its next Mode 4 (hot shutdown) entry.
4241993011 | Vogtle 1 | 09/24/1993 | 12/06/1994 | 9412130311 | <strong>Failure To Perform Leak Rate Testing Following Maintenance</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1993, a review of test requirements found that a recent, improper revision to the Final Safety Analysis Report (FSAR) had incorrectly changed the leakage testing requirement for ten auxiliary component cooling water (ACCW) valves from 10 CFR 50 Appendix J Type C testing to Type A testing. Further review found that maintenance had been performed on one of the valves, 1HV-1979, during the Spring 1993 refueling outage. Since it was no longer listed in the FSAR as requiring Type C testing, the valve was not Type C tested. Therefore, this represented a failure to perform required testing per ASME Section XI criteria for post maintenance testing as required by Technical Specification 4.0.5. <br /><br /> The cause of this event was an inadequate safety evaluation for the FSAR change. The safety evaluation failed to consider that, even though it is seismically qualified and constructed of mostly ASME Class 3 materials, the ACCW system in the containment was not installed to meet the ANSI N271-1976 standard criteria for a closed system. On September 17, 1994, plant personnel performed local leak rate testing on valve 1HV-1979. The valve was found to be leaking excessively. 1HV-1979 was reworked, tested satisfactorily, and returned to service.
4241993012 | Vogtle 1 | 10/13/1993 | 11/05/1993 | 9311100292 | <strong>Failure To Perform Testing Results In Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1993, personnel preparing for the semiannual, Train B hydrogen recombiner surveillance test reviewed a copy of the previous surveillance test performed on May 3, 1993, to determine the last wattmeter power value. While reviewing the data from the May 3, 1993, test, they discovered that the surveillance test had been performed on the Train A recombiner instead of Train B. This represented unit operation in a condition prohibited by the Technical Specifications (TS) because the Train B surveillance test had not been performed within the allowable time period. <br /><br /> The cause of this event was a personnel error on the part of the supervisor who authorized and approved the completed Train A surveillance test, but completed and submitted a Train B surveillance tracking sheet (STS). The supervisor failed to recognize that he had authorized and signed for the incorrect train. The supervisor has been disciplined and reminded of the importance of attention to detail when authorizing work in the plant. Additionally, Operations department management issued a briefing reemphasizing the concepts of component verification when testing and manipulating plant equipment.
4251993001 | Vogtle 2 | 01/29/1993 | 02/18/1993 | 9302230024 | <strong>Cold Overpressurization Protection Setpoints Found To Be Outside Of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1993, plant personnel found that the low temperature lift settings of the Unit 2 power operated relief valves (PORVs) were incorrect and that these valves had, on several previous occasions, been relied on to meet Technical Specification (TS) requirements for the cold overpressurization protection system (COPS). Therefore, the unit had operated in a condition prohibited by the TS on each of these occasions.<br /><br /> The cause of this problem was inadequate procedures. Setpoint information intended for use in Unit 1 was erroneously used in preparing the Unit 2 calibration procedures. The Unit 2 COPS setpoints have been corrected.
4251993002 | Vogtle 2 | 03/19/1993 | 04/15/1993 | 9304200219 | <strong>Containment Personnel Airlock Found Inoperable When Interlock Found Defeated</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1993, personnel discovered that one of the interlocks for the containment building personnel airlock door was defeated. The consequence of this condition was that the outer door of the airlock could have been opened while the inner door was open. This represented operation of the unit in a condition prohibited by the Technical Specifications (TS) because the appropriate TS action statement had not been complied with. <br /><br /> The cause of this event was a personnel error by the individual responsible for reinstating the interlock following the period when the interlocks were defeated for personnel access (during Modes 5 and 6 when containment airlocks are not required to be operable by the TS). The individual has been disciplined regarding the importance of self-checking. Maintenance personnel responsible for performing this activity will be briefed regarding this event and the significance of the failure to ensure the activity was complete.
4251993003 | Vogtle 2 | 05/29/1993 | 06/28/1993 | 9307020167 | <strong>Room Temperature Readings Not Performed - Missed Technical Specification Surveillances</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1993, the reactor operator (RO) was reviewing completed surveillances of room temperature readings, and he noticed that only one page of readings had been taken when there had previously been two pages. His investigation found that three rooms containing main steam isolation valves (MSIVs) had not had their temperature readings taken since 2300 EDT on May 29, 1993, when a revision to Procedure 14001-2, 'Shift Area Temperature Log,' deleted these rooms from the required listing. This represented unit operation in a condition prohibited by the Technical Specifications, since these room temperatures are required to be determined at least once per 12 hours. Temperature readings were then logged for the three rooms at 0547 EDT on May 31, 1993, and were found to be satisfactory.<br /><br /> The cause of this event was a cognitive personnel error by initiating a premature revision of Procedure 14001-2. Procedure 14001-2 had been revised prior to the completion of a design change and the appropriate change to the Technical Specifications. The design change was for the installation of temperature sensors and alarms which would automatically annunciate high temperature conditions in the rooms involved. However, the installation of the sensors and a change to the Technical Specifications had not been completed. After temperature readings were taken for the rooms involved and found to be satisfactory, Procedure 14001-2 was revised to include the three rooms.
4251993004 | Vogtle 2 | 06/28/1993 | 07/16/1993 | 9307220219 | <strong>Manual Reactor Trip Due To Main Feedwater Regulating Valve Failing Closed</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1993, at 0456 EDT, Unit 2 was operating normally when a steam flow/feed flow mismatch alarm was received for steam generators (SG) 2, 3, and 4. Operators observed SG 2 feedwater flow at approximately zero, narrow range (NR) level instrumentation trending down to approximately 45 percent, and main feedwater regulating valve (MFRV) 2 closed. All main feedwater isolation valves (MFIV) and bypass feedwater isolation valves (BFIV) were verified open. With SC water level dropping at a fast rate, the unit shift supervisor (USS) directed the reactor operator (RO) to manually trip the reactor at 0457 EDT. Appropriate procedural steps were implemented to return SG levels to normal and place the unit in a stable condition.<br /><br /> Troubleshooting determined that the cause of this event was the failure of the MFRV 2 tracking/driver card. This card supplies the control signal for MFRV valve position. The card failure caused the valve demand signal to fail low, and MFRV 2 closed, resulting in reduced feed flow to SG 2. The failed circuit card was replaced and will undergo failure analysis.
4251993005 | Vogtle 2 | 08/09/1993 | 08/30/1993 | 9309070362 | <strong>Unit Operation Per Technical Specification 3.0.3 When Both ESF Chillers Were Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1993, personnel were conducting a monthly surveillance test per Procedure 14400-2, "Control Room Emergency Filtration Actuation Logic Test." In accordance with the procedure, the "A" train essential chilled water (ECW) system chiller actuation handswitch had been taken to the "Stop" position to prevent the chiller from starting when an actuation signal was initiated to test the "B" train chiller response. The "B" train chiller was started at 2045 EDT, but moments later it tripped. Personnel exited the procedure and the "A" train chiller was returned to standby status at 2101 EDT. The 16-minute period when neither ECW chiller was available for automatic actuation and service represented unit operation per Technical Specification (TS) 3.0.3 since the ECW chillers perform an engineered safety feature function, and there is no other TS action requirement which addresses unit operation with both chillers out of service. <br /><br /> The cause of the "B" train chiller trip was high condenser pressure due to an excess of non-condensable gases in the system. A clogged purge solenoid valve prevented a control room annunciator from alerting personnel that purging of the excess non-condensable gases from the system was needed. The solenoid valve was replaced, the ECW chiller was purged, and the surveillance was reperformed successfully.
4251993006 | Vogtle 2 | 09/08/1993 | 09/30/1993 | ML09152029 | <strong>Reactor Trip Due To Trip Of Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1993, a quality control (QC) inspector was performing fuse monitoring per an ongoing QC monitoring program. When he attempted to open the cabinet door housing the circuit breaker for the loop 4 reactor coolant pump (RCP), the inspector found that the door was stuck along the bottom edge due to paint buildup on the floor. While holding the door, the inspector used a screwdriver to pry open the door's bottom edge. When the door opened at 1739 EDT, the inspector heard a click, and in the control room operators received various annunciators, including those for a single loop low flow condition and a reactor trip due to low flow in loop 4. A normal unit trip and response ensued. <br /><br /> The cause of this event was a personnel error in prying open the cabinet door which resulted in an inadvertent actuation of a loop 4 RCP breaker relay. The relay, which is mounted on the inside of the cabinet door opened by the QC inspector, is believed to have been jarred by opening the door, initiating a trip of the loop 4 RCP breaker. Unit 2 entered a scheduled refueling outage following the reactor trip. The loop 4 RCP breaker was reset so that the RCP and steam generator could be used as a heat sink during the initial stage of the outage. Closer examination of the cabinet door and relay will be performed later in the refueling outage.
4251993007 | Vogtle 2 | 10/19/1993 | 11/18/1993 | 9311300065 | <strong>Apparent Design Flaw Results In Condition Prohibited By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1993, while in Mode 2 following a scheduled refueling outage, the turbine driven auxiliary feedwater pump (TDAFWP) was started to support valve and response time testing and to complete inservice testing. Approximately 8 seconds after starting, the TDAFWP experienced an electrical overspeed trip while operating at normal speed, and the pump was declared inoperable. Subsequent investigation revealed the cause of the overspeed trip to be related to a recent replacement of a speed monitor during the refueling outage. The speed monitor, which provides input to a backup overspeed trip, had been functionally tested and the Technical Specification (TS) operability surveillance had been satisfactorily performed prior to Mode 2 entry. The testing did not disclose any anomalies in the speed monitoring circuit. Consequently, the unit inadvertently entered Mode 2 with an inoperable TDAFWP, in violation of TS 3.0.4. Troubleshooting showed that operation of the dc motor-operated pump discharge valves created electrical noise "ripples" in the 125 volt dc power supply to the TDAFWP speed control circuitry, which in turn caused the spurious electrical overspeed trip signal. The new speed monitor was apparently sensitive to this type of dc noise and thus initiated the pump trip. This event is reportable per 10 CFR 21 because this condition could have resulted in the creation of a substantial safety hazard. The old speed monitor was reinstalled, successfully tested, and the TDAFWP was declared operable on October 20, 1993.
4401993001 | Perry | 01/09/1993 | 02/05/1993 | 9302110242 | <strong>RWCU Isolation on High Delta Flow While Operating in the Reduced Feedwater Temperature Mode of Operation</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1993 at 1759, an Reactor Water Cleanup (RWCU) isolation occurred as a result of high differential flow. Immediate corrective action was taken to verify that no actual system leakage had occurred. The RWCU system was secured and subsequently returned to service. <br /><br /> The event is attributed to a design deficiency associated with system voiding phenomenon which occurs during cooldown of the RWCU system. This system voiding ultimately caused an isolation on high differential flow. A contributing cause to this RWCU system isolation is inadequate training to a previous procedure change initiated by LER 92-004. Following receipt of the Emergency Response Information System (ERIS) warning message, control room operators did not attempt to isolate the system until they received the 45 second differential flow timer initiation. <br /><br /> All licensed operators are currently being retrained to System Operating Instruction (SOI-G33), 'Reactor Water Cleanup System (Unit 1),' emphasizing the requirement for expeditious shutdown of the RWCU system upon receipt of the ERIS warning message. This training is expected to be complete prior to completion of the current outage. Because the Technical Specification Change Request to increase the delta-flow timer setpoint is expected to be approved in the near-term, no further corrective actions are considered necessary.
4401993002 | Perry | 01/09/1993 | 02/08/1993 | 9302120203 | <strong>Failed LLRT Surveillance Results in Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1993 at 2242, the Secondary Containment Bypass Leakage exceeded the limitations stated in Technical Specification 3.6.1.2.d, resulting in an entry into Technical Specification 3.0.3. Manual shutdown for maintenance was in progress at the time of the event and operators continued to bring the plant towards Operational Condition 4. <br /><br /> The primary root cause has been attributed to improper stroke adjus tment of the Containment Purge 42 inch supply inboard isolation valve (F0045) following actuator work in Refuel Outage 3. A contributing factor was the method used to correct previously identified leakage on November 5, 1992. The leakge past the 18-inch supply inboard isolation valve (F0195) has been attributed to valve travel being slightly out of adjustment, and to limited areas of unequal extrusion of the resilient seal. <br /><br /> The F0045 resilient seal was replaced using the updated vendor information and the valve travel was adjusted. The original seal will be further inspected for hardness. To correct the unequal extrusion of F0195, the clamping forces were relieved and the resilient seal was retightened using updated vendor information. Additionally, minor adjustments were made to the valve travel.
4401993003 | Perry | 01/14/1993 | 08/13/1993 | 9308190108 | <strong>Local Leak Rate Test Results Exceed Allowable Primary Containment Leakage For Main Steam Lines A, B, and D</strong><br /><i>Abstract:&nbsp;</i>During the period January 13 - 14, 1993, Local Leak Rate Testing (LLRT) of the four Main Steam Line (MSL) penetrations was performed to satisfy a previous commitment regarding mid-cycle testing. Three of the four (A, B, and D) MSLs tested were found to have leakage in excess of the Technical Specification limit of 25 standard cubic feet per hour (scfh). <br /><br /> At approximately 1100 on January 12, while raising reactor vessel level for normal shutdown evolutions, water was noted leaking from the lagging at the bottom of the inboard Main Steam Isolation Valves (MSIVs). It was subsequently determined that the six MSIVs which were modified during the last refueling outage (RF03) had indications of leakage around the body to bonnet flange. The primary cause of the valve leakage was attributed to gasket relaxation which resulted from insufficient tensioning of the bonnet flange studs during reassembly of the valves in RF03, combined with non-optimally sized gaskets being installed. MSIV seat leakage was identified after replacing the gaskets in the MSIVs which had previously experienced flange leakage. The seat leakage was repaired by machining or lapping of seating surfaces as necessary. Successful LLRTs were completed on the A, B and D MSLs after repairs.
4401993004 | Perry | 01/21/1993 | 02/22/1993 | 9303010330 | <strong>Inadequate Retest of MOV Results in Tech Spec Violation</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1993, at 1730, motor-operated-valve (MOV) testing of the Main Steam Line Drain and Bypass Outboard Isolation Valve indicated that the thrust produced by the valve actuator at the torque switch setpoint was less than the design thrust required to close the valve under accident conditions. This condition could be traced back to maintenance performed on the valve in April, 1992, and resulted in violation of Technical Specifications LCO 3.6.4 ACTION a. <br /><br /> The root cause of this event is personnel error, failure to follow procedure. The Responsible System Engineer (RSE) did not contact the Component Performance Group (CPG), as required by plant procedures, for advice on the appropriate retest for the work performed in April, 1992. A contributing factor to this event is programmatic weakness in that the CPG review for MOV-related work orders is dependent upon RSE action. <br /><br /> A review is in progress to determine if the operability of any other safety related MOVs under the Generic Letter 89-10 program was compromised by work orders with inappropriate retests related to diagnostic testing requirements. All RSEs will be retrained to the work order retest and review requirements specified in the applicable procedures. System Engineering personnel are developing program improvements to ensure that appropriate retests to MOV related work orders are prescribed and to ensure thorough review of MOV related work orders.
4401993005 | Perry | 01/19/1993 | 03/06/1993 | 9303090415 | <strong>False Indications of Fuel Failures During Fuel Sipping</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1993, during a mid-cycle maintenance outage, fuel vacuum sipping results began to indicate a large number of fuel defects. Sipping identified one significant fuel defect and several bundles with slowly rising indications of fission products. Because of the indeterminate nature of the fuel condition, this condition was considered a significant fuel defect, and was reported via ENS notification on January 19, 1993.<br /><br /> Subsequent examination and testing identified a single fuel failure, with the rest of the 'slow risers' attributed to fission product contamination of the corrosion layer on the most highly exposed bundles in the core. Within a short time, followup sipping identified most of the 'slow risers' to be free of fuel defects. In addition to the single failure identified, nine additional bundles were removed from the core for followup testing. Test results are expected to show these bundles to be free of defects. <br /><br /> The event notification was retracted on February 11, 1993. Because of the significant attention initially focused on this event, this LER is being submitted on a voluntary basis.
4401993006 | Perry | 02/12/1993 | 03/12/1993 | 9303180160 | <strong>Annulus Exhaust Gas Treatment System Auto Start During Transfer of Operating Trains</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1993, at 1314, while transferring the Annulus Exhaust Gas Treatment System (AEGTS) from the B train to the A train, the B train automatically restarted.<br /><br /> The cause of this event was determined to be personnel error, inattention to detail. Although the operator thought he had waited a sufficient amount of time to establish flow in the on-coming A train, the operator did not verify the proper time had elapsed prior to stopping the B fan. A contributing factor was a procedural weakness. The instruction did not caution the operator to wait until the Low Flow alarm cleared. <br /><br /> The operator has been involved with the event investigation and is aware of the importance of strictly adhering to the procedural time requirement. The operating instruction will be changed to provide additional guidance with respect to considering the status of the Low Flow alarm prior to placing one of the fans in STANDBY. This event will be reviewed with licensed and nonlicensed operators as part of routine operator requalification training.
4401993007 | Perry | 02/18/1993 | 03/19/1993 | 9303220333 | <strong>Failure to Perform Engineering Evaluation of Inoperable Snubbers Result in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1993 while performing an evaluation in response to previously initiated nonconformance reports (NRs), it was determined that certain inoperable snubbers which were the subject of the NRs may have been inoperable since January 1991. This hypothesis was supported by a minor Reactor Pressure Vessel (RPV) level offset for the instrument channel associated with the inoperable snubbers. <br /><br /> The mechanical snubber failures were attributed to dried out lubricant resulting from exposure to elevated temperatures in the upper drywell area. The failed snubbers were subsequently replaced. Additional snubbers in the immediate vicinity were stroke tested and found acceptable. Due to a prior occurrence involving elevated drywell temperatures, all mechanical snubbers in the upper drywell area are being monitored to better determine their service life in this environment. <br /><br /> All snubbers in this area will have an augmented functional test performed during the next refueling outage (RFO-4).
4401993008 | Perry | 03/17/1993 | 04/16/1993 | 9304190264 | <strong>Fire Detection Malfunction Results in Fire Protection Program Violation</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1993, between 0823 and 1005, a Proprietary Signaling (Fire and Security Monitoring) System "Fire" side malfunction resulted in a condition which could have adversely affected the ability to achieve and maintain safe shutdown of the reactor in the event of a fire. The system malfunctioned in a way that was not readily perceivable, and this resulted in the inoperability of fire detection equipment for impaired fire barriers without the required continuous fire watches. <br /><br /> The cause of this event is equipment malfunction, design. The "Fire" side computer malfunctioned due to a phenomenon called "Scan Shutdown Condition". In this condition, the "Fire" side computer self-checking feature did not detect a malfunction (because power was not lost); however the function of the computer that scans the alarm panels in the plant and updates alarm status had stopped. The self-checking feature of the computer does not monitor the scan function.<br /><br /> Administrative controls have been implemented to require a check every thirty minutes to ensure the ability of the "Fire" side computer to update alarm state changes. These administrative controls will remain in place until appropriate equipment or software changes to monitor the computer scan function are implemented. Efforts by engineering personnel are in progress to develop a method to automatically monitor the scan function of the "Fire" side computer.
4401993009 | Perry | 03/25/1993 | 10/15/1993 | 9310250296 | <strong>Containment Vessel and Drywell Purge System Isolation Due to High Radiation Signal</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1993 at 1726, the Containment Vessel and Drywell Purge System A train isolated due to a valid high radiation signal, following the initiation of a Reactor Water Cleanup (RWCU) Filter/Demineralizer (F/D) backwash. The high levels of radioactivity which isolated the system were subsequently identified to be noble gas, predominately Xenon-133 and Xenon-135. <br /><br /> The root cause of this event was fuel leakage (Reference LER 93-005, dated 3/6/93), which led to high Iodine loading on the RWCU F/D, and ultimately the generation of high levels of noble gas during RWCU backwash evolutions. A contributing cause was the failure to fully account for the higher activity and radiation levels resulting from the fuel leakage problem. A hold time provision has been built into the RWCU F/D backwash process to allow for noble gas decay and the RWCU system operating instruction has been revised to not require ventilation purge operation during backwash evolutions.
4401993010 | Perry | 03/26/1993 | 04/26/1993 | 9304300223 | <strong>Reactor Shutdown Due to Service Water Pipe Rupture</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1993, at 1525 hours, a manual reactor scram was inserted due a rupture in a 30 inch section of underground Service Water piping. Prior to the event, leak isolation was in progress to determine the source of water which was earlier reported coming from the ground near the Water Treatment Building. An Alert was conservatively declared at approximately 1535 hours due to flooding in plant areas which potentially posed a threat to safe shutdown equipment. <br /><br /> All plant equipment functioned as designed during the plant shutdown with the exception of several minor equipment anomalies. No safety related equipment was affected as a result of the flooding. <br /><br /> The cause for the piping failure was attributed to induced axial piping stress caused by pipe bending as a result of a localized loss of soil support. Appropriate corrective action to effect repairs to the Service Water piping will be completed prior to plant startup. Additional corrective measures will also be taken to minimize water entry into plant buildings.
4401993011 | Perry | 04/19/1993 | 05/19/1993 | 9305270214 | <strong>Excessive Strainer Differential Pressure Across the RHR Suction Strainer Could Have Compromised Long Term Cooling During Post-LOCA Operation</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1993, an engineering evaluation identified that excessive strainer differential pressure across the Residual Heat Removal (RHR) Suction Strainers could have compromised long term cooling during and following 100 days of continuous post Loss of Coolant Accident (LOCA) operation. <br /><br /> The cause of the reduced capability of the RHR pump strainers is considered to be the inadequate cleanliness conditions in the suppression pool. The root causes include inadequate program requirements and inadequate personnel sensitivity to the effects of cleanliness on Emergency Core Cooling System (ECCS) operability. The design of the strainers was not considered to be a factor. <br /><br /> To prevent recurrence, ECCS strainers will be inspected prior to power operation, pump suction pressures will be monitored, visual inspections during Technical Specification Surveillances will be performed, and housekeeping and inspection standards for containment and drywell will be strengthened to ensure that an acceptable level of suppression pool cleanliness is maintained. The redesigned strainers will also provide additional margin with respect to minimizing the potential for strainer fouling, tolerance for accumulating debris, and ensuring structural integrity for all operating and accident loads.
4401993012 | Perry | 06/07/1993 | 07/07/1993 | 9307130057 | <strong>Voltage Fluctuations In Battery Charger Output Cause High Pressure Core Spray Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1993, receipt of a High Pressure Core Spray (HPCS) initiation signal resulted in auto start of the Division 3 Diesel Generator and Emergency Service Water System, followed by High Pressure Core Spray injection with suction from the Suppression Pool. The cause of the event was failure of the Division 3 Reserve Battery Charger to maintain stable output voltage. The voltage transient tripped the 125 VDC to 120 VAC Topaz inverter, which affected the supply to Division 3 transmitters and the associated output signals. Once level transmitter output signals decreased to indicate vessel level 2, the divisional master trip units provided a HPCS initiation signal. Control Room operators secured the system after confirmation of inadvertent initiation. <br /><br /> The power plant responded to the HPCS Initiation as expected. The reactor power, pressure, and level transients were within the limits of the USAR analysis.<br /><br /> Erratic Reserve Charger output and internal control voltages were noted during subsequent testing. All charger components which were considered capable of causing the noted malfunction were replaced, and no further erratic voltages were observed. <br /><br /> Submittal of this report also satisfies the requirements for Technical Specification 3.5.1, action g. which requires a Special Report following any Emergency Core Cooling System actuation and injection into the Reactor Coolant System.
4401993013 | Perry | 06/08/1993 | 07/08/1993 | 9307150095 | <strong>Failure of Control Room Ventilation Supply Fan Motor</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1993 at 0345, with the Control Room Heating, Ventilation and Air Conditioning (CRHVAC) System B Train tagged out of service for maintenance, the CRHVAC System A Train Supply Fan tripped on overcurrent, resulting in both system trains being unavailable. With both system trains inoperable for the Emergency Recirculation Mode per Technical Specification 3.7.2, the plant entered Technical Specification 3.0.3.<br /><br /> The immediate cause of the event was a motor winding insulation failure which ultimately failed phase to phase. The motor was repaired by the manufacturer and returned to service, and both CRHVAC System trains were returned to operable status per Technical Specification 3.7.2. Further investigations are required to evaluate the root cause of the motor winding failure. Corrective actions will be established based on the results of these investigations.
4401993014 | Perry | 07/03/1993 | 08/02/1993 | 9308060201 | <strong>RACS Power Supply Failure Causes Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>At 1530 hours on July 3, 1993 a power supply monitor in the Rod Control and Information System (RCIS) detected less than the required voltage from its power supply. This resulted in loss of control rod scram accumulator status information provided by the RCIS Rod Gang Drive Analyzer, and inhibited control rod motion. Control room operators entered the Technical Specifications for inoperable accumulators and for inoperable control rods. Since demonstration of Control Rod Drive Pump operability could not be accomplished via rod movement, operators entered Technical Specification 3.0.3, with a 7 hour shutdown statement.<br /><br /> Technicians adjusted the power supply monitor and returned RCIS to operable status. Applicable Technical Specifications were exited at 1731 hours. <br /><br /> At 2003 hours RCIS again alarmed out of service, however accumulator status remained available. Technicians reset RCIS to demonstrate Control Rod Drive pump operability by rod motion. Subsequently, operators took RCIS out of service to replace the RACS power supply. After installation and adjustment of the power supply, the accumulators and RCIS were declared operable and applicable Technical Specifications were exited at 0443 hours on July 4, 1993.
4401993015 | Perry | 07/09/1993 | 08/06/1993 | 9308110168 | <strong>Unexpected Reactor Recirculation Pump Fast to Slow Speed Downshift</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1993, at 0537, with the reactor at 100 percent power, and both Reactor Recirculation Pumps in fast speed, both pumps unexpectedly downshifted automatically to slow speed. At 0544, Control Room operators manually scrammed the reactor from 52 percent power in accordance with plant operating procedures after the reactor entered the region of potential instability of the power to flow map.<br /><br /> It was concluded that the most probable cause of the Reactor Recirculation Pump speed downshift was the failure of both Reactor Recirculation Pump Suction Temperature Resistance Temperature Detectors (RTDs). Both RTDs were replaced and subsequently returned to the manufacturer for failure analysis. Any further corrective actions will be determined pending the results of this analysis. Additionally, a modification was made to provide a control room alarm should a RTD failure recur. A time events analyzer has been installed to monitor the Reactor Recirculation Pump fast to slow speed downshift logic circuitry during the current Reactor startup.
4401993016 | Perry | 08/25/1993 | 02/23/1994 | 9403070048 | <strong>Missed Surveillance Requirements for Charcoal Sampling of Required Ventilation Systems Due to Inadequate Program Results in Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1993, it was discovered that fuel handling activities had been performed on August 9, 1993 without three Fuel Handling Building (FHB) ventilation exhaust subsystems operable in violation of Technical Specifications 3.7.7.1 and 3.7.7.2. Subsequent to the initial reporting of this event, an evaluation was performed which identified several times in the past where the charcoal sampling surveillance requirement for the FHB ventilation exhaust system, the Annulus Exhaust Gas Treatment system, and the Control Room Emergency Ventilation system had not been completed within the surveillance time requirements for these three systems. <br /><br /> The cause of this event was an inadequate program to ensure that the charcoal sampling requirements of Technical Specifications were correctly met. The instruction that tracks operating time of the ventilation systems did not identify the surveillance limit for completing the charcoal sampling. <br /><br /> The corrective actions that will be taken include a revision to the appropriate plant instruction which tracks the surveillance interval for these ventilation systems and training for licensed personnel on this event.
4401993017 | Perry | 10/27/1993 | 11/24/1993 | 9312030174 | <strong>Local Leak Rate Testing for Residual Heat Removal System Test Return Lines not Performed in Accordance with 10CFR50 Appendix J Requirement</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1993, a reportability review for a Condition Report corrective action determined that previous local leak rate testing (LLRT) of the Residual Heat Removal (RHR) system A & B test return line containment penetrations did not meet the requirements of Technical Specification 4.6.1.2 which specifies primary containment leak rate testing in accordance with 10CFR50 Appendix J. Type C testing of these containment penetration isolation valves is performed utilizing water as the testing medium based upon these lines being water sealed from the containment atmosphere. However, a potential leakage path was identified which would have invalidated this basis. <br /><br /> This event is attributed to a failure to consider all possible leakage paths when the leak rate test program was initially established. Also contributing to this event were inadequate reviews of previous Perry and industry events.<br /><br /> Corrective actions for this event include a re-review of leak rate testing of this type, a design change to modify the flanges to facilitate leak rate testing, and a revision to the LLRT program to ensure these flanges are appropriately tested.
4401993018 | Perry | 11/04/1993 | 12/04/1993 | 9312140188 | <strong>Technical Specification Violation Due to Installation Deficiencies for Target Rock Valves</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During the period of November 4-8, 1993, six (6) Target Rock solenoid operated valves (SOVs) were determined to be inoperable due to deficiencies identified during the performance of a scheduled equipment qualification (EQ) audit. The deficiencies included loose solenoid housing covers and loose capscrews on the solenoid housing terminal/rectifier brackets. It was assumed that the Action Statements associated with the respective Limiting Conditions for Operation were not complied with due to the length of time the deficiencies existed. A field walkdown of all active safety-related Harsh and Mild Environmental Zone Target Rock SOVs performed after the initial discovery identified six valves requiring rework to correct identified deficiencies. The six valves were determined to have been inoperable in their as-found condition.<br /><br /> The cause of these deficiencies has been attributed to improper assembly during initial installation of the valves during construction. This determination was made after reviewing the work history for the affected valves and inspecting a sample of valves in the warehouse inventory. Existing maintenance instructions for these valves were verified to contain sufficient information to preclude repetition of similar events. As an added measure, appropriate maintenance personnel will receive training with regard to this event.
4401993019 | Perry | 11/15/1993 | 12/15/1993 | 9312220310 | <strong>Failure to Identify Failed Channel Checks Due to Personnel Error Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1993, during the performance of the channel check for the Reactor Water Clean-up system delta flow instruments, it was discovered that the two previous channel checks had failed to pass and the required actions of Technical Specification 3.3.2 had not been performed.<br /><br /> The root cause of this event is multiple personnel errors. For the first channel check failure, the Supervising Operator failed to follow through with the appropriate actions when he discovered the failure. Additionally, the Unit Supervisor failed to perform an adequate review of the data sheets containing the channel check. For the second channel check failure, the Supervising Operator and the Unit Supervisor recognized the discrepancy; however, they did not come to the correct conclusion that the readings did not pass the requirements for the channel check. <br /><br /> As a result of this event, the involved Supervising Operators and Unit Supervisors have been counseled. Additionally, the administrative program for the Technical Specification Rounds will be revised and training will be provided to other licensed operators on this event.
4401993020 | Perry | 12/04/1993 | 12/30/1993 | 9401070199 | <strong>Missed Hourly Fire Watches Results in Fire Protection Program Violation</strong><br /><i>Abstract:&nbsp;</i>On November 25 and December 19, 1993, hourly fire watches implemented to inspect degraded fire barriers were not performed as required by the Fire Protection Program. These events were violations of the Fire Protection Program which would have affected the ability to achieve and maintain safe shutdown in the event of a fire and are reportable as required by Technical Specification 6.9.4. <br /><br /> The cause of these events was personnel error, failure to follow procedure. Plant Administrative Procedure (PAP-1916) "Duties of the Fire Watch" section 5.6, identifies a fire watch as a "physical walkdown of an area as determined by the Fire Watch list to check for conditions that constitute a fire or fire hazard. An hourly Fire Watch shall be performed on a frequency of 60 minutes with a margin of 15 minutes." Security personnel failed to inspect one area of the prescribed Fire Watch List, in contrast with the requirements of PAP-1916. <br /><br /> As a result of these events, both security personnel involved with the missed fire watches were counseled regarding the importance of following procedures. Moreover, all personnel performing fire watches were trained to both of these events. PAP-1916 will be revised to incorporate the requirement for completion of a manual log during performance of the fire watch. Additionally, preprogrammed electronic readers that indicate an area has been missed have been purchased and will be used in the plant beginning the first quarter of 1994.
4401993021 | Perry | 12/23/1993 | 12/20/1996 | 9612260132 | <strong>Improper Setting of Motor-Operated Valve Results in Loss of Emergency Closed Cooling System Safety Function and Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1993, it was identified that a condition existed from March 19 to July 2, 1993, which resulted in operation prohibited by Technical Specifications and which could have prevented the fulfillment of the safety function of both loops of the Emergency Closed Cooling (ECC) system under postulated accident conditions. This situation occurred due to excessive leakage through the ECC to Nuclear Closed Cooling (NCC) system isolation valve OP42-F295A. This valve leakage, coincident with an inoperability of the Division 2 diesel generator during Loss Of Offsite Power (LOOP) conditions, could have caused loss of the ECC loop A cooling water and the availability of ECC loop B, thus preventing the system from fulfilling its safety function. It was also identified that a similar condition existed in 1989, which also could have resulted in the ECC system not performing its safety function. <br /><br /> The excessive leakage through OP42-F295A was caused by a combination of personnel error and inadequate procedural direction for setting motor-operated valve limit switches and mechanical stops. The limit switches and mechanical stops for valve OP42-F295A were subsequently readjusted on July 2, 1993. The procedure for adjusting Limitorque limit/torque switches was revised to provide the requisite level of direction for setting limit and torque switches, and adjusting mechanical stops. Training on this issue was conducted for appropriate maintenance and engineering personnel with emphasis on the necessity of verifying proper butterfly valve closure. <br /><br /> These conditions are being reported in accordance with 10CFR50.73 (a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(D).
4431993001 | Seabrook | 01/03/1993 | 02/02/1993 | 9302040203 | <strong>Manual Reactor Trip Due To Loss of Feedwater</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1993 at 0350 a manual reactor trip was initiated from 100% power. The reactor was manually tripped after both main feedwater pumps (MFP) SJ! shutdown due to low suction pressure. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii) as an automatic actuation of the Reactor Protection System and Engineered Safety Feature (ESF) System. <br /><br /> On January 2, 1993 a failure of the tube side relief valve SN! for the 25A condensate (CO) heater SJ! required isolation of the heater. Subsequent condensate (CO) and feedwater (FW) level oscillations caused the 21/22 CO heater strings to isolate and the heater bypass valve to open. An incorrect restoration of the 21/22 CO heater strings isolated CO flow to the MFPs which caused both pumps to shutdown due to low suction pressure. With no main feedwater flow to the steam generators, the reactor was manually tripped.<br /><br /> The plant response to the trip was normal and no unexpected transients were observed. The primary root cause of the event was incomplete communications and a secondary root cause was lack of procedural guidance.<br /><br /> Immediate corrective action was to walkdown the CO and FW systems and to review the event with the oncoming operating crews. The 25A tube side relief valve was repaired during the power ascension. To prevent recurrence, Operations Management will continue to emphasize the importance of clear, explicit communications and will develop a procedure to respond to heater drain system transients.
4431993002 | Seabrook | 01/07/1993 | 06/21/1993 | 9306290292 | <strong>Potential Premature Opening of CBS Sump Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1993, North Atlantic Operations personnel questioned whether performance of surveillance testing on the Refueling Water Storage Tank (RWST) BP! level instrumentation, which tripped two level channels in Mode 1, was consistent with Technical Specifications. Evaluation has determined that the RWST level instruments were inoperable during (performance of the surveillance testing. In addition, it has been determined that if a Safety Injection (SI) JE! signal had occurred while the RWST level low-low bistables were tripped during surveillance testing, the Containment Building Spray (CBS) BE! recirculation sump isolation valves would open earlier than previously analyzed. At that time it was postulated that the premature opening of the valves during a steam line break could potentially cause air binding of the CBS and Residual Heat Removal (RHR) BP! pumps. Therefore, the event was reported to the NRC on January 8, 1993 pursuant to 10CFR50.72(b)(2)(iii). <br /><br /> Engineering evaluation has determined that a large Loss of Coolant Accident (LOCA) occurring while two RWST level low-low bistables were in the tripped condition could have resulted in containment temperatures and pressures, and peak cladding temperatures which may not have been bounded by the current analyses. <br /><br /> The root cause of the event is failure to adequately recognize potential system interactions during abnormal configurations occurring during surveillance testing. <br /><br /> Corrective action was to revise the affected procedures to eliminate placing two RWST level channels in the tripped condition. In addition, North Atlantic will review surveillance procedures which provide 9 partial actuation of an ESF system to determine any potential safety implications. This event has been reviewed and discussed with the operating crews and other select North Atlantic personnel. <br /><br /> There were no adverse safety consequences as a result of this event.
4431993003 | Seabrook | 01/14/1993 | 02/12/1993 | 9302220254 | <strong>Automatic Reactor Trip Due To A Phase To Ground Fault On The 25 KV System</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1993, at 2019, an automatic reactor trip from 100 percent power occurred. This reactor trip followed a turbine trip caused by a phase to ground fault on the 25 kV main generator isolated phase bus (EL). This event was reported to the NRC at 2135 as an immediate notification pursuant to 10CFR50.72(b)(2)(ii), automatic actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System. <br /><br /> The 25 kV main generator isolated phase bus connects the output of the main generator to the three phase transformer used to step up the 25 kV generator output to the 345 kV grid voltage. Each air-insulated phase of the bus is surrounded by a duct assembly that isolates it from the other phases and the surrounding area. The bus conductors are cooled by a bus cooling unit that includes redundant fans and associated backdraft dampers downstream of the fans. A phase to ground fault occurred when a blade from the damper for the running fan became detached from the damper frame and was carried in the air stream, eventually making contact with the bus and a section of air duct. <br /><br /> There were no adverse safety consequences as a result of this event. The plant response to the trip was normal, and all operator actions were determined to be correct. <br /><br /> The damper blade failure was attributed to an inadequate damper blade pivot pin design by the vendor who supplied the bus duct cooling fan units. Corrective action was to redesign the damper assemblies to reduce the possibility of blade failure and to add a heavy debris screen downstream of the damper to prevent migration of loose parts if a future damper failure should occur.
4431993004 | Seabrook | 01/18/1993 | 02/12/1993 | 9302230047 | <strong>Non Compliance with Technical Specification Actions for Inoperable Radioactive Effluent Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1993 a Steam Generator Blowdown Flush Release Permit was generated to allow the rinsing of a recently regenerated steam generator blowdown demineralizer to the ocean. The flowmeter in this discharge path is not designed for the low conductivities (less than 5 micromhos) which were expected during this evolution. Technical Specification Table 3.3-12 Action 31, allows the continuation of effluent releases with the flowmeter inoperable provided the flow rate is estimated at least once per four hours. On January 18, 1993 at 2135, it was determined that the 4 hour flow estimate was exceeded by 35 minutes. This constituted a condition prohibited by the Technical Specifications. <br /><br /> There were no adverse safety consequences as a result of this event. No radioactive liquid effluent limits were exceeded. <br /><br /> The root cause for this event was determined to be personnel error on the part of the chemistry technician responsible for obtaining the radioactive liquid effluent flow estimation. The technician became involved in other duties and failed to obtain the flow estimate required by Technical Specifications. <br /><br /> The chemistry technician who was responsible for the event was counseled by supervision on his failure to take the proper action. Additionally, this event is scheduled to be discussed with each operating crew by the end of February 1993 The discussion will stress the importance of using the Non-routine Surveillance Log, to assist shift technicians in ensuring performance of Technical Specification activities.
4431993005 | Seabrook | 03/18/1993 | 04/16/1993 | 9304230126 | <strong>Noncompliance with Technical Specification 3.5.1.1 and 3.5.2 Action Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1993 while performing a Miscellaneous Valve Stroke surveillance, two accumulator isolation valves and selected ECCS valves had power restored to their operators. This resulted in a condition prohibited by Technical Specifications 3.5.1.1 and 3.5.2, which require power to be removed from the aforementioned valves in modes 1, 2, and 3. Additionally, with power available to two accumulator isolation valves the action statement for Technical Specification 3.5.1.1 no longer applies, requiring entry into Technical Specification 3.0.3. This constituted a condition prohibited by Technical Specifications. <br /><br /> There were no adverse safety consequences as a result of this event. At no time during the event were the accumulator isolation valves or the selected ECCS valves repositioned. The control room operator would have been alerted of this type condition, had it existed, through: audible alarms, visual alarms and changes in status fights on the main control board. The accumulators and ECCS systems would have performed normally, and as designed, had an event requiring them occurred.<br /><br /> The root cause for this event was determined to be personnel error. The control room operator performing the surveillance procedure missed the step directing the deenergization of MCC E522 and MCC E622. <br /><br /> Immediate corrective action was to deenergize the MCC, removing power from the valve operators. Actions to prevent reoccurrence of the event include: North Atlantic Management will discuss this event with operating crews to include alternate methods of procedural usage to prevent reoccurrence, the responsible individual involved will complete a critique in accordance with North Atlantic self checking (STAR) program, and the Operations Support Group will review industry events and practices relating to procedure interface and documentation.
4431993006 | Seabrook | 04/01/1993 | 07/01/1993 | 9307150023 | <strong>Train A Service Water Inoperability</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1993, while performing surveillance testing, the Train A Cooling Tower Pump discharge valve could not be fully closed utilizing the motor operator attached to the valve. When this valve is not fully closed an interlock prevents starting of the associated train's Service Water (SW) pumps and Cooling Tower Pump [BI]. The pumps would not start automatically following a Loss of Offsite Power with the valve not fully closed and therefore, the pumps were declared inoperable. Technical Specification 3.7.4, Service Water System, does not permit plant operation with 3 pumps within one loop inoperable and thus Technical Specification 3.0.3 was entered. The valve failed to close due to a corrosion product buildup between the valve stem and packing follower. <br /><br /> Subsequent investigation has determined that on two previous occasions, maintenance was performed on the Train A Cooling Tower Pump Discharge Valve which resulted in the inoperability of the Train A SW pumps. The maintenance was performed on October 23, 1990 and May 31, 1991. On both of these occasions Technical Specification Action 3.7.4d was entered for one Cooling Tower Service Water Pump inoperable. The maintenance that was performed did not involve a failure of the valve to close due to corrosion product buildup or over-torquing the packing gland. <br /><br /> There were no adverse safety consequences as a result of the event. Train B SW was OPERABLE and in operation of the occasions that Train A SW was inoperable.
4431993007 | Seabrook | 05/12/1993 | 08/27/1993 | 9309080242 | <strong>Protective Devices Not Analyzed to Function During Environmental Excursions</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1993, North Atlantic Energy Service Corporation (North Atlantic) determined that some electrical circuits containing circuit protective devices were not analyzed to function during environmental excursions to which they may be subjected. The subject electrical circuits containing circuit protective devices consist of non-Class 1E electrical circuits located in hush environments, or mild environments which could experience mi environmental excursion; and Class 1E electrical circuits located in mild environment areas which could experience environmental excursions. This event was previously reported on May 12, 1993, pursuant to 10CFR50.72(b)(ii) as a condition outside the design basis of the plant.<br /><br /> North Atlantic performed an evaluation of the electrical circuits containing circuit protective devices. This evaluation determined that the devices would be capable of performing their circuit protective function if they were subjected to an environmental excursion. The ability of these devices to perform their circuit protective function ensures that Class 1E cable in the same cable tray would not be degraded by a fault occurring on a Class 1E or non-Class 1E load.<br /><br /> The root cause of the event is failure to effectively communicate the requirements of associated circuits. This resulted in the failure to incorporate associated circuit requirements into Seabrook Station programs such as design, testing and procurement.<br /><br /> Immediate corrective action was performance of an Operability Determination which verified that Class 1E cables, which share the same cable tray as non-Class 1E cable, would continue to perform their intended safety function. In addition, North Atlantic replaced the normally energized circuit protective devices located in containment with like devices which had been tested to verify their high current tripping capability.
4431993008 | Seabrook | 05/18/1993 | 07/30/1993 | 9308060381 | <strong>Control Air Not Analyzed to Function During Seismic Event</strong><br /><i>Abstract:&nbsp;</i>North Atlantic Energy Services Corporation (North Atlantic) has identified a condition that is contrary to the description stated in the Updated Final Safety Analysis Report (UFSAR). Specifically, it has been identified that failure of the air supply to the Emergency Diesel Generators (EDG) jacket cooling water temperature control valves during a seismic event could cause overcooling of the EDGs, which could potentially preclude long term operation of the engines. This is contrary to the UFSAR, which states that the functional performance of the cooling water system is not adversely affected environmental occurrences, abnormal operation, accident conditions and loss of power. On May 18, 1993, North Atlantic reported this event pursuant to 10CFR50.72(b)(ii) as a condition outside the design basis of the plant. <br /><br /> The primary root cause of this event was a lack of understanding the significance of control air availability for long term diesel generator operation. <br /><br /> Immediate corrective actions for this occurrence included a Preliminary Operability Determination for the Emergency Diesel Generators. The Operability Determination was supported by a Preliminary Engineering Evaluation which documented the seismic functionability of the diesel air start skid, utilizing available seismic documentation and Engineering judgement. The evaluation concluded that with the use of appropriate operator actions the EDG air start skid will function to support the EDG during a seismic event. The Operations Department revised EDG local alarm response procedures which will provide the method for restoring power to appropriate Motor Control Centers (MCCs), in event that the feeder breakers to the MCCs should trip during a seismic event. Long term corrective actions will include: updating the UFSAR and design documents to reflect appropriate safety classification of starting air components, and updating programs and procedures to ensure long term operability of the EDG.
4431993009 | Seabrook | 05/20/1993 | 10/06/1993 | 9310150055 | <strong>Manual Reactor Trip Due To Inadvertent MSIV Closure</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1993, at 0437 EDT, a manual reactor trip from 100 percent power was initiated when a main steam [SB] isolation valve (MSIV) closed during MSIV quarterly testing. The trip was followed by a Feedwater Isolation and two Emergency Feedwater actuations. This event was reported to the NRC at 0553 EDT as an immediate notification pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System. <br /><br /> During MSIV quarterly testing, the MSIVs are alternately stroked to ten percent closed and then reopened. However, one MSIV failed to return to the open position when the ten percent limit was reached, and instead continued to close. The reactor was manually tripped when the narrow range level in the affected steam generator was twenty-two percent and decreasing. There were no adverse safety consequences as a result of this event. <br /><br /> The cause of the MSIV malfunction was determined to be debris lodged in a hydraulic solenoid valve that allowed the hydraulic pressure keeping the MSIV open to bleed off, resulting in the MSIV drifting closed.
4431993010 | Seabrook | 05/22/1993 | 06/18/1993 | 9306230270 | <strong>Engineered Safety Features Actuation - Feedwater Isolation</strong><br /><i>Abstract:&nbsp;</i>During a plant startup (approximately 14 percent power) on May 22, 1993, at approximately 1000 EDT, Steam Generator (SG) level oscillations occurred in one SG resulting in the SG being overfed and causing a high-high SG water level. This caused a feedwater isolation to all four SG's and additionally caused a turbine trip signal. Operator response to the event prevented a reactor trip and reactor power was reduced to approximately 2.5%. At 1154 EDT, North Atlantic made a four-hour notification to the NRC pursuant to 10 CFR 50.72(b)(2)(ii) since this event constituted an ESF actuation. <br /><br /> There were no adverse safety consequences as a result of this event. All equipment functioned as designed and all operator actions were determined to be appropriate to ensure the safety of the plant and the public. <br /><br /> The root cause for this event was determined to be personnel error on the part of the feed station operator. Specifically, the feed station operator knew the steps involved to successfully transfer to the main feedwater regulating valves (FRV's) but did not properly anticipate and interpret the SG level conditions with respect to existing plant conditions. The extreme sensitivity of the FRV's was not fully realized, as shown by the 'A' FRV being opened approximately 6 percent initially. <br /><br /> Immediate corrective actions, as a result of the Feedwater Isolation, were to reduce power to approximately 2.5% and restore feedwater to the SGs which prevented a reactor trip. Long term corrective actions include: procedure enhancements; low power operator training; an evaluation of simulator enhancements with regard to low power and feedwater operations; and pre-shift briefings for low power evolutions.
4431993011 | Seabrook | 12/19/1992 | 07/30/1993 | 9308060382 | <strong>Voluntary LER for Service Water Pumps SW-P-41B, SW-P-41C and SW-P-41D</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted as a voluntary LER by North Atlantic Energy Corporation (North Atlantic). <br /><br /> At various times during a four month period, three of the four ocean Service Water (SW) Pumps were declared inoperable due to high vibration. The pump high vibration conditions occurred in the following order: SW-P-41C, December 19, 1992; SW-P-41D, February 9, 1993, and SW-P-41B, April 15, 1993. All four ocean SW Pumps (SW-P-41A through SW-P-41D) are Model No. H5056, two stage vertical pumps manufactured by the Johnston Pump/General Valve Co.<br /><br /> There were no adverse safety consequences as a result of these events. <br /><br /> The root cause of the high vibration condition for SW-P-41B, SW-P-41C and SW-P-41D was due to excessive abrasive particles present in the ocean water. The abrasive particles produced accelerated wear of the shaft bearing journals. Contributing to the excessive vibration was the significantly out of balance impellers in each pump. <br /><br /> North Atlantic has replaced/rebuilt all three SW pumps. The replacement/rebuilt pumps were successfully tested and remain in service to date.
4431993012 | Seabrook | 07/27/1993 | 08/26/1993 | 9308310073 | <strong>Reactor Trip Due to Electrical Fault in Solid State Protection System Cabinet</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1993, at 0814 an automatic reactor trip from 100 percent power occurred. This reactor trip was initiated when an electrical fault in the Train 'A' Solid State Protection System (SSPS)[JG] cabinet resulted in a loss of power to the undervoltage (UV) coil for the Train 'A' reactor trip breaker. The deenerigization of the UV coil caused Reactor Trip Breaker (RTB) 'A' to open resulting in a reactor trip. Primary plant response was normal with expected Engineered Safety Feature (ESF) actuations (Emergency Feedwater System [BA] actuation on Steam Generator LO-LO level and Feedwater System [SJ] Isolation in response to the reactor trip). At 0939 EDT on July 27, 1993 North Atlantic made a four-hour notification to the NRC pursuant to 10CFR50.72(b)(2)(ii) since these events resulted in a Reactor Protection System (RPS) actuation and ESF actuations. <br /><br /> There were no adverse safety consequences as a result of this event. Plant equipment functioned as designed in response to the reactor trip and operator actions were determined to be correct in response to the reactor trip. At no time during the event was there any adverse impact on the health and safety of plant employees or the public.<br /><br /> The root cause for this event was determined to be a faulty lamp test assembly in the logic test panel of the Train A SSPS cabinet. The lamp test assembly introduced a short from the SSPS auctioneered 48 VDC bus to logic ground when performing a lamp test. <br /><br /> Short term corrective actions completed prior to reactor startup included replacing the lamp test socket and test circuit driver card. Also a visual inspection of the remaining Train A and B SSPS lamp test sockets was performed to verify pin separation. Long term corrective actions include performing a failure analysis on the lamp test socket and to evaluate the SSPS test circuit to determine whether the potential for the failure of a single lamp test socket resulting in a reactor trip can be eliminated.
4431993013 | Seabrook | 07/30/1993 | 10/27/1993 | 9311040240 | <strong>Missed Surveillance, Technical Specification 3.3.2 - ESFAS Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1993 it was determined that the Steam Generator Blowdown System (SGBD)[WI] containment isolation valves were not being tested adequately to verify their isolation function upon an Emergency Feedwater Pump (EFW) start pursuant to Technical Specification Surveillance Requirement 4.3.2.1, Table 4.3-2, Functional Unit 7b. The SGBD isolation function from an EFW pump start was tested upon the initial discovery and proper isolation was achieved. Therefore, isolation under accident conditions would have been expected. There were no adverse safety consequences as a result of this event.<br /><br /> North Atlantic subsequently reviewed and evaluated the safety analysis with respect to the impact on the decay heat removal and radiological releases if a SGBD isolation valve failed to isolate upon an EFW pump start. The review evaluated the Updated Final Safety Analysis Report Chapter 15 events which require adequate EFW flow to prevent a complete loss of secondary heat sink and ensure continued heat removal. This evaluation determined that the analyses results for these accidents/transients will remain acceptable without crediting SGBD isolation upon an EFW pump start. The testing program will be revised to test the isolation function upon an EFW pump start on at least a refueling outage basis to verify functionality of the isolation function and not to address a Technical Specification requirement. <br /><br /> The root cause of this event has been determined to be inadequate preparation and review of the surveillance procedures.
4431993014 | Seabrook | 08/24/1993 | 09/23/1993 | 9310050294 | <strong>Missed Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On August 24, North Atlantic Energy Service Corporation (North Atlantic) determined that the CHANNEL CHECK requirements of Technical Specification 4.3.2.1, Table 4.3-2, Functional Unit 8.b, had not been satisfied for the RWST low-low level transmitters. Because these transmitters are not provided with indication it was determined that a CHANNEL CHECK could not be performed that would satisfy the intent of Technical Specification Definition 1.6.<br /><br /> North Atlantic established compensatory measures to adequately perform a CHANNEL CHECK. The compensatory measure required North Atlantic personnel to perform a RWST low-low level transmitter operational check at least once per 12 hours. As the operational check involved a significant operational burden without any commensurate increase in safety, North Atlantic requested and was granted enforcement discretion from the CHANNEL CHECK requirement of Technical Specification 4.3.2.1, Table 4.3-2, Functional Unit 8b. North Atlantic also requested an exigent Technical Specification change which proposed replacing the requirement to perform a CHANNEL CHECK with a requirement to perform a Trip Actuating Device Operational Test (TADOT) at least once per 92 days. <br /><br /> There were no adverse safety consequences as a result of the event. Corrective action included establishing a RWST low-low level transmitter operational check and submitting an exigent Technical Specification change request. In addition, North Atlantic will evaluate inclusion of Technical Specification logs as part of the continuing review of Surveillance Procedures to ensure that Technical Specification requirements are met.
4431993015 | Seabrook | 09/08/1993 | 10/08/1993 | 9310190161 | <strong>Emergency Diesel Generator Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1993, North Atlantic Energy Service Corporation (North Atlantic) determined that the plant procedures for performing Technical Specification Surveillance Requirement 4.8.1.1.2 a.5 (verifying proper engine speed and generator voltage and frequency are within specified ranges within 10 seconds after the start signal) did not verify engine speed was at least 514 RPM as specified by this Surveillance Requirement. Generator frequency and voltage have been properly verified.<br /><br /> Engine speed is directly related to generator frequency since the engine and generator are mechanically coupled. An engine speed of 514 RPM corresponds to a frequency of 60 Hz. During plant Technical Specification and procedure development, North Atlantic personnel assumed that verifying generator frequency was 60 +/- 1.2 Hz was sufficient to ensure engine speed was satisfactory. It was not recognized that an engine speed requirement that corresponds to the frequency range was not provided in Surveillance Requirement 4.8.1.1.2 a.5. Therefore, the engine speed requirement of Surveillance Requirement 4.8.1.1.2 a.5 was not addressed by the surveillance procedures.<br /><br /> There were no adverse safety consequences as a result of this condition. The verification that generator frequency was within the required range within 10 seconds of a start signal ensured that engine speed was appropriate. Therefore, there was no affect on diesel generator operability associated with the failure to verify an engine speed of at least 514 RPM. <br /><br /> A License Amendment Request has been submitted to delete the requirement to verify engine speed.
4431993016 | Seabrook | 09/09/1993 | 12/09/1993 | 9312160285 | <strong>Emergency Feedwater System Heat Tracing</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1993, North Atlantic Energy Service Corporation (North Atlantic) identified a condition that could have alone prevented the fulfillment of the safety function of the Emergency Feedwater (EFW)BA! System under certain design basis accident and design basis meteorological conditions. During a review of alarm commitments it was determined that Control Room computer alarms for the Heat Tracing System FD! had been assigned to a logger only function. A safety related process line which requires heat tracing is the common recirculation line from the EFW pumps to the Condensate Storage Tank (CST)KA!. In addition, this line is not equipped with dual heat tracing per previous North Atlantic commitments and as documented in the Safety Evaluation Report, NUREG-0896. It has been determined that this line has the potential to freeze if the heat tracing circuit were to fail during severe design basis cold weather conditions. The failed heat trace circuit would not be detectable due to the absence of the alarm. <br /><br /> There were no adverse consequences as a result of this event. Under design basis accident conditions the EFW system is required to remove residual heat prior to reaching plant conditions when the Residual Heat Removal (RHR)BP! System may be placed in service. If plant operators were required to throttle EFW flow during the course of the cooldown during design basis meteorological conditions, the blocked recirculation flow path may result in both the motor driven and turbine driven EFW pumps being damaged due to inadequate pump flow. This condition which could have led to EFW unavailability, represents a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. The condition can only exist during extreme cold weather conditions. <br /><br /> The failure to provide redundant circuits for heat tracing on the safety-related process lines associated with the Condensate Storage Tank has been attributed to a design omission or oversight in the original plant design. <br /><br /> The immediate corrective action taken was to implement local monitoring of the affected heat trace circuit. Additional corrective actions include local monitoring throughout January and February 1994, reviewing the nuclear safety significance of other heat trace circuits, preparing a heat tracing design basis document, revising the maintenance program for heat tracing systems and reinstating control room heat tracing alarms.
4431993017 | Seabrook | 09/14/1993 | 10/18/1993 | 9310260161 | <strong>Service Water Pump Discharge Check Valve Testing</strong><br /><i>Abstract:&nbsp;</i>North Atlantic procedure OX1416.04 "Service Water Quarterly Pump and Valve Test, and 18 Month Valve Stroke Verification" tests the two ocean service water pumps in each train, their associated discharge isolation motor operated valves (MOV) and their associated discharge check valves. Following performance of OX1416.04 on August 24, 1993, North Atlantic recognized that the Service Water System (SW) configuration entered during the performance of check valve testing pursuant to this procedure would not result in an automatic restart of a service water pump following a loss of offsite power. North Atlantic determined on September 14, 1993, that this configuration represented a condition or operation prohibited by Technical Specifications and is therefore reportable pursuant to 10CFR50.73(a)(2)(i)(B).<br /><br /> There were no adverse safety consequences associated with this event. The root cause of this event has been determined to be a procedural inadequacy. North Atlantic will revise the frequency of SW pump discharge check valve testing from quarterly to COLD SHUTDOWN.
4431993018 | Seabrook | 09/22/1993 | 10/22/1993 | 9310260357 | <strong>Automatic Reactor Trip Due To Main Generator Exciter Brush Failure</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1993, at 0521 EDT, an automatic reactor trip from 100 percent power occurred. This trip was initiated by a reactor coolant pump (RCP) undervoltage reactor trip signal, which was caused by degradation of the main generator [TL] rotor field. Primary plant response was normal with expected Engineered Safety Feature (ESF) actuations. This event was reported to the NRC at 0638 EDT on September 22, 1993 as an immediate notification pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System.<br /><br /> The voltage and current used to develop the magnetic field on the main generator rotor are supplied by a synchronous alternating current exciter directly coupled to the main rotor shaft. The magnitude of the exciter output voltage controlled by varying the exciter field strength. This is accomplished by applying a direct current voltage to two collector rings located on one end of the exciter rotor through six graphite brushes. <br /><br /> The cause of the loss of main generator rotor field was the degradation of the exciter output voltage due to arcing at the exciter brush/collector ring interface. This arcing eventually caused a degradation of electrical contact between the brushes and the collector ring, which led to a degrading exciter field. The degrading exciter field in turn resulted in a degrading main generator field and the Station undervoltage conditions that generated the RCP undervoltage reactor trip signal. <br /><br /> There were no adverse safety consequences as a result of this event.
4431993019 | Seabrook | 10/05/1993 | 11/04/1993 | 9311150048 | <strong>Non-compliance with Technical Specification 6.11 Posting Requirement</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1993, during an unplanned outage, the Train B Residual Heat Removal (RHR) Vault was declared to be a High Radiation Area in anticipation of increasing radiation levels. As such, the accesses to the area were posted pursuant to the requirements of Technical Specification 6.11. On October 5, 1993 it was discovered that a seldom used elevator, which accesses the Train B RHR Vault, was not posted with the required Caution High Radiation Area sign. <br /><br /> Upon discovering that the access was not posted, the elevator key was obtained, the elevator was made inaccessible as an access point, and the elevator key was placed under the control of a Health Physics Supervisor. This rendered the elevator a non-access point and therefore posting was not required. <br /><br /> The cause of the event is procedure inadequacy in that posting procedures did not include adequate guidance for identifying obscure access points and including them in a formal plan for posting infrequently posted areas. An informal plan developed for posting the Train B RHR Vault did not list the elevator as an access point. <br /><br /> Corrective action will include revising radiation protection procedures to include adequate guidance for identifying obscure access points and including them in a formal plan for posting infrequently posted areas.<br /><br /> There were no adverse safety consequences as a result of this event. In addition, the event did not result in any unplanned radiation exposure or any radiation exposure in excess of the limits stated in 10CFR20.101 or 10CFR20.104(a).
4431993020 | Seabrook | 10/20/1993 | 11/19/1993 | 9312020416 | <strong>Inadequate Emergency Diesel Generator Operability Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1993, at 0710 EDT, North Atlantic Energy Service Corporation (North Atlantic) determined that the voltage and frequency recorders used for performing Technical Specification Surveillance Requirement 4.8.1.1.2 a.5 (verifying engine speed, generator voltage, and generator frequency are within specified limits within 10 seconds after a start signal) were inadequate for this purpose. North Atlantic determined these recorders are not capable of verifying that emergency diesel generator voltage and frequency have not exceeded the upper limits specified in Technical Specification Surveillance Requirement 4.8.1.1.2a.5. The method used to verify that the minimum voltage, frequency and engine speed were attained is satisfactory. <br /><br /> There were no adverse safety consequences as a result of this event. Subsequent to the determination that the installed recorders were not adequate, the emergency diesel generators were tested using a portable high speed recorder. This testing verified that both the voltage and frequency of both emergency diesel generators were within the limits specified in Technical Specification 4.8.1.1.2a.5. <br /><br /> The root cause of this condition has been determined to be inadequate review of test instrumentation response characteristics.
4431993021 | Seabrook | 11/17/1993 | 12/17/1993 | 9401030346 | <strong>Control Room Emergency Air Cleanup and Filtration Subsystem Inoperability</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993 at 1026 the plant entered Technical Specification 3.0.3 due to both Control Room Emergency Makeup Air and Filtration Subsystems VI! being inoperable. This event was reported to the NRC at 1119 as an immediate notification pursuant to 10CFR50.72(b)(1)(i)(A),the initiation of any plant shutdown required by the plant's Technical Specifications. <br /><br /> There were no adverse consequences as a result of this event. This event resulted in the plant being in a condition prohibited by Technical Specifications due to having both Control Room Emergency Makeup Air and Filtration Subsystems inoperable. The function of the Control Room Emergency Makeup Air and Filtration Subsystem is to remove particulate and gaseous activity from the control room atmosphere following a core damage event with subsequent release. Additionally, the control room air conditioning units ensure the allowable temperature for continuous-duty rating for the equipment and instrumentation cooled by this system is not exceeded and the control room will remain habitable for operations personnel during and following credible accident conditions. <br /><br /> The root cause for the inoperability of the Control Room Emergency Makeup Air and Filtration Subsystems has been determined to be equipment failure. This is due to a Control Room Emergency Filtration Unit heater failure in one subsystem and a Control Room Air Conditioning Unit oil pump failure in the other subsystem which resulted in both subsystems becoming inoperable.<br /><br /> The immediate corrective action taken was to restore one Control Room Emergency Makeup Air and Filtration Subsystem to OPERABLE status. This was done by removing the Train B Emergency Filtration heater and installing it in the Train A Emergency Filtration unit, These actions resulted in the Train A Control Room Emergency Makeup Air and Filtration Subsystem becoming OPERABLE and exiting Technical Specification 3.0.3. Other corrective actions to prevent this from occurring in the future include: evaluating and scheduling replacement of existing heaters, evaluating other methods to increase the availability of the air conditioning units, preparing a License Amendment change to separate the filtration and air conditioning functions, and evaluating the preventative maintenance program to ensure the proper heater replacement frequencies we specified.
4431993022 | Seabrook | 12/19/1993 | 01/18/1994 | 9401270016 | <strong>Inadequate Overtemperature Delta T and Overpower Delta T Channel Checks</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1993 during a review of the shift Technical Specification logs it was identified that the Overtemperature Delta T (OT Delta T) and Overpower Delta T (OP Delta T) CHANNEL CHECKs were not being adequately performed every 12 hours. The method of satisfying the CHANNEL CHECK surveillance requirement for OT Delta T and OP Delta T channels included a comparison of the OT Delta T and OP Delta T trip setpoints, however, the loop Delta T channels were not included in satisfying these surveillance requirements. The OT Delta T and OP Delta T trips will actuate when any two of the four Delta T channels exceed the variable OT Delta T and OP Delta T trip setpoints. Therefore, the four Delta T channels should have been included in the OT Delta T and OP Delta T CHANNEL CHECKs to ensure the process outputs, in addition to the trip setpoints, are within an allowed tolerance. <br /><br /> There were no adverse consequences as a result of this event. <br /><br /> The root cause for the failure to adequately perform OT Delta T and OP Delta T CHANNEL CHECKs has been determined to be due to an inadequate technical review of the Shift Technical Specification logs.<br /><br /> The immediate corrective action was to perform a CHANNEL CHECK on the four Delta T channels, and to implement supplemental monitoring until a change to the Technical Specification logs was implemented. Additionally, the MODE 1 and MODE 2 Technical Specification logs have been revised to reflect this omission, and all Technical Specification CHANNEL CHECKS will be reviewed and revised, as necessary, to ensure existing CHANNEL CHECK methodology is in full compliance with existing requirements.
4451993001 | Comanche Peak 1 | 01/18/1993 | 02/26/1993 | 9303020509 | <strong>Reactor Trip Caused By Personnel Error During Solid State Protection System Testing</strong><br /><i>Abstract:&nbsp;</i>At 1144 on January 18, 1993, while restoring the Solid State Protection System (SSPS) from a test lineup, the Reactor Operator used an incorrect instruction. As a result, trip blocks were not in place for switch manipulation and a reactor trip occurred while restoring SSPS to a normal lineup. <br /><br /> Root cause of the event was personnel error. Contributing factors were that a test procedure reference was not specific which led the RO to an incorrect instruction and that senior supervision monitoring during the restoration was less than adequate. Corrective actions included event review, training and procedure revision.
4451993002 | Comanche Peak 1 | 01/24/1993 | 02/22/1993 | 9302260327 | <strong>Reactor Trip Due To Spurious Signal In Protection Instrument</strong><br /><i>Abstract:&nbsp;</i>At 1112 a.m. on January 24, 1993, Comanche Peak Steam Electric Station Unit 1 was operating at 100 percent of rated thermal power. During routine performance of the surveillance test on nuclear instrumentation power range channel 3, a spurious signal from pressurizer pressure channel 2 made up the logic for the Over Temperature Nitrogen 16 reactor trip. All systems responded as designed. The root cause of the event was instrument failure during surveillance testing. Corrective action was the replacement of the failed component .
4451993003 | Comanche Peak 1 | 02/26/1993 | 03/29/1993 | 9304010077 | <strong>Actuation Of Unit 1 Train A Solid State Safeguards Sequencer</strong><br /><i>Abstract:&nbsp;</i>At 1005 p.m. on February 26, 1993, Comanche Peak Steam Electric Station Unit 1 was operating at 100 percent of rated thermal power. A spurious Safety Injection Signal (SIS) actuation from the Train A Solid State Safeguards Sequencer (SSSS) (referred to as Sequencer herein) occurred. All systems responded as designed. A suspected faulty card was replaced in the Train A Sequencer and the cabinet was re-energized. Another spurious SIS from the Train A Sequencer occurred upon restoration of power to the Sequencer. The Train A Sequencer card chasis was replaced including the removal of a logic monitoring instrument that was in place on the Train A Sequencer to troubleshoot an intermittent fault in the Train A Sequencer auto test circuit. The Train A Sequencer was then successfully tested and returned to service. The root cause of the event was failure of the instrument used during troubleshooting. The corrective action taken was to remove the failed test instrument from service.
4451993004 | Comanche Peak 1 | 03/19/1993 | 04/16/1993 | 9304200020 | <strong>Failure To Satisfy Technical Specification Surveillance Requirement For Liquid Waste Processing Valve1-7150</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.0.5b requires Inservice Testing of ASME Code Class 1, 2 and 3 pumps and valves to be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10CFR50.55a. <br /><br /> On November 6, 1991, during stroke testing of Liquid Waste Processing valve 1-7150 (LWPS) (EIIS: (ISV)(WE)), a containment isolation valve, the valve stroked closed in four (4) seconds. This was within the acceptance criteria of less than or equal to 4 seconds, but exceeded the alert criteria of 3 seconds. On June 27, 1992, during stroke testing of the same valve, it stroked closed in four seconds. Although the acceptance criteria was met, the alert criteria was exceeded again. Exceeding alert criteria required that valve stroke testing frequency be increased from three (3) months to one (1) month; however, the testing frequency was not increased. Failure to increase surveillance frequency does not meet the requirements of Technical Specification 4.0.5b. <br /><br /> The cause of event was a failure to adequately review test results. The second event occurred because the responsible engineer believed it was necessary to obtain engineering evaluation resolution prior to increasing testing frequency. Corrective actions included personnel indoctrination, enhanced test controls and operator training.
4451993005 | Comanche Peak 1 | 04/01/1993 | 05/03/1993 | 9305110243 | <strong>Failure To Satisfy Technical Specification Surveillance Requirement For Safety Chilled Water System And Component Cooling Water System</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1993, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation with the reactor at 100 percent of rated thermal power. While performing a review of a Surveillance Work Order package for the Safety Chilled Water System, the Inservice Test Coordinator discovered that quarterly valve stroke time testing had not been performed prior to the violation date of March 29,1993. The cause of the event was determined to be personnel error. Corrective action includes a review of surveillance work orders and a reinforcement of expectations with cognizant individuals.
4451993006 | Comanche Peak 1, Comanche Peak 2 | 04/26/1993 | 05/26/1993 | 9306030040 | <strong>Failure To Satisfy Technical Specification Surveillance Requirement For Primary Plant ESF Exhaust Filtration Unit</strong><br /><i>Abstract:&nbsp;</i>In February 1993, Mechanical Maintenance personnel replaced the upstream High Efficiency Particulate Adsorber (HEPA) filter cartridges in Primary Plant ESF Exhaust Filtration Unit CPX-VAFUPK-16 with Prelifter cartridges. <br /><br /> The root causes of the event were determined to be less-than-adequate equipment labeling, specification of the wrong procedure for the task, and a discrepancy in the Master Equipment List (MEL) Parts List. <br /><br /> Corrective actions to be taken are; a) the nomenclature on the labels for the HEPA filters on all atmospheric cleanup filtration units will be changed to eliminate confusion; b) maintenance planners will review this incident for lessons learned to ensure that Preventive Maintenance (PM) activities run for the first time are more closely reviewed; and, c) changes have been made to the appropriate procedures to require review by Procurement Engineering of Design Change Notices (DCNs) which any part/component as originally supplied by a vendor and to revise the MEL Parts List accordingly.
4451993007 | Comanche Peak 1 | 06/26/1993 | 07/16/1993 | 9307210237 | <strong>Manual Reactor Trip Initiated Due To High Stator Temperature On Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1993, Comanche Peak Steam Electric Station Unit 1 was in Mode 1, Power Operation, with the reactor at approximately at 100 percent of rated thermal power. A Control Room alarm indicated excessive temperature on the 1-04 Reactor Coolant Pump (RCP) motor stator. Component Cooling Water flow was increased to increase cooling to the RCP. Personnel were dispatched to the Containment Building to troubleshoot. These efforts were not successful in restoring the indicated temperature to normal. As a result, the Shift Supervisor directed a manual reactor trip. Subsequently, it was discovered that a faulty Resistance Temperature Detector (RTD) caused the excessive temperature indication. Another available RTD was connected to the plant computer and the circuit was functionally tested.
4451993008 | Comanche Peak 1 | 09/20/1993 | 10/18/1993 | 9310220198 | <strong>Missed ASME Section XI Surveillance Due To Less Than Adequate Review Of Work Documents</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.0.5.b requires Inservice Testing of ASME Code Class 1, 2 and 3 Pumps and valves to be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10CFR50.55a. <br /><br /> On September 20, 1993, while performing a review of work documents, the Inservice Test (IST) Coordinator noted that the required surveillance test for Spent Fuel Pool valves XSF-0160 and XSF-0161 had not been performed prior to the violation date of September 13, 1993. The cause of the event was determined to be less than adequate review of work documents when credit was taken for post work testing as surveillances. Corrective actions included performance of the required surveillance and a reinforcement of expectations with cognizant individuals.
4451993009 | Comanche Peak 1 | 10/26/1993 | 12/17/1993 | 9312280156 | <strong>Personnel Errors Leading To Refueling Cavity Water Transients</strong><br /><i>Abstract:&nbsp;</i>Event A - On October 26,1993, Comanche Peak Steam Electric Station (CPSES) Unit 1 was in its third refueling outage. The Unit 1 core was off-loaded into the Fuel Building spent fuel pool. A removable lift gate was installed between the reactor vessel area and the fuel transfer area of the refueling cavity to facilitate the drain down of the reactor vessel area of the refueling cavity. The refueling cavity lift gate has a single inflatable seal to keep it watertight. While transferring the seal supply from Service Air to nitrogen supply, the lift gate seal deflated allowing approximately 18-20,000 gallons of water to flow past the refueling cavity lift gate. The water flowed into the reactor vessel and out the #1 and #4 steam generator hot and cold manways into the 808' elevation of the containment building. <br /><br /> Event B - At 11:57 p.m. that evening, while attempting to drain down the fuel transfer area of the refueling cavity, water was inadvertently sluiced through the drain piping into the reactor vessel area of the refueling cavity causing the reactor vessel to refill. This caused approximately 4,000 gallons of water to spill out of the #1 and #4 SG manways. <br /><br /> This is a voluntary report based on generic industry interest. .
4451993011 | Comanche Peak 1 | 12/24/1993 | 01/24/1994 | 9402030190 | <strong>Reactor Trip Caused By Personnel Error During Main Turbine EHC System Trouble Shooting</strong><br /><i>Abstract:&nbsp;</i>At 11:46 a.m. on December 24, 1993, during trouble shooting on the main Turbine Electro-hydraulic Control System (EHC) Unit 1 received a main turbine low lube oil pressure signal resulting in a turbine electrical trip which in turn caused a reactor trip. Turning gear valve 1-HV-6554A received an open signal due to an erroneous signal (less than 230 RPM) coming from the turbine speed control circuitry. <br /><br /> Contributing factors were lack of specific training on the complexity of the EHC system and use of non-grounded test equipment. Corrective actions included event review, lessons learned and training content review.
4461993001 | Comanche Peak 2 | 02/07/1993 | 03/05/1993 | 9303110216 | <strong>Containment Ventilation Isolation Due To Loss Of Power To Auxiliary Tripping Relay</strong><br /><i>Abstract:&nbsp;</i>At 1655 on February 7, 1993, a breaker was tripped at a Non-1E Instrument Power Distribution Panel to allow replacement of the breaker. A Train B Containment Ventilation isolation (CVI) occurred simultaneously. The Containment Ventilation Isolation signal was reset and Containment Ventilation re-established at 1730 on February 7, 1993. Atmospheric conditions inside containment were normal and the actuation was determined to be the result of an invalid signal. The root cause for the Train B Containment Ventilation Isolation was de-energization of an auxiliary relay which was not shown on the electrical distribution drawing. Corrective action was to revise the affected drawing.
4461993002 | Comanche Peak 2 | 03/15/1993 | 04/15/1993 | 9304160085 | <strong>Personnel Error Leading To Failure To Satisfy Technical Specification Surveillance Requirement For Feedwater Isolation Valve Temperature Monitoring</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3/4.7.13 requires that for MODES 1 through 4 each Main Feedwater Isolation Valve (EIIS: (ISV)(SJ) be determined to be greater than or equal to 90 degrees F at least once per 12 hours except in MODE 1 with the Main Feedwater Isolation Valve open. <br /><br /> On March 15, 1993 at 1900 CST, Auxiliary Operator (utility, non-licensed), asked the Unit 2 Unit Supervisor (utility, licensed) about the status of feedwater system (EIIS: (SJ)) pressure testing and if temperature readings per OPT-102B, 'Local Shiftly Surveillances', were required. After reading a note on the surveillance document, the Unit incorrectly instructed the Auxiliary Operator that recording the temperature was not required.<br /><br /> Previous and subsequent surveillance results were satisfactory. Corrective actions include revising the note to clarify it and counseling the individuals involved.
4461993003 | Comanche Peak 2 | 05/04/1993 | 06/03/1993 | 9306100344 | <strong>Manual Reactor Trip Following Inadvertent Closure Of Feedwater Isolation Valve Caused By Instrumentation Channel Error</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1993, Comanche Peak Steam Electric Station Unit 2 was at approximately 23 percent of rated thermal power after a recent power reduction in preparation for a reactor shutdown from the Remote Shutdown Panel to be performed as part of the initial startup sequence. As a result of a combination of instrument inaccuracies, the feedwater anti- waterhammer permissive was lost, resulting in closure of feedwater isolation valve number 1. With steam generator number 1 at 38 percent level and decreasing, a manual reactor trip was initiated. The cause of the event was instrument error. Corrective action included maintenance on the affected instrumentation channels.
4461993004 | Comanche Peak 2 | 05/14/1993 | 06/11/1993 | 9306160040 | <strong>Failure To Satisfy Technical Specification Surveillance For Verification Of Valve Position</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1993, an operations procedure reviewer discovered that position verification, as required by Technical Specifications (T/S) for some Process Sampling valves, was not incorporated into CPSES Unit 2 procedures. The overall cause of this event was a lack of requirements for reviews by Operations personnel of design changes issued during Unit 2 construction and a lack of attention to detail concerning the specific design change involved in the event. Corrective actions included verifying valve positions, incorporating the position verification for the valves in appropriate procedures and performing reviews for generic implications.
4461993006 | Comanche Peak 2 | 07/03/1993 | 07/30/1993 | 9308040273 | <strong>Personell Error Leading To Inadvertent Auxiliary Feedwater Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>At 1340, on July 3, 1993, CPSES Unit 2 was in Mode 3 Hot Standby and preparing for a Unit 2 reactor startup. The fuses which allow for an Engineered Safety Feature (ESF) auto start of the Auxiliary Feedwater pumps were reinstalled. Since both main feedwater pumps had not been reset from the trip condition, the removal of the fuses caused an ESF signal. The corrective actions were to reset the equipment to normal lineup and remove the fuses, pending installation when required. Cognizant personnel were made aware of the oversight.
4461993007 | Comanche Peak 2 | 09/17/1993 | 10/15/1993 | 9310210190 | <strong>Reactor Protection System Actuation Due To Spike On Source Range Channel</strong><br /><i>Abstract:&nbsp;</i>At approximately 3:43 p.m. CST on September 17, 1993, during a planned shutdown of CPSES Unit 2, Instrument and Control (I&C) technician(s) were troubleshooting the front panel meter of Source Range N-31 when two separate flux doubling actuations occurred and the source range channel indicated intermittently. The boron dilution mitigation system response was as expected. <br /><br /> The cause of the event was deemed to be a material problem with the source range channel drawer, most likely related to the Log Pulse Integrator Board. Corrective actions included realignment of the system, replacement of the board, event review with I&C Technicians and Control Room personnel, and enhancement of the abnormal operating procedure governing actions taken in response to source range instrument malfunctions.
4461993008 | Comanche Peak 2 | 10/01/1993 | 10/29/1993 | 9311170155 | <strong>Auto Start Of Both Motor Driven Feedwater Pumps Which Caused An ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1993, at 0000 CDT CPSES Unit 2 was in mode 2, with reactor power at approximately 2 percent. Main Feedwater Pump tripped on low suction pressure, causing an Auxiliary Feedwater auto-start, the system response was normal. The cause of the event was deemed to be a drift on the Main Feedwater Pump low suction pressure switches. The corrective actions were to recalibrate the switches and implement design modification to replace the subject switches.
4461993009 | Comanche Peak 2 | 08/05/1993 | 11/22/1993 | 9312080011 | <strong>Inadequate Evaluation Of System Vibration Led To Failures Of Welds In The Containment Spray System</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1993, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, 100% power level. The plant operators were performing Containment Spray system surveillances, when a weld crack was discovered. On August 19, 1993, after the repairs had been made to the initial weld crack, another weld crack was discovered. in the containment spray system. <br /><br /> The cause of the cracks was determined to be excessive system vibration. The corrective actions were to repair the welds and provide adequate supports to reduce the level of vibration. <br /><br /> These events were considered to be of a generic interest and therefore are being voluntary reported.
4461993010 | Comanche Peak 2 | 10/22/1993 | 11/22/1993 | 9312080013 | <strong>Missed Surveillance On The Safety Injection Accumulators Due To Less Than Adequate Procedural Guidance For The Accumulator Level Increases</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1993, Comanche Peak Steam Electric Station Unit 2 was in Mode 1. A plant operator during his review of operator logs noticed that the Safety Injection accumulators levels were increased due to valve inleakage. However, the required chemistry samples were not taken. The cause of the event was determined to be less than adequate guidance provided to the operators with respect to accumulator level increases other than increases due to operator actions. <br /><br /> Appropriate plant procedures will be revised to provide guidance regarding accumulator level increases.
4461993011 | Comanche Peak 2 | 11/17/1993 | 12/15/1993 | 9312210195 | <strong>Loose Jam Nut On The Positioner Feedback Linkage Arm Of Separator Drain Tank Normal Valve Caused An ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1. Power operation with reactor power at 100 percent. <br /><br /> At 7:59 p.m. on November 17, 1993 Separator Drain Tank, 2A Normal Drain Valve failed open. The failure of the valve was caused due to the jam nut on the Fisher Positioner feedback linkage arm being loose. The jam nut was apparently loosened due to vibration. <br /><br /> The corrective actions were to tighten the jam nut, inspect other similar and identical feedback positioner arms and apply similar corrective actions as applicable.
4541993001 | Byron 1, Byron 2 | 02/01/1993 | 03/01/1993 | 9303100192 | <strong>Low Temperature Overpressure Protection</strong><br /><i>Abstract:&nbsp;</i>On 12/09/92, Byron Station reviewed Nuclear Network OE 5691 and a related Nuclear Network plant status item though the Operating Experience (OPEX) Program. Station personnel determined that concerns with the Low Temperature Overpressure Protection System (LTOPS) setpoints used in the Technical Specifications and in implementing use of the 10CFR50, Appendix G limits were applicable. The nonconservatism, which occurs when the reactor coolant pumps are running, relates to the pressure difference that may exist between the wide-range pressure transmitters and the pressure corresponding to the reactor vessel location where the heatup and cooldown curves are calculated. Westinghouse did not take this pressure difference into consideration while preparing Byron's curves. <br /><br /> A determination was made that the reactor vessels were operable and that the heatup/cooldown curves may be used with compensatory actions. <br /><br /> The event was caused by a deficiency in Westinghouse's analysis that was used to determine the LTOP setpoints and the licensing bases. <br /><br /> The condition was identified previously by two other stations. CECO has determined that this is a concern at Byron, Braidwood and Zion. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(v), any event or condition that alone could have prevented the fufillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
4541993002 | Byron 1 | 02/26/1993 | 03/25/1993 | 9303300249 | <strong>VQ Valves Failed to Close as required During a Technical Staff Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1993, Technical Staff procedure BVP 600-3, Unit One - Placing Both Trains of SSPS in Test Mode While in Modes 5 and 6, was performed as scheduled during refueling outage B1R05. This procedure installed and labeled several jumpers in Solid State Protection System (SSPS) cabinets. Core alterations resumed on 02-25-93 and Technical Staff performed 1BVS 9.9-1, Unit 1 Containment Ventilation System Auto Isolation Weekly Surveillance, on 02-26-93 as required by Technical Specification 3/4.9.9. On 02-26-93 at 0944, with Unit 1 in Mode 6 (refueling), the Train B valves failed to actuate when the Train B portion of the surveillance was performed. The surveillance failure was investigated and it was discovered a jumper required to be installed by BVP 600-3 was lifted and taped. The jumper was dislodged by an unknown individual sometime after 1BVS 9.9-1 was completed on 02-20-93. This event was not detected and the configuration of the hook at the end of the jumper indicated the lead was most likely not lifted intentionally due to it's bent shape. <br /><br /> An Instrument Maintenance Department Control System Technician (CST) was shocked from this lifted jumper on 02-21-93 during unrelated work in the SSPS system. The CST left the jumper in the lifted state, taped the bare end, and notified his supervisor. The length of the jumper, the supervisor's concern with the worker's safety, and unexpected results during performance the CST's assigned Nuclear Work Request package contributed to this event. <br /><br /> New jumpers with ring end clips and specific lengths were made for future use with this procedure. Nuclear Tracking System items were written to address procedure revisions and to discuss this event with affected departments. <br /><br /> This event is reportable under 10CFR50.73(a)(i)(b) for operations prohibited by the Technical Specifications.
4541993003 | Byron 1 | 03/06/1993 | 04/05/1993 | 9304090200 | <strong>Damaged Fuel Assemblies and Upper Internals</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours on March 6, 1993, during Control Rod Drive Shaft latching activities (FH) [DB], the Fuel Handling Supervisor experienced difficulty latching Rod Control Cluster Assembly (RCCA) R543 at core location N-09. The Upper Internals Package (UIP) was removed and an investigation determined that the guide pins for core locations L-09, M-09, N-09, P-09 and R-09 had not properly seated into their respective fuel assemblies 'S' holes. As a result, the removable top nozzles for fuel assemblies G17E, H17E, and G22E were pushed down damaging the guide thimbles. A total of eleven guide pins were bent. RCCA R543 in fuel assembly G22E and its drive shaft were also damaged.<br /><br /> Two multi-disciplinary teams were formed, one to address the bent pins and recover the damaged assemblies and a second to perform the Root Cause Analysis for the event. Westinghouse Electric Corporation straightened or removed the damaged UIP guide pins prior to reinstallation of the Upper Internals. Commonwealth Edison performed design analyses as required for core redesign and to disposition the removed fuel assembly guide pins. <br /><br /> Recovery activities were initiated for removal of the damaged fuel assemblies. The Fuel Handlers placed the damaged fuel assemblies in the Spent Fuel Pool. Nuclear Fuel Services Department redesigned the core loading pattern with available assemblies and the Fuel Handlers reloaded the core to the new loading pattern. Technical Staff Nuclear Engineers performed a special procedure, SPP 93-016, 'Core Alignment Verification,' to ensure the assemblies were properly aligned in the core. Eleven pins were observed to be bent, two were cut, and nine were straightened prior to resetting the UIP.<br /><br /> This event is being submitted as a Voluntary Report. (0995R/VS-2)
4541993004 | Byron 1, Byron 2 | 12/08/1993 | 01/04/1994 | 9401140114 | <strong>Potential Inoperability Of The Auxiliary Feedwater Switchover Due To Inadequate Design Change</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1993, with both Units in Mode 1 at 98% power, Byron Station was notified of a potential operability issue by Braidwood Station regarding the availability of the motor driven Auxiliary Feedwater pumps (1,2 AF01PA). During an external event (seismic, tornado) where the Condensate Storage Tank (CST) was not available, concurrent with the motor driven AF pump being required to autostart; the pump would start and potentially could trip on low suction pressure (after a 2.5 sec time delay). The switchover of the AF pump suction to the safety related essential service water (SX) supply occurs 4 sec after pump start. Since both time delay relays will reset upon pump trip the automatic switchover may not occur. <br /><br /> A determination was made that the motor driven AF pumps were inoperable and a LCOAR was entered. <br /><br /> The event was caused by an inadequate modification design that failed to consider all failure modes effects on the AF system. <br /><br /> A Temporary Alteration was installed to move the feeds for the 4 second
4551993001 | Byron 2 | 02/23/1993 | 03/19/1993 | 9303260034 | <strong>Wiring Error in SSPS Test Circuit</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1993, with Unit One in Mode 6 (Refueling) and Unit 2 in Mode 1 at 100% reactor power, a wiring discrepancy in Solid State Protection System (SSPS) cabinet 1PA10J was discovered. Continuity checks on the Logic B test switch, were being performed following its replacement under a Nuclear Work Request during the Unit One refueling outage B1R05. The Actuation Logic Test surveillance requirement for Containment Isolation Phase B was not met due to the wiring configuration. The twenty-four hour exemption clause for a missed surveillance was entered per Technical Specification 4.0.3 at 1755 on February 23, 1993. At 2340, Technical Specifications 4.0.3 was exited for Train A SSPS after successful repairs and testing were completed. <br /><br /> The cause of this event is incorrect wiring of the cabinet prior to delivery by the manufacturer.<br /><br /> The incorrect wire was moved from TB501-5 to TB501-6 and testing was performed to verify the Containment Spray and Containment Isolation Phase B logic test circuitry worked properly.<br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), operation prohibited by Technical Specifications - missed surveillance.
4551993002 | Byron 2 | 03/11/1993 | 03/29/1993 | 9304060079 | <strong>Unit 1 Essential Service Water Pump Availability to Unit 2 Surveillance Not Completed</strong><br /><i>Abstract:&nbsp;</i>During the second shift performance of 2BOS 0.1-1,2,3, Shiftly/Daily Operating Surveillance, it was discovered that the Unit 1 Essential Service Water pump availability to Unit 2 surveillance, 2BOS 7.4.1.a-1, had not been performed. The Essential Service Water (SX)[BI] pump availability surveillance was performed at 1121 on March 11, 1993. Having been previously performed at 0254 on March 10, 1993 this exceeded the surveillance's 24 hour frequency.<br /><br /> The root cause of this event was the failure to properly complete the Shiftly/Daily Operating surveillance. The step requiring the performance of the SX availability surveillance was mistakenly marked 'N/A', which resulted in the SX availability surveillance not being performed until 1121 on March 11, 1993. An additional factor is that the Shiftly/Daily Operating surveillance uses discretionary steps to direct operators to perform surveillances, based on plant conditions. <br /><br /> To prevent recurrence, the individuals involved were counseled on the importance of attention to detail and the consequences of complacency. In addition, both Units' Shiftly/Daily Operating surveillances have been revised. <br /><br /> This event is reportable per 10CFR 50.73(a)(2)(1)(B), for any operation or condition prohibited by the Station's Technical Specifications.
4551993003 | Byron 2 | 05/11/1993 | 06/04/1993 | 9306110217 | <strong>Unit 2 Reactor Trip due to Turbine Trip due to Overspeed Trip Actuation caused by a Spiking Power Supply</strong><br /><i>Abstract:&nbsp;</i>At 22:38 on May 11, 1993, a Turbine Emergency Trip Oil Header Pressure Low Alert was received on Byron Unit 2, followed immediately by a Reactor Trip initiated by Turbine trip above P-8 (30% power). The Reactor Trip was initiated by a loss of Electro-Hydraulic fluid pressure in the Emergency Trip header. <br /><br /> The cause of the loss of pressure in the Emergency Trip header was a spurious actuation of the Overspeed Trip Relay due to a spiking power supply. <br /><br /> The immediate corrective action was to replace the faulty power supply board.<br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature including the Reactor Protection System.
4551993004 | Byron 2 | 09/05/1993 | 10/05/1993 | 9310130045 | <strong>Inadvertent Train B Safety Injection Activation due to Mispositioned Test Switch During Surveillance</strong><br /><i>Abstract:&nbsp;</i>During the restoration steps of the Unit Two Train "A" Manual Safety Injection and Manual Phase "A" Initiation surveillance, an inadvertent Safety Injection occurred on "B" Train. The Train "B" Solid State Protection System was being restored when the Multiplexer Test Switch was placed in the "Inhibit" position instead of the intended Input Error Inhibit switch. In the next step, when the Mode Selector switch was placed to "Operate", a Train "B" Safety Injection occurred. Approximately 1200 gallons of Refueling Water Storage Tank water was injected in to the Reactor Coolant System as pressure increased from 360 psig to 400 psig and pressurizer level increased from 87% to 96% (Hot Cal). The Safety Injection signal was reset after the 60 second reset block timed out and the High Head Injection was secured. <br /><br /> The cause of the event was a cognitive and procedural personnel error. Self-Checking practices were not applied. Independent Verification required by the procedure was not done at the proper time. Corrective actions will include training, administrative procedure changes, and surveillance procedure enhancements. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) any event or condition that resulted in manual or automatic actuation of any Engineered Safeguards Feature.
4551993006 | Byron 2, Byron 1 | 09/24/1993 | 10/21/1993 | 9310270244 | <strong>Surveillance For Source Range Instrumentation Missed Due To Incorrect Computer Status Update</strong><br /><i>Abstract:&nbsp;</i>On 09/18/93, a partial performance of surveillance 2BOS 9.2.c-32, 'Analog Channel Operational Test of Source Range Channel N32 in Mode 6' was performed. On 09/20/93, the surveillance was entered into the surveillance Tracking System (GSRV) as a complete surveillance instead of partial surveillance. The complete surveillance subsequently was not performed before it was due. <br /><br /> A failure in the entry and review process for updates to GSRV caused the missed surveillance. Changes to the update process have been made to prevent reoccurrence.<br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B) - Operations prohibited by Technical Specifications.
4551993008 | Byron 2 | 11/23/1993 | 02/08/1995 | 9502150280 | <strong>Reactor Trip/Turbine Trip Due To Solid State Protection System Universal Logic Card Intermittent Failure</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1993, at 0040, with Unit 2 at 100% power and Normal Operating Pressure and Temperature, the Instrument Maintenance Department (IMD) was performing surveillance 2BIS 3.1.1-024 which tested loop LB559C, 2D Steam Generator (SG) level (FW) [JB]. The loop was put in test as required and the appropriate alarms came up. Anticipated Transient Without Scram Mitigation System (AMS) was also put in test per the surveillance and the associated alarms came in. Six minutes into the loop functional check, the 2A Auxiliary Feedwater (AF) [BA] pump auto started and all steam generator blowdown isolation valves closed concurrently. Approximately 3.5 minutes later a reactor trip occurred with reactor trip breaker A opening. All related plant parameters were normal prior to the event. All operations and Instrument Maintenance personnel actions were appropriate prior, during and after the event. <br /><br /> The cause was suspected to be a failure of one of the circuit cards for train 'A' of Solid State Protection System (SSPS) (EF) [JE] SG level. The associated cards were replaced and the removed cards were tested 'on the bench'. One universal logic card showed signs of degrading voltage with time. <br /><br /> Operability tests and functional tests were performed to verify operability of the replaced circuit cards. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature including the Reactor Protection System.
4561993001 | Braidwood 1 | 01/07/1993 | 01/29/1993 | 9302010165 | <strong>Reactor Trip Due to Logic Card Failure in Train B Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1993 while performing Unit One Reactor Coolant Pump Underfrequency Quarterly Surveillance, Unit One experienced a Reactor Trip. The failed component was on the A215 Universal Logic Card which is the decision maker for the 2 out of 4 logic in the RCP-UF circuit. The A215 card was replaced and the SSPS Bi-monthly Diagnostics test was reperformed to ensure the replacement card functioned properly and verify the complete SSPS system was operational. The failed Universal Logic card was sent to the vendor for a detailed failure analysis. There have been previous occurrences of spurious ESF actuations due to problems in the Train B SSPS circuitry.
4561993002 | Braidwood 1, Braidwood 2 | 02/01/1993 | 03/03/1993 | 9303090085 | <strong>Nonconservatism in Heatup/Cooldown and Cold Overpressure Protection PORV Setpoint Curves</strong><br /><i>Abstract:&nbsp;</i>A nonconservative calculation used in the generation of the Heatup Curves, Cooldown Curves, and the Low Temperature Overpressure Protection / Cold Overpressure Mitigation System (LTOP/COMS) Nominal Power Operated Relief Valve (PORV) Pressure Relief Setpoint Curves was identified. The purpose of these curves is to protect the reactor vessel against exceeding 10CFR50 Appendix G limits. This issue was identified after a review of two INPO Nuclear Network informational entry items from Comanche Peak Station. The nonconservatism relates to the pressure difference that exists between the wide-range pressure transmitters and the pressure corresponding to the reactor vessel beltline when one or more of the reactor coolant pumps (RCPs) are running. All components/devices were determined to be operable, with compensatory actions required under certain conditions. The cause of the event has been determined to be a design deficiency in the original Westinghouse analysis used to determine the LTOP/COMS setpoints.<br /><br /> The immediate corrective action was to provide guidance to shutdown three RCPs prior to initiating an RCS cooldown following a reactor shutdown / trip. The appropriate curve book figures and surveillance procedures were revised to account for the 50 psig nonconservatism when four RCPs are running. No other previous events similar to this were identified.
4561993003 | Braidwood 1, Braidwood 2 | 02/23/1993 | 03/22/1993 | 9303250171 | <strong>Missed Technical Specification Surveillance Due to Preservice Design Deficiency in SSPS Test Circuitry</strong><br /><i>Abstract:&nbsp;</i>A lead for the SSPS test logic circuitry was identified as being landed on the wrong terminal board point, preventing independent testing of Containment Isolation Phase 'B', as required by Technical Specification 4.3.2.1. At 1543, Technical Specification 3.0.3 was entered for both units. The root cause of the event was a preservice design deficiency. The test logic circuitry, as supplied by Westinghouse, was wired in accordance with the Westinghouse wiring list, which was incorrect. The incorrectly wired leads were moved to the positions specified on the schematic drawings. Subsequent testing proved the test circuitry was functioning properly. There have been previous reportable events involving wiring discrepancies. However, the causes and corrective actions from these events are not applicable to this event.
4561993004 | Braidwood 1 | 03/28/1993 | 04/23/1993 | 9304260173 | <strong>Technical Specification Violation Due to Incorrect Performance of Quadrant Power Tilt Ration Calculation</strong><br /><i>Abstract:&nbsp;</i>Recalibration of Power Range Nuclear instrumentation, as required by Technical Specification Surveillance Requirements 4.2.1.3, 4.2.1.4, and 4.3.1.1, was in progress. Performance of the calibration renders the Quadrant Power Tilt Ratio (QPTR) alarm inoperable. During the calibration of any Power Range Channel that channel is considered inoperable. Per Technical Specification Surveillance Requirement 4.2.4.1.b, QPTR must be calculated at least once per 12 hours when the alarm is inoperable. Per Technical Specification surveillance Requirement 4.2.4.2, when power is above 75% of Rated Thermal Power, and one Power Range channel is inoperable, the QPTR must be calculated using the Movable Incore Detector System (MIDS). Braidwood Station administratively requires that QPTR be calculated once per 8 hour shift when the alarm is inoperable. On Shift 1 (2300-0700) March 28, 1993, Braidwood Unit 1 was at approximately 98% power. A QPTR calculation was performed while Power Range channel N-42 was inoperable during recalibration. The calculation was performed using the remaining three operable channels, rather than the MIDS as required by Technical Specification surveillance Requirement 4.2.4.2. The error was discovered later on March 28, at which time the alarm and all Power Range channels had been restored to an operable condition. There have been no previous occurrences found relating to this event.
4561993005 | Braidwood 1 | 09/10/1993 | 10/10/1993 | 9310140244 | <strong>Technical Specification surveillance not performed due to personnel and programmatic deficiencies</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1993 it was determined that Braidwood Station Technical Specification surveillance 3/4.7.6.e.6, which is an eighteen month verification that the main control room ventilation envelope can be manually isolated, had not been satisfied for the period between November 1989 and August 1993. This was due to the fact that the station procedure that satisfies this Technical Specification surveillance (BwVS 7.6.e-2) had not been placed in the General Surveillance (GSRV) tracking system. BwVS 7.6.e-2 was successfully performed immediately after discovering it had been missed. The cause of the event was a combination of personnel error and procedural deficiency that existed at the time BwVS 7.6.e-2 was written. The author of BwVS 7.6.e-2 did not ensure that the proper tracking mechanism was in place to have the surveillance conducted on an eighteen month frequency. Also, administrative procedure BwAP 1300-2T3, Permanent Procedure Request/Revision/Deletion, did not question the author of a new procedure whether a GSRV entry had to be made. The current revision of this procedure does provide such instructions, and a GSRV entry has been made to preclude recurrence. This event had no effect on plant or public safety.
4561993006 | Braidwood 1, Braidwood 2 | 12/09/1993 | 02/11/1994 | 9403020001 | <strong>Potential Inoperability of the Auxiliary Feedwater Switchover due to Inadequate Design Change</strong><br /><i>Abstract:&nbsp;</i>Braidwood Station has identified a potential operability issue regarding the availability of the motor driven Auxiliary Feedwater pumps (1,2 AF01PA). During an external event (seismic, tornado) where the Condensate Storage Tank (CST) was not available, concurrent with the motor driven AF pump being required to autostart; the pump would start and potentially could trip on low suction pressure (after a 2.5 sec time delay). The switchover of the AF pump suction to the safety related essential service water (SX) supply occurs 4 sec after pump start. Since both time delay relays will reset upon pump trip the automatic switchover may not occur. A determination was made that the motor driven AF pumps were inoperable and a LCOAR was entered. The event was caused by an inadequate modification design that failed to consider all failure modes effects on the AF system. A Temporary Alteration was installed to move the feeds for the 4 second SX switchover time delay relay to the AF pump starting circuitry. This keeps the timer active when the pump is receiving an auto start signal, ensuring SX switchover occurs on low suction pressure independent of pump trip.
4561993007 | Braidwood 1 | 12/13/1993 | 01/12/1994 | 9403030112 | <strong>Both Trains Control Room Ventilation Inoperable due to Equipment Failure and Procedural Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1993, Braidwood Station tried to start the 'B' control room ventilation make-up fan. The make-up fan tripped on low flow and operating declared the 'B' train of control room ventilation inoperable and entered LCOAR 7.6.1-a. While swapping to the 'A' train of control room ventilation, the main control room pressure became negative. The hydramotor for the supply fan discharge damper failed. operating declared the 'A' train inoperable and entered Technical Specification 3.0.3 for both units at 1324. The flow control loop for the make-up fan was adjusted and the 'B' train of control room ventilation was declared operable. operating exited Technical Specification 3.0.3 at 1352. The cause of the event was a combination of Equipment Failure and Procedural Deficiency. This event did not effect plant or public safety. The failed hydramotor was replaced, the test report packages for the flow control loops will be enhanced, the Frequency of the loop calibration will be increased, and a review of similar hydramotor failures will be done.
4571993001 | Braidwood 2 | 03/11/1993 | 04/05/1993 | 9304160003 | <strong>Technical Specification Violation Due To Head Vent Valve 2RC8070 Being Closed</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in a Refuel Outage in Mode 5. The RCS was in process of being drained down to the reactor flange level in preparation for removal of the reactor head. The conoseals were being removed to allow removal of the reactor head. The drain down was completed and the level was being stabilized at 399'. The Unit 2 Nuclear Station Operator (NSO) noted that vessel level indication was increasing, immediately notified the Unit Supervisor of the anomaly, and stopped all RCS draining. A Field Supervisor in the Unit 2 containment was sent to investigate the RCS vent paths for proper alignment. He verified the Pressurizer vent was correct, and went to verify the reactor head vent. The Head vent path was found isolated as valve 2RC8070 was found to be in the locked closed position. At this time reactor level had stabilized at 404' 6". No water was spilled, since the level was below the open conoseals. With valve 2RC8070 being closed the reactor head was not vented, which maintained the level in the head near the 404' 6" level. The indication in the control room was affected and indicated the incorrect level of 399' prior to opening the conoseals. There has been one previous non-reportable occurrence associated with reactor vessel level indication, which was on Unit 1 and was due to an improper vent of the pressurizer.
4571993002 | Braidwood 2 | 04/14/1993 | 05/14/1993 | 9305180201 | <strong>Unplanned Engineered Safety Feature (ESF) actuation due to management and procedural deficiency</strong><br /><i>Abstract:&nbsp;</i>Braidwood System Engineering was performing a surveillance which required stroking safety injection (SI) accumulator isolation valves 2SI8808A-D. To support this test all four valves were closed and accumulator pressure reduced to 100 psig. While conducting the surveillance, the Operations Department was scheduled to transfer the power supply for instrument Bus 211 from its constant voltage transformer to its inverter. The NSO was monitoring various RCS parameters while the power supply was swapped and he noticed increasing pressurizer level. The contents of the two associated SI accumulators had discharged into the RCS. The cause of the event was procedural deficiency and management deficiency. Procedures ' Instrument Bus Inverter Startup' and '* Transferring An Instrument Bus From The Inverter To The Constant Voltage Transformer' will be revised, and training will be given to all licensed operators on the details of the event. There have been previous occurrences of reactor trip / ESF actuations due to procedural deficiencies.
4571993003 | Braidwood 2 | 04/19/1993 | 05/19/1993 | 9305280246 | <strong>Technical Specifications violated due to Source Range Reactor Trip capability being blocked</strong><br /><i>Abstract:&nbsp;</i>Two Nuclear Station Operators (NSOs) performed the task of blocking the SR monitors in tandem. The two NSOs did not clearly communicate their actions to each other. One of the NSOs informed a third, oncoming NSO of the blocking of the SR monitors. The oncoming NSO was given an inaccurate turnover of the SR monitor status. A Limiting Condition for Operation (LCOAR) was entered for having the SR monitors blocked. Later, when unblocking the SR monitors, the second NSO unblocked the 'Hi Flux at Shutdown' alarm and reset the 'Boron Dilution Prevention System' (BDPS) but failed to unblock the 'Source Level Hi Reactor Trip' function. He was not aware that the latter function had been blocked. The NSO then exited the LCOAR based on this action. Approximately eight hours later, the blocked trip was identified and unblocked. The cause of this event is personnel error and procedural deficiency. Corrective actions include counselling of the individuals involved, and the development of a procedure for properly blocking the Source Range monitors. There has been one previous reportable occurrence of this type.
4571993004 | Braidwood 2 | 07/12/1993 | 08/11/1993 | 9308160233 | <strong>Core reactivity normalization surveillance not performed in required time frame due to personnel error</strong><br /><i>Abstract:&nbsp;</i>Technical Specification Surveillance Requirement 4.1.1.1.2 requires normalization of predicted reactivity values to actual core conditions prior to exceeding a fuel burnup of 60 Effective Full Power Days (EFPD) after each fuel loading. The surveillance that satisfies this requirement (BwVS 1.1.1.2-2) was not performed until approximately 62.67 EFPD after the third refueling outage on Unit 2. No impact on core monitoring occurred because no comparison of the overall core reactivity balance to predicted values (per BwVS 1.1.1.2-1) was performed or due in the period during which normalization was past due. The causes of this event were cognitive personnel error and programmatic deficiency. Methods to better track this type of surveillance, Technical Specification applicability, and surveillance frequency update methods will continue to be investigated. There have been previous occurrences in which Technical Specification surveillances have not been performed within the specified frequency, although the events were seen as unrelated to this event.
4571993005 | Braidwood 2 | 07/20/1993 | 08/19/1993 | 9308250062 | <strong>Missed surveillance on containment isolation valve due to personnel error and management deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1993, Operations Department performed the RC Drain Tank Containment Isolation Valve Stroke Test satisfactorily. On July 1, the Inservice Testing Coordinator (ISTC), after reviewing test results, initiated a Surveillance Request (GSRV) to increase the test frequency for valve 2RE9159B (RE). The ISTC incorrectly had Nuclear Group entered as the responsible department. On July 20, the RE system surveillance was late. The Nuclear Group leader contacted Primary Group, responsible for the RE system. The Primary Group Leader informed Operations of the missed surveillance which was then completed the same day. The causes of the event were: work group misassignment, the GSRV item not reviewed by the Station Surveillance Coordinator, Nuclear Group leader assumed the GSRV item appeared on Primary Group's list, and no proceduralized routing process or formal training for station surveillance requests. The corrective actions include procedural enhancements, training, and counseling. There have been previous reportable missed surveillances, however, the previous causes and corrective actions are not applicable to this event.
4571993006 | Braidwood 2 | 07/27/1993 | 08/26/1993 | 9309010147 | <strong>Operation of RH pump with inadequate oil supply due to clogged orifice</strong><br /><i>Abstract:&nbsp;</i>During an oil change on the 2A Residual Heat Removal (RH) pump motor, the bearing oil reservoir was unable to be drained. An investigation showed that the oil reservoir did not have an adequate amount of oil. The cause of this event is attributed to an obstruction of the orifice separating the sightglass and the bearing reservoir. The cause of the obstruction is due to corrosion particles resulting from a previous seal leak. The 2A RH pump motor was replaced. Subsequent corrective actions will include evaluating RH system seal leakage, enhancing lubrication processes, training, checking other systems with similar designs, and review of the bearing oil temperature probe. There have been no previous occurrences.
4571993007 | Braidwood 2 | 10/03/1993 | 10/26/1993 | 9311030377 | <strong>Reactor Trip Due to LO-2 Level in 2D Steam Generator Due to O-ring Failure in Feedwater Regulating Valve Positioner</strong><br /><i>Abstract:&nbsp;</i>Prior to the event, a Nozzle Flow High/Low alarm occurred on the 2D S/G, all conditions appeared normal. Approximately 30 seconds later the Nozzle Flow High/Low alarmed again, followed immediately by a Steam/Feed Flow Mismatch alarm. It was then noted that turbine load had increased by approximately 50 MWe. Digital Electro-Hydraulic Control was taken to manual in an attempt to stabilize the plant. At 0138 on 10/03/93, the Unit tripped due to LO-2 level in the 2D S/G. The cause of this event was a combination of Equipment Failure and Management/Quality Assurance Deficiency. The O-rings in the valve positioner hardened due to normal aging in a moderate heat environment. The corrective actions are: all four positioners on the Unit 2 FWRVs were replaced, A Preventative Maintenance program will be established for the Unit 2 FWRV positioner internal components every refueling outage. A routine elastomer changeout on valve positioners will be investigated. A routine instrument air filter cleaning/changeout program will also be investigated. The valve positioners on the 2FW046A through D valves will be inspected during the next Unit 2 refuel outage. There has been a reportable event involving a FWRV at Braidwood. A different valve and failure mode was involved, therefore there is no adverse trend.
4581993001 | River Bend | 01/13/1993 | 02/12/1993 | 9302190214 | <strong>RWCU Isolation Setpoint Allowable Valve Was Exceeded Due To Faulty Thermocouple Tester.</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1993 at 0745, with the plant at 100 percent power (Operational Condition 1), the isolation setpoint for temperature unit 1E31-N620A, in the reactor water cleanup system (RWCU), was determined to be above its Technical Specification (TS) allowable value. The trip setpoint value was set very close to the TS allowable value in December 1992. In addition, drifting occurred during the time between the surveillances, resulting in exceeding the TS allowable value. Therefore, the minimum number of operable channels per trip system required by TS Table 3.3.2-1 was not maintained and TS 3.3.2.b was violated. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(b) as operation prohibited by the plant Technical Specifications. <br /><br /> The root cause of this event is failure of a thermocouple tester with ineffective review of STP data. The Technician, Control Operating Foreman, and the Section Supervisor all failed to question the validity of the measurement and test equipment (M&TE) based on the low as-found values.
4581993002 | River Bend | 02/12/1993 | 04/25/1995 | 9505030253 | <strong>Technical Specification Surveillance Requirements Not Properly Implemented in Logic System Functional Tests</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1993 with the plant at 100 percent power (Operational Condition 1), a deficiency in plant surveillance test procedures (STPs) was identified. During a safety system functional assessment (SSFA) performed by Quality Assurance, it was discovered that the logic system functional test (LSFT) that verifies the isolation of reactor core isolation cooling system (RCIC) valve E51-F045 on a reactor water level 8 signal was not being completely satisfied. <br /><br /> Technical Specifications (TS) require that an LSFT and simulated automatic operation of all channels be performed at least once per 18 months. A combination of three surveillance test procedures was intended to meet the TS surveillance requirements; however, the SSFA revealed that these procedures did not provide adequate overlap. <br /><br /> As a result of this initial finding, a comprehensive LSFT program was implemented to review River Bend LSFT's and develop a cross-reference matrix indicating the procedure overlap for TS required surveillances. This report documents the results of the competed review of STPs and the final root cause analysis. For each deficiency identified, the circuitry and/or components were tested and found to be operable.
4581993003 | River Bend | 02/25/1993 | 06/14/1993 | 9306210375 | <strong>Deflation Of Reactor Airlock Door Seals Coincident With Outer Airlock Door Improperly Seated In Its Frame</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1993, it was discovered that two incidents occurred which apparently caused the interlock mechanism in the upper containment airlock at elevation 171' to operate improperly. In one incident the seals on one airlock door were partially deflated while the other airlock door was not completely closed. In the other incident, the reactor building door started to equalize while the outer door was not secured and sealed. Both of these cases constituted breaches of containment. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of a safety function. <br /><br /> Upon identifying the first incident, STP-057-0401 'Primary Containment Airlock Door Interlock Test' was performed to verify operation of the mechanical interlocks. A maintenance work order was generated to inspect the interlock malfunction following the second incident. A prompt modification request has been completed so that the handwheel lock solenoid energizes directly from the airlock door open/close limit switches during manual operation of the door, with power supplied to the airlock. This will properly interlock the doors to prevent misoperation from causing a containment breach.
4581993004 | River Bend | 03/24/1993 | 05/25/1993 | 9306010212 | <strong>Improper Locking Of Containment Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1993 at 1830, with the reactor at 100 percent power (Operational Condition 1), during a routine entry into the 171' elevation airlock, a deficiency was discovered in the locking of the reactor building door. The door was secured using a chain and padlock, with the chain wrapped around a spoke. The chaining configuration prevented entry into the airlock from the reactor building side; however, the chain could be lifted off of the spoke by personnel inside the airlock. A second occurrence involving the auxiliary building door was documented on March 31, 1993 in the 171' airlock. The actions of Technical Specification 3.6.1.4.b require that one airlock door remain locked at all times and that an individual is dedicated to assure that two doors are not opened simultaneously. GSU is submitting this report pursuant to 10CFR50.73(a)(2)(i)(b) as operation prohibited by the Technical Specifications. <br /><br /> Operator aids were posted for the doors in the 113' and 171' elevation containment airlocks. In addition, a modification to install a permanent locking device on each of the airlock doors has been implemented. This event did not result in unauthorized passage through the airlock. As required by Technical Specification 3.6.1.4, Action b, an individual was dedicated to assure that two doors were not open at the same time. In addition, for each case, the door was secured such that it could not have been opened from outside the airlock. The door could only be opened from inside the airlock.
4581993005 | River Bend | 04/15/1993 | 05/17/1993 | 9305210020 | <strong>Inadequate Surveillance Test Procedure For Reactor Core Isolation Cooling Steam Flow-High Timer Function</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1993 with the plant at 100 percent power (Operational Condition 1) during a logic system functional test procedure review program, it was discovered that the reactor core isolation cooling (RCIC) steam line flow - high timer function was not being adequately tested as required by Technical Specification (TS) Surveillance Requirement 4.3.2.1 Table 4.3.2.1-1.5.b. This surveillance is a monthly channel functional test that had never been performed on a monthly frequency. Note that a quarterly channel calibration surveillance implemented all of the requirements except the monthly frequency. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(b) as a condition or operation prohibited by the Technical Specifications. <br /><br /> The root cause of this event was the failure to include a monthly channel functional test in the initial procedure development process. Additional investigation revealed that this condition was also missed in subsequent reviews and revisions of these STPs. Corrective actions include revisions to the appropriate STPs to implement the monthly channel functional test, training for responsible personnel on this event, and retraining on the Technical Specification definitions for channel calibration, channel functional and logic system functional tests.
4581993006 | River Bend | 04/19/1993 | 05/26/1993 | 9306040179 | <strong>Sticking Of Main Steam Isolation Valve Combined With Improper Disposition</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1993 at 2312, with the reactor in cold shutdown (Operational Condition 4), during trouble shooting on inboard main steam line isolation valve (MSIV) 1B21*AOVF022B, the valve failed to stroke closed when given a close signal from the control room. GSU has since determined that this valve had been inoperable for a period of time exceeding the action statement of Technical Specification 3.4.7. This report is submitted pursuant to 10CFR50.73 (a)(2)(i)(b) as operation prohibited by the Technical Specifications. <br /><br /> The two major aspects of this event were (1) that MSIV 1B21*AOVF022B had failed; it was stuck in the open position, and (2) that evidence of the valve failure emerged on February 27, 1993 following the failure of a partial stroke test. However, following evaluation of indications, Operations personnel signed off the surveillance test procedure as "acceptable with comments." The result of this disposition was that the valve condition went unidentified until April 19, 1993. <br /><br /> GSU's evaluation of the safety significance of this event revealed only one postulated event which might, under worst-case assumptions, exceed the design basis analysis and/or regulatory limits. The probability of this event would place it in the range considered to be incredible. In addition, this evaluation confirmed that the outboard MSIV provides an adequate boundary to the release of radioactive materials.
4581993007 | River Bend | 04/20/1993 | 05/20/1993 | 9305270254 | <strong>Isolation Of Main Steam Isolation Valves Due To Personnel Lack Of Understanding While Unique Maintenance Conditions Prevailed</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1993 at 0911, with the reactor in Cold Shutdown (operational Condition 4), an isolation of inboard and outboard main steam isolation valves and main steam line drains occurred. The isolation signal was low condenser vacuum. GSU is submitting this report pursuant to 10CFR50.73(a)(2)(iv) as an automatic actuation of an engineered safety feature (ESF). <br /><br /> The root cause was determined by barrier analysis. The root cause is that the operating crew did not understand the specific details of the turbine control logic for the unique maintenance conditions that existed at the time of the event. This lack of understanding was also responsible for the absence of precautions in Operations Department procedures. Therefore, the protection of a procedural barrier did not exist. Corrective actions include revision of Operations policies and procedures. All systems functioned as designed during this event.
4581993008 | River Bend | 04/29/1993 | 07/22/1993 | 9307270131 | <strong>Improperly Prepared Relief Request For In-Service Testing Program Results In Non-Compliance With Main Steam Isolation Valve Testing Requirement</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1993, with the plant in Operational Condition 4 (Cold Shutdown), an investigation was initiated due to an apparent conflict between GSU's Safety Evaluation Report (SER) concerning the in-service testing (IST) program for pumps and valves and the River Bend IST Program Plan. Part of the SER, relief request (RR) #40, is worded such that it requires MSIV testing ever cold shutdown. This is in conflict with the IST Program Plan. However, since it is part of the SER, it is required pursuant to Technical Specification 4.0.5. During a cold shutdown in December 1992, the MSIV testing requirement was not met. Therefore, GSU has concluded that this event is reportable pursuant to 10CFR50.73(a)(2)(i)(b) as a condition prohibited by the Technical Specifications. <br /><br /> The root cause has been determined to be personnel error when testing frequency changes were processed on relief request #40 including the word 'every.' GSU has revised the MSIV fast full stroke testing frequency during cold shutdowns to be consistent ASME Section XI Subsection IWV-3411.
4581993009 | River Bend | 05/04/1993 | 06/04/1993 | 9306090437 | <strong>Quarterly In-Service Inspection Surveillance For Control Building Chilled Water Pump 'D' Was Missed Due To A Cognitive Human Error</strong><br /><i>Abstract:&nbsp;</i>At 1800 on May 4, 1993, with the reactor in Operational Condition 4 (Cold Shutdown) for planned outage (PO)-93-01, Operations personnel discovered that surveillance test procedure (STP)-410-6312, 'CONTROL BLDG CHILLED WATER SYSTEM QUARTERLY PUMP AND VALVE OPERABILITY DIV II' had not been completed for the control building chilled water pump, HVK*P1D, within the required Technical Specification time frame, rendering HVK*P1D inoperable on 4/18/93. The redundant pump HVK*P1B, was already inoperable due to failure of the applicable portion of (STP)-410-6312 on 2/10/93. Therefore, the Division II control building ventilation system (HVK/HVC) was rendered inoperable. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical Specifications and 10CFR50.73(a)(2)(vii) as an event in which a single cause or condition caused an independent train to become inoperable. <br /><br /> The root cause of this event was a cognitive error in that comments were not properly transferred from the STP data package cover sheet to the 'green sheet.' Corrective actions include procedural improvement, briefings for Operations personnel, and revision of Administrative Procedure (ADM)-0015, 'Station Surveillance Test Program' to require including a copy of the STP data package cover sheet with each 'green sheet' with an estimated completion date of July 31, 1993.
4581993010 | River Bend | 05/14/1993 | 08/16/1993 | 9308250443 | <strong>Loss Of Shutdown Cooling During De-Energization Of A Power Distribution Panel</strong><br /><i>Abstract:&nbsp;</i>On 05/14/93 with the plant in Operational Condition 4 (Cold Shutdown), shutdown cooling (SDC) was lost for approximately three minutes when one of the SDC suction valves closed. This occurred due to the initiation of a spurious engineered safety feature (ESF) actuation signal during de-energization of a 120 VAC power distribution panel. Therefore, this report is submitted pursuant to 10CFR50.73(b)(2)(iv) as an ESF actuation.<br /><br /> The root cause of this incident was that on-shift management personnel missed the need for compensatory measures when opening breaker #22 to prevent a loss of SDC. Corrective actions include revising procedural guidance to clarify which valve isolates when breaker #22 is opened. The duration of the loss was minimal (3 minutes) and instrumentation indicated no change in reactor coolant temperature.
4581993011 | River Bend | 05/21/1993 | 06/21/1993 | 9306290317 | <strong>Past Placement Of The Mode Switch In The Refuel Position During Testing Of Switch Interlock Functions</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1993 at approximately 1050, during testing of mode switch interlock functions, a question was raised regarding the mode switch position during this evolution. It was later determined that in the past, the mode switch had been placed in the 'Refuel' position during testing of switch interlock functions. Technical Specification Table 1.2 does not permit this; therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(b) as a condition prohibited by the Technical Specifications. <br /><br /> The root cause for this event consisted of the initial interpretation of the Technical Specifications and the presence of conflicting information in surveillance test procedures. <br /><br /> Corrective actions included revision of General Operating Procedure (GOP)-002 'Plant Shutdown' to emphasize specific guidance concerning mode switch requirements, revision of other procedures to be consistent with the TS requirements, and training.<br /><br /> Figure 'Required Number of Digits/Characters for Each Block' omitted.
4581993012 | River Bend | 06/03/1993 | 08/26/1993 | 9309020183 | <strong>SURVEILLANCE TESTS FOR THE HIGH DRYWELL PRESSURE TIMER FUNCTION OF THE AUTOMATIC DEPRESSURIZATION SYSTEM HAVE NOT BEEN DEVELOPED PER TECHNICAL SPECIFICATIONS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On June 3, 1993 with the plant in cold shutdown (Operational Condition 4), a deficiency in plant surveillance test procedures (STPs) was identified. During a logic system functional test review, it was discovered that the channel functional and channel calibration tests were not being performed as required by Technical Specifications. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(b) as operation prohibited by the Technical Specifications. A change analysis was performed which revealed the primary causal factor was inattention to detail during the initial procedure development process. Surveillance test procedures, STP-051-4297 and STP-051-4294, were created to perform the channel calibration of the ADS drywell high pressure bypass timers 'E' and 'F'. STP-051-4597 and STP-051-4594 were created to perform the channel functional tests of these same timers. Following this event, these timers were verified to be functioning properly and within the Technical Specification allowable setpoint limits. Therefore, GSU is confident that these timers have been operable since the initial procedure development and the pre-operational system testing. GSU's review of STPs based on MIL STD 105E revealed additional surveillances that were not being performed or did not completely meet the requirements of TS. The performance of revised STPs and preventative maintenance work orders verified that all untested circuitry was satisfactory.
4581993013 | River Bend | 06/29/1993 | 10/05/1993 | 9310120375 | <strong>Trip Of High Pressure Core Spray Pump Breaker Following Start Due To Failed Over Frequency Relay</strong><br /><i>Abstract:&nbsp;</i>At 0933 on June 29, 1993, with the plant at 100 percent power (Operational Condition 1), the high pressure core spray pump failed to start and run during a surveillance test due to a failed over-frequency relay. This report is submitted pursuant to 10CFR50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of a safety function. <br /><br /> GSU performed extensive testing on the over frequency relay. The testing revealed that the relay would consistently trip at a lower frequency value than its design setpoint, indicating relay failure as the root cause of the event. A new relay was obtained from the warehouse, tested satisfactorily, and installed in the switchgear. The HPCS pump motor was successfully started and operability was verified. Due to redundancies inherent in the ECCS system design, failure of the HPCS pump to start is bounded by the safety analysis. <br /><br /> This supplement is submitted to provide information concerning the dates for training on NUREG-1022 and the results of GSU's review concerning previous failures of single-train safety systems.
4581993014 | River Bend | 07/01/1993 | 11/05/1993 | 9311180129 | <strong>Improper Substitution Of A Sprinkler System For A Passive Fire-Rated Barrier</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1993, as part of a corrective action review of modification requests and associated 10CFR50.59 evaluations, GSU identified a deficiency in fire barrier separation requirements. Contrary to Branch Technical Position BTP CMEB 9.5-1, a sprinkler system was installed as a substitute for a passive fire-rated barrier under modification request (MR) 85-0548. From January 10, 1989 until a firewatch was established on October 26, 1989, compliance with Technical Specification 3.7.7 was not maintained. Therefore, this report is submitted pursuant to 10CFR50.73(a)(2)(i)(b). <br /><br /> The root cause investigation revealed an improper understanding of the extent to which an approved deviation (in this case for fire areas) could be expanded to include post-fire safe shutdown components under the provisions of 10CFR50.59 and NSAC 125 guidance. <br /><br /> Intensive training in the preparation and review of 10CFR50.59 evaluations has been provided for all engineers within the last year. GSU's increased emphasis on attention to detail and technical accuracy of 10CFR50.59 evaluations provides a high level of confidence that this error will not be repeated in the future. In addition, GSU's intensive review of previous 10CFR50.59 evaluations provides confidence that this is the only case of its kind. <br /><br /> The hourly firewatch patrols currently in place provide the proper compensatory action pursuant to Technical Specification 3.7.7.
4581993015 | River Bend | 07/23/1993 | 08/23/1993 | 9308300127 | <strong>Time Response Testing Of Isolation Instrumentation For The Reactor Water Cleanup And Reactor Core Isolation Cooling Systems Not Performed At The Intervals Required By The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1993 with the plant in Operational Condition 4 (Cold Shutdown), a deficiency in plant surveillance test procedures (STPs) was identified. During a technical review of surveillance test schedule requested by the STP scheduling coordinator, it was discovered that the time response testing of the isolation instrumentation of the reactor water cleanup (RWCU) and reactor core isolation cooling (RCIC) systems was not being performed at the proper time intervals. The last performance of these STPs such that the TS requirements were met was on October 18, 1985. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(b) as operation prohibited by the Technical Specifications. All instrument response times were found to be within tolerance. Based on these results, there is a high degree of confidence that these response times have been within tolerance since their last performance.
4581993016 | River Bend | 07/27/1993 | 08/27/1993 | 9309030333 | <strong>High Pressure Core Spray System Actuation Due To Improperly Prepared Revision To A Surveillance Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1993, with the plant in Operational Condition 4 (Cold Shutdown), the high pressure core spray (HPCS) system actuated. A test signal, initiated to perform a partial time response test on the system, resulted in the start of the HPCS diesel generator and the HPCS pump. Therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(b). The injection valve did not open since it was interlocked closed due to high reactor vessel water level. <br /><br /> The portion of the test being performed at the time of the event was a new test sequence which involved partially disabling the HPCS initiation logic. In preparing the STP revision to test this circuitry, leads were lifted to prevent the initiation of the remaining logic. This was the only action taken to prevent such an initiation. The primary root cause for this actuation was a personnel error in the development of the STP revision. The procedure did not explicitly state what was to be done to the leads once they were lifted. The procedure should have required the leads to be separated. However, this was not the case, and the leads were taped together, resulting in the actuation. Corrective actions included revision of the applicable STP, and training for electrical and instrumentation and controls (I&C) technicians.
4581993017 | River Bend | 08/10/1993 | 09/09/1993 | 9309170119 | <strong>Main Steam Isolation Valve Closure & RX Scram Due To Shorted Leads (Human Error)</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1993, at approximately 2149 with the plant at 75% power (Operational Condition 1), a personnel error, during "trouble shooting" the operation of the steam bypass & pressure regulating system, initiated a main steam isolation valve (MSIV) closure and subsequently a reactor scram. Investigation into the cause of this transient revealed that an instrumentation and control (I&C) technician was disconnecting a piece of test equipment from a circuit card in the Channel B steam bypass control circuitry. While disconnecting the test equipment, the technician shorted a signal common to +22vdc resulting in the partial loss of power for the steam bypass system. The root cause for this event was that the management policies and expectations were not effectively communicated to the workers, planners and line management. The persons performing the test should have implemented measures to isolate the surrounding work area once they had identified the confined working conditions. <br /><br /> Consistent with strengthening the program for GSU's management policies and expectations, I & C personnel have been instructed that they are responsible for screening the work area for possible unanticipated effects on the plant. Precautions/prerequisites that match the current plant conditions shall be specifically included in MWO test packages. A review of the plant response to this transient indicates that all plant systems reacted as designed. An analysis of the key plant parameters important to plant safety indicates that these parameters remained well within all safety limits. .
4581993018 | River Bend | 08/13/1993 | 12/15/1993 | 9312220356 | <strong>Isolation Of Reactor Core Isolation Cooling System During A Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>At 0815 on 8/13/93 with the unit in Operational condition 3 (Hot Shutdown), a Division II reactor core isolation cooling (RCIC) isolation occurred, causing RCIC steam supply valves E51*MOVF063 and E51*MOVF076 to automatically close. The isolation occurred during the performance of the RCIC equipment room ambient temperature high monthly channel functional position of surveillance test procedure (STP)-207-4241. An investigation by System Engineering could not found a problem with the procedure or any portion of the circuitry. <br /><br /> The investigation indicates that the root cause is the technician connected a digital multimeter to the wrong terminals of the relay base. This allowed sufficient current into the rest of the circuit to cause the isolation. A caution statement has been added to STP-207-4241 and a step has been added to verify that no voltage exists prior to measuring continuity across the terminal point of the relay. Following this event, corrective actions to eliminate the potential for human errors that could lead to RCIC isolations were identified in LER 93-022. These corrective actions included procedural revisions and a modification request to install a switch with a keyed lock to permit isolation of the relays that initiate isolation of the RCIC valves. The event was not safety significant since the system could have been placed in service at any time and the high pressure core spray system was available at all times.
4581993019 | River Bend | 08/17/1993 | 09/23/1993 | 9310010121 | <strong>Equipment Qualification Lifetime of a Hydrogen Igniter Cable Exceeded Due to Localized High Drywell Temperature</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1993, following engineering evaluation, GSU determined that hydrogen igniter cable 1HCSBBC534 had exceeded its equipment qualification lifetime due to localized high drywell temperatures. The affected circuit includes several hydrogen igniters. The localized high temperatures in the drywell were due to conditions discovered on July 15, 1993 by a GSU engineer conducting informal drywell temperature research on his own initiative. The engineer discovered that a reactor vessel insulation access door was open and access panels in the reactor vessel skirt insulation were not in their proper locations. These conditions disrupted the normal reactor vessel skirt cooling flow paths and led to higher temperatures in the drywell and particularly in the area of the hydrogen igniter cable. Since the qualified lifetime of the cable has been exceeded, GSU considers the cable to have become inoperable during cycle 5, prior to the shutdown on April 17, 1993. Therefore, this condition is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as operation prohibited by Technical Specification 3.6.6.3.<br /><br /> The hydrogen igniter cable was replaced. In addition, extensive corrective actions have been taken to prevent recurrence, including improvements in maintenance planning guidelines for insulation work and the drywell closure checklist to assure proper inspections of reactor vessel insulation.
4581993020 | River Bend | 08/21/1993 | 10/22/1993 | 9310270200 | <strong>Tornado Dampers In The Diesel Generator Building Would Not Reopen Following A Postulated Tornado Due To An Incomplete Purchase Specification</strong><br /><i>Abstract:&nbsp;</i>During a recent review of memos issued by Engineering to Operations concerning operability of the plant or plant equipment, as part of the corrective actions taken in response to problems with the River Bend Station airlocks, GSU determined that the exhaust tornado dampers for several buildings would not reopen following the passage of a postulated tornado. This condition was applicable to the diesel generator building, auxiliary building, control building, fuel building and standby cooling tower. The postulated tornado would enter the site and cause a loss of offsite power. On August 21, 1993, with the reactor in Operational Condition 3 (Hot Shutdown), GSU's evaluation of this event revealed that the postulated tornado event could have resulted in damage to the diesel generator systems. This report is submitted pursuant to 10CFR50.73(a)(2)(v), as a condition that alone could prevent the fulfillment of a safety function. <br /><br /> The root cause of this event was a failure to provide adequate information in a purchase specification. The exhaust tornado dampers in the diesel building, 1HVP*DMP1OA, B, and 11A, have been modified by blocking them open in accordance with modification request (MR) 93-0055. Evaluation of the other buildings has revealed that design features and/or alarms followed by operator actions would mitigate the consequences of the postulated tornado.
4581993021 | River Bend | 09/09/1993 | 10/06/1993 | 9310140183 | <strong>Associated Circuits, Common Enclosure Concern Identified With Control Circuits For 4160V And 480V Loads To Remote Shutdown System</strong><br /><i>Abstract:&nbsp;</i>At 0930 hours on 9/9/93 with the reactor at full power in operational mode 1, it was discovered that 4160 volt and 480 volt loads required for shutdown in the event of a control room fire may not have been available when required due to inadequate electrical protection. A fire protection team was organized as part of the corrective actions for NRC Inspection Report 93-09. Due to the heightened awareness and questioning attitude of the electrical design member of the fire protection team, it was found that fuses protecting the control circuits for these loads do not adequately protect the cables in the circuits in the event of a control room fire. <br /><br /> A review of this event indicates that the preliminary root cause is that the scope of compliance with Sections III.G and III.L of 10CFR50, Appendix R, concerning associated circuits and alternate shutdown capability, was not clearly understood during the development of the RBS Fire Hazards Analysis. <br /><br /> The action statement for RBS Technical Specification 3/4.3.7.4 'Remote Shutdown Monitoring Instrumentation and Controls' was entered upon discovery of this issue. Appropriately sized fuses were installed to ensure that these circuits are available for post fire safe shutdown or that they are no longer an associated circuit concern. <br /><br /> Concerns related to the identified condition were limited to cables entering the main control room and the ability of the circuits to remain functional for shutdown actions initiated from outside the main control room. This issue resulted in the potential for credited safe shutdown components to be unavailable if a fire would have occurred in the main control room.
4581993022 | River Bend | 09/24/1993 | 10/25/1993 | 9311010143 | <strong>Reactor Core Isolation Cooling System Isolation (ESF) When Isolation Valve Closed -- Cause Unknown</strong><br /><i>Abstract:&nbsp;</i>At 2140 on 9/24/93 with the plant at 100 percent power and the unit in Operational Condition 1, an engineered safety feature (ESF) actuation occurred during the performance of surveillance test procedure STP-207-5255. While in the process of performing the STP an isolation of the RCIC steam supply valve (E51*MOVF063) occurred. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) as an ESF actuation. <br /><br /> GSU has performed extensive testing on the circuit that caused the isolation. However, since the isolation signal could not be reproduced, it was not possible to conclusively determine the cause of the isolation. It is believed that the cause of the isolation was a malfunction of a temperature switch. <br /><br /> The temperature switch and relays were replaced. To further reduce the possible introduction of any spurious signal, the STP will specify that additional leads will be lifted by the I&C technician during future performance of STPs to isolate downstream portions of the circuit until an MR can be completed to place a switch in the circuit. <br /><br /> The high pressure core spray system was operable and available at the time of the occurrence. The containment isolation function of the isolation valve was not compromised, the system would have isolated should it have been called upon. The isolation did not degrade the ability of the plant to mitigate the consequences of an accident at any time; i.e., there was no safety significance involved with this event.
4581993023 | River Bend | 09/22/1993 | 10/22/1993 | 9310270070 | <strong>Improper Engagement Of Containment Airlock Door Handwheel Locking Mechanism Due To Inadequate Development Of Testing And Acceptance Criteria Supporting A Plant Modification</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1993, while performing STP-057-0401, an operator was carefully observing the function of the handwheel locking mechanism solenoid plunger on the lower containment airlock to determine if it would fail to properly engage the interlock lever of the door. The operator discovered that the handwheel could be rotated such that proper engagement would not occur. In this configuration, the affected containment airlock interlocks were declared inoperable per Technical Specification 3.6.1.4 and secured accordingly. Since this condition has possibly existed since the solenoids were re-energized per prompt modification request (PMR) 93-0009 in March 1993, this report is submitted pursuant 10CFR50.73(a)(2)(i)(B) as operation prohibited by the Technical Specification. <br /><br /> The root cause of this event is that engineers specified inadequate testing and acceptance criteria in a modification to address previous airlock problems. Corrective actions included modification of the interlock levers of the handwheel locking mechanisms, revision of the applicable surveillance test procedure, and training for all independent reviewers of modification requests on the expectations and requirements of the independent review process.
4581993024 | River Bend | 10/14/1993 | 10/28/1994 | 9411040048 | <strong>Reactor Scram During Turbine Testing Due To Failure Of Relay Contacts To Open</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1993, at 0842, with the plant at 95 percent power (Operational Condition 1) for the performance of routine turbine testing, a turbine trip and reactor scram occurred due to the failure of relay contacts to open per design. This report is submitted pursuant to 10CFR50.73(a)(2)(iv), as an automatic actuation of an engineered safety feature (ESF).<br /><br /> Entergy has concluded that this event was caused by the failure of the K15-1 relay contacts to open. During troubleshooting, the failure of the K15 relay could not be recreated. Following troubleshooting, the K15 relay was replaced and successfully tested. The plant was safely brought to the Hot Shutdown condition. The relay was subsequently tested in the relay shop and all test results were satisfactory. The failure mode could not be identified.
4581993025 | River Bend | 11/04/1993 | 12/06/1993 | 9312150263 | <strong>Train B Of The RHR System Rendered Inoperable While The HPCS System Was Out Of Service (Technical Specification 3.0.3 Entry) Due To Personnel Failures To Recognize The Resulting ECCS System Configuration</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1993 at approximately 2232, with the plant in Operational Condition 1 (Power Operation), loop B of the low pressure coolant injection (LPCI) system (residual heat removal (RHR) system - train B), was inadvertently rendered inoperable while the high pressure core spray system was out of service to support unrelated testing. This condition, HPCS and LPCI - B inoperable, is not specifically addressed by Technical Specification (TS) 3.5.1, "BCCS - Operating," and thus, requires entry into TS 3.0.3. Therefore, this report is submitted pursuant to 10CFR 50.73(a)(2)(i)(B), as operation prohibited by the Technical Specifications. <br /><br /> The root cause of this event is that Operations personnel did not recognize the resulting ECCS system configuration when RHR B was rendered inoperable to perform a retest. In Response to this event, GSU formed a team to review the event and initiated an operations accountability review. These reviews revealed that existing procedures are adequate. Counseling was provided for all of the individuals involved and Night Orders have been initiated to implement required reading for all Operations personnel, consisting of the condition report response documenting this event. Disciplinary actions are under evaluation. The ECCS configuration required by the River Bend Station design basis was maintained throughout this event.
4581993026 | River Bend | 11/17/1993 | 04/26/1994 | 9405020253 | <strong>Isolation Of The Reactor Core Isolation Cooling System Due To An Apparent Failure Of A Relay</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1993 at 2302, with the reactor in Operational Condition 1 (Power Operation) at 100 percent power, a containment isolation valve (1E51*MOVF064) inadvertently closed during a surveillance test on the reactor core isolation cooling system (RCIC). This event is reportable as an engineered safety feature actuation (ESF) pursuant to 10CFR50.73(a)(2)(iv). <br /><br /> GSU has concluded that a relay failure occurred which led to the isolation of the valve. The three relays associated with this RCIC isolation were replaced and shipped to their manufacturer for failure analysis. Although an erratically performing contact in one of the relays was noted during onsite testing, testing by the manufacturer did not detect any anomalies. Following replacement of the relays, the surveillance test procedure was successfully performed with the replacement relays.<br /><br /> All other plant equipment functioned as required during this event. Throughout this event, core cooling capability was assured since the high pressure core spray system was available.
4581993027 | River Bend | 11/20/1993 | 12/20/1993 | 9312280193 | <strong>Fire Watch Patrol Not Completed In A Timely Manner During A Security Computer System Outage Due To Conflicting Priorities For Security Personnel</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1993, with the reactor in Operational Condition 1 (Power Operation) at 100 percent power, a fire watch patrol in the fuel building which was due to be completed at 0800 was late by approximately 19 minutes. This occurred following an equipment failure in the security access computer which caused the fire watch to be denied entry into the fuel building when he attempted to use his key card. The late completion of the fire watch route did not meet the one-hour time unit specified by Technical Specifications 3.7.7 and 3.3.7.8, a condition prohibited by the Technical Specifications.<br /><br /> The cause of this event was that security personnel did not respond in a timely manner to allow manual actions by the fire watch due to conflicting priorities. The attention of security personnel was focused on meeting compensatory requirements of the security computer system outage. Failure to do this could have resulted in degraded plant security and a reportable condition. Assisting the fire watch conflicted with this priority. Corrective actions include permitting fire watches to use the emergency thumb latch in the event that computer access is unavailable. No fires occurred for the time period that the fire watch patrol was overdue. The area where detection was out of service was in the same fire area as the fire watch, and was partially visible from the location where the fire watch was waiting for security personnel to arrive. Detection systems in the remaining areas of the patrol route remained functional.
4611993001 | Clinton 1 | 03/16/1993 | 04/12/1993 | 9304190083 | <strong>Vendor Failure to Design Flywheel and Unexplained Capped Constant Bleed Drain On Air Tank Result in High Compressor Motor Current and Inoperable H sub 2 O sub 2 Analyzers</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, Illinois Power (IP) concluded that both divisions of hydrogen and oxygen analyzers had not been operable because their backup air supply systems were not capable of running for the period necessary to support operation of the analyzers following an accident and loss of plant Instrument Air. Therefore the requirements of Technical Specification 3.3.7.5 were not met. The cause of the event is attributed to the vendor's failure to include a flywheel in the design of the backup air supply compressor motor. In addition, unauthorized caps were found to be blocking the air tank constant bleed orifices. These conditions resulted in high motor current readings in excess of the motor nameplate and an overload trip of the division 1 analyzer. IP believes the caps were installed after initial operations but has been unsuccessful in identifying an installing work document. Corrective actions include installing flywheels, removing caps, determining if other positive displacement equipment may have similar problems, and installing labels identifying the orifices are not to be blocked.
4611993002 | Clinton 1 | 09/30/1993 | 10/28/1993 | 9311050003 | <strong>Unexpected Containment Isolations During Emergency Diesel Generator/Low Pressure Coolant Injection Test When Fuse Blows Due To Degraded Inverter Components and Solid State Logic Protection System Deenergizes.</strong><br /><i>Abstract:&nbsp;</i>While the plant was in REFUELING, a test of the Emergency Diesel Generator (EDG) and the B and C Low Pressure Coolant Injection (LPCI) loops produced several unexpected reactions. During the test, the power supply input fuse blew on the Nuclear Systems Protection System inverter. The fuse blew between the time offsite power was disconnected and the EDG picked up the alternating current (AC) loads and while the LPCI initiation pushbutton was depressed. As a result, the NSPS bus which powers the solid state logic protection systems lost its normal (inverter) and alternate (AC) power supplies. Because the logic protection systems lost power, the LPCI pumps did not start and the injection and minimum flow valves did not actuate as expected, the reactor core isolation cooling system received an unexpected signal to start, and several containment isolation valves closed unexpectedly, The fuse has failed in the past but with different results. The most probable cause of the blown fuse is degraded components within the inverter. Corrective actions include performing additional troubleshooting and testing, replacing inverter capacitors, and inspecting the inverter cabinet.
4611993003 | Clinton 1 | 11/13/1993 | 12/10/1993 | 9312200221 | <strong>Inadvertent Bumping of Transmitter Simulator During Reactor Protection System Logic System Functional Test Causes Reactor SCRAM, Containment Isolation, and Loss of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>While the plant was in COLD SHUTDOWN, and a Logic System Functional Test (LSFT) of the Reactor Protection System was in progress, low reactor water level 3 trip signals were generated causing a reactor SCRAM, closure of containment isolation valves and shut-off of shutdown cooling for about thirty-six minutes. Operators were fully aware that shutdown cooling had been isolated and were closely monitoring plant parameters which remained within acceptable ranges. The Reactor Water Cleanup System was in operation during the event, thereby fulfilling the Technical Specification ACTION which requires that an alternate means of reactor coolant circulation be established within one hour of a loss of forced reactor coolant circulation. All control rods had been fully inserted before the event. A technician performing the test caused the event by inadvertently bumping a transmitter simulator installed on an Analog Trip Module (ATM), resulting in generation of an unexpected trip signal which completed the SCRAM and isolation trip logics. Corrective action for the event includes: briefing personnel about precautions to be taken when working around simulators installed on ATMs; installing labels on simulators directing that potentiometer locks be used to prevent accidental setting changes; and revising LSFT procedures to include precautions to be taken when working around simulators.
4611993004 | Clinton 1 | 10/02/1993 | 11/19/1993 | 9312080036 | <strong>Failure of Shutdown Service Water System Pump to Automatically Restart During Emergency Diesel Generator/Emergency Core Cooling System Testing Due to Breaker Relay Contact Sequencing.</strong><br /><i>Abstract:&nbsp;</i>During a test of the Emergency Diesel Generator (EDG) and the Division 1 Emergency Core Cooling System, while the plant was in REFUELING, the Division 1 Shutdown Service Water system (SX) pump did not automatically restart as expected. The pump motor's breaker closed in response to a simulated Loss Of Coolant Accident (LOCA) signal, then tripped open on bus undervoltage, as designed, but failed to reclose upon return of bus voltage when the EDG picked up loads. The cause of the failure is attributed to the tight timing tolerance in the sequencing of electrical contacts in the breaker logic. The sequencing was such that the anti-pump coil did not drop out as it should have when the breaker tripped concurrent with a sustained start (LOCA) signal. Thus, the anti-pump coil remained energized preventing reclosure of the breaker following the breaker tripping open. Contact sequencing was not previously identified as critical to proper breaker functioning. Corrective actions for this event include modifying the logic for the Divisions 1 and 2 SX pump motor breakers, and reviewing other safety-related breakers receiving LOCA and undervoltage signals for similar deficiencies.
4611993005 | Clinton 1 | 09/29/1993 | 11/19/1993 | 9312080156 | <strong>Actuator Assemblies for Feedwater Containment Isolation Check Valves Were Incapable of Fully Seating the Valve Disc As Required by the Design Basis Due to Deficient Manufacturer Design.</strong><br /><i>Abstract:&nbsp;</i>With the plant shut down for refueling, local leak rate tests (LLRTs) identified unacceptable leakage rates for two feedwater air-assisted outboard containment isolation check valves; however, the inboard containment isolation valves were capable of preventing leakage to the outside environment. During the investigation to determine the cause of the unacceptable leakage rates, the actuator assemblies on the outboard valves were found to be incapable of performing their design function of fully seating the valve disc as required by the design basis, and were therefore reportable. The cause of this problem is a deficient manufacturer design. The manufacturer's design includes actuator assembly parts that were incapable of providing a closing force on the disc during full disk travel. A contributing factor was Illinois Power's failure to fully understand the actuator's function. Corrective actions include initiating a design change to fabricate and install proper actuator assembly parts, verifying proper actuator operation, and reperforming LLRTs. .
4611993006 | Clinton 1 | 12/06/1993 | 01/05/1994 | 9401120063 | <strong>Manual SCRAM due to Decreasing Reactor Water Level Caused by High Rotor Thrust Trip of Only Available Reactor Feed Pump</strong><br /><i>Abstract:&nbsp;</i>With the plant in STARTUP at about five percent reactor power, one turbine-driven reactor feed pump (TDRFP) uncoupled for an overspeed test and the motor-driven reactor feed pump (MDRFP) out of service to repair an oil leak, the only operating TDRFP tripped. Attempts to reset and restart the TDRFP were unsuccessful. Reactor water level dropped, and operators initiated a manual reactor SCRAM prior to the low reactor water level trip. Three groups of containment isolation valves received signals to close when water level dropped to the low reactor water level trip. Water level dropped to minus 19 inches on the wide-range level instrument before being restored. The most probable cause of the TDRFP trips were momentary rotor thrusts that activated the turbine thrust bearing wear detection trip system. Contributing to the cause of this event were operating the TDRFP at a continuous low-power/low-flow condition using high pressure steam, and continuing the plant startup after taking the MDRFP out of service. Corrective actions include: a review of the event to identify possible improvements to the reliability of the thrust wear detection trip system; continued evaluation of the event and incorporation of the lessons learned into the appropriate procedures to provide guidance on operating the plant at low-power/low-flow conditions; and operator review of the event.
4611993007 | Clinton 1 | 12/20/1993 | 01/17/1994 | 9402150395 | <strong>Incorrectly Positioned Steam Flow Control Valve Due To Operators' Lack of Full Understanding of the Design of the Valve's Controller Results in Saturated Offgas System, Loss of Condenser Vacuum, and Manual Reactor SCRAM</strong><br /><i>Abstract:&nbsp;</i>With the plant at 100 percent reactor power, operators were attempting to place a second Steam Jet Air Ejector (SJAE) in service so its new steam flow pressure controller could be tuned. When the main steam inlet isolation valve was opened, a high steam flow rate saturated the offgas system desiccant dryer with moisture and iced up the charcoal adsorber gas cooler, causing a loss of the capability to remove non-combustibles from the condenser. This led to the loss of condenser vacuum and a manual reactor scram at sixty percent reactor power. In preparing to put the SJAE in service, the operator verified the steam flow pressure controller setpoint dial was set at the zero position as directed by the procedure. The steam flow control valve was believed to be fully closed, which would have prevented the high steam flow when the isolation valve was opened. The cause of this event is a lack of operators' full understanding of the steam flow pressure controller design and how it relates to operating the control valve. Corrective action for the event includes revising the system operating procedure to identify the proper operation of the controller and training operators on that operation.
4611993008 | Clinton 1 | 12/30/1993 | 01/28/1994 | 9402100036 | <strong>Failure to Ensure Completion of Surveillance Within the Allowed Interval Results in Late Verification of Trip Setpoints for Average Power Range Monitors</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1993, Illinois Power determined that the Technical Specification surveillance requirement for setpoint verification of the Average Power Range Monitors (APRM) Flow-Biased Simulated Thermal Power-High Reactor Protection System trip functions was not completed within the specified surveillance interval and the allowed 25 percent extension. The surveillance was subsequently performed with satisfactory results. The cause of this event is attributed to personnel errors. The surveillance was not completed as scheduled due to available Control and Instrumentation Maintenance personnel performing other tasks and the work coordinator's failure to ensure completion within allowable time limitations. Further, Operations Support personnel failed to identify that the surveillance was overdue while preparing the report of late surveillances. Corrective action includes changing the daily activity schedule format to indicate the date scheduled surveillances exceed the surveillance interval and extension, and briefing Maintenance personnel on the use of the schedule to track completion of required surveillances.
4821993001 | Wolf Creek | 03/04/1993 | 04/05/1993 | 9304080148 | <strong>Inadequate Technical Specifications Developed By Westinghouse Results In A Failure To Include All Time Delays In Technical Specification Response Time Testing</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1993, at approximately 1150 CST, it was determined that the plant was potentially in a condition outside its design basis since not all time delays associated with the Reactor Coolant Pump (RCP) Undervoltage Trip function were included in the response time testing of the RCP Undervoltage Reactor Trip Circuit. A subsequent evaluation concluded that although all testing required to fulfill all of the assumptions within the Safety Analysis were not performed, the plant never operated in a condition outside its design basis. However, it was determined by management that due to the potential generic significance of the issue a voluntary Licensee Event Report would be submitted.<br /><br /> The root cause of this condition was inadequate Technical Specifications developed by Westinghouse for Wolf Creek Generating Station implementation. Although surveillance testing was accomplished in accordance with the requirements of Technical Specifications, the testing was not performed to the design basis. The appropriate procedures will be revised to include the additional time delays by June 1, 1993. Also, the potential generic implications of this event will be brought to the attention of the Westinghouse Owners' Group for further consideration and review.
4821993002 | Wolf Creek | 03/10/1993 | 04/06/1993 | 9304120143 | <strong>Containment Purge Isolation Signal and Control Room Ventilation Isolation Signal caused by the unidirectional characteristics of Target Rock Solenoid Operated Valves.</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1993, at 1123 CST, the Wolf Creek Generating Station Control Room received two automatic Engineered Safety Featured Actuation Signals (ESFAS): Control Room Ventilation Isolation Signal (CRVIS) and Containment Purge Isolation Signal (CPIS). The actuations were caused by a high gaseous radiation signal from Containment Purge Radiation Monitor GTRE22. Due to the increased radiation levels in Containment, from unknown causes, a Containment evacuation was ordered by the Shift Supervisor. The Equipment Hatch and Personnel Hatch inner door were closed within 22 minutes of the event, and verified closed in the Control Room within 29 minutes of the event.<br /><br /> Prior to the event, the plant was in MODE 5, Reactor Coolant System (RCS) temperature was approximately 100 degrees Fahrenheit, RCS vented (0 psig), and reactor vessel water level was 18' below the flange. Preparations to break the Conoseals were in progress. <br /><br /> Again, on March 11, 1993, at 0340 CST, GTRE22 went into the 'alert' range but no ESFAS occurred. Prior to this second occurrence, the plant was in MODE 6, all vessel head studs were detensioned and RCS was at about 100 degrees Fahrenheit, Reactor vessel level was 18 inches below the flange.<br /><br /> A number of areas were identified for possible improvement including the time frame for Pressurizer Relief Tank (PRT) purging and depressurization, evaluation of Target Rock Solenoid Operated Valve (SOV) applications in clearance orders, the replacement schedule for Target Rock SOVs, and incorporation of the unidirectional characteristics of SOVs into licensed and non-licensed training.
4821993003 | Wolf Creek | 03/13/1993 | 04/09/1993 | 9304120144 | <strong>Personnel Error By Licensed Operators Results In A Direct Flow Path Between The Containment Atmosphere And The Auxiliary Building During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1993, at 1645 CST, with the plant in Mode 6, Refueling, it was discovered that a direct flow path had been created between the Containment atmosphere and the Auxiliary Building during fuel movement in violation of Technical Specification 3.9.4. The direct flow path was created during the performance of procedure SYS EF-420, which is used to drain Train 'B' of the Essential Service Water System while in Mode 6. The procedure was originally required to be performed during Mode 5 or No Mode. The direct flow path existed for approximately 19 hours and Containment integrity was immediately restored upon discovery.<br /><br /> This event occurred as a result of cognitive personnel error by licensed operators who failed to review procedure SYS EF-420 to ensure compliance with the requirements of Technical Specification 3.9.4 prior to revising the procedure to allow its performance during Mode 6. The individuals involved will make presentations to the Operating Crews and to Wolf Creek Nuclear Operating Corporation management emphasizing the 'STAR' (Stop, Think, Act, Review) program and explain how self-checking techniques could have been used during this event. Also, a permanent revision to procedure SYS EF-420 will be made to clearly address the requirements of Technical Specification 3.9.4 during the draining of Trains 'A' and 'B' of the Essential Service Water system.
4821993004 | Wolf Creek | 03/16/1993 | 08/12/1993 | 9308170231 | <strong>Grid-To-Rod Fretting Results In Broken Fuel Rod</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1993, at 1045 CST, during fuel off-load operations following operating Cycle 6, it was discovered that a broken fuel rod segment, approximately 11-12 inches in length, was protruding out of fuel assembly F67 at core position H-6. Inspection activities resulted in the discovery of additional defective fuel rods in fuel assemblies F43, F54, and F67. This supplement report describes the results of additional evaluations which have been conducted since the submittal of the original report and to make minor editorial changes. <br /><br /> From the various investigations and evaluations conducted, grid-to-rod fretting has been identified as the principle failure mechanism. Based on analyses performed, it is believed that fluid-elastic excitation induced by cross flow is the root cause for the leaking fuel rods experienced in Cycles 5 and 6. Fuel modifications will be recommended by the fuel manufacturer (Westinghouse) to enhance fuel performance.
4821993005 | Wolf Creek | 03/22/1993 | 04/20/1993 | 9304260138 | <strong>Failure to perform "As Found" Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1993, a Wolf Creek Nuclear Operating Corporation (WCNOC) maintenance electrician was performing Work Request (WR) 04447-92 to replace or refurbish the actuator for Centrifugal Charging Pumps to Regenerative Heat Exchanger Containment Isolation Valve BG HV-8105 at Wolf Creek Generating Station (WCGS). This electrician skipped a step in the Supplemental Work Instructions and removed the valve's actuator before a pre-replacement ("as found") Local Leak Rate Test (LLRT) could be performed and verified. On March 23, 1993, Results Engineering personnel discovered that the actuator had been removed prior to the required "as found" LLRT being performed. The Control Room was notified and a Performance Improvement Request (PIR) was initiated to determine a root cause and proper corrective action.<br /><br /> Prior to the event, the plant was in MODE E (i.e., no fuel in the vessel), Reactor Coolant System (RCS) temperature was less than 100 degrees Fahrenheit, RCS vented (0 psig), and reactor vessel water level was at Mid-Loop to perform various maintenance activities and to complete eddy current testing on the "B" Steam Generator. <br /><br /> The root cause of this event has been attributed to cognitive personnel error on the part of a licensee maintenance electrician (non-licensed). The first step in the work instructions that pertained to verifying that a "PRE Replacement LLRT has been performed" was clear. <br /><br /> Areas addressed for improvement include the proper review of work instructions prior to the commencement of work and ensuring that adequate attention is given to job prerequisites and sign-offs.
4821993007 | Wolf Creek | 04/13/1993 | 05/11/1993 | 9305180425 | <strong>Late Surveillance Test Performance Caused By Lack Of Oversight Of The Surveillance Program Results In A Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1993, at approximately 1715 CDT, it was determined that surveillance test procedure STS EJ-100B, 'Residual Heat Removal System Inservice Pump B Test,' had not been accomplished by April 10, 1993. This surveillance test is required to be performed on a quarterly basis per Technical Specification 4.0.5 to demonstrate operability of Residual Heat Removal Pump (RHR) 'B'. On April 14, 1993, at 0010 CDT, RHR Pump 'B' was declared operable following the successful performance of surveillance test procedure STS EJ-100B. <br /><br /> The root cause of this event was a lack of oversight of the Surveillance Program. After it was identified that STS EJ-100B had the potential for becoming late, an attempt to resolve the deficiencies was not performed in accordance with step 6.6.2.5.1.2 of Administrative Procedure ADM 02- 300. Corrective actions include the proceduralization of the use of a Past Due Notification Sheet, which will be routed to the Control Room when a surveillance test procedure has not been completed at least two days prior to its late date. This will eliminate the use of verbal communications to relay information regarding surveillances becoming late and will place the Control Room in the information loop.
4821993008 | Wolf Creek | 04/27/1993 | 09/29/1993 | 9310050089 | <strong>Flux Doubling Circuit for Modes 3, 4, and 5 was blocked several days</strong><br /><i>Abstract:&nbsp;</i>April 16, 1993, at 1054 CDT, Instrumentation and Control (I&C) Technicians began performing surveillance test procedure (STS) IC-725B, "7300 Process and N.I. Response Time Test (2/4 Logic) Protection Set II" Revision 6. During performance of STS IC-725B both channels of Flux Doubling were blocked by Control Room Operators. At 1833 CDT, STS IC-725B was suspended due to the end of the shift and Flux Doubling was reinstated. STS IC-725B was recommenced on April 17, 1993, at 0754 CDT, and Flux Doubling blocked. STS IC-725B was again suspended at 1631 CDT, due to plant conditions and Flux Doubling was reinstated. Although Control Room Operators blocked both channels of Flux Doubling SE-RA! during the performance of STS IC-725B the requirements of Wolf Creek Generating Station (WCGS) Technical Specification (TS) Limiting Condition for Operation (LCO), Table 3.3-1 Action Statement 5b, were not met as required. <br /><br /> LER 93-008-00 detailed similar occurrences of Flux Doubling being blocked during performance of STS IC-725A and STS IC-725C without the appropriate TS actions being met on April 27 and April 28, 1993.<br /><br /> The root cause of this event is a misunderstanding of the applicability of TS 3.3.1 as specified in Table 3.3-1, Item 6.b., which states the requirements for source range neutron flux instrumentation while in Modes 3, 4, and 5. To avoid future misunderstandings I&C has enhanced their procedures to reference TS 3.3.1, and to emphasize that these requirements must be met if Flux Doubling is to be blocked or bypassed. In addition, alarm response procedure ALR 00-57B, "SR Flux Doubled BYP/BLOC, " was revised to reference TS 3.3.1.
4821993009 | Wolf Creek | 05/04/1993 | 06/01/1993 | 9306100381 | <strong>Receipt of Inadvertant Safety Injection Signal Due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1993, at 1500 CDT, upon completion of surveillance test procedure STS KJ-001B, 'Integrated D/G and Safeguards Actuation Test - Train B,' Operations personnel were performing Engineered Safety Feature Actuation Systems (ESFAS) restoration activities and preparing to place both trains of the Solid State Protection System (SSPS) in normal. The Supervising Operator erroneously instructed the Reactor Operator to reset the 'B' Steamline Low Pressure Safety Injection (SI) signal rather than block the SI signal. Upon resetting the 'B' Steamline Low Pressure SI signal a valid 'B' Train SI signal due to low steamline pressure was received. <br /><br /> This event was reported to the NRC Emergency Operations Center via the Emergency Notification System at 1700 CDT on May 4, 1993.<br /><br /> The root cause of this event is cognitive personnel error by licensed Operators. The responsible personnel have been directed to review the event and the activities leading up to the event to determine the circumstances and precautions which could have been implemented to prevent this event. Upon completion of this review the responsible personnel will prepare and give a presentation to their peers and Wolf Creek Nuclear Operating Corporation (WCNOC) management on the results of this review and how correctly performing the appropriate self-checking actions would have prevented this event. This action is being implemented as part of WCNOC's 'POSITIVE DISCIPLINE' program.
4821993010 | Wolf Creek | 05/08/1993 | 06/02/1993 | 9306070354 | <strong>Mode Change with the Motor-driven Auxiliary Feedwater Pumps in "Pull-to-Lock"</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1993, at 1838 CDT, Wolf Creek Generating Station (WCGS) entered Mode 3 (HOT STANDBY) from Mode 4 (HOT SHUTDOWN) with both Motor-Driven Auxiliary Feedwater Pumps (MDAFWP's) BA-P! rendered inoperable by their handswitches being in "pull-to-lock". Placing the handswitches in "pull- to-lock" prevents pumps from automatically starting. This situation remained uncorrected until May 9, 1993, at 0753 CDT, when the handswitches were returned to NORMAL to comply with Technical Specification 3.7.1.2. <br /><br /> WCGS Technical Specification Limiting Condition for peration (LCO) 3.7.1.2 requires that these pumps be operable in Modes 1, 2, and 3. The appropriate Action Statement, Action "b", was neither entered nor performed as required. Additionally, Technical Specification 3.0.4 was not adhered to as entry into an Operational Mode was made without all requisite LCO's being met. <br /><br /> The root cause of this event was failure of the Control Room Operating Crews to control plant work activity such that thorough consideration of administrative requirements could be made. <br /><br /> As an immediate corrective action management's expectations were clarified regarding turnovers, Control Room professionalism, and communications with the Operating Crews. Procedural changes were made to enhance the effectiveness of the Mode change review process. .
4821993011 | Wolf Creek | 05/18/1993 | 06/30/1993 | 9307070033 | <strong>NPIS Axial Flux Difference Limits were not updated with Tech. Specs. revision.</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1993, a reactor engineer at Wolf Creek Generating Station (WCGS) discovered that the Nuclear Plant Instrumentation System (NPIS) software used to calculate the upper and lower Axial Flux Differential (AFD) limits for Control Room Annunciator 79D (Delta Flux Out of Band) was not updated prior to Mode 1 operation, above 50 percent rated thermal power, following the sixth refueling outage to correspond with changes in those limits effected by Amendment 61, dated March 30, 1993, to the WCGS Operating License. Technical Specification (T/S) Amendment 61 discussed changes associated with cycle 7 and included the initiation of the 'Core Operating Limits Report' (COLR) for cycle 7 operation. Wolf Creek Generating Station failed to perform T/S Surveillance Requirement 4.2.1.1.b from May 18, 1993, through June 3, 1993, while the AFD limits were outside of COLR requirements. <br /><br /> The root cause was determined to be an inadequate review of the COLR by a Wolf Creek Nuclear Operating Corporation (WCNOC) reactor engineer (non-licensed). The review performed did not identify the NPIS software as being affected by the changed AFD limits. <br /><br /> On June 4, 1993, the NPIS software was updated to reflect the changes specified in the COLR. Reactor Engineering will develop a procedure which provides a checklist to ensure consideration of areas which can be affected by design changes important to safety, as applicable.
4821993012 | Wolf Creek | 05/10/1993 | 10/03/1997 | 9710090059 | <strong>Small Frictional Force Release In the Reactor Coolant System Support System During Heat-up Causing Unusual Noise</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1993, at 1507 CDT, with the unit in MODE 3, "HOT STANDBY," at approximately 540 OF the Control Room received an alarm on Annunciator 98E, "Seismic Recorder On." Loose Parts and Vibration Monitoring System (LPVMS) annunciator alarms were also received. Personnel inside the Containment Building reported hearing a single loud metallic slap (sound). Personnel in the Auxiliary Building reported hearing a rumble (thunder like) sound. A Reactor Coolant System (RCS) leak rate test was performed and an extensive walk down of the RCS, connecting systems, and the Containment, Auxiliary, Control and Turbine Buildings did not identify any evidence of RCS leakage or equipment damage. An evaluation of the data from this noise event and the fifth refueling outage noise events (which occurred on January 9, 1992, February 28, 1992, and March 16, 1992) revealed the events had occurred under similar plant conditions. It is believed a small frictional force release in the support system of the RCS occurring during heat-up from cold shutdown is the cause of the event. The exact location of the frictional force release could not be determined. However, analysis of the noise magnitude and consequences demonstrated that the subsequent heat-up and power operation of the Wolf Creek Generating Station (WCGS) would be within the design and licensing bases and would not involve changes in the plant Technical specifications or the plant license as described in the Updated Safety Analysis Report. Additionally, the magnitude of the noise and the degree of associated RCS movement has reduced in level with each event.
4821993013 | Wolf Creek | 08/26/1993 | 09/24/1993 | 9309290155 | <strong>Incorrect Wiring of the 10-60 Meter Differential Temperature Instrument</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1993, at 1430 CDT, Wolf Creek Generating Station's meteorological tower [IS-TWR] was de-energized for modifications and declared inoperable. The required Technical Specification instrumentation was declared operable at 1803 CDT on August 14, 1993. During later calibration of similar non-Technical Specification instrumentation, it was discovered that the 10-60 Meter Differential Temperature (Delta T) [TT] instrument had been wired incorrectly. This was reported to the Control Room on August 26, 1993, at 1-715 CDT, and the instrument declared inoperable since August 9, 1993. The wiring error was corrected and the instrument returned to operable status on August 27, 1993, at 1100 CDT. Because the period of inoperability extended beyond a 7 day period, and a Special Report pursuant to Technical Specification 6.9.2 was not submitted within the following 10 days, this incident is being reported as a condition prohibited by Technical Specifications. <br /><br /> As-built information that was incorporated into the modification drawings for PMR 03489 as a drawing clarification was incomplete. The 10-60 Meter Delta T cable tab markers were reversed in the field due to personnel error. Therefore the as-built drawings, as issued under the PMR, altered the field wiring configuration such that an incorrect wiring connection was allowed to go undetected during performance of a surveillance test procedure. The root cause of this event was personnel error in that the correct wiring configuration in the field was not confirmed. A contributing factor was that the technician performing the surveillance did not recognize the wiring error because he reversed the test equipment simulator constant and variable. Had the correct constant and variable been used, this reversed wiring error would have been discovered. The meteorological tower drawing as-builts have been established per PMR 03489 to reflect the correct field wiring configuration.
4821993014 | Wolf Creek | 05/01/1990 | 12/10/1993 | 9312160143 | <strong>Essential Service Water System Low Flow Prior to Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>Wolf Creek NUclear Operating Corporation (WCNOC) formed a Service Water Assessment Team (SWAT) which conducted a Service Water Assessment from July 1, through October 15, 1993. The goal of the assessment was to review data to identify potential programmatic or design improvements and assess current concerns with system operation and maintenance. The assessment included, in addition to other items, a review of past Defect Deficiency Reports (DDRs) and Reportability Evaluation Requests (RERs) that pertained to the Service Water System (SWS), Essential Service Water System (ESWS), Ultimate Heat Sink, supporting systems and portions of systems serviced by ESWS and SWS including heat exchangers, room coolers, air compressors, air conditioning units, etc.<br /><br /> SWAT reviewed DDR 90-021, initiated May 1, 1990, which was determined to be not reportable at the time due to the fact that no "as found" data was available (a non-conservative interpretation of NUREG-1022). However, Refueling Outage IV (RE IV) normal mode and Post Loss-OF-Coolant-Accident flow balances on the "A" and "B" ESWS trains identified problems that likely existed prior to RF IV since they were indicative of overall system fouling and subsequent long-term degradation. <br /><br /> In response to the SWAT review, RER 93-045 and Performance Improvement Request 93-1176 were initiated to conservatively determine, based on engineering judgement, if ESWS flow rates to safety-related components were below design flows prior to RF IV. As a result of these investigations a conservative determination was made that ESWS flows were likely below design requirements prior to Refuel IV.
4821993015 | Wolf Creek | 03/17/1993 | 11/26/1993 | 9312060081 | <strong>Breech of Containment During Refueling Operations due to Sampling.</strong><br /><i>Abstract:&nbsp;</i>Wolf creek Nuclear operating corporation (WCNOC) received information from the Callaway Nuclear Plant that when they changed filters on the containment atmospheric radiation monitors during core alterations or fuel movement, a breech of containment integrity occurred. Technical Specification 3.9.4.c was therefore violated during the time it took to change the filters. WCNOC then reviewed its corresponding Chemistry procedures for similar problems as part of its operating experience reviews. The investigation revealed that two Chemistry procedures were deficient in this regard. <br /><br /> WCGS Technical Specification Limiting Condition for Operation (LCO) 3.9.4.c stipulates that each containment building penetration providing direct access from the containment atmosphere to the outside atmosphere shall be either: 1) Closed by an isolation valve, blind flange, or manual valve, or 2) Be capable of being closed by an OPERABLE automatic containment purge isolation valve. This Specification is applicable during core alterations or movement of irradiated fuel in the containment. <br /><br /> Contrary to the above, on March 17, 1993, at 0009 hours CST, the particulate filter on containment atmospheric radiation monitor GT RE-31 was changed during fuel movement without isolating its containment penetrations. This is one of many similar occurrences during refueling outages. This incident is reportable under 10 CFR 50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications. <br /><br /> The root cause of this occurrence was inadequate procedural guidance. The investigation also revealed that in some cases Chemistry technicians did not closely adhere to WCNOC's standards for procedural usage.
4821993016 | Wolf Creek | 11/01/1993 | 12/10/1993 | 9312170036 | <strong>Programmatic Deficiencies Result in Unqualified Fire Brigade Member</strong><br /><i>Abstract:&nbsp;</i>Wolf Creek Generating Station (WCGS) Technical Specification Administrative Requirement 6.2.2.e specifies that the Unit Staff will include a 5 member fire brigade at all times. <br /><br /> Contrary to the above, on November 1, 1993, an individual whose fire brigade qualifications had lapsed served as a member of the fire brigade. This incident is being reported under 10 CFR 50.73 (a) (2) (i) (B) as a condition prohibited by Technical Specifications.<br /><br /> The root cause of this occurrence is attributed to an incomplete and inadequately implemented process used to verify personnel are current in fire brigade qualifications. This process was established as a corrective action in response to a previous similar occurrence. Responsibility for the overall verification program will be consolidated under the Fire Protection Specialist. Additionally, a hard copy roster will be used for watchbill verification in place of the computer program described in WCGS Licensee Event Report 90-022-00.
4831993001 | Callaway | 09/16/1993 | 10/08/1993 | 9310140324 | <strong>Non-Conservative Setpoints for Gaseous Radiation Monitors Due to Failure to Incorporate Change into Setpoint Database During Construction</strong><br /><i>Abstract:&nbsp;</i>On 9/16/93, evaluation of a discrepancy between the Final Safety Analysis Report and Callaway Equipment List (CEL) determined that use of an incorrect controlling isotope had resulted in non-conservative setpoints for Control Room HVAC Radiation Monitors (GKRE0004 and GKRE0005) and Containment Purge Monitors (GTRE0022 and GTRE0033). These non-conservative setpoints could have allowed Technical Specification (T/S) values to be exceeded for T/S 3.3.3.1 actual submersion dose rate (from 1984 to 1/1/93) and T/S 4.9.4.2 trip setpoint concentration (from 3/22/92 to 4/17/92 during core alterations). The plant was in Mode 1, 90% power, at time of discovery. <br /><br /> During construction (1984), Callaway revised the controlling isotope for these radiation monitors from Krypton (Kr-85) to Xenon (Xe-133). This change in controlling isotopes caused a change in the conversion factor that was not incorporated into the Bechtel setpoint document (JU-8000). Monitor setpoints were calculated using the JU-8000 conversion factor and checked against CEL (developed from JU-8000). The reason the data was not incorporated into the JU-8000 is indeterminate due to time lapse since the error. <br /><br /> GKRE0004 and GKRE0005 were declared inoperable. Control Room Emergency Ventilation was isolated and operated in recirculation to meet T/S 3.3.3.1 until proper setpoints were instituted. GTRE0022 and GTRE0033 setpoints were recalculated using Xe-133 and will be instituted prior to core alterations. Other gaseous effluent and process radiation monitors were reviewed to ensure the correct isotope had been used for setpoint calculations; no other T/S problems were found. The current design control and licensing document change process was evaluated and determined to be adequate to prevent recurrence.
4831993002 | Callaway | 10/10/1993 | 11/09/1993 | 9311150223 | <strong>Core Alteration Performed Without an Operable Boron Injection Flowpath</strong><br /><i>Abstract:&nbsp;</i>On 10/10/93 at 1530, a core alteration was performed without an operable boration injection flowpath. The plant was in Mode 6 - refueling.<br /><br /> On 10/10/93, the operable boron injection flowpath consisted of the 'A' Boric Acid Storage Tank, the 'A' Boric Acid Transfer Pump, and the 'B' Centrifugal Charging Pump. Both the 'A' and 'B' Emergency Diesel Generators (EDG) were operable. On 10/10/93 at 1347, the 'A' EDG was removed from service, rendering the boron injection flowpath inoperable. At 1530, before control room personnel realized the inoperable EDG made the boron injection flowpath inoperable, a core alteration was performed when the upper internals assembly was removed from the reactor vessel. Prior to additional core alterations, the boron injection flowpath was re-aligned to an operable configuration. <br /><br /> This can be attributed to a lack of clear plant direction and understanding of which boron injection flowpath equipment must be capable of being powered by an EDG when in Modes 5 and 6.<br /><br /> The appropriate procedures will be revised to provide guidance for the necessary reviews and verification prior to removing an EDG from service in Modes 5 and 6. The plant will evaluate submittal of a T/S change to eliminate the requirements for an operable boration flowpath in Mode 6 when all boron dilution flowpaths have been isolated.
4831993003 | Callaway | 10/14/1993 | 11/15/1993 | 9311300061 | <strong>Core Alterations Performed with Direct Flowpath from Containment Atmosphere Due to Work on Containment Atmosphere Monitors</strong><br /><i>Abstract:&nbsp;</i>On 10/14/93, it was determined that work on the Containment Atmosphere Radiation Monitors (GTRE0031 and GTRE0032) and the hydrogen analyzer created flow paths from containment atmosphere. A review of similar penetrations showed that routine containment atmosphere sampling also created a flow path from containment. During the time the flow paths existed, core alterations were in progress. Technical Specification (T/S) 3.9.4, which requires each penetration providing direct access from containment to be closed during core alterations, was not met. The plant was in Mode 6, Refueling.<br /><br /> This event can be attributed to a lack of management work control over the specific work on the radiation monitors and the hydrogen analyzer. Penetrations may have been overlooked due to their small size and their function to monitor containment atmosphere. The work being performed would have been acceptable in higher modes since the penetrations are protected by a Containment Isolation Signal, conditioning personnel to believe the work was allowable.<br /><br /> Upon discovery, containment integrity was restored. Technicians were instructed to isolate GTRE0031 and GTRE0032 prior to filter changeout and to take containment atmosphere samples locally. A review will be performed to determine if there are similar situations at other penetrations. Administrative controls will be provided to assure compliance with T/S. Training will emphasize the connection between containment integrity and core alterations. T/S 3.9.4 will be evaluated for changes.
4831993004 | Callaway | 10/28/1993 | 11/26/1993 | 9312060036 | <strong>Overtemperature Delta Temperature Time Constant Set Non- Conservatively With Respect to Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 10/28/93 while in Mode 6 - Refueling, it was determined that an overtemperature-delta temperature (OTdeltaT) setpoint had been set non-conservatively with respect to Technical Specifications since 5/7/93 following an 18-month calibration during power operations. The root cause of this event is a human performance error by Instrument and Control technicians when calculating the time constant. The procedure providing instruction for the channel calibration/functional test surveillance did not provide a verification for the time constant setpoint after the card was placed in the cabinet. This event will be reviewed with technicians and emphasis placed on self-checking of work performed. The appropriate procedure will be revised to ensure an adequate retest of time constant setpoints each time the circuit boards are adjusted. The time constant setpoints for the remaining channels were verified to be properly calibrated. Other surveillances involving time constants have been reviewed to assure adequate verification is provided following any setpoint adjustments. The OTdeltaT reactor trip provides core protection to prevent Departure from Nucleate Boiling (DNBR). A safety evaluation has concluded that the minimum DNBR remained above the safety analysis limit and the design basis continues to be met.
4831993005 | Callaway | 11/14/1993 | 12/13/1993 | 9312200321 | <strong>Engineered Safety Feature (ESF) Actuation on High Steam Generator (S/G) Level Due to Testing of the Auxiliary Feedwater Motor-Operated Flow Control Valves</strong><br /><i>Abstract:&nbsp;</i>On 11/14/ 93 at 18:16 CST, while performing OSP-AL-V0002, a Steam Generator (S/G) 'A' hi-hi level/turbine trip alarm and resultant Feedwater Isolation Signal (FWIS) were received. This procedure verifies that each auxiliary feedwater motor operated flow control valve limits the flow to each S/G from the motor driven pumps. The control loop for ALHV0007, feeding S/G 'A' was being adjusted to prevent flow oscillations. The plant was in Mode 4, Hot Shutdown. <br /><br /> When the licensed Reactor Operator (RO) began the procedure, blowdown isolation valve on S/G 'A' was isolated to fix a broken air line. The RO started filling while valve ALHV0007 were being adjusted. Approximately four minutes later, while the RO was securing flow to S/G 'A' at 75 % , the alarm was received. He assumed that he had another 3 % to go before hitting the 78 % level trip setpoint. It was later observed that the level recorder was selected to the transmitter that was indicating the lowest level. <br /><br /> The system/component line ups that existed due to testing and maintenance made it difficult to determine if a valid FWIS had been generated. The FWIS was discovered to have been valid on 11/15/93 while troubleshooting a discrepancy in 'A' and 'B' train Main Steam and Feedwater Isolation Signal cabinets. <br /><br /> The root cause of the event was that the S/G level was allowed to be taken too close to the high level setpoint for a FWIS while utilizing the lowest reading indication. To prevent recurrence, OSP-AL-V0002 will be revised to specifically state a level band for S/G control. Also, all licensed personnel will be reminded of the importance to utilize all available indications and to allow sufficient margin for actuation setpoints when performing infrequent evolutions.
4981993001 | South Texas 1 | 01/05/1993 | 02/03/1993 | 9302110289 | <strong>Technical Specification 3.0.3 Entry Due to Two Reactor Coolant System Delta-T Channels Being Inoperable at the Same Time</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1993, at 1033 hours, Unit 1 was in Mode 1 at 77% power. While performing a Delta-T evaluation on the Reactor Coolant System (RCS), it was discovered that the RCS loop 3 was outside Technical Specification 2.2.1 and was declared inoperable. Prior to this event, Excore Power Range channel (N44) had been declared inoperable, with the bistables tripped for RCS loop 4 Overtemperature Delta Temperature (OTDT), to conduct corrective maintenance on the rod stop bistables. As a result, Unit 1 entered Technical Specification 3.0.3 when Delta-T loop 3 and loop 4 were both inoperable and compliance with Technical Specification 3.3.1 could not be maintained. The cause of this event has been attributed to procedure that lacked specific criteria for declaring a channel inoperable and for coordinating the Delta-T evaluations with other cross train activities. corrective actions include restoring the RCS loop 4 OTDT bistables and the power range channel (N44), discussing this event during Licensed Operator Requalification Training, and revising the procedure governing reload startup testing to provide specific guidelines for declaring a loop inoperable if it is outside the requirements of Technical Specifications.
4981993002 | South Texas 1 | 01/09/1993 | 02/08/1993 | 9302120204 | <strong>Technical Specification 3.0.3 Entry due to Two Channels of Power Range Nuclear Instrumentation Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 9,1993, at 0175 hours, Unit 1 was in Mode 1 at 74% power. A Tech Spec 3.0.3 condition was declared due to two channels of Power Range Nuclear Instrumentation (NI) being inoperable. The cause of this event was inadequate procedural guidance in that the calibration procedure did not specify the appropriate action to take if an NI channel is inoperable. Corrective action includes revising the channel calorimetric procedure to insure that appropriate actions are taken so that calorimetrics are performed for NIs being returned to service and performing a review to determine if other surveillance procedures could be susceptible to similar problems.
4981993003 | South Texas 1, South Texas 2 | 01/12/1993 | 02/11/1993 | 9302170313 | <strong>Technical Specification 3.0.3 Required Shutdown of Both Units Due to Inoperable Steam Line Pressure Channels</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1993, Unit 1 and 2 were in Mode 1 at 75% and 96% power, respectively. During an Engineering review of the surveillance data for the low steam line pressure and the high negative steam line pressure rate, it was observed that the tolerance band used during calibration would allow the Technical Specification (TS) value not to be met. HL&P determined that nine of the required twelve channels of low steam line pressure and five of the required twelve high negative steam line pressure rate channels for Unit 1 were inoperable. Additionally, all twelve channels of low steam line pressure and seven of the twelve channels of high negative steam line pressure rate for Unit 2 were also inoperable. This condition placed the Units in a Technical Specification 3.0.3 condition. The cause of this event was a lack of understanding by procedure writers regarding the calibration of time constants. Actions to correct this event are, the affected time constants for the Units were calibrated, the steam line surveillance procedures were placed on administrative hold pending revision, a TS Interpretation was written to address setpoint tolerances, and a review process will be established to determine the accuracy of surveillance procedures with respect to the design basis.
4981993004 | South Texas 1 | 01/12/1993 | 02/11/1993 | 9302170306 | <strong>Technical Specification Violation Due to the Failure to Perform a Surveillance Required by ASME Section XI Codes</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1993 at 1300 hours, Unit 1 was in Mode 1 at 74% power. An evaluation performed by plant personnel determined that a condition prohibited by Technical Specifications had occurred due to an ASME Section XI Code surveillance test exceeding its grace period for the Outside Containment Isolation Supplementary Purge Valve. This rendered the valve technically inoperable and the action statement for Technical Specification 3.6.3 should have been entered and the other isolation valve in that line should have been secured. The cause of this event is an error in the plant surveillance database which shows that governing procedure can only be performed in Modes 5 and 6 and an incorrect interpretation by Operations personnel. Corrective actions include changing the desk top instruction for the plant surveillance coordinator to include revising the plant condition mode on the surveillance scheduling sheets and performing a review of the Pump and Valve Inservice test plan to verify that the classification of cold shutdown valves is consistent with the mode specified for the performance of the Inservice test procedures.
4981993005 | South Texas 1 | 01/20/1993 | 11/23/1993 | 9312030095 | <strong>Standby Diesel Generator 13 Failure to Start</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1993, Unit 1 was in Mode 1 at 95% power. Standby Diesel Generator 13 failed to start during a monthly surveillance, due to paint which had been applied to the fuel injection pumps. The paint ran into the fuel metering rod ports and caused binding of the fuel metering rods. The primary cause of this event was the lack of proper work process control. Contributing causes were inadequate implementation of lessons learned from industry operating experience and inadequate verbal communications which led to a lack of clearly defined responsibility for ensuring paint was not applied inappropriately. Corrective actions that have been or will be taken include revising work process control documents to include specific guidance on painting activities and pre-job briefings, enhancing the Operating Experience Review program, performing a case study of the event for training purposes, and including the event in the Licensed Operators Requalification Program. This event is also being reported as a valid failure of Standby Diesel Generator 13. The performance described herein clearly does not meet management's expectations. Efforts to improve station safety culture are ongoing.
4981993006 | South Texas 1 | 01/21/1993 | 02/19/1993 | 9302240262 | <strong>Technical Specification Violation Due to an RCS Delta Temperature/Average Temperature Loop Found Out-of- Tolerance</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1993, at 1800 hours,Unit 1 was in Mode 1 at 95% power. An evaluation performed by plant personnel determined that from January 8, 1993 to January 12, 1993, Unit 1 was in a condition prohibited by Technical Specifications. The lead time constant of Reactor Coolant System Delta Temperature/Average Temperature loop RC-0430, was left outside the allowed tolerance of 5% of nominal value. This rendered the affected bistable inoperable. Per the Technical Specifications, this channel should have been placed in trip within six hours. The cause of this event was personnel error. The procedure governing the Delta Temperature/Average Temperature loop RC-0430 incorporated an incorrect graph for the Lead/Lag time constant. A contributing cause was an inadequate review of the procedure. Corrective actions include correcting the graph, recalibrating the RC-0430 temperature loop, recalibrating two additional affected loops, and reviewing this event with Maintenance Department procedure writers.
4981993007 | South Texas 1, South Texas 2 | 02/04/1993 | 03/05/1993 | 9303090357 | <strong>Technical Specification Required Shutdown due to the Inoperability of an Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1993, Unit 1 was in Mode 1 at 98% power. At 0937 hours, Unit 1 commenced a plant shutdown and an Unusual Event was declared due to the failure to return the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) 14 to an operable status within the required Technical Specification allowed time. On February 1, 1993, during performance of a surveillance test, TDAFWP 14 tripped on overspeed. This resulted in the pump being declared inoperable and Unit 1 entering a 72 hour action statement. On February 3, 1993, Unit 2 experienced a reactor trip at which time TDAFWP 24 oversped and tripped. Since the 72 hour allowed time was due to expire soon and the cause of the Unit 2 overspeed had not been determined, Unit 1 was shutdown. The cause of the TDAFWP 14 overspeed events was water intrusion into the TDAFWP turbine adversely affecting performance. Corrective actions included extensive testing, analysis, and component examination to determine the causes of overspeed trips on TDAFWP 14 and TDAFWP 24.
4981993008 | South Texas 1, South Texas 2 | 02/06/1993 | 03/04/1993 | 9303090042 | <strong>Technical Specifications Violation Due to a Failure to Perform RCB Pressure Surveillances</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1993, Unit 1 and Unit 2 were in Mode 4 at 0% power. While performing the Unit 1 required shift surveillance, the operator observed that the requirement of Technical Specification 3.3.2 for Containment Pressure High-1 had not been recorded in the log as required. The cause for this violation of Technical Specifications was inaccurate surveillance logs. In the attempt to combine the Unit 1 and Unit 2 procedures into a common procedure, instructions for containment pressure channel check in Mode 4 were inadvertently excluded. Upon identification of the missed surveillance readings, immediate corrective actions included: a field change (FC) was approved to correct the log error, the surveillance (channel check) was performed satisfactorily, and an archival computer report was generated to verify that the containment pressure channels had been within the required tolerances while in Mode 4. HL&P is developing a surveillance procedure enhancement program to ensure that surveillance procedures accurately reflect the design basis and adequately perform the Technical Specification intended functions.
4981993009 | South Texas 1, South Texas 2 | 02/17/1993 | 05/20/1993 | 9305260483 | <strong>Technical Specification 3.0.3 Entry Due to Potentially Undersized Fuses in the Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1993, Unit 1 was in Mode 5 and Unit 2 was in Mode 4, both at 0% power. Plant personnel determined that a potentially unanalyzed condition existed in both units related to a failed fuse event that occurred on February 13, 1993. This unanalyzed condition involved suspected undersized fuses found in the Solid State Protection System (SSPS) in which an inrush current could cause the fuses to fail and prevent the fulfillment of the SSPS's intended safety function. In response to the inoperable SSPS actuation cabinets, Unit 2 entered Technical Specification Section 3.0.3 and plant cooldown to Mode 5 was initiated at 1030 on February 17, 1993. Unit 1 was already in Mode 5. The event was caused by the random age related failure of a SSPS fuse. In response to the event, the 10 amp fuses were replaced with 20 amp fuses in both Units, other 120 volt vital A.C. distribution and class 1E DC circuit panels were reviewed for similar conditions, field verification of selected protective devices was conducted, and a failure analysis of the blown fuse was performed by an independent laboratory and reviewed by the fuse manufacturer. Additionally, lessons learned will be formally factored into the design process.
4981993010 | South Texas 1 | 02/23/1993 | 03/26/1993 | 9303310182 | <strong>Unplanned Actuation of an ESF Damper due to the Presence of Halon</strong><br /><i>Abstract:&nbsp;</i>On February 24,, 1993, Unit 1 was in Mode 5 at 0% power. At 0000 hours, a halon actuation occurred in the plant computer room, associated distribution room and associated battery room. Subsequently, an Engineered Safety Features (ESF) automatic isolation of the plant computer room damper (HE-FV-9603) occurred due to the presence of a halon actuation signal. Operators then manually closed the main supply damper to the computer and relay room (HE-9699). Automatic closure of the dampers associated with the distribution and battery rooms also occurred to isolate these rooms due to the presence of the halon actuation signal. The cause of this event was that the effects of an electrical load test on the Fire Protection System were not considered prior to the performance of the test. A contributing cause was less than adequate guidance on the use of load cells. Corrective actions include revising the Fire Hazards Evaluations procedure to include examples of activities which require performance of a Fire Hazard Evaluation, and performing an evaluation to determine if additional measures can be taken to prevent future inadvertent actuations of the fire protection system. Additionally, the Planners Guide will be revised to add precautions for the use of load cells.
4981993011 | South Texas 1, South Texas 2 | 03/17/1993 | 04/16/1993 | 9304190254 | <strong>Technical Specifications Violation Due to a Failure to Perform Damper Position Verification During Required Surveillance</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1993, at 0900 hours, Unit 1 was in Mode 5 at 0% power and Unit 2 was in Mode 6 at 0% power. It was discovered that the monthly surveillance for the Fuel Handling Building (FHB) Heating, Ventilation and Air Conditioning (HVAC) Exhaust System did not verify that the FHB Outside Air Supply Relief Dampers opened when the FHB HVAC Emergency Exhaust System was actuated for the surveillance. This discovery was made while performing a walkdown verification of a new procedure about to be approved. The cause of this event is an inadequate surveillance procedure. The corrective actions for this event include testing the dampers, revising the surveillance procedures, revising the checklist for reviewing surveillance procedures, and implementing a surveillance procedure enhancement program.
4981993012 | South Texas 1, South Texas 2 | 04/05/1993 | 07/13/1993 | 9307220230 | <strong>Technical Specification Violation due to Incorrect Settings of Several Molded Case Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1993, at 1100 hours, Unit 1 was in Mode 5 at 0% power and Unit 2 was defueled while in a refueling outage. Plant personnel determined that a reportable condition existed because the setpoints of the Class 1E 480 VAC magnetic adjustable molded case circuit breakers were incorrect which could cause potentially unexpected breaker trips. Unit 1 had five loads which were declared inoperable until breaker testing could confirm otherwise. Unit 2 had seven loads declared inoperable. These loads are safety-related motor operated valves (MOVs) in various systems. The cause of this event was that the instructions for setting circuit breaker magnetic adjustable elements did not provide sufficient clarity to ensure consistent application. Corrective actions include revising the test procedure to clarify the methodology used to establish the breaker setpoints and conducting training on the procedure and test methodology. Analysis of safety-related molded case circuit breakers was performed to determine if the loads were, in fact, actually inoperable. The results of the breaker testing of the 12 originally declared inoperable loads fed by improperly set breakers determined that these MOV loads were actually operable following analysis of the as-found breaker settings.
4981993013 | South Texas 1 | 04/08/1993 | 05/07/1993 | 9305130120 | <strong>Technical Specification Violation due to Performing Positive Reactivity Changes in Mode 5 Without an Operable Centrifugal Charging Pump</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1993, Unit 1 was in Mode 5 at 0% power with the Reactor Coolant System (RCS) temperature and pressure at 192 degrees and 380 psig, respectively. Plant personnel completed a reportability review and determined that on April 1, 1993, during the time periods from 1305 to 1729 hours and from 1817 to 2058 hours (a total of seven hours, nine minutes), Technical specification 3.1.2.1 and 3.1.2.3 were violated. Positive reactivity changes were made while operating a functional but administratively inoperable Centrifugal Charging Pump (CCP). The cause of this event was the use of an ineffective system for tracking inoperable Technical Specification equipment and actions during an outage. Corrective actions include placing temporary labels on the control board to remind personnel of important Technical specification equipment status, and placing an information board in the control room highlighting key Technical Specification action times and dates.<br /><br /> Additionally, this event will be included in Licensed Operator Requalification Training.
4981993014 | South Texas 1 | 04/23/1993 | 05/21/1993 | 9306010006 | <strong>Technical Specification Violation due to Control Room Envelope HVAC not Operated in Correct Mode</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993, Unit 1 was in Mode 5 at 0% power. Plant personnel completed a reportability review which determined that on two separate occasions in May, 1990, the Control Room Envelope (CRE) Heating, Ventilating and Air conditioning (HVAC) system was not operated in the correct mode. This constituted a violation of Technical Specifications 3.7.7 and 3.3.3.7. Since this event occurred approximately three years ago the root cause of this event cannot be determined, but is speculated to be inadequate tracking and implementation of the Technical Specification Limiting Conditions for Operation (LCOs) and Actions regarding CRE HVAC, Essential Chill Water System and the Chemical Detection System while in Mode 5. The ability to track and implement Technical Specification LCOs and Actions as well as reduce administrative burden of the on-shift Senior Reactor Operators has been significantly improved since May, 1990.
4981993015 | South Texas 1 | 04/23/1993 | 05/21/1993 | 9305280334 | <strong>Technical Specification Violation due to Non-conservative Determination of Equipment Service Time</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1993, Unit 1 was in Mode 5 at 0% power. Plant personnel completed a reportability review which determined that in May, 1990, the Control Room Makeup and Cleanup Filtration System service time exceeded the applicable surveillance requirements. This constituted a violation of Technical Specification 4.7.7. The cause of this event was the failure to develop a run hour tracking method which accounted for operation of the cleanup fans independent of the makeup fans in Modes 5 and 6. The run times for both the cleanup and makeup fans are currently being monitored individually.
4981993016 | South Texas 1, South Texas 2 | 05/03/1993 | 07/15/1993 | 9307220320 | <strong>Technical Specifications Violation due to Circuitry for the Steam Generator Power Operated Relief Valves and Post Accident Monitoring Instruments Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1993, at 1640 hours, Unit 1 was in Mode 5 at 0% power and Unit 2 defueled. It was discovered that circuitry for the Unit 1 Steam Generator Power Operated Relief Valves and Post Accident Monitoring Instruments had not been configured in its qualified condition since January 4, 1993. This discovery was made during review of a work package. The work package indicated that screws were missing from the circuit card cages and power supply racks in the Qualified Display Processing System and an engineering evaluation that had been requested had not been performed. The cause of the event is less than adequate work practices in not replacing the screws following maintenance activities. Contributing factors include less than adequate knowledge of seismic fastener requirements and the failure to assess the impact of the missing screws in a timely manner. Corrective actions for this event include replacing the missing screws, inspecting their similar equipment for missing screws, reviewing work documents for their uncompleted engineering evaluations, improving maintenance work practices, training with regard to equipment qualification, and enhancing the process by which deficient conditions are evaluated by engineering.
4981993017 | South Texas 1, South Texas 2 | 05/27/1993 | 07/20/1993 | 9307290167 | <strong>Extension of FWIBV Positioner and Solenoid Equipment Beyond Qualification Life</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1993, Unit 1 was in Mode 5 at 0% power and Unit 2 was defueled in a refueling outage. Plant personnel concluded that, based on a May 21, 1993 determination that the Feedwater Isolation Bypass Valves (FWIBVs) in both units were inoperable since the pneumatic positioners and solenoids had remained in service beyond their qualified life, this event was reportable. STP personnel determined that Technical Specification 3.7.1.7 had been violated during various modes of operation since 1992. The inappropriate extension of the equipment qualification life of the FWIBV positioner and solenoids was the result of incorrectly interpreting design documents. Corrective actions include reviewing other safety-related valves with positioners for similar problems, reviewing other solenoid valves qualified for service in a harsh environment to determine if similar problems could exist, reviewing safety-related components which have been classified as non-safety to determine generic implications, and modifying the pneumatic control scheme of the FWIBV to ensure closure of the valves independent of the positioner upon de-energization of the safety-related solenoid valves. Further evaluation determined that the qualified life of the FWIBV positioners and solenoids had, in fact, not been exceeded and no violation of Technical Specifications occurred.
4981993018 | South Texas 1, South Texas 2 | 07/07/1993 | 08/06/1993 | 9308110126 | <strong>Remote Position Indication Verification Tests on Safety Injection System Accumulator Valves not Performed in Accordance with Technical Specification 4.0.5</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1993, Unit 1 was in Mode 5 at 105 degrees F and 85 psig and Unit 2 was defueled in a refueling outage. It was discovered that Technical Specification 4.0.5 had not been met because the Remote Position indication (RPI) verification test for the Safety Injection (SI) System accumulator vent valves PV-3928, PV-3929, and PV-3930, and accumulator header vent valves HV-899 and HCV-900 had not been performed within the two year period required by Section XI of the ASME Boiler and Pressure Vessel Code. The valves had been added to the Inservice Test (IST) Plans, but permanent test procedures had not been issued for RPI verification. The cause of this event was that changes to the IST Plan were not being reflected in associated documents such as test procedures. Corrective actions for this event include performing RPI verification tests on the affected valves, reviewing the IST Plan and test procedures that implement the IST Plan to ensure that Section XI requirements are satisfied, and conveying standards and expectations to appropriate personnel concerning the implementation of requirements in plant documents.
4981993019 | South Texas 1, South Texas 2 | 07/09/1993 | 08/05/1993 | 9308110073 | <strong>Failure to Meet Technical Specification Surveillance Testing Requirements of the Main Steamline Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1993, Unit 1 was in Mode 5 at 0% power and Unit 2 was defueled in a refueling outage. HL&P personnel determined that a Technical specification requirement was not being met in that the actuation logic surveillance test for the Main Steamline Isolation Valves (MSIV) had not been completely implemented. During a design review of the Solid State Protection System (SSPS) wiring, the System Engineer discovered that the Logic Test for the MSIV Actuation function failed to perform a continuity test through the final output device (Master Relays) as required by the Technical Specification 1.2 definition of a Logic Test. Technical Specification 4.3.2 requires that a monthly surveillance of the Steamline Isolation Actuation Logic and Actuation Relays be performed. The surveillance test previously performed had failed to meet the Technical specification requirements. The cause of this event was an inadequate design of the testing function of the Solid State Protection System with regards to the Main Steamline Isolation Valve. Corrective actions include performing a review of all SSPS design changes related to logic circuitry for proper design.
4981993020 | South Texas 1, South Texas 2 | 08/13/1993 | 09/10/1993 | 9309170206 | <strong>Entry into Technical Specification 3.0.3 Due to The FWIBV Being Determined to Be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1993, Unit 1 was in Mode 3 at 0% power. STP personnel identified that there was back leakage past the "D" Train Feedwater Isolation Bypass Valve (FWIBV). While in Mode 3 for testing of the Steam Driven Auxiliary Feedwater Pump, the Control Room operators noted a decrease in the "D" Steam Generator (S/G) water level, although there was no demand on the S/G. Investigation revealed that FWIBV FV-7145A was 10-15% open. FWIBV FV-7145A was placed in manual control and closed. After FWIBV FV-7145A was closed, S/G "D" level stabilized and conditions returned to normal. The remaining FWIBVs were also placed in manual control and closed. All FWIBVs were subsequently declared inoperable and the plant entered Technical specification 3.0.3. The cause of the unexpected back flow through FWIBV FV-7145A was the result of a design deficiency that manifested itself during an unusual plant configuration. Corrective actions include performing a review to determine if any additional valves are affected and implementing a modification to correct the design deficiency.
4981993021 | South Texas 1 | 09/29/1993 | 10/29/1993 | 9311010170 | <strong>Regarding Failure to Provide Backup Overcurrent Protection for Penetration Conductors</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1993, Units 1 and 2 were defueled. During maintenance activities on May 19, 1993, a load center contained a terminal block with a broken barrier between adjacent points. The wiring was restored as originally found and verified against vendor connection diagram. The "as left" configuration did not agree with the design document. The wiring arrangement was checked against plant drawings when revealed that the penetration protection backup fuse (15A) was not wired in the circuit as required. The subject circuit provides power to the space heaters for the Train "B" RHR pump motor. The space heater was verified as being energized as required when the motor was not running. However, the backup protection device was not in the circuit designed as required by the UFSAR. The apparent cause of this event is believed to be improper rewiring of the circuits. The design change was correctly installed in 1985. Since then, no other design changes have been made that would affect this portion of the circuitry. Corrective actions include reworking the wiring for the RHR pump motor space heater circuits prior to startup of Unit 1.
4981993022 | South Texas 1, South Texas 2 | 04/14/1993 | 01/18/1994 | 9401260035 | <strong>Deviation from the Method for the Contamination Sampling of the Fuel Oil System</strong><br /><i>Abstract:&nbsp;</i>This Voluntary LER is being submitted at the NRC staff's request. On April 14, 1993, Unit 1 was in Mode 5 at 0% power and Unit 2 was defueled while in a refueling outage. Plant personnel discovered the sample containers used for sampling the Diesel Generator Fuel Oil Storage Tanks (DGFOST) for particulate contamination monthly surveillances were not prepared in accordance with the Particulate Contaminant in Aviation Turbine Fuels (ASTM-D2276-78) as required by Technical Specification 4.8.1.1.2d. Technical Specification 4.8.1.1.2d requires that the DGFOSTs be sampled in accordance with ASTM-D2276-78 once every 31 days to verify that the total particulate contamination is less than 10 ppm. The preparation method for the sample containers in question used the Standard Practice for Manual Sampling Of Petroleum Products (ASTM-D4057) which is the required method for sampling new fuel oil prior to addition to the DGFOST. Due to the deviation from ASTM-D2276-78, it was concluded that the analytical results could be biased. This deviation was determined to be in the conservatively high direction and as such there was no potential violation of the fuel contamination control requirements. Corrective actions include developing a fuel oil program to sample and analyze fuel oil instead of specific ASTM Methods, and submitting a Technical Specification change to implement the fuel oil program.
4981993023 | South Texas 1 | 12/31/1993 | 01/31/1994 | 9404110002 | <strong>Inadvertent ESF Actuation of Standby Diesel Generator 12 During Testing</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1993, Unit 1 was in Mode 5 at 0% power. At approximately 0206 hours, a non-emergency Engineered Safety Features (ESF) actuation of Standby Diesel Generator (SDG) 12 occurred. Instrumentation & Control (I&C) Technicians were installing test leads to a recorder which would measure the voltage, frequency and the presence of a 125 vdc start signal. The test leads for the voltage and frequency transducers were connected without incident. When the second lead of the 125 vdc pair was connected to the appropriate terminal, the technician noticed an electrical arc. When the connection was made, ESF SDG 12 started. This condition was not recreated during the investigation. The test equipment and diesel circuitry were checked for malfunction and degradation. All were found satisfactory.
4991993001 | South Texas 2 | 01/23/1993 | 04/21/1993 | 9304260188 | <strong>Reactor Trip Due to Failure of a Main Turbine Electro- Hydraulic Control Line</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1993, Unit 2 was in Mode 1 at 100% power. At 2324 hours, Unit 2 automatically tripped from full power due to a turbine trip above the P-9 (50% power) setpoint as the result of a depressurization of the Electro-Hydraulic Control (EHC) supply header. The low EHC System pressure was due to a leak on the low pressure governor valve line of the Steam Generator Feedwater Pump (SGFP) #22. The failure initiated on the outside surface with no defect present. Towards the latter part of the failure, secondary fatigue initiated from the inside as well. Rapid changes in the valve position created excessive movement within the valve and low pressure line. The excessive movement was apparently the result of an exposed wire on the Linear Variable Differential Transformer (LVDT). Corrective actions include replacing the failed EHC line and the LVDT.
4991993002 | South Texas 2 | 01/28/1993 | 02/26/1993 | 9303040022 | <strong>Unplanned ESF Actuation of an ECW Screen Wash Booster Pump</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1993, Unit 2 was in Mode 1 at 65% power. At 2250 hours, Instrumentation and Control (I&C) technicians were performing preventive maintenance activities on the Essential Cooling Water (ECW) system when an unplanned Engineered Safety Features (ESF) actuation of the ECW Screen Wash Booster pump occurred. The cause of this event was that the Preventive Maintenance instructions did not specifically state the correct type equipment to be used for the application. The technician used the wrong type of test equipment for the calibration causing a false signal to be sent. Contributing causes were that the preventive maintenance instruction did not specifically identify parallel process connected ESF actuation equipment and less than adequate labeling of the instrument cabinet. Additionally, the I&C Technicians did not recognize the proper test equipment for the specific application. Corrective actions include revising the preventive maintenance activity to provide a caution that specifies the correct type of test equipment, placing labels on instrument cabinets, discussing this event with I&C personnel, evaluating the need for additional training on Measuring and Testing Equipment and performing a review of other preventive maintenance activities to identify similar problems.
4991993003 | South Texas 2 | 02/03/1993 | 03/05/1993 | 9303090296 | <strong>Technical Specification 3.0.3 Entry Due to the Inoperability of the DRPI System</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1993, at 1000 hours, Unit 2 was in Mode 1 at 100% power. The Unit entered Technical Specification 3.0.3 due to the loss of the Digital On February 3, 1993, at 1000 hours, Unit 2 was in Mode 1 at 100% power. The Unit entered Technical Specification 3.0.3 due to the loss of the Digital Rod Position Indication (DRPI) System. This incident occurred during the performance of the Unit Vent Particulate and Effluent Monitor Digital Channel Operational Test (DCOT) for radiation monitor RT-8010A. The distribution panel, DP003, which supplies power to both the RT-8010A monitor and the DRPI System, experienced a degraded voltage condition during the energization of the RT-8010A monitor. The transfer switch, for the normal/alternate power supply to the distribution panel, responding to the degraded voltage condition on the normal supply attempted to transfer to the alternate supply. The transfer switch malfunctioned and latched mid-way through the transfer resulting in a loss of power to the distribution panel and its subsequent loads. Troubleshooting activities have been performed on the auto transfer switch to determine the cause of the malfunction. As a result of the findings, HL&P will implement a design change to remove the load associated with monitor RT-8010A from distribution panel DP003, create Preventive Maintenance activities to test/inspect these and similar auto transfer switches, and an investigation will be performed to identify if a similar condition exists in Unit 1.
4991993004 | South Texas 2 | 02/03/1993 | 03/05/1993 | 9303090320 | <strong>Reactor Trip Due to Low Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1993, Unit 2 was in Mode 1 at 100% power. At 1448 hours, Unit 2 experienced an automatic reactor trip due to low Steam Generator water level. The low Steam Generator water level was caused by a loss of Steam-driven Feedwater pump #21 in conjunction with a failure of the Startup Feedwater Pump due to low oil pressure. The cause of this event was ineffective action to correct previous failures of the Startup Feedwater pumps and Steam Driven Feedwater pumps. Corrective actions include troubleshooting and repairing the Startup Feedwater pump and Steam Driven Feedwater pump. A walkdown of both units' Feedwater Isolation Bypass Valves was conducted to identify similar problems with valve positioners. Modifications to improve the reliability of the Steam Driven Feedwater pumps and Startup Feedwater pumps will be implemented. \
4991993005 | South Texas 2 | 02/14/1993 | 05/14/1993 | 9305210207 | <strong>Control Room Unmanned by a Senior Licensed Operator</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1993, at 0433 hours, Unit 2 was in Mode 4 at 0% power. The on-duty Shift Supervisor designated the Unit Supervisor as the individual responsible for the control room command function and exited the control room. The Unit Supervisor exited the control room to observe a surveillance, leaving the control room unmanned by a Senior Operator for a period of 41 seconds. This action violated Technical Specification requirement 6.2.2.b, which requires at least one Senior Operator present in the control room while the unit is in Mode 1, 2, 3, or 4. The cause of this event was inappropriate action by the Unit Supervisor. Corrective actions for this event include a Human Performance Review, verbal discussions on the command and control function requirements by Management, and procedures will be revised to add a required discussion concerning command and control function for License Activation Certification. This event will also be included in Licensed Operator Requalification Training.
4991993006 | South Texas 2 | 02/17/1993 | 06/01/1994 | 9409290253 | <strong>Technical Specification Violation due to Train A Cold Leg Injection Motor Operated Valve Being Inoperable for Greater Than 72 Hours</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 17, 1993, Unit 2 was in Mode 4 at 0% power. After a recent Motor Operated Valve failure, review of completed work packages on a Low Head Safety Injection/Residual Heat Removal cold leg injection valve (MOV-0031A) was conducted. It was determined that on April 9, 1989, MOV- 0031A could not be operated from the control room handswitch and was not repaired until November 8, 1990 (a period of 19 months). This valve is required to be capable of being closed hours after a Loss of Coolant Accident to establish hot leg recirculation. The cause for this Technical Specification violation was a misinterpretation of the requirement for hot leg recirculation capability. Corrective actions include discussing this event in Licensed Operator Requalification Training and performing a review of work packages on key systems to identify any additional cases of improper operability determinations. Additionally, Houston Lighting & Power evaluated the adequacy of the programmatic controls regarding operability determinations and made enhancements. LER-94\L93006R1.U2
4991993007 | South Texas 2 | 03/10/1993 | 04/07/1993 | 9304130226 | <strong>Technical Specification Violation due to the Control Room Envelope HVAC not in Required Mode of Operation</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1993, Unit 2 was in Mode 6 during a refueling outage. At 1312 hours, it was determined that the Control Room Envelope (CRE) Heating, Ventilating; and Air Conditioning (HVAC) system was not in the mode of operation required per Technical Specification 3.7.7a and 3.3.3.7b. The cause of this event was the implementation and use of a computer program for the control of safety related equipment without the formality of procedural reviews and approvals. The contributing causes of this event were the de-sensitization of the Control Room supervision to multiple operability requirements due to the control of pertinent shift documents being maintained outside the controls area and the CRE HVAC system being in the recirculation mode of operation masking the necessity to be in the filtered recirculation mode of operation. Corrective actions include suspending the use of the computer-generated Operability Tracking Log index pending correction of the computer program, maintaining a manually updated index for the Operability Tracking Log within the controls area, and providing training reinforcing the different modes of operation for the CRE HVAC system including the Technical Specification requirements for each mode.
4991993008 | South Texas 2 | 05/05/1993 | 12/15/1993 | 9312220353 | <strong>Failure to Maintain Environmental Qualification of a Residual Heat Removal Motor Operated Valve</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1993, at 1400 hours, Unit 2 was defueled at 0% power. It was discovered that a Residual Heat Removal Pump suction Motor Operated Valve (MOV) had not been environmentally qualified since November 29, 1990 because replacement of a 'T' drain was not completed. This discovery was made during a review of work documents prompted by the NRC Diagnostic Evaluation Team. The apparent cause of the event is lack of knowledge regarding the requirements to maintain the environmental qualification of harsh environment MOVs. Corrective actions for this event include replacing the 'T' drain, walking down other MOVs, reviewing open work documents for similar issues, screening new Service Requests for similar issues, and training on equipment qualification requirements.
4991993009 | South Texas 2 | 04/26/1993 | 05/25/1993 | 9306030078 | <strong>Technical Specification Violation due to the Use of Inappropriate Reference Value Data for a RHR Pump Inservice Test</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1993, Unit 2 was in a refueling outage in No Mode. Plant personnel completed a reportability review which determined that Technical Specification 3.5.6 and 4.0.5 were violated due to the use of inappropriate reference values for differential pressure during surveillance testing of the Residual Heat Removal (RHR) pump 2A. The cause of this event was less than adequate attention to detail by the preparer and the subsequent reviewers during preparation, review and approval of a field change to a procedure. A revision to the surveillance procedure incorporated the inappropriate reference values for differential pressure. Corrective actions include revising the surveillance procedure to incorporate the appropriate reference values and providing lessons learned from this event to appropriate personnel. Additionally, a review of a sample of other completed field changes will be performed to ensure this is an isolated incident.
4991993010 | South Texas 2 | 05/26/1993 | 06/25/1993 | 9307010182 | <strong>Failure of an Essential Cooling Water Traveling Screen Coupling</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1993, Unit 2 was defueled during a refueling outage. During a post-maintenance run of the Essential Cooling Water (ECW) 2A traveling screen, Maintenance personnel discovered that the screen drive coupling was damaged. The coupling transfers motive force from the drive motor to the traveling screen speed reducer while allowing for equipment misalignment. coupling inspections of Unit 2 Trains B and C indicated similar coupling damage, with half of the couplings exhibiting cracks while the other half appeared normal. The failure of the couplings affected all three Unit 2 trains of ECW, thus rendering all Standby Diesel Generators (SDG) technically inoperable (but still functional). Unit 2 declared an Unusual Event. Unit 1 ECW Trains A, B and C couplings were satisfactory. The cause of this event was failure to inspect/replace the traveling screen couplings. Information regarding nominal expected lifetime was not in the vendor manual. Corrective actions include developing preventive maintenance activities to inspect/replace the couplings, incorporating vendor information detailing expected life of the couplings into the vendor manual and performing a review to identify other mild environment Equipment Qualification Program Preventive Maintenance activities that may have been cancelled based on incomplete information.
4991993011 | South Texas 2 | 04/01/1993 | 02/14/1995 | 9502220153 | <strong>Pressurizer Safety Valve and Main Steam Safety Valve Setpoints Outside Required Tolerance</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1993, Unit 2 was defueled during a refueling outage. After being reset at the second refueling outage for Unit 2 (2RE02) to the specified value of 2485 psig +/- 1.0%, the setpoint for the Unit 2 Pressurizer Safety Valves were found to range from 3.8% below to 2.1% above the required setpoint during the third refueling outage (2RE03). This is a deviation from the +/- 1.0% Technical Specification requirement. The Unit 2 Pressurizer Safety Valves (PSV-3450, 3451 & 3452) had been sent to Wyle Laboratories for setpoint verification testing. Pressurizer Safety Valve setpoint drift is an industry-wide problem which has been known for some time. The Westinghouse Owners Group has addressed this generic issue in WCAP-12910, which makes specific recommendations relative to Pressurizer Safety Valve setpoint verification testing. Corrective actions include modifying the test procedure to test the Pressurizer Safety Valve lift setpoint on saturated steam as recommended by WCAP-12910. <br /><br /> In addition to the above, additional Pressurizer Safety Valve out of tolerance conditions were discovered which were not previously identified. Several Main Steam Safety Valve setpoints were also found to be outside the required tolerances.
4991993012 | South Texas 2 | 06/14/1993 | 07/29/1993 | 9308030143 | <strong>Loss of Spent Fuel Cooling for Approximately 13 Hours</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1993, Unit 2 was in a refueling outage with the core unloaded and stored in the spent fuel pool. At 1420 hours, the 1E distribution panel DP001 was transferred from its main to alternate power supply to support maintenance activities. This transfer required DP001 to be momentarily de-energized. When DP001 was re-energized, the Component Cooling Water (CCW) common header isolation relay for low CCW surge tank level responded before the CCW surge tank level switch. This resulted in a signal that isolated CCW to the spent fuel pool heat exchangers. Due to insufficient control board awareness by operations and the failure of an operator to notice changes in CCW flow induced noise and vibration during local operator rounds, this condition was not discovered until 0315 hours on June 14, 1993. Fuel pool temperature increased from 99 degrees F to 118 degrees F. Once discovered, operators restored cooling to the spent fuel pool. Efforts are being initiated to enhance operator control board awareness and awareness during normal operator rounds. HL&P is evaluating a design change to install an annunciator for loss of fuel pool cooling. Based on the fuel pool temperature remaining below the FSAR assumed maximum and other independent methods for fuel pool cooling being available, there were no adverse safety consequences from this event.
4991993013 | South Texas 2 | 07/19/1993 | 05/27/1994 | 9406060148 | <strong>Inadvertent ESF Actuation due to a Component Cooling Water Pump Start During a Maintenance Work Activity</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1993, at 2044 hours, Unit 2 was defueled in a refueling outage. The 'B' train (2B) Component Cooling Water (CCW) pump received an automatic actuation from the non-nuclear supply header low pressure signal. The low header pressure was caused when a Motor Operated Valve (MOV-0235) was opened to equalize pressure across the valve. Due to a downstream valve, MOV-0236 being closed and indications that the piping in between the valves had been filled, it was assumed that a low header pressure condition would not occur. When the valve was opened, the CCW pump auto started and the operator stationed at the valve reported flow noises. The causes of this event were attributed to less than adequate plant impact review by the Unit Supervisor, seat leakage past MOV-0236 and untimely implementation of a recommended action from previous events. Corrective actions include placing a time delay in the CCW pump automatic starting circuit and revising the guidance for control of the CCW pump mode selector switch.
4991993014 | South Texas 2 | 08/16/1993 | 09/15/1993 | 9309210226 | <strong>Failure to Fully Meet Technical Specification Testing Requirements of the Containment Hydrogen Monitors</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1993, STP personnel determined that the requirements of a Technical Specification were not fully met on February 21, 1989. Technical Specification 4.3.3.6 for the Containment Hydrogen Concentration requires that a channel check be performed to ensure the operability of the Containment Hydrogen Monitors in modes 1, 2 and 3. This was done via a channel check which was identified as being inadequate for determining the operability of these monitors. In all but one case, the requirements of this Technical Specification were met by the performance of two other surveillance procedures which adequately verified the operation of these channels. The only time that the requirements of this Technical Specification were not met was on February 21, 1989 when Unit 2 was initially taken to Mode 3. The cause of this event was an inadequate surveillance test procedure. Corrective actions include performing a review to determine if any other Qualified Display Parameter System (QDPS) Technical Specification channel checks were incorrectly performed and revising the Analog Channel Operational Test (ACOT) surveillance to ensure performance of the surveillance prior to Mode 3, if not current.
4991993015 | South Texas 2 | 10/19/1993 | 11/18/1993 | 9312010222 | <strong>Inadvertent Start of Standby Diesel Generator 22 due to Spurious Operation of a Transistor</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1993, Unit 2 was defueled. While Standby Diesel Generator (SDG) 21 was operating during a test run, SDG 22 auto-started while it was in auto/standby mode. It was verified that no one was in e SDG room at the time of the start. The SDG was placed in cooldown and the sequencer reset. The SDG completed a full cooldown cycle and was placed in 'Pull to Stop'. The cause of the inadvertent start of SDG 22 was the spurious failure of a transistor. Failure of varistors in the control circuitry caused voltage spikes which degraded the transistor's operational characteristics and resulted in spurious transistor operation. Varistors are electrical components which provide variable resistance depending on the applied electrical potential. Varistors are used in the SDG Control Cabinets to disperse stored energy in the control circuitry relays and solenoids. Because of the degraded varistors, the stored magnetic field energy in the relay/solenoid coils is not dissipated which causes voltage spikes in the control power. This voltage noise could degrade other electrical components including transistors. Corrective actions include bringing a vendor representative onsite to conduct a review of the SDG control panels and the recent varistor problem, incorporating varistor performance characteristics into the SDG vendor manual, and performing an evaluation to determine the failure mechanism.
4991993016 | South Texas 2 | 10/31/1993 | 11/29/1993 | 9312080103 | <strong>Regarding an Inadvertent Engineered Safety Feature Actuation and Component Cooling Water Pump Start due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1993 at 1331, Unit 2 was defueled. The 'A' train (2A) Component Cooling Water (CCW) pump received a start signal when the Component Cooling Water/Essential Cooling Water (CCW/ECW) Train 'A' Mode Selector Switch was inadvertently switched to the 'Run' position. The cause of this event was inadequate attention to detail and failure to properly implement station self-verification techniques. Corrective action involved constructive discipline of the operator. Personnel performance standards expected by station management and understood by watchstanding personnel were clearly not met during this incident.
5281993001 | Palo Verde 1 | 01/30/1993 | 02/24/1993 | 9303020339 | <strong>Turbine Trip/Reactor Trip on Moisture Separator Reheater High Level</strong><br /><i>Abstract:&nbsp;</i>At approximately 0603 MST on January 30, 1993, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 96 percent power when a Unit 1 Main Turbine trip occurred. Control Room operators initiated a manual reactor trip after receiving high pressurizer pressure pretrip alarms in anticipation of the Reactor Protection System high pressurizer pressure trip. <br /><br /> At approximately 0615 MST on January 30, 1993, Control Room operators stabilized the plant in Mode 3 (HOT STANDBY). The Shift Supervisor classified the event as an uncomplicated reactor trip in accordance with Emergency Plan Implementing Procedures. No other safety system responses occurred and none were required. <br /><br /> APS Maintenance personnel have determined that the cause of the Main Turbine trip was due to the failure of Moisture Separator Reheater D Drain Tank high level controller. This resulted in a high level condition in Moisture Separator Reheater D which actuated the Main Turbine's electrical trip system. <br /><br /> No previous similar events have been reported pursuant to 10CFR50.73.
5281993002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 02/10/1993 | 03/11/1993 | 9303190189 | <strong>Loss of Train "B" Diesel Generator Components Due to a Control Room Fire</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1993, at approximately 1300 MST, Palo Verde Units 1, 2, and 3 were in Mode 1 (POWER OPERATION) when APS Engineering personnel (utility, non-licensed) determined that a design basis Appendix R fire in the Control Room (Fire Zone 17) concurrent with a loss of offsite power, could adversely affect the ability to achieve and maintain safe shutdown. A Control Room fire-induced fault in Train "B" Diesel Generator control circuits could cause the loss of control power to the Train "B" Diesel Generator Output Breaker and Diesel Generator Room Essential Exhaust Fan Breaker and loss of power to the Diesel Generator Control Panels. It was determined that the current post-fire procedure did not provide sufficient guidance to mitigate the consequences of the identified condition and therefore, a single fire could adversely affect the ability to achieve and maintain safe shutdown. <br /><br /> The cause of this condition was that the original PVNGS 10CFR50, Appendix R analysis process did not reveal a design deficiency in the electrical design of the isolation transfer switch control circuitry, for the Train "B" Diesel Generator Output Breaker, the Diesel Generator Room Essential Exhaust Fan, and the Diesel Generator Control Panels.<br /><br /> Four previous similar events were prepared and submitted pursuant to Technical Specification 6.9.3 and 10CFR50.73 in LERs 528/91-008-01, 528/91-011-00, 528/92-010-00, and 528/92-015-00.
5281993003 | Palo Verde 1 | 02/13/1993 | 05/29/1993 | 9306080242 | <strong>Loss of Power to Train A Class 1E 4.16 Kv Bus</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1993, at approximately 0614 MST Palo Verde Unit 1 was in Mode 1 (POWER OPERATIONS), operating at approximately 100 percent power when the normal supply breaker to the Unit 1, non-Class 1E 13.8 kV, Intermediate Bus opened on overcurrent. This resulted in a loss of power to the Unit 1 Train A Class 1E 4.16 kV bus. The Loss Of Power Engineered Safety Feature (ESF) signal automatically load shed the Class 1E 4.16 kV bus and started the Train A Emergency Diesel Generator. All equipment functioned as designed, and no other ESF signals were actuated or required. Unit 1 continued to operate normally at 100 percent power. Units 2 and 3 were not affected by this event. <br /><br /> An initial inspection of the switchgear indicated that the normal supply breaker to the Intermediate Bus tripped on overcurrent. An Equipment Root Cause of Failure Analysis determined that damage on the C phase, line side to bus interface, of the normal supply breaker for the switchyard relay building was caused by an overcurrent condition induced by insulation breakdown on the breaker bushings. The damaged line side to bus interface was removed from the switchyard control power switchgear and the Intermediate Bus was re-energized from its alternate supply. The Emergency Diesel Generator was shutdown at approximately 1617 MST on February 13, 1993.<br /><br /> No similar events have been previously reported pursuant to 10CFR50.73.
5281993004 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/20/1993 | 09/29/1993 | 9310050105 | <strong>ASME Section XI Testing of Charging Pumps not in Compliance with Code Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1993, at approximately 1340 MST, Units 1 and 3 were in Mode 1 (POWER OPERATION), operating at approximately 100 percent power, and Unit 2 was in Mode 6 (REFUELING) with the Reactor Coolant System at approximately 95 degrees Fahrenheit and at atmospheric pressure, when APS Engineering personnel determined that Technical Specification (TS) Surveillance Requirement (SR) 4.0.5, for performing the inservice testing of the ASME Code Class 2 charging pumps, had not been performed in accordance with the ASME Boiler and Pressure Vessel Code, Section XI. TS SR 4.1.2.3 and 4.1.2.4 are satisfied by ASME Section XI testing in accordance with SR 4.0.5. Subsequent testing in accordance with Paragraph IWP-4120 indicated that the Unit 1 and Unit 3 charging pumps have been and continue to be capable of performing their intended safety function. Satisfactory testing of the Unit 2 charging pumps was performed during the recent 2R4 refueling outage. <br /><br /> APS Engineering personnel have performed an initial review of the instrumentation used to perform ASME Section XI testing. The results of this investigation identified 22 instances in which instruments were either not within the accuracy or full-scale range requirements as specified by Section XI. The additional 22 instances identified during the investigation have been reviewed and it was determined that the effected equipment was not operated in a condition that seriously degraded the plant or principal safety barriers. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281993005 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 07/28/1992 | 07/15/1993 | 9307270179 | <strong>Loss of Redundant Trains of Safe Shutdown Equipment Due to a Single Fire</strong><br /><i>Abstract:&nbsp;</i>At approximately 0745 MST, on July 28, 1992, as a result of the 10CFR50 Appendix R reconstitution project, it was identified that redundant trains of safe shutdown (SSD) equipment could be rendered inoperable by a single fire. This condition was limited to equipment powered from the SSD 125 volt DC ungrounded Class IE power supplies. The initial evaluation which was completed on October 22, 1992, identified 200 pieces of SSD equipment that may be impacted by the condition. Compensatory measures (fire watches) were established in all affected areas/fire zones in the power block. <br /><br /> On June 22, 1993, a final evaluation was completed that identified that 8 pieces of the previously identified equipment would require a design change to provide the necessary electrical protection. Plant Change Request (PCR) 93-13-ZZ-001 was approved by the Plant Modification Committee on June 29, 1993, The implementation of the modification has been scheduled in accordance with PVNGS Long Range Planning and are currently planned for refueling outages 1R5, 2R6, and 3R5. <br /><br /> Previous similar events were reported pursuant to TS 6.9.3 in LERs 528/91-008-01, 528/91-011-00, 528/92-010-00, and 528/92-015-00.
5281993006 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/05/1993 | 06/18/1993 | 9307010044 | <strong>Shutdown Cooling Isolation Valves Thermal Overload Protection not Bypassed</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1993, at approximately 1600 MST, Palo Verde Units 1 and 3 were in MODE 1 (POWER OPERATION) operating at approximately 100 percent power and Palo Verde Unit 2 was in Mode 6 (REFUELING) and in the process of reloading the core when it was determined that Units 1, 2, and 3 were in a condition prohibited by Technical Specifications (TS). TS Limiting Condition for Operation (LCO) 3.8.4.2, requires that thermal overload protection bypass be provided on the Shutdown Cooling suction isolation valves so the valves will not be prevented from performing their function under accident conditions. Then at approximately 1640 MST, APS Engineering personnel identified that the original design of the valves' motor control circuits may not meet design requirements for thermal overload protection bypass. The NRC Operations Center was notified that PVNGS Units 1, 2 and 3 were in a condition outside their design basis at approximately 1725 MST on May 5, 1993. <br /><br /> Bypassing of the thermal overload protection on the Units 1 and 3 valves was completed at approximately 2245 MST on May 5, 1993. Unit 2 was refueling and had one loop of Shutdown Cooling in service when the conditions were discovered. Based on Technical Specification Interpretations, bypassing of the thermal overloads was not immediately required. Bypassing the thermal overload protection on the Unit 2 valves was completed on May 25, 1993. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281993007 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/30/1993 | 07/28/1993 | 9308060303 | <strong>Snubber Testing not in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1993, at approximately 1330 MST, APS Management and the NRC discussed APS' interpretation of Technical Specification 4.7.9.e, for snubber testing. APS concluded that it had incorrectly interpreted the Technical Specification. Additionally, APS had not informed the NRC Regional Administrator that the surveillance requirement would be implemented differently than previously identified. <br /><br /> Palo Verde Units 1, 2, and 3 entered the ACTION for Limiting Condition for Operation 3.7.9, at approximately 1330 MST on May 12, 1993, and a Notice of Enforcement Discretion was requested. At approximately 1400 MST on May 14, 1993, APS was notified of the Commission's intent to exercise discretion in enforcing compliance with the ACTION statement of TS 3.7.9, until the NRC takes action on a request for a license amendment. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281993008 | Palo Verde 1 | 02/24/1993 | 07/29/1993 | 9308100004 | <strong>Gaseous Radwaste System Oxygen Monitor out of service for 18 days</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1993, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a PVNGS Incident Investigation evaluation determined that one of the oxygen monitors for the gaseous radwaste system (GRS) explosive gas monitoring system had been inoperable for 18 days. The evaluation determined that one of the GRS explosive gas monitoring system oxygen monitor's microprocessor had 'locked up' on February 7, 1993 and the condition had remained undetected until February 24, 1993 when a Chemistry technician performing the daily channel check noticed that the monitor was not updating the display field. Upon discovery, the Chemistry technician placed the backup oxygen monitor in service in order to comply with the appropriate Technical Specifications (TS) Limiting Condition for Operation (LCO). TS LCO 3.3.3.8 requires that at a minimum two explosive gas monitoring instrumentation channels shall be OPERABLE. A follow up review of the event determined that the TS LCO 3.3.3.8 ACTION to perform daily grab samples, with less than the minimum number of channels OPERABLE, had not been completed. Therefore, from February 7, 1993 to February 24, 1993, Unit 1 was operating in a condition prohibited by TS. <br /><br /> The cause of the oxygen monitor's microprocessor lock-up was determined to be a random component failure. As corrective action, the chemistry technicians were instructed to ensure that the GRS explosive gas monitoring system is updating the display field during the performance of the daily channel check. There have been no previous similar events reported pursuant to 10CFR50.73.
5281993009 | Palo Verde 1 | 10/22/1993 | 03/30/1994 | 9404120019 | <strong>MSSV and PSV Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1993, while Unit 1 was in Mode 6 (REFUELING) with the Reactor Coolant System at approximately 96 degrees Fahrenheit and at atmospheric pressure, an Arizona Public Service Company (APS) engineering evaluation of ASME Code surveillance testing results for Unit 1, Cycle 4 determined that 18 of the 20 Main Steam Safety Valves (MSSV) and 4 of the 4 Pressurizer Safety Valves (PSV) as-found relief settings were out of the tolerance limits specified in Technical Specifications (TS) 3.7.1.1 and 3.4.2.2. The testing and adjustments were performed during the period of August 17, 1993 through October 21, 1993.<br /><br /> The MSSVs were disassembled, inspected, reworked (as required), reassembled, and retested. The MSSVs and PSVs lift setpoints were adjusted to within the TS limits. APS is continuing its efforts to enhance MSSV setpoint repeatability to within the TS required plus or minus 1 percent tolerance. This effort is part of an Engineering Issues Plan with a goal of reducing the number of as-found tests outside the TS tolerance. <br /><br /> Previous events were reported in LERs 528/88-014-01, 528/89-007-02, 528/89-010-00, 529/89-002-00, 529/89-007-00, 529/90-004-01, 529/91-005-01, 530/91-001-01, 528/92-004-01, and 530/92-005-00, and 529/93-002-01.
5281993010 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 11/05/1993 | 01/26/1994 | 9402030172 | <strong>Inoperable Motor-operated Valves in Multiple Systems due to Various Deficiencies Found During Generic Letter 89-10 Testing</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1993, at approximately 1200 MST, Palo Verde Unit 1 was in Mode 5 (COLD SHUTDOWN), Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) operating at approximately 85 percent power, and Palo Verde Unit 3 was in Mode 3 (HOT STANDBY) at normal operating temperature and pressure when, following data analysis of testing performed in accordance with the recommendations of Generic Letter (GL) 89-10, "Safety Related Motor-Operated Valve Testing and Surveillance," APS Engineering personnel determined that, in the past, the capability of a number of motor-operated valves (MOVs) to perform their intended safety function under design basis conditions was questionable. Therefore, the MOVs and/or their associated safety systems may have been inoperable at certain times in the past and applicable Technical Specifications Limiting Condition for Operation ACTION statements may not have been met. <br /><br /> The MOVs did not meet the new performance criteria established in accordance with GL 89-10 recommendations (i.e., the as-found MOV switch settings were non-conservative compared to those established by the PVNGS MOV Program). The MOVs had been set up and tested under pre-existing testing programs. Following identification of the MOV deficiencies, the MOV switch settings were adjusted and verified to be in full compliance with the provisions of the current PVNGS MOV Program prior to return to service. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.<br /><br /> [NOTE: The entire LER has been revised]
5281993011 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 01/14/1993 | 06/17/1996 | 9606250302 | <strong>Potential Safety-Related Equipment Problems Due to Upgraded Grid Voltage</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1992, APS Engineering personnel identified that preliminary auxiliary power system calculations indicated that with the switchyard voltage at its design basis minimum of 95 percent and with the startup transformer (SUT) secondary winding fully loaded, downstream voltages could be less than the Class 1E 4.16 kV bus undervoltage (UV) relay setpoints. This scenario would result in shedding of Class 1E 4.16 kV loads from preferred power and automatically starting and sequentially loading the emergency diesel generators (EDG). As an immediate corrective action, switchyard voltages were administratively maintained between 100 to 102.5 percent. Additional preliminary analysis completed on January 14, 1993 indicated that it may be possible to have substandard voltages on the Class 1E 480V power system, with the switchyard voltage between 95 and 100 percent and with the SUT secondary winding fully loaded, without actuation of the Class 1E 4.16 kV bus UV relays nor load shed and EDG start. On December 23, 1993, a postulated UV scenario was documented in which Class 1E equipment could be subjected to double sequencing, That is, following a unit trip and a safety injection actuation signal, with the switchyard voltage less than 99.5 percent, the SUT secondary windings fully loaded, and a successful fast bus transfer, the UV relays would drop out during load sequencing on offsite power and may not reset, resulting in a load shed, the closing of the EDG breakers, and resequencing of loads on to the EDG. <br /><br /> NOTE: Scenarios 3 and 4 were added to supplement 2 to LER 528/93-011.
5291993001 | Palo Verde 2 | 03/14/1993 | 08/14/1993 | 9308310239 | <strong>Manual Reactor Trip Following a Steam Generator Tube Rupture</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1993, at approximately 0434 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 98 percent power when a steam generator tube ruptured in Steam Generator 2. At approximately 0447 MST, the reactor was manually tripped due to low pressurizer level and pressure. Approximately 22 seconds later, valid actuations of the Safety Injection Actuation System (SIAS) and the Containment Isolation Actuation System (CIAS) occurred due to low pressurizer pressure. Pressurizer level was restored and a controlled cooldown and depressurization of the Reactor Coolant System (RCS) was conducted in accordance with approved procedures. A steam generator tube rupture in Steam Generator 2 was diagnosed, and the steam generator was successfully isolated. <br /><br /> This event was investigated in accordance with the PVNGS Incident Investigation Program. The rupture of the steam generator tube was due to intergranular attack/intergranular stress corrosion cracking (IGA/IGSCC) which occurred as a result of tube-to-tube crevice formation. The cause of the SIAS and CIAS was the loss of RCS inventory and the contraction of the RCS upon reactor trip. Pursuant to Technical Specifications 3.5.2, ACTION b, this LER also provides the Special Report required for an Emergency Core Cooling System actuation. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291993002 | Palo Verde 2 | 05/18/1993 | 12/21/1993 | 9401030312 | <strong>MSSV and PSV Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1993, while Unit 2 was in Mode 6 (REFUELING) with the Reactor Coolant System at approximately 96 degrees Fahrenheit and at atmospheric pressure, an Arizona Public Service engineering evaluation of ASME Code surveillance testing results determined that 15 of the 20 Main Steam Safety Valves (MSSV) and 4 of the 4 Pressurizer Safety Valves (PSV) as-found relief settings were out of the tolerance limits specified in Technical Specifications (TS) 3.7.1.1 and 3.4.2.2. As immediate corrective action, the MSSVs and the PSVs were disassembled, inspected, reworked (as required), reassembled, retested, and their lift setpoints were adjusted to within the TS limits. <br /><br /> APS is continuing its efforts to enhance MSSV setpoint repeatability to within the TS required +/- 1 percent tolerance. This effort is part of an Engineering Issues Plan with the goal of significantly reducing the number of as-found tests outside the TS tolerance. <br /><br /> Previous similar events were reported in MSSV and PSV LERs 528/88-014-01, 528/89-007-02, 528/89-010-00, 529/89-002-00, 529/89-007-00, 529/90-004-01, 529/91-005-01, 530/91-001-01, 528/92-004-01, and 530/92-005-00.
5291993003 | Palo Verde 2 | 08/14/1993 | 09/13/1993 | 9309210258 | <strong>Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1993, at approximately 0415 MST, Palo Verde Unit 2 was in Mode 3 (HOT STANDBY), when Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 following the determination that the TS LCO 3.1.2.2 Operating Reactivity Control Systems Flow Paths ACTION statement could not be met. TS LCO 3.1.2.2 requires that at least two of three specified boron injection flow paths that are gravity-fed to a charging pump and then to the reactor coolant system (RCS) be OPERABLE. Control Room personnel recognized that TS Surveillance Requirement (SR) 4.1.2.2.1.b could not be met because the reactor coolant pump (RCP) seal controlled bleedoff flow indication used to perform the surveillance testing was not functioning properly. Therefore, Control Room personnel could not calculate the boron injection flow to the RCS as necessary to satisfy TS SR 4.1.2.2.1.b and to demonstrate that the three boron injection flow paths required by TS LCO 3.1.2.2 were OPERABLE. At approximately 0900 MST on August 14, 1993, the unit entered Mode 4 (HOT SHUTDOWN). At approximately 1000 MST, Control Room personnel exited TS LCO 3.0.3 (i.e., no longer at normal operating pressure and the bleedoff flow indication was restored).<br /><br /> The cause of the RCP seal controlled bleedoff flow indication not functioning properly is due to manufacturing and/or installation error. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291993004 | Palo Verde 2 | 11/01/1993 | 11/25/1993 | 9312090060 | <strong>Reactor Trip and Auxiliary Feedwater Actuation Signals Following Degraded Voltage on non-Class IE 4160V Bus</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1993, at approximately 0807 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at a approximately 85 percent steady-state power, when a reactor power cutback to approximately 45 percent power occurred following the loss of a main feedwater pump (MFWP), and at approximately 0808 MST, a reactor trip occurred on low steam generator water level. The reactor trip was initiated by a non-Class 1E 4.16 kV switchgear bus load shed which caused the loss of two condensate pumps and a heater drain pump. Both MFWPs tripped on low suction pressure. Immediately following the reactor trip, the SG-2 water level reached the RPS trip setpoint for low steam generator water level, followed by the Engineered Safety Feature Actuation System (ESFAS) actuation of both Auxiliary Feedwater Actuation Systems (AFAS-1 and AFAS-2) on low-low steam generator water level for both steam generators. Per design, the AFAS signals automatically started the Train A and Train B Emergency Diesel Generators. The steam generator water levels were restored using auxiliary feedwater. By approximately 0830 MST on November 1, 1993, the plant was stabilized in Mode 3 (HOT STANDBY) and the event was diagnosed as an uncomplicated reactor trip. No other safety system responses occurred and none were required. All plant equipment responded as designed. <br /><br /> The NBN-S01 load shed was caused by an insufficient electrical contact in a potential transformer (PT). The PT was adjusted and returned to service.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291993005 | Palo Verde 2 | 11/23/1993 | 01/27/1994 | 9402030186 | <strong>Failure to Demonstrate OPERABILITY of A.C. Offsite Sources Within One Hour</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1993, at approximately 0630 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 85 percent power when Control Room personnel identified that Surveillance Requirement (SR), 4.8.1.1.1.a had not been completed within the required time (1 hour). This SR verifies the correct breaker alignment of the offsite transmission network and the onsite Class 1E distribution system. <br /><br /> Diesel Generator B had been removed from service at approximately 0443 MST on November 23, 1993. The required surveillance was completed at approximately 0700 MST with no problems noted.<br /><br /> There have been three previous similar events reported in LERs 529/89-004-00, 529/88-003-00, and 528/86-001-00.
5301993001 | Palo Verde 3 | 02/04/1993 | 03/04/1993 | 9303150145 | <strong>Reactor Trip Due to Loss of Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1993, at approximately 1523 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred due to Steam Generator Number 2 (SG-2) water level reaching the Reactor Protection System trip setpoint for low steam generator water level following the loss of Main Feedwater Pump A. Immediately following the reactor trip, a low steam generator water level alarm annunciated for SG-1, followed by the Engineered Safety Feature Actuation System (ESFAS) actuation of both Auxiliary Feedwater Actuation Systems (AFAS-1 and AFAS-2) on low-low steam generator water level for both steam generators. The Steam Bypass Control System responded as designed to control the secondary system pressure. The injection of auxiliary feedwater to the steam generators, combined with the quick-opening of the steam bypass control valves (SBCVs), caused reactor coolant temperature to decrease, which resulted in a primary system pressure decrease below the low pressurizer pressure setpoint of 1837 pounds per square inch absolute (psia). Valid ESFAS actuations of the Safety Injection Actuation System (SIAS) and the Containment Isolation Actuation System (CIAS) occurred due to low pressurizer pressure. The event was diagnosed as an uncomplicated reactor trip. By approximately 1559 MST on February 4, 1993, the plant was stabilized in Mode 3 (HOT STANDBY).<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73. This LER also serves as a Special Report prepared and submitted pursuant to Technical Specification (TS) 3.5.2 ACTION b and TS 6.9.2.
5301993002 | Palo Verde 3 | 04/02/1993 | 07/20/1993 | 9308040039 | <strong>Spurious Opening of Steam Bypass Control Valves Caused Reactor Power Excursion</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1993, at approximately 1501 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when a Steam Bypass Control System (SBCS) perturbation occurred in Unit 3 during the initiation of a quick open retest of steam bypass control valve (SBCV) 1005 following SBCS design modification installations. <br /><br /> Control Room indication was that SBCVs 1001 through 1006 each received a 100 percent modulation demand and five of the eight SBCVs modulated open (SBCV 1005 was isolated for the quick open retest and SBCVs 1007 and 1008 were not required to open). The resultant excess steam flow caused reactor power to increase. Control Room personnel observed steam generator pressure and level fluctuations and reactor coolant system pressure fluctuations. Per the retest contingency plan, for any demand indication on any SBCV, a reactor operator placed the SBCS to EMERGENCY OFF. The SBCVs quick closed and reactor power returned to normal. No safety system responses occurred and none were required.<br /><br /> The SBCS perturbation occurred when the SBCS Mode Selection Switch was positioned from OPERATE to VALVE TEST in order to perform the SBCV 1005 quick open retest. The effect of the switch anomaly has been documented since 1986 and procedures were updated to include a precaution to switch the SBCS Master Controller to MANUAL mode prior to positioning the SBCS Mode Selection Switch. Until the recent implementation of a design change package to optimize the SBCS, the procedural precaution had been adequate to prevent inadvertent SBCV motion when positioning to VALVE TEST.
5301993003 | Palo Verde 3 | 07/03/1993 | 09/24/1993 | 9310010051 | <strong>Emergency Diesel Generator Unable to Start and Run in Manual Test Mode</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1993, APS management determined that Unit 3's Emergency Diesel Generator B, (EDG-B) had been inoperable from July 3, 1993 to July 10, 1993. From July 3, 1993 to July 10, 1993, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power. During that period, EDG-B was not capable of satisfying the Technical Specifications Surveillance Requirement (TS SR) 4.8.1.1.2.a.4 in Manual Test mode. However, EDG-B remained capable of performing its specified safety function in Emergency mode (i.e., standby power source that is capable of starting and loading as required by an emergency automatic start signal to provide the power required for safe shutdown). On July 27, 1993, the event was determined not to be reportable under 10CFR50.73 as a condition that could have prevented the safe shutdown of the plant or as a condition prohibited by TS. On August 19, 1993, it was identified that the current licensing basis for the EDG provides for manual starting control and demonstration of operability by starting in the Manual Test mode. Based on the apparent discrepancy between the specified safety function and the current licensing basis, APS management determined that EDG-B had been inoperable from July 3, 1993 to July 10, 1993. Therefore, a condition prohibited by TS had occurred when the unit did not comply with TS Limiting Condition for Operation (LCO) 3.8.1.1 ACTION b (i.e., restore the EDG to OPERABLE status within 72 hours). <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301993004 | Palo Verde 3 | 11/03/1993 | 11/20/1993 | 9312060238 | <strong>Manual Reactor Trip Following Control Rod Misalignment</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1993, at approximately 1619 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 24 percent power when Control Room personnel manually tripped the reactor when it was recognized that subgroup 5 of control element assembly (CEA) regulating group 4 had slipped into the reactor core during reactor power reduction. All CEAs inserted as designed. The reactor trip was followed by a Main Turbine/Main Generator trip. By approximately 1630 MST on November 3, 1993, the plant was stabilized in Mode 3 (HOT STANDBY) and the Shift Supervisor diagnosed the event as an uncomplicated reactor trip. No Engineered Safety Feature Actuation System actuations occurred and none were required. All plant equipment responded as designed. <br /><br /> The cause of the subgroup 5 of CEA regulating group 4 slip could not be determined. No problems or abnormalities that could have contributed to the subgroup slip were found during the performance of the troubleshooting. Since the event could not be recreated, APS management determined that the most probable components that could cause the event (i.e., subgroup 5 supply breaker and phase synchronizing cards) would be replaced.<br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301993005 | Palo Verde 3 | 03/09/1993 | 03/05/1998 | 9803100025 | <strong>Missed Technical Specification ACTION Statement Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1993, at approximately 2010 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when the requirement of Technical Specification Limiting Condition for Operation (TS LCO) 3.8.1.1 ACTION b for one emergency diesel generator inoperable was not met within the one hour allowed by TS. Between 0200 MST and 0400 MST on March 10, 1993, Control Room personnel discovered the missed TS LCO ACTION and subsequently performed the surveillance satisfactorily. <br /><br /> The cause of the event was attributed to personnel error. The root cause of the personnel error was indeterminate due to limited information available after five years had lapsed since the event occurred. The NRC initially identified the event in late 1997. The APS investigation surrounding the event was completed by APS on February 10, 1998. The APS investigation determined that an LER was required to be submitted to report the event. As corrective action, appropriate disciplinary action was issued to applicable Control Room personnel. <br /><br /> No previous similar events have been reported pursuant to 10CFR50.73.